## Sheet1
Project Name | Categoría* | Project Filed by | Region/Municipality | Filing Date | Funds |  | Estimated Cost ($M) | Contract Costs ($M) | Approval Energy Bureau |  | Project Phase |  |  |  |  | Comentarios | Plant | RO Date
[5 empty] | Origin | Disbursement Amount |  |  | Cost ($) | Date | Phase** | Permits Status | Start Date | Completition Date | % Completed
Generation Aguirre Black Start | G | PREPA | Salinas | 2021-04-28 |  |  | 45.2 | [9 empty] | Aguirre | 2021-06-08
FAASt Cambalache Power Plant – Flood Protection Barrier – Generation | G | PREPA | Arecibo | 2021-04-28 | Federal |  | 4 |  |  |  | Planning | 75% |  |  |  |  | Cambalache | 2021-06-08
Mobile Generation Units Purchases | G | PREPA | Island Wide | 2021-04-28 | Federal |  | 59.8 |  |  |  | Completed |  | 2019-05-21 | 2020-08-22 | 100% |  | Island Wide | 2021-06-08
Palo Seco Steam Plant Repairs | G | PREPA | Cataño | 2021-08-20 | Federal-Insurance |  | 2.55 | [9 empty] | Palo Seco | 2021-09-08
New Simple Cycle Gas Turbines at Yabucoa | G | PREPA | Yabucoa | 2021-09-08 | Federal |  | 45.2 |  |  |  | Design | [5 empty] | Yabucoa | 2021-09-28
Raw Water Tanks 1 & 2 | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto/Fiona) |  | 3 | 5 | 40200000 | 2020-05-22 | Construction |  | 2022-04-12 | 2025-04-30 | 55% |  | Costa Sur | 2021-12-01
Demin Water Tanks 5 & 6 | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto) |  | 4.1 | 3.95 |  | 2020-05-22 | Completed |  | 2021-07-06 | 2022-12-16 | 100% |  | Costa Sur | 2021-12-01
Diesel Service Tank | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto) |  | 1 |  |  | 2020-05-22 | Planning |  |  |  |  | The Repair of this tank may be discarded, depending on the New Lay out of the Peakers for CS Powe Plant. | Costa Sur | 2021-12-01
Water Discharge Channel | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto/Fiona) |  | 6.7 | 5.7 |  | 2020-05-22 | Construction |  | 2021-03-30 | 2025-05-15 | 10% | Pending to complete a negotiation for Value Engineering. To start pile driving on May 2024. | Costa Sur | 2021-12-01
Control Room 5 & 6 | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto) |  | 0.41 | 0.41 |  | 2020-05-22 | Completed |  | 2020-05-11 | 2020-07-24 | 100% |  | Costa Sur | 2021-12-01
Main Power Transformers 4, 5 & 6 | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto) |  | 0.08 | 0.08 |  | 2020-05-22 | Completed |  | 2020-06-01 | 2020-11-20 | 100% |  | Costa Sur | 2021-12-01
Boilers 5 & 6 | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto) |  | 0.71 | 0.71 |  | 2020-05-22 | Completed |  | 2020-05-18 | 2020-11-30 | 100% |  | Costa Sur | 2021-12-01
Condensate Water Tank 5 | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto) |  | 0.35 | 0.35 |  | 2020-05-22 | Completed |  | 2020-05-18 | 2020-07-31 | 100% |  | Costa Sur | 2021-12-01
New Condensate Water Tank 6 | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto) |  | 0.85 | 0.85 |  | 2020-05-22 | Completed |  | 2020-09-14 | 2021-01-13 | 100% |  | Costa Sur | 2021-12-01
Structural Repairs Units 1-4 | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto) |  | 0.86 | 0.73 |  | 2020-05-22 | Completed |  | 2020-07-16 | 2020-09-17 | 100% |  | Costa Sur | 2021-12-01
Old Demi Plant | G | PREPA | Guayanilla | 2021-11-08 | Federal (Terremoto) |  | 0.21 | 0.21 |  | 2020-05-22 | Completed |  | 2020-06-08 | 2020-07-11 | 100% |  | Costa Sur | 2021-12-01
Sanitary Water Pumping System | G | PREPA | Arecibo | 2021-12-01 | Insurance-Federal (Hurricane Maria) |  | 0.06 | 0.06 |  |  | Completed |  | 2018-07-12 | 2021-01-15 | 100% |  | Cambalache | 2021-12-20
Hydraulic Equipment | G | PREPA | Arecibo | 2021-12-01 | Insurance-Federal (Hurricane Maria) |  | 0.04 | 0.04 |  |  | Completed |  | 2017-09-21 | 2018-09-30 | 100% |  | Cambalache | 2021-12-20
Different Areas | G | PREPA | Arecibo | 2021-12-01 | Insurance-Federal (Hurricane Maria) |  | 0.2 | 0.2 |  |  | Completed |  | 2017-10-13 | 2018-09-18 | 100% |  | Cambalache | 2021-12-20
Different AC units of the Plant | G | PREPA | Arecibo | 2021-12-01 | Insurance-Federal (Hurricane Maria) |  | 0.05 | 0.05 |  |  | Completed |  | 2017-12-14 | 2018-03-14 | 100% |  | Cambalache | 2021-12-20
Generation Plant Fences | G | PREPA | Arecibo | 2021-12-01 | Insurance-Federal (Hurricane Maria) |  | 0.2 | 0.2 |  |  | Completed |  | 2018-02-05 | 2018-09-18 | 100% |  | Cambalache | 2021-12-20
Storm Water Pump System | G | PREPA | Arecibo | 2021-12-01 | Insurance-Federal (Hurricane Maria) |  | 0.34 | 0.34 |  |  | Completed |  | 2018-06-05 | 2020-02-03 | 100% |  | Cambalache | 2021-12-20
Fuel Transfer Pump | G | PREPA | Arecibo | 2021-12-01 |  |  | 0 | 0 |  |  | Completed |  | 2017-10-23 | 2017-11-14 | 100% |  | Cambalache | 2021-12-20
Cable Trays | G | PREPA | Arecibo | 2021-12-01 | Insurance-Federal (Hurricane Maria) |  | 0.06 | 0.06 |  |  | Completed |  | 2017-09-15 | 2017-09-30 | 100% |  | Cambalache | 2021-12-20
Lighting | G | PREPA | Arecibo | 2021-12-01 | Insurance-Federal (Hurricane Maria) |  | 0.04 | 0.04 |  |  | Completed |  | 2018-07-24 | 2018-10-28 | 100% |  | Cambalache | 2021-12-20
Gas Generator | G | PREPA | Mayaguez | 2021-12-01 |  |  | 0.01 | [9 empty] | Mayaguez | 2021-12-20
Brush Generator | G | PREPA | Mayaguez | 2021-12-01 |  |  | 0.07 | [9 empty] | Mayaguez | 2021-12-20
Fuel Tank 1 | G | PREPA | Mayaguez | 2021-12-01 | NME |  | 0.03 |  |  |  | Design |  | 2024-11-15 | 2025-11-14 |  | Specifications to be submitted on February 2024 to start procurement process. | Mayaguez | 2021-12-20
Plant Operations | G | PREPA | Mayaguez | 2021-12-01 |  |  | 0.08 | [9 empty] | Mayaguez | 2021-12-20
Cooling Towers 3 & 4 | G | PREPA | Cataño | 2021-12-01 | Federal-Insurance |  | 1.43 | 1.44 |  |  | Completed |  | 2018-02-08 | 2018-06-29 | 100% |  | Palo Seco | 2021-12-20
Boilers’ Cameras | G | PREPA | Cataño | 2021-12-01 | Federal-Insurance |  | 0.03 | 0.03 |  |  | Completed |  | 2018-11-01 | 2019-02-25 | 100% |  | Palo Seco | 2021-12-20
Federal Alert System | G | PREPA | Cataño | 2021-12-01 | Federal-Insurance |  | 0.01 | 0.01 |  |  | Completed |  | 2018-01-31 | 2018-04-07 | 100% |  | Palo Seco | 2021-12-20
All Generation Units | G | PREPA | Cataño | 2021-12-01 | Federal-Insurance |  | 1.04 | 1.04 |  |  | Completed |  | 2018-06-25 | 2020-07-31 | 100% |  | Palo Seco | 2021-12-20
Boilers 7 & 8 | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0.41 | 0.41 |  |  | Completed |  | 2020-01-29 | 2020-01-30 | 100% |  | San Juan | 2021-12-20
Boilers 9 & 10 | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0.34 | 0.48 |  |  | Completed |  | 2019-10-03 | 2020-02-01 | 100% |  | San Juan | 2021-12-20
Units 9 & 10 | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0.04 | 0.04 |  |  | Completed |  | 2017-10-28 | 2017-10-28 | 100% |  | San Juan | 2021-12-20
Units 7 & 8 | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0.1 | 0.1 |  |  | Completed |  | 2017-12-30 | 2019-05-20 | 100% |  | San Juan | 2021-12-20
Plant’s Emergency Notification System | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0.01 | 0.01 |  |  | Completed |  | 2018-05-17 | 2018-05-18 | 100% |  | San Juan | 2021-12-20
Dikes R1, R2, R3, R4 | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0.1 | 0.1 |  |  | Completed |  | 2019-05-18 | 2019-10-19 | 100% |  | San Juan | 2021-12-20
Boiler’s Dining Room AC | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0 | 0.004 |  |  | Completed |  | 2019-01-29 | 2019-01-29 | 100% |  | San Juan | 2021-12-20
NPDES office AC | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0 | 0.001 |  |  | Completed |  | 2018-11-30 | 2018-11-30 | 100% |  | San Juan | 2021-12-20
Units 5 & 6 | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0.02 | 0.02 |  |  | Completed |  | 2018-05-17 | 2018-05-18 | 100% |  | San Juan | 2021-12-20
General Mechanic Workshop | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0.19 | 0.19 |  |  | Completed |  | 2019-03-04 | 2019-04-05 | 100% |  | San Juan | 2021-12-20
Power Plant Rehabilitation contracts | G | PREPA | San Juan | 2021-12-01 | Federal-Insurance |  | 0.17 | 0.17 |  |  | Completed |  | 2018-11-15 | 2019-03-31 | 100% |  | San Juan | 2021-12-20
Units 5 and 6 Cooling Tower Replacement | G | PREPA | San Juan | 2022-01-13 | Federal |  | 1.89 | 1.41 | 1.89 | 2022-02-10 | Completed |  | 2022-02-07 | 2022-12-22 | 100% |  | San Juan | 2022-02-10
Units 5 and 6 Condenser Repair and Coating Application | G | PREPA | San Juan | 2022-01-13 | Federal (50%)/NME (50%) |  | 1.03 | 1.04 | 1.04 | 2022-02-10 | (1) Completed, (1) in Procurement |  | 2022-02-26 | 2024-10-22 | 50% |  | San Juan | 2022-02-10
Units 5 and 6 High Pressure Bleed Valve, Low Pressure Bleed Valve and Heat Injection Steam Valve | G | PREPA | San Juan | 2022-01-13 | Federal |  | 0.37 | 0.37 | 0.37 | 2022-02-10 | Completed |  | 2021-12-09 | 2022-05-20 | 100% |  | San Juan | 2022-02-10
Units 5 and 6 Black Start Emergency Generator Upgrade | G | PREPA | San Juan | 2022-01-13 | Federal |  | 0.35 | 0.35 | 0.35 | 2022-02-10 | Completed |  | 2022-10-24 | 2023-12-31 | 100% |  | San Juan | 2022-02-10
Units 5 and 6 1Replacement of Outlet Valves and Elbow Condenser | G | PREPA | San Juan | 2022-01-13 | Federal |  | 0.67 |  | 0.67 | 2022-02-10 | Completed |  | 2022-01-24 | 2023-01-31 | 100% |  | San Juan | 2022-02-10
Control System Upgrade units 5 & 6 | G | PREPA | San Juan | 2022-01-13 | Federal |  | 3.2 | 3.2 | 3.2 | 2022-02-10 | Completed |  | 2022-01-24 | 2023-03-14 | 100% |  | San Juan | 2022-02-10
Installation of Modules D&E HRSG Unit 5 | G | PREPA | San Juan | 2022-01-13 | Federal |  | 9.75 |  | 9.75 | 2022-02-10 | Completed |  | 2022-02-17 | 2022-06-20 | 100% |  | San Juan | 2022-02-10
Replacement of the Online Condenser Cleaner Unit 5 | G | PREPA | San Juan | 2022-01-13 | Federal |  | 3.6 |  | 3.6 | 2022-02-10 | Procurement |  | 2024-04-30 | 2025-12-31 |  | Bidders Questions answered. 02/12/2024. Procurement process | San Juan | 2022-02-10
Replacement of Load Center 1- 4 Condenser Circulating Water Pump | G | PREPA | Salinas | 2022-01-13 | Federal |  | 0.63 |  | 0.63 | 2022-02-10 | Procurement |  | 2024-04-15 | 2025-09-30 |  | Awarding process is in progress PO 101421 | Aguirre | 2022-02-10
Sea Water Intake Structural Repairs Work | G | PREPA | Salinas | 2022-01-13 | Federal |  | 5.27 |  | 5.27 | 2022-02-10 | Permitting |  | 2024-08-31 | 2025-08-31 |  |  | Aguirre | 2022-02-10
Rehabilitation Fuel Tank Farm Liners | G | PREPA | Salinas | 2022-01-13 | Federal |  | 1.29 | 1.67 | 1.29 | 2022-02-10 | Completed |  | 2023-03-20 | 2024-02-22 | 100% | Turn Over Package in process. Expected due date on 2-23-24. | Aguirre | 2022-02-10
Two New Condenser Discharge Water Pumps Motors | G | PREPA | Salinas | 2022-01-13 | Federal |  | 0.75 | 0.64 | 0.75 | 2022-02-10 | Completed |  | 2022-02-11 | 2022-07-28 | 100% |  | Aguirre | 2022-02-10
Two New CCWP Motors | G | PREPA | Salinas | 2022-01-13 | Federal |  | 0.64 |  | 0.64 | 2022-02-10 | Procurement |  | 2024-04-25 | 2025-04-24 |  | CR-284433 was prepared and is on the approval prcess as of 2/1/2024. | Aguirre | 2022-02-10
Aguirre Combine Cycle plant Permanent Repairs | G | PREPA | Salinas | 2022-01-13 |  |  | 0.72 |  | 0.72 | 2022-02-10 | [6 empty] | Aguirre | 2022-02-10
Aguirre CC- Hot Gas Path Inspection Work Units 1-1 and 1-2 | G | PREPA | Salinas | 2022-01-13 | Federal/NME |  | 1.09 |  | 1.09 | 2022-02-10 | Construction |  | 2022-06-17 | 2023-12-31 | 50% | U1-1 was completed. U1-2 in Planning. | Aguirre | 2022-02-10
Unit 1 - Major Inspection (Replacement Turbo- Generator) | G | PREPA | Salinas | 2022-01-13 | Federal |  | 11.16 | 12.5 | 11.16 | 2022-02-10 | Completed |  | 2022-03-28 | 2023-03-07 | 100% |  | Aguirre | 2022-02-10
Unit 2 Excitation System | G | PREPA | Salinas | 2022-01-13 | Federal |  | 1.52 | 1.52 | 1.52 | 2022-02-10 | Construction |  | 2022-04-25 | 2024-04-30 | 85% | Equipment is at U.S. Coordination is underway for installation on April 1, 2024. | Aguirre | 2022-02-10
Design Fire Pump for Aguirre Power Complex | G | PREPA | Salinas | 2022-01-13 | Federal |  | 0.28 | 0.18 | 0.28 | 2022-02-10 | In Progress |  | 2024-02-23 | 2024-06-23 | 1% |  | Aguirre | 2022-02-10
Procurement of Air-Preheaters Baskets, Unit 5 | G | PREPA | Guayanilla | 2022-01-13 | Federal |  | 1.97 | 1.1 | 1.97 | 2022-02-10 | Completed |  | 2021-12-20 | 2022-06-22 | 100% |  | Costa Sur | 2022-02-10
Procurement of Condenser Circulating Water Pump (CCWP) and Boiler Circulating Water Pump (BCWP) Spare Motors for Units 5 and 6 | G | PREPA | Guayanilla | 2022-01-13 | Federal |  | 0.87 |  | 0.87 | 2022-02-10 | Procurement |  | 2024-03-31 | 2025-05-31 | 50% | CCWP CR-252638 RFP 422, BCWP CR-252637 PO-101391 was signed by contractor. | Costa Sur | 2022-02-10
Replacement of Unit 5 Electric Load Center | G | PREPA | Guayanilla | 2022-01-13 | Federal |  | 0.29 | 0.29 | 0.29 | 2022-02-10 | Construction |  | 2022-11-30 | 2025-01-31 | 25% | Awaiting procurement if contractor accepts federal clauses. If not, Genera will pay for NME equipment that is in fabrication. Expected to arrive Sept 2024 (2.8.24 Extend contract to Dec 2024). | Costa Sur | 2022-02-10
BFWP Inner Barrel Bundle | G | PREPA | Guayanilla | 2022-01-13 | NME |  | 1.63 | 1.63 | 1.63 | 2022-02-10 | Construction |  | 2021-09-15 | 2024-03-22 | 98% |  | Costa Sur | 2022-02-10
Mega-Gens Environmental Commissioning | G | PREPA | Cataño | 2022-01-13 | NME |  | 1.04 | 1.38 |  |  | Completed |  | 2021-08-30 | 2022-12-31 | 100% |  | Palo Seco | 2022-02-10
Unit 1A, 1B and 4A Rehabilitation | G | PREPA | Mayaguez | 2022-01-13 | Federal |  | 18 | 18 | 18 | 2022-02-10 | Completed | [5 empty] | Mayaguez | 2022-02-10
Inner Barrel Bundle | G | PREPA | Salinas | 2022-01-25 | Federal |  | 1.63 | 1.63 | 1.63 | 2022-02-18 | Construction |  | 2022-10-17 | 2024-04-30 | 70% | In manufacturing. A site visit by Operations is being coordinated for assembly of the Bundle. | Aguirre | 2022-02-18
Replacement of Excitation System Units 5 and 6 | G | PREPA | Guayanilla | 2022-01-25 | Federal |  | 2.76 | 1.56 | 2.76 | 2022-02-18 | Construction/Procurement |  | 2022-11-17 | 2025-06-30 | 40% | U5 PO-97370 change request was approved, replace installation for U6. Equipo propuesto para llegar Feb. 2024. $1,564,397. U5 CR-252645 se envio para ruta de aprobacion, esta aprobado. $1,196,537. | Costa Sur | 2022-02-18
Unit 6 LP-B Installation Work (Failure) | G | PREPA | Guayanilla | 2022-01-25 | Federal |  | 2.09 | 2.08 | 2.08 | 2022-02-18 | Completed |  | 2021-10-13 | 2021-12-22 | 100% |  | Costa Sur | 2022-02-18
Fuel Tanks Level Measurement System | G | PREPA | Cataño | 2022-01-25 | Federal |  | 0.55 | 1.56 | 0.55 | 2022-02-18 | Completed |  | 2023-06-13 | 2024-02-05 | 100% | Substantial completion was accepted. Punch list was send to contractor. Contractor is working on the punch list. | Palo Seco | 2022-02-18
Water Retention Tank Num. 3 | G | PREPA | Cataño | 2022-01-25 | Federal |  | 0.8 | 0.65 | 0.8 | 2022-02-18 | Completed |  | 2022-12-12 | 2023-05-31 | 100% |  | Palo Seco | 2022-02-18
Contract, on request, for Crane Services PS4 | G | PREPA | Cataño | 2022-01-25 | NME |  | 0.7 | 0.7 | 0.7 | 2022-02-18 | In Progress |  | 2022-08-19 | 2024-06-30 |  | This is a Services Upon Request Contract based on necessities. | Palo Seco | 2022-02-18
Upgrade OSI DCS | G | PREPA | Cataño | 2022-01-25 | Federal |  | 1.15 |  | 1.15 | 2022-02-18 | Planning/Design |  | 2024-04-30 | 2025-02-28 |  | Proposal was submitted back to GE Caribe for final revision. | Palo Seco | 2022-02-18
Procurement of Water Heater 5 (Deaerator) Spare Pump | G | PREPA | Guayanilla | 2022-02-02 | Federal |  | 0.4 | 0.4 | 0.4 | 2022-02-24 | Completed |  | 2022-10-07 | 2023-04-14 | 100% |  | Costa Sur | 2022-02-28
Procurement of Induced Draft Fan (IDF) and Forced Draft Fan (FDF) Spare Motors for Units 5 and 6 | G | PREPA | Guayanilla | 2022-02-02 | Federal |  | 1.16 |  | 1.16 | 2022-02-24 | Procurement |  | 2024-04-30 | 2025-05-31 |  | Procurement IDF CR-252640 RFP-4217, FDF CR-252642 RFP-4206 | Costa Sur | 2022-02-28
Procurement of Condensate Pump (CP) Motor for Units 5 and 6 | G | PREPA | Guayanilla | 2022-02-02 | Federal |  | 0.87 |  | 0.87 | 2022-02-24 | Procurement |  | 2024-05-31 | 2025-04-15 |  | Procurement CR-255079 RFP-4224 | Costa Sur | 2022-02-28
Replacement of 4160 V Electric Cable Normal Transformer 5A, 5B | G | PREPA | Guayanilla | 2022-02-02 | Federal |  | 0.38 |  | 0.38 | 2022-02-24 | Completed |  | 2022-07-20 | 2023-12-17 | 100% |  | Costa Sur | 2022-02-28
AGC - Replacement Project | G | PREPA | Guayanilla | 2022-02-02 | NME |  | 0.4 | 0.4 | 0.4 | 2022-02-24 | Completed |  |  |  | 100% | Plant personnel carried out the project with Genera's budget. | Costa Sur | 2022-02-28
Fuel Igniters Procurement and Replacement Work | G | PREPA | Guayanilla | 2022-02-02 | Federal/NME |  | 2.36 | 2.03 | 2.36 | 2022-02-24 | Construction |  | 2021-03-01 | 2025-12-31 | 75% | Purchase of equipment PO-92497, Material purchased. Project has been paid ($2,033,000). Installation will be with NME account PO 98525. Federal - Equipment Purchase; NME - Installation. | Costa Sur | 2022-02-28
New Water Condensate 1-2 Tank | G | PREPA | Cataño | 2022-02-02 | Federal |  | 1 | 1.66 | 1 | 2022-02-24 | Completed |  | 2023-01-25 | 2023-12-27 | 100% | Final Acceptance accomplished on 02-12-2024. | Palo Seco | 2022-02-28
Unit PS3 - Major Outage - Boiler Sections Replacement and Repairs; MPT, Generator and turbine Repair & Auxiliary Equipment Inspection Work | G | PREPA | Cataño | 2022-02-02 | Federal |  | 15 | 15 | 15 | 2022-02-24 | Construction |  | 2024-01-03 | 2024-05-30 | 25% |  | Palo Seco | 2022-02-28
Control System Power Plant Maintenance -Generator and Technical Services | G | PREPA | Arecibo | 2022-02-02 | NME |  | 2.5 | 2.5 | 2.5 | 2022-02-24 | In Progress |  | 2022-07-01 | 2024-06-30 | 75% | Services Contract Upon Request Control Systems Maintenance Work | Cambalache | 2022-02-28
Automatic Voltage Regulator & SFC Upgrade for 2 Units | G | PREPA | Arecibo | 2022-02-02 | Federal |  | 1.04 | 1.04 | 1.043 | 2022-02-24 | Construction |  | 2022-03-10 | 2025-06-30 | 90% |  | Cambalache | 2022-02-28
LTSA Units Camb 1-2-3 | G | PREPA | Arecibo | 2022-02-02 | NME |  | 12 |  | 12 | 2022-02-24 | Construction | [5 empty] | Cambalache | 2022-02-28
Unit 5 SCR - Ammonium Procurement | G | PREPA | San Juan | 2022-02-02 | Operational |  | 0.5 | 0.5 | 0.5 | 2022-02-24 | In Progress | [5 empty] | San Juan | 2022-02-28
Units 5 and 6 New High Pressure Pumps | G | PREPA | San Juan | 2022-01-28 | Federal |  | 1.6 | 1.6 | 1.6 | 2022-03-09 | Construction |  | 2023-02-09 | 2024-04-30 | 70% | MR-748156 PO-98466. ESI's Keila Hernández informed Eng. Molina that new pumps drawings will NOT be submitted (01-09-2024) | San Juan | 2022-03-09
Unit 7 Air Preheater Maintenance and Replacement | G | PREPA | San Juan | 2022-01-28 | Federal |  | 0.6 | 0.4 | 0.6 | 2022-03-09 | Construction |  | 2023-06-05 | 2023-08-15 | 100% | All documents were received. DCMC Partnesr has already started requesting documents for the claim. 02/22/2024 | San Juan | 2022-03-09
Repairs to Nautilus Water Treatment System | G | PREPA | San Juan | 2022-01-28 | Federal |  | 0.25 | 0.1 | 0.25 | 2022-03-09 | Completed |  | 2022-10-04 | 2023-03-24 | 100% |  | San Juan | 2022-03-09
Replacement of Two Uninterruptible Power Supply Systems for Units 7 and 8 | G | PREPA | San Juan | 2022-01-28 | Federal |  | 0.45 | 0.74 | 0.45 | 2022-03-09 | Construction |  | 2023-03-15 | 2024-06-30 | 35% | Delays to be expected - Equipment to be delivered in March 2024 02/22/2024 | San Juan | 2022-03-09
Units 7-10 New Raw Water Tank | G | PREPA | San Juan | 2022-01-28 | Federal |  | 1 | 1.47 | 1 | 2022-03-09 | Completed |  | 2022-10-31 | 2023-06-30 | 100% |  | San Juan | 2022-03-09
Units 5-10 Heavy Equipment Rental Services | G | PREPA | San Juan | 2022-01-28 | NME |  | 0.85 | 0.85 | 0.85 | 2022-03-09 | In Progress |  | 2022-01-21 | 60/30/24 |  |  | San Juan | 2022-03-09
Water Treatment and Technical Assistance Cooling Water System | G | PREPA | San Juan | 2022-01-28 |  |  | 0.23 |  | 0.23 | 2022-03-09 | [6 empty] | San Juan | 2022-03-09
Unit 6 - Major Overhaul CT Repairs) | G | PREPA | San Juan | 2022-01-28 | Federal |  | 12.77 |  | 12.77 | 2022-03-09 | Procurement |  | 2024-03-22 | 2024-05-31 |  | 80% Planning & Procurement completed for an outage date start on March 24, 2024. CT Repairs under coordination with MPS. Contract Requisition for replacement of battery banks & chargers is currently undergoing. Will recommend to specify current Cyberex equipment configuration, as no other single manfuacturer package of battery UPS bank - charger combination was found in compliance with the plant's needs. | San Juan | 2022-03-09
Unit 6 - Major Overhaul (Steam Turbine) | G | PREPA | San Juan | 2022-01-28 | Federal |  | 12.77 |  | 12.77 | 2022-03-09 | Procurement |  | 2024-11-01 | 2025-02-15 |  | Bid process for ST Repair resumed as RFP 4172. Pre-bid meeting held on 11/21/2023. Closing date for submitting proposals on February 15, 2024. //2.12.24-80% Planning// | San Juan | 2022-03-09
Procurement of Stages 1, 2, 3 Turbine Rotor Bucket Set, Aguirre Combined Cycle | G | PREPA | Salinas | 2022-01-28 | Federal |  | 0.5 |  | 0.5 | 2022-03-09 | Completed |  | 2022-06-17 | 2022-07-07 | 100% |  | Aguirre | 2022-03-09
New Water Condensate Tank for the Aguirre Combined Cycle | G | PREPA | Salinas | 2022-01-28 | Federal |  | 0.41 | 1.35 | 0.41 | 2022-03-09 | Construction |  | 2023-01-30 | 2023-04-10 | 98% | Large pumps are behind schedule, no confirmed delivery date. This week they are finishing pending work and the preparation of the final list. 02/08/2024 | Aguirre | 2022-03-09
Major inspection Unit 1-3 | G | PREPA | Salinas | 2022-01-28 | Federal |  | 2.56 |  | 2.56 | 2022-03-09 | Procurement |  | 2024-04-25 | 2024-08-31 |  | 95% progress in procurement for both unit 1-3 Major Overhaul. Award notification issued. | Aguirre | 2022-03-09
Purchase and Installation Breakers 480 V | G | PREPA | Salinas | 2022-01-28 | Federal |  | 0.35 |  | 0.31 | 2022-03-09 | Procurement |  | 2024-04-15 | 2024-06-30 |  |  | Aguirre | 2022-03-09
Travelling Screens Replacement | G | PREPA | Guayanilla | 2022-01-28 | Federal |  | 5 |  | 5 | 2022-03-09 | Permitting/Procurement |  | 2024-07-01 | 2025-12-31 |  | Design & Permits Phase completed. CR 270402 under review snce 12-26-2023. H Jimenez/Procurement Pending | Costa Sur | 2022-03-09
Procurement and Replacement of Regulator Valves for Boiler Feed Water Units 5 & 6 | G | PREPA | Guayanilla | 2022-01-28 | Federal |  | 0.3 | 0.3 | 0.3 | 2022-03-09 | Completed |  | 2024-07-01 | 2025-06-30 |  | Unit 5 completed. In Planning Unit 6// Contrato U6 102043 | Costa Sur | 2022-03-09
Low Pressure Water Heater 3 Repair Work | G | PREPA | Guayanilla | 2022-01-28 | Federal |  | 0.4 | 0.91 | 0.4 | 2022-03-09 | Completed |  | 2022-02-17 | 2023-11-21 | 100% |  | Costa Sur | 2022-03-09
CS 5 Major Outage Unit 5 - Boiler Sections Replacement and Repairs & Auxiliary Equipment Repairs | G | PREPA | Guayanilla | 2022-01-28 | Federal |  | 9 | 0.65 | 9 | 2022-03-09 | Design |  | 2023-08-01 | 2025-12-31 |  | Original Budet of $9,000,000 was reduced by $649,455 (Contracts 100997, 101262) which are two projects covered under this FEMA project. This two projects are completed. Genera is doing planning and design of specs for the procurement of auxiliary equipment, such as compressors, motors, pumps and boiler parts for this units for future replacement. | Costa Sur | 2022-03-09
Water Heater 6 Replacement Work | G | PREPA | Guayanilla | 2022-01-28 | Federal |  | 2 |  | 2 | 2022-03-09 | Planning |  | 2023-08-01 | 2024-12-31 |  | This item will be managed by CPM Major Equipment Replacement | Costa Sur | 2022-03-09
Upgrade to Mark Vie | G | PREPA | Cataño | 2022-01-28 | Federal |  | 0.5 |  | 0.5 | 2022-03-09 | Planning/Design |  | 2024-05-15 | 2025-05-14 |  | Proposal was submitted back to GE Caribe for final revision. | Palo Seco | 2022-03-09
Replacement of Air-Preheaters Baskets, Unit 5 | G | PREPA | Guayanilla | 2022-02-08 | Federal |  | 0.7 |  | 0.7 | 2022-04-13 | Design |  | 2024-12-01 | 2025-01-12 |  | 2.8.24 Consultar con Jesús Cintrón //SOW Instalation ( Att J. Perez)-12-13-23 Interview W SOUCO CE - M Beauchamp. JC Mechanical meeting Pending. Expected Project Submission compliance subjected to PMO/SOUCO meeting regarding Funding Issues). No Change | Costa Sur | 2022-04-13
CS 5Major Inspection Unit 5 - HP/IP/LP Turbine Rotor Replacement | G | PREPA | Guayanilla | 2022-02-08 | Federal |  | 5.9 | 13.78 | 5.9 | 2022-04-13 | Completed |  | 2024-04-01 | 6/62/24 | 100% | Project completed. Only waiting for Balance Man from MD&A and unit to be ready for start up. | Costa Sur | 2022-04-13
Caustic Soda and Acid Tanks Replacement Works | G | PREPA | Guayanilla | 2022-02-08 | Federal |  | 0.75 | 0.48 | 0.75 | 2022-04-13 | Construction |  | 2022-10-11 | 2024-05-31 | 64% | Steel Catwalks on Fabrication Process. Expect to perform installation during April 2024. | Costa Sur | 2022-04-13
Unit 6 - HP/IP/LP Inspection (Failure) | G | PREPA | Guayanilla | 2022-02-08 | NME |  | 1.06 | 0 | 1.06 | 2022-04-13 | Planning |  | 2021-10-31 | 2021-12-22 | 100% | This Project was performed under Unit 6 LP-B Installation Work (Failure) | Costa Sur | 2022-04-13
Steam Rotor Replacement Unit 5 & CT Repairs | G | PREPA | San Juan | 2022-02-14 | Federal |  | 12.06 | 12.06 | 12.06 | 2022-04-13 | Completed |  | 2022-04-15 | 2022-06-15 | 100% |  | San Juan | 2022-04-13
LTSA SJ5 | G | PREPA | San Juan | 2022-02-14 | NME |  | 8 | 8 | 8 | 2022-04-13 | Construction |  |  |  | 40% |  | San Juan | 2022-04-13
LTSA SJ6 | G | PREPA | San Juan | 2022-02-14 | NME |  | 8 | 8 | 8 | 2022-04-13 | Construction |  |  |  | 60% |  | San Juan | 2022-04-13
Procurement of Spare Generator Breakers for Frame 5000 Hitachi Gas Turbines | G | PREPA | Hydrogas | 2022-02-14 |  |  | 0.65 |  | 0.65 | 2022-04-13 | [6 empty] | Hydrogas | 2022-04-13
Procurement of Turbo- Compressors for Frame 5000 Gas Turbines | G | PREPA | Hydrogas | 2022-02-14 |  |  | 7.8 |  | 7.8 | 2022-04-13 | [6 empty] | Hydrogas | 2022-04-13
Procurement of Spare Speed Reduction Gear for Frame 5000 Gas Turbines | G | PREPA | Hydrogas | 2022-02-14 |  |  | 1.56 |  | 1.56 | 2022-04-13 | [6 empty] | Hydrogas | 2022-04-13
New Spare Three Exhaust Plenums for Frame 5000 Gas Turbines | G | PREPA | Hydrogas | 2022-02-14 |  |  | 0.78 |  | 0.78 | 2022-04-13 | [6 empty] | Hydrogas | 2022-04-13
Procurement of Three Exhaust Gas Diffusion Ducts for Frame 5000 Gas Turbines | G | PREPA | Hydrogas | 2022-02-14 |  |  | 0.39 |  | 0.39 | 2022-04-13 | [6 empty] | Hydrogas | 2022-04-13
Major Outage Turbo - compressor (CT) 15 units | G | PREPA | Hydrogas | 2022-02-14 |  |  | 39 |  | 39 | 2022-04-13 | [6 empty] | Hydrogas | 2022-04-13
Upgrade to Foxboro Simulation System | G | PREPA | Guayanilla | 2022-02-14 | Federal |  | 0.5 | 0.5 | 0.5 | 2022-04-13 | Planning |  | 2024-06-15 | 2025-07-31 | 5% | LT Automation proposal update was requested. | Costa Sur | 2022-04-13
Stamp R- Mechanical Repairs Works for boilers and turbo Generator Contract. | G | PREPA | Island wide | 2022-02-14 | NME |  | 1.95 | 2.93 | 1.95 | 2022-04-13 | In Progress |  | 2022-05-05 | 2024-06-30 | 75% | Contract for Services Upon Request for Power Plants | Island wide | 2022-04-13
Hydro blasting Service for Condenser | G | PREPA | Island wide | 2022-02-14 | NME |  | 0.65 | 1.3 | 0.95 | 2022-07-11 | In Progress |  | 2022-03-17 | 2024-06-30 | 65% | Contract for Services Upon Request for Power Plants | Island wide | 2022-04-13
Interior Dry Cleaning Service for Boilers. Environmental compliance cleaning of boiler interior | G | PREPA | Island wide | 2022-02-14 | NME |  | 0.85 | 0.85 | 0.85 | 2022-04-13 | In Progress |  | 2022-03-22 | 2024-06-30 | 55% | Contract for Services Upon Request for Power Plants | Island wide | 2022-04-13
Electrical and instrumentatin works in power plants. | G | PREPA | Island wide | 2022-02-14 | NME |  | 0.85 | 1.8 | 0.85 | 2022-04-13 | In Progress |  | 2022-04-11 | 2024-06-30 | 65% | Contract for Services Upon Request for Power Plants | Island wide | 2022-04-13
Procurement Acid for all power plants | G | PREPA | Island wide | 2022-02-14 |  |  | 1 |  | 1 | 2022-04-13 | [6 empty] | Island wide | 2022-04-13
Refractory, Insulation, stack, and painting Application works | G | PREPA | Island wide | 2022-02-14 | NME |  | 1.95 | 3.3 | 1.95 | 2022-04-13 | In Progress |  | 2022-03-23 | 2024-06-30 | 65% | Contract for Services Upon Request for Power Plants | Island wide | 2022-04-13
Scaffolding Inside and outside Boilers works. | G | PREPA | Island wide | 2022-02-14 | NME |  | 1.99 | 4.8 | 1.99 | 2022-04-13 | In Progress |  | 2022-03-29 | 2024-06-30 | 79% | Contract for Services Upon Request for Power Plants | Island wide | 2022-04-13
Waste management Services contract for power plants | G | PREPA | Island wide | 2022-02-14 |  |  | 1 |  | 1 | 2022-04-13 | [6 empty] | Island wide | 2022-04-13
Non Destructive examinationsand inspection services | G | PREPA | Island wide | 2022-02-14 | NME |  | 0.75 | 0.75 | 0.75 | 2022-04-13 | In Progress |  | 2022-06-02 | 2024-06-30 | 60% | Contract for Services Upon Request for Power Plants | Island wide | 2022-04-13
Inspection and maintenance Cargo Elevator | G | PREPA | Island wide | 2022-02-14 | NME |  | 0.9 | 0.9 | 0.9 | 2022-04-13 | In Progress |  | 2022-03-23 | 2024-06-30 | 60% | Contract for Services Upon Request for Power Plants | Island wide | 2022-04-13
Coating application Boilers Structures and Chimneys All Power Plants | G | PREPA | Island wide | 2022-02-14 | NME |  | 3.6 |  | 3.6 | 2022-04-13 | Design |  | 2024-07-31 | 2024-06-30 |  |  | Island wide | 2022-04-13
Cooling tower Unit 10 Repairs (SJ PP) | G | PREPA | San Juan | 2022-02-08 | Federal |  | 0.39 |  | 0.39 | 2022-06-04 | Design |  | 2024-07-01 | 2025-02-15 |  |  | San Juan | 2022-06-04
Structural Repairs Fuel Service Tank 10 (SJ PP) | G | PREPA | San Juan | 2022-02-02 | Federal |  | 0.65 | 0.95 | 0.65 | 2022-06-04 | Completed |  | 2022-10-17 | 2023-09-01 | 100% |  | San Juan | 2022-06-04
Unit PS 3 & 4 Refractory Insulation, scaffolding and Painting Application Works | G | PREPA | Cataño | 2022-01-25 | Federal |  | 0.7 | 1.5 | 0.7 | 2022-06-04 | In Progress |  | 2023-04-10 | 2024-06-30 |  | This is a Services Upon Request Contract based on necessities. | Palo Seco | 2022-06-04
Procurement Turning Gear Sytem Units 3&4 (PS SP) | G | PREPA | Cataño | 2022-01-25 | Federal |  | 0.3 |  | 0.3 | 2022-06-04 | Procurement |  | 2024-04-15 | 2025-02-01 |  | Siemens- aclarar status de vendor en LUMA 11/9/2023 | Palo Seco | 2022-06-04
Unit 4 Superheater header Num 5 Material and Installation (PS SP) | G | PREPA | Cataño | 2022-01-25 | Federal |  | 2.24 |  | 2.24 | 2022-06-04 | Procurement |  | 2024-05-01 | 2025-05-01 |  | Expensive proposal, Request revision and include installation. Luis Lopez, verificar compra de material. Verificar si puede comprarse sole source. | Palo Seco | 2022-06-04
Unit 1 South Wall Boiler Tubing Replacement and Boilers repairsAguirre PP | G | PREPA | Salinas | 2022-06-24 | Federal |  | 5.98 | 5.4 | 5.98 | 2022-07-21 | Completed |  | 2022-03-28 | 2022-06-19 | 100% |  | Aguirre | 2022-07-21
PS 3 Procurement and Delivery of Water Wall Boiler Tubes and Economizer Unit PS3 | G | PREPA | Cataño | 2022-06-24 | Federal |  | 4.03 | 4 | 4.03 | 2022-07-21 | Completed |  | 2022-09-22 | 2023-06-01 | 100% |  | Palo Seco | 2022-07-21
PS 3 Low Pressure Turbine Rotor Refurbished, Unit 3 | G | PREPA | Cataño | 2022-06-24 | Federal |  | 3.5 | 0.7 | 3.5 | 2022-07-21 | Construction |  | 2024-01-03 | 2024-05-30 | 15% |  | Palo Seco | 2022-07-21
Unit 7 Rehabilitation (Turbine) SJ PP | G | PREPA | San Juan | 2022-06-24 | Federal |  | 10 | 10 | 10 | 2022-10-21 | Design |  | 2024-10-29 | 2025-02-28 |  | Awaiting Tech Spec. 02/22/2024 | San Juan | 2022-10-21
Unit 7 Major Outage- Boiler section Replacement and Repairs & Auxiliary Equipment Inspection Work SJ PP | G | PREPA | San Juan | 2022-06-24 | Federal |  | 8 | 8 | 8 | 2022-10-21 | Procurement |  | 2024-10-29 | 2025-02-28 |  | CR approved, auction on February 19, 2024. 02/22/2024. Original Budet of $10,000,000 was reduced by $1,987,511 (PO 99910,) which is Purchase Order of Parts authorized under the PW 11085 | San Juan | 2022-10-21
San Juan Central Plant Unit 6: Installation of Modules D&E HRSG Unit 6 | G | PREPA | San Juan | 2023-03-10 | Federal |  | 12.15 |  | 12.15 | 2023-03-20 | Procurement |  | 2024-11-01 | 2025-02-15 | 50% |  | San Juan | 2023-03-20
Mayaguez Unit 3B Gas Generators Inspections and Repairs | G | PREPA | Mayaguez | 2023-06-22 | NME |  | 4.05 |  |  |  | Planning |  | 2024-05-01 | 2024-08-01 |  |  | Mayaguez | 2023-07-06
Fuel Efficiency Improvement- first group | G | Genera | Island wide | 2023-10-15 |  |  | 106.76 | [9 empty] | Island wide | 2023-11-08
Critical components Replacements | G | Genera | Island wide | 2023-10-15 | Federal |  | 127.32 |  |  |  | Procurement/Design |  |  |  | 10% |  | Island wide | 2023-11-08
Generation Fleet Battery Energy Storage System (BESS) project (430 MW) | G | Genera | Various Municipalities | 2023-10-27 | Federal |  | 647.58 |  |  |  | Procurement |  |  |  | 70% |  | Various Municipalities | 2024-02-01
* Category | [10 empty] | ** Phase
G |  | Generation | Generation | Generation | [6 empty] | D | Design
T |  | Transmition | Transmition | Transmition | [6 empty] | P | Permitting
D |  | Distribution | Distribution | Distribution | [6 empty] | S | Auction
S |  | Substations | Substations | Substations | [6 empty] | C | Construction
H |  | Hydroelectric | Hydroelectric | Hydroelectric
IT |  | IT/Telecom | IT/Telecom | IT/Telecom
Edif. |  | Buildings | Buildings | Buildings
AA |  | Environmental Matters | Environmental Matters | Environmental Matters