## 2024-06-12
LEGACY GENERATION ASSETS FLEET STATUS (Forecast)
2024-06-12
Power Station |  | Unit | Capacity (MW) | Available Capacity | Condition | Outage Date | Expected Return | Comments
Base Generation
San Juan |  | CT 5 | 160 | 155 | Available
|  | STG 5 | 60 | 55 | Available
|  | CT 6 | 160 | 155 | Available
|  | STG 6 | 60 | 55 | Available |  |  | -Start-up process.
|  | 7 | 100 |  | Not available | 2024-03-24 | 2024-06-23 | -The unit had failure in the stator rotor, it is replaced with rotor from unit 10.
|  | 8 | 0 |  | Not available |  |  | Unit off line not return to service : 115 KV Pipe type cable failure. Boiler tube leakage, Feedwater heater 6 water leakage. Boiler air in leakages. Due for major inspection.
|  | 9 | 100 | 90 | Available |  |  | -The unit is limited by high temperature in the generator.
|  | 10 | 0 |  | Not available | 2016-03-13 |  | Unit off line not return to service ; Turbine failure.
Palo Seco |  | 1 |  |  | Not available | 2020-08-01 |  | -Gen failure. Air filtration in boiler. In plan to be retired.
|  | 2 |  |  | Not available |  |  | -Gen failer. Boiler Rupture. In plan to be retired.
|  | 3 | 216 |  | Not available | 2023-11-21 | 2024-06-22 | -Unit out of service for scheduled major and environmental maintenance
|  | 4 | 216 |  | Not available | 2023-08-08 | 2025-02-28 | -The unit had major generator rotor failure. We are working on a competitive process to replace it.
Aguirre |  | 1 | 450 | 325 | Available |  |  | -Unit limited by high differential in the air heaters.
|  | 2 | 450 | 180 | Available |  |  | -Unit limited by low condenser vacuum, problems in the seals of the LP's turbines and chloride pass in the auxiliary condenser.
Costa Sur |  | 5 | 410 | 260 | Available |  |  | -The unit is limited by broken boiler.
|  | 6 | 410 | 370 | Available |  |  | -The unit limited by high pressure differential in the air heaters.
Total Base Generation |  |  | 2792 | 1645 | 58.92% |  |  | Available
Reserve Generation Fleet
Aguirre Combined Cycle |  | 1-1 | 50 | 50 | Available
|  | 1-2 | 50 | 50 | Available
|  | 1-3 | 50 |  | Not available | 2022-02-14 | TBD | -The unit is out of service for major inspection.
|  | 1-4 | 50 |  | Not available | 2022-11-01 | 2024-06-10 | -Unit not available due to failure in the control system.
|  | STG-1 | 96 |  | Not available | 2024-06-11 | 2024-06-12 | -Control system problems.
|  | 2-1 | 50 |  | Not available | 2021-07-10 | 2024-08-01 | -MPT failure, affecting units 2-1 and 2-2.
|  | 2-2 | 50 |  | Not available | 2016-09-17 | 2024-08-01 | -MPT failure, affecting units 2-1 and 2-2.
|  | 2-3 | 50 |  | Not available | 2023-12-28 | 2025-03-01 | -The unit requires a combustion inspection.
|  | 2-4 | 50 | 50 | Available |  |  | -The unit requires major maintenance, including HGPI.
|  | STG-2 | 96 |  | Not available | 2017-06-28 | TBD | -The unit has vibration problems in the turbine and requires repair of auxiliary equipment.
Total Aguirre CC |  |  | 592 | 150 | 25.34% |  |  | Availability
DAGUAO |  | 1-1 | 21 | 20 | Available
|  | 1-2 | 21 |  | Not available | 2024-06-05 | 2024-06-12 | -Generator differential lockout.
AGUIRRE |  | 2-1 | 21 |  | Not available |  |  | -Unit requires major turbine repair and a complete generator assembly.
|  | 2-2 | 21 |  | Not available |  | 2024-08-01 | -Mark I control system calibration and generator balance.
PALO SECO |  | 1-1 | 21 | 18 | Available
|  | 1-2 | 21 | 18 | Available
|  | 2-1 | 21 | 18 | Available
|  | 2-2 |  |  | Not available |  |  | Overdue for major inspection. Unit will be replaced by the new Pratt & Whitney aeroderivative units in terms of air permits.
|  | 3-1 |  |  | Not available |  |  | Unit will be replaced by the new Pratt & Whitney aeroderivative units in terms of air permits.
|  | 3-2 |  |  | Not available |  |  | High Vibrations. Unit will be replaced by the new Pratt & Whitney aeroderivative units in terms of air permits.
PALO SECO |  | MP 1 | 27 | 27 | Available
|  | MP 2 | 27 | 27 | Available
|  | MP 3 | 27 | 27 | Available
COSTA SUR |  | 1-1 | 21 |  | Not available |  |  | -Turbine bearing 2 problems. Need journal repairs.
|  | 1-2 | 21 |  | Not available |  | TBD | -Mark I control system calibration.
JOBOS |  | 1-1 | 21 |  | Not available |  |  | - Generator failure.
|  | 1-2 | 21 | 20 | Available
YABUCOA |  | 1-1 | 21 |  | Not available |  |  | -Generator high vibrations. Generator bearing replacement.
|  | 1-2 | 21 | 16 | Available
VEGA BAJA |  | 1-1 | 21 |  | Not available |  |  | -Turbocompressor replacement.
|  | 1-2 | 21 |  | Not available |  |  | -Turbocompressor major failure.
PS TM 1 |  | 1 | 25 | 23 | Available
PS TM 2 |  | 2 | 25 | 23 | Available
PS TM 3 |  | 3 | 20 | 20 | Available
PS TM 4 |  | 4 | 20 | 20 | Available
PS TM 5 |  | 5 | 30 |  | Available
PS TM 6 |  | 6 | 30 |  | Available
PS TM 7 |  | 7 | 30 |  | Available
SJ TM 1 |  | 1 | 25 | 24 | Available
SJ TM 2 |  | 2 | 25 | 24 | Available
SJ TM 3 |  | 3 | 25 |  | Not available | 2024-06-11 | 2024-07-02 | -HGPI
SJ TM 4 |  | 4 | 25 | 24 | Available
SJ TM 5 |  | 5 | 25 | 24 | Available
SJ TM 6 |  | 6 | 25 | 24 | Available
SJ TM 7 |  | 7 | 25 | 25 | Available
SJ TM 8 |  | 8 | 25 | 25 | Available
SJ TM 9 |  | 9 | 25 | 25 | Available
SJ TM 10 |  | 10 | 25 | 25 | Available
Total Peaking Units |  |  | 826 | 497 | 60.17% |  |  | Availability
MAYAGUEZ |  | 1A | 27.5 | 25 | Available
|  | 1B | 27.5 | 25 | Available
|  | 2A | 27.5 | 25 | Available
|  | 2B | 27.5 | 25 | Available
|  | 3A | 27.5 | 18 | Available
|  | 3B | 27.5 |  | Not available | 2024-04-11 | TBD | -The unit not available due to vibrations in the PT.
|  | 4A | 27.5 | 21 | Available
|  | 4B | 27.5 | 22 | Available
Total Mayaguez |  |  | 220 | 161 | 73.18%
CAMBALACHE |  | 1 | 82.5 |  | Not available | 2011-09-10 | TBD | -Unit out of service, requires major maintenance.
|  | 2 | 82.5 | 77 | Available
|  | 3 | 82.5 | 77 | Available
Total Cambalache |  |  | 247.5 | 154 | 62.22%
VIEQUES |  | 1 | 3.3 |  | Not available | 2024-05-28 | TBD | -Control problems.
|  | 2 | 3.3 |  | Not available | 2024-05-29 | TBD | -Control problems.
CULEBRA |  | 1 | 2.2 | 2.2 | Available
|  | 2 | 2.2 | 2.2 | Available
|  | 3 | 2.2 |  | Not available |  | 2024-07-01 | -Excitation problems.
Total Vieques and Culebra |  |  | 13.2 | 4.4 | 33.33%
Total Peaking & Emergency Units |  |  | 1898.7 | 966.4 | 50.9% |  |  | Availability
HYDROELECTRICS
| Toro Negro | 1-1 | 1.5 | 1.5 | Available
| Toro Negro | 1-2 | 1.5 | 1.5 | Available
| Toro Negro | 1-3 | 1.5 | 1.5 | Available
| Toro Negro | 1-4 | 4.5 | 4.5 | Available
| Toro Negro | 2 | 2 |  | Not Available |  |  | Penstock failure. Repair works currently on-going.
| Yauco | 1 | 25 |  | Not Available |  |  | Pending turbine and generator major overhaul budget approvals.
| Yauco | 2-1 | 4.5 | 4.5 | Available |  |  | Limited pending relay protection system modifications.
| Yauco | 2-2 | 4.5 | 4.3 | Available
| Garzas | 1-1 | 3.6 | 4 | Available
| Garzas | 1-2 | 3.6 |  | Available
| Garzas | 2 | 5 |  | Not Available |  |  | Transmission line failure due to Hurricane Maria.
| Caonillas | 1-1 | 9 |  | Not Available |  |  | Station flooding failure due to Hurricane Maria. In preparation of specifications and bid process documents.
| Caonillas | 1-2 | 9 |  | Not Available |  |  | Station flooding failure due to Hurricane Maria. In preparation of specifications and bid process documents.
| Caonillas | 2 | 3.6 |  | Not Available |  |  | Pending major overhaul budget approvals.
| Dos Bocas | 1 | 5 |  | Not Available |  |  | Generator failure during Hurricane Maria. Pending contract award for generator rewinding works.
| Dos Bocas | 2 | 5 | 5 | Available
| Dos Bocas | 3 | 5 |  | Available
| Patillas | 1-1 | 0.8 |  | Not Available |  |  | Downstream flow risk concerns.
| Patillas | 1-2 | 0.6 |  | Not Available |  |  | Downstream flow risk concerns.
| Río Blanco | 1 | 2.5 |  | Not Available |  |  | Penstock major failure. Pending budget allocation.
| Río Blanco | 2 | 2.5 |  | Not Available |  |  | Penstock major failure. Pending budget allocation.
Total Hydro |  |  | 100.2 | 26.8 | 26.75%
Total GENERA PR |  |  | 4690.7 | 2611.4 | 55.67% |  |  | Available
Private Power Producers
AES |  | 1 | 254 |  | Not available | 2024-05-10 | 2024-06-21 | -Annual scheduled maintenance.
|  | 2 | 254 | 247 | Available
Total AES |  |  | 508 | 247 |  |  |  |  | 13.75
Ecoelectrica |  | CT 1 | 165 | 176 | Available |  |  | -These units have been leaving in coordination due to natural gas supply problems. From May 20 to the present. The ship is expected to arrive on Monday, 27.
|  | CT 2 | 165 | 176 | Available
|  | STM | 200 | 214 | Available
Total Ecoelectrica |  |  | 530 | 566
PRIVATE PRODUCERS GENERATION |  |  | 1038 | 813 | 78.32% |  |  | Available
Hydroelectric |  |  | 99.8 | 16 | Available
RENEWABLES
SOLAR
| AES ILUMINA |  | 20 | 20
| WINDMAR |  | 2.1 | 2.1
| SAN FERMIN |  | 20 | 20
| HORIZON |  | 10 | 10
| ORIANA |  | 45 | 45 |  |  |  | Internal Tests
| COTO LAUREL |  | 10 | 10
| FONROCHE |  | 40 | 40 |  |  |  | Hurricane Maria. Internal Tests.
WIND
| BECHARA |  |  | 0
| PATTERN |  | 75 | 75
| PUNTA LIMA |  |  | 0 |  |  |  | Hurricane Maria
LANDFILL GAS
| FAJARDO |  | 2.4 | 2.4
| TOA BAJA |  | 2.4 | 2.4
TOTAL RENEWABLES |  |  | 226.9 | 226.9 | 100% |  |  | Available
SYSTEM GRAND TOTAL |  |  | 5828.5 | 3440.4 | 59.03% |  |  | Available
SYSTEM GRAND TOTAL |  |  | 5828.9 | 3451.2 | 59.21% |  |  | Available without Renovables
Formulas:
Expected Return = [Outage Date]+21
Operations
Note on I20: Hugal R. Rios Diaz: La unidad salió el 4 de enero por problemas con ESST.
Note on I21: Hugal R. Rios Diaz: La unidad salió el 4 de enero por problemas con ESST.
Note on A57: Hugal R. Rios Diaz: 2024-103-16 GeneraPR tomó administración de estas unidades (14). El costo promedio del gas natural ~15($/MMBtu)
Note on E57: Hugal R. Rios Diaz: Al no tener información suficiente de tomó la decisión de tener disponible lo informado por el TOC. Se hacen gestiones para obtener los datos finales.
Note on A61: Hugal R. Rios Diaz: 2024-03-20 En proceso de ser adquiridas, notificó el Ing. Daniel Hndz.
Note on A64: Hugal R. Rios Diaz: GE TM2500 - Aeroderivative gas turbine. TM -Trailer monted
Note on H123: Hugal R. Rios Diaz: Se recibió email de Daniel con datos de AES con nueva fecha de entrada de AES