VEGA BAJA | 2022-03-31 20:16 | 2022-04-01 07:25 | 35 | 011:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | B22033100216 | New_Event | Bad Weather | Include | Include | Weather | 669 | 2022-03-31 | 23415 | keep | 0 | Mar | 2022 | 0.015948 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-03-31 20:44 | 2022-03-31 21:00 | 4 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R22033100107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2022-03-31 | 64 | keep | 0 | Mar | 2022 | 4.359e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-03-31 20:50 | 2022-03-31 22:18 | 124 | 001:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22033100108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-03-31 | 10912 | keep | 0 | Mar | 2022 | 0.0074321 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
BAYAMON | 2022-03-31 21:13 | 2022-03-31 22:33 | 1587 | 001:20 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | ALIMENTADOR SECCIONALIZADO | S22033100149 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 80 | 2022-03-31 | 126960 | keep | 0 | Mar | 2022 | 0.086472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-31 21:14 | 2022-04-01 05:30 | 6 | 008:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA AVERIADA EN TRANSFORMADOR | A22033100114 | New_Event | Cutout Failure | Include | Include | Equipment | 496 | 2022-03-31 | 2976 | keep | 0 | Mar | 2022 | 0.0020269 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-31 21:27 | 2022-03-31 21:28 | 1935 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA GUARAGUAO AL HACER PRUEBA LINEA 3400 | B22033100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 1935 | keep | 0 | Mar | 2022 | 0.0013179 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2022-03-31 21:27 | 2022-03-31 21:28 | 3 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA GUARAGUAO AL HACER PRUEBA LINEA 3400 | B22033100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 3 | keep | 0 | Mar | 2022 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-31 21:27 | 2022-03-31 21:28 | 61 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA GUARAGUAO AL HACER PRUEBA LINEA 3400 | B22033100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 61 | keep | 0 | Mar | 2022 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-03-31 21:27 | 2022-03-31 21:28 | 1501 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA GUARAGUAO AL HACER PRUEBA LINEA 3400 | B22033100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 1501 | keep | 0 | Mar | 2022 | 0.0010223 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-03-31 21:27 | 2022-03-31 21:28 | 546 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA GUARAGUAO AL HACER PRUEBA LINEA 3400 | B22033100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 546 | keep | 0 | Mar | 2022 | 0.00037188 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
CAGUAS | 2022-03-31 21:47 | 2022-04-01 07:35 | 100 | 009:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22033100530 | New_Event | Vegetation Contact | Include | Include | Vegetation | 588 | 2022-03-31 | 58800 | keep | 0 | Mar | 2022 | 0.040048 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-31 21:51 | 2022-04-01 18:12 | 50 | 020:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22033100532 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1221 | 2022-03-31 | 61050 | keep | 0 | Mar | 2022 | 0.041581 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-31 21:51 | 2022-04-01 10:07 | 45 | 012:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22033100116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 736 | 2022-03-31 | 33120 | keep | 0 | Mar | 2022 | 0.022558 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-03-31 22:33 | 2022-03-31 22:46 | 1984 | 000:13 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO EN RISER FRENTE A GASOLINERA TOTAL - AVE. LUIS VIGOREAUX PARA SECCIONALIZAR AVERIA DEL 1529-12 QUE LLEVA TRANSFERIDA LA CARGA DEL 1911-07 | S22033100085 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 13 | 2022-03-31 | 25792 | keep | 0 | Mar | 2022 | 0.017567 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-31 22:33 | 2022-03-31 22:46 | 577 | 000:13 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO EN RISER FRENTE A GASOLINERA TOTAL - AVE. LUIS VIGOREAUX PARA SECCIONALIZAR AVERIA DEL 1529-12 QUE LLEVA TRANSFERIDA LA CARGA DEL 1911-07 | S22033100085 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 13 | 2022-03-31 | 7501 | keep | 0 | Mar | 2022 | 0.0051089 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-31 22:37 | 2022-04-01 03:45 | 80 | 005:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE VIENTO | M2203310301 | New_Event | Bad Weather | Include | Include | Weather | 308 | 2022-03-31 | 24640 | keep | 0 | Mar | 2022 | 0.016782 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-31 22:46 | 2022-04-01 01:06 | 1587 | 002:20 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | ALIMENTADOR SECCIONALIZADO | S22033100149 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 140 | 2022-03-31 | 222180 | keep | 0 | Mar | 2022 | 0.15133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-31 23:13 | 2022-04-01 03:15 | 50 | 004:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22033100306 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-03-31 | 12100 | keep | 0 | Mar | 2022 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-31 23:22 | 2022-04-01 09:43 | 170 | 010:21 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S22033100705 | New_Event | Vegetation Contact | Include | Include | Vegetation | 621 | 2022-03-31 | 105570 | keep | 0 | Mar | 2022 | 0.071903 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
CANOVANAS | 2022-03-31 23:34 | 2022-03-31 23:39 | 1894 | 000:05 | S | NO SE REPORTO CAUSA | EN DISPARO DEL 2302-01 SE LLEVO LA ALTA | R22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-03-31 | 9470 | keep | 0 | Mar | 2022 | 0.00645 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2022-03-31 23:34 | 2022-03-31 23:39 | 4154 | 000:05 | S | NO SE REPORTO CAUSA | EN DISPARO DEL 2302-01 SE LLEVO LA ALTA | R22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-03-31 | 20770 | keep | 0 | Mar | 2022 | 0.014146 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2022-03-31 23:34 | 2022-03-31 23:39 | 424 | 000:05 | S | NO SE REPORTO CAUSA | EN DISPARO DEL 2302-01 SE LLEVO LA ALTA | R22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-03-31 | 2120 | keep | 0 | Mar | 2022 | 0.0014439 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2022-03-31 23:34 | 2022-04-01 02:45 | 2708 | 003:11 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVANDOSE LA ALTA SE DEJO LA CARGA TRANSFERIADA AL 2302-02. LLEVA EL 40% DEL 2404-05 Y EL 10% DEL 2402-02 | R22033100183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2022-03-31 | 517228 | keep | 0 | Mar | 2022 | 0.35228 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-03-31 23:34 | 2022-03-31 23:46 | 2524 | 000:12 | T | NO SE REPORTO CAUSA | EN DISPARO DEL 2302-01 Y SE LLEVO LA ALTA | R22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-03-31 | 30288 | keep | 0 | Mar | 2022 | 0.020629 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-03-31 23:34 | 2022-03-31 23:46 | 1648 | 000:12 | T | NO SE REPORTO CAUSA | EN DISPARO DEL 2302-01 SE LLEVO LA ALTA | R22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-03-31 | 19776 | keep | 0 | Mar | 2022 | 0.013469 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-03-31 23:34 | 2022-04-01 04:27 | 418 | 004:53 | P | PROTECCION DEFECTUOSA | DISPARO INTERRUPTOR LLEVANDOSE LA ALTA SE DEJO LA CARGA TRANSFERIADA AL 2302-02, 10% DEL 2402-02 POR 2302-01 | R22033100183 | New_Event | Protection Miscoordination | Include | Include | Other | 293 | 2022-03-31 | 122474 | keep | 0 | Mar | 2022 | 0.083416 | 0.0002847 | Sustained | FALSE | FALSE | Not_TMED_Event | 418
CANOVANAS | 2022-03-31 23:34 | 2022-04-01 04:10 | 1385 | 004:36 | P | PROTECCION DEFECTUOSA | DISPARO INTERRUPTOR LLEVANDOSE LA ALTA SE DEJO LA CARGA TRANSFERIADA AL 2302-02, 40% DEL 2404-05 POR 2302-01 | R22033100183 | New_Event | Protection Miscoordination | Include | Include | Other | 276 | 2022-03-31 | 382260 | keep | 0 | Mar | 2022 | 0.26036 | 0.00094332 | Sustained | FALSE | FALSE | Not_TMED_Event | 1385
BARRANQUITAS | 2022-04-01 | 2022-04-01 15:57 | 200 | 015:57 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 25 KVA POR 37.5 KVA | C22040100006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 957 | 2022-04-01 | 191400 | keep | 0 | Apr | 2022 | 0.13036 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-04-01 00:02 | 2022-04-01 10:31 | 2 | 010:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | TOMA SECUNDARIA DERRIBADA POR VEHICULO DE CARGA SE RETIRO TOMA AVERIADA Y SE RECONECTO CASA VECINA | R22040100006 | New_Event |  |  | Include | Wildlife | 629 | 2022-04-01 | 1258 | keep | 0 | Apr | 2022 | 0.00085682 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-04-01 01:06 | 2022-04-01 01:10 | 1984 | 000:04 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | LLEVA LA CARGA DEL 1911-07 SE CERRO DE RISER @ VACUUM SWITCH FRENTE A FARMACIA PLAZA DE GARDEN HILLS PARA SECCIONALIZAR TRAMO AVERIADO DEL 1529-12, ACTUALMENTE EL 1529-12 ENTRO 90% EN SERVICIO, Y EL 1911-07 ENTRO 100% EN SERVICIO G.O.I. BY-220331-01 | S22033100085 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 4 | 2022-04-01 | 7936 | keep | 0 | Apr | 2022 | 0.0054052 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-01 01:06 | 2022-04-01 01:10 | 577 | 000:04 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | CARGA TRANSFERIDA AL 1529-12 SE CERRO DE RISER @ VACOOM SWITCH FRENTE A FARMACIA PLAZA DE GARDEN HILLS PARA SECCIONALIZAR TRAMO AVERIADO DEL 1529-12, EL 1529-12 ENTRO 90% EN SERVICIO, Y EL 1911-07 ENTRO 100% EN SERVICIO G.O.I. BY-220331-01 | S22033100085 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 4 | 2022-04-01 | 2308 | keep | 0 | Apr | 2022 | 0.001572 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-01 01:10 | 2022-04-02 15:47 | 198 | 038:37 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARARON EMPALMES ENTRE SU-1 Y RISER | S22033100149 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 2317 | 2022-04-01 | 458766 | keep | 0 | Apr | 2022 | 0.31246 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
VEGA BAJA | 2022-04-01 01:29 | 2022-04-01 01:30 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
CANOVANAS | 2022-04-01 04:31 | 2022-04-01 05:10 | 3766 | 000:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO INTERRUPTOR FUERA DE SERVICIO SE REALIZO PRUEBA Y PROBO BUENO | R22033100086 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2022-04-01 | 146874 | keep | 0 | Apr | 2022 | 0.10004 | 0.002565 | Sustained | FALSE | FALSE | Not_TMED_Event | 3766
SAN JUAN | 2022-04-01 05:51 | 2022-04-01 05:52 | 858 | 000:01 | P | NO SE REPORTO CAUSA | 20% DE LA CARGA TRANSFERIDA AL 1303-02 DISPARO Y SE CERRO POR CONTROL | S22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 858 | keep | 0 | Apr | 2022 | 0.00058438 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-04-01 05:51 | 2022-04-01 05:52 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 20% DEL 1204-02 | S22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 2435 | keep | 0 | Apr | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CANOVANAS | 2022-04-01 05:59 | 2022-04-01 09:22 | 180 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTE DE LINEA | R22040100108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2022-04-01 | 36540 | keep | 0 | Apr | 2022 | 0.024887 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
VEGA BAJA | 2022-04-01 06:01 | 2022-04-01 06:02 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 3332 | keep | 0 | Apr | 2022 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
BAYAMON | 2022-04-01 06:16 | 2022-04-01 12:13 | 120 | 005:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | S22040100037 | New_Event | Cutout Failure | Include | Include | Equipment | 357 | 2022-04-01 | 42840 | keep | 0 | Apr | 2022 | 0.029178 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BARRANQUITAS | 2022-04-01 06:20 | 2022-04-01 10:32 | 90 | 004:12 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22040100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2022-04-01 | 22680 | keep | 0 | Apr | 2022 | 0.015447 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-04-01 06:26 | 2022-04-01 06:29 | 3766 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA RETORNAR CONDUCTOR ZAFADO SOBRE CRUCETA | R22040100000 | Partial_restoration | Wire Down | Include | Include | Equipment | 3 | 2022-04-01 | 11298 | keep | 0 | Apr | 2022 | 0.007695 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-01 06:40 | 2022-04-01 14:18 | 50 | 007:38 | P | DESGANCHE | SE DESGANCHO 1 X 50 EN C/L | C22040100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 458 | 2022-04-01 | 22900 | keep | 0 | Apr | 2022 | 0.015597 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-01 06:42 | 2022-04-01 06:43 | 4537 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA SOLO EL 70% DE SU CARGA | S22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 4537 | keep | 0 | Apr | 2022 | 0.0030901 | 0.0030901 | Momentary | FALSE | FALSE | Not_TMED_Event | 4537
SAN JUAN | 2022-04-01 06:42 | 2022-04-01 06:44 | 6244 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-01 | 12488 | keep | 0 | Apr | 2022 | 0.0085055 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
CAGUAS | 2022-04-01 06:53 | 2022-04-01 14:24 | 30 | 007:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C22040100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 451 | 2022-04-01 | 13530 | keep | 0 | Apr | 2022 | 0.0092152 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-04-01 06:57 | 2022-04-01 07:42 | 65 | 000:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER Y 1 X 25 EN SWITCH UNIT 1 NO CAUSA | P22040100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-04-01 | 2925 | keep | 0 | Apr | 2022 | 0.0019922 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-04-01 07:16 | 2022-04-01 09:35 | 12 | 002:19 | P | NO SE REPORTO CAUSA | 2 X 20 EN C/L | B22040100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-04-01 | 1668 | keep | 0 | Apr | 2022 | 0.0011361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-04-01 07:40 | 2022-04-01 07:41 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 2610 | keep | 0 | Apr | 2022 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
BAYAMON | 2022-04-01 07:42 | 2022-04-01 12:10 | 4 | 004:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO XMR PARA REEMPLAZAR BAJANTE PRIMARIO DE CAJA A TRANSFORMADOR | S22040100048 | New_Event | Wire Down | Include | Include | Equipment | 268 | 2022-04-01 | 1072 | keep | 0 | Apr | 2022 | 0.00073013 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-01 07:58 | 2022-04-01 07:59 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 LLEVA 1711-04 | B22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 1983 | keep | 0 | Apr | 2022 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-04-01 07:58 | 2022-04-01 07:59 | 500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1801-02 LLEVA PARTE DEL 1717-01 | B22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 500 | keep | 0 | Apr | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-04-01 07:58 | 2022-04-01 07:59 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 LLEVA 1711-04 Y PARTE DEL 1717-01 | B22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 186 | keep | 0 | Apr | 2022 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
SAN JUAN | 2022-04-01 08:00 | 2022-04-01 08:01 | 3433 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 80% DE SU CARGA | S22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 3433 | keep | 0 | Apr | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
CAGUAS | 2022-04-01 08:18 | 2022-04-01 08:19 | 638 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C22040100021 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-01 | 638 | keep | 0 | Apr | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
BAYAMON | 2022-04-01 08:19 | 2022-04-01 09:52 | 36 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22040100050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-04-01 | 3348 | keep | 0 | Apr | 2022 | 0.0022803 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-04-01 08:19 | 2022-04-01 11:44 | 160 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | C22040100023 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 205 | 2022-04-01 | 32800 | keep | 0 | Apr | 2022 | 0.02234 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2022-04-01 08:30 | 2022-04-01 08:31 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 2234 | keep | 0 | Apr | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-04-01 08:59 | 2022-04-01 17:55 | 19 | 008:56 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B22040100055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 536 | 2022-04-01 | 10184 | keep | 0 | Apr | 2022 | 0.0069363 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
VEGA BAJA | 2022-04-01 09:04 | 2022-04-01 10:00 | 45 | 000:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L AVE | B22040100056 | New_Event |  |  | Include | Wildlife | 56 | 2022-04-01 | 2520 | keep | 0 | Apr | 2022 | 0.0017164 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-04-01 09:13 | 2022-04-01 10:16 | 1225 | 001:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTEERUPTOR PERSONAL DE CAROLINA SECCIONALIZANDO EL AREA PARA REEMPLAZO DE POSTE EN EL 1602-01, 2 AISLADORES DE LOS MACHETES ESTABAN PARTIDOS CAUSANDO AVERIA AL 1203-01. LLEVA EL 1203-03 | S22040100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 63 | 2022-04-01 | 77175 | keep | 0 | Apr | 2022 | 0.052564 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-04-01 09:13 | 2022-04-01 10:16 | 616 | 001:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR CARGA POR EL 1203-01 | S22040100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 63 | 2022-04-01 | 38808 | keep | 0 | Apr | 2022 | 0.026432 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-04-01 09:13 | 2022-04-01 14:42 | 763 | 005:29 | T | DESCONECTIVO DEFECTUOSO | REEMPLAZO DE MACHETES QUEMADOS EN RISER DE SALIDA SJ-220401-50 | R22040100133 | New_Event | Switch Failure | Include | Include | Equipment | 329 | 2022-04-01 | 251027 | keep | 0 | Apr | 2022 | 0.17097 | 0.00051968 | Sustained | FALSE | FALSE | Not_TMED_Event | 763
SAN JUAN | 2022-04-01 09:13 | 2022-04-01 13:25 | 1259 | 004:12 | T | AISLADOR ROTO, PARTIDO O SAFADO | OPERACIONES CON LA VL 2022-00529 REALIZADNO OERACIONES CON LA VL HABIAN 2 AISLADORES PARTIDOS EN LOS MACHETES EL CUAL CAUSO AVERIA. | R22040100133 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 252 | 2022-04-01 | 317268 | keep | 0 | Apr | 2022 | 0.21609 | 0.0008575 | Sustained | FALSE | FALSE | Not_TMED_Event | 1259
SAN JUAN | 2022-04-01 09:13 | 2022-04-01 13:25 | 1051 | 004:12 | T | AISLADOR ROTO, PARTIDO O SAFADO | OPERACIONES CON LA VL 2022-00529 REALIZADNO OERACIONES CON LA VL HABIAN 2 AISLADORES PARTIDOS EN LOS MACHETES EL CUAL CAUSO AVERIA. | R22040100133 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 252 | 2022-04-01 | 264852 | keep | 0 | Apr | 2022 | 0.18039 | 0.00071583 | Sustained | FALSE | FALSE | Not_TMED_Event | 1051
SAN JUAN | 2022-04-01 09:13 | 2022-04-01 09:23 | 1026 | 000:10 | T | AISLADOR ROTO, PARTIDO O SAFADO | PERSONAL REALIZANDO OPERACIONES EN 1602-01 Y 1203-01 HABIAN AISLADORES PARTIDOS Y CAUSO DISPARO | R22040100132 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 10 | 2022-04-01 | 10260 | keep | 0 | Apr | 2022 | 0.006988 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
VEGA BAJA | 2022-04-01 09:29 | 2022-04-01 11:42 | 30 | 002:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22040100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-04-01 | 3990 | keep | 0 | Apr | 2022 | 0.0027176 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-01 09:48 | 2022-04-01 15:00 | 40 | 005:12 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22040100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 312 | 2022-04-01 | 12480 | keep | 0 | Apr | 2022 | 0.0085001 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-01 09:53 | 2022-04-01 14:42 | 50 | 004:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22040100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 289 | 2022-04-01 | 14450 | keep | 0 | Apr | 2022 | 0.0098418 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-01 09:57 | 2022-04-01 13:15 | 200 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M22040100018 | New_Event |  |  | Include | Wildlife | 198 | 2022-04-01 | 39600 | keep | 0 | Apr | 2022 | 0.026971 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-04-01 10:00 | 2022-04-01 10:01 | 3387 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE CERRO POR SCADA | B22040100000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-01 | 3387 | keep | 0 | Apr | 2022 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2022-04-01 10:01 | 2022-04-01 11:38 | 45 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L AVE | B22040100056 | 1st_after_momentary |  |  | Include | Wildlife | 97 | 2022-04-01 | 4365 | keep | 0 | Apr | 2022 | 0.002973 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-04-01 10:04 | 2022-04-01 11:39 | 20 | 001:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA INDICA SERVICE FOREMAN NO IDENTIFICO CAUSA | A22040100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2022-04-01 | 1900 | keep | 0 | Apr | 2022 | 0.0012941 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-04-01 10:05 | 2022-04-01 10:06 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
ARECIBO | 2022-04-01 10:05 | 2022-04-01 10:30 | 12 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22040100005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2022-04-01 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-01 10:22 | 2022-04-01 12:30 | 10 | 002:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIAS | C22040100048 | New_Event | Bad Weather | Include | Include | Weather | 128 | 2022-04-01 | 1280 | keep | 0 | Apr | 2022 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-01 10:35 | 2022-04-01 14:45 | 100 | 004:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22040100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2022-04-01 | 25000 | keep | 0 | Apr | 2022 | 0.017027 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-04-01 10:48 | 2022-04-01 15:29 | 7 | 004:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22040100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2022-04-01 | 1967 | keep | 0 | Apr | 2022 | 0.0013397 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-04-01 11:06 | 2022-04-01 16:48 | 200 | 005:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS PRIMARIAS 1 X 100 Y 1 X 80 | R22040100161 | New_Event | Cutout Failure | Include | Include | Equipment | 342 | 2022-04-01 | 68400 | keep | 0 | Apr | 2022 | 0.046587 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-04-01 11:10 | 2022-04-01 12:40 | 13 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22040100009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-04-01 | 1170 | keep | 0 | Apr | 2022 | 0.00079688 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-04-01 11:23 | 2022-04-01 14:40 | 50 | 003:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L SE REPARO BAJANTE | B22040100070 | New_Event | Wire Down | Include | Include | Equipment | 197 | 2022-04-01 | 9850 | keep | 0 | Apr | 2022 | 0.0067088 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-01 11:23 | 2022-04-02 13:00 | 60 | 025:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA EVENTO ORIGINAL M22040100032 A LA 11:23 LO ASIGNA A LAS LLAMADAS NUEVAS M22040200003 | M22040100032 | New_Event | Wire Down | Include | Include | Equipment | 1537 | 2022-04-01 | 92220 | keep | 0 | Apr | 2022 | 0.062811 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-01 11:29 | 2022-04-01 14:07 | 80 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22040100118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-04-01 | 12640 | keep | 0 | Apr | 2022 | 0.008609 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-04-01 11:29 | 2022-04-01 15:47 | 40 | 004:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22040100087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2022-04-01 | 10320 | keep | 0 | Apr | 2022 | 0.0070289 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-01 11:32 | 2022-04-01 14:43 | 50 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22040100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2022-04-01 | 9550 | keep | 0 | Apr | 2022 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-04-01 11:35 | 2022-04-01 14:17 | 25 | 002:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR Y RETEZAR SECUNDARIA | R22040100167 | New_Event | Secondary Wire Down | Include | Include | Equipment | 162 | 2022-04-01 | 4050 | keep | 0 | Apr | 2022 | 0.0027584 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-04-01 11:45 | 2022-04-01 12:46 | 1681 | 001:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-01 Y 1346-06 A TRAVES DEL BKR 1303-04 | S22040100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-04-01 | 102541 | keep | 0 | Apr | 2022 | 0.06984 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-01 11:45 | 2022-04-01 12:46 | 1598 | 001:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO PARA REALIZAR DESGANCHE 95% EN SERVICIO CARGA POR EL 1303-04 | S22040100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-04-01 | 97478 | keep | 0 | Apr | 2022 | 0.066392 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2022-04-01 11:53 | 2022-04-01 15:05 | 150 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040100022 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2022-04-01 | 28800 | keep | 0 | Apr | 2022 | 0.019616 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-04-01 12:00 | 2022-04-01 12:41 | 1 | 000:41 | P | NO SE REPORTO CAUSA | 1 SMU20 DE 100 AMP | B22040100075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2022-04-01 | 41 | keep | 0 | Apr | 2022 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-01 12:06 | 2022-04-01 13:15 | 50 | 001:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA LINEAS CRUZADAS | M12040100034 | New_Event | Wire Down | Include | Include | Equipment | 69 | 2022-04-01 | 3450 | keep | 0 | Apr | 2022 | 0.0023498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-04-01 12:09 | 2022-04-01 14:50 | 1 | 002:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22040100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-04-01 | 161 | keep | 0 | Apr | 2022 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-04-01 12:15 | 2022-04-01 12:16 | 1637 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040100027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 1637 | keep | 0 | Apr | 2022 | 0.001115 | 0.001115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1637
GUAYAMA | 2022-04-01 12:19 | 2022-04-01 15:10 | 100 | 002:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | P22040100029 | New_Event |  |  | Include | Wildlife | 171 | 2022-04-01 | 17100 | keep | 0 | Apr | 2022 | 0.011647 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-01 12:42 | 2022-04-01 12:52 | 1271 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE VERIFICO PERSONAL FUERA | C22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-04-01 | 12710 | keep | 0 | Apr | 2022 | 0.0086567 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
YAUCO | 2022-04-01 12:45 | 2022-04-01 13:44 | 1325 | 000:59 | T | DESGANCHE | DISPARO ALIMENTADOR SE ABRIERON MACHETES PARA SECCIONALIZAR AVERIA BAMBUAS CRUZANDO FASES | P22040100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-04-01 | 78175 | keep | 0 | Apr | 2022 | 0.053245 | 0.00090245 | Sustained | FALSE | FALSE | Not_TMED_Event | 1325
SAN JUAN | 2022-04-01 12:46 | 2022-04-01 14:27 | 1596 | 001:41 | P | DESGANCHE | ALIMENTADOR SECCIONALIZADO | S22040100000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-04-01 | 161196 | keep | 0 | Apr | 2022 | 0.10979 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-04-01 12:50 | 2022-04-01 13:44 | 1343 | 000:54 | T | DESGANCHE | DISPARO ALIMENTADOR SE ABRIERON MACHETES PARA SECCIONALIZAR AVERIA BAMBUAS CRUZANDO FASES | P22040100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-04-01 | 72522 | keep | 0 | Apr | 2022 | 0.049394 | 0.00091471 | Sustained | FALSE | FALSE | Not_TMED_Event | 1343
BAYAMON | 2022-04-01 13:05 | 2022-04-01 13:34 | 2858 | 000:29 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO POSTE IMPACTADO POR CAMION Y SE CERRO POR SCADA | B22040100078 | New_Event |  |  | Include | Wildlife | 29 | 2022-04-01 | 82882 | keep | 0 | Apr | 2022 | 0.056451 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2022-04-01 13:34 | 2022-04-01 15:40 | 1143 | 002:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZARON AISLADORES SE REPARO TOMA Y SE NORMALIZO CERRANDO MACHETES | B22040100078 | Partial_restoration |  |  | Include | Wildlife | 126 | 2022-04-01 | 144018 | keep | 0 | Apr | 2022 | 0.09809 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-01 13:36 | 2022-04-01 14:35 | 25 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R22040100204 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-04-01 | 1475 | keep | 0 | Apr | 2022 | 0.0010046 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-04-01 13:44 | 2022-04-01 18:26 | 1343 | 004:42 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES | P22040100042 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-04-01 | 378726 | keep | 0 | Apr | 2022 | 0.25795 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-04-01 13:44 | 2022-04-01 18:24 | 150 | 004:40 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES | P22040100040 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 280 | 2022-04-01 | 42000 | keep | 0 | Apr | 2022 | 0.028606 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-01 13:46 | 2022-04-01 16:17 | 25 | 002:31 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN RISER PROVICIONAL Y SE REMPLAZO PARARRAYO | R22040100206 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 151 | 2022-04-01 | 3775 | keep | 0 | Apr | 2022 | 0.0025711 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-01 13:47 | 2022-04-01 15:00 | 752 | 001:13 | T | DESGANCHE | DISPARO DE INTERRUPTOR POR RAMA SOBRE LA LINEA EN TRONCAL DEL ALIMENTADOR. SU CARGA ESTA TRANSFERIDA AL 5018-04. | P22040100047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-04-01 | 54896 | keep | 0 | Apr | 2022 | 0.037389 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2022-04-01 13:47 | 2022-04-01 15:00 | 2696 | 001:13 | T | DESGANCHE | DISPARO DE INTERRUPTOR POR RAMA SOBRE LA LINEA EN TRONCAL DEL ALIMENTADOR. ESTA LLEVANDO LA CARGA DEL 5011-04. | P22040100047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-04-01 | 196808 | keep | 0 | Apr | 2022 | 0.13405 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
CAGUAS | 2022-04-01 13:56 | 2022-04-01 16:22 | 65 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22040100131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-04-01 | 9490 | keep | 0 | Apr | 2022 | 0.0064636 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-04-01 14:08 | 2022-04-01 14:09 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 2402-04 | R22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 3699 | keep | 0 | Apr | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
BAYAMON | 2022-04-01 14:12 | 2022-04-02 11:04 | 6 | 020:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE XMR PARA REPARAR SECUNDARIA | B22040100088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1252 | 2022-04-01 | 7512 | keep | 0 | Apr | 2022 | 0.0051164 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-04-01 14:15 | 2022-04-01 22:38 | 40 | 008:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X40 EN C/L & SE REMPLAZO CAJA PRIMARIA | B22040100090 | New_Event | Cutout Failure | Include | Include | Equipment | 503 | 2022-04-01 | 20120 | keep | 0 | Apr | 2022 | 0.013704 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-01 14:19 | 2022-04-01 17:16 | 130 | 002:57 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN C/L | B22040100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2022-04-01 | 23010 | keep | 0 | Apr | 2022 | 0.015672 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
UTUADO | 2022-04-01 14:22 | 2022-04-01 14:50 | 1 | 000:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040100040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-04-01 | 28 | keep | 0 | Apr | 2022 | 1.9071e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-01 14:23 | 2022-04-01 19:22 | 60 | 004:59 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22040100065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 299 | 2022-04-01 | 17940 | keep | 0 | Apr | 2022 | 0.012219 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-01 14:27 | 2022-04-01 14:30 | 1681 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-01 Y 1346-06 A TRAVES DEL BKR 1303-04.CERRANDO MACHETE DE CAMINO LUIS VIGOREAUX PROBO MALO | S22040100000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-04-01 | 5043 | keep | 0 | Apr | 2022 | 0.0034348 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-01 14:27 | 2022-04-01 14:30 | 1598 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR REALIZANDO OPERACIONES DE CAMPO. SE ABRIO NUEVAMENTE MACHETE CAMINO LUIS VIGOREAUX PARA REALIZAR DESGANCHE | S22040100000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-04-01 | 4794 | keep | 0 | Apr | 2022 | 0.0032652 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-01 14:30 | 2022-04-01 14:57 | 1596 | 000:27 | P | DESGANCHE | SE REALIZO DESGANCHE DE BAMBUAS Y SE CERRO MACHETE | S22040100000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 27 | 2022-04-01 | 43092 | keep | 0 | Apr | 2022 | 0.02935 | 0.001087 | Sustained | FALSE | FALSE | Not_TMED_Event | 1596
ARECIBO | 2022-04-01 14:30 | 2022-04-01 16:40 | 10 | 002:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE UNO DE 50KVA POR UNO DE 50KVA | A22040100037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 130 | 2022-04-01 | 1300 | keep | 0 | Apr | 2022 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-04-01 14:30 | 2022-04-01 17:24 | 1 | 002:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-04-01 | 174 | keep | 0 | Apr | 2022 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-01 14:32 | 2022-04-02 15:40 | 110 | 025:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040100071 | New_Event |  |  | Include | Wildlife | 1508 | 2022-04-01 | 165880 | keep | 0 | Apr | 2022 | 0.11298 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
ARECIBO | 2022-04-01 14:36 | 2022-04-02 16:20 | 12 | 025:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22040100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1544 | 2022-04-01 | 18528 | keep | 0 | Apr | 2022 | 0.012619 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-04-01 14:43 | 2022-04-01 20:29 | 29 | 005:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A22040100043 | New_Event | Wire Down | Include | Include | Equipment | 346 | 2022-04-01 | 10034 | keep | 0 | Apr | 2022 | 0.0068341 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
ARECIBO | 2022-04-01 14:47 | 2022-04-01 18:29 | 50 | 003:42 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2022-04-01 | 11100 | keep | 0 | Apr | 2022 | 0.0075602 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-01 14:58 | 2022-04-01 18:17 | 30 | 003:19 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | C22040100143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-04-01 | 5970 | keep | 0 | Apr | 2022 | 0.0040661 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-01 14:59 | 2022-04-01 17:04 | 80 | 002:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M22040100076 | New_Event | Bad Weather | Include | Include | Weather | 125 | 2022-04-01 | 10000 | keep | 0 | Apr | 2022 | 0.006811 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-01 14:59 | 2022-04-01 20:57 | 151 | 005:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22040100049 | New_Event | Bad Weather | Include | Include | Weather | 358 | 2022-04-01 | 54058 | keep | 0 | Apr | 2022 | 0.036819 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
HUMACAO | 2022-04-01 15:00 | 2022-04-01 18:31 | 1 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22040100152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-04-01 | 211 | keep | 0 | Apr | 2022 | 0.00014371 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-01 15:00 | 2022-04-01 15:24 | 1 | 000:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22040100108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-04-01 | 24 | keep | 0 | Apr | 2022 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-01 15:12 | 2022-04-01 15:14 | 3387 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-01 | 6774 | keep | 0 | Apr | 2022 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
ARECIBO | 2022-04-01 15:15 | 2022-04-01 16:42 | 13 | 001:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZARON DOS TRANSFORMADORES CON ESCAPE DE ACEITE DOS DE 50KVA POR DOS DE 50KVA | A22040100050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 87 | 2022-04-01 | 1131 | keep | 0 | Apr | 2022 | 0.00077032 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2022-04-01 15:16 | 2022-04-01 17:33 | 140 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040100054 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2022-04-01 | 19180 | keep | 0 | Apr | 2022 | 0.013063 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
MAYAGÃœEZ | 2022-04-01 15:21 | 2022-04-01 20:39 | 250 | 005:18 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA POR VIENTOS | M22040100081 | New_Event | Bad Weather | Include | Include | Weather | 318 | 2022-04-01 | 79500 | keep | 0 | Apr | 2022 | 0.054147 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2022-04-01 15:23 | 2022-04-01 18:36 | 40 | 003:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22040100056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-04-01 | 7720 | keep | 0 | Apr | 2022 | 0.0052581 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-04-01 15:25 | 2022-04-02 14:59 | 50 | 023:34 | P | DESGANCHE | SE DESGANCHO Y SE CERRO FASE DE MACHETE ABIERTA DE ANOCHE | B22040100112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1414 | 2022-04-01 | 70700 | keep | 0 | Apr | 2022 | 0.048153 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-01 15:36 | 2022-04-01 17:29 | 20 | 001:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22040100066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-04-01 | 2260 | keep | 0 | Apr | 2022 | 0.0015393 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-04-01 15:41 | 2022-04-01 17:51 | 6 | 002:10 | P | DESGANCHE | 1 X10 EN XMR DESGANCHE | S22040100199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-04-01 | 780 | keep | 0 | Apr | 2022 | 0.00053125 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-01 15:45 | 2022-04-01 15:46 | 12 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR Y SE CERRO PUENTE DE LINEA PRIMARIA EN TRANSFORMADOR | S22040100059 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-01 | 12 | keep | 0 | Apr | 2022 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-04-01 15:51 | 2022-04-01 17:36 | 50 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | P22040100069 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2022-04-01 | 5250 | keep | 0 | Apr | 2022 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-01 15:53 | 2022-04-01 19:24 | 1066 | 003:31 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR TRES VECES Y QUEDO FUERA DE SERVICIO. SE PATRULLO Y NO SE ENCONTRO CAUSA. SE PROCEDIO A CERRAR POR SCADA Y QUEDO EN SERVICIO TOTAL. | A22040100071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-04-01 | 224926 | keep | 0 | Apr | 2022 | 0.1532 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
ARECIBO | 2022-04-01 15:57 | 2022-04-01 20:32 | 20 | 004:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2022-04-01 | 5500 | keep | 0 | Apr | 2022 | 0.003746 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-01 16:00 | 2022-04-01 18:43 | 65 | 002:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22040100230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-04-01 | 10595 | keep | 0 | Apr | 2022 | 0.0072162 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-04-01 16:00 | 2022-04-01 18:37 | 80 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22040100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-04-01 | 12560 | keep | 0 | Apr | 2022 | 0.0085546 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-01 16:01 | 2022-04-02 13:28 | 100 | 021:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22040100099 | New_Event | Wire Down | Include | Include | Equipment | 1287 | 2022-04-01 | 128700 | keep | 0 | Apr | 2022 | 0.087657 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-01 16:02 | 2022-04-02 16:45 | 40 | 024:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040100064 | New_Event | Bad Weather | Include | Include | Weather | 1483 | 2022-04-01 | 59320 | keep | 0 | Apr | 2022 | 0.040403 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-01 16:04 | 2022-04-01 17:21 | 13 | 001:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR POR AVE | M22040100066 | New_Event |  |  | Include | Wildlife | 77 | 2022-04-01 | 1001 | keep | 0 | Apr | 2022 | 0.00068178 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2022-04-01 16:08 | 2022-04-01 19:30 | 9 | 003:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 8 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22040100069 | New_Event | Wire Down | Include | Include | Equipment | 202 | 2022-04-01 | 1818 | keep | 0 | Apr | 2022 | 0.0012382 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-04-01 16:19 | 2022-04-01 18:02 | 20 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22040100117 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2022-04-01 | 2060 | keep | 0 | Apr | 2022 | 0.0014031 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-01 16:22 | 2022-04-01 18:36 | 100 | 002:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE | C22040100154 | New_Event |  |  | Include | Wildlife | 134 | 2022-04-01 | 13400 | keep | 0 | Apr | 2022 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-01 16:59 | 2022-04-02 13:08 | 4 | 020:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PARTIDA EN TRANSFORMADOR | C22040100158 | New_Event | Cutout Failure | Include | Include | Equipment | 1209 | 2022-04-01 | 4836 | keep | 0 | Apr | 2022 | 0.0032938 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-04-01 16:59 | 2022-04-02 09:25 | 200 | 016:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22040100113 | New_Event | Cutout Failure | Include | Include | Equipment | 986 | 2022-04-01 | 197200 | keep | 0 | Apr | 2022 | 0.13431 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-04-01 17:00 | 2022-04-01 19:40 | 2 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARARON SECUNDARIAS | M22040100110 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2022-04-01 | 320 | keep | 0 | Apr | 2022 | 0.00021795 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-04-01 17:05 | 2022-04-01 17:06 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 922 | keep | 0 | Apr | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-04-01 17:05 | 2022-04-01 17:06 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 135 | keep | 0 | Apr | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-04-01 17:23 | 2022-04-01 18:30 | 12 | 001:07 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE Y SE RETEZO TRENSA ABIERTA SECUNDARIA | S22040100194 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 67 | 2022-04-01 | 804 | keep | 0 | Apr | 2022 | 0.0005476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-04-01 17:35 | 2022-04-02 11:22 | 15 | 017:47 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR SE REALIZO DESGANCHE Y REPARO SECUNDARIA | S22040100205 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1067 | 2022-04-01 | 16005 | keep | 0 | Apr | 2022 | 0.010901 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-04-01 17:42 | 2022-04-01 19:38 | 4 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040100090 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2022-04-01 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-01 18:03 | 2022-04-01 22:24 | 38 | 004:21 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | C22040100160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2022-04-01 | 9918 | keep | 0 | Apr | 2022 | 0.0067551 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
ARECIBO | 2022-04-01 18:11 | 2022-04-01 20:07 | 9 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22040100096 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2022-04-01 | 1044 | keep | 0 | Apr | 2022 | 0.00071106 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2022-04-01 18:24 | 2022-04-02 15:26 | 1 | 021:02 | P | ERROR HUMANO | SE CERRO RISER PRIMARIO ABIERTO DEBIDO A AVERIA DEL DIA ANTERIOR | P22040200018 | New_Event | Human Error | Include | Include | Other | 1262 | 2022-04-01 | 1262 | keep | 0 | Apr | 2022 | 0.00085954 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-01 18:27 | 2022-04-01 23:50 | 20 | 005:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22040100137 | New_Event | Bad Weather | Include | Include | Weather | 323 | 2022-04-01 | 6460 | keep | 0 | Apr | 2022 | 0.0043999 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-01 18:38 | 2022-04-01 21:18 | 40 | 002:40 | P | DESGANCHE | 1 X 80 EN CORTE DELINEA Y SE REALIZO DESGANCHE | S22040100209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-04-01 | 6400 | keep | 0 | Apr | 2022 | 0.004359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-01 18:58 | 2022-04-01 18:59 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-01 | 2178 | keep | 0 | Apr | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
ARECIBO | 2022-04-01 19:01 | 2022-04-03 07:54 | 30 | 036:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | A22040100106 | New_Event | Cutout Failure | Include | Include | Equipment | 2213 | 2022-04-01 | 66390 | keep | 0 | Apr | 2022 | 0.045218 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-04-01 19:08 | 2022-04-01 19:09 | 3502 | 000:01 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE CERRO POR SCADA Y QUEDO EN SERVICIO | A22040100107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-01 | 3502 | keep | 0 | Apr | 2022 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-04-01 19:09 | 2022-04-01 22:20 | 200 | 003:11 | P | DESGANCHE | 3 X 200 EN CORTE DE LINEA SE SEPARO LINEAS CRUZADAS POR ARBOL QUE CAYO SOBRE ELLAS | A22040100120 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-04-01 | 38200 | keep | 0 | Apr | 2022 | 0.026018 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-04-01 19:15 | 2022-04-01 21:12 | 6 | 001:57 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A22040100091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-04-01 | 702 | keep | 0 | Apr | 2022 | 0.00047813 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-04-01 19:18 | 2022-04-01 20:29 | 1 | 001:11 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040100111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-04-01 | 71 | keep | 0 | Apr | 2022 | 4.8358e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-01 19:21 | 2022-04-02 11:34 | 19 | 016:13 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | S22040100213 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 973 | 2022-04-01 | 18487 | keep | 0 | Apr | 2022 | 0.012591 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-04-01 19:42 | 2022-04-01 21:20 | 10 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 10 EN XMR SE REPARO SECUNDARIA | B22040100142 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2022-04-01 | 980 | keep | 0 | Apr | 2022 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-01 20:01 | 2022-04-02 10:29 | 30 | 014:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE POR AVE | S22040100215 | New_Event |  |  | Include | Wildlife | 868 | 2022-04-01 | 26040 | keep | 0 | Apr | 2022 | 0.017736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-04-01 20:15 | 2022-04-02 04:20 | 150 | 008:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 80 EN CORTES DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22040100171 | New_Event | Wire Down | Include | Include | Equipment | 485 | 2022-04-01 | 72750 | keep | 0 | Apr | 2022 | 0.04955 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-04-01 20:18 | 2022-04-01 21:06 | 15 | 000:48 | P | DESGANCHE | 1 X 20 EN TRASNFORMADOR Y SE REALIZO DESGANCHE | R22040100239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2022-04-01 | 720 | keep | 0 | Apr | 2022 | 0.00049039 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-01 20:24 | 2022-04-01 22:53 | 35 | 002:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X65 EN C/L & SE RETIRO SERPIENTE DEL 13KV | B22040100144 | New_Event |  |  | Include | Wildlife | 149 | 2022-04-01 | 5215 | keep | 0 | Apr | 2022 | 0.0035519 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-04-01 22:03 | 2022-04-01 22:34 | 65 | 000:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R22040100242 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 31 | 2022-04-01 | 2015 | keep | 0 | Apr | 2022 | 0.0013724 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-04-01 22:08 | 2022-04-01 23:50 | 30 | 001:42 | P | DESGANCHE | SE REALIZO DESGANCHE 1 X 30 EN CORTE DE LINEA | R22040100243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-04-01 | 3060 | keep | 0 | Apr | 2022 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-01 22:15 | 2022-04-02 10:30 | 36 | 012:15 | P | ESTRUCTURA AVERIADA | 1 X 40 EN C/L SE SECCIONALIZO POSTES EN EL SUELO | B22040100151 | New_Event | Defective Pole | Include | Include | Equipment | 735 | 2022-04-01 | 26460 | keep | 0 | Apr | 2022 | 0.018022 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2022-04-01 22:15 | 2022-04-02 18:38 | 40 | 020:23 | P | ESTRUCTURA AVERIADA | SE SUBIO CONDUCTOR Y SE CERRO C/L | B22040100151 | New_Event | Defective Pole | Include | Include | Equipment | 1223 | 2022-04-01 | 48920 | keep | 0 | Apr | 2022 | 0.033319 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-04-01 22:17 | 2022-04-02 09:54 | 99 | 011:37 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTES DE LINEA | R22040100244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 697 | 2022-04-01 | 69003 | keep | 0 | Apr | 2022 | 0.046998 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
CAGUAS | 2022-04-01 22:29 | 2022-04-02 10:33 | 120 | 012:04 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | C22040100190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 724 | 2022-04-01 | 86880 | keep | 0 | Apr | 2022 | 0.059174 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-04-01 22:54 | 2022-04-02 00:31 | 12 | 001:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X10 EN XMR & SE CERRO PUENTE PRIMARIO DE LINEA @ CAJA | S22040100222 | New_Event | Wire Down | Include | Include | Equipment | 97 | 2022-04-01 | 1164 | keep | 0 | Apr | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-04-01 23:06 | 2022-04-02 11:55 | 6 | 012:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | A22040100154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 769 | 2022-04-01 | 4614 | keep | 0 | Apr | 2022 | 0.0031426 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-01 23:20 | 2022-04-02 01:39 | 7 | 002:19 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE SECUNDARIO PARTIDO Y SE CERRO EL TRANSFORMADOR QUE SE HABIA ABIERTO PARA RETIRAR PELIGRO | M22040100219 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 139 | 2022-04-01 | 973 | keep | 0 | Apr | 2022 | 0.00066271 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-04-01 23:50 | 2022-04-01 23:52 | 1894 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-01 | 3788 | keep | 0 | Apr | 2022 | 0.00258 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2022-04-01 23:50 | 2022-04-01 23:52 | 4154 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-01 | 8308 | keep | 0 | Apr | 2022 | 0.0056585 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2022-04-01 23:50 | 2022-04-01 23:52 | 424 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-01 | 848 | keep | 0 | Apr | 2022 | 0.00057757 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2022-04-01 23:50 | 2022-04-01 23:52 | 2524 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION | R22040100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-01 | 5048 | keep | 0 | Apr | 2022 | 0.0034382 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-04-01 23:50 | 2022-04-01 23:52 | 1648 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION | R22040100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-01 | 3296 | keep | 0 | Apr | 2022 | 0.0022449 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-04-01 23:52 | 2022-04-02 14:13 | 30 | 014:21 | P | DESGANCHE | SE REALIZO DESGANCHE 1 X 30 EN CORTE DE LINEA | R22040100243 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 861 | 2022-04-01 | 25830 | keep | 0 | Apr | 2022 | 0.017593 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-02 00:10 | 2022-04-02 14:55 | 15 | 014:45 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR | S22040200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 885 | 2022-04-02 | 13275 | keep | 0 | Apr | 2022 | 0.0090415 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-02 01:10 | 2022-04-02 09:38 | 98 | 008:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA NO FUNDIO | S22040200005 | New_Event | Cutout Failure | Include | Include | Equipment | 508 | 2022-04-02 | 49784 | keep | 0 | Apr | 2022 | 0.033908 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
CANOVANAS | 2022-04-02 01:55 | 2022-04-02 01:56 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 2302-02 | R22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 2708 | keep | 0 | Apr | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-04-02 01:55 | 2022-04-02 01:56 | 2524 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 2302-01 | R22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 2524 | keep | 0 | Apr | 2022 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-04-02 03:45 | 2022-04-02 13:02 | 30 | 009:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON CULEBRA | R22040200002 | New_Event |  |  | Include | Wildlife | 557 | 2022-04-02 | 16710 | keep | 0 | Apr | 2022 | 0.011381 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-04-02 03:49 | 2022-04-02 03:50 | 2859 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C22040200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-02 | 2859 | keep | 0 | Apr | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CAGUAS | 2022-04-02 03:50 | 2022-04-02 10:18 | 60 | 006:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22040200058 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 388 | 2022-04-02 | 23280 | keep | 0 | Apr | 2022 | 0.015856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-04-02 05:04 | 2022-04-02 15:45 | 40 | 010:41 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22040200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 641 | 2022-04-02 | 25640 | keep | 0 | Apr | 2022 | 0.017463 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-02 05:10 | 2022-04-02 06:12 | 175 | 001:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C22040200034 | New_Event | Bad Weather | Include | Include | Weather | 62 | 2022-04-02 | 10850 | keep | 0 | Apr | 2022 | 0.0073899 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
CANOVANAS | 2022-04-02 05:24 | 2022-04-02 11:53 | 63 | 006:29 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 Y 1 X 65 EN SU'S SE REEMPLAZO TERMINACION QUEMADA EN SU 2 | R22040200003 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 389 | 2022-04-02 | 24507 | keep | 0 | Apr | 2022 | 0.016692 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
VEGA BAJA | 2022-04-02 05:48 | 2022-04-02 07:13 | 3000 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 DE MANATI TC A VEGA BAJA | B22040200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-04-02 | 255000 | keep | 0 | Apr | 2022 | 0.17368 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2022-04-02 05:48 | 2022-04-02 07:13 | 908 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 DE MANATI TC A VEGA BAJA | B22040200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-04-02 | 77180 | keep | 0 | Apr | 2022 | 0.052567 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
VEGA BAJA | 2022-04-02 05:48 | 2022-04-02 07:13 | 3332 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 DE MANATI TC A VEGA BAJA | B22040200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-04-02 | 283220 | keep | 0 | Apr | 2022 | 0.1929 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2022-04-02 05:48 | 2022-04-02 07:13 | 2610 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 DE MANATI TC A VEGA BAJA | B22040200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-04-02 | 221850 | keep | 0 | Apr | 2022 | 0.1511 | 0.0017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2022-04-02 05:48 | 2022-04-02 07:13 | 3076 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 DE MANATI TC A VEGA BAJA | B22040200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-04-02 | 261460 | keep | 0 | Apr | 2022 | 0.17808 | 0.002095 | Sustained | FALSE | FALSE | Not_TMED_Event | 3076
ARECIBO | 2022-04-02 06:17 | 2022-04-02 10:49 | 30 | 004:32 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22040200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 272 | 2022-04-02 | 8160 | keep | 0 | Apr | 2022 | 0.0055577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-02 06:22 | 2022-04-02 06:23 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-01 LLEVA CARGA 1206-02 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-04-02 06:22 | 2022-04-02 06:23 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 1206-01 | S22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
CAGUAS | 2022-04-02 06:23 | 2022-04-02 11:22 | 100 | 004:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22040200020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 299 | 2022-04-02 | 29900 | keep | 0 | Apr | 2022 | 0.020365 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-04-02 06:24 | 2022-04-02 10:00 | 300 | 003:36 | P | DESGANCHE | 2 X 100 EN CORTES DE LINEA | C22040200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-04-02 | 64800 | keep | 0 | Apr | 2022 | 0.044135 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-04-02 06:34 | 2022-04-02 06:35 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1206-03 | S22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 10211 | keep | 0 | Apr | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-04-02 06:34 | 2022-04-02 06:35 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1204-05 | S22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 4133 | keep | 0 | Apr | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BARRANQUITAS | 2022-04-02 06:42 | 2022-04-02 13:45 | 12 | 007:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN XMR SE ELIMINO SECUNDARIA VACANTE | C22040200025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 423 | 2022-04-02 | 5076 | keep | 0 | Apr | 2022 | 0.0034572 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-02 06:55 | 2022-04-02 08:46 | 60 | 001:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C22040200027 | New_Event |  |  | Include | Wildlife | 111 | 2022-04-02 | 6660 | keep | 0 | Apr | 2022 | 0.0045361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-04-02 07:01 | 2022-04-02 11:17 | 50 | 004:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUAS | A22040200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-04-02 | 12800 | keep | 0 | Apr | 2022 | 0.008718 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-02 07:06 | 2022-04-02 09:30 | 80 | 002:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-04-02 | 11520 | keep | 0 | Apr | 2022 | 0.0078462 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-02 07:13 | 2022-04-02 15:24 | 1 | 008:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22040200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 491 | 2022-04-02 | 491 | keep | 0 | Apr | 2022 | 0.00033442 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-02 07:25 | 2022-04-02 07:28 | 1802 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-02 | 5406 | keep | 0 | Apr | 2022 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2022-04-02 07:39 | 2022-04-02 07:44 | 748 | 000:05 | T | ESTRUCTURA AVERIADA | DISPARO DE 1802-02 LLEVA 1802-01 | B22040200087 | New_Event | Defective Pole | Include | Include | Equipment | 5 | 2022-04-02 | 3740 | keep | 0 | Apr | 2022 | 0.0025473 | 0.00050946 | Momentary | FALSE | FALSE | Not_TMED_Event | 748
BAYAMON | 2022-04-02 07:39 | 2022-04-02 07:44 | 33 | 000:05 | T | ESTRUCTURA AVERIADA | DISPARO DE 1802-02 LLEVA 1802-01 | B22040200087 | New_Event | Defective Pole | Include | Include | Equipment | 5 | 2022-04-02 | 165 | keep | 0 | Apr | 2022 | 0.00011238 | 2.2476e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2022-04-02 07:44 | 2022-04-02 16:56 | 20 | 009:12 | P | ESTRUCTURA AVERIADA | 2 X 50 EN C/L Y 2 X 10 EN XMR SE RELOCALIZO LINEA PRIMARIA POSTE Y XMR | B22040200088 | Partial_restoration | Defective Pole | Include | Include | Equipment | 552 | 2022-04-02 | 11040 | keep | 0 | Apr | 2022 | 0.0075193 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-02 07:47 | 2022-04-02 12:32 | 50 | 004:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22040200023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2022-04-02 | 14250 | keep | 0 | Apr | 2022 | 0.0097056 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-02 08:03 | 2022-04-02 14:50 | 50 | 006:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A22040200005 | New_Event | Wire Down | Include | Include | Equipment | 407 | 2022-04-02 | 20350 | keep | 0 | Apr | 2022 | 0.01386 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-02 08:18 | 2022-04-02 08:19 | 763 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041020000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 763 | keep | 0 | Apr | 2022 | 0.00051968 | 0.00051968 | Momentary | FALSE | FALSE | Not_TMED_Event | 763
FAJARDO | 2022-04-02 08:23 | 2022-04-02 15:21 | 25 | 006:58 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO PARTIDO | R22040200015 | New_Event | Defective Pole | Include | Include | Equipment | 418 | 2022-04-02 | 10450 | keep | 0 | Apr | 2022 | 0.0071174 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-02 08:32 | 2022-04-02 11:40 | 13 | 003:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA PAJARO CRUZO FASE | P22040200003 | New_Event |  |  | Include | Wildlife | 188 | 2022-04-02 | 2444 | keep | 0 | Apr | 2022 | 0.0016646 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2022-04-02 08:32 | 2022-04-02 10:50 | 10 | 002:18 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN MONTURA SE RETIRO RAMAS | B22040200094 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 138 | 2022-04-02 | 1380 | keep | 0 | Apr | 2022 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-04-02 08:50 | 2022-04-02 14:39 | 10 | 005:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22040200005 | New_Event |  |  | Include | Wildlife | 349 | 2022-04-02 | 3490 | keep | 0 | Apr | 2022 | 0.002377 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 09:12 | 693 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-02 | 4158 | keep | 0 | Apr | 2022 | 0.002832 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 09:12 | 47 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-02 | 282 | keep | 0 | Apr | 2022 | 0.00019207 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 09:12 | 1256 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-02 | 7536 | keep | 0 | Apr | 2022 | 0.0051327 | 0.00085546 | Sustained | FALSE | FALSE | Not_TMED_Event | 1256
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 09:12 | 558 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-02 | 3348 | keep | 0 | Apr | 2022 | 0.0022803 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 10:08 | 1192 | 001:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 62 | 2022-04-02 | 73904 | keep | 0 | Apr | 2022 | 0.050336 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 10:08 | 3041 | 001:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 62 | 2022-04-02 | 188542 | keep | 0 | Apr | 2022 | 0.12842 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 10:08 | 390 | 001:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 62 | 2022-04-02 | 24180 | keep | 0 | Apr | 2022 | 0.016469 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 10:08 | 650 | 001:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 62 | 2022-04-02 | 40300 | keep | 0 | Apr | 2022 | 0.027448 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 11:37 | 569 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-04-02 | 85919 | keep | 0 | Apr | 2022 | 0.058519 | 0.00038754 | Sustained | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 11:37 | 1245 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-04-02 | 187995 | keep | 0 | Apr | 2022 | 0.12804 | 0.00084796 | Sustained | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 11:37 | 1155 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-04-02 | 174405 | keep | 0 | Apr | 2022 | 0.11879 | 0.00078667 | Sustained | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 11:37 | 867 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-04-02 | 130917 | keep | 0 | Apr | 2022 | 0.089167 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 11:37 | 257 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-04-02 | 38807 | keep | 0 | Apr | 2022 | 0.026431 | 0.00017504 | Sustained | FALSE | FALSE | Not_TMED_Event | 257
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 11:37 | 1336 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-04-02 | 201736 | keep | 0 | Apr | 2022 | 0.1374 | 0.00090994 | Sustained | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 11:37 | 3315 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-04-02 | 500565 | keep | 0 | Apr | 2022 | 0.34093 | 0.0022578 | Sustained | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 11:37 | 1718 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-04-02 | 259418 | keep | 0 | Apr | 2022 | 0.17669 | 0.0011701 | Sustained | FALSE | FALSE | Not_TMED_Event | 1718
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 10:07 | 154 | 001:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 61 | 2022-04-02 | 9394 | keep | 0 | Apr | 2022 | 0.0063982 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 10:07 | 1261 | 001:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 61 | 2022-04-02 | 76921 | keep | 0 | Apr | 2022 | 0.052391 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 10:07 | 3894 | 001:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 61 | 2022-04-02 | 237534 | keep | 0 | Apr | 2022 | 0.16178 | 0.0026522 | Sustained | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 10:07 | 997 | 001:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 61 | 2022-04-02 | 60817 | keep | 0 | Apr | 2022 | 0.041422 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2022-04-02 09:06 | 2022-04-02 10:07 | 1497 | 001:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 61 | 2022-04-02 | 91317 | keep | 0 | Apr | 2022 | 0.062196 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
VEGA BAJA | 2022-04-02 09:16 | 2022-04-02 09:17 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
ARECIBO | 2022-04-02 09:24 | 2022-04-02 12:10 | 1 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE PRIMARIO | A22040200011 | New_Event | Wire Down | Include | Include | Equipment | 166 | 2022-04-02 | 166 | keep | 0 | Apr | 2022 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-02 09:27 | 2022-04-02 13:04 | 150 | 003:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU | S22040200035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2022-04-02 | 32550 | keep | 0 | Apr | 2022 | 0.02217 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-04-02 09:43 | 2022-04-02 09:44 | 70 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22040200027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 70 | keep | 0 | Apr | 2022 | 4.7677e-05 | 4.7677e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-04-02 10:11 | 2022-04-02 10:12 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 4085 | keep | 0 | Apr | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2022-04-02 10:11 | 2022-04-02 10:12 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040200060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 3699 | keep | 0 | Apr | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CAGUAS | 2022-04-02 10:18 | 2022-04-02 10:19 | 2859 | 000:01 | T | DESGANCHE | RECIERRE | C22040200059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-02 | 2859 | keep | 0 | Apr | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CAGUAS | 2022-04-02 10:19 | 2022-04-02 13:10 | 60 | 002:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22040200058 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-04-02 | 10260 | keep | 0 | Apr | 2022 | 0.006988 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-02 10:41 | 2022-04-02 13:00 | 30 | 002:19 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B22040200101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-04-02 | 4170 | keep | 0 | Apr | 2022 | 0.0028402 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-04-02 10:45 | 2022-04-02 11:28 | 10 | 000:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA SULFATADA | R22040200067 | New_Event | Cutout Failure | Include | Include | Equipment | 43 | 2022-04-02 | 430 | keep | 0 | Apr | 2022 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-02 10:53 | 2022-04-02 10:55 | 6285 | 000:02 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR ALIMENTADOR PARA RETIRAR BAMBUS SOBRE LINEA 2500 | M22040200234 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-02 | 12570 | keep | 0 | Apr | 2022 | 0.0085614 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2022-04-02 10:55 | 2022-04-02 11:48 | 2150 | 000:53 | P | LINEA DE TRANSMISION 38KV | SE RETIRO BAMBUS SOBRE LINEAS SE CERRO INTERRUPTOR | M22040200238 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 53 | 2022-04-02 | 113950 | keep | 0 | Apr | 2022 | 0.077611 | 0.0014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 2150
SAN JUAN | 2022-04-02 11:02 | 2022-04-02 12:21 | 6 | 001:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22040200044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 79 | 2022-04-02 | 474 | keep | 0 | Apr | 2022 | 0.00032284 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-02 11:09 | 2022-04-02 12:06 | 514 | 000:57 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1520-05 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1520-01 Y 1520-04. SE ABRIO AMARRE CONTRA 1520-04 Y SE CERRO POR SCADA | S22040200052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-04-02 | 29298 | keep | 0 | Apr | 2022 | 0.019955 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2022-04-02 11:09 | 2022-04-02 12:18 | 752 | 001:09 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1520-05 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1520-01 Y 1520-04. SE CERRO AMARRE CONTRA 1520-04 Y ENTRO UN 50% | S22040200052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-04-02 | 51888 | keep | 0 | Apr | 2022 | 0.035341 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2022-04-02 11:09 | 2022-04-02 12:06 | 68 | 000:57 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1520-05 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1520-01 Y 1520-04. SE ABRIO AMARRE CONTRA 1520-04 Y SE CERRO POR SCADA | S22040200052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-04-02 | 3876 | keep | 0 | Apr | 2022 | 0.0026399 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
CAGUAS | 2022-04-02 11:28 | 2022-04-02 16:30 | 30 | 005:02 | P | ESTRUCTURA AVERIADA | 1 X 20 EN C/L SE REMPLAZO POSTE | C22040200060 | New_Event | Defective Pole | Include | Include | Equipment | 302 | 2022-04-02 | 9060 | keep | 0 | Apr | 2022 | 0.0061707 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-04-02 11:37 | 2022-04-02 14:25 | 25 | 002:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22040200020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-04-02 | 4200 | keep | 0 | Apr | 2022 | 0.0028606 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-02 11:45 | 2022-04-02 14:04 | 100 | 002:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M22040200272 | New_Event | Wire Down | Include | Include | Equipment | 139 | 2022-04-02 | 13900 | keep | 0 | Apr | 2022 | 0.0094672 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-02 11:57 | 2022-04-02 11:58 | 3070 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 3070 | keep | 0 | Apr | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
CAGUAS | 2022-04-02 12:15 | 2022-04-02 14:50 | 30 | 002:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | C22040200071 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2022-04-02 | 4650 | keep | 0 | Apr | 2022 | 0.0031671 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-02 12:18 | 2022-04-02 13:10 | 376 | 000:52 | P | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE REPORTO CAUSA. SE CERRO MACHETES Y ENTRO EN SU TOTALIDAD | S22040200052 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-04-02 | 19552 | keep | 0 | Apr | 2022 | 0.013317 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-04-02 12:39 | 2022-04-02 19:21 | 29 | 006:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22040200105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 402 | 2022-04-02 | 11658 | keep | 0 | Apr | 2022 | 0.0079402 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CANOVANAS | 2022-04-02 12:40 | 2022-04-02 15:07 | 100 | 002:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA, Y 1X15 EN XMR | R22040200090 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2022-04-02 | 14700 | keep | 0 | Apr | 2022 | 0.010012 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-02 13:05 | 2022-04-02 22:14 | 42 | 009:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X30 EN C/L & SE REMOVIO COTORRA (AVE) DEL 13KV | B22040200108 | New_Event |  |  | Include | Wildlife | 549 | 2022-04-02 | 23058 | keep | 0 | Apr | 2022 | 0.015705 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
CAGUAS | 2022-04-02 13:06 | 2022-04-02 15:15 | 100 | 002:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 EN CORTE DE LINEA SE REMPLAZO AISLADOR | C22040200074 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 129 | 2022-04-02 | 12900 | keep | 0 | Apr | 2022 | 0.0087861 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-02 13:08 | 2022-04-02 18:00 | 20 | 004:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEAS CRUZADAS HAY QUE RETEZARLAS | A22040200024 | New_Event | Wire Down | Include | Include | Equipment | 292 | 2022-04-02 | 5840 | keep | 0 | Apr | 2022 | 0.0039776 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-02 13:10 | 2022-04-02 15:40 | 25 | 002:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22040200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-04-02 | 3750 | keep | 0 | Apr | 2022 | 0.0025541 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-04-02 13:12 | 2022-04-02 15:30 | 10 | 002:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22040200025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-04-02 | 1380 | keep | 0 | Apr | 2022 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-04-02 13:17 | 2022-04-02 14:21 | 25 | 001:04 | P | NO SE REPORTO CAUSA | 1X25 EN CL | R22040200097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-04-02 | 1600 | keep | 0 | Apr | 2022 | 0.0010898 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-02 13:18 | 2022-04-02 14:00 | 2 | 000:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22040200089 | New_Event | Bad Weather | Include | Include | Weather | 42 | 2022-04-02 | 84 | keep | 0 | Apr | 2022 | 5.7212e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2022-04-02 13:22 | 2022-04-03 09:40 | 100 | 020:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22040200077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1218 | 2022-04-02 | 121800 | keep | 0 | Apr | 2022 | 0.082957 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-02 13:31 | 2022-04-02 18:30 | 1 | 004:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22040200027 | New_Event | Bad Weather | Include | Include | Weather | 299 | 2022-04-02 | 299 | keep | 0 | Apr | 2022 | 0.00020365 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-02 13:35 | 2022-04-02 14:25 | 9 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS | A22040200017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-04-02 | 450 | keep | 0 | Apr | 2022 | 0.00030649 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-04-02 13:40 | 2022-04-02 13:46 | 60 | 000:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22040200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-04-02 | 360 | keep | 0 | Apr | 2022 | 0.00024519 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-02 14:05 | 2022-04-03 09:42 | 60 | 019:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22040200296 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1177 | 2022-04-02 | 70620 | keep | 0 | Apr | 2022 | 0.048099 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-04-02 14:07 | 2022-04-02 14:08 | 390 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR | M22040200301 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-02 | 390 | keep | 0 | Apr | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2022-04-02 14:08 | 2022-04-02 16:00 | 25 | 001:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22040200311 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 112 | 2022-04-02 | 2800 | keep | 0 | Apr | 2022 | 0.0019071 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-02 14:12 | 2022-04-02 14:13 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22040200033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 449 | keep | 0 | Apr | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
PONCE | 2022-04-02 14:12 | 2022-04-02 16:02 | 50 | 001:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASES PRIMARIA POR RAMA | P22040200032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-04-02 | 5500 | keep | 0 | Apr | 2022 | 0.003746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-02 14:24 | 2022-04-02 16:23 | 100 | 001:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 2 X 50 EN C/L | R22040200103 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2022-04-02 | 11900 | keep | 0 | Apr | 2022 | 0.008105 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-04-02 14:28 | 2022-04-02 15:36 | 1 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22040200084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-04-02 | 68 | keep | 0 | Apr | 2022 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-02 14:28 | 2022-04-02 14:29 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA TRES OPERACIONES Y QUEDA EN SERVICIO | P22040200036 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 449 | keep | 0 | Apr | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
MAYAGÃœEZ | 2022-04-02 14:34 | 2022-04-02 15:55 | 50 | 001:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-04-02 | 4050 | keep | 0 | Apr | 2022 | 0.0027584 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-04-02 14:50 | 2022-04-02 14:51 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22040200315 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 1047 | keep | 0 | Apr | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
HUMACAO | 2022-04-02 14:52 | 2022-04-02 14:53 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | C22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 2450 | keep | 0 | Apr | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
PONCE | 2022-04-02 15:03 | 2022-04-02 16:44 | 5 | 001:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN TRANSFORMADOR | P22040200038 | New_Event | Wire Down | Include | Include | Equipment | 101 | 2022-04-02 | 505 | keep | 0 | Apr | 2022 | 0.00034395 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-04-02 15:05 | 2022-04-02 15:39 | 30 | 000:34 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22040200106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2022-04-02 | 1020 | keep | 0 | Apr | 2022 | 0.00069472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-04-02 15:10 | 2022-04-02 15:11 | 154 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 15900 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-02 | 154 | keep | 0 | Apr | 2022 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2022-04-02 15:10 | 2022-04-02 15:11 | 1261 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 15900 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-02 | 1261 | keep | 0 | Apr | 2022 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2022-04-02 15:10 | 2022-04-02 15:11 | 3894 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 15900 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-02 | 3894 | keep | 0 | Apr | 2022 | 0.0026522 | 0.0026522 | Momentary | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2022-04-02 15:10 | 2022-04-02 15:11 | 997 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 15900 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-02 | 997 | keep | 0 | Apr | 2022 | 0.00067905 | 0.00067905 | Momentary | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2022-04-02 15:10 | 2022-04-02 15:11 | 1497 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 15900 | M22040200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-02 | 1497 | keep | 0 | Apr | 2022 | 0.0010196 | 0.0010196 | Momentary | FALSE | FALSE | Not_TMED_Event | 1497
HUMACAO | 2022-04-02 15:14 | 2022-04-02 17:00 | 50 | 001:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | C22040200094 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2022-04-02 | 5300 | keep | 0 | Apr | 2022 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-02 15:27 | 2022-04-02 20:36 | 50 | 005:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22040200082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 309 | 2022-04-02 | 15450 | keep | 0 | Apr | 2022 | 0.010523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-02 15:27 | 2022-04-02 15:28 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE LLEVA A SU VEZ LA CARGA DEL 1346-05 | S22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 922 | keep | 0 | Apr | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-04-02 15:27 | 2022-04-02 15:28 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE LLEVA A SU VEZ LA CARGA DEL 1346-05 | S22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 135 | keep | 0 | Apr | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
PONCE | 2022-04-02 15:30 | 2022-04-02 15:46 | 3 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN MONTURA DE TRANSFORMADORES PARA REPARAR CONEXIONES SECUNDARIAS | P22040200039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2022-04-02 | 48 | keep | 0 | Apr | 2022 | 3.2693e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-04-02 15:33 | 2022-04-02 15:35 | 222 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1907-03 Y SE CERRO POR SCADA LLEVA 1909-09 | S22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-02 | 444 | keep | 0 | Apr | 2022 | 0.00030241 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-04-02 15:33 | 2022-04-02 15:35 | 4456 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1907-03 Y SE CERRO POR SCADA LLEVA 1909-09 | S22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-02 | 8912 | keep | 0 | Apr | 2022 | 0.0060699 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-04-02 15:40 | 2022-04-02 19:34 | 35 | 003:54 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S22040200084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 234 | 2022-04-02 | 8190 | keep | 0 | Apr | 2022 | 0.0055782 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-04-02 16:00 | 2022-04-02 17:30 | 60 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A12040200034 | New_Event | Bad Weather | Include | Include | Weather | 90 | 2022-04-02 | 5400 | keep | 0 | Apr | 2022 | 0.0036779 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-02 16:05 | 2022-04-03 11:05 | 5 | 019:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22040200035 | New_Event | Wire Down | Include | Include | Equipment | 1140 | 2022-04-02 | 5700 | keep | 0 | Apr | 2022 | 0.0038822 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-04-02 16:07 | 2022-04-03 12:07 | 160 | 020:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CORTE DE LINEA ABIERTO | C22040200098 | New_Event | Wire Down | Include | Include | Equipment | 1200 | 2022-04-02 | 192000 | keep | 0 | Apr | 2022 | 0.13077 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
MAYAGÃœEZ | 2022-04-02 16:09 | 2022-04-03 11:55 | 10 | 019:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA SE RETIRO GLOBO ENREDADO EN LAS LINEAS | M22040200332 | New_Event |  |  | Include | Wildlife | 1186 | 2022-04-02 | 11860 | keep | 0 | Apr | 2022 | 0.0080778 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-02 16:17 | 2022-04-02 16:18 | 3701 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO | C22040200000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-02 | 3701 | keep | 0 | Apr | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
SAN JUAN | 2022-04-02 16:18 | 2022-04-02 17:44 | 10 | 001:26 | P | DESGANCHE | 1 X 10 EN TRASNFROMADOR SE REALIZO DESGANCHE | R22040200110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-04-02 | 860 | keep | 0 | Apr | 2022 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-02 16:18 | 2022-04-02 18:00 | 60 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE RETIRO AVE | C22040200000 | 1st_after_momentary |  |  | Include | Wildlife | 102 | 2022-04-02 | 6120 | keep | 0 | Apr | 2022 | 0.0041683 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 873 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 2619 | keep | 0 | Apr | 2022 | 0.0017838 | 0.0005946 | Momentary | FALSE | FALSE | Not_TMED_Event | 873
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 1261 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 3783 | keep | 0 | Apr | 2022 | 0.0025766 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 2713 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 8139 | keep | 0 | Apr | 2022 | 0.0055434 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 51 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO LLEVA LA CARGA DE 6001-05 | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 153 | keep | 0 | Apr | 2022 | 0.00010421 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 285 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO CARGA SE ENCUENTRA POR 6001-04 | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 855 | keep | 0 | Apr | 2022 | 0.00058234 | 0.00019411 | Momentary | FALSE | FALSE | Not_TMED_Event | 285
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 1253 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO LLEVA LA CARGA DE 6010-02 | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 3759 | keep | 0 | Apr | 2022 | 0.0025602 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 1266 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO CARGA POR 6010-01 | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 3798 | keep | 0 | Apr | 2022 | 0.0025868 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 411 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 1233 | keep | 0 | Apr | 2022 | 0.00083979 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 1444 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO CARGA POR 6014-02 | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 4332 | keep | 0 | Apr | 2022 | 0.0029505 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 3630 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO LLEVA LA CARGA DE 6014-01 | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 10890 | keep | 0 | Apr | 2022 | 0.0074171 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 871 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO CARGA POR 6012-05 | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 2613 | keep | 0 | Apr | 2022 | 0.0017797 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 1617 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 4851 | keep | 0 | Apr | 2022 | 0.003304 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 1017 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 3051 | keep | 0 | Apr | 2022 | 0.002078 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 828 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 2484 | keep | 0 | Apr | 2022 | 0.0016918 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 863 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 2589 | keep | 0 | Apr | 2022 | 0.0017634 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 309 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 927 | keep | 0 | Apr | 2022 | 0.00063138 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 176 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 528 | keep | 0 | Apr | 2022 | 0.00035962 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-04-02 16:27 | 2022-04-02 16:30 | 108 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-02 | 324 | keep | 0 | Apr | 2022 | 0.00022067 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2022-04-02 16:33 | 2022-04-02 16:34 | 1984 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1529-12 QUE A SU VEZ LLEVA LA CARGA DEL 1911-07 | S22040200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-02 | 1984 | keep | 0 | Apr | 2022 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-04-02 16:33 | 2022-04-02 16:34 | 577 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1529-12 QUE A SUVEZ LLEVA LA CARGA DEL 1911-07 | S22040200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-02 | 577 | keep | 0 | Apr | 2022 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
ARECIBO | 2022-04-02 16:33 | 2022-04-02 19:15 | 3431 | 002:42 | T | AISLADOR ROTO, PARTIDO O SAFADO | LINEAS CRUZADAS SE REMPLAZO AISLADOR | A22040200040 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 162 | 2022-04-02 | 555822 | keep | 0 | Apr | 2022 | 0.37857 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2022-04-02 16:36 | 2022-04-02 17:56 | 1984 | 001:20 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1529-12 QUE LLEVA A SU VEZ LA CARGA DEL 1911-07. SE REALIZO DESGANCHE A VARETA Y SE CERRO INTERRUPTOR POR SCADA. | S22040200082 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-04-02 | 158720 | keep | 0 | Apr | 2022 | 0.1081 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-04-02 16:36 | 2022-04-02 17:56 | 577 | 001:20 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1529-12 QUE LLEVA A SU VEZ LA CARGA DEL 1911-07. SE REALIZO DESGANCHE A VARETA Y SE CERRO INTERRUPTOR POR SCADA. | S22040200082 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-04-02 | 46160 | keep | 0 | Apr | 2022 | 0.031439 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
SAN JUAN | 2022-04-02 16:47 | 2022-04-02 20:08 | 50 | 003:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO CAJA QUEMADA | S22040200100 | New_Event | Cutout Failure | Include | Include | Equipment | 201 | 2022-04-02 | 10050 | keep | 0 | Apr | 2022 | 0.006845 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-02 17:07 | 2022-04-02 17:30 | 100 | 000:23 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL QUEMANDO SOBRE LA LINEA | C22040200110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-04-02 | 2300 | keep | 0 | Apr | 2022 | 0.0015665 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-02 17:21 | 2022-04-02 19:25 | 10 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR Y SE REEMPLAZO PORTA FUSIBLE | R22040200113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-04-02 | 1240 | keep | 0 | Apr | 2022 | 0.00084456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-02 17:21 | 2022-04-02 17:40 | 100 | 000:19 | P | DESGANCHE | 2 X 100 Y 2 X 80 EN CORTE DE LINEA SE DESGANCHO | C22040200112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 19 | 2022-04-02 | 1900 | keep | 0 | Apr | 2022 | 0.0012941 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-02 17:36 | 2022-04-02 17:37 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 2302-02 | R22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 2708 | keep | 0 | Apr | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-04-02 17:36 | 2022-04-02 17:37 | 2524 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 2302-01 SE CERRO POR SCADA | R22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 2524 | keep | 0 | Apr | 2022 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-04-02 17:37 | 2022-04-02 18:46 | 60 | 001:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22040200120 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-04-02 | 4140 | keep | 0 | Apr | 2022 | 0.0028197 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-02 17:50 | 2022-04-02 22:39 | 60 | 004:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22040200373 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-04-02 | 17340 | keep | 0 | Apr | 2022 | 0.01181 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-02 17:52 | 2022-04-02 17:53 | 974 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | BARRA 11 DE AGOSTO | M22040200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-04-02 | 974 | keep | 0 | Apr | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
AGUADILLA | 2022-04-02 17:59 | 2022-04-03 00:24 | 12 | 006:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22040200375 | New_Event | Bad Weather | Include | Include | Weather | 385 | 2022-04-02 | 4620 | keep | 0 | Apr | 2022 | 0.0031467 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-04-02 18:02 | 2022-04-02 18:45 | 20 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA RPARAR BAJANTE SECUNDARIO | R22040200107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2022-04-02 | 860 | keep | 0 | Apr | 2022 | 0.00058574 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-02 18:07 | 2022-04-03 09:14 | 60 | 015:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22040200068 | New_Event | Cutout Failure | Include | Include | Equipment | 907 | 2022-04-02 | 54420 | keep | 0 | Apr | 2022 | 0.037065 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-02 18:13 | 2022-04-02 21:17 | 80 | 003:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE | R22040200122 | New_Event |  |  | Include | Wildlife | 184 | 2022-04-02 | 14720 | keep | 0 | Apr | 2022 | 0.010026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-04-02 18:31 | 2022-04-02 19:27 | 6 | 000:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22040200044 | New_Event |  |  | Include | Wildlife | 56 | 2022-04-02 | 336 | keep | 0 | Apr | 2022 | 0.00022885 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-04-02 18:31 | 2022-04-02 18:32 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22040200045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 3718 | keep | 0 | Apr | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2022-04-02 18:58 | 2022-04-02 21:09 | 100 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA | B22040200131 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2022-04-02 | 13100 | keep | 0 | Apr | 2022 | 0.0089224 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-04-02 19:25 | 2022-04-02 21:01 | 40 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR GLOBO | P22040200048 | New_Event |  |  | Include | Wildlife | 96 | 2022-04-02 | 3840 | keep | 0 | Apr | 2022 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-04-02 19:39 | 2022-04-03 10:48 | 40 | 015:09 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | B22040200138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 909 | 2022-04-02 | 36360 | keep | 0 | Apr | 2022 | 0.024765 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-02 19:41 | 2022-04-03 10:29 | 150 | 014:48 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | M22040200393 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 888 | 2022-04-02 | 133200 | keep | 0 | Apr | 2022 | 0.090722 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-04-02 19:50 | 2022-04-03 15:06 | 40 | 019:16 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C22040200126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1156 | 2022-04-02 | 46240 | keep | 0 | Apr | 2022 | 0.031494 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-02 19:55 | 2022-04-02 21:30 | 30 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040200083 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2022-04-02 | 2850 | keep | 0 | Apr | 2022 | 0.0019411 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-04-02 20:00 | 2022-04-03 10:03 | 2 | 014:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | P22040200054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 843 | 2022-04-02 | 1686 | keep | 0 | Apr | 2022 | 0.0011483 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-04-02 20:04 | 2022-04-02 22:36 | 38 | 002:32 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22040200140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-04-02 | 5776 | keep | 0 | Apr | 2022 | 0.003934 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CANOVANAS | 2022-04-02 20:06 | 2022-04-02 22:28 | 80 | 002:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22040200130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-04-02 | 11360 | keep | 0 | Apr | 2022 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-02 21:20 | 2022-04-03 13:50 | 30 | 016:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22040200412 | New_Event | Bad Weather | Include | Include | Weather | 990 | 2022-04-02 | 29700 | keep | 0 | Apr | 2022 | 0.020229 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-04-02 21:39 | 2022-04-03 02:00 | 10 | 004:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | M22040200417 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2022-04-02 | 2610 | keep | 0 | Apr | 2022 | 0.0017777 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-04-02 21:59 | 2022-04-03 10:42 | 156 | 012:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22040200141 | New_Event | Cutout Failure | Include | Include | Equipment | 763 | 2022-04-02 | 119028 | keep | 0 | Apr | 2022 | 0.081069 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
CAGUAS | 2022-04-02 22:02 | 2022-04-02 22:04 | 1879 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-02 | 3758 | keep | 0 | Apr | 2022 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
BAYAMON | 2022-04-02 22:36 | 2022-04-03 09:03 | 20 | 010:27 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L Y 1 X 10 EN XMR | B22040200148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 627 | 2022-04-02 | 12540 | keep | 0 | Apr | 2022 | 0.0085409 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-04-02 22:45 | 2022-04-03 10:29 | 6 | 011:44 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C22040200132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 704 | 2022-04-02 | 4224 | keep | 0 | Apr | 2022 | 0.0028769 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-02 22:48 | 2022-04-03 14:00 | 200 | 015:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22040200426 | New_Event | Bad Weather | Include | Include | Weather | 912 | 2022-04-02 | 182400 | keep | 0 | Apr | 2022 | 0.12423 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-04-02 23:01 | 2022-04-02 23:02 | 3003 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SADA | R22040200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-02 | 3003 | keep | 0 | Apr | 2022 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2022-04-02 23:10 | 2022-04-03 09:47 | 500 | 010:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR DEL SUELO | R22040200146 | New_Event | Wire Down | Include | Include | Equipment | 637 | 2022-04-02 | 318500 | keep | 0 | Apr | 2022 | 0.21693 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BARRANQUITAS | 2022-04-02 23:37 | 2022-04-03 15:36 | 90 | 015:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22040200134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 959 | 2022-04-02 | 86310 | keep | 0 | Apr | 2022 | 0.058785 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2022-04-03 00:47 | 2022-04-03 09:15 | 90 | 008:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22040300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 508 | 2022-04-03 | 45720 | keep | 0 | Apr | 2022 | 0.03114 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2022-04-03 01:13 | 2022-04-03 01:14 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
CAGUAS | 2022-04-03 01:19 | 2022-04-03 07:21 | 1290 | 006:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO ZAFADO HACIA TRANSFORMADOR | C22040300001 | New_Event | Wire Down | Include | Include | Equipment | 362 | 2022-04-03 | 466980 | keep | 0 | Apr | 2022 | 0.31806 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2022-04-03 01:30 | 2022-04-03 08:42 | 25 | 007:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22040300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 432 | 2022-04-03 | 10800 | keep | 0 | Apr | 2022 | 0.0073558 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-03 02:31 | 2022-04-03 09:06 | 66 | 006:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22040300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 395 | 2022-04-03 | 26070 | keep | 0 | Apr | 2022 | 0.017756 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
ARECIBO | 2022-04-03 03:05 | 2022-04-03 04:45 | 10 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE SECCIONALIZO LINEA SECUNDARIA CRUZADA | A22040200137 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2022-04-03 | 1000 | keep | 0 | Apr | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-03 03:40 | 2022-04-03 09:44 | 20 | 006:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C22040300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 364 | 2022-04-03 | 7280 | keep | 0 | Apr | 2022 | 0.0049584 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-04-03 03:49 | 2022-04-03 12:10 | 200 | 008:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22040300002 | New_Event | Cutout Failure | Include | Include | Equipment | 501 | 2022-04-03 | 100200 | keep | 0 | Apr | 2022 | 0.068246 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-04-03 04:14 | 2022-04-03 06:42 | 83 | 002:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22040300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-04-03 | 12284 | keep | 0 | Apr | 2022 | 0.0083666 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
CANOVANAS | 2022-04-03 05:22 | 2022-04-03 20:25 | 10 | 015:03 | P | NO SE REPORTO CAUSA | 1 X10 EN TRANSFORMADOR NO CAUSA | R22040300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 903 | 2022-04-03 | 9030 | keep | 0 | Apr | 2022 | 0.0061503 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-03 05:27 | 2022-04-03 09:00 | 40 | 003:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22040300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-04-03 | 8520 | keep | 0 | Apr | 2022 | 0.0058029 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-04-03 06:34 | 2022-04-03 12:42 | 55 | 006:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22040300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2022-04-03 | 20240 | keep | 0 | Apr | 2022 | 0.013785 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
UTUADO | 2022-04-03 06:44 | 2022-04-03 10:07 | 25 | 003:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-04-03 | 5075 | keep | 0 | Apr | 2022 | 0.0034566 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-04-03 06:49 | 2022-04-03 06:50 | 4882 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22040300017 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-03 | 4882 | keep | 0 | Apr | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2022-04-03 06:50 | 2022-04-03 12:30 | 15 | 005:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22040300018 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 340 | 2022-04-03 | 5100 | keep | 0 | Apr | 2022 | 0.0034736 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-04-03 06:51 | 2022-04-03 06:52 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 2106 | keep | 0 | Apr | 2022 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
PONCE | 2022-04-03 07:00 | 2022-04-03 11:30 | 12 | 004:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR POR CONTACTO DE AVE | P22040300005 | New_Event |  |  | Include | Wildlife | 270 | 2022-04-03 | 3240 | keep | 0 | Apr | 2022 | 0.0022067 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-04-03 07:15 | 2022-04-03 17:10 | 80 | 009:55 | P | NO SE REPORTO CAUSA | 1 X 40, 1 X 30 EN CORTE DE LINEA 1 X 10 EN XMR | R22040300014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 595 | 2022-04-03 | 47600 | keep | 0 | Apr | 2022 | 0.03242 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-03 07:15 | 2022-04-03 08:08 | 60 | 000:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C22040300014 | New_Event |  |  | Include | Wildlife | 53 | 2022-04-03 | 3180 | keep | 0 | Apr | 2022 | 0.0021659 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-04-03 07:21 | 2022-04-03 09:20 | 1 | 001:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22040300007 | New_Event | Wire Down | Include | Include | Equipment | 119 | 2022-04-03 | 119 | keep | 0 | Apr | 2022 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-03 07:31 | 2022-04-03 10:10 | 1 | 002:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA INFORMA JOURNEY LINEMAN NO IDENTIFICO CAUSA | A22040300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2022-04-03 | 159 | keep | 0 | Apr | 2022 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-03 07:31 | 2022-04-03 07:32 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 2610 | keep | 0 | Apr | 2022 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
SAN JUAN | 2022-04-03 07:42 | 2022-04-03 07:43 | 1026 | 000:01 | T | OTRAS CAUSAS | RECIERRE | R22040300019 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-04-03 | 1026 | keep | 0 | Apr | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2022-04-03 07:43 | 2022-04-03 12:58 | 34 | 005:15 | P | OTRAS CAUSAS | PROBLEMA DEL CLIENTE SE REEMPLAZO CAJA, DISCO QUEMADO Y BAJANTE PRIMARIO HACIA CAJA 3 X 15 EN BANCO DE TRANSFORMADORES Y 1 X 30 EN CORTE DE LINEA | R22040300020 | 1st_after_momentary | Other Causes | Include | Include | Other | 315 | 2022-04-03 | 10710 | keep | 0 | Apr | 2022 | 0.0072945 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
ARECIBO | 2022-04-03 07:45 | 2022-04-03 13:51 | 100 | 006:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 366 | 2022-04-03 | 36600 | keep | 0 | Apr | 2022 | 0.024928 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-03 08:26 | 2022-04-03 08:27 | 718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 90% DEL 1901-05 | S22040300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 718 | keep | 0 | Apr | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
SAN JUAN | 2022-04-03 08:26 | 2022-04-03 08:30 | 686 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22040300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-03 | 2744 | keep | 0 | Apr | 2022 | 0.0018689 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
BAYAMON | 2022-04-03 08:26 | 2022-04-03 08:27 | 558 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 90% POR EL 1330-01 | S22040300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 558 | keep | 0 | Apr | 2022 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
MAYAGÃœEZ | 2022-04-03 09:06 | 2022-04-03 13:35 | 50 | 004:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22040300047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2022-04-03 | 13450 | keep | 0 | Apr | 2022 | 0.0091607 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-03 09:07 | 2022-04-04 09:31 | 50 | 024:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22040300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1464 | 2022-04-03 | 73200 | keep | 0 | Apr | 2022 | 0.049856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-04-03 09:24 | 2022-04-03 14:00 | 1 | 004:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22040300014 | New_Event | Bad Weather | Include | Include | Weather | 276 | 2022-04-03 | 276 | keep | 0 | Apr | 2022 | 0.00018798 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-04-03 09:26 | 2022-04-03 09:27 | 934 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36400 | A22040300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-03 | 934 | keep | 0 | Apr | 2022 | 0.00063614 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-04-03 09:26 | 2022-04-03 09:27 | 4 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36400 | A22040300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-03 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-04-03 09:26 | 2022-04-03 09:27 | 1479 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36400 | A22040300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-03 | 1479 | keep | 0 | Apr | 2022 | 0.0010073 | 0.0010073 | Momentary | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-04-03 09:26 | 2022-04-03 09:27 | 1841 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36400 | A22040300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-03 | 1841 | keep | 0 | Apr | 2022 | 0.0012539 | 0.0012539 | Momentary | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-04-03 09:26 | 2022-04-03 09:27 | 1950 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36400 | A22040300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-03 | 1950 | keep | 0 | Apr | 2022 | 0.0013281 | 0.0013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 1950
ARECIBO | 2022-04-03 09:27 | 2022-04-03 11:25 | 50 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A22040300010 | New_Event |  |  | Include | Wildlife | 118 | 2022-04-03 | 5900 | keep | 0 | Apr | 2022 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-04-03 09:30 | 2022-04-03 13:21 | 100 | 003:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | CRUCE CON AVE Y SE REEMPLAZO CAJA QUEMADA 1 X 80 EN CORTE DE LINEA | C22040300026 | New_Event |  |  | Include | Wildlife | 231 | 2022-04-03 | 23100 | keep | 0 | Apr | 2022 | 0.015733 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-03 09:32 | 2022-04-03 09:33 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1709-01 SPARE QUE LLEVA 1720-07 | S22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 6136 | keep | 0 | Apr | 2022 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
ARECIBO | 2022-04-03 09:35 | 2022-04-03 09:36 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22040300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 2107 | keep | 0 | Apr | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
FAJARDO | 2022-04-03 09:47 | 2022-04-03 13:58 | 100 | 004:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | R22040200146 | Partial_restoration | Wire Down | Include | Include | Equipment | 251 | 2022-04-03 | 25100 | keep | 0 | Apr | 2022 | 0.017095 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-03 09:53 | 2022-04-03 10:54 | 50 | 001:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22040300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-04-03 | 3050 | keep | 0 | Apr | 2022 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-03 10:03 | 2022-04-03 15:55 | 6 | 005:52 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22040300055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2022-04-03 | 2112 | keep | 0 | Apr | 2022 | 0.0014385 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-04-03 10:25 | 2022-04-03 10:59 | 8 | 000:34 | P | DESGANCHE | SE REMPLAZO PARARRAYO QUEMADO DE 3KV POR DESGANCHE | P22040300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 34 | 2022-04-03 | 272 | keep | 0 | Apr | 2022 | 0.00018526 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-03 10:28 | 2022-04-03 11:37 | 36 | 001:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22040300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-04-03 | 2484 | keep | 0 | Apr | 2022 | 0.0016918 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
VEGA BAJA | 2022-04-03 10:28 | 2022-04-03 11:31 | 1 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22040300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-04-03 | 63 | keep | 0 | Apr | 2022 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-03 10:29 | 2022-04-03 12:14 | 4 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22040300010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2022-04-03 | 420 | keep | 0 | Apr | 2022 | 0.00028606 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-04-03 10:37 | 2022-04-03 10:39 | 327 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE | C22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-03 | 654 | keep | 0 | Apr | 2022 | 0.00044544 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
CAGUAS | 2022-04-03 10:38 | 2022-04-03 13:14 | 16 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AUTO PRIVADO IMPACTO TRANSFORMADOR | C22040300036 | New_Event |  |  | Include | Wildlife | 156 | 2022-04-03 | 2496 | keep | 0 | Apr | 2022 | 0.0017 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-04-03 10:48 | 2022-04-03 14:46 | 1 | 003:58 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER NO CAUSA | C22040300038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 238 | 2022-04-03 | 238 | keep | 0 | Apr | 2022 | 0.0001621 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-03 11:19 | 2022-04-03 14:29 | 30 | 003:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22040300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-04-03 | 5700 | keep | 0 | Apr | 2022 | 0.0038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-04-03 11:53 | 2022-04-03 15:55 | 50 | 004:02 | P | DESGANCHE | 1 X 50 EN C/L Y SE REALIZO DESGANCHE | R22040300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-04-03 | 12100 | keep | 0 | Apr | 2022 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-03 11:59 | 2022-04-03 12:04 | 922 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1346-05 | S22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-04-03 | 4610 | keep | 0 | Apr | 2022 | 0.0031399 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-04-03 11:59 | 2022-04-03 12:04 | 135 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA LA CARGA DEL 1346-05 | S22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-04-03 | 675 | keep | 0 | Apr | 2022 | 0.00045974 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-04-03 12:38 | 2022-04-03 13:54 | 14 | 001:16 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN RISER Y SE CAMBIO PISTOLA DEL PM | S22040300012 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 76 | 2022-04-03 | 1064 | keep | 0 | Apr | 2022 | 0.00072469 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-04-03 12:54 | 2022-04-03 16:52 | 1352 | 003:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE Y SE CERRO INTERRUPTOR POR SCADA LLEVA LA CARGA DEL 6014-03 | M22040300071 | New_Event | Wire Down | Include | Include | Equipment | 238 | 2022-04-03 | 321776 | keep | 0 | Apr | 2022 | 0.21916 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-04-03 12:54 | 2022-04-03 16:52 | 871 | 003:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA POR 6012-05 | M22040300071 | New_Event | Wire Down | Include | Include | Equipment | 238 | 2022-04-03 | 207298 | keep | 0 | Apr | 2022 | 0.14119 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2022-04-03 13:04 | 2022-04-03 14:36 | 6 | 001:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE ABIERTO A BUSHING | R22040300070 | New_Event | Wire Down | Include | Include | Equipment | 92 | 2022-04-03 | 552 | keep | 0 | Apr | 2022 | 0.00037596 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-04-03 13:32 | 2022-04-03 16:44 | 5 | 003:12 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE CRITICO | C22040300043 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 192 | 2022-04-03 | 960 | keep | 0 | Apr | 2022 | 0.00065385 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-04-03 14:04 | 2022-04-03 17:20 | 60 | 003:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22040300033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-04-03 | 11760 | keep | 0 | Apr | 2022 | 0.0080097 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-03 14:08 | 2022-04-03 15:15 | 20 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA Y SE REPORTO CRUCE POR AVE | S22040300019 | New_Event |  |  | Include | Wildlife | 67 | 2022-04-03 | 1340 | keep | 0 | Apr | 2022 | 0.00091267 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-03 14:30 | 2022-04-03 15:59 | 1 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A22040300036 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2022-04-03 | 89 | keep | 0 | Apr | 2022 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-03 15:08 | 2022-04-03 19:59 | 1192 | 004:51 | T | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEAS Y SE CERRO POR SCADA | M22040300117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2022-04-03 | 346872 | keep | 0 | Apr | 2022 | 0.23625 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
SAN JUAN | 2022-04-03 15:26 | 2022-04-03 15:27 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1346-05 | S22040300000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 922 | keep | 0 | Apr | 2022 | 0.00062797 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-03 15:26 | 2022-04-03 15:27 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1346-05 | S22040300000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 135 | keep | 0 | Apr | 2022 | 9.1948e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-03 15:39 | 2022-04-03 18:47 | 50 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22040300044 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2022-04-03 | 9400 | keep | 0 | Apr | 2022 | 0.0064023 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-04-03 15:43 | 2022-04-03 23:35 | 400 | 007:52 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN DIFERENTES CORTES DE LINEA REQUIERE DESGANCHE | M22040300133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 472 | 2022-04-03 | 188800 | keep | 0 | Apr | 2022 | 0.12859 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
ARECIBO | 2022-04-03 16:01 | 2022-04-03 17:28 | 1 | 001:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | A22040300048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-04-03 | 87 | keep | 0 | Apr | 2022 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-03 16:17 | 2022-04-03 21:14 | 7 | 004:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA EN TRANSFORMADOR | B22040300014 | New_Event | Wire Down | Include | Include | Equipment | 297 | 2022-04-03 | 2079 | keep | 0 | Apr | 2022 | 0.001416 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-04-03 16:30 | 2022-04-03 16:31 | 3432 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR A TRAVES DE LA PORTATIL 22. 20% DE SU CARGA POR EL 1303-02 | S22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 3432 | keep | 0 | Apr | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-04-03 16:30 | 2022-04-03 16:31 | 552 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 60% DE LA CARGA POR EL 1206-04 | S22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 552 | keep | 0 | Apr | 2022 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2022-04-03 16:30 | 2022-04-03 16:31 | 1483 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 40% DE LA CARGA POR EL 1206-04 Y OTRO 30% POR EL 1336-08 | S22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 1483 | keep | 0 | Apr | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
MAYAGÃœEZ | 2022-04-03 17:28 | 2022-04-03 19:03 | 150 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22040300188 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2022-04-03 | 14250 | keep | 0 | Apr | 2022 | 0.0097056 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-04-03 17:30 | 2022-04-03 19:15 | 80 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22040300018 | New_Event |  |  | Include | Wildlife | 105 | 2022-04-03 | 8400 | keep | 0 | Apr | 2022 | 0.0057212 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-03 18:32 | 2022-04-03 22:10 | 6 | 003:38 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S22040300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2022-04-03 | 1308 | keep | 0 | Apr | 2022 | 0.00089087 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-04-03 18:45 | 2022-04-03 18:46 | 3 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA QUEMADA | C22040300022 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-04-03 | 3 | keep | 0 | Apr | 2022 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-04-03 18:58 | 2022-04-03 20:40 | 40 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RATA | P22040300025 | New_Event |  |  | Include | Wildlife | 102 | 2022-04-03 | 4080 | keep | 0 | Apr | 2022 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-03 19:04 | 2022-04-04 01:00 | 100 | 005:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22040300214 | New_Event | Bad Weather | Include | Include | Weather | 356 | 2022-04-03 | 35600 | keep | 0 | Apr | 2022 | 0.024247 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-03 19:21 | 2022-04-04 07:55 | 20 | 012:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22040300223 | New_Event | Wire Down | Include | Include | Equipment | 754 | 2022-04-03 | 15080 | keep | 0 | Apr | 2022 | 0.010271 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-03 19:39 | 2022-04-04 14:09 | 10 | 018:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22040300058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1110 | 2022-04-03 | 11100 | keep | 0 | Apr | 2022 | 0.0075602 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-04-03 19:50 | 2022-04-03 22:38 | 424 | 002:48 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO RISER AVERIADO POR DISPARO Y SE TRANSFIRIO LA CARGA AL 2003-01 | R22040300088 | New_Event |  |  | Include | Wildlife | 168 | 2022-04-03 | 71232 | keep | 0 | Apr | 2022 | 0.048516 | 0.00028878 | Sustained | FALSE | FALSE | Not_TMED_Event | 424
HUMACAO | 2022-04-03 19:52 | 2022-04-04 07:37 | 100 | 011:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C22040300055 | New_Event |  |  | Include | Wildlife | 705 | 2022-04-03 | 70500 | keep | 0 | Apr | 2022 | 0.048017 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-03 20:04 | 2022-04-03 21:12 | 200 | 001:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22040300241 | New_Event | Bad Weather | Include | Include | Weather | 68 | 2022-04-03 | 13600 | keep | 0 | Apr | 2022 | 0.0092629 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-04-03 20:34 | 2022-04-03 20:36 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22040300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-03 | 4252 | keep | 0 | Apr | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-04-03 20:40 | 2022-04-03 20:41 | 327 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 327 | keep | 0 | Apr | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2022-04-03 20:42 | 2022-04-03 22:30 | 327 | 001:48 | T | NO SE REPORTO CAUSA | DISPARO NO SE ENCONTRO CAUSA | C22040300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 108 | 2022-04-03 | 35316 | keep | 0 | Apr | 2022 | 0.024054 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
CAGUAS | 2022-04-03 20:42 | 2022-04-04 11:25 | 200 | 014:43 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22040300063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 883 | 2022-04-03 | 176600 | keep | 0 | Apr | 2022 | 0.12028 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-04-03 23:24 | 2022-04-03 23:25 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22040300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-03 | 1192 | keep | 0 | Apr | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2022-04-04 02:34 | 2022-04-04 02:35 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 1827 | keep | 0 | Apr | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
UTUADO | 2022-04-04 03:06 | 2022-04-04 13:16 | 30 | 010:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 610 | 2022-04-04 | 18300 | keep | 0 | Apr | 2022 | 0.012464 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-04 03:48 | 2022-04-04 13:10 | 81 | 009:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S22040400019 | New_Event | Cutout Failure | Include | Include | Equipment | 562 | 2022-04-04 | 45522 | keep | 0 | Apr | 2022 | 0.031005 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
UTUADO | 2022-04-04 04:55 | 2022-04-04 09:51 | 20 | 004:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-04-04 | 5920 | keep | 0 | Apr | 2022 | 0.0040321 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-04 05:47 | 2022-04-04 11:35 | 50 | 005:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22040400023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 348 | 2022-04-04 | 17400 | keep | 0 | Apr | 2022 | 0.011851 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-04 05:53 | 2022-04-04 06:38 | 4 | 000:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE MONTURA TRIFASICA | P22040400126 | New_Event | Wire Down | Include | Include | Equipment | 45 | 2022-04-04 | 180 | keep | 0 | Apr | 2022 | 0.0001226 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-04-04 05:54 | 2022-04-04 05:55 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2404-06 | R22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 4085 | keep | 0 | Apr | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-04-04 05:54 | 2022-04-04 05:55 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2402-03 | R22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 7621 | keep | 0 | Apr | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
SAN JUAN | 2022-04-04 05:56 | 2022-04-04 05:58 | 225 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-5 | S22040400026 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-04-04 | 450 | keep | 0 | Apr | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-04 05:56 | 2022-04-04 05:58 | 870 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1303-04 | S22040400026 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-04-04 | 1740 | keep | 0 | Apr | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-04-04 06:02 | 2022-04-04 08:18 | 225 | 002:16 | T | DESCONECTIVO DEFECTUOSO | SE CERRO N/O 1908-3 Y 1303-4 PARA SECCIONALIZAR AVERIA DEL 1303-5 MACHETE QUEMADO | S22040400026 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 136 | 2022-04-04 | 30600 | keep | 0 | Apr | 2022 | 0.020842 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-04 06:02 | 2022-04-04 08:56 | 870 | 002:54 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO AVE. LOS ROMEROS Y SE CERRO INTERRUPTOR | S22040400026 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 174 | 2022-04-04 | 151380 | keep | 0 | Apr | 2022 | 0.1031 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-04-04 06:04 | 2022-04-04 12:30 | 130 | 006:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | R22040400020 | New_Event | Wire Down | Include | Include | Equipment | 386 | 2022-04-04 | 50180 | keep | 0 | Apr | 2022 | 0.034177 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
ARECIBO | 2022-04-04 06:35 | 2022-04-04 16:18 | 30 | 009:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22040400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 583 | 2022-04-04 | 17490 | keep | 0 | Apr | 2022 | 0.011912 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-04 07:44 | 2022-04-04 17:36 | 1 | 009:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN RISER IGUANA CRUZO LINEAS | A22040400011 | New_Event |  |  | Include | Wildlife | 592 | 2022-04-04 | 592 | keep | 0 | Apr | 2022 | 0.00040321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-04 08:06 | 2022-04-04 11:10 | 20 | 003:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE | S22040400106 | New_Event |  |  | Include | Wildlife | 184 | 2022-04-04 | 3680 | keep | 0 | Apr | 2022 | 0.0025064 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-04-04 08:10 | 2022-04-04 08:11 | 778 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040400185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 778 | keep | 0 | Apr | 2022 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2022-04-04 08:10 | 2022-04-04 08:11 | 113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040400185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 113 | keep | 0 | Apr | 2022 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
CANOVANAS | 2022-04-04 08:20 | 2022-04-04 14:00 | 1 | 005:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 15 EN BANCO DE TRANSFORMADORES CRURCE POR RATA | R22040400037 | New_Event |  |  | Include | Wildlife | 340 | 2022-04-04 | 340 | keep | 0 | Apr | 2022 | 0.00023157 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-04 08:40 | 2022-04-04 18:40 | 100 | 010:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22040400025 | New_Event | Bad Weather | Include | Include | Weather | 600 | 2022-04-04 | 60000 | keep | 0 | Apr | 2022 | 0.040866 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-04 08:51 | 2022-04-04 10:53 | 20 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN RISER AVE CRUZO RISER | M22040400026 | New_Event |  |  | Include | Wildlife | 122 | 2022-04-04 | 2440 | keep | 0 | Apr | 2022 | 0.0016619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-04-04 08:52 | 2022-04-04 18:48 | 40 | 009:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22040400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 596 | 2022-04-04 | 23840 | keep | 0 | Apr | 2022 | 0.016237 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-04-04 08:55 | 2022-04-04 10:02 | 20 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR AVE | P22040400200 | New_Event |  |  | Include | Wildlife | 67 | 2022-04-04 | 1340 | keep | 0 | Apr | 2022 | 0.00091267 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-04-04 09:07 | 2022-04-04 13:00 | 35 | 003:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L AVE | B22040400018 | New_Event |  |  | Include | Wildlife | 233 | 2022-04-04 | 8155 | keep | 0 | Apr | 2022 | 0.0055543 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-04-04 09:09 | 2022-04-04 12:30 | 20 | 003:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5KVA POR 37.5KVA | B22040400018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 201 | 2022-04-04 | 4020 | keep | 0 | Apr | 2022 | 0.002738 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-04-04 09:32 | 2022-04-04 11:28 | 6 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C22040400044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-04-04 | 696 | keep | 0 | Apr | 2022 | 0.00047404 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-04 09:35 | 2022-04-04 15:55 | 10 | 006:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | M22040400038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 380 | 2022-04-04 | 3800 | keep | 0 | Apr | 2022 | 0.0025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-04 09:39 | 2022-04-04 11:32 | 4 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO CAUSA | C22040400031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2022-04-04 | 452 | keep | 0 | Apr | 2022 | 0.00030786 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-04-04 10:04 | 2022-04-04 12:35 | 3 | 002:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO ABIERTO | C22040400033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 151 | 2022-04-04 | 453 | keep | 0 | Apr | 2022 | 0.00030854 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-04-04 10:25 | 2022-04-04 17:34 | 50 | 007:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L LEVANTO CONDUCTOR | C22040400035 | New_Event | Wire Down | Include | Include | Equipment | 429 | 2022-04-04 | 21450 | keep | 0 | Apr | 2022 | 0.014609 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-04-04 10:28 | 2022-04-04 13:32 | 1 | 003:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M22040400044 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2022-04-04 | 184 | keep | 0 | Apr | 2022 | 0.00012532 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-04 10:34 | 2022-04-04 11:30 | 14 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE DESCRUZO SECUNDARIA | C22040400038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2022-04-04 | 784 | keep | 0 | Apr | 2022 | 0.00053398 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2022-04-04 10:39 | 2022-04-04 12:10 | 60 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DEL LINEA NO CAUSA | C22040400039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2022-04-04 | 5460 | keep | 0 | Apr | 2022 | 0.0037188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-04-04 10:43 | 2022-04-04 12:13 | 16 | 001:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA A 2,4KV POR UNO DE LA MISMA CAPACIDAD | P22040400247 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2022-04-04 | 1440 | keep | 0 | Apr | 2022 | 0.00098078 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2022-04-04 11:10 | 2022-04-04 13:18 | 220 | 002:08 | P | NO SE REPORTO CAUSA | 2 X100 EN CORTE DE LINEA NO CAUSA | C22040400044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2022-04-04 | 28160 | keep | 0 | Apr | 2022 | 0.01918 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2022-04-04 11:18 | 2022-04-04 13:55 | 1 | 002:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN CORTE DE LINEA. SE REEMPLAZO PORTAFUSIBLE QUEMADO Y SE REALIZO DESGANCHE | S22040400149 | New_Event | Cutout Failure | Include | Include | Equipment | 157 | 2022-04-04 | 157 | keep | 0 | Apr | 2022 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-04 11:26 | 2022-04-04 14:23 | 105 | 002:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22040400032 | New_Event | Wire Down | Include | Include | Equipment | 177 | 2022-04-04 | 18585 | keep | 0 | Apr | 2022 | 0.012658 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
PONCE | 2022-04-04 11:31 | 2022-04-04 12:11 | 109 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA QUEMADA | P22040400264 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2022-04-04 | 4360 | keep | 0 | Apr | 2022 | 0.0029696 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
BAYAMON | 2022-04-04 11:45 | 2022-04-04 14:42 | 100 | 002:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN RISER Y 1 X 80 EN C/L CAUSA AVE | B22040400033 | New_Event |  |  | Include | Wildlife | 177 | 2022-04-04 | 17700 | keep | 0 | Apr | 2022 | 0.012055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-04 12:03 | 2022-04-04 14:05 | 50 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | R22040400051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-04-04 | 6100 | keep | 0 | Apr | 2022 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-04 12:18 | 2022-04-04 14:44 | 134 | 002:26 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R22040400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2022-04-04 | 19564 | keep | 0 | Apr | 2022 | 0.013325 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
MAYAGÃœEZ | 2022-04-04 12:19 | 2022-04-04 12:52 | 1268 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22040400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2022-04-04 | 41844 | keep | 0 | Apr | 2022 | 0.0285 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2022-04-04 12:19 | 2022-04-04 12:52 | 2064 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22040400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2022-04-04 | 68112 | keep | 0 | Apr | 2022 | 0.046391 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2022-04-04 12:19 | 2022-04-04 12:52 | 3036 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22040400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2022-04-04 | 100188 | keep | 0 | Apr | 2022 | 0.068238 | 0.0020678 | Sustained | FALSE | FALSE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2022-04-04 12:19 | 2022-04-04 12:52 | 2952 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22040400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2022-04-04 | 97416 | keep | 0 | Apr | 2022 | 0.06635 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
BAYAMON | 2022-04-04 12:22 | 2022-04-04 19:02 | 50 | 006:40 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGACHE | S22040400160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2022-04-04 | 20000 | keep | 0 | Apr | 2022 | 0.013622 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-04 12:25 | 2022-04-04 19:13 | 15 | 006:48 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M22040400069 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 408 | 2022-04-04 | 6120 | keep | 0 | Apr | 2022 | 0.0041683 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-04-04 12:52 | 2022-04-04 15:20 | 10 | 002:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ROTA | M22040400101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 148 | 2022-04-04 | 1480 | keep | 0 | Apr | 2022 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-04 12:58 | 2022-04-04 12:59 | 1681 | 000:01 | T | DESGANCHE | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO SU CARGA POR 1303-4 | S22040400166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-04 | 1681 | keep | 0 | Apr | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-04 12:58 | 2022-04-04 12:59 | 1598 | 000:01 | T | DESGANCHE | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO SU CARGA POR 1303-4 | S22040400166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-04 | 1598 | keep | 0 | Apr | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-04-04 13:00 | 2022-04-04 13:58 | 1681 | 000:58 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-1 ATRAVES DEL INTERRUPTOR 1303-04. SE SECCIONALIZO EN CAMINO LUIS VIGOREAUX Y SE CERRO POR SCADA | S22040400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-04-04 | 97498 | keep | 0 | Apr | 2022 | 0.066405 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-04 13:00 | 2022-04-04 13:58 | 1598 | 000:58 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1346-06 ATRAVES DEL INTERRUPTOR 1303-04. SE SECCIONALIZO AVERIA POR DESGANCHE DEL ALIMENATDOR 1303-01 Y SE CERRO POR SCADA | S22040400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-04-04 | 92684 | keep | 0 | Apr | 2022 | 0.063127 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
MAYAGÃœEZ | 2022-04-04 13:19 | 2022-04-04 13:20 | 1268 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22040400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-04 | 1268 | keep | 0 | Apr | 2022 | 0.00086363 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-04 13:19 | 2022-04-04 13:20 | 2064 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22040400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-04 | 2064 | keep | 0 | Apr | 2022 | 0.0014058 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-04 13:19 | 2022-04-04 13:20 | 3036 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22040400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-04 | 3036 | keep | 0 | Apr | 2022 | 0.0020678 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-04 13:19 | 2022-04-04 13:20 | 2952 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22040400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-04 | 2952 | keep | 0 | Apr | 2022 | 0.0020106 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-04 13:25 | 2022-04-04 13:26 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 959 | keep | 0 | Apr | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
MAYAGÃœEZ | 2022-04-04 13:29 | 2022-04-04 17:50 | 200 | 004:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M22040400115 | New_Event | Cutout Failure | Include | Include | Equipment | 261 | 2022-04-04 | 52200 | keep | 0 | Apr | 2022 | 0.035553 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-04-04 13:32 | 2022-04-04 13:54 | 1268 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 SE PASO LA CARGA A LINEA 1200 | M22040400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2022-04-04 | 27896 | keep | 0 | Apr | 2022 | 0.019 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2022-04-04 13:32 | 2022-04-04 13:54 | 2064 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 SE PASO LA CARGA A LINEA 1200 | M22040400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2022-04-04 | 45408 | keep | 0 | Apr | 2022 | 0.030927 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2022-04-04 13:32 | 2022-04-04 13:54 | 3036 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 SE PASO LA CARGA A LINEA 1200 | M22040400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2022-04-04 | 66792 | keep | 0 | Apr | 2022 | 0.045492 | 0.0020678 | Sustained | FALSE | FALSE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2022-04-04 13:32 | 2022-04-04 13:54 | 2952 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 SE PASO LA CARGA A LINEA 1200 | M22040400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2022-04-04 | 64944 | keep | 0 | Apr | 2022 | 0.044233 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
BAYAMON | 2022-04-04 13:37 | 2022-04-04 17:26 | 20 | 003:49 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B22040400042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-04-04 | 4580 | keep | 0 | Apr | 2022 | 0.0031194 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-04-04 13:43 | 2022-04-04 14:59 | 10 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R22040400067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2022-04-04 | 760 | keep | 0 | Apr | 2022 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-04 13:58 | 2022-04-04 15:03 | 84 | 001:05 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON LOS MACHETES | S22040400239 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 65 | 2022-04-04 | 5460 | keep | 0 | Apr | 2022 | 0.0037188 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-04 14:00 | 2022-04-04 14:35 | 50 | 000:35 | P | DESGANCHE | 1 X 65 EN C/L | C22040400079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2022-04-04 | 1750 | keep | 0 | Apr | 2022 | 0.0011919 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-04 14:18 | 2022-04-04 15:59 | 100 | 001:41 | P | DESGANCHE | 2 X 80 EN C/L | C22040400083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-04-04 | 10100 | keep | 0 | Apr | 2022 | 0.0068791 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-04-04 14:24 | 2022-04-04 14:44 | 20 | 000:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | P22040400169 | New_Event | Cutout Failure | Include | Include | Equipment | 20 | 2022-04-04 | 400 | keep | 0 | Apr | 2022 | 0.00027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-04 14:27 | 2022-04-04 15:43 | 1 | 001:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER MAL TIEMPO VIENTOS FUERTES | A22040400051 | New_Event | Bad Weather | Include | Include | Weather | 76 | 2022-04-04 | 76 | keep | 0 | Apr | 2022 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-04 14:36 | 2022-04-04 17:55 | 64 | 003:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 100 AMP. CRUCE POR IGUANA | R22040400070 | New_Event |  |  | Include | Wildlife | 199 | 2022-04-04 | 12736 | keep | 0 | Apr | 2022 | 0.0086744 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
BAYAMON | 2022-04-04 14:40 | 2022-04-04 14:41 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22040400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 959 | keep | 0 | Apr | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
GUAYAMA | 2022-04-04 14:57 | 2022-04-04 16:51 | 25 | 001:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22040400282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-04-04 | 2850 | keep | 0 | Apr | 2022 | 0.0019411 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-04-04 15:02 | 2022-04-04 18:03 | 1 | 003:01 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 20A NO CAUSA | C2204040090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-04-04 | 181 | keep | 0 | Apr | 2022 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-04 15:03 | 2022-04-04 21:20 | 25 | 006:17 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22040400239 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 377 | 2022-04-04 | 9425 | keep | 0 | Apr | 2022 | 0.0064193 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-04-04 15:08 | 2022-04-04 19:02 | 50 | 003:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-04-04 | 11700 | keep | 0 | Apr | 2022 | 0.0079688 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-04 15:23 | 2022-04-04 15:24 | 3432 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR A TRAVES DE LA PORTATIL 22. 20% DE SU CARGA POR EL 1303-02 | S22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 3432 | keep | 0 | Apr | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
UTUADO | 2022-04-04 15:38 | 2022-04-04 16:50 | 30 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040400056 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2022-04-04 | 2160 | keep | 0 | Apr | 2022 | 0.0014712 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-04 15:40 | 2022-04-04 15:41 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22040400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 959 | keep | 0 | Apr | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
SAN JUAN | 2022-04-04 16:00 | 2022-04-05 14:00 | 10 | 022:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN TRANSFORMADOR Y SE REPARO BAJANTE NEUTRAL | S22040400245 | New_Event | Wire Down | Include | Include | Equipment | 1320 | 2022-04-04 | 13200 | keep | 0 | Apr | 2022 | 0.0089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-04 16:00 | 2022-04-04 17:20 | 4 | 001:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN RISER | S22040400250 | New_Event | Wire Down | Include | Include | Equipment | 80 | 2022-04-04 | 320 | keep | 0 | Apr | 2022 | 0.00021795 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-04 16:01 | 2022-04-04 19:27 | 100 | 003:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 80 EN CORTE DE LINEA | S22040400242 | New_Event | Cutout Failure | Include | Include | Equipment | 206 | 2022-04-04 | 20600 | keep | 0 | Apr | 2022 | 0.014031 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-04 16:03 | 2022-04-05 10:39 | 1 | 018:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22040400244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1116 | 2022-04-04 | 1116 | keep | 0 | Apr | 2022 | 0.0007601 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-04 16:03 | 2022-04-04 17:45 | 3 | 001:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO CONEXIONES SECUNDARIAS | A22040400058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 102 | 2022-04-04 | 306 | keep | 0 | Apr | 2022 | 0.00020842 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-04-04 16:30 | 2022-04-04 16:45 | 50 | 000:15 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22040400288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 15 | 2022-04-04 | 750 | keep | 0 | Apr | 2022 | 0.00051082 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-04-04 16:37 | 2022-04-04 19:55 | 400 | 003:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE CERRO PUENTE PRIMARIO | P22040400289 | New_Event | Wire Down | Include | Include | Equipment | 198 | 2022-04-04 | 79200 | keep | 0 | Apr | 2022 | 0.053943 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-04-04 16:50 | 2022-04-04 16:51 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22040400257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 3718 | keep | 0 | Apr | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-04-04 16:57 | 2022-04-05 11:05 | 75 | 018:08 | P | DESGANCHE | 1 X 65 EN RISER Y 2 X 50 EN OTRO RISER | S22040400261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1088 | 2022-04-04 | 81600 | keep | 0 | Apr | 2022 | 0.055577 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-04-04 16:59 | 2022-04-05 09:48 | 306 | 016:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22040400098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1009 | 2022-04-04 | 308754 | keep | 0 | Apr | 2022 | 0.21029 | 0.00020842 | Sustained | FALSE | FALSE | Not_TMED_Event | 306
ARECIBO | 2022-04-04 17:12 | 2022-04-04 17:13 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CANOVANAS | 2022-04-04 17:14 | 2022-04-04 17:15 | 1257 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 60% DE LA CARGA POR EL 2302-03 Y 10% POR EL 2302-01 EN SERVICIO | R22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 1257 | keep | 0 | Apr | 2022 | 0.00085614 | 0.00085614 | Momentary | FALSE | FALSE | Not_TMED_Event | 1257
CANOVANAS | 2022-04-04 17:14 | 2022-04-04 17:15 | 2079 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 60% DE LA CARGA POR EL 2402-02 EN SERVICIO | R22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 2079 | keep | 0 | Apr | 2022 | 0.001416 | 0.001416 | Momentary | FALSE | FALSE | Not_TMED_Event | 2079
CANOVANAS | 2022-04-04 17:14 | 2022-04-04 17:15 | 2675 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 2402-02 EN SERVICIO | R22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 2675 | keep | 0 | Apr | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2022-04-04 17:17 | 2022-04-04 19:19 | 8 | 002:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | R22040400080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-04-04 | 976 | keep | 0 | Apr | 2022 | 0.00066475 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-04-04 17:17 | 2022-04-04 18:49 | 30 | 001:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22040400302 | New_Event |  |  | Include | Wildlife | 92 | 2022-04-04 | 2760 | keep | 0 | Apr | 2022 | 0.0018798 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-04 17:33 | 2022-04-04 17:34 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1801-02 | B22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 1983 | keep | 0 | Apr | 2022 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-04-04 17:33 | 2022-04-04 17:34 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1711-04 | B22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 186 | keep | 0 | Apr | 2022 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
ARECIBO | 2022-04-04 17:40 | 2022-04-04 17:42 | 3654 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CERRADO POR SCADA | A22040400061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-04 | 7308 | keep | 0 | Apr | 2022 | 0.0049774 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
CAGUAS | 2022-04-04 17:48 | 2022-04-05 08:46 | 2 | 014:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR PALOMA | C22040400107 | New_Event |  |  | Include | Wildlife | 898 | 2022-04-04 | 1796 | keep | 0 | Apr | 2022 | 0.0012232 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-04-04 18:06 | 2022-04-04 20:22 | 135 | 002:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | R22040400092 | New_Event | Cutout Failure | Include | Include | Equipment | 136 | 2022-04-04 | 18360 | keep | 0 | Apr | 2022 | 0.012505 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
CAGUAS | 2022-04-04 18:25 | 2022-04-04 19:19 | 1 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN RISER CRUCE X AVE | C22040400116 | New_Event |  |  | Include | Wildlife | 54 | 2022-04-04 | 54 | keep | 0 | Apr | 2022 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-04 18:39 | 2022-04-05 01:44 | 250 | 007:05 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | M22040400209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2022-04-04 | 106250 | keep | 0 | Apr | 2022 | 0.072366 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-04-04 19:13 | 2022-04-04 21:22 | 200 | 002:09 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22040400330 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-04-04 | 25800 | keep | 0 | Apr | 2022 | 0.017572 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-04-04 19:20 | 2022-04-04 21:45 | 4381 | 002:25 | T | LINEA DE TRANSMISION 38KV | SE REMOVIO OVERHEAD PARTIDO LINEA 1200 QUE CAYO ENCIMA DE ALIMENTADOR Y SE CERRO INTERRUPTOR MANUAL RTU FUERA DE SERVICIO POR REEMPLAZO | M22040400235 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 145 | 2022-04-04 | 635245 | keep | 0 | Apr | 2022 | 0.43266 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
CAGUAS | 2022-04-04 19:30 | 2022-04-06 13:47 | 10 | 042:17 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA | C22040400125 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2537 | 2022-04-04 | 25370 | keep | 0 | Apr | 2022 | 0.017279 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-04 19:30 | 2022-04-06 14:49 | 14 | 043:19 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO BAMBUA Y ENREDADERA | C22040400125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2599 | 2022-04-04 | 36386 | keep | 0 | Apr | 2022 | 0.024782 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-04-04 19:37 | 2022-04-05 10:04 | 13 | 014:27 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | S22040400335 | New_Event | Vegetation Contact | Include | Include | Vegetation | 867 | 2022-04-04 | 11271 | keep | 0 | Apr | 2022 | 0.0076766 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2022-04-04 19:55 | 2022-04-04 19:56 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-04 | 1310 | keep | 0 | Apr | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-04-04 20:09 | 2022-04-05 | 80 | 003:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | B22040400068 | New_Event |  |  | Include | Wildlife | 231 | 2022-04-04 | 18480 | keep | 0 | Apr | 2022 | 0.012587 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-04 20:33 | 2022-04-05 00:06 | 30 | 003:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22040400278 | New_Event | Bad Weather | Include | Include | Weather | 213 | 2022-04-04 | 6390 | keep | 0 | Apr | 2022 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-04 21:56 | 2022-04-05 17:35 | 12 | 019:39 | P | NO SE REPORTO CAUSA | 3 X 15 EN TRANSFORMADOR | S22040400356 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1179 | 2022-04-04 | 14148 | keep | 0 | Apr | 2022 | 0.0096361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-04-04 22:34 | 2022-04-05 15:11 | 1 | 016:37 | P | NO SE REPORTO CAUSA | 1 X 25 EN BANCO DE TRANFORMADORES BOMBAS AAA | S22040400359 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 997 | 2022-04-04 | 997 | keep | 0 | Apr | 2022 | 0.00067905 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-04 23:10 | 2022-04-05 12:34 | 150 | 013:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22040400305 | New_Event | Cutout Failure | Include | Include | Equipment | 804 | 2022-04-04 | 120600 | keep | 0 | Apr | 2022 | 0.08214 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-04-05 02:46 | 2022-04-05 02:47 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22040500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 2999 | keep | 0 | Apr | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 1339 | keep | 0 | Apr | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 470 | keep | 0 | Apr | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 2483 | keep | 0 | Apr | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 2190 | keep | 0 | Apr | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 3006 | keep | 0 | Apr | 2022 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 179 | keep | 0 | Apr | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 107 | keep | 0 | Apr | 2022 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 1666 | keep | 0 | Apr | 2022 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 4387 | keep | 0 | Apr | 2022 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 3147 | keep | 0 | Apr | 2022 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-04-05 02:54 | 2022-04-05 02:55 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22040500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 4304 | keep | 0 | Apr | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
CAGUAS | 2022-04-05 06:23 | 2022-04-05 14:10 | 165 | 007:47 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22040500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 467 | 2022-04-05 | 77055 | keep | 0 | Apr | 2022 | 0.052482 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
FAJARDO | 2022-04-05 06:41 | 2022-04-05 08:42 | 90 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R22040500003 | New_Event |  |  | Include | Wildlife | 121 | 2022-04-05 | 10890 | keep | 0 | Apr | 2022 | 0.0074171 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2022-04-05 06:48 | 2022-04-05 19:15 | 10 | 012:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A22040500002 | New_Event | Wire Down | Include | Include | Equipment | 747 | 2022-04-05 | 7470 | keep | 0 | Apr | 2022 | 0.0050878 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-05 07:06 | 2022-04-05 10:40 | 20 | 003:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA AVE CRUZO LINEAS | A22040500003 | New_Event |  |  | Include | Wildlife | 214 | 2022-04-05 | 4280 | keep | 0 | Apr | 2022 | 0.0029151 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-04-05 07:08 | 2022-04-05 15:18 | 8 | 008:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22040500009 | New_Event | Bad Weather | Include | Include | Weather | 490 | 2022-04-05 | 3920 | keep | 0 | Apr | 2022 | 0.0026699 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-05 07:23 | 2022-04-05 07:24 | 553 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO 40% DE SU CARGA POR 1204-1 QUE A SU VEZ A TRAVES PORTATIL#22 | S22040500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-05 | 553 | keep | 0 | Apr | 2022 | 0.00037665 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2022-04-05 07:38 | 2022-04-05 07:39 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 3597 | keep | 0 | Apr | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
SAN JUAN | 2022-04-05 07:39 | 2022-04-05 07:40 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 2203 | keep | 0 | Apr | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
UTUADO | 2022-04-05 07:42 | 2022-04-05 10:46 | 70 | 003:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22040500007 | New_Event | Bad Weather | Include | Include | Weather | 184 | 2022-04-05 | 12880 | keep | 0 | Apr | 2022 | 0.0087725 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-04-05 07:46 | 2022-04-05 07:47 | 6197 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22040500018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 6197 | keep | 0 | Apr | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
MAYAGÃœEZ | 2022-04-05 07:52 | 2022-04-05 11:57 | 50 | 004:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-04-05 | 12250 | keep | 0 | Apr | 2022 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-05 07:54 | 2022-04-05 08:46 | 5 | 000:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN CORTE DE LINEA VECINO CORTANDO ARBOL LO DEJO CAER SOBRE LA LINEA | C22040500013 | New_Event |  |  | Include | Wildlife | 52 | 2022-04-05 | 260 | keep | 0 | Apr | 2022 | 0.00017708 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-04-05 07:58 | 2022-04-05 14:30 | 36 | 006:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22040500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-04-05 | 14112 | keep | 0 | Apr | 2022 | 0.0096116 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2022-04-05 08:03 | 2022-04-05 15:00 | 12 | 006:57 | P | DESGANCHE | SE RETIRO BAMBUS SOBRE LAS LINEAS | M22040500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 417 | 2022-04-05 | 5004 | keep | 0 | Apr | 2022 | 0.0034082 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-05 08:05 | 2022-04-05 08:06 | 3871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 3871 | keep | 0 | Apr | 2022 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
HUMACAO | 2022-04-05 08:16 | 2022-04-05 09:53 | 3 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN BANCO DE TRANSFORMADORES SE RETIRO NIDO DE PAJARO | C22040500020 | New_Event |  |  | Include | Wildlife | 97 | 2022-04-05 | 291 | keep | 0 | Apr | 2022 | 0.0001982 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-04-05 08:19 | 2022-04-05 08:20 | 761 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1421-1 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22040500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 761 | keep | 0 | Apr | 2022 | 0.00051831 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2022-04-05 08:19 | 2022-04-05 08:20 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1310-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22040500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 1498 | keep | 0 | Apr | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
CAGUAS | 2022-04-05 08:23 | 2022-04-05 09:49 | 86 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 Y 1 X 30 EN CORTES DE LINEA CRUCE POR AVE | C22040500021 | New_Event |  |  | Include | Wildlife | 86 | 2022-04-05 | 7396 | keep | 0 | Apr | 2022 | 0.0050374 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
BAYAMON | 2022-04-05 08:27 | 2022-04-05 13:45 | 70 | 005:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 00 EN CORTE DE LINEA TRONCAL Y 1 X 80 EN CORTE DE LINEA RAMAL. SE REEMPLAZO CAJA AVERIADA | S22040500018 | New_Event | Cutout Failure | Include | Include | Equipment | 318 | 2022-04-05 | 22260 | keep | 0 | Apr | 2022 | 0.015161 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2022-04-05 08:40 | 2022-04-05 12:15 | 1 | 003:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | RISER AVERIADO POR ACCIDENTE | R22040500006 | New_Event |  |  | Include | Wildlife | 215 | 2022-04-05 | 215 | keep | 0 | Apr | 2022 | 0.00014644 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-05 08:54 | 2022-04-05 11:00 | 5 | 002:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN CORTE DE LINEA VECINO CORTANDO ARBOL LO DEJO CAER SOBRE LINEA | C22040500013 | Partial_restoration |  |  | Include | Wildlife | 126 | 2022-04-05 | 630 | keep | 0 | Apr | 2022 | 0.00042909 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-05 08:55 | 2022-04-05 18:33 | 150 | 009:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040500024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 578 | 2022-04-05 | 86700 | keep | 0 | Apr | 2022 | 0.059051 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-04-05 08:57 | 2022-04-05 11:09 | 90 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R22040500003 | Partial_restoration |  |  | Include | Wildlife | 132 | 2022-04-05 | 11880 | keep | 0 | Apr | 2022 | 0.0080914 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-05 08:58 | 2022-04-05 10:30 | 2 | 001:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR PALOMA | C22040400107 | New_Event |  |  | Include | Wildlife | 92 | 2022-04-05 | 184 | keep | 0 | Apr | 2022 | 0.00012532 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-04-05 09:08 | 2022-04-05 09:32 | 100 | 000:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | R22040500035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-04-05 | 2400 | keep | 0 | Apr | 2022 | 0.0016346 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-04-05 09:10 | 2022-04-05 13:32 | 12 | 004:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | R22040500035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 262 | 2022-04-05 | 3144 | keep | 0 | Apr | 2022 | 0.0021414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-05 09:11 | 2022-04-05 11:33 | 250 | 002:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L SE REMPLAZARON 2 CAJAS PRIMARIAS Y SE REALIZO DESGANCHE | B22040500020 | New_Event | Cutout Failure | Include | Include | Equipment | 142 | 2022-04-05 | 35500 | keep | 0 | Apr | 2022 | 0.024179 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2022-04-05 09:12 | 2022-04-05 09:45 | 16 | 000:33 | P | SOBRECARGA | 1 X 20 EN CORTE DE LINEA ESO INFORMO PERSONAL DE CAMPO | M22040500015 | New_Event | Trip Due To Overload | Include | Include | Other | 33 | 2022-04-05 | 528 | keep | 0 | Apr | 2022 | 0.00035962 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-04-05 09:13 | 2022-04-05 09:14 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 1746 | keep | 0 | Apr | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2022-04-05 09:14 | 2022-04-05 15:40 | 100 | 006:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L Y 1 X 80 EN SU - 12 | B22040500104 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 386 | 2022-04-05 | 38600 | keep | 0 | Apr | 2022 | 0.02629 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-05 09:15 | 2022-04-05 11:39 | 5 | 002:24 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R22040500039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 144 | 2022-04-05 | 720 | keep | 0 | Apr | 2022 | 0.00049039 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-04-05 09:17 | 2022-04-05 09:18 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22040500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 1342 | keep | 0 | Apr | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
AGUADILLA | 2022-04-05 09:35 | 2022-04-05 09:52 | 1 | 000:17 | P | DESGANCHE | 1 X 40 EN RISER SE NECESITA DESGANCHE | M22040500050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2022-04-05 | 17 | keep | 0 | Apr | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-05 09:39 | 2022-04-05 12:13 | 50 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22040500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-04-05 | 7700 | keep | 0 | Apr | 2022 | 0.0052444 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-04-05 09:41 | 2022-04-06 08:32 | 8 | 022:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS EN BAJANTES DE XMR | B22040500065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1371 | 2022-04-05 | 10968 | keep | 0 | Apr | 2022 | 0.0074703 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-04-05 10:00 | 2022-04-05 11:50 | 150 | 001:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040500059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-04-05 | 16500 | keep | 0 | Apr | 2022 | 0.011238 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-04-05 10:07 | 2022-04-05 10:08 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 3046 | keep | 0 | Apr | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
MAYAGÃœEZ | 2022-04-05 10:35 | 2022-04-05 12:21 | 15 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M2204050072 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2022-04-05 | 1590 | keep | 0 | Apr | 2022 | 0.0010829 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-05 10:38 | 2022-04-05 14:04 | 1 | 003:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22040500076 | New_Event | Bad Weather | Include | Include | Weather | 206 | 2022-04-05 | 206 | keep | 0 | Apr | 2022 | 0.00014031 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-05 10:39 | 2022-04-05 10:40 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1206-3 | S22040500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 10211 | keep | 0 | Apr | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-04-05 10:39 | 2022-04-05 10:40 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1204-05 | S22040500059 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 4133 | keep | 0 | Apr | 2022 | 0.002815 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-05 10:40 | 2022-04-05 14:30 | 1 | 003:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22040400244 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 230 | 2022-04-05 | 230 | keep | 0 | Apr | 2022 | 0.00015665 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-05 10:40 | 2022-04-05 13:18 | 80 | 002:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | R22040500045 | New_Event |  |  | Include | Wildlife | 158 | 2022-04-05 | 12640 | keep | 0 | Apr | 2022 | 0.008609 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-05 10:46 | 2022-04-05 10:48 | 1106 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1529-15 LLEVANDO 60% CARGA 1346-02 SE CERRO POR SCADA | S22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-05 | 2212 | keep | 0 | Apr | 2022 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
BAYAMON | 2022-04-05 10:46 | 2022-04-05 10:48 | 1802 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR 1529-12 LLEVANDO 60% DEL 1346-2 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22040500000 | New_Event |  |  | Include | Wildlife | 2 | 2022-04-05 | 3604 | keep | 0 | Apr | 2022 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-04-05 10:46 | 2022-04-05 10:47 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040500047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 2179 | keep | 0 | Apr | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
UTUADO | 2022-04-05 10:47 | 2022-04-05 13:29 | 1 | 002:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22040500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-04-05 | 162 | keep | 0 | Apr | 2022 | 0.00011034 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-05 10:48 | 2022-04-05 15:00 | 65 | 004:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA Y SE RETIRO IGUANA | S22040500110 | 1st_after_momentary |  |  | Include | Wildlife | 252 | 2022-04-05 | 16380 | keep | 0 | Apr | 2022 | 0.011156 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-04-05 10:48 | 2022-04-05 17:40 | 50 | 006:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | M22040500078 | New_Event | Wire Down | Include | Include | Equipment | 412 | 2022-04-05 | 20600 | keep | 0 | Apr | 2022 | 0.014031 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-05 10:54 | 2022-04-05 11:35 | 4 | 000:41 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR PARA REMPLAZO DE PEDESTAL | B22040500074 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 41 | 2022-04-05 | 164 | keep | 0 | Apr | 2022 | 0.0001117 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-04-05 11:05 | 2022-04-06 12:43 | 12 | 025:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR BARRA PEDESTAL | S22040400146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1538 | 2022-04-05 | 18456 | keep | 0 | Apr | 2022 | 0.01257 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-04-05 11:18 | 2022-04-05 11:38 | 90 | 000:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R22040500003 | New_Event |  |  | Include | Wildlife | 20 | 2022-04-05 | 1800 | keep | 0 | Apr | 2022 | 0.001226 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-04-05 11:19 | 2022-04-05 11:21 | 614 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-05 | 1228 | keep | 0 | Apr | 2022 | 0.00083639 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
CAGUAS | 2022-04-05 11:20 | 2022-04-05 11:26 | 2859 | 000:06 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA ABRIR MACHETE AVERIADO | C22040500127 | New_Event | Switch Failure | Include | Include | Equipment | 6 | 2022-04-05 | 17154 | keep | 0 | Apr | 2022 | 0.011684 | 0.0019473 | Sustained | FALSE | FALSE | Not_TMED_Event | 2859
BAYAMON | 2022-04-05 11:25 | 2022-04-05 11:34 | 1 | 000:09 | P | NO SE REPORTO CAUSA | 3 X 10 FUSIBLES TIPO NX EN BANCO DE TRANSFORMADORES | S22040500088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-04-05 | 9 | keep | 0 | Apr | 2022 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-05 11:38 | 2022-04-05 14:22 | 16 | 002:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE ELIMINO TOMA CRUZADA | A22040500066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 164 | 2022-04-05 | 2624 | keep | 0 | Apr | 2022 | 0.0017872 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-04-05 11:44 | 2022-04-05 23:00 | 15 | 011:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22040500104 | New_Event | Bad Weather | Include | Include | Weather | 676 | 2022-04-05 | 10140 | keep | 0 | Apr | 2022 | 0.0069063 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-05 11:52 | 2022-04-05 15:02 | 28 | 003:10 | P | DESGANCHE | 1 X 40 EN C/L | R22040500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-04-05 | 5320 | keep | 0 | Apr | 2022 | 0.0036234 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
ARECIBO | 2022-04-05 11:52 | 2022-04-05 16:00 | 15 | 004:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A22040500070 | New_Event | Wire Down | Include | Include | Equipment | 248 | 2022-04-05 | 3720 | keep | 0 | Apr | 2022 | 0.0025337 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-04-05 11:54 | 2022-04-05 19:31 | 100 | 007:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22040500110 | New_Event | Bad Weather | Include | Include | Weather | 457 | 2022-04-05 | 45700 | keep | 0 | Apr | 2022 | 0.031126 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-04-05 11:54 | 2022-04-05 15:40 | 5 | 003:46 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15 KVA X 25 KVA DEFECTUOSO Y 200 PIES DE SECUNDARIA | C22040500072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 226 | 2022-04-05 | 1130 | keep | 0 | Apr | 2022 | 0.00076964 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-04-05 12:00 | 2022-04-06 18:12 | 1 | 030:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE DEL WR 6090720 DEL DIA 5 CLIENTE SIN SERVICIO NO LE CREARON EVENTO CREARON WR | P22040600141 | New_Event |  |  | Include | Wildlife | 1812 | 2022-04-05 | 1812 | keep | 0 | Apr | 2022 | 0.0012341 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-05 12:01 | 2022-04-05 12:02 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 3114 | keep | 0 | Apr | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
ARECIBO | 2022-04-05 12:09 | 2022-04-05 14:08 | 1 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER UL2 NO NOTIFICO CAUSA | A22040500072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2022-04-05 | 119 | keep | 0 | Apr | 2022 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-05 12:11 | 2022-04-05 14:19 | 1 | 002:08 | P | OTRAS CAUSAS | 1 SMU 20 DE 20 AMP. CONTAMINACION EN TRANSCLOSURE SE ORIENTO AL CLIENTE | C22040500153 | New_Event | Other Causes | Include | Include | Other | 128 | 2022-04-05 | 128 | keep | 0 | Apr | 2022 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-05 12:13 | 2022-04-05 12:14 | 614 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22040500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 614 | keep | 0 | Apr | 2022 | 0.00041819 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
VEGA BAJA | 2022-04-05 12:16 | 2022-04-06 09:30 | 1 | 021:14 | P | NO SE REPORTO CAUSA | 2 X 20 EN MONTURA | B22040500102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1274 | 2022-04-05 | 1274 | keep | 0 | Apr | 2022 | 0.00086772 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-05 12:32 | 2022-04-05 12:43 | 110 | 000:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE ABRIO MACHETE Y SE SECCIONALIZO A TRAVES GOI PARA REMPLAZAR AISLADOR | S22040500092 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 11 | 2022-04-05 | 1210 | keep | 0 | Apr | 2022 | 0.00082413 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2022-04-05 12:35 | 2022-04-05 15:02 | 1 | 002:27 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO RAMA EN CONTACTO CON LA CAJA | C22040500161 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 147 | 2022-04-05 | 147 | keep | 0 | Apr | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-05 12:35 | 2022-04-05 21:42 | 15 | 009:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A22040500074 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 547 | 2022-04-05 | 8205 | keep | 0 | Apr | 2022 | 0.0055884 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-05 12:36 | 2022-04-06 19:15 | 30 | 030:39 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO DE RISER @ T-1 | B22040500105 | New_Event | UG Cable Fault | Include | Include | Equipment | 1839 | 2022-04-05 | 55170 | keep | 0 | Apr | 2022 | 0.037576 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-05 12:43 | 2022-04-05 14:12 | 110 | 001:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y SE RESTABLECIO SERVICIO | S22040500092 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 89 | 2022-04-05 | 9790 | keep | 0 | Apr | 2022 | 0.0066679 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-05 13:11 | 2022-04-05 14:34 | 214 | 001:23 | P | HERRAJE ROTO O PODRIDO | 1 X 80 EN CORTE DE LINEA CRUCETA DEFECTUOSA | C22040500166 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 83 | 2022-04-05 | 17762 | keep | 0 | Apr | 2022 | 0.012098 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
UTUADO | 2022-04-05 13:13 | 2022-04-05 13:14 | 934 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36400 | A22040500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 934 | keep | 0 | Apr | 2022 | 0.00063614 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-04-05 13:13 | 2022-04-05 13:14 | 4 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36400 | A22040500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-04-05 13:13 | 2022-04-05 13:14 | 1479 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36400 | A22040500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-05 | 1479 | keep | 0 | Apr | 2022 | 0.0010073 | 0.0010073 | Momentary | FALSE | FALSE | Not_TMED_Event | 1479
HUMACAO | 2022-04-05 13:17 | 2022-04-05 13:19 | 2873 | 000:02 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA DEJAR MACHETE DEFECTUOSO COMO N/O SE TRABAJO CON GOI CG-220405-01 | C22040500167 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-04-05 | 5746 | keep | 0 | Apr | 2022 | 0.0039136 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
ARECIBO | 2022-04-05 13:26 | 2022-04-05 15:28 | 1 | 002:02 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR CLIENTE REPARO AVERIA INTERNA | A22040500077 | New_Event | Other Causes | Include | Include | Other | 122 | 2022-04-05 | 122 | keep | 0 | Apr | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-05 13:36 | 2022-04-05 14:20 | 10 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22040500079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2022-04-05 | 440 | keep | 0 | Apr | 2022 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-04-05 13:39 | 2022-04-05 15:24 | 70 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22040500079 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2022-04-05 | 7350 | keep | 0 | Apr | 2022 | 0.0050061 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-04-05 13:41 | 2022-04-05 13:42 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 959 | keep | 0 | Apr | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
UTUADO | 2022-04-05 13:42 | 2022-04-05 17:06 | 20 | 003:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A22040500080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-04-05 | 4080 | keep | 0 | Apr | 2022 | 0.0027789 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-04-05 13:45 | 2022-04-06 16:53 | 150 | 027:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | M22040500134 | New_Event | Wire Down | Include | Include | Equipment | 1628 | 2022-04-05 | 244200 | keep | 0 | Apr | 2022 | 0.16632 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-04-05 13:59 | 2022-04-05 18:46 | 120 | 004:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22040500122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2022-04-05 | 34440 | keep | 0 | Apr | 2022 | 0.023457 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-04-05 14:00 | 2022-04-05 14:03 | 225 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-05 | 675 | keep | 0 | Apr | 2022 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-05 14:00 | 2022-04-05 14:03 | 870 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-05 | 2610 | keep | 0 | Apr | 2022 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-04-05 14:03 | 2022-04-05 15:20 | 10 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR Y SE REPARO NEUTRAL EN BAJANTE SECUNDARIO | S22040500245 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2022-04-05 | 770 | keep | 0 | Apr | 2022 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-05 14:14 | 2022-04-06 11:23 | 1 | 021:09 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 15KVA X 15KVA | A22040500084 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1269 | 2022-04-05 | 1269 | keep | 0 | Apr | 2022 | 0.00086431 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-05 14:32 | 2022-04-05 16:10 | 60 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22040500151 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2022-04-05 | 5880 | keep | 0 | Apr | 2022 | 0.0040048 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-04-05 14:35 | 2022-04-05 15:50 | 200 | 001:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 65 EN C/LÂ´S CRUCE X AVE | R22040500099 | New_Event |  |  | Include | Wildlife | 75 | 2022-04-05 | 15000 | keep | 0 | Apr | 2022 | 0.010216 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-04-05 14:52 | 2022-04-05 20:52 | 150 | 006:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y CRUCETA | B22040500129 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2022-04-05 | 54000 | keep | 0 | Apr | 2022 | 0.036779 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-04-05 15:12 | 2022-04-05 15:13 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22040500159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 390 | keep | 0 | Apr | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
ARECIBO | 2022-04-05 15:15 | 2022-04-05 15:59 | 15 | 000:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON "BUSHING" QUEMADO | A22040500091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 44 | 2022-04-05 | 660 | keep | 0 | Apr | 2022 | 0.00044952 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-05 15:31 | 2022-04-05 21:33 | 50 | 006:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | M22040500163 | New_Event |  |  | Include | Wildlife | 362 | 2022-04-05 | 18100 | keep | 0 | Apr | 2022 | 0.012328 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-05 15:31 | 2022-04-05 21:39 | 25 | 006:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22040500096 | New_Event | Bad Weather | Include | Include | Weather | 368 | 2022-04-05 | 9200 | keep | 0 | Apr | 2022 | 0.0062661 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-04-05 15:36 | 2022-04-05 18:05 | 1 | 002:29 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINDA | C22040500188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-04-05 | 149 | keep | 0 | Apr | 2022 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-05 15:52 | 2022-04-06 06:21 | 10 | 014:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ABIERTA CRUZADA | M22040500165 | New_Event | Secondary Wire Down | Include | Include | Equipment | 869 | 2022-04-05 | 8690 | keep | 0 | Apr | 2022 | 0.0059187 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-05 15:58 | 2022-04-05 17:51 | 38 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO PITIRRE DE PARARRAYO | C22040500190 | New_Event |  |  | Include | Wildlife | 113 | 2022-04-05 | 4294 | keep | 0 | Apr | 2022 | 0.0029246 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
PONCE | 2022-04-05 16:04 | 2022-04-05 16:05 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040500095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 2163 | keep | 0 | Apr | 2022 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
BAYAMON | 2022-04-05 16:07 | 2022-04-05 22:35 | 46 | 006:28 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | B22040500146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 388 | 2022-04-05 | 17848 | keep | 0 | Apr | 2022 | 0.012156 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
SAN JUAN | 2022-04-05 16:10 | 2022-04-05 17:10 | 8 | 001:00 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | R22040500115 | New_Event | Service Transformer Failure | Include | Include | Equipment | 60 | 2022-04-05 | 480 | keep | 0 | Apr | 2022 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-05 16:15 | 2022-04-05 20:28 | 100 | 004:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22040500147 | New_Event | Wire Down | Include | Include | Equipment | 253 | 2022-04-05 | 25300 | keep | 0 | Apr | 2022 | 0.017232 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-04-05 16:16 | 2022-04-05 17:17 | 12 | 001:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR PAJARO CRUZO FASE | P22040500098 | New_Event |  |  | Include | Wildlife | 61 | 2022-04-05 | 732 | keep | 0 | Apr | 2022 | 0.00049856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-05 16:25 | 2022-04-05 18:14 | 1 | 001:49 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA BAMBUA CRUZO LA LINEA | C22040500195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-04-05 | 109 | keep | 0 | Apr | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-05 16:27 | 2022-04-06 13:28 | 50 | 021:01 | P | NO SE REPORTO CAUSA | 3 X 80 EN CORTE DE LINEA | S22040500139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1261 | 2022-04-05 | 63050 | keep | 0 | Apr | 2022 | 0.042943 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-05 16:37 | 2022-04-05 19:01 | 150 | 002:24 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22040500102 | New_Event | Bad Weather | Include | Include | Weather | 144 | 2022-04-05 | 21600 | keep | 0 | Apr | 2022 | 0.014712 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-04-05 16:48 | 2022-04-05 17:15 | 5 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO BANCO DE TRANSFORMADORES PARA REEMPLAZAR CONECTORES Y NEUTRAL SECUNDARIO | C22040500197 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2022-04-05 | 135 | keep | 0 | Apr | 2022 | 9.1948e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-04-05 17:00 | 2022-04-05 17:59 | 1 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO ZAFADO EN TRANSFORMADOR | A22040500106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-04-05 | 59 | keep | 0 | Apr | 2022 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-05 17:40 | 2022-04-06 11:25 | 20 | 017:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22040500201 | New_Event |  |  | Include | Wildlife | 1065 | 2022-04-05 | 21300 | keep | 0 | Apr | 2022 | 0.014507 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-04-05 17:50 | 2022-04-05 18:44 | 50 | 000:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22040500202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-04-05 | 2700 | keep | 0 | Apr | 2022 | 0.001839 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-05 17:59 | 2022-04-05 18:07 | 2 | 000:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C22040500204 | New_Event |  |  | Include | Wildlife | 8 | 2022-04-05 | 16 | keep | 0 | Apr | 2022 | 1.0898e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-04-05 18:00 | 2022-04-05 19:47 | 6 | 001:47 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE PARTIDO | A22040500107 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 107 | 2022-04-05 | 642 | keep | 0 | Apr | 2022 | 0.00043726 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-04-05 18:01 | 2022-04-05 19:53 | 15 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO NEUTRAL PARTIDO | A22040500118 | New_Event | Wire Down | Include | Include | Equipment | 112 | 2022-04-05 | 1680 | keep | 0 | Apr | 2022 | 0.0011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-05 18:03 | 2022-04-05 18:04 | 50 | 000:01 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN C/LÂ´S | R22040500116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-05 | 50 | keep | 0 | Apr | 2022 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-05 18:05 | 2022-04-05 21:11 | 3006 | 003:06 | S | LINEA DE TRANSMISION 38KV | SE DISPARO LINEA 17800 Y SUBESTACION SE FUE A LOCKOUT SE VERIFICO EN SUBESTACION Y SE ENCONTRO ANIMAL QUEMADO BUSHING DEL GCB 0010. SE TRABAJO SITUACION Y SE CERRO INTERRUPTOR POR SCADA. | M22040500210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2022-04-05 | 559116 | keep | 0 | Apr | 2022 | 0.38081 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-04-05 18:05 | 2022-04-05 21:11 | 179 | 003:06 | S | LINEA DE TRANSMISION 38KV | SE DISPARO LINEA 17800 Y SUBESTACION SE FUE A LOCKOUT SE VERIFICO EN SUBESTACION Y SE ENCONTRO ANIMAL QUEMADO (GATO EN GCB 0010). SE TRABAJO SITUACION Y SE CERRO INTERRUPTOR POR SCADA. | M22040500210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2022-04-05 | 33294 | keep | 0 | Apr | 2022 | 0.022676 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
SAN JUAN | 2022-04-05 18:06 | 2022-04-06 13:11 | 11 | 019:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE DE LINEA A CAJA | S22040500157 | New_Event | Wire Down | Include | Include | Equipment | 1145 | 2022-04-05 | 12595 | keep | 0 | Apr | 2022 | 0.0085784 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2022-04-05 18:07 | 2022-04-05 18:09 | 1310 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-05 | 2620 | keep | 0 | Apr | 2022 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2022-04-05 18:15 | 2022-04-05 21:50 | 20 | 003:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A22040500134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-04-05 | 4300 | keep | 0 | Apr | 2022 | 0.0029287 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-04-05 18:24 | 2022-04-05 20:26 | 8 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE CAJA A XMR NO FUNDIO | R22040500125 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2022-04-05 | 976 | keep | 0 | Apr | 2022 | 0.00066475 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-05 18:39 | 2022-04-05 19:43 | 50 | 001:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA SE ENCONTRO AVE | B22040500174 | New_Event |  |  | Include | Wildlife | 64 | 2022-04-05 | 3200 | keep | 0 | Apr | 2022 | 0.0021795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-05 18:40 | 2022-04-05 20:03 | 343 | 001:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO LINEA A CAJA EN CORTE DE LINEA | B22040500175 | New_Event | Wire Down | Include | Include | Equipment | 83 | 2022-04-05 | 28469 | keep | 0 | Apr | 2022 | 0.01939 | 0.00023362 | Sustained | FALSE | FALSE | Not_TMED_Event | 343
FAJARDO | 2022-04-05 18:49 | 2022-04-05 21:00 | 40 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | R22040500127 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2022-04-05 | 5240 | keep | 0 | Apr | 2022 | 0.0035689 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-05 19:10 | 2022-04-05 19:20 | 13 | 000:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A22040500095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 10 | 2022-04-05 | 130 | keep | 0 | Apr | 2022 | 8.8542e-05 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2022-04-05 19:12 | 2022-04-05 19:13 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-03 QUE A SU VEZ LLEVA LA CARGA DEL 1346-04 | S22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 726 | keep | 0 | Apr | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-04-05 19:12 | 2022-04-05 19:13 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-03 QUE A SU VEZ LLEVA LA CARGA DEL 1346-04 | S22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-05 | 3932 | keep | 0 | Apr | 2022 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
BAYAMON | 2022-04-05 19:16 | 2022-04-06 19:15 | 6 | 023:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA TRANSFORMADOR | S22040500173 | New_Event | Wire Down | Include | Include | Equipment | 1439 | 2022-04-05 | 8634 | keep | 0 | Apr | 2022 | 0.0058806 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-04-05 19:25 | 2022-04-05 22:33 | 85 | 003:08 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22040500215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2022-04-05 | 15980 | keep | 0 | Apr | 2022 | 0.010884 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2022-04-05 19:46 | 2022-04-06 04:34 | 193 | 008:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO DE LINEA A RISER | S22040500187 | New_Event | Wire Down | Include | Include | Equipment | 528 | 2022-04-05 | 101904 | keep | 0 | Apr | 2022 | 0.069406 | 0.00013145 | Sustained | FALSE | FALSE | Not_TMED_Event | 193
AGUADILLA | 2022-04-05 19:55 | 2022-04-05 22:40 | 25 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO VIENTOS FUERTES | M22040500288 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2022-04-05 | 4125 | keep | 0 | Apr | 2022 | 0.0028095 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-04-05 20:42 | 2022-04-06 14:41 | 5 | 017:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO | S22040500196 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1079 | 2022-04-05 | 5395 | keep | 0 | Apr | 2022 | 0.0036745 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-04-05 20:48 | 2022-04-06 07:03 | 30 | 010:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE POR RAMA | C22040500222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 615 | 2022-04-05 | 18450 | keep | 0 | Apr | 2022 | 0.012566 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-05 21:11 | 2022-04-05 21:45 | 1 | 000:34 | P | OTRAS CAUSAS | 2 X 20 EN SUB PRIVADA | B22040500199 | New_Event | Other Causes | Include | Include | Other | 34 | 2022-04-05 | 34 | keep | 0 | Apr | 2022 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-05 23:23 | 2022-04-06 18:36 | 6 | 019:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO 2 X 10 EN TRANSFORMADOR | S22040500211 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1153 | 2022-04-05 | 6918 | keep | 0 | Apr | 2022 | 0.0047118 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-06 00:20 | 2022-04-06 09:45 | 13 | 009:25 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22040600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 565 | 2022-04-06 | 7345 | keep | 0 | Apr | 2022 | 0.0050026 | 8.8542e-06 | Sustained | FALSE | FALSE | TMED_Event | 13
ARECIBO | 2022-04-06 00:41 | 2022-04-06 09:48 | 15 | 009:07 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22040600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 547 | 2022-04-06 | 8205 | keep | 0 | Apr | 2022 | 0.0055884 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
BAYAMON | 2022-04-06 00:43 | 2022-04-06 01:58 | 9 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22040600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-04-06 | 675 | keep | 0 | Apr | 2022 | 0.00045974 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
BAYAMON | 2022-04-06 01:59 | 2022-04-06 02:00 | 4089 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 4089 | keep | 0 | Apr | 2022 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | TMED_Event | 4089
CANOVANAS | 2022-04-06 03:33 | 2022-04-06 03:34 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 4188 | keep | 0 | Apr | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | TMED_Event | 4188
BAYAMON | 2022-04-06 03:47 | 2022-04-06 08:33 | 15 | 004:46 | P | CABLE SOTERRADO AVERIADO | 1X30 DE RISER @ T-2 AVERIA NUEVA: T-2 @ T-3, AVERIA VIEJA: SU-2 @ T-4, FUERA DE SERVICIO: T-3 & T-4, SE LE REFIRIO AL DISTRITO | B22040600005 | New_Event | UG Cable Fault | Include | Include | Equipment | 286 | 2022-04-06 | 4290 | keep | 0 | Apr | 2022 | 0.0029219 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
SAN JUAN | 2022-04-06 04:01 | 2022-04-06 04:02 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-01 LLEVA CARGA 1206-02 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | TMED_Event | 300
SAN JUAN | 2022-04-06 04:01 | 2022-04-06 04:02 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-01 LLEVA CARGA 1206-02 | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | TMED_Event | 733
BAYAMON | 2022-04-06 04:10 | 2022-04-06 06:41 | 65 | 002:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE LEVANTO PRIMARIA | S22040600001 | New_Event | Wire Down | Include | Include | Equipment | 151 | 2022-04-06 | 9815 | keep | 0 | Apr | 2022 | 0.006685 | 4.4271e-05 | Sustained | FALSE | FALSE | TMED_Event | 65
CAGUAS | 2022-04-06 05:08 | 2022-04-06 10:30 | 148 | 005:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22040600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2022-04-06 | 47656 | keep | 0 | Apr | 2022 | 0.032458 | 0.0001008 | Sustained | FALSE | FALSE | TMED_Event | 148
HUMACAO | 2022-04-06 06:14 | 2022-04-06 06:15 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 3701 | keep | 0 | Apr | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | TMED_Event | 3701
BAYAMON | 2022-04-06 06:16 | 2022-04-06 10:14 | 70 | 003:58 | P | DESGANCHE | 1X50 EN C/L SE RETIRO RAMA DEL 13KV | B22040600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2022-04-06 | 16660 | keep | 0 | Apr | 2022 | 0.011347 | 4.7677e-05 | Sustained | FALSE | FALSE | TMED_Event | 70
HUMACAO | 2022-04-06 06:17 | 2022-04-06 11:13 | 30 | 004:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22040600016 | New_Event | Bad Weather | Include | Include | Weather | 296 | 2022-04-06 | 8880 | keep | 0 | Apr | 2022 | 0.0060481 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
SAN JUAN | 2022-04-06 06:35 | 2022-04-06 15:25 | 2 | 008:50 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S22040600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 530 | 2022-04-06 | 1060 | keep | 0 | Apr | 2022 | 0.00072196 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
HUMACAO | 2022-04-06 06:42 | 2022-04-06 09:02 | 273 | 002:20 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA NO CAUSA | C22040600017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2022-04-06 | 38220 | keep | 0 | Apr | 2022 | 0.026031 | 0.00018594 | Sustained | FALSE | FALSE | TMED_Event | 273
CANOVANAS | 2022-04-06 06:53 | 2022-04-06 06:54 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1894 | keep | 0 | Apr | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | TMED_Event | 1894
CANOVANAS | 2022-04-06 06:53 | 2022-04-06 06:54 | 4154 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 4154 | keep | 0 | Apr | 2022 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | TMED_Event | 4154
AGUADILLA | 2022-04-06 06:53 | 2022-04-06 17:15 | 2 | 010:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE CORTE DE LINEA | M22040600012 | New_Event | Cutout Failure | Include | Include | Equipment | 622 | 2022-04-06 | 1244 | keep | 0 | Apr | 2022 | 0.00084728 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
CANOVANAS | 2022-04-06 06:54 | 2022-04-06 10:11 | 20 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO CAUSA | R22040600005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 197 | 2022-04-06 | 3940 | keep | 0 | Apr | 2022 | 0.0026835 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
SAN JUAN | 2022-04-06 06:56 | 2022-04-06 06:57 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 2179 | keep | 0 | Apr | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | TMED_Event | 2179
SAN JUAN | 2022-04-06 07:16 | 2022-04-06 07:17 | 137 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3100 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-06 | 137 | keep | 0 | Apr | 2022 | 9.331e-05 | 9.331e-05 | Momentary | FALSE | FALSE | TMED_Event | 137
SAN JUAN | 2022-04-06 07:16 | 2022-04-06 07:17 | 457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3100 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-06 | 457 | keep | 0 | Apr | 2022 | 0.00031126 | 0.00031126 | Momentary | FALSE | FALSE | TMED_Event | 457
SAN JUAN | 2022-04-06 07:16 | 2022-04-06 07:17 | 1225 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3100 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-06 | 1225 | keep | 0 | Apr | 2022 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | TMED_Event | 1225
SAN JUAN | 2022-04-06 07:16 | 2022-04-06 07:17 | 1452 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3100 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-06 | 1452 | keep | 0 | Apr | 2022 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | TMED_Event | 1452
SAN JUAN | 2022-04-06 07:16 | 2022-04-06 07:17 | 616 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3100 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-06 | 616 | keep | 0 | Apr | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | TMED_Event | 616
SAN JUAN | 2022-04-06 07:16 | 2022-04-06 07:17 | 3432 | 000:01 | P | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3100 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-06 | 3432 | keep | 0 | Apr | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | TMED_Event | 3432
SAN JUAN | 2022-04-06 07:16 | 2022-04-06 07:17 | 552 | 000:01 | P | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3100. 60% DE SU CARGA POR EL 1206-04 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-06 | 552 | keep | 0 | Apr | 2022 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | TMED_Event | 552
SAN JUAN | 2022-04-06 07:16 | 2022-04-06 07:17 | 27 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3100 SU CARGA POR 1203-1 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-06 | 27 | keep | 0 | Apr | 2022 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | TMED_Event | 27
PONCE | 2022-04-06 07:25 | 2022-04-06 12:10 | 10 | 004:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR POR AVE | P22040600007 | New_Event |  |  | Include | Wildlife | 285 | 2022-04-06 | 2850 | keep | 0 | Apr | 2022 | 0.0019411 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
MAYAGÃœEZ | 2022-04-06 07:26 | 2022-04-06 14:30 | 140 | 007:04 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE | M22040500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 424 | 2022-04-06 | 59360 | keep | 0 | Apr | 2022 | 0.04043 | 9.5353e-05 | Sustained | FALSE | FALSE | TMED_Event | 140
SAN JUAN | 2022-04-06 07:35 | 2022-04-06 07:36 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1206-01 LLEVA CARGA 1206-02 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S22040600022 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | TMED_Event | 300
SAN JUAN | 2022-04-06 07:35 | 2022-04-06 07:36 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1206-01 | S22040600022 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | TMED_Event | 733
ARECIBO | 2022-04-06 07:35 | 2022-04-06 10:53 | 100 | 003:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REEMPLAZARON AISLADORES | A22040600003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 198 | 2022-04-06 | 19800 | keep | 0 | Apr | 2022 | 0.013486 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
BAYAMON | 2022-04-06 07:47 | 2022-04-06 14:00 | 1 | 006:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B22040600008 | New_Event | Wire Down | Include | Include | Equipment | 373 | 2022-04-06 | 373 | keep | 0 | Apr | 2022 | 0.00025405 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
MAYAGÃœEZ | 2022-04-06 07:52 | 2022-04-06 12:45 | 80 | 004:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22040500019 | New_Event | Bad Weather | Include | Include | Weather | 293 | 2022-04-06 | 23440 | keep | 0 | Apr | 2022 | 0.015965 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
CAGUAS | 2022-04-06 07:56 | 2022-04-06 07:57 | 853 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22040600032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 853 | keep | 0 | Apr | 2022 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | TMED_Event | 853
MAYAGÃœEZ | 2022-04-06 08:07 | 2022-04-06 14:34 | 1 | 006:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22040600021 | New_Event | Bad Weather | Include | Include | Weather | 387 | 2022-04-06 | 387 | keep | 0 | Apr | 2022 | 0.00026358 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CAGUAS | 2022-04-06 08:08 | 2022-04-06 08:09 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22040600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 4634 | keep | 0 | Apr | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | TMED_Event | 4634
VEGA BAJA | 2022-04-06 08:09 | 2022-04-06 09:14 | 1 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2X10 EN MONTURA DE XMERS (POR AVE EN LA LINEA) | B22040600010 | New_Event |  |  | Include | Wildlife | 65 | 2022-04-06 | 65 | keep | 0 | Apr | 2022 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
MAYAGÃœEZ | 2022-04-06 08:16 | 2022-04-06 20:43 | 60 | 012:27 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR | M22040600022 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 747 | 2022-04-06 | 44820 | keep | 0 | Apr | 2022 | 0.030527 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
SAN JUAN | 2022-04-06 08:25 | 2022-04-06 08:26 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22040600037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 3957 | keep | 0 | Apr | 2022 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | TMED_Event | 3957
HUMACAO | 2022-04-06 08:32 | 2022-04-06 08:33 | 327 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 327 | keep | 0 | Apr | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | TMED_Event | 327
SAN JUAN | 2022-04-06 08:33 | 2022-04-06 13:17 | 110 | 004:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-8C NO CAUSA | R22040600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 284 | 2022-04-06 | 31240 | keep | 0 | Apr | 2022 | 0.021277 | 7.492e-05 | Sustained | FALSE | FALSE | TMED_Event | 110
BAYAMON | 2022-04-06 08:33 | 2022-04-06 08:34 | 5961 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | B22040600000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-04-06 | 5961 | keep | 0 | Apr | 2022 | 0.00406 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2022-04-06 08:34 | 2022-04-06 10:50 | 15 | 002:16 | P | CABLE SOTERRADO AVERIADO | 1X30 DE RISER @ T-2 AVERIA NUEVA: T-2 @ T-3, AVERIA VIEJA: SU-2 @ T-4, FUERA DE SERVICIO: T-3 & T-4, SE LE REFIRIO AL DISTRITO | B22040600005 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 136 | 2022-04-06 | 2040 | keep | 0 | Apr | 2022 | 0.0013894 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
MAYAGÃœEZ | 2022-04-06 08:40 | 2022-04-06 08:41 | 4641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22040600029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 4641 | keep | 0 | Apr | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | TMED_Event | 4641
SAN JUAN | 2022-04-06 08:48 | 2022-04-06 08:51 | 828 | 000:03 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 60% POR 1206-4 | S22040600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-06 | 2484 | keep | 0 | Apr | 2022 | 0.0016918 | 0.00056395 | Momentary | FALSE | FALSE | TMED_Event | 828
SAN JUAN | 2022-04-06 08:48 | 2022-04-06 08:51 | 1977 | 000:03 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 40% POR 1206-4 | S22040600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-06 | 5931 | keep | 0 | Apr | 2022 | 0.0040396 | 0.0013465 | Momentary | FALSE | FALSE | TMED_Event | 1977
SAN JUAN | 2022-04-06 08:48 | 2022-04-06 08:51 | 8711 | 000:03 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 PARTE POR 1206-3 | S22040600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-06 | 26133 | keep | 0 | Apr | 2022 | 0.017799 | 0.005933 | Momentary | FALSE | FALSE | TMED_Event | 8711
SAN JUAN | 2022-04-06 08:48 | 2022-04-06 08:51 | 300 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 INTERRUPTOR 1206-01 LLEVA CARGA 1206-02 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S22040600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-06 | 900 | keep | 0 | Apr | 2022 | 0.00061299 | 0.00020433 | Momentary | FALSE | FALSE | TMED_Event | 300
SAN JUAN | 2022-04-06 08:48 | 2022-04-06 08:51 | 733 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 SU CARGA POR 1206-1 | S22040600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-06 | 2199 | keep | 0 | Apr | 2022 | 0.0014977 | 0.00049924 | Momentary | FALSE | FALSE | TMED_Event | 733
SAN JUAN | 2022-04-06 08:48 | 2022-04-06 08:51 | 4133 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 LLEVA PARTE 1204-5 | S22040600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-06 | 12399 | keep | 0 | Apr | 2022 | 0.0084449 | 0.002815 | Momentary | FALSE | FALSE | TMED_Event | 4133
SAN JUAN | 2022-04-06 08:48 | 2022-04-06 08:51 | 1799 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S22040600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-06 | 5397 | keep | 0 | Apr | 2022 | 0.0036759 | 0.0012253 | Momentary | FALSE | FALSE | TMED_Event | 1799
SAN JUAN | 2022-04-06 08:48 | 2022-04-06 08:51 | 487 | 000:03 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 20% POR 1206-4 | S22040600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-06 | 1461 | keep | 0 | Apr | 2022 | 0.00099508 | 0.00033169 | Momentary | FALSE | FALSE | TMED_Event | 487
GUAYAMA | 2022-04-06 08:55 | 2022-04-06 08:56 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | TMED_Event | 4132
GUAYAMA | 2022-04-06 08:55 | 2022-04-06 08:56 | 4279 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | TMED_Event | 4279
GUAYAMA | 2022-04-06 08:55 | 2022-04-06 08:56 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | TMED_Event | 464
GUAYAMA | 2022-04-06 09:03 | 2022-04-06 09:04 | 4132 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P22040600015 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-06 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | TMED_Event | 4132
GUAYAMA | 2022-04-06 09:03 | 2022-04-06 09:04 | 4279 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040600015 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | TMED_Event | 4279
GUAYAMA | 2022-04-06 09:03 | 2022-04-06 09:04 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040600015 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | TMED_Event | 464
GUAYAMA | 2022-04-06 09:04 | 2022-04-06 13:06 | 15 | 004:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZARON BAJANTES PRIMARIOS DE RISER | P22040600012 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 242 | 2022-04-06 | 3630 | keep | 0 | Apr | 2022 | 0.0024724 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
CAGUAS | 2022-04-06 09:07 | 2022-04-06 09:08 | 2457 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22040600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 2457 | keep | 0 | Apr | 2022 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | TMED_Event | 2457
BARRANQUITAS | 2022-04-06 09:20 | 2022-04-06 10:19 | 14 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO Y 40 PIES DE SECUNDARIA | C22040600047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-04-06 | 826 | keep | 0 | Apr | 2022 | 0.00056258 | 9.5353e-06 | Sustained | FALSE | FALSE | TMED_Event | 14
VEGA BAJA | 2022-04-06 09:31 | 2022-04-06 11:38 | 80 | 002:07 | P | DESGANCHE | 1X100 EN C/L SE REALIZO DESGANCHE | B22040600013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-04-06 | 10160 | keep | 0 | Apr | 2022 | 0.0069199 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
CANOVANAS | 2022-04-06 09:46 | 2022-04-06 10:15 | 4085 | 000:29 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF 2402-03 LLEVANDO LA CARGA DEL 2404-06 SE VERIFICO PERSONAL TRABAJANDO, NO SE REPORTO CAUSA. | R22040600014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-04-06 | 118465 | keep | 0 | Apr | 2022 | 0.080686 | 0.0027823 | Sustained | FALSE | FALSE | TMED_Event | 4085
CANOVANAS | 2022-04-06 09:46 | 2022-04-06 10:15 | 7621 | 000:29 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF 2402-03 LLEVANDO LA CARGA DEL 2404-06 SE VERIFICO PERSONAL TRABAJANDO, NO SE REPORTO CAUSA. | R22040600014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-04-06 | 221009 | keep | 0 | Apr | 2022 | 0.15053 | 0.0051906 | Sustained | FALSE | FALSE | TMED_Event | 7621
ARECIBO | 2022-04-06 09:57 | 2022-04-06 13:03 | 160 | 003:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | A22040600014 | New_Event | Cutout Failure | Include | Include | Equipment | 186 | 2022-04-06 | 29760 | keep | 0 | Apr | 2022 | 0.020269 | 0.00010898 | Sustained | FALSE | FALSE | TMED_Event | 160
FAJARDO | 2022-04-06 10:09 | 2022-04-06 11:24 | 1463 | 001:15 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR NEUTRAL PRIMARIO ROTO EN SALIDA DEL 2001-04. SW- SJ-220406-50 | R22040600060 | New_Event | Wire Down | Include | Include | Equipment | 75 | 2022-04-06 | 109725 | keep | 0 | Apr | 2022 | 0.074733 | 0.00099644 | Sustained | FALSE | FALSE | TMED_Event | 1463
HUMACAO | 2022-04-06 10:10 | 2022-04-06 12:59 | 46 | 002:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22040600055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-04-06 | 7774 | keep | 0 | Apr | 2022 | 0.0052948 | 3.133e-05 | Sustained | FALSE | FALSE | TMED_Event | 46
CAGUAS | 2022-04-06 10:16 | 2022-04-06 12:25 | 50 | 002:09 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22040600056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-04-06 | 6450 | keep | 0 | Apr | 2022 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2022-04-06 10:22 | 2022-04-06 16:15 | 40 | 005:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA | B22040600017 | New_Event | Cutout Failure | Include | Include | Equipment | 353 | 2022-04-06 | 14120 | keep | 0 | Apr | 2022 | 0.0096171 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
SAN JUAN | 2022-04-06 10:25 | 2022-04-06 10:26 | 1825 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22040600091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1825 | keep | 0 | Apr | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | TMED_Event | 1825
FAJARDO | 2022-04-06 10:27 | 2022-04-06 13:19 | 10 | 002:52 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R22040600074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-04-06 | 1720 | keep | 0 | Apr | 2022 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
FAJARDO | 2022-04-06 10:40 | 2022-04-06 10:41 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040600076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1830 | keep | 0 | Apr | 2022 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | TMED_Event | 1830
CANOVANAS | 2022-04-06 10:45 | 2022-04-06 10:46 | 3838 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 3838 | keep | 0 | Apr | 2022 | 0.002614 | 0.002614 | Momentary | FALSE | FALSE | TMED_Event | 3838
BAYAMON | 2022-04-06 10:50 | 2022-04-06 20:43 | 20 | 009:53 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO | B22040600005 | New_Event | UG Cable Fault | Include | Include | Equipment | 593 | 2022-04-06 | 11860 | keep | 0 | Apr | 2022 | 0.0080778 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
FAJARDO | 2022-04-06 10:51 | 2022-04-06 10:52 | 710 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2201-04 LLEVANDO LA CARGA DEL 2201-03 | R22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 710 | keep | 0 | Apr | 2022 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | TMED_Event | 710
FAJARDO | 2022-04-06 10:51 | 2022-04-06 10:52 | 1197 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2201-04 LLEVANDO LA CARGA DEL 2201-03 | R22040600079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1197 | keep | 0 | Apr | 2022 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | TMED_Event | 1197
FAJARDO | 2022-04-06 10:54 | 2022-04-06 10:55 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040600081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1234 | keep | 0 | Apr | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | TMED_Event | 1234
CAGUAS | 2022-04-06 10:55 | 2022-04-06 12:28 | 26 | 001:33 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTES DE LINEA | C22040600064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-04-06 | 2418 | keep | 0 | Apr | 2022 | 0.0016469 | 1.7708e-05 | Sustained | FALSE | FALSE | TMED_Event | 26
BAYAMON | 2022-04-06 11:01 | 2022-04-06 14:32 | 300 | 003:31 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUAS | S22040600111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-04-06 | 63300 | keep | 0 | Apr | 2022 | 0.043113 | 0.00020433 | Sustained | FALSE | FALSE | TMED_Event | 300
SAN JUAN | 2022-04-06 11:05 | 2022-04-06 11:08 | 225 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-5 SE PROBO QUEDO EN SERVICIO | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-06 | 675 | keep | 0 | Apr | 2022 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | TMED_Event | 225
SAN JUAN | 2022-04-06 11:05 | 2022-04-06 11:08 | 870 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1303-4 SE PROBO QUEDO EN SERVICIO | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-06 | 2610 | keep | 0 | Apr | 2022 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | TMED_Event | 870
CAGUAS | 2022-04-06 11:05 | 2022-04-06 15:24 | 8 | 004:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22040600066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 259 | 2022-04-06 | 2072 | keep | 0 | Apr | 2022 | 0.0014112 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
FAJARDO | 2022-04-06 11:07 | 2022-04-06 13:13 | 10 | 002:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA CRUCE POR AVE | R22040600082 | New_Event |  |  | Include | Wildlife | 126 | 2022-04-06 | 1260 | keep | 0 | Apr | 2022 | 0.00085818 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
HUMACAO | 2022-04-06 11:23 | 2022-04-06 15:06 | 50 | 003:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C22040600072 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 223 | 2022-04-06 | 11150 | keep | 0 | Apr | 2022 | 0.0075942 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2022-04-06 11:36 | 2022-04-06 18:00 | 122 | 006:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22040600139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 384 | 2022-04-06 | 46848 | keep | 0 | Apr | 2022 | 0.031908 | 8.3094e-05 | Sustained | FALSE | FALSE | TMED_Event | 122
VEGA BAJA | 2022-04-06 11:44 | 2022-04-06 15:00 | 50 | 003:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22040600026 | New_Event | Wire Down | Include | Include | Equipment | 196 | 2022-04-06 | 9800 | keep | 0 | Apr | 2022 | 0.0066747 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
CAGUAS | 2022-04-06 11:56 | 2022-04-06 11:57 | 2906 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 2906 | keep | 0 | Apr | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | TMED_Event | 2906
BAYAMON | 2022-04-06 12:10 | 2022-04-06 18:35 | 156 | 006:25 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22040600154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2022-04-06 | 60060 | keep | 0 | Apr | 2022 | 0.040907 | 0.00010625 | Sustained | FALSE | FALSE | TMED_Event | 156
YAUCO | 2022-04-06 12:13 | 2022-04-06 14:45 | 1637 | 002:32 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SE ABRIERON MACHETES EN CARR 368 Y SE REALIZO PRUEBA A INTERRUPTOR QUEDANDO EN SERVICIO | P22040600053 | New_Event |  |  | Include | Wildlife | 152 | 2022-04-06 | 248824 | keep | 0 | Apr | 2022 | 0.16947 | 0.001115 | Sustained | FALSE | FALSE | TMED_Event | 1637
UTUADO | 2022-04-06 12:18 | 2022-04-06 13:31 | 70 | 001:13 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | A22040600027 | New_Event | Bad Weather | Include | Include | Weather | 73 | 2022-04-06 | 5110 | keep | 0 | Apr | 2022 | 0.0034804 | 4.7677e-05 | Sustained | FALSE | FALSE | TMED_Event | 70
SAN JUAN | 2022-04-06 12:23 | 2022-04-06 14:55 | 411 | 002:32 | P | LINEA DE TRANSMISION 38KV | SE PASO 90% AL 1205-02 POR PUENTE ABIERTO EN LINEA 3100 | S22040600158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2022-04-06 | 62472 | keep | 0 | Apr | 2022 | 0.042549 | 0.00027993 | Sustained | FALSE | FALSE | TMED_Event | 411
SAN JUAN | 2022-04-06 12:23 | 2022-04-06 12:28 | 3432 | 000:05 | P | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA A PETICION DARIEN Y FRANCISCO RODRIGUEZ POR PUENTE ABIERTO LINEA 3100, LLAMO JUAN C. OTERO PIDIENDO ENERGIZAR YA QUE TRAMO ABIERTO ESTA CERCA DE LA SUBES. 1201 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-04-06 | 17160 | keep | 0 | Apr | 2022 | 0.011688 | 0.0023375 | Momentary | FALSE | FALSE | TMED_Event | 3432
SAN JUAN | 2022-04-06 12:23 | 2022-04-06 12:28 | 552 | 000:05 | P | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA A PETICION DARIEN Y FRANCISCO RODRIGUEZ POR PUENTE ABIERTO LINEA 3100, LUEGO LLAMO JUAN C. OTERO PIDIENDO ENERGIZAR YA QUE TRAMO ABIERTO ESTA CERCA DE LA SUB 1201. 60% DE SU CARGA POR EL 1206-04 | S22040600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-04-06 | 2760 | keep | 0 | Apr | 2022 | 0.0018798 | 0.00037596 | Momentary | FALSE | FALSE | TMED_Event | 552
SAN JUAN | 2022-04-06 12:24 | 2022-04-06 14:55 | 46 | 002:31 | P | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO PUENTE ABIERTO L-3100 Y SE NORMALIZARON LAS CARGAS | S22040600243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-04-06 | 6946 | keep | 0 | Apr | 2022 | 0.0047309 | 3.133e-05 | Sustained | FALSE | FALSE | TMED_Event | 46
SAN JUAN | 2022-04-06 12:28 | 2022-04-06 14:55 | 28 | 002:27 | P | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO TRAMO PARA CERRAR PUENTE L-3100 Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S22040600243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 147 | 2022-04-06 | 4116 | keep | 0 | Apr | 2022 | 0.0028034 | 1.9071e-05 | Sustained | FALSE | FALSE | TMED_Event | 28
SAN JUAN | 2022-04-06 12:28 | 2022-04-06 13:59 | 109 | 001:31 | P | LINEA DE TRANSMISION 38KV | SE PASO 80% AL 1342-4 CERRANDO N/O FTE. FERRETERIA LA FAMILIA POR AVERIA PUENTE ABIERTO L-3100 | S22040600158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 91 | 2022-04-06 | 9919 | keep | 0 | Apr | 2022 | 0.0067558 | 7.4239e-05 | Sustained | FALSE | FALSE | TMED_Event | 109
CANOVANAS | 2022-04-06 12:30 | 2022-04-06 14:00 | 10 | 001:30 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L NO CAUSA | R22040600090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2022-04-06 | 900 | keep | 0 | Apr | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
MAYAGÃœEZ | 2022-04-06 12:31 | 2022-04-06 12:32 | 528 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22040600108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 528 | keep | 0 | Apr | 2022 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | TMED_Event | 528
ARECIBO | 2022-04-06 12:38 | 2022-04-06 17:00 | 6 | 004:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040600029 | New_Event | Bad Weather | Include | Include | Weather | 262 | 2022-04-06 | 1572 | keep | 0 | Apr | 2022 | 0.0010707 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
SAN JUAN | 2022-04-06 12:41 | 2022-04-06 12:42 | 4481 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO SOLO LLEVA 70% DE SU CARGA EL OTRO 30% POR 1619-02 | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 4481 | keep | 0 | Apr | 2022 | 0.003052 | 0.003052 | Momentary | FALSE | FALSE | TMED_Event | 4481
SAN JUAN | 2022-04-06 12:41 | 2022-04-06 12:42 | 60 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 60 | keep | 0 | Apr | 2022 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | TMED_Event | 60
MAYAGÃœEZ | 2022-04-06 12:43 | 2022-04-08 18:39 | 1617 | 053:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3236 | 2022-04-06 | 5232612 | keep | 0 | Apr | 2022 | 3.5639 | 0.0011013 | Sustained | FALSE | FALSE | TMED_Event | 1617
MAYAGÃœEZ | 2022-04-06 12:43 | 2022-04-08 18:39 | 1017 | 053:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3236 | 2022-04-06 | 3291012 | keep | 0 | Apr | 2022 | 2.2415 | 0.00069267 | Sustained | FALSE | FALSE | TMED_Event | 1017
MAYAGÃœEZ | 2022-04-06 12:43 | 2022-04-08 18:39 | 828 | 053:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3236 | 2022-04-06 | 2679408 | keep | 0 | Apr | 2022 | 1.8249 | 0.00056395 | Sustained | FALSE | FALSE | TMED_Event | 828
SAN JUAN | 2022-04-06 12:54 | 2022-04-06 12:55 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1206-01 LLEVA CARGA 1206-02 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | TMED_Event | 300
SAN JUAN | 2022-04-06 12:54 | 2022-04-06 12:55 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1206-01 | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | TMED_Event | 641
MAYAGÃœEZ | 2022-04-06 13:00 | 2022-04-06 13:01 | 1268 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M12040600116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1268 | keep | 0 | Apr | 2022 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | TMED_Event | 1268
CAGUAS | 2022-04-06 13:08 | 2022-04-06 18:00 | 20 | 004:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR CRUCE POR LAGARTO Y SE REEMPLAZO CAJA PRIMARIA | C22040600093 | New_Event |  |  | Include | Wildlife | 292 | 2022-04-06 | 5840 | keep | 0 | Apr | 2022 | 0.0039776 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
MAYAGÃœEZ | 2022-04-06 13:18 | 2022-04-06 13:19 | 1268 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22040600121 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1268 | keep | 0 | Apr | 2022 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | TMED_Event | 1268
GUAYAMA | 2022-04-06 13:21 | 2022-04-06 13:22 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22040600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1945 | keep | 0 | Apr | 2022 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | TMED_Event | 1945
GUAYAMA | 2022-04-06 13:21 | 2022-04-06 13:22 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 4003-03 | P22040600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 215 | keep | 0 | Apr | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | TMED_Event | 215
BARRANQUITAS | 2022-04-06 13:23 | 2022-04-06 14:05 | 8 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C22040600097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-04-06 | 336 | keep | 0 | Apr | 2022 | 0.00022885 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
ARECIBO | 2022-04-06 13:37 | 2022-04-06 19:13 | 10 | 005:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22040600038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 336 | 2022-04-06 | 3360 | keep | 0 | Apr | 2022 | 0.0022885 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
MAYAGÃœEZ | 2022-04-06 13:45 | 2022-04-06 18:06 | 150 | 004:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1 X 40 EN DIFERENTES CORTES DE LINEA AVE CRUZO FASES | M22040600127 | New_Event |  |  | Include | Wildlife | 261 | 2022-04-06 | 39150 | keep | 0 | Apr | 2022 | 0.026665 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
MAYAGÃœEZ | 2022-04-06 13:45 | 2022-04-06 16:23 | 75 | 002:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22040600036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-04-06 | 11850 | keep | 0 | Apr | 2022 | 0.008071 | 5.1082e-05 | Sustained | FALSE | FALSE | TMED_Event | 75
MAYAGÃœEZ | 2022-04-06 13:48 | 2022-04-06 13:49 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22040600133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 863 | keep | 0 | Apr | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | TMED_Event | 863
SAN JUAN | 2022-04-06 13:57 | 2022-04-06 14:01 | 922 | 000:04 | T | NO SE REPORTO CAUSA | RECERRO UNA VEZ QUEDO ABIERTO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1401-8 | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-06 | 3688 | keep | 0 | Apr | 2022 | 0.0025119 | 0.00062797 | Momentary | FALSE | FALSE | TMED_Event | 922
SAN JUAN | 2022-04-06 13:57 | 2022-04-06 14:01 | 135 | 000:04 | T | NO SE REPORTO CAUSA | RECERRO UNA VEZ QUEDO ABIERTO SE PROBO QUEDO EN SERVICIO LLEVA 1346-5 | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-06 | 540 | keep | 0 | Apr | 2022 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | TMED_Event | 135
CANOVANAS | 2022-04-06 14:01 | 2022-04-06 17:49 | 30 | 003:48 | P | DESGANCHE | 1 X 30 EN C/L | R22040600097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2022-04-06 | 6840 | keep | 0 | Apr | 2022 | 0.0046587 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
GUAYAMA | 2022-04-06 14:10 | 2022-04-06 15:44 | 200 | 001:34 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE EN N/C Y SE CERRO EL MISMO | P22040600093 | New_Event | Switch Failure | Include | Include | Equipment | 94 | 2022-04-06 | 18800 | keep | 0 | Apr | 2022 | 0.012805 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
BAYAMON | 2022-04-06 14:14 | 2022-04-06 16:20 | 50 | 002:06 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | B22040600052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-04-06 | 6300 | keep | 0 | Apr | 2022 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2022-04-06 14:19 | 2022-04-06 18:00 | 50 | 003:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22040600054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-04-06 | 11050 | keep | 0 | Apr | 2022 | 0.0075261 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
GUAYAMA | 2022-04-06 14:30 | 2022-04-06 15:20 | 4 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | P22040600102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-04-06 | 200 | keep | 0 | Apr | 2022 | 0.00013622 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
FAJARDO | 2022-04-06 14:33 | 2022-04-06 16:02 | 40 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN C/L Y 1 X 10 EN XMR CRUCE X CULEBRA | R22040600099 | New_Event |  |  | Include | Wildlife | 89 | 2022-04-06 | 3560 | keep | 0 | Apr | 2022 | 0.0024247 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
ARECIBO | 2022-04-06 14:34 | 2022-04-06 18:07 | 10 | 003:33 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A22040600041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-04-06 | 2130 | keep | 0 | Apr | 2022 | 0.0014507 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
AGUADILLA | 2022-04-06 14:41 | 2022-04-06 14:42 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1047 | keep | 0 | Apr | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | TMED_Event | 1047
YAUCO | 2022-04-06 14:45 | 2022-04-06 16:32 | 982 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | LINEA PRIMARIA CRUZADA POR TENSOR DE POSTE SECUNDARIO SE CORRIGIO CONDICION Y SE CERRO MACHETES | P22040600115 | Partial_restoration |  |  | Include | Wildlife | 107 | 2022-04-06 | 105074 | keep | 0 | Apr | 2022 | 0.071565 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-04-06 14:55 | 2022-04-06 18:22 | 28 | 003:27 | P | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO TRAMO PARA CERRAR PUENTE L-3100 Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S22040600243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 207 | 2022-04-06 | 5796 | keep | 0 | Apr | 2022 | 0.0039476 | 1.9071e-05 | Sustained | FALSE | FALSE | TMED_Event | 28
SAN JUAN | 2022-04-06 14:55 | 2022-04-06 18:22 | 46 | 003:27 | P | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO PUENTE ABIERTO L-3100 Y SE NORMALIZARON LAS CARGAS | S22040600243 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 207 | 2022-04-06 | 9522 | keep | 0 | Apr | 2022 | 0.0064854 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
AGUADILLA | 2022-04-06 15:14 | 2022-04-06 15:15 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 390 | keep | 0 | Apr | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | TMED_Event | 390
SAN JUAN | 2022-04-06 15:19 | 2022-04-06 18:01 | 3432 | 002:42 | P | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA PARA REPARAR PUENTE PRIMARIO L-3100 | S22040600243 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 162 | 2022-04-06 | 555984 | keep | 0 | Apr | 2022 | 0.37868 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-04-06 15:19 | 2022-04-06 18:01 | 552 | 002:42 | P | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA PARA REPARAR PUENTE PRIMARIO L-3100. 60% DE SU CARGA POR EL 1206-04 | S22040600243 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 162 | 2022-04-06 | 89424 | keep | 0 | Apr | 2022 | 0.060906 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
FAJARDO | 2022-04-06 15:23 | 2022-04-06 18:03 | 1 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR Y REPARO SECUNDARIA | R22040600101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2022-04-06 | 160 | keep | 0 | Apr | 2022 | 0.00010898 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CAGUAS | 2022-04-06 15:26 | 2022-04-06 16:18 | 50 | 000:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C22040600185 | New_Event | Bad Weather | Include | Include | Weather | 52 | 2022-04-06 | 2600 | keep | 0 | Apr | 2022 | 0.0017708 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
SAN JUAN | 2022-04-06 15:35 | 2022-04-06 16:59 | 3046 | 001:24 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO EL ALIMENTADOR | R22030600102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-04-06 | 255864 | keep | 0 | Apr | 2022 | 0.17427 | 0.0020746 | Sustained | FALSE | FALSE | TMED_Event | 3046
BAYAMON | 2022-04-06 15:45 | 2022-04-06 18:20 | 40 | 002:35 | P | DESGANCHE | 2 X 100 Y 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22040600258 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-04-06 | 6200 | keep | 0 | Apr | 2022 | 0.0042228 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
BAYAMON | 2022-04-06 16:00 | 2022-04-06 18:00 | 15 | 002:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22040600066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 120 | 2022-04-06 | 1800 | keep | 0 | Apr | 2022 | 0.001226 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
UTUADO | 2022-04-06 16:03 | 2022-04-06 17:47 | 25 | 001:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-04-06 | 2600 | keep | 0 | Apr | 2022 | 0.0017708 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
BARRANQUITAS | 2022-04-06 16:04 | 2022-04-06 19:15 | 161 | 003:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE RETEZO LINEA | C22040600113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-04-06 | 30751 | keep | 0 | Apr | 2022 | 0.020944 | 0.00010966 | Sustained | FALSE | FALSE | TMED_Event | 161
GUAYAMA | 2022-04-06 16:08 | 2022-04-06 17:35 | 12 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22040600134 | New_Event |  |  | Include | Wildlife | 87 | 2022-04-06 | 1044 | keep | 0 | Apr | 2022 | 0.00071106 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
BAYAMON | 2022-04-06 16:12 | 2022-04-06 16:13 | 766 | 000:01 | P | NO SE REPORTO CAUSA | INTERRUPTOR 1909-07 RECERRO LLEVANDO 50% DEL 1709-03 | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 766 | keep | 0 | Apr | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | TMED_Event | 766
BAYAMON | 2022-04-06 16:12 | 2022-04-06 16:13 | 1139 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 50% DEL 1709-03 | S22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 1139 | keep | 0 | Apr | 2022 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | TMED_Event | 1139
ARECIBO | 2022-04-06 16:23 | 2022-04-06 16:25 | 3654 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A22040600052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-06 | 7308 | keep | 0 | Apr | 2022 | 0.0049774 | 0.0024887 | Momentary | FALSE | FALSE | TMED_Event | 3654
ARECIBO | 2022-04-06 16:25 | 2022-04-06 20:37 | 1 | 004:12 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22040600053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2022-04-06 | 252 | keep | 0 | Apr | 2022 | 0.00017164 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 16:27 | 2022-04-06 20:15 | 10 | 003:48 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22040600069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2022-04-06 | 2280 | keep | 0 | Apr | 2022 | 0.0015529 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
UTUADO | 2022-04-06 16:39 | 2022-04-06 17:59 | 3 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | A22040600055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2022-04-06 | 240 | keep | 0 | Apr | 2022 | 0.00016346 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
HUMACAO | 2022-04-06 16:46 | 2022-04-06 16:47 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22040600118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 2450 | keep | 0 | Apr | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | TMED_Event | 2450
CAGUAS | 2022-04-06 16:48 | 2022-04-06 18:20 | 3 | 001:32 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA ELIMINAR POSTE SECUNDARIO PARTIDO Y RELOCALIZAR SECUNDARIA | C22040600117 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 92 | 2022-04-06 | 276 | keep | 0 | Apr | 2022 | 0.00018798 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
MAYAGÃœEZ | 2022-04-06 16:58 | 2022-04-06 20:43 | 40 | 003:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M22040600211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-04-06 | 9000 | keep | 0 | Apr | 2022 | 0.0061299 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
SAN JUAN | 2022-04-06 16:59 | 2022-04-06 17:17 | 914 | 000:18 | P | CABLE SOTERRADO AVERIADO | ALIMENTADOR SECCIONALIZADO | R22040600102 | New_Event | UG Cable Fault | Include | Include | Equipment | 18 | 2022-04-06 | 16452 | keep | 0 | Apr | 2022 | 0.011205 | 0.00062252 | Sustained | FALSE | FALSE | TMED_Event | 914
SAN JUAN | 2022-04-06 17:02 | 2022-04-06 18:28 | 2782 | 001:26 | T | NO SE REPORTO CAUSA | DISPARO SE RESETO BANDERA Y SE SECCIONALIZO 50% EN SERVICIO | S22040600305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2022-04-06 | 239252 | keep | 0 | Apr | 2022 | 0.16295 | 0.0018948 | Sustained | FALSE | FALSE | TMED_Event | 2782
FAJARDO | 2022-04-06 17:03 | 2022-04-06 20:02 | 9 | 002:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 65 EN C/L ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO Y REMPLAZO HERRAJE DE CAJA | R22040600194 | New_Event | Secondary Wire Down | Include | Include | Equipment | 179 | 2022-04-06 | 1611 | keep | 0 | Apr | 2022 | 0.0010972 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
UTUADO | 2022-04-06 17:07 | 2022-04-06 19:43 | 60 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040600059 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2022-04-06 | 9360 | keep | 0 | Apr | 2022 | 0.0063751 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
BAYAMON | 2022-04-06 17:10 | 2022-04-06 18:50 | 60 | 001:40 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LA LINEA | B22040600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-04-06 | 6000 | keep | 0 | Apr | 2022 | 0.0040866 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
SAN JUAN | 2022-04-06 17:17 | 2022-04-06 17:18 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO REALIZANDO PRUEBAS | R22030600102 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 3046 | keep | 0 | Apr | 2022 | 0.0020746 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-04-06 17:18 | 2022-04-06 18:17 | 914 | 000:59 | P | CABLE SOTERRADO AVERIADO | ALIMENTADOR SECCIONALIZADO | R22040600102 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 59 | 2022-04-06 | 53926 | keep | 0 | Apr | 2022 | 0.036729 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2022-04-06 17:19 | 2022-04-06 20:43 | 100 | 003:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA Y CERRO PUENTE NO FUNDIO | C22040600127 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2022-04-06 | 20400 | keep | 0 | Apr | 2022 | 0.013894 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
YAUCO | 2022-04-06 17:52 | 2022-04-06 21:00 | 80 | 003:08 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22040600139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2022-04-06 | 15040 | keep | 0 | Apr | 2022 | 0.010244 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
MAYAGÃœEZ | 2022-04-06 18:00 | 2022-04-06 20:01 | 3147 | 002:01 | T | BREAKER DEFECTUOSO O NO OPERA | SE TRANSFIRIO CARGA AL 6704-01 POR MECANISMO DE CIERRE DAÃ‘ADO | M22040600242 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 121 | 2022-04-06 | 380787 | keep | 0 | Apr | 2022 | 0.25935 | 0.0021434 | Sustained | FALSE | FALSE | TMED_Event | 3147
SAN JUAN | 2022-04-06 18:17 | 2022-04-06 18:19 | 3046 | 000:02 | T | CABLE SOTERRADO AVERIADO | DISPARO PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA | R22040600102 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 2 | 2022-04-06 | 6092 | keep | 0 | Apr | 2022 | 0.0041492 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-04-06 18:19 | 2022-04-06 18:42 | 914 | 000:23 | P | CABLE SOTERRADO AVERIADO | ALIMENTADOR SECCIONALIZADO | R22040600102 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 23 | 2022-04-06 | 21022 | keep | 0 | Apr | 2022 | 0.014318 | 0.00062252 | Sustained | FALSE | FALSE | TMED_Event | 914
BAYAMON | 2022-04-06 18:22 | 2022-04-06 20:00 | 100 | 001:38 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B22040600081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-04-06 | 9800 | keep | 0 | Apr | 2022 | 0.0066747 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
SAN JUAN | 2022-04-06 18:28 | 2022-04-06 18:32 | 1391 | 000:04 | P | NO SE REPORTO CAUSA | SE CERRO MACHETE EDUARDO CONDE ESQ. MERHOFF 90% EN SERVICIO | S22040600305 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-06 | 5564 | keep | 0 | Apr | 2022 | 0.0037896 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-04-06 18:32 | 2022-04-06 18:38 | 139 | 000:06 | P | NO SE REPORTO CAUSA | SE CERRO MACHETE EDUARDO CONDE ESQ. BARTOLOME DE LAS CASAS 100% EN SERVICIO | S22040600305 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-04-06 | 834 | keep | 0 | Apr | 2022 | 0.00056803 | 9.4672e-05 | Sustained | FALSE | FALSE | TMED_Event | 139
SAN JUAN | 2022-04-06 18:42 | 2022-04-06 18:44 | 3046 | 000:02 | T | CABLE SOTERRADO AVERIADO | DISPARO PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA | R22040600102 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 2 | 2022-04-06 | 6092 | keep | 0 | Apr | 2022 | 0.0041492 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-04-06 18:44 | 2022-04-06 19:48 | 914 | 001:04 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA SOTERRADA Y SE CERRO N/O CONTRA EL MISMO BKR | R22040600102 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 64 | 2022-04-06 | 58496 | keep | 0 | Apr | 2022 | 0.039841 | 0.00062252 | Sustained | FALSE | FALSE | TMED_Event | 914
SAN JUAN | 2022-04-06 19:01 | 2022-04-06 19:24 | 411 | 000:23 | P | LINEA DE TRANSMISION 38KV | SE ABRIO N/O CONTRA 1205-2 PARA CERRAR MACHETE N.C. CAMINO CULEBRA NO FASEAN | S22040600243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2022-04-06 | 9453 | keep | 0 | Apr | 2022 | 0.0064384 | 0.00027993 | Sustained | FALSE | FALSE | TMED_Event | 411
FAJARDO | 2022-04-06 19:22 | 2022-04-06 19:23 | 240 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040600197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-06 | 240 | keep | 0 | Apr | 2022 | 0.00016346 | 0.00016346 | Momentary | FALSE | FALSE | TMED_Event | 240
ARECIBO | 2022-04-06 19:24 | 2022-04-06 20:02 | 1 | 000:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22040600070 | New_Event | Wire Down | Include | Include | Equipment | 38 | 2022-04-06 | 38 | keep | 0 | Apr | 2022 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2022-04-06 20:13 | 2022-04-08 04:33 | 1644 | 032:20 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1940 | 2022-04-06 | 3189360 | keep | 0 | Apr | 2022 | 2.1723 | 0.0011197 | Sustained | FALSE | FALSE | TMED_Event | 1644
PONCE | 2022-04-06 20:34 | 2022-04-07 18:41 | 293 | 022:07 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040700045 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1327 | 2022-04-06 | 388811 | keep | 0 | Apr | 2022 | 0.26482 | 0.00019956 | Sustained | FALSE | FALSE | TMED_Event | 293
BAYAMON | 2022-04-06 20:43 | 2022-04-08 20:58 | 1 | 048:15 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2895 | 2022-04-06 | 2895 | keep | 0 | Apr | 2022 | 0.0019718 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-09 12:50 | 47 | 064:07 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 1001-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3847 | 2022-04-06 | 180809 | keep | 0 | Apr | 2022 | 0.12315 | 3.2011e-05 | Sustained | FALSE | FALSE | TMED_Event | 47
BAYAMON | 2022-04-06 20:43 | 2022-04-08 20:58 | 245 | 048:15 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2895 | 2022-04-06 | 709275 | keep | 0 | Apr | 2022 | 0.48308 | 0.00016687 | Sustained | FALSE | FALSE | TMED_Event | 245
BAYAMON | 2022-04-06 20:43 | 2022-04-08 20:56 | 35 | 048:13 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2893 | 2022-04-06 | 101255 | keep | 0 | Apr | 2022 | 0.068964 | 2.3838e-05 | Sustained | FALSE | FALSE | TMED_Event | 35
BAYAMON | 2022-04-06 20:43 | 2022-04-08 20:58 | 126 | 048:15 | T | LINEA DE TRANSMISION | APAGON GENERAL SU CARGA POR 1001-3 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2895 | 2022-04-06 | 364770 | keep | 0 | Apr | 2022 | 0.24844 | 8.5818e-05 | Sustained | FALSE | FALSE | TMED_Event | 126
BAYAMON | 2022-04-06 20:43 | 2022-04-09 20:30 | 46 | 071:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4307 | 2022-04-06 | 198122 | keep | 0 | Apr | 2022 | 0.13494 | 3.133e-05 | Sustained | FALSE | FALSE | TMED_Event | 46
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 396 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 352836 | keep | 0 | Apr | 2022 | 0.24031 | 0.00026971 | Sustained | FALSE | FALSE | TMED_Event | 396
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 119 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 106029 | keep | 0 | Apr | 2022 | 0.072216 | 8.105e-05 | Sustained | FALSE | FALSE | TMED_Event | 119
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 290 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 258390 | keep | 0 | Apr | 2022 | 0.17599 | 0.00019752 | Sustained | FALSE | FALSE | TMED_Event | 290
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 390 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 347490 | keep | 0 | Apr | 2022 | 0.23667 | 0.00026563 | Sustained | FALSE | FALSE | TMED_Event | 390
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 719 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 640629 | keep | 0 | Apr | 2022 | 0.43633 | 0.00048971 | Sustained | FALSE | FALSE | TMED_Event | 719
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 67 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 59697 | keep | 0 | Apr | 2022 | 0.040659 | 4.5633e-05 | Sustained | FALSE | FALSE | TMED_Event | 67
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 1 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 891 | keep | 0 | Apr | 2022 | 0.00060686 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 275 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 245025 | keep | 0 | Apr | 2022 | 0.16689 | 0.0001873 | Sustained | FALSE | FALSE | TMED_Event | 275
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 142 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 126522 | keep | 0 | Apr | 2022 | 0.086174 | 9.6716e-05 | Sustained | FALSE | FALSE | TMED_Event | 142
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:34 | 45 | 014:51 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 891 | 2022-04-06 | 40095 | keep | 0 | Apr | 2022 | 0.027309 | 3.0649e-05 | Sustained | FALSE | FALSE | TMED_Event | 45
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:32 | 93 | 014:49 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 889 | 2022-04-06 | 82677 | keep | 0 | Apr | 2022 | 0.056311 | 6.3342e-05 | Sustained | FALSE | FALSE | TMED_Event | 93
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:33 | 418 | 014:50 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 890 | 2022-04-06 | 372020 | keep | 0 | Apr | 2022 | 0.25338 | 0.0002847 | Sustained | FALSE | FALSE | TMED_Event | 418
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:33 | 295 | 014:50 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 890 | 2022-04-06 | 262550 | keep | 0 | Apr | 2022 | 0.17882 | 0.00020092 | Sustained | FALSE | FALSE | TMED_Event | 295
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:33 | 948 | 014:50 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 890 | 2022-04-06 | 843720 | keep | 0 | Apr | 2022 | 0.57465 | 0.00064568 | Sustained | FALSE | FALSE | TMED_Event | 948
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:38 | 350 | 010:55 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 655 | 2022-04-06 | 229250 | keep | 0 | Apr | 2022 | 0.15614 | 0.00023838 | Sustained | FALSE | FALSE | TMED_Event | 350
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:38 | 215 | 010:55 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 655 | 2022-04-06 | 140825 | keep | 0 | Apr | 2022 | 0.095915 | 0.00014644 | Sustained | FALSE | FALSE | TMED_Event | 215
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:38 | 262 | 010:55 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 655 | 2022-04-06 | 171610 | keep | 0 | Apr | 2022 | 0.11688 | 0.00017845 | Sustained | FALSE | FALSE | TMED_Event | 262
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:38 | 90 | 010:55 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL LLEVA 65% 1104-3 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 655 | 2022-04-06 | 58950 | keep | 0 | Apr | 2022 | 0.040151 | 6.1299e-05 | Sustained | FALSE | FALSE | TMED_Event | 90
BAYAMON | 2022-04-06 20:43 | 2022-04-08 03:44 | 68 | 031:01 | S | LINEA DE TRANSMISION | APAGON GENERAL LLEVANDO LA CARGA DEL 1102-04, 1102-05, 1105-04 Y 1105-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 126548 | keep | 0 | Apr | 2022 | 0.086191 | 4.6314e-05 | Sustained | FALSE | FALSE | TMED_Event | 68
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 03:44 | 171 | 031:01 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 318231 | keep | 0 | Apr | 2022 | 0.21675 | 0.00011647 | Sustained | FALSE | FALSE | TMED_Event | 171
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 03:44 | 1837 | 031:01 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 3418657 | keep | 0 | Apr | 2022 | 2.3284 | 0.0012512 | Sustained | FALSE | FALSE | TMED_Event | 1837
BAYAMON | 2022-04-06 20:43 | 2022-04-08 03:44 | 536 | 031:01 | S | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 1102-01 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 997496 | keep | 0 | Apr | 2022 | 0.67939 | 0.00036507 | Sustained | FALSE | FALSE | TMED_Event | 536
BAYAMON | 2022-04-06 20:43 | 2022-04-08 03:44 | 348 | 031:01 | S | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 1102-01 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 647628 | keep | 0 | Apr | 2022 | 0.4411 | 0.00023702 | Sustained | FALSE | FALSE | TMED_Event | 348
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:51 | 333 | 015:08 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL SU CARGA POR 1133-4 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 908 | 2022-04-06 | 302364 | keep | 0 | Apr | 2022 | 0.20594 | 0.0002268 | Sustained | FALSE | FALSE | TMED_Event | 333
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:51 | 308 | 015:08 | T | LINEA DE TRANSMISION | APAGON GENERAL SU CARGA POR 1133-4 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 908 | 2022-04-06 | 279664 | keep | 0 | Apr | 2022 | 0.19048 | 0.00020978 | Sustained | FALSE | FALSE | TMED_Event | 308
BAYAMON | 2022-04-06 20:43 | 2022-04-08 03:44 | 308 | 031:01 | T | LINEA DE TRANSMISION | APAGON GENERAL SU CARGA POR 1102-01 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 573188 | keep | 0 | Apr | 2022 | 0.3904 | 0.00020978 | Sustained | FALSE | FALSE | TMED_Event | 308
BAYAMON | 2022-04-06 20:43 | 2022-04-08 03:44 | 370 | 031:01 | T | LINEA DE TRANSMISION | APAGON GENERAL SU CARGA POR 1102-01 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 688570 | keep | 0 | Apr | 2022 | 0.46898 | 0.00025201 | Sustained | FALSE | FALSE | TMED_Event | 370
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:43 | 3 | 015:00 | T | LINEA DE TRANSMISION | APAGON GENERAL SU CARGA POR 1617-5 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 900 | 2022-04-06 | 2700 | keep | 0 | Apr | 2022 | 0.001839 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 12:29 | 1 | 063:46 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3826 | 2022-04-06 | 3826 | keep | 0 | Apr | 2022 | 0.0026059 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 12:30 | 1964 | 063:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3827 | 2022-04-06 | 7516228 | keep | 0 | Apr | 2022 | 5.1193 | 0.0013377 | Sustained | FALSE | FALSE | TMED_Event | 1964
BAYAMON | 2022-04-06 20:43 | 2022-04-09 12:30 | 733 | 063:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3827 | 2022-04-06 | 2805191 | keep | 0 | Apr | 2022 | 1.9106 | 0.00049924 | Sustained | FALSE | FALSE | TMED_Event | 733
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:11 | 76 | 055:28 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3328 | 2022-04-06 | 252928 | keep | 0 | Apr | 2022 | 0.17227 | 5.1763e-05 | Sustained | FALSE | FALSE | TMED_Event | 76
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:11 | 1079 | 055:28 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3328 | 2022-04-06 | 3590912 | keep | 0 | Apr | 2022 | 2.4458 | 0.0007349 | Sustained | FALSE | FALSE | TMED_Event | 1079
BAYAMON | 2022-04-06 20:43 | 2022-04-07 08:20 | 1105 | 011:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 697 | 2022-04-06 | 770185 | keep | 0 | Apr | 2022 | 0.52457 | 0.00075261 | Sustained | FALSE | FALSE | TMED_Event | 1105
BAYAMON | 2022-04-06 20:43 | 2022-04-09 03:39 | 181 | 054:56 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3296 | 2022-04-06 | 596576 | keep | 0 | Apr | 2022 | 0.40633 | 0.00012328 | Sustained | FALSE | FALSE | TMED_Event | 181
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:39 | 351 | 054:56 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3296 | 2022-04-06 | 1156896 | keep | 0 | Apr | 2022 | 0.78796 | 0.00023906 | Sustained | FALSE | FALSE | TMED_Event | 351
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:39 | 570 | 054:56 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3296 | 2022-04-06 | 1878720 | keep | 0 | Apr | 2022 | 1.2796 | 0.00038822 | Sustained | FALSE | FALSE | TMED_Event | 570
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 03:44 | 218 | 031:01 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 405698 | keep | 0 | Apr | 2022 | 0.27632 | 0.00014848 | Sustained | FALSE | FALSE | TMED_Event | 218
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 03:44 | 455 | 031:01 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 846755 | keep | 0 | Apr | 2022 | 0.57672 | 0.0003099 | Sustained | FALSE | FALSE | TMED_Event | 455
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 03:44 | 1526 | 031:01 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 2839886 | keep | 0 | Apr | 2022 | 1.9342 | 0.0010394 | Sustained | FALSE | FALSE | TMED_Event | 1526
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 03:44 | 283 | 031:01 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1861 | 2022-04-06 | 526663 | keep | 0 | Apr | 2022 | 0.35871 | 0.00019275 | Sustained | FALSE | FALSE | TMED_Event | 283
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:06 | 2566 | 010:23 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 623 | 2022-04-06 | 1598618 | keep | 0 | Apr | 2022 | 1.0888 | 0.0017477 | Sustained | FALSE | FALSE | TMED_Event | 2566
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:06 | 17 | 010:23 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 623 | 2022-04-06 | 10591 | keep | 0 | Apr | 2022 | 0.0072135 | 1.1579e-05 | Sustained | FALSE | FALSE | TMED_Event | 17
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:05 | 1447 | 010:22 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL LLEVANDO LA CARGA DEL 1419-09 Y 1419-12 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 622 | 2022-04-06 | 900034 | keep | 0 | Apr | 2022 | 0.61301 | 0.00098555 | Sustained | FALSE | FALSE | TMED_Event | 1447
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 19:55 | 1268 | 047:12 | T | LINEA DE TRANSMISION | APAGON GENERAL | S2204060000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2832 | 2022-04-06 | 3590976 | keep | 0 | Apr | 2022 | 2.4458 | 0.00086363 | Sustained | FALSE | FALSE | TMED_Event | 1268
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:00 | 287 | 010:17 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1416-01 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 617 | 2022-04-06 | 177079 | keep | 0 | Apr | 2022 | 0.12061 | 0.00019547 | Sustained | FALSE | FALSE | TMED_Event | 287
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 00:25 | 32 | 051:42 | T | LINEA DE TRANSMISION | APAGON GENERAL 1113-03 LLEVA PARTE DEL 1105-01 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3102 | 2022-04-06 | 99264 | keep | 0 | Apr | 2022 | 0.067608 | 2.1795e-05 | Sustained | FALSE | FALSE | TMED_Event | 32
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 00:25 | 553 | 051:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3102 | 2022-04-06 | 1715406 | keep | 0 | Apr | 2022 | 1.1684 | 0.00037665 | Sustained | FALSE | FALSE | TMED_Event | 553
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 00:13 | 1021 | 051:30 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3090 | 2022-04-06 | 3154890 | keep | 0 | Apr | 2022 | 2.1488 | 0.0006954 | Sustained | FALSE | FALSE | TMED_Event | 1021
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:51 | 3708 | 015:08 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 908 | 2022-04-06 | 3366864 | keep | 0 | Apr | 2022 | 2.2932 | 0.0025255 | Sustained | FALSE | FALSE | TMED_Event | 3708
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:01 | 24 | 015:18 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 918 | 2022-04-06 | 22032 | keep | 0 | Apr | 2022 | 0.015006 | 1.6346e-05 | Sustained | FALSE | FALSE | TMED_Event | 24
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:01 | 1 | 015:18 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 918 | 2022-04-06 | 918 | keep | 0 | Apr | 2022 | 0.00062525 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:49 | 118 | 015:06 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 906 | 2022-04-06 | 106908 | keep | 0 | Apr | 2022 | 0.072815 | 8.0369e-05 | Sustained | FALSE | FALSE | TMED_Event | 118
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:49 | 134 | 015:06 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 906 | 2022-04-06 | 121404 | keep | 0 | Apr | 2022 | 0.082688 | 9.1267e-05 | Sustained | FALSE | FALSE | TMED_Event | 134
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:49 | 114 | 015:06 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 906 | 2022-04-06 | 103284 | keep | 0 | Apr | 2022 | 0.070346 | 7.7645e-05 | Sustained | FALSE | FALSE | TMED_Event | 114
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:06 | 867 | 010:23 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL SE CERRO INTERRUPTOR 1111-01 CARGA POR 1111-01 Y 1119-04 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 623 | 2022-04-06 | 540141 | keep | 0 | Apr | 2022 | 0.36789 | 0.00059051 | Sustained | FALSE | FALSE | TMED_Event | 867
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:50 | 343 | 015:07 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 907 | 2022-04-06 | 311101 | keep | 0 | Apr | 2022 | 0.21189 | 0.00023362 | Sustained | FALSE | FALSE | TMED_Event | 343
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:50 | 996 | 015:07 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 907 | 2022-04-06 | 903372 | keep | 0 | Apr | 2022 | 0.61528 | 0.00067837 | Sustained | FALSE | FALSE | TMED_Event | 996
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:50 | 169 | 015:07 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 907 | 2022-04-06 | 153283 | keep | 0 | Apr | 2022 | 0.1044 | 0.00011511 | Sustained | FALSE | FALSE | TMED_Event | 169
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:50 | 5 | 015:07 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 907 | 2022-04-06 | 4535 | keep | 0 | Apr | 2022 | 0.0030888 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:50 | 466 | 015:07 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL CARGA POR 1116-04 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 907 | 2022-04-06 | 422662 | keep | 0 | Apr | 2022 | 0.28787 | 0.00031739 | Sustained | FALSE | FALSE | TMED_Event | 466
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:50 | 316 | 015:07 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 907 | 2022-04-06 | 286612 | keep | 0 | Apr | 2022 | 0.19521 | 0.00021523 | Sustained | FALSE | FALSE | TMED_Event | 316
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:50 | 1356 | 015:07 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 907 | 2022-04-06 | 1229892 | keep | 0 | Apr | 2022 | 0.83767 | 0.00092357 | Sustained | FALSE | FALSE | TMED_Event | 1356
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:25 | 2124 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 7098408 | keep | 0 | Apr | 2022 | 4.8347 | 0.0014466 | Sustained | FALSE | FALSE | TMED_Event | 2124
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:25 | 1825 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL 1118-09 LLEVA 1118-08 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 6099150 | keep | 0 | Apr | 2022 | 4.1541 | 0.001243 | Sustained | FALSE | FALSE | TMED_Event | 1825
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:25 | 4398 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL 1118-09 LLEVA 1118-08 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 14698116 | keep | 0 | Apr | 2022 | 10.0108 | 0.0029955 | Sustained | FALSE | FALSE | TMED_Event | 4398
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 16:55 | 2782 | 044:12 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL LLEVA 20% 1111-1 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2652 | 2022-04-06 | 7377864 | keep | 0 | Apr | 2022 | 5.025 | 0.0018948 | Sustained | FALSE | FALSE | TMED_Event | 2782
BAYAMON | 2022-04-06 20:43 | 2022-04-07 14:16 | 1 | 017:33 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1053 | 2022-04-06 | 1053 | keep | 0 | Apr | 2022 | 0.00071719 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 14:17 | 863 | 017:34 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1054 | 2022-04-06 | 909602 | keep | 0 | Apr | 2022 | 0.61953 | 0.00058779 | Sustained | FALSE | FALSE | TMED_Event | 863
BAYAMON | 2022-04-06 20:43 | 2022-04-10 17:29 | 1 | 092:46 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5566 | 2022-04-06 | 5566 | keep | 0 | Apr | 2022 | 0.003791 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 14:13 | 2720 | 017:30 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1050 | 2022-04-06 | 2856000 | keep | 0 | Apr | 2022 | 1.9452 | 0.0018526 | Sustained | FALSE | FALSE | TMED_Event | 2720
BAYAMON | 2022-04-06 20:43 | 2022-04-07 14:17 | 1 | 017:34 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1054 | 2022-04-06 | 1054 | keep | 0 | Apr | 2022 | 0.00071787 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 14:17 | 1 | 017:34 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1054 | 2022-04-06 | 1054 | keep | 0 | Apr | 2022 | 0.00071787 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 14:17 | 1 | 017:34 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1054 | 2022-04-06 | 1054 | keep | 0 | Apr | 2022 | 0.00071787 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 14:17 | 1 | 017:34 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1054 | 2022-04-06 | 1054 | keep | 0 | Apr | 2022 | 0.00071787 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:51 | 620 | 015:08 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 908 | 2022-04-06 | 562960 | keep | 0 | Apr | 2022 | 0.38343 | 0.00042228 | Sustained | FALSE | FALSE | TMED_Event | 620
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:51 | 451 | 015:08 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 908 | 2022-04-06 | 409508 | keep | 0 | Apr | 2022 | 0.27891 | 0.00030717 | Sustained | FALSE | FALSE | TMED_Event | 451
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:51 | 333 | 015:08 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 908 | 2022-04-06 | 302364 | keep | 0 | Apr | 2022 | 0.20594 | 0.0002268 | Sustained | FALSE | FALSE | TMED_Event | 333
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 04:47 | 137 | 008:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 484 | 2022-04-06 | 66308 | keep | 0 | Apr | 2022 | 0.045162 | 9.331e-05 | Sustained | FALSE | FALSE | TMED_Event | 137
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 04:47 | 457 | 008:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 484 | 2022-04-06 | 221188 | keep | 0 | Apr | 2022 | 0.15065 | 0.00031126 | Sustained | FALSE | FALSE | TMED_Event | 457
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 04:47 | 1225 | 008:04 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 484 | 2022-04-06 | 592900 | keep | 0 | Apr | 2022 | 0.40382 | 0.00083434 | Sustained | FALSE | FALSE | TMED_Event | 1225
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 04:47 | 1452 | 008:04 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 484 | 2022-04-06 | 702768 | keep | 0 | Apr | 2022 | 0.47865 | 0.00098895 | Sustained | FALSE | FALSE | TMED_Event | 1452
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 04:47 | 616 | 008:04 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 484 | 2022-04-06 | 298144 | keep | 0 | Apr | 2022 | 0.20306 | 0.00041955 | Sustained | FALSE | FALSE | TMED_Event | 616
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 18:20 | 4291 | 021:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1297 | 2022-04-06 | 5565427 | keep | 0 | Apr | 2022 | 3.7906 | 0.0029226 | Sustained | FALSE | FALSE | TMED_Event | 4291
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 22:02 | 1381 | 025:19 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL ENTRO EN SERVICIO EL 1206-04 QUE LLEVA 60% DEL 1204-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1519 | 2022-04-06 | 2097739 | keep | 0 | Apr | 2022 | 1.4288 | 0.00094059 | Sustained | FALSE | FALSE | TMED_Event | 1381
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:50 | 1483 | 017:07 | P | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL. INTERRUPTOR 1336-08 LLEVA CARGA 1336-09 30% 1204-04 Y PARTE 1204-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1027 | 2022-04-06 | 1523041 | keep | 0 | Apr | 2022 | 1.0373 | 0.0010101 | Sustained | FALSE | FALSE | TMED_Event | 1483
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:50 | 10211 | 017:07 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL. INTERRUPTOR 1336-08 LLEVA CARGA 1336-09 30% 1204-04 Y PARTE 1204-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1027 | 2022-04-06 | 10486697 | keep | 0 | Apr | 2022 | 7.1424 | 0.0069547 | Sustained | FALSE | FALSE | TMED_Event | 10211
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 10:40 | 108 | 013:57 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 837 | 2022-04-06 | 90396 | keep | 0 | Apr | 2022 | 0.061568 | 7.3558e-05 | Sustained | FALSE | FALSE | TMED_Event | 108
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 10:40 | 1368 | 013:57 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 837 | 2022-04-06 | 1145016 | keep | 0 | Apr | 2022 | 0.77987 | 0.00093174 | Sustained | FALSE | FALSE | TMED_Event | 1368
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 10:40 | 2064 | 013:57 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 837 | 2022-04-06 | 1727568 | keep | 0 | Apr | 2022 | 1.1766 | 0.0014058 | Sustained | FALSE | FALSE | TMED_Event | 2064
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 04:47 | 641 | 008:04 | T | LINEA DE TRANSMISION | APAGON GENERAL INTERRUPTOR 1206-01 LLEVA CARGA 1206-02 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S2204060000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 484 | 2022-04-06 | 310244 | keep | 0 | Apr | 2022 | 0.21131 | 0.00043658 | Sustained | FALSE | FALSE | TMED_Event | 641
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 19:34 | 733 | 046:51 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1206-1 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2811 | 2022-04-06 | 2060463 | keep | 0 | Apr | 2022 | 1.4034 | 0.00049924 | Sustained | FALSE | FALSE | TMED_Event | 733
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 21:36 | 4133 | 024:53 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL LLLEVA PARTE 1204-5 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1493 | 2022-04-06 | 6170569 | keep | 0 | Apr | 2022 | 4.2027 | 0.002815 | Sustained | FALSE | FALSE | TMED_Event | 4133
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 22:02 | 1799 | 025:19 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL INTERRUPTOR 1206-04 LLEVA 40% 1204-04 Y 60% 1204-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1519 | 2022-04-06 | 2732681 | keep | 0 | Apr | 2022 | 1.8612 | 0.0012253 | Sustained | FALSE | FALSE | TMED_Event | 1799
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 13:49 | 1061 | 041:06 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2466 | 2022-04-06 | 2616426 | keep | 0 | Apr | 2022 | 1.782 | 0.00072264 | Sustained | FALSE | FALSE | TMED_Event | 1061
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 12:54 | 742 | 040:11 | T | LINEA DE TRANSMISION | APAGON GENERAL 1335-05 LLEVA 40% DEL 1301-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2411 | 2022-04-06 | 1788962 | keep | 0 | Apr | 2022 | 1.2185 | 0.00050537 | Sustained | FALSE | FALSE | TMED_Event | 742
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 13:49 | 998 | 041:06 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2466 | 2022-04-06 | 2461068 | keep | 0 | Apr | 2022 | 1.6762 | 0.00067973 | Sustained | FALSE | FALSE | TMED_Event | 998
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:09 | 1397 | 055:26 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3326 | 2022-04-06 | 4646422 | keep | 0 | Apr | 2022 | 3.1647 | 0.00095149 | Sustained | FALSE | FALSE | TMED_Event | 1397
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:47 | 998 | 015:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 904 | 2022-04-06 | 902192 | keep | 0 | Apr | 2022 | 0.61448 | 0.00067973 | Sustained | FALSE | FALSE | TMED_Event | 998
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:47 | 2435 | 015:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 904 | 2022-04-06 | 2201240 | keep | 0 | Apr | 2022 | 1.4993 | 0.0016585 | Sustained | FALSE | FALSE | TMED_Event | 2435
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:47 | 726 | 015:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 904 | 2022-04-06 | 656304 | keep | 0 | Apr | 2022 | 0.44701 | 0.00049448 | Sustained | FALSE | FALSE | TMED_Event | 726
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:47 | 225 | 015:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 904 | 2022-04-06 | 203400 | keep | 0 | Apr | 2022 | 0.13853 | 0.00015325 | Sustained | FALSE | FALSE | TMED_Event | 225
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:47 | 870 | 015:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 904 | 2022-04-06 | 786480 | keep | 0 | Apr | 2022 | 0.53567 | 0.00059255 | Sustained | FALSE | FALSE | TMED_Event | 870
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 627 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 368676 | keep | 0 | Apr | 2022 | 0.2511 | 0.00042705 | Sustained | FALSE | FALSE | TMED_Event | 627
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 293 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 172284 | keep | 0 | Apr | 2022 | 0.11734 | 0.00019956 | Sustained | FALSE | FALSE | TMED_Event | 293
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 761 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 447468 | keep | 0 | Apr | 2022 | 0.30477 | 0.00051831 | Sustained | FALSE | FALSE | TMED_Event | 761
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 11:23 | 451 | 038:40 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2320 | 2022-04-06 | 1046320 | keep | 0 | Apr | 2022 | 0.71264 | 0.00030717 | Sustained | FALSE | FALSE | TMED_Event | 451
BAYAMON | 2022-04-06 20:43 | 2022-04-07 04:37 | 7 | 007:54 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 474 | 2022-04-06 | 3318 | keep | 0 | Apr | 2022 | 0.0022599 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:30 | 277 | 009:47 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 587 | 2022-04-06 | 162599 | keep | 0 | Apr | 2022 | 0.11075 | 0.00018866 | Sustained | FALSE | FALSE | TMED_Event | 277
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 04:37 | 15 | 007:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 474 | 2022-04-06 | 7110 | keep | 0 | Apr | 2022 | 0.0048426 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:30 | 5 | 009:47 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 587 | 2022-04-06 | 2935 | keep | 0 | Apr | 2022 | 0.001999 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:57 | 428 | 010:14 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 614 | 2022-04-06 | 262792 | keep | 0 | Apr | 2022 | 0.17899 | 0.00029151 | Sustained | FALSE | FALSE | TMED_Event | 428
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:57 | 570 | 010:14 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 614 | 2022-04-06 | 349980 | keep | 0 | Apr | 2022 | 0.23837 | 0.00038822 | Sustained | FALSE | FALSE | TMED_Event | 570
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:57 | 90 | 010:14 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 614 | 2022-04-06 | 55260 | keep | 0 | Apr | 2022 | 0.037637 | 6.1299e-05 | Sustained | FALSE | FALSE | TMED_Event | 90
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:57 | 549 | 010:14 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 614 | 2022-04-06 | 337086 | keep | 0 | Apr | 2022 | 0.22959 | 0.00037392 | Sustained | FALSE | FALSE | TMED_Event | 549
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:57 | 155 | 010:14 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 614 | 2022-04-06 | 95170 | keep | 0 | Apr | 2022 | 0.06482 | 0.00010557 | Sustained | FALSE | FALSE | TMED_Event | 155
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 05:06 | 100 | 056:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3383 | 2022-04-06 | 338300 | keep | 0 | Apr | 2022 | 0.23041 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 05:06 | 644 | 056:23 | T | LINEA DE TRANSMISION | APAGON GENERAL LLEVA EL 1329-04 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3383 | 2022-04-06 | 2178652 | keep | 0 | Apr | 2022 | 1.4839 | 0.00043863 | Sustained | FALSE | FALSE | TMED_Event | 644
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 05:06 | 525 | 056:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3383 | 2022-04-06 | 1776075 | keep | 0 | Apr | 2022 | 1.2097 | 0.00035758 | Sustained | FALSE | FALSE | TMED_Event | 525
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 05:06 | 45 | 056:23 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1329-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3383 | 2022-04-06 | 152235 | keep | 0 | Apr | 2022 | 0.10369 | 3.0649e-05 | Sustained | FALSE | FALSE | TMED_Event | 45
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 05:06 | 418 | 056:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3383 | 2022-04-06 | 1414094 | keep | 0 | Apr | 2022 | 0.96313 | 0.0002847 | Sustained | FALSE | FALSE | TMED_Event | 418
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 04:23 | 718 | 007:40 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 460 | 2022-04-06 | 330280 | keep | 0 | Apr | 2022 | 0.22495 | 0.00048903 | Sustained | FALSE | FALSE | TMED_Event | 718
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:10 | 533 | 055:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3327 | 2022-04-06 | 1773291 | keep | 0 | Apr | 2022 | 1.2078 | 0.00036302 | Sustained | FALSE | FALSE | TMED_Event | 533
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:10 | 844 | 055:27 | P | LINEA DE TRANSMISION | APAGON GENERAL PARTE DEL 1330-04 POR 1345-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3327 | 2022-04-06 | 2807988 | keep | 0 | Apr | 2022 | 1.9125 | 0.00057484 | Sustained | FALSE | FALSE | TMED_Event | 844
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 09:08 | 1384 | 036:25 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2185 | 2022-04-06 | 3024040 | keep | 0 | Apr | 2022 | 2.0597 | 0.00094264 | Sustained | FALSE | FALSE | TMED_Event | 1384
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 08:50 | 869 | 036:07 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2167 | 2022-04-06 | 1883123 | keep | 0 | Apr | 2022 | 1.2826 | 0.00059187 | Sustained | FALSE | FALSE | TMED_Event | 869
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 16:57 | 1208 | 044:14 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2654 | 2022-04-06 | 3206032 | keep | 0 | Apr | 2022 | 2.1836 | 0.00082276 | Sustained | FALSE | FALSE | TMED_Event | 1208
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 08:50 | 375 | 036:07 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2167 | 2022-04-06 | 812625 | keep | 0 | Apr | 2022 | 0.55348 | 0.00025541 | Sustained | FALSE | FALSE | TMED_Event | 375
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 08:50 | 608 | 036:07 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2167 | 2022-04-06 | 1317536 | keep | 0 | Apr | 2022 | 0.89737 | 0.00041411 | Sustained | FALSE | FALSE | TMED_Event | 608
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:39 | 602 | 054:56 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3296 | 2022-04-06 | 1984192 | keep | 0 | Apr | 2022 | 1.3514 | 0.00041002 | Sustained | FALSE | FALSE | TMED_Event | 602
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:39 | 314 | 054:56 | T | LINEA DE TRANSMISION | APAGON GENERAL 1335-05 LLEVA 40% DEL 1301-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3296 | 2022-04-06 | 1034944 | keep | 0 | Apr | 2022 | 0.7049 | 0.00021386 | Sustained | FALSE | FALSE | TMED_Event | 314
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 17:59 | 6481 | 045:16 | T | LINEA DE TRANSMISION | APAGON GENERAL CERRADO 1619-02 LLEVANDO 30% DEL 1336-06 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2716 | 2022-04-06 | 17602396 | keep | 0 | Apr | 2022 | 11.9889 | 0.0044142 | Sustained | FALSE | FALSE | TMED_Event | 6481
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:37 | 6244 | 054:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3294 | 2022-04-06 | 20567736 | keep | 0 | Apr | 2022 | 14.0086 | 0.0042528 | Sustained | FALSE | FALSE | TMED_Event | 6244
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:50 | 5290 | 017:07 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL. INTERRUPTOR 1336-08 LLEVA CARGA 1336-09 30% 1204-04 Y PARTE 1204-05 PARTE DE 1336-08 POR 1424-08 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1027 | 2022-04-06 | 5432830 | keep | 0 | Apr | 2022 | 3.7003 | 0.003603 | Sustained | FALSE | FALSE | TMED_Event | 5290
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:50 | 207 | 017:07 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL. INTERRUPTOR 1336-08 LLEVA CARGA 1336-09 30% 1204-04 Y PARTE 1204-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1027 | 2022-04-06 | 212589 | keep | 0 | Apr | 2022 | 0.14479 | 0.00014099 | Sustained | FALSE | FALSE | TMED_Event | 207
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 23:54 | 403 | 027:11 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. CARGA POR EL 1336-07 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1631 | 2022-04-06 | 657293 | keep | 0 | Apr | 2022 | 0.44768 | 0.00027448 | Sustained | FALSE | FALSE | TMED_Event | 403
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:25 | 255 | 014:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 882 | 2022-04-06 | 224910 | keep | 0 | Apr | 2022 | 0.15319 | 0.00017368 | Sustained | FALSE | FALSE | TMED_Event | 255
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:25 | 928 | 014:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 882 | 2022-04-06 | 818496 | keep | 0 | Apr | 2022 | 0.55747 | 0.00063206 | Sustained | FALSE | FALSE | TMED_Event | 928
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:25 | 200 | 014:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 882 | 2022-04-06 | 176400 | keep | 0 | Apr | 2022 | 0.12015 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:25 | 185 | 014:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 882 | 2022-04-06 | 163170 | keep | 0 | Apr | 2022 | 0.11113 | 0.000126 | Sustained | FALSE | FALSE | TMED_Event | 185
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:25 | 73 | 014:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 882 | 2022-04-06 | 64386 | keep | 0 | Apr | 2022 | 0.043853 | 4.972e-05 | Sustained | FALSE | FALSE | TMED_Event | 73
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:02 | 356 | 015:19 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 919 | 2022-04-06 | 327164 | keep | 0 | Apr | 2022 | 0.22283 | 0.00024247 | Sustained | FALSE | FALSE | TMED_Event | 356
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:02 | 790 | 015:19 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 919 | 2022-04-06 | 726010 | keep | 0 | Apr | 2022 | 0.49448 | 0.00053807 | Sustained | FALSE | FALSE | TMED_Event | 790
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:02 | 29 | 015:19 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 919 | 2022-04-06 | 26651 | keep | 0 | Apr | 2022 | 0.018152 | 1.9752e-05 | Sustained | FALSE | FALSE | TMED_Event | 29
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:02 | 390 | 015:19 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 919 | 2022-04-06 | 358410 | keep | 0 | Apr | 2022 | 0.24411 | 0.00026563 | Sustained | FALSE | FALSE | TMED_Event | 390
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:02 | 291 | 015:19 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 919 | 2022-04-06 | 267429 | keep | 0 | Apr | 2022 | 0.18214 | 0.0001982 | Sustained | FALSE | FALSE | TMED_Event | 291
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 08:49 | 1825 | 036:06 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2166 | 2022-04-06 | 3952950 | keep | 0 | Apr | 2022 | 2.6923 | 0.001243 | Sustained | FALSE | FALSE | TMED_Event | 1825
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 21:37 | 47 | 048:54 | T | LINEA DE TRANSMISION | SE CERRO POR SCADA | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2934 | 2022-04-06 | 137898 | keep | 0 | Apr | 2022 | 0.093922 | 3.2011e-05 | Sustained | FALSE | FALSE | TMED_Event | 47
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 08:49 | 315 | 036:06 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2166 | 2022-04-06 | 682290 | keep | 0 | Apr | 2022 | 0.4647 | 0.00021455 | Sustained | FALSE | FALSE | TMED_Event | 315
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:09 | 2 | 055:26 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3326 | 2022-04-06 | 6652 | keep | 0 | Apr | 2022 | 0.0045306 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:09 | 2391 | 055:26 | T | LINEA DE TRANSMISION | APAGON GENERAL 1343-05 LLEVA CARGA DEL 1908-3 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3326 | 2022-04-06 | 7952466 | keep | 0 | Apr | 2022 | 5.4164 | 0.0016285 | Sustained | FALSE | FALSE | TMED_Event | 2391
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 11:07 | 660 | 038:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2304 | 2022-04-06 | 1520640 | keep | 0 | Apr | 2022 | 1.0357 | 0.00044952 | Sustained | FALSE | FALSE | TMED_Event | 660
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 11:07 | 435 | 038:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2304 | 2022-04-06 | 1002240 | keep | 0 | Apr | 2022 | 0.68262 | 0.00029628 | Sustained | FALSE | FALSE | TMED_Event | 435
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 11:07 | 259 | 038:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2304 | 2022-04-06 | 596736 | keep | 0 | Apr | 2022 | 0.40643 | 0.0001764 | Sustained | FALSE | FALSE | TMED_Event | 259
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 11:07 | 686 | 038:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2304 | 2022-04-06 | 1580544 | keep | 0 | Apr | 2022 | 1.0765 | 0.00046723 | Sustained | FALSE | FALSE | TMED_Event | 686
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 11:07 | 953 | 038:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2304 | 2022-04-06 | 2195712 | keep | 0 | Apr | 2022 | 1.4955 | 0.00064908 | Sustained | FALSE | FALSE | TMED_Event | 953
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:44 | 1 | 016:01 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 961 | 2022-04-06 | 961 | keep | 0 | Apr | 2022 | 0.00065453 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:44 | 1844 | 016:01 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL 60% POR 1529-15 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 961 | 2022-04-06 | 1772084 | keep | 0 | Apr | 2022 | 1.207 | 0.0012559 | Sustained | FALSE | FALSE | TMED_Event | 1844
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:44 | 2422 | 016:01 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 961 | 2022-04-06 | 2327542 | keep | 0 | Apr | 2022 | 1.5853 | 0.0016496 | Sustained | FALSE | FALSE | TMED_Event | 2422
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:47 | 3932 | 015:04 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1303-3 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 904 | 2022-04-06 | 3554528 | keep | 0 | Apr | 2022 | 2.421 | 0.0026781 | Sustained | FALSE | FALSE | TMED_Event | 3932
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 12:56 | 135 | 040:13 | T | LINEA DE TRANSMISION | DISPARO AL CERRAR N/O SE VERIFICO Y SE CERRO LOCAMENTE 100% | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2413 | 2022-04-06 | 325755 | keep | 0 | Apr | 2022 | 0.22187 | 9.1948e-05 | Sustained | FALSE | FALSE | TMED_Event | 135
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:47 | 1598 | 015:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 904 | 2022-04-06 | 1444592 | keep | 0 | Apr | 2022 | 0.98391 | 0.0010884 | Sustained | FALSE | FALSE | TMED_Event | 1598
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:12 | 1000 | 015:29 | P | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 929 | 2022-04-06 | 929000 | keep | 0 | Apr | 2022 | 0.63274 | 0.0006811 | Sustained | FALSE | FALSE | TMED_Event | 1000
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:22 | 278 | 010:39 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 639 | 2022-04-06 | 177642 | keep | 0 | Apr | 2022 | 0.12099 | 0.00018934 | Sustained | FALSE | FALSE | TMED_Event | 278
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:22 | 1290 | 010:39 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1424-8 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 639 | 2022-04-06 | 824310 | keep | 0 | Apr | 2022 | 0.56143 | 0.00087861 | Sustained | FALSE | FALSE | TMED_Event | 1290
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:37 | 7 | 009:54 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1359-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 594 | 2022-04-06 | 4158 | keep | 0 | Apr | 2022 | 0.002832 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:35 | 17 | 009:52 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 592 | 2022-04-06 | 10064 | keep | 0 | Apr | 2022 | 0.0068545 | 1.1579e-05 | Sustained | FALSE | FALSE | TMED_Event | 17
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:37 | 2 | 009:54 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 594 | 2022-04-06 | 1188 | keep | 0 | Apr | 2022 | 0.00080914 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-04-06 20:43 | 2022-04-07 19:43 | 8 | 023:00 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1359-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1380 | 2022-04-06 | 11040 | keep | 0 | Apr | 2022 | 0.0075193 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
BAYAMON | 2022-04-06 20:43 | 2022-04-07 19:43 | 6 | 023:00 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1359-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1380 | 2022-04-06 | 8280 | keep | 0 | Apr | 2022 | 0.0056395 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
BAYAMON | 2022-04-06 20:43 | 2022-04-07 19:43 | 1 | 023:00 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1359-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1380 | 2022-04-06 | 1380 | keep | 0 | Apr | 2022 | 0.00093991 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:36 | 312 | 009:53 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 593 | 2022-04-06 | 185016 | keep | 0 | Apr | 2022 | 0.12601 | 0.0002125 | Sustained | FALSE | FALSE | TMED_Event | 312
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 837 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL SU CARGA 1401-7 | S22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 492156 | keep | 0 | Apr | 2022 | 0.33521 | 0.00057008 | Sustained | FALSE | FALSE | TMED_Event | 837
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 908 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL LLEVA 1401-6 | S22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 533904 | keep | 0 | Apr | 2022 | 0.36364 | 0.00061843 | Sustained | FALSE | FALSE | TMED_Event | 908
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 135 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL SE SECCIONALIZO ABRIENDO N/O CONTRA 1346-5 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 79380 | keep | 0 | Apr | 2022 | 0.054065 | 9.1948e-05 | Sustained | FALSE | FALSE | TMED_Event | 135
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 1 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 588 | keep | 0 | Apr | 2022 | 0.00040048 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 1295 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 761460 | keep | 0 | Apr | 2022 | 0.51863 | 0.00088202 | Sustained | FALSE | FALSE | TMED_Event | 1295
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:44 | 143 | 016:01 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTA SUR. APAGON GENERAL. INTERRUPTOR 1404-06 LLEVA 80% 1404-07 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 961 | 2022-04-06 | 137423 | keep | 0 | Apr | 2022 | 0.093598 | 9.7397e-05 | Sustained | FALSE | FALSE | TMED_Event | 143
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:42 | 271 | 015:59 | P | LINEA DE TRANSMISION | DISPARO 0080 COSTA SUR. APAGON GENERAL. 80% POR 1404-06 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 959 | 2022-04-06 | 259889 | keep | 0 | Apr | 2022 | 0.17701 | 0.00018458 | Sustained | FALSE | FALSE | TMED_Event | 271
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:45 | 328 | 016:02 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTA SUR. APAGON GENERAL. | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 962 | 2022-04-06 | 315536 | keep | 0 | Apr | 2022 | 0.21491 | 0.0002234 | Sustained | FALSE | FALSE | TMED_Event | 328
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:45 | 485 | 016:02 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTA SUR. APAGON GENERAL. INTERRUPTOR 1404-09 LLEVA CARGA 1420-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 962 | 2022-04-06 | 466570 | keep | 0 | Apr | 2022 | 0.31778 | 0.00033033 | Sustained | FALSE | FALSE | TMED_Event | 485
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:29 | 23 | 015:46 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTE SUR. APAGON GENERAL | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 946 | 2022-04-06 | 21758 | keep | 0 | Apr | 2022 | 0.014819 | 1.5665e-05 | Sustained | FALSE | FALSE | TMED_Event | 23
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:29 | 530 | 015:46 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTE SUR. APAGON GENERAL | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 946 | 2022-04-06 | 501380 | keep | 0 | Apr | 2022 | 0.34149 | 0.00036098 | Sustained | FALSE | FALSE | TMED_Event | 530
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:29 | 37 | 015:46 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTE SUR. APAGON GENERAL | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 946 | 2022-04-06 | 35002 | keep | 0 | Apr | 2022 | 0.02384 | 2.5201e-05 | Sustained | FALSE | FALSE | TMED_Event | 37
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:29 | 929 | 015:46 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTE SUR. APAGON GENERAL. INTERRUPTOR 1414-03 LLEVA LLEVA 1421-04 Y 1421-03 | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 946 | 2022-04-06 | 878834 | keep | 0 | Apr | 2022 | 0.59857 | 0.00063274 | Sustained | FALSE | FALSE | TMED_Event | 929
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:29 | 21 | 015:46 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTE SUR. APAGON GENERAL. | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 946 | 2022-04-06 | 19866 | keep | 0 | Apr | 2022 | 0.013531 | 1.4303e-05 | Sustained | FALSE | FALSE | TMED_Event | 21
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:00 | 262 | 010:17 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 617 | 2022-04-06 | 161654 | keep | 0 | Apr | 2022 | 0.1101 | 0.00017845 | Sustained | FALSE | FALSE | TMED_Event | 262
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:00 | 296 | 010:17 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 617 | 2022-04-06 | 182632 | keep | 0 | Apr | 2022 | 0.12439 | 0.0002016 | Sustained | FALSE | FALSE | TMED_Event | 296
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:00 | 79 | 010:17 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 617 | 2022-04-06 | 48743 | keep | 0 | Apr | 2022 | 0.033199 | 5.3807e-05 | Sustained | FALSE | FALSE | TMED_Event | 79
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:00 | 1129 | 010:17 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 617 | 2022-04-06 | 696593 | keep | 0 | Apr | 2022 | 0.47445 | 0.00076896 | Sustained | FALSE | FALSE | TMED_Event | 1129
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:00 | 1573 | 010:17 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 617 | 2022-04-06 | 970541 | keep | 0 | Apr | 2022 | 0.66103 | 0.0010714 | Sustained | FALSE | FALSE | TMED_Event | 1573
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 849 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 845604 | keep | 0 | Apr | 2022 | 0.57594 | 0.00057825 | Sustained | FALSE | FALSE | TMED_Event | 849
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 893 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL LLEVA 10% 1422-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 889428 | keep | 0 | Apr | 2022 | 0.60579 | 0.00060822 | Sustained | FALSE | FALSE | TMED_Event | 893
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 602 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 599592 | keep | 0 | Apr | 2022 | 0.40838 | 0.00041002 | Sustained | FALSE | FALSE | TMED_Event | 602
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 43 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 42828 | keep | 0 | Apr | 2022 | 0.02917 | 2.9287e-05 | Sustained | FALSE | FALSE | TMED_Event | 43
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 1389 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 1383444 | keep | 0 | Apr | 2022 | 0.94226 | 0.00094604 | Sustained | FALSE | FALSE | TMED_Event | 1389
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:05 | 266 | 010:22 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL CARGA POR EL 1112-04 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 622 | 2022-04-06 | 165452 | keep | 0 | Apr | 2022 | 0.11269 | 0.00018117 | Sustained | FALSE | FALSE | TMED_Event | 266
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:34 | 1 | 010:51 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 651 | 2022-04-06 | 651 | keep | 0 | Apr | 2022 | 0.00044339 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:34 | 1 | 010:51 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 651 | 2022-04-06 | 651 | keep | 0 | Apr | 2022 | 0.00044339 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:05 | 73 | 010:22 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL CARGA POR EL 1112-04 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 622 | 2022-04-06 | 45406 | keep | 0 | Apr | 2022 | 0.030926 | 4.972e-05 | Sustained | FALSE | FALSE | TMED_Event | 73
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:30 | 448 | 015:47 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 947 | 2022-04-06 | 424256 | keep | 0 | Apr | 2022 | 0.28896 | 0.00030513 | Sustained | FALSE | FALSE | TMED_Event | 448
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:23 | 1191 | 010:40 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 640 | 2022-04-06 | 762240 | keep | 0 | Apr | 2022 | 0.51916 | 0.00081118 | Sustained | FALSE | FALSE | TMED_Event | 1191
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:23 | 60 | 010:40 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 640 | 2022-04-06 | 38400 | keep | 0 | Apr | 2022 | 0.026154 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:23 | 546 | 010:40 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 640 | 2022-04-06 | 349440 | keep | 0 | Apr | 2022 | 0.238 | 0.00037188 | Sustained | FALSE | FALSE | TMED_Event | 546
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:36 | 449 | 010:53 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 653 | 2022-04-06 | 293197 | keep | 0 | Apr | 2022 | 0.1997 | 0.00030581 | Sustained | FALSE | FALSE | TMED_Event | 449
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:45 | 4 | 016:02 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTA SUR. APAGON GENERAL. INTERRUPTOR 1404-09 LLEVA CARGA 1420-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 962 | 2022-04-06 | 3848 | keep | 0 | Apr | 2022 | 0.0026209 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 1498 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 880824 | keep | 0 | Apr | 2022 | 0.59993 | 0.0010203 | Sustained | FALSE | FALSE | TMED_Event | 1498
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:48 | 164 | 010:05 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL SU CARGA POR 1531-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 605 | 2022-04-06 | 99220 | keep | 0 | Apr | 2022 | 0.067578 | 0.0001117 | Sustained | FALSE | FALSE | TMED_Event | 164
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:29 | 533 | 015:46 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTE SUR. APAGON GENERAL. INTERRUPTOR 1414-03 LLEVA LLEVA 1421-04 Y 1421-03 | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 946 | 2022-04-06 | 504218 | keep | 0 | Apr | 2022 | 0.34342 | 0.00036302 | Sustained | FALSE | FALSE | TMED_Event | 533
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 12:29 | 451 | 015:46 | T | LINEA DE TRANSMISION | DISPARO 0080 COSTE SUR. APAGON GENERAL. INTERRUPTOR 1414-03 LLEVA LLEVA 1421-04 Y 1421-03 | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 946 | 2022-04-06 | 426646 | keep | 0 | Apr | 2022 | 0.29059 | 0.00030717 | Sustained | FALSE | FALSE | TMED_Event | 451
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:31 | 766 | 009:48 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 588 | 2022-04-06 | 450408 | keep | 0 | Apr | 2022 | 0.30677 | 0.00052172 | Sustained | FALSE | FALSE | TMED_Event | 766
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 673 | 016:36 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL CARGA POR EL 1423-04 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 670308 | keep | 0 | Apr | 2022 | 0.45654 | 0.00045838 | Sustained | FALSE | FALSE | TMED_Event | 673
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 372 | 016:36 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL CARGA POR EL 1423-04 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 370512 | keep | 0 | Apr | 2022 | 0.25235 | 0.00025337 | Sustained | FALSE | FALSE | TMED_Event | 372
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 732 | 016:36 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL CARGA POR EL 1423-04 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 729072 | keep | 0 | Apr | 2022 | 0.49657 | 0.00049856 | Sustained | FALSE | FALSE | TMED_Event | 732
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 06:57 | 637 | 010:14 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL CARGA POR EL 1328-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 614 | 2022-04-06 | 391118 | keep | 0 | Apr | 2022 | 0.26639 | 0.00043386 | Sustained | FALSE | FALSE | TMED_Event | 637
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 721 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 718116 | keep | 0 | Apr | 2022 | 0.48911 | 0.00049107 | Sustained | FALSE | FALSE | TMED_Event | 721
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 325 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 323700 | keep | 0 | Apr | 2022 | 0.22047 | 0.00022136 | Sustained | FALSE | FALSE | TMED_Event | 325
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 600 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 597600 | keep | 0 | Apr | 2022 | 0.40702 | 0.00040866 | Sustained | FALSE | FALSE | TMED_Event | 600
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 267 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL LLEVA LA CARGA DEL 1422-03, 1422-04 Y 90% DEL 1422-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 265932 | keep | 0 | Apr | 2022 | 0.18113 | 0.00018185 | Sustained | FALSE | FALSE | TMED_Event | 267
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:19 | 621 | 016:36 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 996 | 2022-04-06 | 618516 | keep | 0 | Apr | 2022 | 0.42127 | 0.00042296 | Sustained | FALSE | FALSE | TMED_Event | 621
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:19 | 2203 | 014:36 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 876 | 2022-04-06 | 1929828 | keep | 0 | Apr | 2022 | 1.3144 | 0.0015005 | Sustained | FALSE | FALSE | TMED_Event | 2203
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:22 | 246 | 010:39 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 639 | 2022-04-06 | 157194 | keep | 0 | Apr | 2022 | 0.10706 | 0.00016755 | Sustained | FALSE | FALSE | TMED_Event | 246
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 07:22 | 9 | 010:39 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 639 | 2022-04-06 | 5751 | keep | 0 | Apr | 2022 | 0.003917 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:35 | 601 | 014:52 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 892 | 2022-04-06 | 536092 | keep | 0 | Apr | 2022 | 0.36513 | 0.00040934 | Sustained | FALSE | FALSE | TMED_Event | 601
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:35 | 640 | 014:52 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 892 | 2022-04-06 | 570880 | keep | 0 | Apr | 2022 | 0.38882 | 0.0004359 | Sustained | FALSE | FALSE | TMED_Event | 640
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:35 | 1699 | 014:52 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 892 | 2022-04-06 | 1515508 | keep | 0 | Apr | 2022 | 1.0322 | 0.0011572 | Sustained | FALSE | FALSE | TMED_Event | 1699
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:35 | 892 | 014:52 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL LLEVA 60% DEL 1301-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 892 | 2022-04-06 | 795664 | keep | 0 | Apr | 2022 | 0.54192 | 0.00060754 | Sustained | FALSE | FALSE | TMED_Event | 892
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:35 | 1066 | 014:52 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 892 | 2022-04-06 | 950872 | keep | 0 | Apr | 2022 | 0.64763 | 0.00072605 | Sustained | FALSE | FALSE | TMED_Event | 1066
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:24 | 34 | 055:41 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3341 | 2022-04-06 | 113594 | keep | 0 | Apr | 2022 | 0.077368 | 2.3157e-05 | Sustained | FALSE | FALSE | TMED_Event | 34
BAYAMON | 2022-04-06 20:43 | 2022-04-07 22:52 | 19 | 026:09 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1569 | 2022-04-06 | 29811 | keep | 0 | Apr | 2022 | 0.020304 | 1.2941e-05 | Sustained | FALSE | FALSE | TMED_Event | 19
BAYAMON | 2022-04-06 20:43 | 2022-04-08 04:35 | 534 | 031:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1912 | 2022-04-06 | 1021008 | keep | 0 | Apr | 2022 | 0.6954 | 0.0003637 | Sustained | FALSE | FALSE | TMED_Event | 534
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:10 | 790 | 055:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3327 | 2022-04-06 | 2628330 | keep | 0 | Apr | 2022 | 1.7901 | 0.00053807 | Sustained | FALSE | FALSE | TMED_Event | 790
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:53 | 193 | 027:10 | T | LINEA DE TRANSMISION | APAGON GENERAL EL 80% DEL 1519-03 ESTA POR EL 1910-01 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1630 | 2022-04-06 | 314590 | keep | 0 | Apr | 2022 | 0.21427 | 0.00013145 | Sustained | FALSE | FALSE | TMED_Event | 193
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:10 | 433 | 055:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3327 | 2022-04-06 | 1440591 | keep | 0 | Apr | 2022 | 0.98118 | 0.00029491 | Sustained | FALSE | FALSE | TMED_Event | 433
BAYAMON | 2022-04-06 20:43 | 2022-04-08 04:35 | 558 | 031:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1912 | 2022-04-06 | 1066896 | keep | 0 | Apr | 2022 | 0.72666 | 0.00038005 | Sustained | FALSE | FALSE | TMED_Event | 558
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:09 | 514 | 015:26 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 926 | 2022-04-06 | 475964 | keep | 0 | Apr | 2022 | 0.32418 | 0.00035008 | Sustained | FALSE | FALSE | TMED_Event | 514
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:09 | 681 | 015:26 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 926 | 2022-04-06 | 630606 | keep | 0 | Apr | 2022 | 0.4295 | 0.00046383 | Sustained | FALSE | FALSE | TMED_Event | 681
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:09 | 752 | 015:26 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 926 | 2022-04-06 | 696352 | keep | 0 | Apr | 2022 | 0.47428 | 0.00051218 | Sustained | FALSE | FALSE | TMED_Event | 752
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:09 | 68 | 015:26 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 926 | 2022-04-06 | 62968 | keep | 0 | Apr | 2022 | 0.042887 | 4.6314e-05 | Sustained | FALSE | FALSE | TMED_Event | 68
BAYAMON | 2022-04-06 20:43 | 2022-04-08 04:36 | 271 | 031:53 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1913 | 2022-04-06 | 518423 | keep | 0 | Apr | 2022 | 0.3531 | 0.00018458 | Sustained | FALSE | FALSE | TMED_Event | 271
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:08 | 74 | 036:25 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1529-11 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2185 | 2022-04-06 | 161690 | keep | 0 | Apr | 2022 | 0.11013 | 5.0401e-05 | Sustained | FALSE | FALSE | TMED_Event | 74
BAYAMON | 2022-04-06 20:43 | 2022-04-07 04:37 | 771 | 007:54 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 474 | 2022-04-06 | 365454 | keep | 0 | Apr | 2022 | 0.24891 | 0.00052512 | Sustained | FALSE | FALSE | TMED_Event | 771
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:48 | 946 | 010:05 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 1525-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 605 | 2022-04-06 | 572330 | keep | 0 | Apr | 2022 | 0.38981 | 0.00064432 | Sustained | FALSE | FALSE | TMED_Event | 946
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:47 | 590 | 010:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 604 | 2022-04-06 | 356360 | keep | 0 | Apr | 2022 | 0.24272 | 0.00040185 | Sustained | FALSE | FALSE | TMED_Event | 590
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:48 | 1860 | 010:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 605 | 2022-04-06 | 1125300 | keep | 0 | Apr | 2022 | 0.76644 | 0.0012668 | Sustained | FALSE | FALSE | TMED_Event | 1860
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:48 | 937 | 010:05 | T | LINEA DE TRANSMISION | APAGON GENERAL LLEVA LA CARGA DEL 1525-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 605 | 2022-04-06 | 566885 | keep | 0 | Apr | 2022 | 0.3861 | 0.00063819 | Sustained | FALSE | FALSE | TMED_Event | 937
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 727 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 463099 | keep | 0 | Apr | 2022 | 0.31541 | 0.00049516 | Sustained | FALSE | FALSE | TMED_Event | 727
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 1420 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 904540 | keep | 0 | Apr | 2022 | 0.61608 | 0.00096716 | Sustained | FALSE | FALSE | TMED_Event | 1420
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 290 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 184730 | keep | 0 | Apr | 2022 | 0.12582 | 0.00019752 | Sustained | FALSE | FALSE | TMED_Event | 290
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 610 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 388570 | keep | 0 | Apr | 2022 | 0.26465 | 0.00041547 | Sustained | FALSE | FALSE | TMED_Event | 610
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 842 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 536354 | keep | 0 | Apr | 2022 | 0.36531 | 0.00057348 | Sustained | FALSE | FALSE | TMED_Event | 842
BAYAMON | 2022-04-06 20:43 | 2022-04-09 11:49 | 1370 | 063:06 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3786 | 2022-04-06 | 5186820 | keep | 0 | Apr | 2022 | 3.5327 | 0.0009331 | Sustained | FALSE | FALSE | TMED_Event | 1370
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:08 | 1984 | 036:25 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2185 | 2022-04-06 | 4335040 | keep | 0 | Apr | 2022 | 2.9526 | 0.0013513 | Sustained | FALSE | FALSE | TMED_Event | 1984
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:09 | 199 | 036:26 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2186 | 2022-04-06 | 435014 | keep | 0 | Apr | 2022 | 0.29629 | 0.00013554 | Sustained | FALSE | FALSE | TMED_Event | 199
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:09 | 1802 | 036:26 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL LLEVA 60% 1346-2 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2186 | 2022-04-06 | 3939172 | keep | 0 | Apr | 2022 | 2.683 | 0.0012273 | Sustained | FALSE | FALSE | TMED_Event | 1802
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 437 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL CARGA POR EL 1530-07 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 278369 | keep | 0 | Apr | 2022 | 0.1896 | 0.00029764 | Sustained | FALSE | FALSE | TMED_Event | 437
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 643 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL LLEVA LA CARGA DEL 1526-02 Y 1530-06 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 409591 | keep | 0 | Apr | 2022 | 0.27897 | 0.00043794 | Sustained | FALSE | FALSE | TMED_Event | 643
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 1085 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 691145 | keep | 0 | Apr | 2022 | 0.47074 | 0.00073899 | Sustained | FALSE | FALSE | TMED_Event | 1085
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 1310 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 834470 | keep | 0 | Apr | 2022 | 0.56835 | 0.00089224 | Sustained | FALSE | FALSE | TMED_Event | 1310
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:20 | 411 | 010:37 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 637 | 2022-04-06 | 261807 | keep | 0 | Apr | 2022 | 0.17832 | 0.00027993 | Sustained | FALSE | FALSE | TMED_Event | 411
BAYAMON | 2022-04-06 20:43 | 2022-04-07 05:13 | 427 | 008:30 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 510 | 2022-04-06 | 217770 | keep | 0 | Apr | 2022 | 0.14832 | 0.00029083 | Sustained | FALSE | FALSE | TMED_Event | 427
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:49 | 427 | 010:06 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 606 | 2022-04-06 | 258762 | keep | 0 | Apr | 2022 | 0.17624 | 0.00029083 | Sustained | FALSE | FALSE | TMED_Event | 427
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:56 | 164 | 010:13 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 613 | 2022-04-06 | 100532 | keep | 0 | Apr | 2022 | 0.068472 | 0.0001117 | Sustained | FALSE | FALSE | TMED_Event | 164
BAYAMON | 2022-04-06 20:43 | 2022-04-07 06:53 | 353 | 010:10 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 610 | 2022-04-06 | 215330 | keep | 0 | Apr | 2022 | 0.14666 | 0.00024043 | Sustained | FALSE | FALSE | TMED_Event | 353
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:46 | 763 | 017:03 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 1602-05 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1023 | 2022-04-06 | 780549 | keep | 0 | Apr | 2022 | 0.53163 | 0.00051968 | Sustained | FALSE | FALSE | TMED_Event | 763
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 04:47 | 27 | 008:04 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 1203-01 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 484 | 2022-04-06 | 13068 | keep | 0 | Apr | 2022 | 0.0089006 | 1.839e-05 | Sustained | FALSE | FALSE | TMED_Event | 27
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:46 | 1259 | 017:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600218 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1023 | 2022-04-06 | 1287957 | keep | 0 | Apr | 2022 | 0.87722 | 0.0008575 | Sustained | FALSE | FALSE | TMED_Event | 1259
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:46 | 1051 | 017:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600219 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1023 | 2022-04-06 | 1075173 | keep | 0 | Apr | 2022 | 0.7323 | 0.00071583 | Sustained | FALSE | FALSE | TMED_Event | 1051
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:46 | 188 | 017:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1023 | 2022-04-06 | 192324 | keep | 0 | Apr | 2022 | 0.13099 | 0.00012805 | Sustained | FALSE | FALSE | TMED_Event | 188
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 09:20 | 1862 | 036:37 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2197 | 2022-04-06 | 4090814 | keep | 0 | Apr | 2022 | 2.7862 | 0.0012682 | Sustained | FALSE | FALSE | TMED_Event | 1862
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 09:20 | 1613 | 036:37 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2197 | 2022-04-06 | 3543761 | keep | 0 | Apr | 2022 | 2.4136 | 0.0010986 | Sustained | FALSE | FALSE | TMED_Event | 1613
SAN JUAN | 2022-04-06 20:43 | 2022-04-08 09:20 | 1448 | 036:37 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2197 | 2022-04-06 | 3181256 | keep | 0 | Apr | 2022 | 2.1667 | 0.00098623 | Sustained | FALSE | FALSE | TMED_Event | 1448
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 1 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 712 | keep | 0 | Apr | 2022 | 0.00048494 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 1 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 712 | keep | 0 | Apr | 2022 | 0.00048494 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 1 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 712 | keep | 0 | Apr | 2022 | 0.00048494 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 1 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 712 | keep | 0 | Apr | 2022 | 0.00048494 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 1 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 712 | keep | 0 | Apr | 2022 | 0.00048494 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 9 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA X 1615-09 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 6408 | keep | 0 | Apr | 2022 | 0.0043645 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 6 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 4272 | keep | 0 | Apr | 2022 | 0.0029096 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 23:06 | 1 | 026:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1583 | 2022-04-06 | 1583 | keep | 0 | Apr | 2022 | 0.0010782 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 23:06 | 1 | 026:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1583 | 2022-04-06 | 1583 | keep | 0 | Apr | 2022 | 0.0010782 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 12 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 8544 | keep | 0 | Apr | 2022 | 0.0058193 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:43 | 3 | 015:00 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 900 | 2022-04-06 | 2700 | keep | 0 | Apr | 2022 | 0.001839 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 7 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA X 1615-06 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 4984 | keep | 0 | Apr | 2022 | 0.0033946 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:43 | 1 | 015:00 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 900 | 2022-04-06 | 900 | keep | 0 | Apr | 2022 | 0.00061299 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 08:35 | 4 | 011:52 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA X 1616-15 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 712 | 2022-04-06 | 2848 | keep | 0 | Apr | 2022 | 0.0019398 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 11:43 | 4 | 015:00 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 900 | 2022-04-06 | 3600 | keep | 0 | Apr | 2022 | 0.0024519 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:21 | 331 | 054:38 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3278 | 2022-04-06 | 1085018 | keep | 0 | Apr | 2022 | 0.739 | 0.00022544 | Sustained | FALSE | FALSE | TMED_Event | 331
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:22 | 1132 | 054:39 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3279 | 2022-04-06 | 3711828 | keep | 0 | Apr | 2022 | 2.5281 | 0.000771 | Sustained | FALSE | FALSE | TMED_Event | 1132
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:22 | 234 | 054:39 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3279 | 2022-04-06 | 767286 | keep | 0 | Apr | 2022 | 0.5226 | 0.00015938 | Sustained | FALSE | FALSE | TMED_Event | 234
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:19 | 2179 | 054:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3276 | 2022-04-06 | 7138404 | keep | 0 | Apr | 2022 | 4.8619 | 0.0014841 | Sustained | FALSE | FALSE | TMED_Event | 2179
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:20 | 234 | 054:37 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3277 | 2022-04-06 | 766818 | keep | 0 | Apr | 2022 | 0.52228 | 0.00015938 | Sustained | FALSE | FALSE | TMED_Event | 234
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 14:31 | 36 | 017:48 | T | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR. INTERRUPTOR 1620-03 LLEVA 1620-01 Y 95% 1336-10 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1068 | 2022-04-06 | 38448 | keep | 0 | Apr | 2022 | 0.026187 | 2.4519e-05 | Sustained | FALSE | FALSE | TMED_Event | 36
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 14:29 | 3718 | 017:46 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1066 | 2022-04-06 | 3963388 | keep | 0 | Apr | 2022 | 2.6994 | 0.0025323 | Sustained | FALSE | FALSE | TMED_Event | 3718
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 14:31 | 1073 | 017:48 | T | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR. INTERRUPTOR 1620-03 LLEVA 1620-01 Y 95% 1336-10 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1068 | 2022-04-06 | 1145964 | keep | 0 | Apr | 2022 | 0.78051 | 0.00073082 | Sustained | FALSE | FALSE | TMED_Event | 1073
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 14:30 | 172 | 017:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1067 | 2022-04-06 | 183524 | keep | 0 | Apr | 2022 | 0.125 | 0.00011715 | Sustained | FALSE | FALSE | TMED_Event | 172
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 14:30 | 1615 | 017:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1067 | 2022-04-06 | 1723205 | keep | 0 | Apr | 2022 | 1.1737 | 0.0011 | Sustained | FALSE | FALSE | TMED_Event | 1615
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 02:36 | 5668 | 053:53 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3233 | 2022-04-06 | 18324644 | keep | 0 | Apr | 2022 | 12.4808 | 0.0038604 | Sustained | FALSE | FALSE | TMED_Event | 5668
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 02:36 | 1026 | 053:53 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3233 | 2022-04-06 | 3317058 | keep | 0 | Apr | 2022 | 2.2592 | 0.0006988 | Sustained | FALSE | FALSE | TMED_Event | 1026
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:01 | 3046 | 054:18 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3258 | 2022-04-06 | 9923868 | keep | 0 | Apr | 2022 | 6.7591 | 0.0020746 | Sustained | FALSE | FALSE | TMED_Event | 3046
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:01 | 2891 | 054:18 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3258 | 2022-04-06 | 9418878 | keep | 0 | Apr | 2022 | 6.4152 | 0.001969 | Sustained | FALSE | FALSE | TMED_Event | 2891
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:18 | 99 | 054:35 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3275 | 2022-04-06 | 324225 | keep | 0 | Apr | 2022 | 0.22083 | 6.7428e-05 | Sustained | FALSE | FALSE | TMED_Event | 99
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:18 | 31 | 054:35 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA X 1646-06 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3275 | 2022-04-06 | 101525 | keep | 0 | Apr | 2022 | 0.069148 | 2.1114e-05 | Sustained | FALSE | FALSE | TMED_Event | 31
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:18 | 1474 | 054:35 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA X 1647-06 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3275 | 2022-04-06 | 4827350 | keep | 0 | Apr | 2022 | 3.2879 | 0.0010039 | Sustained | FALSE | FALSE | TMED_Event | 1474
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:02 | 2053 | 054:19 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3259 | 2022-04-06 | 6690727 | keep | 0 | Apr | 2022 | 4.557 | 0.0013983 | Sustained | FALSE | FALSE | TMED_Event | 2053
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 03:02 | 61 | 054:19 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3259 | 2022-04-06 | 198799 | keep | 0 | Apr | 2022 | 0.1354 | 4.1547e-05 | Sustained | FALSE | FALSE | TMED_Event | 61
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:25 | 614 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 2051988 | keep | 0 | Apr | 2022 | 1.3976 | 0.00041819 | Sustained | FALSE | FALSE | TMED_Event | 614
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:25 | 770 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 2573340 | keep | 0 | Apr | 2022 | 1.7527 | 0.00052444 | Sustained | FALSE | FALSE | TMED_Event | 770
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:25 | 1271 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 4247682 | keep | 0 | Apr | 2022 | 2.8931 | 0.00086567 | Sustained | FALSE | FALSE | TMED_Event | 1271
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:25 | 247 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 825474 | keep | 0 | Apr | 2022 | 0.56223 | 0.00016823 | Sustained | FALSE | FALSE | TMED_Event | 247
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 02:19 | 165 | 053:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600214 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3216 | 2022-04-06 | 530640 | keep | 0 | Apr | 2022 | 0.36142 | 0.00011238 | Sustained | FALSE | FALSE | TMED_Event | 165
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 02:19 | 437 | 053:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600224 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3216 | 2022-04-06 | 1405392 | keep | 0 | Apr | 2022 | 0.95721 | 0.00029764 | Sustained | FALSE | FALSE | TMED_Event | 437
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 02:19 | 363 | 053:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600225 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3216 | 2022-04-06 | 1167408 | keep | 0 | Apr | 2022 | 0.79512 | 0.00024724 | Sustained | FALSE | FALSE | TMED_Event | 363
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 04:25 | 14 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA X 1118-07 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 46788 | keep | 0 | Apr | 2022 | 0.031867 | 9.5353e-06 | Sustained | FALSE | FALSE | TMED_Event | 14
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 02:19 | 2245 | 053:36 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 1657-02 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3216 | 2022-04-06 | 7219920 | keep | 0 | Apr | 2022 | 4.9175 | 0.0015291 | Sustained | FALSE | FALSE | TMED_Event | 2245
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 02:20 | 1 | 053:37 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3217 | 2022-04-06 | 3217 | keep | 0 | Apr | 2022 | 0.0021911 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-06 20:43 | 2022-04-09 02:35 | 1 | 053:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3232 | 2022-04-06 | 3232 | keep | 0 | Apr | 2022 | 0.0022013 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:28 | 1 | 026:45 | S | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1605 | 2022-04-06 | 1605 | keep | 0 | Apr | 2022 | 0.0010932 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:28 | 81 | 026:45 | S | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1605 | 2022-04-06 | 130005 | keep | 0 | Apr | 2022 | 0.088546 | 5.5169e-05 | Sustained | FALSE | FALSE | TMED_Event | 81
BAYAMON | 2022-04-06 20:43 | 2022-04-08 08:51 | 1633 | 036:08 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2168 | 2022-04-06 | 3540344 | keep | 0 | Apr | 2022 | 2.4113 | 0.0011122 | Sustained | FALSE | FALSE | TMED_Event | 1633
BAYAMON | 2022-04-06 20:43 | 2022-04-08 08:50 | 1243 | 036:07 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2167 | 2022-04-06 | 2693581 | keep | 0 | Apr | 2022 | 1.8346 | 0.0008466 | Sustained | FALSE | FALSE | TMED_Event | 1243
BAYAMON | 2022-04-06 20:43 | 2022-04-09 05:07 | 1300 | 056:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3384 | 2022-04-06 | 4399200 | keep | 0 | Apr | 2022 | 2.9963 | 0.00088542 | Sustained | FALSE | FALSE | TMED_Event | 1300
BAYAMON | 2022-04-06 20:43 | 2022-04-09 05:07 | 41 | 056:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3384 | 2022-04-06 | 138744 | keep | 0 | Apr | 2022 | 0.094498 | 2.7925e-05 | Sustained | FALSE | FALSE | TMED_Event | 41
BAYAMON | 2022-04-06 20:43 | 2022-04-08 07:22 | 1399 | 034:39 | T | LINEA DE TRANSMISION | APAGON GENERAL - CARGA TRANSFERIDA AL 1704-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2079 | 2022-04-06 | 2908521 | keep | 0 | Apr | 2022 | 1.981 | 0.00095285 | Sustained | FALSE | FALSE | TMED_Event | 1399
BAYAMON | 2022-04-06 20:43 | 2022-04-08 07:22 | 302 | 034:39 | T | LINEA DE TRANSMISION | APAGON GENERAL - LLEVA LA CARGA DEL 1704-01 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2079 | 2022-04-06 | 627858 | keep | 0 | Apr | 2022 | 0.42763 | 0.00020569 | Sustained | FALSE | FALSE | TMED_Event | 302
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:41 | 1048 | 036:58 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2218 | 2022-04-06 | 2324464 | keep | 0 | Apr | 2022 | 1.5832 | 0.00071379 | Sustained | FALSE | FALSE | TMED_Event | 1048
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:41 | 573 | 036:58 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2218 | 2022-04-06 | 1270914 | keep | 0 | Apr | 2022 | 0.86561 | 0.00039027 | Sustained | FALSE | FALSE | TMED_Event | 573
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:41 | 1313 | 036:58 | T | LINEA DE TRANSMISION | APAGON GENERAL - CARGA TRANSFERIDA AL 1704-04 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2218 | 2022-04-06 | 2912234 | keep | 0 | Apr | 2022 | 1.9835 | 0.00089428 | Sustained | FALSE | FALSE | TMED_Event | 1313
BAYAMON | 2022-04-06 20:43 | 2022-04-09 05:07 | 478 | 056:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3384 | 2022-04-06 | 1617552 | keep | 0 | Apr | 2022 | 1.1017 | 0.00032556 | Sustained | FALSE | FALSE | TMED_Event | 478
BAYAMON | 2022-04-06 20:43 | 2022-04-09 05:07 | 573 | 056:24 | T | LINEA DE TRANSMISION | APAGON GENERAL - LLEVA LA CARGA DEL 1704-05 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3384 | 2022-04-06 | 1939032 | keep | 0 | Apr | 2022 | 1.3207 | 0.00039027 | Sustained | FALSE | FALSE | TMED_Event | 573
BAYAMON | 2022-04-06 20:43 | 2022-04-09 05:07 | 949 | 056:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3384 | 2022-04-06 | 3211416 | keep | 0 | Apr | 2022 | 2.1873 | 0.00064636 | Sustained | FALSE | FALSE | TMED_Event | 949
BAYAMON | 2022-04-06 20:43 | 2022-04-09 05:07 | 67 | 056:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3384 | 2022-04-06 | 226728 | keep | 0 | Apr | 2022 | 0.15442 | 4.5633e-05 | Sustained | FALSE | FALSE | TMED_Event | 67
BAYAMON | 2022-04-06 20:43 | 2022-04-09 05:07 | 637 | 056:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3384 | 2022-04-06 | 2155608 | keep | 0 | Apr | 2022 | 1.4682 | 0.00043386 | Sustained | FALSE | FALSE | TMED_Event | 637
BAYAMON | 2022-04-06 20:43 | 2022-04-08 07:10 | 959 | 034:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2067 | 2022-04-06 | 1982253 | keep | 0 | Apr | 2022 | 1.3501 | 0.00065317 | Sustained | FALSE | FALSE | TMED_Event | 959
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:47 | 1382 | 037:04 | T | LINEA DE TRANSMISION | APAGON GENERAL - LLEVA LA CARGA DEL 1706-03 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2224 | 2022-04-06 | 3073568 | keep | 0 | Apr | 2022 | 2.0934 | 0.00094127 | Sustained | FALSE | FALSE | TMED_Event | 1382
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:47 | 663 | 037:04 | T | LINEA DE TRANSMISION | APAGON GENERAL - CARGA TRANASFERIDA AL 1706-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2224 | 2022-04-06 | 1474512 | keep | 0 | Apr | 2022 | 1.0043 | 0.00045157 | Sustained | FALSE | FALSE | TMED_Event | 663
BAYAMON | 2022-04-06 20:43 | 2022-04-09 00:21 | 1935 | 051:38 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3098 | 2022-04-06 | 5994630 | keep | 0 | Apr | 2022 | 4.0829 | 0.0013179 | Sustained | FALSE | FALSE | TMED_Event | 1935
BAYAMON | 2022-04-06 20:43 | 2022-04-09 00:21 | 3 | 051:38 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3098 | 2022-04-06 | 9294 | keep | 0 | Apr | 2022 | 0.0063301 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
BAYAMON | 2022-04-06 20:43 | 2022-04-09 00:22 | 61 | 051:39 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3099 | 2022-04-06 | 189039 | keep | 0 | Apr | 2022 | 0.12875 | 4.1547e-05 | Sustained | FALSE | FALSE | TMED_Event | 61
BAYAMON | 2022-04-06 20:43 | 2022-04-09 00:22 | 1501 | 051:39 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3099 | 2022-04-06 | 4651599 | keep | 0 | Apr | 2022 | 3.1682 | 0.0010223 | Sustained | FALSE | FALSE | TMED_Event | 1501
BAYAMON | 2022-04-06 20:43 | 2022-04-09 00:22 | 546 | 051:39 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3099 | 2022-04-06 | 1692054 | keep | 0 | Apr | 2022 | 1.1525 | 0.00037188 | Sustained | FALSE | FALSE | TMED_Event | 546
BAYAMON | 2022-04-06 20:43 | 2022-04-09 00:21 | 707 | 051:38 | T | LINEA DE TRANSMISION | APAGON GENERAL PARTE POR 1707-01 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3098 | 2022-04-06 | 2190286 | keep | 0 | Apr | 2022 | 1.4918 | 0.00048153 | Sustained | FALSE | FALSE | TMED_Event | 707
BAYAMON | 2022-04-06 20:43 | 2022-04-09 00:46 | 1498 | 052:03 | T | LINEA DE TRANSMISION | APAGON GENERAL 1708-03 LLEVA PARTE DEL 1708-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3123 | 2022-04-06 | 4678254 | keep | 0 | Apr | 2022 | 3.1863 | 0.0010203 | Sustained | FALSE | FALSE | TMED_Event | 1498
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:45 | 1221 | 027:02 | T | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1622 | 2022-04-06 | 1980462 | keep | 0 | Apr | 2022 | 1.3489 | 0.00083162 | Sustained | FALSE | FALSE | TMED_Event | 1221
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:19 | 1100 | 036:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2196 | 2022-04-06 | 2415600 | keep | 0 | Apr | 2022 | 1.6453 | 0.0007492 | Sustained | FALSE | FALSE | TMED_Event | 1100
BAYAMON | 2022-04-06 20:43 | 2022-04-09 03:40 | 2402 | 054:57 | T | LINEA DE TRANSMISION | APAGON GENERAL 1709-02 LLEVA 1720-08 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3297 | 2022-04-06 | 7919394 | keep | 0 | Apr | 2022 | 5.3939 | 0.001636 | Sustained | FALSE | FALSE | TMED_Event | 2402
BAYAMON | 2022-04-06 20:43 | 2022-04-08 20:57 | 1533 | 048:14 | T | LINEA DE TRANSMISION | APAGON GENERAL 50% X 1909-07 Y LLEVA 1709-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2894 | 2022-04-06 | 4436502 | keep | 0 | Apr | 2022 | 3.0217 | 0.0010441 | Sustained | FALSE | FALSE | TMED_Event | 1533
BAYAMON | 2022-04-06 20:43 | 2022-04-08 20:57 | 2364 | 048:14 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA TRANSFERIDA AL 1709-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2894 | 2022-04-06 | 6841416 | keep | 0 | Apr | 2022 | 4.6597 | 0.0016101 | Sustained | FALSE | FALSE | TMED_Event | 2364
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:46 | 5809 | 016:03 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 963 | 2022-04-06 | 5594067 | keep | 0 | Apr | 2022 | 3.8101 | 0.0039565 | Sustained | FALSE | FALSE | TMED_Event | 5809
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:46 | 3941 | 016:03 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 963 | 2022-04-06 | 3795183 | keep | 0 | Apr | 2022 | 2.5849 | 0.0026842 | Sustained | FALSE | FALSE | TMED_Event | 3941
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:46 | 3871 | 016:03 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 963 | 2022-04-06 | 3727773 | keep | 0 | Apr | 2022 | 2.539 | 0.0026365 | Sustained | FALSE | FALSE | TMED_Event | 3871
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:46 | 5191 | 016:03 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 963 | 2022-04-06 | 4998933 | keep | 0 | Apr | 2022 | 3.4048 | 0.0035356 | Sustained | FALSE | FALSE | TMED_Event | 5191
BAYAMON | 2022-04-06 20:43 | 2022-04-08 12:21 | 1588 | 039:38 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2378 | 2022-04-06 | 3776264 | keep | 0 | Apr | 2022 | 2.572 | 0.0010816 | Sustained | FALSE | FALSE | TMED_Event | 1588
BAYAMON | 2022-04-06 20:43 | 2022-04-09 11:52 | 723 | 063:09 | T | LINEA DE TRANSMISION | APAGON GENERAL LLEVA 1711-05 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3789 | 2022-04-06 | 2739447 | keep | 0 | Apr | 2022 | 1.8658 | 0.00049243 | Sustained | FALSE | FALSE | TMED_Event | 723
BAYAMON | 2022-04-06 20:43 | 2022-04-09 06:14 | 13 | 057:31 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3451 | 2022-04-06 | 44863 | keep | 0 | Apr | 2022 | 0.030556 | 8.8542e-06 | Sustained | FALSE | FALSE | TMED_Event | 13
BAYAMON | 2022-04-06 20:43 | 2022-04-08 19:48 | 1983 | 047:05 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA TRANSFERIDA AL 1801-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2825 | 2022-04-06 | 5601975 | keep | 0 | Apr | 2022 | 3.8155 | 0.0013506 | Sustained | FALSE | FALSE | TMED_Event | 1983
BAYAMON | 2022-04-06 20:43 | 2022-04-09 11:52 | 1976 | 063:09 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA TRANSFERIDA AL 1711-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3789 | 2022-04-06 | 7487064 | keep | 0 | Apr | 2022 | 5.0994 | 0.0013458 | Sustained | FALSE | FALSE | TMED_Event | 1976
BAYAMON | 2022-04-06 20:43 | 2022-04-07 21:17 | 5252 | 024:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1474 | 2022-04-06 | 7741448 | keep | 0 | Apr | 2022 | 5.2727 | 0.0035771 | Sustained | FALSE | FALSE | TMED_Event | 5252
BAYAMON | 2022-04-06 20:43 | 2022-04-09 06:15 | 77 | 057:32 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3452 | 2022-04-06 | 265804 | keep | 0 | Apr | 2022 | 0.18104 | 5.2444e-05 | Sustained | FALSE | FALSE | TMED_Event | 77
BAYAMON | 2022-04-06 20:43 | 2022-04-08 17:59 | 5961 | 045:16 | T | LINEA DE TRANSMISION | APAGON GENERAL LLEVA 95% 1717-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2716 | 2022-04-06 | 16190076 | keep | 0 | Apr | 2022 | 11.027 | 0.00406 | Sustained | FALSE | FALSE | TMED_Event | 5961
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:25 | 1408 | 014:42 | T | LINEA DE TRANSMISION | APAGON GENERAL - LLEVA LA CARGA DEL 1714-03 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 882 | 2022-04-06 | 1241856 | keep | 0 | Apr | 2022 | 0.84582 | 0.00095898 | Sustained | FALSE | FALSE | TMED_Event | 1408
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:25 | 455 | 014:42 | T | LINEA DE TRANSMISION | APAGON GENERAL - CARGA TRANSFERIDA AL 1714-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 882 | 2022-04-06 | 401310 | keep | 0 | Apr | 2022 | 0.27333 | 0.0003099 | Sustained | FALSE | FALSE | TMED_Event | 455
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:25 | 878 | 014:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 882 | 2022-04-06 | 774396 | keep | 0 | Apr | 2022 | 0.52744 | 0.000598 | Sustained | FALSE | FALSE | TMED_Event | 878
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:28 | 98 | 026:45 | S | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1605 | 2022-04-06 | 157290 | keep | 0 | Apr | 2022 | 0.10713 | 6.6747e-05 | Sustained | FALSE | FALSE | TMED_Event | 98
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:28 | 74 | 026:45 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1605 | 2022-04-06 | 118770 | keep | 0 | Apr | 2022 | 0.080894 | 5.0401e-05 | Sustained | FALSE | FALSE | TMED_Event | 74
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:28 | 776 | 026:45 | S | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1605 | 2022-04-06 | 1245480 | keep | 0 | Apr | 2022 | 0.84829 | 0.00052853 | Sustained | FALSE | FALSE | TMED_Event | 776
BAYAMON | 2022-04-06 20:43 | 2022-04-07 18:54 | 450 | 022:11 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1331 | 2022-04-06 | 598950 | keep | 0 | Apr | 2022 | 0.40794 | 0.00030649 | Sustained | FALSE | FALSE | TMED_Event | 450
BAYAMON | 2022-04-06 20:43 | 2022-04-07 18:54 | 651 | 022:11 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1331 | 2022-04-06 | 866481 | keep | 0 | Apr | 2022 | 0.59016 | 0.00044339 | Sustained | FALSE | FALSE | TMED_Event | 651
BAYAMON | 2022-04-06 20:43 | 2022-04-07 21:49 | 1812 | 025:06 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1506 | 2022-04-06 | 2728872 | keep | 0 | Apr | 2022 | 1.8586 | 0.0012341 | Sustained | FALSE | FALSE | TMED_Event | 1812
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:11 | 4100 | 026:28 | P | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL. INTERRUPTOR 1717-01 10% DE SU CARGA POR 1806-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1588 | 2022-04-06 | 6510800 | keep | 0 | Apr | 2022 | 4.4345 | 0.0027925 | Sustained | FALSE | FALSE | TMED_Event | 4100
BAYAMON | 2022-04-06 20:43 | 2022-04-08 17:59 | 911 | 045:16 | T | LINEA DE TRANSMISION | APAGON GENERAL SE CERRO INTERRUPTOR 1713-05 QUE ESTA LLEVANDO EL 95% DE LA CARGA DEL 1717-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2716 | 2022-04-06 | 2474276 | keep | 0 | Apr | 2022 | 1.6852 | 0.00062048 | Sustained | FALSE | FALSE | TMED_Event | 911
BAYAMON | 2022-04-06 20:43 | 2022-04-07 18:11 | 4431 | 021:28 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1288 | 2022-04-06 | 5707128 | keep | 0 | Apr | 2022 | 3.8871 | 0.0030179 | Sustained | FALSE | FALSE | TMED_Event | 4431
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:11 | 1362 | 026:28 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL. INTERRUPTOR 1717-04 LLEVA 20% 1716-02 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1588 | 2022-04-06 | 2162856 | keep | 0 | Apr | 2022 | 1.4731 | 0.00092765 | Sustained | FALSE | FALSE | TMED_Event | 1362
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:11 | 341 | 026:28 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL. | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1588 | 2022-04-06 | 541508 | keep | 0 | Apr | 2022 | 0.36882 | 0.00023225 | Sustained | FALSE | FALSE | TMED_Event | 341
BAYAMON | 2022-04-06 20:43 | 2022-04-07 22:25 | 1210 | 025:42 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1542 | 2022-04-06 | 1865820 | keep | 0 | Apr | 2022 | 1.2708 | 0.00082413 | Sustained | FALSE | FALSE | TMED_Event | 1210
BAYAMON | 2022-04-06 20:43 | 2022-04-07 18:19 | 3438 | 021:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040500000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1296 | 2022-04-06 | 4455648 | keep | 0 | Apr | 2022 | 3.0347 | 0.0023416 | Sustained | FALSE | FALSE | TMED_Event | 3438
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:48 | 2605 | 027:05 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR BKR 1718-03 LLEVA 40% 1710-05 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1625 | 2022-04-06 | 4233125 | keep | 0 | Apr | 2022 | 2.8832 | 0.0017743 | Sustained | FALSE | FALSE | TMED_Event | 2605
BAYAMON | 2022-04-06 20:43 | 2022-04-09 05:06 | 73 | 056:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3383 | 2022-04-06 | 246959 | keep | 0 | Apr | 2022 | 0.1682 | 4.972e-05 | Sustained | FALSE | FALSE | TMED_Event | 73
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:46 | 3597 | 016:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 963 | 2022-04-06 | 3463911 | keep | 0 | Apr | 2022 | 2.3593 | 0.0024499 | Sustained | FALSE | FALSE | TMED_Event | 3597
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:46 | 492 | 016:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 963 | 2022-04-06 | 473796 | keep | 0 | Apr | 2022 | 0.3227 | 0.0003351 | Sustained | FALSE | FALSE | TMED_Event | 492
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:46 | 4028 | 016:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 963 | 2022-04-06 | 3878964 | keep | 0 | Apr | 2022 | 2.6419 | 0.0027435 | Sustained | FALSE | FALSE | TMED_Event | 4028
BAYAMON | 2022-04-06 20:43 | 2022-04-07 12:46 | 2617 | 016:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 963 | 2022-04-06 | 2520171 | keep | 0 | Apr | 2022 | 1.7165 | 0.0017824 | Sustained | FALSE | FALSE | TMED_Event | 2617
BAYAMON | 2022-04-06 20:43 | 2022-04-09 03:40 | 6136 | 054:57 | T | LINEA DE TRANSMISION | APAGON GENERAL SARGA DEL 1720-07 POR 1709-01 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3297 | 2022-04-06 | 20230392 | keep | 0 | Apr | 2022 | 13.7788 | 0.0041792 | Sustained | FALSE | FALSE | TMED_Event | 6136
BAYAMON | 2022-04-06 20:43 | 2022-04-09 03:40 | 1 | 054:57 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR 1709-2 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3297 | 2022-04-06 | 3297 | keep | 0 | Apr | 2022 | 0.0022456 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-09 00:08 | 1514 | 051:25 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3085 | 2022-04-06 | 4670690 | keep | 0 | Apr | 2022 | 3.1812 | 0.0010312 | Sustained | FALSE | FALSE | TMED_Event | 1514
BAYAMON | 2022-04-06 20:43 | 2022-04-09 00:08 | 1105 | 051:25 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3085 | 2022-04-06 | 3408925 | keep | 0 | Apr | 2022 | 2.3218 | 0.00075261 | Sustained | FALSE | FALSE | TMED_Event | 1105
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:10 | 966 | 055:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3327 | 2022-04-06 | 3213882 | keep | 0 | Apr | 2022 | 2.189 | 0.00065794 | Sustained | FALSE | FALSE | TMED_Event | 966
BAYAMON | 2022-04-06 20:43 | 2022-04-08 19:48 | 186 | 047:05 | T | LINEA DE TRANSMISION | APAGON GENERAL LLEVA CARGA 1711-04 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2825 | 2022-04-06 | 525450 | keep | 0 | Apr | 2022 | 0.35788 | 0.00012668 | Sustained | FALSE | FALSE | TMED_Event | 186
BAYAMON | 2022-04-06 20:43 | 2022-04-09 02:38 | 1746 | 053:55 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3235 | 2022-04-06 | 5648310 | keep | 0 | Apr | 2022 | 3.847 | 0.0011892 | Sustained | FALSE | FALSE | TMED_Event | 1746
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:11 | 112 | 055:28 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3328 | 2022-04-06 | 372736 | keep | 0 | Apr | 2022 | 0.25387 | 7.6283e-05 | Sustained | FALSE | FALSE | TMED_Event | 112
BAYAMON | 2022-04-06 20:43 | 2022-04-09 02:17 | 748 | 053:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3214 | 2022-04-06 | 2404072 | keep | 0 | Apr | 2022 | 1.6374 | 0.00050946 | Sustained | FALSE | FALSE | TMED_Event | 748
BAYAMON | 2022-04-06 20:43 | 2022-04-09 02:17 | 33 | 053:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3214 | 2022-04-06 | 106062 | keep | 0 | Apr | 2022 | 0.072238 | 2.2476e-05 | Sustained | FALSE | FALSE | TMED_Event | 33
BAYAMON | 2022-04-06 20:43 | 2022-04-09 03:19 | 67 | 054:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3276 | 2022-04-06 | 219492 | keep | 0 | Apr | 2022 | 0.1495 | 4.5633e-05 | Sustained | FALSE | FALSE | TMED_Event | 67
BAYAMON | 2022-04-06 20:43 | 2022-04-09 03:19 | 1587 | 054:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3276 | 2022-04-06 | 5199012 | keep | 0 | Apr | 2022 | 3.541 | 0.0010809 | Sustained | FALSE | FALSE | TMED_Event | 1587
BAYAMON | 2022-04-06 20:43 | 2022-04-08 23:23 | 521 | 050:40 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3040 | 2022-04-06 | 1583840 | keep | 0 | Apr | 2022 | 1.0787 | 0.00035485 | Sustained | FALSE | FALSE | TMED_Event | 521
BAYAMON | 2022-04-06 20:43 | 2022-04-09 03:19 | 1307 | 054:36 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3276 | 2022-04-06 | 4281732 | keep | 0 | Apr | 2022 | 2.9163 | 0.00089019 | Sustained | FALSE | FALSE | TMED_Event | 1307
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:50 | 3798 | 027:07 | T | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1627 | 2022-04-06 | 6179346 | keep | 0 | Apr | 2022 | 4.2087 | 0.0025868 | Sustained | FALSE | FALSE | TMED_Event | 3798
BAYAMON | 2022-04-06 20:43 | 2022-04-07 21:49 | 4622 | 025:06 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1506 | 2022-04-06 | 6960732 | keep | 0 | Apr | 2022 | 4.7409 | 0.003148 | Sustained | FALSE | FALSE | TMED_Event | 4622
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:51 | 4089 | 027:08 | T | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1628 | 2022-04-06 | 6656892 | keep | 0 | Apr | 2022 | 4.534 | 0.002785 | Sustained | FALSE | FALSE | TMED_Event | 4089
BAYAMON | 2022-04-06 20:43 | 2022-04-08 17:16 | 959 | 044:33 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2673 | 2022-04-06 | 2563407 | keep | 0 | Apr | 2022 | 1.7459 | 0.00065317 | Sustained | FALSE | FALSE | TMED_Event | 959
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:51 | 1297 | 056:08 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3368 | 2022-04-06 | 4368296 | keep | 0 | Apr | 2022 | 2.9752 | 0.00088338 | Sustained | FALSE | FALSE | TMED_Event | 1297
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:51 | 451 | 056:08 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3368 | 2022-04-06 | 1518968 | keep | 0 | Apr | 2022 | 1.0346 | 0.00030717 | Sustained | FALSE | FALSE | TMED_Event | 451
BAYAMON | 2022-04-06 20:43 | 2022-04-08 17:16 | 1264 | 044:33 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2673 | 2022-04-06 | 3378672 | keep | 0 | Apr | 2022 | 2.3012 | 0.0008609 | Sustained | FALSE | FALSE | TMED_Event | 1264
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:51 | 620 | 056:08 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3368 | 2022-04-06 | 2088160 | keep | 0 | Apr | 2022 | 1.4222 | 0.00042228 | Sustained | FALSE | FALSE | TMED_Event | 620
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:26 | 293 | 014:43 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 883 | 2022-04-06 | 258719 | keep | 0 | Apr | 2022 | 0.17621 | 0.00019956 | Sustained | FALSE | FALSE | TMED_Event | 293
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:26 | 315 | 014:43 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 883 | 2022-04-06 | 278145 | keep | 0 | Apr | 2022 | 0.18944 | 0.00021455 | Sustained | FALSE | FALSE | TMED_Event | 315
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:26 | 216 | 014:43 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 883 | 2022-04-06 | 190728 | keep | 0 | Apr | 2022 | 0.1299 | 0.00014712 | Sustained | FALSE | FALSE | TMED_Event | 216
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:26 | 1310 | 014:43 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 883 | 2022-04-06 | 1156730 | keep | 0 | Apr | 2022 | 0.78784 | 0.00089224 | Sustained | FALSE | FALSE | TMED_Event | 1310
BAYAMON | 2022-04-06 20:43 | 2022-04-08 17:57 | 222 | 045:14 | T | LINEA DE TRANSMISION | APAGON GENERAL LLEVA LA CARGA 1909-09 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2714 | 2022-04-06 | 602508 | keep | 0 | Apr | 2022 | 0.41037 | 0.0001512 | Sustained | FALSE | FALSE | TMED_Event | 222
BAYAMON | 2022-04-06 20:43 | 2022-04-07 22:01 | 2466 | 025:18 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1518 | 2022-04-06 | 3743388 | keep | 0 | Apr | 2022 | 2.5496 | 0.0016796 | Sustained | FALSE | FALSE | TMED_Event | 2466
BAYAMON | 2022-04-06 20:43 | 2022-04-08 03:17 | 2435 | 030:34 | T | LINEA DE TRANSMISION | APAGON GENERAL BKR 1909-08 LLEVA 1907-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1834 | 2022-04-06 | 4465790 | keep | 0 | Apr | 2022 | 3.0416 | 0.0016585 | Sustained | FALSE | FALSE | TMED_Event | 2435
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:37 | 3 | 016:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1014 | 2022-04-06 | 3042 | keep | 0 | Apr | 2022 | 0.0020719 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:37 | 3957 | 016:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1014 | 2022-04-06 | 4012398 | keep | 0 | Apr | 2022 | 2.7328 | 0.0026951 | Sustained | FALSE | FALSE | TMED_Event | 3957
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:37 | 58 | 016:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1014 | 2022-04-06 | 58812 | keep | 0 | Apr | 2022 | 0.040057 | 3.9504e-05 | Sustained | FALSE | FALSE | TMED_Event | 58
SAN JUAN | 2022-04-06 20:43 | 2022-04-07 13:37 | 386 | 016:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1014 | 2022-04-06 | 391404 | keep | 0 | Apr | 2022 | 0.26658 | 0.0002629 | Sustained | FALSE | FALSE | TMED_Event | 386
BAYAMON | 2022-04-06 20:43 | 2022-04-09 03:38 | 1139 | 054:55 | T | LINEA DE TRANSMISION | APAGON GENERAL 1909-07 LLEVA 50% DEL 1709-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3295 | 2022-04-06 | 3753005 | keep | 0 | Apr | 2022 | 2.5562 | 0.00077577 | Sustained | FALSE | FALSE | TMED_Event | 1139
BAYAMON | 2022-04-06 20:43 | 2022-04-08 03:17 | 2956 | 030:34 | T | LINEA DE TRANSMISION | APAGON GENERAL BKR 1909-08 LLEVA 1907-05 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1834 | 2022-04-06 | 5421304 | keep | 0 | Apr | 2022 | 3.6924 | 0.0020133 | Sustained | FALSE | FALSE | TMED_Event | 2956
BAYAMON | 2022-04-06 20:43 | 2022-04-08 17:57 | 4456 | 045:14 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA TRANSFERIDA AL 1907-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2714 | 2022-04-06 | 12093584 | keep | 0 | Apr | 2022 | 8.2369 | 0.003035 | Sustained | FALSE | FALSE | TMED_Event | 4456
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:57 | 37 | 027:14 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1634 | 2022-04-06 | 60458 | keep | 0 | Apr | 2022 | 0.041178 | 2.5201e-05 | Sustained | FALSE | FALSE | TMED_Event | 37
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:57 | 7 | 027:14 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1634 | 2022-04-06 | 11438 | keep | 0 | Apr | 2022 | 0.0077904 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:57 | 2 | 027:14 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1634 | 2022-04-06 | 3268 | keep | 0 | Apr | 2022 | 0.0022258 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-04-06 20:43 | 2022-04-08 09:08 | 577 | 036:25 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2185 | 2022-04-06 | 1260745 | keep | 0 | Apr | 2022 | 0.85869 | 0.00039299 | Sustained | FALSE | FALSE | TMED_Event | 577
BAYAMON | 2022-04-06 20:43 | 2022-04-08 17:56 | 57 | 045:13 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2713 | 2022-04-06 | 154641 | keep | 0 | Apr | 2022 | 0.10533 | 3.8822e-05 | Sustained | FALSE | FALSE | TMED_Event | 57
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:11 | 212 | 055:28 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3328 | 2022-04-06 | 705536 | keep | 0 | Apr | 2022 | 0.48054 | 0.00014439 | Sustained | FALSE | FALSE | TMED_Event | 212
BAYAMON | 2022-04-06 20:43 | 2022-04-07 07:45 | 72 | 011:02 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 662 | 2022-04-06 | 47664 | keep | 0 | Apr | 2022 | 0.032464 | 4.9039e-05 | Sustained | FALSE | FALSE | TMED_Event | 72
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:11 | 5 | 055:28 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3328 | 2022-04-06 | 16640 | keep | 0 | Apr | 2022 | 0.011333 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:11 | 5 | 055:28 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3328 | 2022-04-06 | 16640 | keep | 0 | Apr | 2022 | 0.011333 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:11 | 686 | 055:28 | T | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3328 | 2022-04-06 | 2283008 | keep | 0 | Apr | 2022 | 1.5549 | 0.00046723 | Sustained | FALSE | FALSE | TMED_Event | 686
FAJARDO | 2022-04-06 20:43 | 2022-04-07 12:45 | 1571 | 016:02 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600246 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 962 | 2022-04-06 | 1511302 | keep | 0 | Apr | 2022 | 1.0293 | 0.00107 | Sustained | FALSE | FALSE | TMED_Event | 1571
FAJARDO | 2022-04-06 20:43 | 2022-04-07 12:45 | 2041 | 016:02 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600223 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 962 | 2022-04-06 | 1963442 | keep | 0 | Apr | 2022 | 1.3373 | 0.0013901 | Sustained | FALSE | FALSE | TMED_Event | 2041
FAJARDO | 2022-04-06 20:43 | 2022-04-07 12:45 | 625 | 016:02 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 962 | 2022-04-06 | 601250 | keep | 0 | Apr | 2022 | 0.40951 | 0.00042568 | Sustained | FALSE | FALSE | TMED_Event | 625
FAJARDO | 2022-04-06 20:43 | 2022-04-07 12:45 | 1463 | 016:02 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600221 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 962 | 2022-04-06 | 1407406 | keep | 0 | Apr | 2022 | 0.95858 | 0.00099644 | Sustained | FALSE | FALSE | TMED_Event | 1463
FAJARDO | 2022-04-06 20:43 | 2022-04-09 00:11 | 1902 | 051:28 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3088 | 2022-04-06 | 5873376 | keep | 0 | Apr | 2022 | 4.0003 | 0.0012954 | Sustained | FALSE | FALSE | TMED_Event | 1902
FAJARDO | 2022-04-06 20:43 | 2022-04-09 00:11 | 970 | 051:28 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3088 | 2022-04-06 | 2995360 | keep | 0 | Apr | 2022 | 2.0401 | 0.00066066 | Sustained | FALSE | FALSE | TMED_Event | 970
FAJARDO | 2022-04-06 20:43 | 2022-04-09 00:11 | 3003 | 051:28 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3088 | 2022-04-06 | 9273264 | keep | 0 | Apr | 2022 | 6.316 | 0.0020453 | Sustained | FALSE | FALSE | TMED_Event | 3003
FAJARDO | 2022-04-06 20:43 | 2022-04-09 00:28 | 1394 | 051:45 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600024 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3105 | 2022-04-06 | 4328370 | keep | 0 | Apr | 2022 | 2.948 | 0.00094945 | Sustained | FALSE | FALSE | TMED_Event | 1394
FAJARDO | 2022-04-06 20:43 | 2022-04-09 00:28 | 412 | 051:45 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600242 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3105 | 2022-04-06 | 1279260 | keep | 0 | Apr | 2022 | 0.8713 | 0.00028061 | Sustained | FALSE | FALSE | TMED_Event | 412
FAJARDO | 2022-04-06 20:43 | 2022-04-09 00:29 | 424 | 051:46 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600243 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3106 | 2022-04-06 | 1316944 | keep | 0 | Apr | 2022 | 0.89696 | 0.00028878 | Sustained | FALSE | FALSE | TMED_Event | 424
FAJARDO | 2022-04-06 20:43 | 2022-04-09 02:12 | 240 | 053:29 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600244 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3209 | 2022-04-06 | 770160 | keep | 0 | Apr | 2022 | 0.52455 | 0.00016346 | Sustained | FALSE | FALSE | TMED_Event | 240
FAJARDO | 2022-04-06 20:43 | 2022-04-07 20:50 | 2722 | 024:07 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600245 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1447 | 2022-04-06 | 3938734 | keep | 0 | Apr | 2022 | 2.6827 | 0.0018539 | Sustained | FALSE | FALSE | TMED_Event | 2722
FAJARDO | 2022-04-06 20:43 | 2022-04-08 09:10 | 1234 | 036:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600220 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2187 | 2022-04-06 | 2698758 | keep | 0 | Apr | 2022 | 1.8381 | 0.00084047 | Sustained | FALSE | FALSE | TMED_Event | 1234
FAJARDO | 2022-04-06 20:43 | 2022-04-09 00:08 | 76 | 051:25 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600222 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3085 | 2022-04-06 | 234460 | keep | 0 | Apr | 2022 | 0.15969 | 5.1763e-05 | Sustained | FALSE | FALSE | TMED_Event | 76
FAJARDO | 2022-04-06 20:43 | 2022-04-08 20:56 | 2286 | 048:13 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600215 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2893 | 2022-04-06 | 6613398 | keep | 0 | Apr | 2022 | 4.5044 | 0.001557 | Sustained | FALSE | FALSE | TMED_Event | 2286
FAJARDO | 2022-04-06 20:43 | 2022-04-08 20:56 | 693 | 048:13 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600215 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2893 | 2022-04-06 | 2004849 | keep | 0 | Apr | 2022 | 1.3655 | 0.000472 | Sustained | FALSE | FALSE | TMED_Event | 693
FAJARDO | 2022-04-06 20:43 | 2022-04-07 05:22 | 4098 | 008:39 | T | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 519 | 2022-04-06 | 2126862 | keep | 0 | Apr | 2022 | 1.4486 | 0.0027911 | Sustained | FALSE | FALSE | TMED_Event | 4098
FAJARDO | 2022-04-06 20:43 | 2022-04-07 05:24 | 956 | 008:41 | T | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 521 | 2022-04-06 | 498076 | keep | 0 | Apr | 2022 | 0.33924 | 0.00065113 | Sustained | FALSE | FALSE | TMED_Event | 956
FAJARDO | 2022-04-06 20:43 | 2022-04-08 12:59 | 2343 | 040:16 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2416 | 2022-04-06 | 5660688 | keep | 0 | Apr | 2022 | 3.8555 | 0.0015958 | Sustained | FALSE | FALSE | TMED_Event | 2343
FAJARDO | 2022-04-06 20:43 | 2022-04-08 13:50 | 1830 | 041:07 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2467 | 2022-04-06 | 4514610 | keep | 0 | Apr | 2022 | 3.0749 | 0.0012464 | Sustained | FALSE | FALSE | TMED_Event | 1830
FAJARDO | 2022-04-06 20:43 | 2022-04-08 12:59 | 710 | 040:16 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2416 | 2022-04-06 | 1715360 | keep | 0 | Apr | 2022 | 1.1683 | 0.00048358 | Sustained | FALSE | FALSE | TMED_Event | 710
FAJARDO | 2022-04-06 20:43 | 2022-04-08 12:59 | 1197 | 040:16 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2416 | 2022-04-06 | 2891952 | keep | 0 | Apr | 2022 | 1.9697 | 0.00081527 | Sustained | FALSE | FALSE | TMED_Event | 1197
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 11:06 | 1894 | 038:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600226 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2303 | 2022-04-06 | 4361882 | keep | 0 | Apr | 2022 | 2.9709 | 0.00129 | Sustained | FALSE | FALSE | TMED_Event | 1894
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 10:30 | 4154 | 037:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600227 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2267 | 2022-04-06 | 9417118 | keep | 0 | Apr | 2022 | 6.414 | 0.0028293 | Sustained | FALSE | FALSE | TMED_Event | 4154
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 11:06 | 424 | 038:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600228 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2303 | 2022-04-06 | 976472 | keep | 0 | Apr | 2022 | 0.66507 | 0.00028878 | Sustained | FALSE | FALSE | TMED_Event | 424
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 10:30 | 2708 | 037:47 | T | LINEA DE TRANSMISION | APAGON GENERAL 2302-02 LLEVANDO LA CARGA DEL 2302-01 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2267 | 2022-04-06 | 6139036 | keep | 0 | Apr | 2022 | 4.1813 | 0.0018444 | Sustained | FALSE | FALSE | TMED_Event | 2708
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 10:30 | 2524 | 037:47 | T | LINEA DE TRANSMISION | APAGON GENERAL 2302-02 LLEVANDO LA CARGA DEL 2302-01 | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2267 | 2022-04-06 | 5721908 | keep | 0 | Apr | 2022 | 3.8972 | 0.0017191 | Sustained | FALSE | FALSE | TMED_Event | 2524
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 12:37 | 1648 | 039:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2394 | 2022-04-06 | 3945312 | keep | 0 | Apr | 2022 | 2.6871 | 0.0011224 | Sustained | FALSE | FALSE | TMED_Event | 1648
CANOVANAS | 2022-04-06 20:43 | 2022-04-09 03:54 | 539 | 055:11 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3311 | 2022-04-06 | 1784629 | keep | 0 | Apr | 2022 | 1.2155 | 0.00036711 | Sustained | FALSE | FALSE | TMED_Event | 539
CANOVANAS | 2022-04-06 20:43 | 2022-04-09 03:41 | 3012 | 054:58 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3298 | 2022-04-06 | 9933576 | keep | 0 | Apr | 2022 | 6.7657 | 0.0020515 | Sustained | FALSE | FALSE | TMED_Event | 3012
CANOVANAS | 2022-04-06 20:43 | 2022-04-09 13:02 | 2106 | 064:19 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3859 | 2022-04-06 | 8127054 | keep | 0 | Apr | 2022 | 5.5353 | 0.0014344 | Sustained | FALSE | FALSE | TMED_Event | 2106
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 10:16 | 635 | 037:33 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2253 | 2022-04-06 | 1430655 | keep | 0 | Apr | 2022 | 0.97441 | 0.0004325 | Sustained | FALSE | FALSE | TMED_Event | 635
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 10:16 | 3766 | 037:33 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2253 | 2022-04-06 | 8484798 | keep | 0 | Apr | 2022 | 5.779 | 0.002565 | Sustained | FALSE | FALSE | TMED_Event | 3766
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 10:16 | 1380 | 037:33 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2253 | 2022-04-06 | 3109140 | keep | 0 | Apr | 2022 | 2.1176 | 0.00093991 | Sustained | FALSE | FALSE | TMED_Event | 1380
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 12:23 | 3838 | 039:40 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 9134440 | keep | 0 | Apr | 2022 | 6.2214 | 0.002614 | Sustained | FALSE | FALSE | TMED_Event | 3838
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 12:23 | 817 | 039:40 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 1944460 | keep | 0 | Apr | 2022 | 1.3244 | 0.00055645 | Sustained | FALSE | FALSE | TMED_Event | 817
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 12:23 | 1124 | 039:40 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 2675120 | keep | 0 | Apr | 2022 | 1.822 | 0.00076555 | Sustained | FALSE | FALSE | TMED_Event | 1124
CANOVANAS | 2022-04-06 20:43 | 2022-04-07 12:32 | 2039 | 015:49 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 949 | 2022-04-06 | 1935011 | keep | 0 | Apr | 2022 | 1.3179 | 0.0013888 | Sustained | FALSE | FALSE | TMED_Event | 2039
CANOVANAS | 2022-04-06 20:43 | 2022-04-07 12:32 | 4188 | 015:49 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 949 | 2022-04-06 | 3974412 | keep | 0 | Apr | 2022 | 2.707 | 0.0028524 | Sustained | FALSE | FALSE | TMED_Event | 4188
CANOVANAS | 2022-04-06 20:43 | 2022-04-07 12:32 | 4085 | 015:49 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 949 | 2022-04-06 | 3876665 | keep | 0 | Apr | 2022 | 2.6404 | 0.0027823 | Sustained | FALSE | FALSE | TMED_Event | 4085
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 20:57 | 2580 | 048:14 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2894 | 2022-04-06 | 7466520 | keep | 0 | Apr | 2022 | 5.0854 | 0.0017572 | Sustained | FALSE | FALSE | TMED_Event | 2580
CANOVANAS | 2022-04-06 20:43 | 2022-04-08 20:52 | 500 | 048:09 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2889 | 2022-04-06 | 1444500 | keep | 0 | Apr | 2022 | 0.98384 | 0.00034055 | Sustained | FALSE | FALSE | TMED_Event | 500
CANOVANAS | 2022-04-06 20:43 | 2022-04-07 12:32 | 2078 | 015:49 | P | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 949 | 2022-04-06 | 1972022 | keep | 0 | Apr | 2022 | 1.3431 | 0.0014153 | Sustained | FALSE | FALSE | TMED_Event | 2078
CANOVANAS | 2022-04-06 20:43 | 2022-04-07 12:32 | 7621 | 015:49 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA X 2402-03 | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 949 | 2022-04-06 | 7232329 | keep | 0 | Apr | 2022 | 4.9259 | 0.0051906 | Sustained | FALSE | FALSE | TMED_Event | 7621
CANOVANAS | 2022-04-06 20:43 | 2022-04-07 12:32 | 3699 | 015:49 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 949 | 2022-04-06 | 3510351 | keep | 0 | Apr | 2022 | 2.3909 | 0.0025194 | Sustained | FALSE | FALSE | TMED_Event | 3699
CANOVANAS | 2022-04-06 20:43 | 2022-04-07 12:32 | 2675 | 015:49 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 949 | 2022-04-06 | 2538575 | keep | 0 | Apr | 2022 | 1.729 | 0.0018219 | Sustained | FALSE | FALSE | TMED_Event | 2675
FAJARDO | 2022-04-06 20:43 | 2022-04-07 08:08 | 1839 | 011:25 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 685 | 2022-04-06 | 1259715 | keep | 0 | Apr | 2022 | 0.85799 | 0.0012525 | Sustained | FALSE | FALSE | TMED_Event | 1839
FAJARDO | 2022-04-06 20:43 | 2022-04-07 08:05 | 1778 | 011:22 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 682 | 2022-04-06 | 1212596 | keep | 0 | Apr | 2022 | 0.82589 | 0.001211 | Sustained | FALSE | FALSE | TMED_Event | 1778
FAJARDO | 2022-04-06 20:43 | 2022-04-07 08:09 | 1376 | 011:26 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 686 | 2022-04-06 | 943936 | keep | 0 | Apr | 2022 | 0.64291 | 0.00093719 | Sustained | FALSE | FALSE | TMED_Event | 1376
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:13 | 3833 | 015:30 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 930 | 2022-04-06 | 3564690 | keep | 0 | Apr | 2022 | 2.4279 | 0.0026106 | Sustained | FALSE | FALSE | TMED_Event | 3833
HUMACAO | 2022-04-06 20:43 | 2022-04-08 07:58 | 181 | 035:15 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600196 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2115 | 2022-04-06 | 382815 | keep | 0 | Apr | 2022 | 0.26073 | 0.00012328 | Sustained | FALSE | FALSE | TMED_Event | 181
HUMACAO | 2022-04-06 20:43 | 2022-04-08 23:47 | 2299 | 051:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600197 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3064 | 2022-04-06 | 7044136 | keep | 0 | Apr | 2022 | 4.7977 | 0.0015658 | Sustained | FALSE | FALSE | TMED_Event | 2299
HUMACAO | 2022-04-06 20:43 | 2022-04-09 02:13 | 776 | 053:30 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600198 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3210 | 2022-04-06 | 2490960 | keep | 0 | Apr | 2022 | 1.6966 | 0.00052853 | Sustained | FALSE | FALSE | TMED_Event | 776
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:30 | 519 | 015:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600192 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 947 | 2022-04-06 | 491493 | keep | 0 | Apr | 2022 | 0.33475 | 0.00035349 | Sustained | FALSE | FALSE | TMED_Event | 519
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:30 | 1117 | 015:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600193 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 947 | 2022-04-06 | 1057799 | keep | 0 | Apr | 2022 | 0.72046 | 0.00076078 | Sustained | FALSE | FALSE | TMED_Event | 1117
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:30 | 4161 | 015:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 947 | 2022-04-06 | 3940467 | keep | 0 | Apr | 2022 | 2.6838 | 0.002834 | Sustained | FALSE | FALSE | TMED_Event | 4161
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:10 | 327 | 015:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600188 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 927 | 2022-04-06 | 303129 | keep | 0 | Apr | 2022 | 0.20646 | 0.00022272 | Sustained | FALSE | FALSE | TMED_Event | 327
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:10 | 5630 | 015:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600189 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 927 | 2022-04-06 | 5219010 | keep | 0 | Apr | 2022 | 3.5546 | 0.0038346 | Sustained | FALSE | FALSE | TMED_Event | 5630
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:10 | 2126 | 015:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600190 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 927 | 2022-04-06 | 1970802 | keep | 0 | Apr | 2022 | 1.3423 | 0.001448 | Sustained | FALSE | FALSE | TMED_Event | 2126
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:10 | 551 | 015:27 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600191 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 927 | 2022-04-06 | 510777 | keep | 0 | Apr | 2022 | 0.34789 | 0.00037528 | Sustained | FALSE | FALSE | TMED_Event | 551
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:07 | 2354 | 015:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 924 | 2022-04-06 | 2175096 | keep | 0 | Apr | 2022 | 1.4814 | 0.0016033 | Sustained | FALSE | FALSE | TMED_Event | 2354
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:07 | 3025 | 015:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 924 | 2022-04-06 | 2795100 | keep | 0 | Apr | 2022 | 1.9037 | 0.0020603 | Sustained | FALSE | FALSE | TMED_Event | 3025
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:07 | 1593 | 015:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 924 | 2022-04-06 | 1471932 | keep | 0 | Apr | 2022 | 1.0025 | 0.001085 | Sustained | FALSE | FALSE | TMED_Event | 1593
HUMACAO | 2022-04-06 20:43 | 2022-04-09 02:12 | 2450 | 053:29 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600199 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3209 | 2022-04-06 | 7862050 | keep | 0 | Apr | 2022 | 5.3548 | 0.0016687 | Sustained | FALSE | FALSE | TMED_Event | 2450
HUMACAO | 2022-04-06 20:43 | 2022-04-08 05:45 | 640 | 033:02 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040900000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1982 | 2022-04-06 | 1268480 | keep | 0 | Apr | 2022 | 0.86396 | 0.0004359 | Sustained | FALSE | FALSE | TMED_Event | 640
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:30 | 3701 | 015:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040700220 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 947 | 2022-04-06 | 3504847 | keep | 0 | Apr | 2022 | 2.3871 | 0.0025207 | Sustained | FALSE | FALSE | TMED_Event | 3701
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:30 | 989 | 015:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040700221 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 947 | 2022-04-06 | 936583 | keep | 0 | Apr | 2022 | 0.6379 | 0.0006736 | Sustained | FALSE | FALSE | TMED_Event | 989
HUMACAO | 2022-04-06 20:43 | 2022-04-08 14:19 | 1467 | 041:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600196 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2496 | 2022-04-06 | 3661632 | keep | 0 | Apr | 2022 | 2.4939 | 0.00099917 | Sustained | FALSE | FALSE | TMED_Event | 1467
HUMACAO | 2022-04-06 20:43 | 2022-04-09 02:14 | 1835 | 053:31 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600222 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3211 | 2022-04-06 | 5892185 | keep | 0 | Apr | 2022 | 4.0131 | 0.0012498 | Sustained | FALSE | FALSE | TMED_Event | 1835
HUMACAO | 2022-04-06 20:43 | 2022-04-09 02:14 | 71 | 053:31 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040900442 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3211 | 2022-04-06 | 227981 | keep | 0 | Apr | 2022 | 0.15528 | 4.8358e-05 | Sustained | FALSE | FALSE | TMED_Event | 71
HUMACAO | 2022-04-06 20:43 | 2022-04-07 22:38 | 676 | 025:55 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1555 | 2022-04-06 | 1051180 | keep | 0 | Apr | 2022 | 0.71595 | 0.00046042 | Sustained | FALSE | FALSE | TMED_Event | 676
HUMACAO | 2022-04-06 20:43 | 2022-04-07 22:38 | 2873 | 025:55 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1555 | 2022-04-06 | 4467515 | keep | 0 | Apr | 2022 | 3.0428 | 0.0019568 | Sustained | FALSE | FALSE | TMED_Event | 2873
HUMACAO | 2022-04-06 20:43 | 2022-04-07 22:38 | 3902 | 025:55 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1555 | 2022-04-06 | 6067610 | keep | 0 | Apr | 2022 | 4.1326 | 0.0026576 | Sustained | FALSE | FALSE | TMED_Event | 3902
HUMACAO | 2022-04-06 20:43 | 2022-04-07 22:37 | 1089 | 025:54 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1554 | 2022-04-06 | 1692306 | keep | 0 | Apr | 2022 | 1.1526 | 0.00074171 | Sustained | FALSE | FALSE | TMED_Event | 1089
HUMACAO | 2022-04-06 20:43 | 2022-04-07 22:37 | 3896 | 025:54 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1554 | 2022-04-06 | 6054384 | keep | 0 | Apr | 2022 | 4.1236 | 0.0026535 | Sustained | FALSE | FALSE | TMED_Event | 3896
HUMACAO | 2022-04-06 20:43 | 2022-04-07 22:37 | 1467 | 025:54 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1554 | 2022-04-06 | 2279718 | keep | 0 | Apr | 2022 | 1.5527 | 0.00099917 | Sustained | FALSE | FALSE | TMED_Event | 1467
HUMACAO | 2022-04-06 20:43 | 2022-04-09 03:07 | 1891 | 054:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600195 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3264 | 2022-04-06 | 6172224 | keep | 0 | Apr | 2022 | 4.2039 | 0.001288 | Sustained | FALSE | FALSE | TMED_Event | 1891
HUMACAO | 2022-04-06 20:43 | 2022-04-08 00:48 | 1250 | 028:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1685 | 2022-04-06 | 2106250 | keep | 0 | Apr | 2022 | 1.4346 | 0.00085137 | Sustained | FALSE | FALSE | TMED_Event | 1250
HUMACAO | 2022-04-06 20:43 | 2022-04-08 09:17 | 1467 | 036:34 | P | LINEA DE TRANSMISION | APAGON GENERAL | C22040600196 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2194 | 2022-04-06 | 3218598 | keep | 0 | Apr | 2022 | 2.1922 | 0.00099917 | Sustained | FALSE | FALSE | TMED_Event | 1467
HUMACAO | 2022-04-06 20:43 | 2022-04-09 00:48 | 1827 | 052:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600196 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3125 | 2022-04-06 | 5709375 | keep | 0 | Apr | 2022 | 3.8886 | 0.0012444 | Sustained | FALSE | FALSE | TMED_Event | 1827
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:07 | 3420 | 015:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 924 | 2022-04-06 | 3160080 | keep | 0 | Apr | 2022 | 2.1523 | 0.0023293 | Sustained | FALSE | FALSE | TMED_Event | 3420
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:07 | 4 | 015:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 924 | 2022-04-06 | 3696 | keep | 0 | Apr | 2022 | 0.0025173 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
HUMACAO | 2022-04-06 20:43 | 2022-04-07 12:07 | 3 | 015:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600158 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 924 | 2022-04-06 | 2772 | keep | 0 | Apr | 2022 | 0.001888 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
CAGUAS | 2022-04-06 20:43 | 2022-04-07 14:44 | 1590 | 018:01 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1081 | 2022-04-06 | 1718790 | keep | 0 | Apr | 2022 | 1.1707 | 0.0010829 | Sustained | FALSE | FALSE | TMED_Event | 1590
CAGUAS | 2022-04-06 20:43 | 2022-04-07 18:54 | 1 | 022:11 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1331 | 2022-04-06 | 1331 | keep | 0 | Apr | 2022 | 0.00090654 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CAGUAS | 2022-04-06 20:43 | 2022-04-09 04:25 | 1510 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040900000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 5046420 | keep | 0 | Apr | 2022 | 3.4371 | 0.0010285 | Sustained | FALSE | FALSE | TMED_Event | 1510
CAGUAS | 2022-04-06 20:43 | 2022-04-07 18:55 | 166 | 022:12 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1332 | 2022-04-06 | 221112 | keep | 0 | Apr | 2022 | 0.1506 | 0.00011306 | Sustained | FALSE | FALSE | TMED_Event | 166
CAGUAS | 2022-04-06 20:43 | 2022-04-08 17:03 | 554 | 044:20 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2660 | 2022-04-06 | 1473640 | keep | 0 | Apr | 2022 | 1.0037 | 0.00037733 | Sustained | FALSE | FALSE | TMED_Event | 554
CAGUAS | 2022-04-06 20:43 | 2022-04-09 05:06 | 1116 | 056:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3383 | 2022-04-06 | 3775428 | keep | 0 | Apr | 2022 | 2.5714 | 0.0007601 | Sustained | FALSE | FALSE | TMED_Event | 1116
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:17 | 718 | 053:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3214 | 2022-04-06 | 2307652 | keep | 0 | Apr | 2022 | 1.5717 | 0.00048903 | Sustained | FALSE | FALSE | TMED_Event | 718
CAGUAS | 2022-04-06 20:43 | 2022-04-07 13:47 | 329 | 017:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1024 | 2022-04-06 | 336896 | keep | 0 | Apr | 2022 | 0.22946 | 0.00022408 | Sustained | FALSE | FALSE | TMED_Event | 329
CAGUAS | 2022-04-06 20:43 | 2022-04-07 13:47 | 1879 | 017:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1024 | 2022-04-06 | 1924096 | keep | 0 | Apr | 2022 | 1.3105 | 0.0012798 | Sustained | FALSE | FALSE | TMED_Event | 1879
CAGUAS | 2022-04-06 20:43 | 2022-04-07 12:48 | 1084 | 016:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 965 | 2022-04-06 | 1046060 | keep | 0 | Apr | 2022 | 0.71247 | 0.00073831 | Sustained | FALSE | FALSE | TMED_Event | 1084
CAGUAS | 2022-04-06 20:43 | 2022-04-07 13:47 | 817 | 017:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600177 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1024 | 2022-04-06 | 836608 | keep | 0 | Apr | 2022 | 0.56981 | 0.00055645 | Sustained | FALSE | FALSE | TMED_Event | 817
CAGUAS | 2022-04-06 20:43 | 2022-04-07 13:36 | 3005 | 016:53 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 1908-05 | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1013 | 2022-04-06 | 3044065 | keep | 0 | Apr | 2022 | 2.0733 | 0.0020467 | Sustained | FALSE | FALSE | TMED_Event | 3005
CAGUAS | 2022-04-06 20:43 | 2022-04-09 04:53 | 125 | 056:10 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040900000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3370 | 2022-04-06 | 421250 | keep | 0 | Apr | 2022 | 0.28691 | 8.5137e-05 | Sustained | FALSE | FALSE | TMED_Event | 125
CAGUAS | 2022-04-06 20:43 | 2022-04-09 04:53 | 638 | 056:10 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040900174 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3370 | 2022-04-06 | 2150060 | keep | 0 | Apr | 2022 | 1.4644 | 0.00043454 | Sustained | FALSE | FALSE | TMED_Event | 638
CAGUAS | 2022-04-06 20:43 | 2022-04-08 04:08 | 6197 | 031:25 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 11681345 | keep | 0 | Apr | 2022 | 7.9561 | 0.0042207 | Sustained | FALSE | FALSE | TMED_Event | 6197
CAGUAS | 2022-04-06 20:43 | 2022-04-09 04:54 | 906 | 056:11 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040900174 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3371 | 2022-04-06 | 3054126 | keep | 0 | Apr | 2022 | 2.0802 | 0.00061707 | Sustained | FALSE | FALSE | TMED_Event | 906
CAGUAS | 2022-04-06 20:43 | 2022-04-09 04:26 | 1153 | 055:43 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600170 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3343 | 2022-04-06 | 3854479 | keep | 0 | Apr | 2022 | 2.6253 | 0.0007853 | Sustained | FALSE | FALSE | TMED_Event | 1153
CAGUAS | 2022-04-06 20:43 | 2022-04-08 08:49 | 1709 | 036:06 | T | LINEA DE TRANSMISION | APAGON GENERAL (BLACKOUT) | C22040600171 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2166 | 2022-04-06 | 3701694 | keep | 0 | Apr | 2022 | 2.5212 | 0.001164 | Sustained | FALSE | FALSE | TMED_Event | 1709
CAGUAS | 2022-04-06 20:43 | 2022-04-09 04:26 | 1320 | 055:43 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600169 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3343 | 2022-04-06 | 4412760 | keep | 0 | Apr | 2022 | 3.0055 | 0.00089905 | Sustained | FALSE | FALSE | TMED_Event | 1320
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:17 | 2448 | 053:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600172 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3214 | 2022-04-06 | 7867872 | keep | 0 | Apr | 2022 | 5.3588 | 0.0016673 | Sustained | FALSE | FALSE | TMED_Event | 2448
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:17 | 128 | 053:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600173 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3214 | 2022-04-06 | 411392 | keep | 0 | Apr | 2022 | 0.2802 | 8.718e-05 | Sustained | FALSE | FALSE | TMED_Event | 128
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:17 | 273 | 053:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600173 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3214 | 2022-04-06 | 877422 | keep | 0 | Apr | 2022 | 0.59761 | 0.00018594 | Sustained | FALSE | FALSE | TMED_Event | 273
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:17 | 1772 | 053:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600173 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3214 | 2022-04-06 | 5695208 | keep | 0 | Apr | 2022 | 3.879 | 0.0012069 | Sustained | FALSE | FALSE | TMED_Event | 1772
CAGUAS | 2022-04-06 20:43 | 2022-04-09 04:27 | 4369 | 055:44 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3344 | 2022-04-06 | 14609936 | keep | 0 | Apr | 2022 | 9.9508 | 0.0029757 | Sustained | FALSE | FALSE | TMED_Event | 4369
CAGUAS | 2022-04-06 20:43 | 2022-04-09 05:05 | 676 | 056:22 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3382 | 2022-04-06 | 2286232 | keep | 0 | Apr | 2022 | 1.5571 | 0.00046042 | Sustained | FALSE | FALSE | TMED_Event | 676
CAGUAS | 2022-04-06 20:43 | 2022-04-09 05:05 | 1606 | 056:22 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3382 | 2022-04-06 | 5431492 | keep | 0 | Apr | 2022 | 3.6994 | 0.0010938 | Sustained | FALSE | FALSE | TMED_Event | 1606
CAGUAS | 2022-04-06 20:43 | 2022-04-09 05:05 | 725 | 056:22 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3382 | 2022-04-06 | 2451950 | keep | 0 | Apr | 2022 | 1.67 | 0.00049379 | Sustained | FALSE | FALSE | TMED_Event | 725
CAGUAS | 2022-04-06 20:43 | 2022-04-09 01:37 | 1228 | 052:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600167 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3174 | 2022-04-06 | 3897672 | keep | 0 | Apr | 2022 | 2.6547 | 0.00083639 | Sustained | FALSE | FALSE | TMED_Event | 1228
CAGUAS | 2022-04-06 20:43 | 2022-04-09 01:37 | 1271 | 052:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600165 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3174 | 2022-04-06 | 4034154 | keep | 0 | Apr | 2022 | 2.7476 | 0.00086567 | Sustained | FALSE | FALSE | TMED_Event | 1271
CAGUAS | 2022-04-06 20:43 | 2022-04-08 20:11 | 1893 | 047:28 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2848 | 2022-04-06 | 5391264 | keep | 0 | Apr | 2022 | 3.672 | 0.0012893 | Sustained | FALSE | FALSE | TMED_Event | 1893
CAGUAS | 2022-04-06 20:43 | 2022-04-09 01:38 | 473 | 052:55 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600166 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3175 | 2022-04-06 | 1501775 | keep | 0 | Apr | 2022 | 1.0229 | 0.00032216 | Sustained | FALSE | FALSE | TMED_Event | 473
CAGUAS | 2022-04-06 20:43 | 2022-04-09 01:33 | 2276 | 052:50 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3170 | 2022-04-06 | 7214920 | keep | 0 | Apr | 2022 | 4.914 | 0.0015502 | Sustained | FALSE | FALSE | TMED_Event | 2276
CAGUAS | 2022-04-06 20:43 | 2022-04-09 01:33 | 777 | 052:50 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3170 | 2022-04-06 | 2463090 | keep | 0 | Apr | 2022 | 1.6776 | 0.00052921 | Sustained | FALSE | FALSE | TMED_Event | 777
CAGUAS | 2022-04-06 20:43 | 2022-04-09 01:33 | 12 | 052:50 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3170 | 2022-04-06 | 38040 | keep | 0 | Apr | 2022 | 0.025909 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CAGUAS | 2022-04-06 20:43 | 2022-04-09 01:33 | 1290 | 052:50 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3170 | 2022-04-06 | 4089300 | keep | 0 | Apr | 2022 | 2.7852 | 0.00087861 | Sustained | FALSE | FALSE | TMED_Event | 1290
CAGUAS | 2022-04-06 20:43 | 2022-04-08 19:46 | 2302 | 047:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2823 | 2022-04-06 | 6498546 | keep | 0 | Apr | 2022 | 4.4261 | 0.0015679 | Sustained | FALSE | FALSE | TMED_Event | 2302
CAGUAS | 2022-04-06 20:43 | 2022-04-08 20:29 | 1342 | 047:46 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2866 | 2022-04-06 | 3846172 | keep | 0 | Apr | 2022 | 2.6196 | 0.00091403 | Sustained | FALSE | FALSE | TMED_Event | 1342
CAGUAS | 2022-04-06 20:43 | 2022-04-09 05:06 | 34 | 056:23 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3383 | 2022-04-06 | 115022 | keep | 0 | Apr | 2022 | 0.078341 | 2.3157e-05 | Sustained | FALSE | FALSE | TMED_Event | 34
CAGUAS | 2022-04-06 20:43 | 2022-04-09 04:24 | 2608 | 055:41 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3341 | 2022-04-06 | 8713328 | keep | 0 | Apr | 2022 | 5.9346 | 0.0017763 | Sustained | FALSE | FALSE | TMED_Event | 2608
CAGUAS | 2022-04-06 20:43 | 2022-04-09 04:25 | 845 | 055:42 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600175 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3342 | 2022-04-06 | 2823990 | keep | 0 | Apr | 2022 | 1.9234 | 0.00057553 | Sustained | FALSE | FALSE | TMED_Event | 845
CAGUAS | 2022-04-06 20:43 | 2022-04-08 23:54 | 476 | 051:11 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3071 | 2022-04-06 | 1461796 | keep | 0 | Apr | 2022 | 0.99562 | 0.0003242 | Sustained | FALSE | FALSE | TMED_Event | 476
CAGUAS | 2022-04-06 20:43 | 2022-04-09 00:03 | 1655 | 051:20 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3080 | 2022-04-06 | 5097400 | keep | 0 | Apr | 2022 | 3.4718 | 0.0011272 | Sustained | FALSE | FALSE | TMED_Event | 1655
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:16 | 361 | 053:33 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3213 | 2022-04-06 | 1159893 | keep | 0 | Apr | 2022 | 0.79 | 0.00024588 | Sustained | FALSE | FALSE | TMED_Event | 361
CAGUAS | 2022-04-06 20:43 | 2022-04-08 23:54 | 2842 | 051:11 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3071 | 2022-04-06 | 8727782 | keep | 0 | Apr | 2022 | 5.9445 | 0.0019357 | Sustained | FALSE | FALSE | TMED_Event | 2842
CAGUAS | 2022-04-06 20:43 | 2022-04-09 06:31 | 1702 | 057:48 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3468 | 2022-04-06 | 5902536 | keep | 0 | Apr | 2022 | 4.0202 | 0.0011592 | Sustained | FALSE | FALSE | TMED_Event | 1702
CAGUAS | 2022-04-06 20:43 | 2022-04-09 06:31 | 918 | 057:48 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3468 | 2022-04-06 | 3183624 | keep | 0 | Apr | 2022 | 2.1684 | 0.00062525 | Sustained | FALSE | FALSE | TMED_Event | 918
CAGUAS | 2022-04-06 20:43 | 2022-04-07 22:36 | 1261 | 025:53 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1553 | 2022-04-06 | 1958333 | keep | 0 | Apr | 2022 | 1.3338 | 0.00085886 | Sustained | FALSE | FALSE | TMED_Event | 1261
CAGUAS | 2022-04-06 20:43 | 2022-04-07 22:35 | 1922 | 025:52 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1552 | 2022-04-06 | 2982944 | keep | 0 | Apr | 2022 | 2.0317 | 0.0013091 | Sustained | FALSE | FALSE | TMED_Event | 1922
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:16 | 853 | 053:33 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3213 | 2022-04-06 | 2740689 | keep | 0 | Apr | 2022 | 1.8667 | 0.00058097 | Sustained | FALSE | FALSE | TMED_Event | 853
CAGUAS | 2022-04-06 20:43 | 2022-04-08 20:58 | 2900 | 048:15 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2895 | 2022-04-06 | 8395500 | keep | 0 | Apr | 2022 | 5.7181 | 0.0019752 | Sustained | FALSE | FALSE | TMED_Event | 2900
CAGUAS | 2022-04-06 20:43 | 2022-04-08 04:05 | 2178 | 031:22 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1882 | 2022-04-06 | 4098996 | keep | 0 | Apr | 2022 | 2.7918 | 0.0014834 | Sustained | FALSE | FALSE | TMED_Event | 2178
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:15 | 1 | 053:32 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3212 | 2022-04-06 | 3212 | keep | 0 | Apr | 2022 | 0.0021877 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:15 | 3108 | 053:32 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600159 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3212 | 2022-04-06 | 9982896 | keep | 0 | Apr | 2022 | 6.7993 | 0.0021168 | Sustained | FALSE | FALSE | TMED_Event | 3108
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:15 | 958 | 053:32 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600160 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3212 | 2022-04-06 | 3077096 | keep | 0 | Apr | 2022 | 2.0958 | 0.00065249 | Sustained | FALSE | FALSE | TMED_Event | 958
CAGUAS | 2022-04-06 20:43 | 2022-04-07 10:40 | 2789 | 013:57 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 837 | 2022-04-06 | 2334393 | keep | 0 | Apr | 2022 | 1.5899 | 0.0018996 | Sustained | FALSE | FALSE | TMED_Event | 2789
CAGUAS | 2022-04-06 20:43 | 2022-04-08 08:49 | 1725 | 036:06 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2166 | 2022-04-06 | 3736350 | keep | 0 | Apr | 2022 | 2.5448 | 0.0011749 | Sustained | FALSE | FALSE | TMED_Event | 1725
CAGUAS | 2022-04-06 20:43 | 2022-04-08 23:45 | 4634 | 051:02 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3062 | 2022-04-06 | 14189308 | keep | 0 | Apr | 2022 | 9.6643 | 0.0031562 | Sustained | FALSE | FALSE | TMED_Event | 4634
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:14 | 1378 | 053:31 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600241 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3211 | 2022-04-06 | 4424758 | keep | 0 | Apr | 2022 | 3.0137 | 0.00093855 | Sustained | FALSE | FALSE | TMED_Event | 1378
CAGUAS | 2022-04-06 20:43 | 2022-04-09 02:14 | 1307 | 053:31 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600242 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3211 | 2022-04-06 | 4196777 | keep | 0 | Apr | 2022 | 2.8584 | 0.00089019 | Sustained | FALSE | FALSE | TMED_Event | 1307
CAGUAS | 2022-04-06 20:43 | 2022-04-08 04:08 | 293 | 031:25 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 552305 | keep | 0 | Apr | 2022 | 0.37617 | 0.00019956 | Sustained | FALSE | FALSE | TMED_Event | 293
CAGUAS | 2022-04-06 20:43 | 2022-04-08 08:48 | 4390 | 036:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2165 | 2022-04-06 | 9504350 | keep | 0 | Apr | 2022 | 6.4734 | 0.00299 | Sustained | FALSE | FALSE | TMED_Event | 4390
CAGUAS | 2022-04-06 20:43 | 2022-04-09 17:02 | 2092 | 068:19 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4099 | 2022-04-06 | 8575108 | keep | 0 | Apr | 2022 | 5.8405 | 0.0014249 | Sustained | FALSE | FALSE | TMED_Event | 2092
CAGUAS | 2022-04-06 20:43 | 2022-04-08 09:17 | 540 | 036:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2194 | 2022-04-06 | 1184760 | keep | 0 | Apr | 2022 | 0.80693 | 0.00036779 | Sustained | FALSE | FALSE | TMED_Event | 540
CAGUAS | 2022-04-06 20:43 | 2022-04-08 08:48 | 131 | 036:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2165 | 2022-04-06 | 283615 | keep | 0 | Apr | 2022 | 0.19317 | 8.9224e-05 | Sustained | FALSE | FALSE | TMED_Event | 131
CAGUAS | 2022-04-06 20:43 | 2022-04-08 08:48 | 2281 | 036:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2165 | 2022-04-06 | 4938365 | keep | 0 | Apr | 2022 | 3.3635 | 0.0015536 | Sustained | FALSE | FALSE | TMED_Event | 2281
CAGUAS | 2022-04-06 20:43 | 2022-04-08 08:48 | 1569 | 036:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2165 | 2022-04-06 | 3396885 | keep | 0 | Apr | 2022 | 2.3136 | 0.0010686 | Sustained | FALSE | FALSE | TMED_Event | 1569
CAGUAS | 2022-04-06 20:43 | 2022-04-08 08:48 | 2417 | 036:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2165 | 2022-04-06 | 5232805 | keep | 0 | Apr | 2022 | 3.564 | 0.0016462 | Sustained | FALSE | FALSE | TMED_Event | 2417
CAGUAS | 2022-04-06 20:43 | 2022-04-08 20:54 | 1516 | 048:11 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2891 | 2022-04-06 | 4382756 | keep | 0 | Apr | 2022 | 2.9851 | 0.0010325 | Sustained | FALSE | FALSE | TMED_Event | 1516
CAGUAS | 2022-04-06 20:43 | 2022-04-08 03:19 | 3131 | 030:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1836 | 2022-04-06 | 5748516 | keep | 0 | Apr | 2022 | 3.9153 | 0.0021325 | Sustained | FALSE | FALSE | TMED_Event | 3131
CAGUAS | 2022-04-06 20:43 | 2022-04-07 12:51 | 2907 | 016:08 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 968 | 2022-04-06 | 2813976 | keep | 0 | Apr | 2022 | 1.9166 | 0.0019799 | Sustained | FALSE | FALSE | TMED_Event | 2907
CAGUAS | 2022-04-06 20:43 | 2022-04-07 23:49 | 1647 | 027:06 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1626 | 2022-04-06 | 2678022 | keep | 0 | Apr | 2022 | 1.824 | 0.0011218 | Sustained | FALSE | FALSE | TMED_Event | 1647
CAGUAS | 2022-04-06 20:43 | 2022-04-07 23:54 | 598 | 027:11 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1631 | 2022-04-06 | 975338 | keep | 0 | Apr | 2022 | 0.6643 | 0.0004073 | Sustained | FALSE | FALSE | TMED_Event | 598
CAGUAS | 2022-04-06 20:43 | 2022-04-07 23:56 | 2486 | 027:13 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1633 | 2022-04-06 | 4059638 | keep | 0 | Apr | 2022 | 2.765 | 0.0016932 | Sustained | FALSE | FALSE | TMED_Event | 2486
CAGUAS | 2022-04-06 20:43 | 2022-04-08 03:19 | 1403 | 030:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1836 | 2022-04-06 | 2575908 | keep | 0 | Apr | 2022 | 1.7544 | 0.00095558 | Sustained | FALSE | FALSE | TMED_Event | 1403
CAGUAS | 2022-04-06 20:43 | 2022-04-07 23:56 | 1001 | 027:13 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1633 | 2022-04-06 | 1634633 | keep | 0 | Apr | 2022 | 1.1133 | 0.00068178 | Sustained | FALSE | FALSE | TMED_Event | 1001
CAGUAS | 2022-04-06 20:43 | 2022-04-08 00:09 | 889 | 027:26 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1646 | 2022-04-06 | 1463294 | keep | 0 | Apr | 2022 | 0.99664 | 0.00060549 | Sustained | FALSE | FALSE | TMED_Event | 889
CAGUAS | 2022-04-06 20:43 | 2022-04-07 23:57 | 2435 | 027:14 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 3602-01 | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1634 | 2022-04-06 | 3978790 | keep | 0 | Apr | 2022 | 2.7099 | 0.0016585 | Sustained | FALSE | FALSE | TMED_Event | 2435
CAGUAS | 2022-04-06 20:43 | 2022-04-08 19:46 | 3463 | 047:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2823 | 2022-04-06 | 9776049 | keep | 0 | Apr | 2022 | 6.6584 | 0.0023586 | Sustained | FALSE | FALSE | TMED_Event | 3463
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 17:03 | 2725 | 044:20 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2660 | 2022-04-06 | 7248500 | keep | 0 | Apr | 2022 | 4.9369 | 0.001856 | Sustained | FALSE | FALSE | TMED_Event | 2725
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 09:07 | 1834 | 036:24 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2184 | 2022-04-06 | 4005456 | keep | 0 | Apr | 2022 | 2.7281 | 0.0012491 | Sustained | FALSE | FALSE | TMED_Event | 1834
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 00:37 | 1437 | 027:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1674 | 2022-04-06 | 2405538 | keep | 0 | Apr | 2022 | 1.6384 | 0.00097873 | Sustained | FALSE | FALSE | TMED_Event | 1437
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 09:17 | 2565 | 036:34 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA X 3502-02 | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2194 | 2022-04-06 | 5627610 | keep | 0 | Apr | 2022 | 3.8329 | 0.001747 | Sustained | FALSE | FALSE | TMED_Event | 2565
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 09:17 | 3565 | 036:34 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2194 | 2022-04-06 | 7821610 | keep | 0 | Apr | 2022 | 5.3273 | 0.0024281 | Sustained | FALSE | FALSE | TMED_Event | 3565
CAGUAS | 2022-04-06 20:43 | 2022-04-09 00:47 | 1017 | 052:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3124 | 2022-04-06 | 3177108 | keep | 0 | Apr | 2022 | 2.1639 | 0.00069267 | Sustained | FALSE | FALSE | TMED_Event | 1017
CAGUAS | 2022-04-06 20:43 | 2022-04-09 00:48 | 1017 | 052:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3125 | 2022-04-06 | 3178125 | keep | 0 | Apr | 2022 | 2.1646 | 0.00069267 | Sustained | FALSE | FALSE | TMED_Event | 1017
CAGUAS | 2022-04-06 20:43 | 2022-04-09 00:48 | 1854 | 052:05 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3125 | 2022-04-06 | 5793750 | keep | 0 | Apr | 2022 | 3.9461 | 0.0012628 | Sustained | FALSE | FALSE | TMED_Event | 1854
CAGUAS | 2022-04-06 20:43 | 2022-04-07 23:49 | 2859 | 027:06 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1626 | 2022-04-06 | 4648734 | keep | 0 | Apr | 2022 | 3.1662 | 0.0019473 | Sustained | FALSE | FALSE | TMED_Event | 2859
CAGUAS | 2022-04-06 20:43 | 2022-04-07 23:57 | 1565 | 027:14 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1634 | 2022-04-06 | 2557210 | keep | 0 | Apr | 2022 | 1.7417 | 0.0010659 | Sustained | FALSE | FALSE | TMED_Event | 1565
CAGUAS | 2022-04-06 20:43 | 2022-04-09 00:46 | 976 | 052:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3123 | 2022-04-06 | 3048048 | keep | 0 | Apr | 2022 | 2.076 | 0.00066475 | Sustained | FALSE | FALSE | TMED_Event | 976
CAGUAS | 2022-04-06 20:43 | 2022-04-09 00:46 | 548 | 052:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3123 | 2022-04-06 | 1711404 | keep | 0 | Apr | 2022 | 1.1656 | 0.00037324 | Sustained | FALSE | FALSE | TMED_Event | 548
CAGUAS | 2022-04-06 20:43 | 2022-04-08 23:37 | 315 | 050:54 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3054 | 2022-04-06 | 962010 | keep | 0 | Apr | 2022 | 0.65522 | 0.00021455 | Sustained | FALSE | FALSE | TMED_Event | 315
CAGUAS | 2022-04-06 20:43 | 2022-04-08 09:19 | 870 | 036:36 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040800000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2196 | 2022-04-06 | 1910520 | keep | 0 | Apr | 2022 | 1.3012 | 0.00059255 | Sustained | FALSE | FALSE | TMED_Event | 870
CAGUAS | 2022-04-06 20:43 | 2022-04-08 20:30 | 2906 | 047:47 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2867 | 2022-04-06 | 8331502 | keep | 0 | Apr | 2022 | 5.6745 | 0.0019793 | Sustained | FALSE | FALSE | TMED_Event | 2906
CAGUAS | 2022-04-06 20:43 | 2022-04-09 00:47 | 2343 | 052:04 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3124 | 2022-04-06 | 7319532 | keep | 0 | Apr | 2022 | 4.9853 | 0.0015958 | Sustained | FALSE | FALSE | TMED_Event | 2343
CAGUAS | 2022-04-06 20:43 | 2022-04-08 12:39 | 327 | 039:56 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040900000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2396 | 2022-04-06 | 783492 | keep | 0 | Apr | 2022 | 0.53363 | 0.00022272 | Sustained | FALSE | FALSE | TMED_Event | 327
CAGUAS | 2022-04-06 20:43 | 2022-04-07 21:16 | 1843 | 024:33 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1473 | 2022-04-06 | 2714739 | keep | 0 | Apr | 2022 | 1.849 | 0.0012553 | Sustained | FALSE | FALSE | TMED_Event | 1843
CAGUAS | 2022-04-06 20:43 | 2022-04-08 01:00 | 2203 | 028:17 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1697 | 2022-04-06 | 3738491 | keep | 0 | Apr | 2022 | 2.5463 | 0.0015005 | Sustained | FALSE | FALSE | TMED_Event | 2203
CAGUAS | 2022-04-06 20:43 | 2022-04-07 15:24 | 2457 | 018:41 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1121 | 2022-04-06 | 2754297 | keep | 0 | Apr | 2022 | 1.8759 | 0.0016735 | Sustained | FALSE | FALSE | TMED_Event | 2457
FAJARDO | 2022-04-06 20:43 | 2022-04-07 08:09 | 293 | 011:26 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 686 | 2022-04-06 | 200998 | keep | 0 | Apr | 2022 | 0.1369 | 0.00019956 | Sustained | FALSE | FALSE | TMED_Event | 293
FAJARDO | 2022-04-06 20:43 | 2022-04-07 08:09 | 1215 | 011:26 | S | LINEA DE TRANSMISION | APAGON GENERAL | R22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 686 | 2022-04-06 | 833490 | keep | 0 | Apr | 2022 | 0.56769 | 0.00082753 | Sustained | FALSE | FALSE | TMED_Event | 1215
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 05:51 | 386 | 057:08 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700108 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3428 | 2022-04-06 | 1323208 | keep | 0 | Apr | 2022 | 0.90123 | 0.0002629 | Sustained | FALSE | FALSE | TMED_Event | 386
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 05:51 | 610 | 057:08 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700108 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3428 | 2022-04-06 | 2091080 | keep | 0 | Apr | 2022 | 1.4242 | 0.00041547 | Sustained | FALSE | FALSE | TMED_Event | 610
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 06:51 | 1785 | 058:08 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700108 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3488 | 2022-04-06 | 6226080 | keep | 0 | Apr | 2022 | 4.2406 | 0.0012158 | Sustained | FALSE | FALSE | TMED_Event | 1785
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 05:51 | 1233 | 057:08 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700108 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3428 | 2022-04-06 | 4226724 | keep | 0 | Apr | 2022 | 2.8788 | 0.00083979 | Sustained | FALSE | FALSE | TMED_Event | 1233
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 05:24 | 584 | 056:41 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700177 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3401 | 2022-04-06 | 1986184 | keep | 0 | Apr | 2022 | 1.3528 | 0.00039776 | Sustained | FALSE | FALSE | TMED_Event | 584
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 05:24 | 1658 | 056:41 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700177 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3401 | 2022-04-06 | 5638858 | keep | 0 | Apr | 2022 | 3.8406 | 0.0011293 | Sustained | FALSE | FALSE | TMED_Event | 1658
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 05:24 | 630 | 056:41 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700177 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3401 | 2022-04-06 | 2142630 | keep | 0 | Apr | 2022 | 1.4593 | 0.00042909 | Sustained | FALSE | FALSE | TMED_Event | 630
GUAYAMA | 2022-04-06 20:43 | 2022-04-07 12:23 | 4132 | 015:40 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR SE TRANSFIERE CARGA A 4006-05 CERRANDO AMARRE CON 4003-02 EN SUBESTACION DE JOBOS TC | P22040700244 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 940 | 2022-04-06 | 3884080 | keep | 0 | Apr | 2022 | 2.6454 | 0.0028143 | Sustained | FALSE | FALSE | TMED_Event | 4132
GUAYAMA | 2022-04-06 20:43 | 2022-04-07 12:23 | 4279 | 015:40 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040700244 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 940 | 2022-04-06 | 4022260 | keep | 0 | Apr | 2022 | 2.7395 | 0.0029144 | Sustained | FALSE | FALSE | TMED_Event | 4279
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 05:02 | 1945 | 056:19 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR CARGA TRANSFERIDA AL 4006-04 | P22040700244 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3379 | 2022-04-06 | 6572155 | keep | 0 | Apr | 2022 | 4.4763 | 0.0013247 | Sustained | FALSE | FALSE | TMED_Event | 1945
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 05:02 | 1173 | 056:19 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700244 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3379 | 2022-04-06 | 3963567 | keep | 0 | Apr | 2022 | 2.6996 | 0.00079892 | Sustained | FALSE | FALSE | TMED_Event | 1173
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 05:02 | 215 | 056:19 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR LLEVA LA CARGA DEL 4003-03 | P22040700244 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3379 | 2022-04-06 | 726485 | keep | 0 | Apr | 2022 | 0.49481 | 0.00014644 | Sustained | FALSE | FALSE | TMED_Event | 215
GUAYAMA | 2022-04-06 20:43 | 2022-04-07 12:23 | 464 | 015:40 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040700244 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 940 | 2022-04-06 | 436160 | keep | 0 | Apr | 2022 | 0.29707 | 0.00031603 | Sustained | FALSE | FALSE | TMED_Event | 464
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 04:40 | 2100 | 055:57 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700181 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3357 | 2022-04-06 | 7049700 | keep | 0 | Apr | 2022 | 4.8015 | 0.0014303 | Sustained | FALSE | FALSE | TMED_Event | 2100
GUAYAMA | 2022-04-06 20:43 | 2022-04-08 09:18 | 922 | 036:35 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700181 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2195 | 2022-04-06 | 2023790 | keep | 0 | Apr | 2022 | 1.3784 | 0.00062797 | Sustained | FALSE | FALSE | TMED_Event | 922
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 04:40 | 1676 | 055:57 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700181 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3357 | 2022-04-06 | 5626332 | keep | 0 | Apr | 2022 | 3.8321 | 0.0011415 | Sustained | FALSE | FALSE | TMED_Event | 1676
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 04:40 | 2844 | 055:57 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700181 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3357 | 2022-04-06 | 9547308 | keep | 0 | Apr | 2022 | 6.5026 | 0.001937 | Sustained | FALSE | FALSE | TMED_Event | 2844
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 04:18 | 2775 | 055:35 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700184 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3335 | 2022-04-06 | 9254625 | keep | 0 | Apr | 2022 | 6.3033 | 0.00189 | Sustained | FALSE | FALSE | TMED_Event | 2775
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 00:44 | 1457 | 052:01 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040600184 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3121 | 2022-04-06 | 4547297 | keep | 0 | Apr | 2022 | 3.0971 | 0.00099236 | Sustained | FALSE | FALSE | TMED_Event | 1457
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 04:18 | 1086 | 055:35 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700184 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3335 | 2022-04-06 | 3621810 | keep | 0 | Apr | 2022 | 2.4668 | 0.00073967 | Sustained | FALSE | FALSE | TMED_Event | 1086
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 04:18 | 2134 | 055:35 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700184 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3335 | 2022-04-06 | 7116890 | keep | 0 | Apr | 2022 | 4.8473 | 0.0014535 | Sustained | FALSE | FALSE | TMED_Event | 2134
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 01:39 | 1464 | 052:56 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700185 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3176 | 2022-04-06 | 4649664 | keep | 0 | Apr | 2022 | 3.1669 | 0.00099712 | Sustained | FALSE | FALSE | TMED_Event | 1464
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 01:39 | 1833 | 052:56 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700185 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3176 | 2022-04-06 | 5821608 | keep | 0 | Apr | 2022 | 3.9651 | 0.0012484 | Sustained | FALSE | FALSE | TMED_Event | 1833
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 01:39 | 1565 | 052:56 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700185 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3176 | 2022-04-06 | 4970440 | keep | 0 | Apr | 2022 | 3.3853 | 0.0010659 | Sustained | FALSE | FALSE | TMED_Event | 1565
GUAYAMA | 2022-04-06 20:43 | 2022-04-09 01:39 | 977 | 052:56 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700185 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3176 | 2022-04-06 | 3102952 | keep | 0 | Apr | 2022 | 2.1134 | 0.00066543 | Sustained | FALSE | FALSE | TMED_Event | 977
PONCE | 2022-04-06 20:43 | 2022-04-07 23:56 | 1922 | 027:13 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040800003 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1633 | 2022-04-06 | 3138626 | keep | 0 | Apr | 2022 | 2.1377 | 0.0013091 | Sustained | FALSE | FALSE | TMED_Event | 1922
PONCE | 2022-04-06 20:43 | 2022-04-07 23:56 | 2235 | 027:13 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040800003 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1633 | 2022-04-06 | 3649755 | keep | 0 | Apr | 2022 | 2.4858 | 0.0015222 | Sustained | FALSE | FALSE | TMED_Event | 2235
PONCE | 2022-04-06 20:43 | 2022-04-07 23:56 | 713 | 027:13 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040800003 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1633 | 2022-04-06 | 1164329 | keep | 0 | Apr | 2022 | 0.79302 | 0.00048562 | Sustained | FALSE | FALSE | TMED_Event | 713
PONCE | 2022-04-06 20:43 | 2022-04-07 23:56 | 1067 | 027:13 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040800003 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1633 | 2022-04-06 | 1742411 | keep | 0 | Apr | 2022 | 1.1867 | 0.00072673 | Sustained | FALSE | FALSE | TMED_Event | 1067
PONCE | 2022-04-06 20:43 | 2022-04-07 22:57 | 75 | 026:14 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040600160 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1574 | 2022-04-06 | 118050 | keep | 0 | Apr | 2022 | 0.080403 | 5.1082e-05 | Sustained | FALSE | FALSE | TMED_Event | 75
PONCE | 2022-04-06 20:43 | 2022-04-07 22:57 | 449 | 026:14 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040600160 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1574 | 2022-04-06 | 706726 | keep | 0 | Apr | 2022 | 0.48135 | 0.00030581 | Sustained | FALSE | FALSE | TMED_Event | 449
PONCE | 2022-04-06 20:43 | 2022-04-08 16:05 | 1093 | 043:22 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040600189 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2602 | 2022-04-06 | 2843986 | keep | 0 | Apr | 2022 | 1.937 | 0.00074444 | Sustained | FALSE | FALSE | TMED_Event | 1093
PONCE | 2022-04-06 20:43 | 2022-04-09 01:42 | 1067 | 052:59 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700190 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3179 | 2022-04-06 | 3391993 | keep | 0 | Apr | 2022 | 2.3103 | 0.00072673 | Sustained | FALSE | FALSE | TMED_Event | 1067
PONCE | 2022-04-06 20:43 | 2022-04-09 02:27 | 836 | 053:44 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700190 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3224 | 2022-04-06 | 2695264 | keep | 0 | Apr | 2022 | 1.8357 | 0.0005694 | Sustained | FALSE | FALSE | TMED_Event | 836
PONCE | 2022-04-06 20:43 | 2022-04-09 02:29 | 1339 | 053:46 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700190 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3226 | 2022-04-06 | 4319614 | keep | 0 | Apr | 2022 | 2.9421 | 0.00091199 | Sustained | FALSE | FALSE | TMED_Event | 1339
PONCE | 2022-04-06 20:43 | 2022-04-09 01:40 | 1295 | 052:57 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700190 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3177 | 2022-04-06 | 4114215 | keep | 0 | Apr | 2022 | 2.8022 | 0.00088202 | Sustained | FALSE | FALSE | TMED_Event | 1295
PONCE | 2022-04-06 20:43 | 2022-04-07 18:11 | 978 | 021:28 | T | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700081 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1288 | 2022-04-06 | 1259664 | keep | 0 | Apr | 2022 | 0.85795 | 0.00066611 | Sustained | FALSE | FALSE | TMED_Event | 978
PONCE | 2022-04-06 20:43 | 2022-04-09 00:37 | 1730 | 051:54 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700080 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3114 | 2022-04-06 | 5387220 | keep | 0 | Apr | 2022 | 3.6692 | 0.0011783 | Sustained | FALSE | FALSE | TMED_Event | 1730
PONCE | 2022-04-06 20:43 | 2022-04-07 18:11 | 1320 | 021:28 | S | LINEA DE TRANSMISION | AVERIA INTERRUPTOR 0082 DE COSTA SUR | P22040700082 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1288 | 2022-04-06 | 1700160 | keep | 0 | Apr | 2022 | 1.158 | 0.00089905 | Sustained | FALSE | FALSE | TMED_Event | 1320
PONCE | 2022-04-06 20:43 | 2022-04-07 18:11 | 274 | 021:28 | S | LINEA DE TRANSMISION | AVERIA INTERRUPTOR 0082 DE COSTA SUR | P22040700082 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1288 | 2022-04-06 | 352912 | keep | 0 | Apr | 2022 | 0.24037 | 0.00018662 | Sustained | FALSE | FALSE | TMED_Event | 274
PONCE | 2022-04-06 20:43 | 2022-04-09 03:22 | 891 | 054:39 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700085 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3279 | 2022-04-06 | 2921589 | keep | 0 | Apr | 2022 | 1.9899 | 0.00060686 | Sustained | FALSE | FALSE | TMED_Event | 891
PONCE | 2022-04-06 20:43 | 2022-04-09 03:22 | 527 | 054:39 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700085 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3279 | 2022-04-06 | 1728033 | keep | 0 | Apr | 2022 | 1.177 | 0.00035894 | Sustained | FALSE | FALSE | TMED_Event | 527
PONCE | 2022-04-06 20:43 | 2022-04-09 03:18 | 542 | 054:35 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700085 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3275 | 2022-04-06 | 1775050 | keep | 0 | Apr | 2022 | 1.209 | 0.00036915 | Sustained | FALSE | FALSE | TMED_Event | 542
PONCE | 2022-04-06 20:43 | 2022-04-07 23:46 | 1293 | 027:03 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700088 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1623 | 2022-04-06 | 2098539 | keep | 0 | Apr | 2022 | 1.4293 | 0.00088066 | Sustained | FALSE | FALSE | TMED_Event | 1293
PONCE | 2022-04-06 20:43 | 2022-04-07 23:46 | 426 | 027:03 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700088 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1623 | 2022-04-06 | 691398 | keep | 0 | Apr | 2022 | 0.47091 | 0.00029015 | Sustained | FALSE | FALSE | TMED_Event | 426
PONCE | 2022-04-06 20:43 | 2022-04-07 23:46 | 1556 | 027:03 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700088 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1623 | 2022-04-06 | 2525388 | keep | 0 | Apr | 2022 | 1.72 | 0.0010598 | Sustained | FALSE | FALSE | TMED_Event | 1556
PONCE | 2022-04-06 20:43 | 2022-04-07 23:16 | 2751 | 026:33 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700071 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1593 | 2022-04-06 | 4382343 | keep | 0 | Apr | 2022 | 2.9848 | 0.0018737 | Sustained | FALSE | FALSE | TMED_Event | 2751
PONCE | 2022-04-06 20:43 | 2022-04-07 23:16 | 576 | 026:33 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700071 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1593 | 2022-04-06 | 917568 | keep | 0 | Apr | 2022 | 0.62495 | 0.00039231 | Sustained | FALSE | FALSE | TMED_Event | 576
PONCE | 2022-04-06 20:43 | 2022-04-07 23:16 | 2584 | 026:33 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700071 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1593 | 2022-04-06 | 4116312 | keep | 0 | Apr | 2022 | 2.8036 | 0.00176 | Sustained | FALSE | FALSE | TMED_Event | 2584
PONCE | 2022-04-06 20:43 | 2022-04-07 23:16 | 1606 | 026:33 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700071 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1593 | 2022-04-06 | 2558358 | keep | 0 | Apr | 2022 | 1.7425 | 0.0010938 | Sustained | FALSE | FALSE | TMED_Event | 1606
PONCE | 2022-04-06 20:43 | 2022-04-07 23:16 | 29 | 026:33 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700071 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1593 | 2022-04-06 | 46197 | keep | 0 | Apr | 2022 | 0.031465 | 1.9752e-05 | Sustained | FALSE | FALSE | TMED_Event | 29
PONCE | 2022-04-06 20:43 | 2022-04-07 23:16 | 4035 | 026:33 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700068 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1593 | 2022-04-06 | 6427755 | keep | 0 | Apr | 2022 | 4.3779 | 0.0027482 | Sustained | FALSE | FALSE | TMED_Event | 4035
PONCE | 2022-04-06 20:43 | 2022-04-07 23:16 | 3718 | 026:33 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700068 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1593 | 2022-04-06 | 5922774 | keep | 0 | Apr | 2022 | 4.034 | 0.0025323 | Sustained | FALSE | FALSE | TMED_Event | 3718
PONCE | 2022-04-06 20:43 | 2022-04-09 01:38 | 1212 | 052:55 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040600163 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3175 | 2022-04-06 | 3848100 | keep | 0 | Apr | 2022 | 2.6209 | 0.00082549 | Sustained | FALSE | FALSE | TMED_Event | 1212
PONCE | 2022-04-06 20:43 | 2022-04-09 02:59 | 200 | 054:16 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040600164 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3256 | 2022-04-06 | 651200 | keep | 0 | Apr | 2022 | 0.44353 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
PONCE | 2022-04-06 20:43 | 2022-04-09 02:59 | 423 | 054:16 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040600164 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3256 | 2022-04-06 | 1377288 | keep | 0 | Apr | 2022 | 0.93806 | 0.0002881 | Sustained | FALSE | FALSE | TMED_Event | 423
PONCE | 2022-04-06 20:43 | 2022-04-09 01:38 | 520 | 052:55 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040600199 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3175 | 2022-04-06 | 1651000 | keep | 0 | Apr | 2022 | 1.1245 | 0.00035417 | Sustained | FALSE | FALSE | TMED_Event | 520
PONCE | 2022-04-06 20:43 | 2022-04-09 04:49 | 1078 | 056:06 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700038 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3366 | 2022-04-06 | 3628548 | keep | 0 | Apr | 2022 | 2.4714 | 0.00073422 | Sustained | FALSE | FALSE | TMED_Event | 1078
PONCE | 2022-04-06 20:43 | 2022-04-09 04:49 | 1109 | 056:06 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700038 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3366 | 2022-04-06 | 3732894 | keep | 0 | Apr | 2022 | 2.5425 | 0.00075533 | Sustained | FALSE | FALSE | TMED_Event | 1109
PONCE | 2022-04-06 20:43 | 2022-04-09 04:50 | 2689 | 056:07 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700038 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3367 | 2022-04-06 | 9053863 | keep | 0 | Apr | 2022 | 6.1665 | 0.0018315 | Sustained | FALSE | FALSE | TMED_Event | 2689
PONCE | 2022-04-06 20:43 | 2022-04-09 04:49 | 1157 | 056:06 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700038 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3366 | 2022-04-06 | 3894462 | keep | 0 | Apr | 2022 | 2.6525 | 0.00078803 | Sustained | FALSE | FALSE | TMED_Event | 1157
PONCE | 2022-04-06 20:43 | 2022-04-09 01:35 | 1076 | 052:52 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700203 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3172 | 2022-04-06 | 3413072 | keep | 0 | Apr | 2022 | 2.3246 | 0.00073286 | Sustained | FALSE | FALSE | TMED_Event | 1076
PONCE | 2022-04-06 20:43 | 2022-04-09 01:39 | 595 | 052:56 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700203 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3176 | 2022-04-06 | 1889720 | keep | 0 | Apr | 2022 | 1.2871 | 0.00040525 | Sustained | FALSE | FALSE | TMED_Event | 595
PONCE | 2022-04-06 20:43 | 2022-04-09 01:39 | 1007 | 052:56 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700203 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3176 | 2022-04-06 | 3198232 | keep | 0 | Apr | 2022 | 2.1783 | 0.00068586 | Sustained | FALSE | FALSE | TMED_Event | 1007
PONCE | 2022-04-06 20:43 | 2022-04-09 01:39 | 9 | 052:56 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700203 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3176 | 2022-04-06 | 28584 | keep | 0 | Apr | 2022 | 0.019468 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
PONCE | 2022-04-06 20:43 | 2022-04-08 03:31 | 3744 | 030:48 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040600162 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1848 | 2022-04-06 | 6918912 | keep | 0 | Apr | 2022 | 4.7124 | 0.00255 | Sustained | FALSE | FALSE | TMED_Event | 3744
PONCE | 2022-04-06 20:43 | 2022-04-08 03:35 | 2379 | 030:52 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040600158 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1852 | 2022-04-06 | 4405908 | keep | 0 | Apr | 2022 | 3.0008 | 0.0016203 | Sustained | FALSE | FALSE | TMED_Event | 2379
PONCE | 2022-04-06 20:43 | 2022-04-08 09:18 | 778 | 036:35 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040800345 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2195 | 2022-04-06 | 1707710 | keep | 0 | Apr | 2022 | 1.1631 | 0.00052989 | Sustained | FALSE | FALSE | TMED_Event | 778
PONCE | 2022-04-06 20:43 | 2022-04-08 09:18 | 1746 | 036:35 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040800168 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2195 | 2022-04-06 | 3832470 | keep | 0 | Apr | 2022 | 2.6103 | 0.0011892 | Sustained | FALSE | FALSE | TMED_Event | 1746
PONCE | 2022-04-06 20:43 | 2022-04-09 01:39 | 11 | 052:56 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040600159 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3176 | 2022-04-06 | 34936 | keep | 0 | Apr | 2022 | 0.023795 | 7.492e-06 | Sustained | FALSE | FALSE | TMED_Event | 11
PONCE | 2022-04-06 20:43 | 2022-04-07 18:00 | 23 | 021:17 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700039 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1277 | 2022-04-06 | 29371 | keep | 0 | Apr | 2022 | 0.020004 | 1.5665e-05 | Sustained | FALSE | FALSE | TMED_Event | 23
PONCE | 2022-04-06 20:43 | 2022-04-07 18:00 | 969 | 021:17 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700040 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1277 | 2022-04-06 | 1237413 | keep | 0 | Apr | 2022 | 0.8428 | 0.00065998 | Sustained | FALSE | FALSE | TMED_Event | 969
PONCE | 2022-04-06 20:43 | 2022-04-07 18:00 | 1712 | 021:17 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700041 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1277 | 2022-04-06 | 2186224 | keep | 0 | Apr | 2022 | 1.489 | 0.001166 | Sustained | FALSE | FALSE | TMED_Event | 1712
PONCE | 2022-04-06 20:43 | 2022-04-07 18:00 | 18 | 021:17 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700042 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1277 | 2022-04-06 | 22986 | keep | 0 | Apr | 2022 | 0.015656 | 1.226e-05 | Sustained | FALSE | FALSE | TMED_Event | 18
PONCE | 2022-04-06 20:43 | 2022-04-07 18:00 | 494 | 021:17 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700042 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1277 | 2022-04-06 | 630838 | keep | 0 | Apr | 2022 | 0.42966 | 0.00033646 | Sustained | FALSE | FALSE | TMED_Event | 494
PONCE | 2022-04-06 20:43 | 2022-04-09 03:52 | 1952 | 055:09 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700167 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3309 | 2022-04-06 | 6459168 | keep | 0 | Apr | 2022 | 4.3993 | 0.0013295 | Sustained | FALSE | FALSE | TMED_Event | 1952
PONCE | 2022-04-06 20:43 | 2022-04-09 03:52 | 607 | 055:09 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700167 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3309 | 2022-04-06 | 2008563 | keep | 0 | Apr | 2022 | 1.368 | 0.00041342 | Sustained | FALSE | FALSE | TMED_Event | 607
PONCE | 2022-04-06 20:43 | 2022-04-09 03:52 | 292 | 055:09 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700167 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3309 | 2022-04-06 | 966228 | keep | 0 | Apr | 2022 | 0.65809 | 0.00019888 | Sustained | FALSE | FALSE | TMED_Event | 292
PONCE | 2022-04-06 20:43 | 2022-04-09 03:52 | 462 | 055:09 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700167 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3309 | 2022-04-06 | 1528758 | keep | 0 | Apr | 2022 | 1.0412 | 0.00031467 | Sustained | FALSE | FALSE | TMED_Event | 462
PONCE | 2022-04-06 20:43 | 2022-04-09 03:52 | 1 | 055:09 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700167 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3309 | 2022-04-06 | 3309 | keep | 0 | Apr | 2022 | 0.0022537 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
PONCE | 2022-04-06 20:43 | 2022-04-07 16:07 | 349 | 019:24 | T | LINEA DE TRANSMISION | BLACKOUT BKR QUEMADO EN SWITCH YARD DE COSTA SUR | P22040700044 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1164 | 2022-04-06 | 406236 | keep | 0 | Apr | 2022 | 0.27669 | 0.0002377 | Sustained | FALSE | FALSE | TMED_Event | 349
PONCE | 2022-04-06 20:43 | 2022-04-07 21:16 | 653 | 024:33 | T | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700213 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1473 | 2022-04-06 | 961869 | keep | 0 | Apr | 2022 | 0.65512 | 0.00044476 | Sustained | FALSE | FALSE | TMED_Event | 653
PONCE | 2022-04-06 20:43 | 2022-04-09 03:51 | 860 | 055:08 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040600214 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3308 | 2022-04-06 | 2844880 | keep | 0 | Apr | 2022 | 1.9376 | 0.00058574 | Sustained | FALSE | FALSE | TMED_Event | 860
PONCE | 2022-04-06 20:43 | 2022-04-08 08:51 | 948 | 036:08 | T | LINEA DE TRANSMISION | DEFICIENCIA EN GENERACION | P220406000XX | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2168 | 2022-04-06 | 2055264 | keep | 0 | Apr | 2022 | 1.3998 | 0.00064568 | Sustained | FALSE | FALSE | TMED_Event | 948
PONCE | 2022-04-06 20:43 | 2022-04-07 18:00 | 7 | 021:17 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040700041 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1277 | 2022-04-06 | 8939 | keep | 0 | Apr | 2022 | 0.0060883 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
PONCE | 2022-04-06 20:43 | 2022-04-07 16:07 | 114 | 019:24 | T | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700247 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1164 | 2022-04-06 | 132696 | keep | 0 | Apr | 2022 | 0.090379 | 7.7645e-05 | Sustained | FALSE | FALSE | TMED_Event | 114
PONCE | 2022-04-06 20:43 | 2022-04-08 12:38 | 120 | 039:55 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700217 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2395 | 2022-04-06 | 287400 | keep | 0 | Apr | 2022 | 0.19575 | 8.1731e-05 | Sustained | FALSE | FALSE | TMED_Event | 120
PONCE | 2022-04-06 20:43 | 2022-04-08 12:38 | 120 | 039:55 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR CARGA TRANSFERIDA AL 5016-02 | P22040700217 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2395 | 2022-04-06 | 287400 | keep | 0 | Apr | 2022 | 0.19575 | 8.1731e-05 | Sustained | FALSE | FALSE | TMED_Event | 120
PONCE | 2022-04-06 20:43 | 2022-04-08 01:36 | 2446 | 028:53 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR CARGA TRANSFERIDA AL 5018-03 | P22040700220 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1733 | 2022-04-06 | 4238918 | keep | 0 | Apr | 2022 | 2.8871 | 0.001666 | Sustained | FALSE | FALSE | TMED_Event | 2446
PONCE | 2022-04-06 20:43 | 2022-04-09 05:11 | 752 | 056:28 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR CARGA TRANSFERIDA AL 5018-04 | P22040700221 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3388 | 2022-04-06 | 2547776 | keep | 0 | Apr | 2022 | 1.7353 | 0.00051218 | Sustained | FALSE | FALSE | TMED_Event | 752
PONCE | 2022-04-06 20:43 | 2022-04-08 09:18 | 113 | 036:35 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR CARGA TRANSFERIDA AL 5004-08 | P22040700161 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2195 | 2022-04-06 | 248035 | keep | 0 | Apr | 2022 | 0.16894 | 7.6964e-05 | Sustained | FALSE | FALSE | TMED_Event | 113
PONCE | 2022-04-06 20:43 | 2022-04-07 18:41 | 253 | 021:58 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700046 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1318 | 2022-04-06 | 333454 | keep | 0 | Apr | 2022 | 0.22711 | 0.00017232 | Sustained | FALSE | FALSE | TMED_Event | 253
PONCE | 2022-04-06 20:43 | 2022-04-07 18:41 | 900 | 021:58 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700047 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1318 | 2022-04-06 | 1186200 | keep | 0 | Apr | 2022 | 0.80792 | 0.00061299 | Sustained | FALSE | FALSE | TMED_Event | 900
PONCE | 2022-04-06 20:43 | 2022-04-07 18:41 | 1615 | 021:58 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700048 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1318 | 2022-04-06 | 2128570 | keep | 0 | Apr | 2022 | 1.4498 | 0.0011 | Sustained | FALSE | FALSE | TMED_Event | 1615
PONCE | 2022-04-06 20:43 | 2022-04-07 18:41 | 3 | 021:58 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700049 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1318 | 2022-04-06 | 3954 | keep | 0 | Apr | 2022 | 0.0026931 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
PONCE | 2022-04-06 20:43 | 2022-04-09 01:45 | 2163 | 053:02 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700050 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3182 | 2022-04-06 | 6882666 | keep | 0 | Apr | 2022 | 4.6878 | 0.0014732 | Sustained | FALSE | FALSE | TMED_Event | 2163
PONCE | 2022-04-06 20:43 | 2022-04-07 20:50 | 1340 | 024:07 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700051 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1447 | 2022-04-06 | 1938980 | keep | 0 | Apr | 2022 | 1.3206 | 0.00091267 | Sustained | FALSE | FALSE | TMED_Event | 1340
PONCE | 2022-04-06 20:43 | 2022-04-08 20:56 | 2039 | 048:13 | T | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700052 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2893 | 2022-04-06 | 5898827 | keep | 0 | Apr | 2022 | 4.0177 | 0.0013888 | Sustained | FALSE | FALSE | TMED_Event | 2039
PONCE | 2022-04-06 20:43 | 2022-04-07 22:44 | 2113 | 026:01 | T | LINEA DE TRANSMISION | DEFICIENCIA EN GENERACION | P22040700053 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1561 | 2022-04-06 | 3298393 | keep | 0 | Apr | 2022 | 2.2465 | 0.0014392 | Sustained | FALSE | FALSE | TMED_Event | 2113
PONCE | 2022-04-06 20:43 | 2022-04-08 12:38 | 1478 | 039:55 | T | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700217 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2395 | 2022-04-06 | 3539810 | keep | 0 | Apr | 2022 | 2.4109 | 0.0010067 | Sustained | FALSE | FALSE | TMED_Event | 1478
PONCE | 2022-04-06 20:43 | 2022-04-08 22:44 | 396 | 050:01 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700054 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3001 | 2022-04-06 | 1188396 | keep | 0 | Apr | 2022 | 0.80941 | 0.00026971 | Sustained | FALSE | FALSE | TMED_Event | 396
PONCE | 2022-04-06 20:43 | 2022-04-09 01:36 | 1979 | 052:53 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700055 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3173 | 2022-04-06 | 6279367 | keep | 0 | Apr | 2022 | 4.2768 | 0.0013479 | Sustained | FALSE | FALSE | TMED_Event | 1979
PONCE | 2022-04-06 20:43 | 2022-04-09 05:10 | 3114 | 056:27 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700219 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3387 | 2022-04-06 | 10547118 | keep | 0 | Apr | 2022 | 7.1836 | 0.0021209 | Sustained | FALSE | FALSE | TMED_Event | 3114
PONCE | 2022-04-06 20:43 | 2022-04-09 01:36 | 5069 | 052:53 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700220 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3173 | 2022-04-06 | 16083937 | keep | 0 | Apr | 2022 | 10.9547 | 0.0034525 | Sustained | FALSE | FALSE | TMED_Event | 5069
PONCE | 2022-04-06 20:43 | 2022-04-09 05:11 | 2696 | 056:28 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700221 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3388 | 2022-04-06 | 9134048 | keep | 0 | Apr | 2022 | 6.2212 | 0.0018362 | Sustained | FALSE | FALSE | TMED_Event | 2696
PONCE | 2022-04-06 20:43 | 2022-04-09 04:53 | 5063 | 056:10 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700274 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3370 | 2022-04-06 | 17062310 | keep | 0 | Apr | 2022 | 11.6211 | 0.0034484 | Sustained | FALSE | FALSE | TMED_Event | 5063
PONCE | 2022-04-06 20:43 | 2022-04-09 11:13 | 1863 | 062:30 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700113 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3750 | 2022-04-06 | 6986250 | keep | 0 | Apr | 2022 | 4.7583 | 0.0012689 | Sustained | FALSE | FALSE | TMED_Event | 1863
PONCE | 2022-04-06 20:43 | 2022-04-09 11:13 | 708 | 062:30 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700113 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3750 | 2022-04-06 | 2655000 | keep | 0 | Apr | 2022 | 1.8083 | 0.00048222 | Sustained | FALSE | FALSE | TMED_Event | 708
PONCE | 2022-04-06 20:43 | 2022-04-09 00:27 | 167 | 051:44 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3104 | 2022-04-06 | 518368 | keep | 0 | Apr | 2022 | 0.35306 | 0.00011374 | Sustained | FALSE | FALSE | TMED_Event | 167
PONCE | 2022-04-06 20:43 | 2022-04-09 00:27 | 26 | 051:44 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3104 | 2022-04-06 | 80704 | keep | 0 | Apr | 2022 | 0.054967 | 1.7708e-05 | Sustained | FALSE | FALSE | TMED_Event | 26
YAUCO | 2022-04-06 20:43 | 2022-04-09 04:05 | 591 | 055:22 | S | LINEA DE TRANSMISION | DISPARO UNDAD COSTA SUR | P22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3322 | 2022-04-06 | 1963302 | keep | 0 | Apr | 2022 | 1.3372 | 0.00040253 | Sustained | FALSE | FALSE | TMED_Event | 591
YAUCO | 2022-04-06 20:43 | 2022-04-09 04:05 | 591 | 055:22 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700074 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3322 | 2022-04-06 | 1963302 | keep | 0 | Apr | 2022 | 1.3372 | 0.00040253 | Sustained | FALSE | FALSE | TMED_Event | 591
YAUCO | 2022-04-06 20:43 | 2022-04-09 01:48 | 1924 | 053:05 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700191 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3185 | 2022-04-06 | 6127940 | keep | 0 | Apr | 2022 | 4.1737 | 0.0013104 | Sustained | FALSE | FALSE | TMED_Event | 1924
YAUCO | 2022-04-06 20:43 | 2022-04-09 01:48 | 968 | 053:05 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700191 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3185 | 2022-04-06 | 3083080 | keep | 0 | Apr | 2022 | 2.0999 | 0.0006593 | Sustained | FALSE | FALSE | TMED_Event | 968
YAUCO | 2022-04-06 20:43 | 2022-04-09 01:48 | 680 | 053:05 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700191 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3185 | 2022-04-06 | 2165800 | keep | 0 | Apr | 2022 | 1.4751 | 0.00046314 | Sustained | FALSE | FALSE | TMED_Event | 680
YAUCO | 2022-04-06 20:43 | 2022-04-09 03:55 | 2246 | 055:12 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700191 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3312 | 2022-04-06 | 7438752 | keep | 0 | Apr | 2022 | 5.0665 | 0.0015297 | Sustained | FALSE | FALSE | TMED_Event | 2246
YAUCO | 2022-04-06 20:43 | 2022-04-07 23:46 | 2011 | 027:03 | T | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700194 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1623 | 2022-04-06 | 3263853 | keep | 0 | Apr | 2022 | 2.223 | 0.0013697 | Sustained | FALSE | FALSE | TMED_Event | 2011
YAUCO | 2022-04-06 20:43 | 2022-04-09 01:49 | 339 | 053:06 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700195 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3186 | 2022-04-06 | 1080054 | keep | 0 | Apr | 2022 | 0.73562 | 0.00023089 | Sustained | FALSE | FALSE | TMED_Event | 339
YAUCO | 2022-04-06 20:43 | 2022-04-08 21:50 | 2470 | 049:07 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700072 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2947 | 2022-04-06 | 7279090 | keep | 0 | Apr | 2022 | 4.9578 | 0.0016823 | Sustained | FALSE | FALSE | TMED_Event | 2470
YAUCO | 2022-04-06 20:43 | 2022-04-08 18:24 | 1182 | 045:41 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040700196 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2741 | 2022-04-06 | 3239862 | keep | 0 | Apr | 2022 | 2.2067 | 0.00080505 | Sustained | FALSE | FALSE | TMED_Event | 1182
YAUCO | 2022-04-06 20:43 | 2022-04-09 01:50 | 2340 | 053:07 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700197 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3187 | 2022-04-06 | 7457580 | keep | 0 | Apr | 2022 | 5.0793 | 0.0015938 | Sustained | FALSE | FALSE | TMED_Event | 2340
YAUCO | 2022-04-06 20:43 | 2022-04-09 01:50 | 1637 | 053:07 | T | LINEA DE TRANSMISION | DISPARO UNIDAD 5 DE COSTA SUR | P22040700198 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3187 | 2022-04-06 | 5217119 | keep | 0 | Apr | 2022 | 3.5534 | 0.001115 | Sustained | FALSE | FALSE | TMED_Event | 1637
YAUCO | 2022-04-06 20:43 | 2022-04-09 03:09 | 1475 | 054:26 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700065 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3266 | 2022-04-06 | 4817350 | keep | 0 | Apr | 2022 | 3.2811 | 0.0010046 | Sustained | FALSE | FALSE | TMED_Event | 1475
YAUCO | 2022-04-06 20:43 | 2022-04-09 03:10 | 661 | 054:27 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700065 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3267 | 2022-04-06 | 2159487 | keep | 0 | Apr | 2022 | 1.4708 | 0.0004502 | Sustained | FALSE | FALSE | TMED_Event | 661
YAUCO | 2022-04-06 20:43 | 2022-04-08 21:50 | 502 | 049:07 | T | LINEA DE TRANSMISION | INTERRUPTOR 0082 230K AVERIADO EN COSTA SUR | P22040700059 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2947 | 2022-04-06 | 1479394 | keep | 0 | Apr | 2022 | 1.0076 | 0.00034191 | Sustained | FALSE | FALSE | TMED_Event | 502
YAUCO | 2022-04-06 20:43 | 2022-04-08 22:04 | 2747 | 049:21 | T | LINEA DE TRANSMISION | INTERRUPTOR 0082 230K AVERIADO EN COSTA SUR | P22040700062 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2961 | 2022-04-06 | 8133867 | keep | 0 | Apr | 2022 | 5.5399 | 0.001871 | Sustained | FALSE | FALSE | TMED_Event | 2747
YAUCO | 2022-04-06 20:43 | 2022-04-09 04:01 | 1587 | 055:18 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700062 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3318 | 2022-04-06 | 5265666 | keep | 0 | Apr | 2022 | 3.5864 | 0.0010809 | Sustained | FALSE | FALSE | TMED_Event | 1587
YAUCO | 2022-04-06 20:43 | 2022-04-09 04:01 | 2671 | 055:18 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700063 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3318 | 2022-04-06 | 8862378 | keep | 0 | Apr | 2022 | 6.0361 | 0.0018192 | Sustained | FALSE | FALSE | TMED_Event | 2671
YAUCO | 2022-04-06 20:43 | 2022-04-09 02:17 | 508 | 053:34 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700064 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3214 | 2022-04-06 | 1632712 | keep | 0 | Apr | 2022 | 1.112 | 0.000346 | Sustained | FALSE | FALSE | TMED_Event | 508
YAUCO | 2022-04-06 20:43 | 2022-04-09 02:17 | 64 | 053:34 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700064 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3214 | 2022-04-06 | 205696 | keep | 0 | Apr | 2022 | 0.1401 | 4.359e-05 | Sustained | FALSE | FALSE | TMED_Event | 64
YAUCO | 2022-04-06 20:43 | 2022-04-09 06:14 | 207 | 057:31 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700066 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3451 | 2022-04-06 | 714357 | keep | 0 | Apr | 2022 | 0.48655 | 0.00014099 | Sustained | FALSE | FALSE | TMED_Event | 207
YAUCO | 2022-04-06 20:43 | 2022-04-09 06:14 | 286 | 057:31 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700066 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3451 | 2022-04-06 | 986986 | keep | 0 | Apr | 2022 | 0.67223 | 0.00019479 | Sustained | FALSE | FALSE | TMED_Event | 286
YAUCO | 2022-04-06 20:43 | 2022-04-08 20:29 | 1569 | 047:46 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040700209 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2866 | 2022-04-06 | 4496754 | keep | 0 | Apr | 2022 | 3.0627 | 0.0010686 | Sustained | FALSE | FALSE | TMED_Event | 1569
YAUCO | 2022-04-06 20:43 | 2022-04-08 20:08 | 2309 | 047:25 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040700210 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2845 | 2022-04-06 | 6569105 | keep | 0 | Apr | 2022 | 4.4742 | 0.0015726 | Sustained | FALSE | FALSE | TMED_Event | 2309
YAUCO | 2022-04-06 20:43 | 2022-04-08 23:37 | 2179 | 050:54 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040700211 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3054 | 2022-04-06 | 6654666 | keep | 0 | Apr | 2022 | 4.5325 | 0.0014841 | Sustained | FALSE | FALSE | TMED_Event | 2179
YAUCO | 2022-04-06 20:43 | 2022-04-09 01:50 | 2440 | 053:07 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040600212 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3187 | 2022-04-06 | 7776280 | keep | 0 | Apr | 2022 | 5.2964 | 0.0016619 | Sustained | FALSE | FALSE | TMED_Event | 2440
YAUCO | 2022-04-06 20:43 | 2022-04-09 04:00 | 1352 | 055:17 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040600206 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3317 | 2022-04-06 | 4484584 | keep | 0 | Apr | 2022 | 3.0544 | 0.00092084 | Sustained | FALSE | FALSE | TMED_Event | 1352
YAUCO | 2022-04-06 20:43 | 2022-04-09 00:35 | 3973 | 051:52 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040600207 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3112 | 2022-04-06 | 12363976 | keep | 0 | Apr | 2022 | 8.421 | 0.002706 | Sustained | FALSE | FALSE | TMED_Event | 3973
YAUCO | 2022-04-06 20:43 | 2022-04-09 04:00 | 2484 | 055:17 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040600208 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3317 | 2022-04-06 | 8239428 | keep | 0 | Apr | 2022 | 5.6118 | 0.0016918 | Sustained | FALSE | FALSE | TMED_Event | 2484
PONCE | 2022-04-06 20:43 | 2022-04-07 20:11 | 562 | 023:28 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700091 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1408 | 2022-04-06 | 791296 | keep | 0 | Apr | 2022 | 0.53895 | 0.00038278 | Sustained | FALSE | FALSE | TMED_Event | 562
PONCE | 2022-04-06 20:43 | 2022-04-07 20:11 | 688 | 023:28 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700092 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1408 | 2022-04-06 | 968704 | keep | 0 | Apr | 2022 | 0.65978 | 0.00046859 | Sustained | FALSE | FALSE | TMED_Event | 688
PONCE | 2022-04-06 20:43 | 2022-04-07 20:11 | 658 | 023:28 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700092 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1408 | 2022-04-06 | 926464 | keep | 0 | Apr | 2022 | 0.63101 | 0.00044816 | Sustained | FALSE | FALSE | TMED_Event | 658
PONCE | 2022-04-06 20:43 | 2022-04-08 00:41 | 1717 | 027:58 | T | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700093 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1678 | 2022-04-06 | 2881126 | keep | 0 | Apr | 2022 | 1.9623 | 0.0011694 | Sustained | FALSE | FALSE | TMED_Event | 1717
PONCE | 2022-04-06 20:43 | 2022-04-08 12:23 | 974 | 039:40 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR CARGA TRANSFERIDA AL 5802-04 | P22040700094 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 2318120 | keep | 0 | Apr | 2022 | 1.5789 | 0.00066339 | Sustained | FALSE | FALSE | TMED_Event | 974
PONCE | 2022-04-06 20:43 | 2022-04-09 04:14 | 1905 | 055:31 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700216 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3331 | 2022-04-06 | 6345555 | keep | 0 | Apr | 2022 | 4.3219 | 0.0012975 | Sustained | FALSE | FALSE | TMED_Event | 1905
PONCE | 2022-04-06 20:43 | 2022-04-08 12:23 | 1262 | 039:40 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700094 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 3003560 | keep | 0 | Apr | 2022 | 2.0457 | 0.00085954 | Sustained | FALSE | FALSE | TMED_Event | 1262
PONCE | 2022-04-06 20:43 | 2022-04-09 01:45 | 200 | 053:02 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700218 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3182 | 2022-04-06 | 636400 | keep | 0 | Apr | 2022 | 0.43345 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
PONCE | 2022-04-06 20:43 | 2022-04-07 20:11 | 4009 | 023:28 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700350 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1408 | 2022-04-06 | 5644672 | keep | 0 | Apr | 2022 | 3.8446 | 0.0027305 | Sustained | FALSE | FALSE | TMED_Event | 4009
PONCE | 2022-04-06 20:43 | 2022-04-08 00:41 | 222 | 027:58 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700096 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1678 | 2022-04-06 | 372516 | keep | 0 | Apr | 2022 | 0.25372 | 0.0001512 | Sustained | FALSE | FALSE | TMED_Event | 222
PONCE | 2022-04-06 20:43 | 2022-04-08 00:41 | 537 | 027:58 | S | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700096 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1678 | 2022-04-06 | 901086 | keep | 0 | Apr | 2022 | 0.61373 | 0.00036575 | Sustained | FALSE | FALSE | TMED_Event | 537
PONCE | 2022-04-06 20:43 | 2022-04-07 19:07 | 1033 | 022:24 | T | LINEA DE TRANSMISION | BREAKER 230KV SWICHYARD COSTA SUR QUEMADO | P22040700097 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1344 | 2022-04-06 | 1388352 | keep | 0 | Apr | 2022 | 0.9456 | 0.00070357 | Sustained | FALSE | FALSE | TMED_Event | 1033
PONCE | 2022-04-06 20:43 | 2022-04-09 01:45 | 485 | 053:02 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700099 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3182 | 2022-04-06 | 1543270 | keep | 0 | Apr | 2022 | 1.0511 | 0.00033033 | Sustained | FALSE | FALSE | TMED_Event | 485
PONCE | 2022-04-06 20:43 | 2022-04-07 01:45 | 732 | 005:02 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | P22040700100 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 302 | 2022-04-06 | 221064 | keep | 0 | Apr | 2022 | 0.15057 | 0.00049856 | Sustained | FALSE | FALSE | TMED_Event | 732
PONCE | 2022-04-06 20:43 | 2022-04-09 09:42 | 234 | 060:59 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3659 | 2022-04-06 | 856206 | keep | 0 | Apr | 2022 | 0.58316 | 0.00015938 | Sustained | FALSE | FALSE | TMED_Event | 234
PONCE | 2022-04-06 20:43 | 2022-04-08 23:40 | 234 | 050:57 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700101 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3057 | 2022-04-06 | 715338 | keep | 0 | Apr | 2022 | 0.48721 | 0.00015938 | Sustained | FALSE | FALSE | TMED_Event | 234
PONCE | 2022-04-06 20:43 | 2022-04-09 09:42 | 2468 | 060:59 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | P22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3659 | 2022-04-06 | 9030412 | keep | 0 | Apr | 2022 | 6.1506 | 0.0016809 | Sustained | FALSE | FALSE | TMED_Event | 2468
PONCE | 2022-04-06 20:43 | 2022-04-08 23:40 | 2468 | 050:57 | S | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700101 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3057 | 2022-04-06 | 7544676 | keep | 0 | Apr | 2022 | 5.1386 | 0.0016809 | Sustained | FALSE | FALSE | TMED_Event | 2468
PONCE | 2022-04-06 20:43 | 2022-04-09 01:48 | 2035 | 053:05 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 DE COSTA SUR | P22040700103 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3185 | 2022-04-06 | 6481475 | keep | 0 | Apr | 2022 | 4.4145 | 0.001386 | Sustained | FALSE | FALSE | TMED_Event | 2035
PONCE | 2022-04-06 20:43 | 2022-04-08 13:29 | 2308 | 040:46 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040700104 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2446 | 2022-04-06 | 5645368 | keep | 0 | Apr | 2022 | 3.845 | 0.001572 | Sustained | FALSE | FALSE | TMED_Event | 2308
PONCE | 2022-04-06 20:43 | 2022-04-08 12:23 | 1650 | 039:40 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040700105 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 3927000 | keep | 0 | Apr | 2022 | 2.6747 | 0.0011238 | Sustained | FALSE | FALSE | TMED_Event | 1650
PONCE | 2022-04-06 20:43 | 2022-04-09 05:19 | 1571 | 056:36 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040700106 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3396 | 2022-04-06 | 5335116 | keep | 0 | Apr | 2022 | 3.6337 | 0.00107 | Sustained | FALSE | FALSE | TMED_Event | 1571
PONCE | 2022-04-06 20:43 | 2022-04-09 05:19 | 752 | 056:36 | T | LINEA DE TRANSMISION | AVERIA EN INTERRUPTOR 0082 230KV EN COSTA SUR | P22040700107 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3396 | 2022-04-06 | 2553792 | keep | 0 | Apr | 2022 | 1.7394 | 0.00051218 | Sustained | FALSE | FALSE | TMED_Event | 752
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 12:23 | 873 | 039:40 | T | LINEA DE TRANSMISION | RELEVO DE CARGA POR AVERIA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 2077740 | keep | 0 | Apr | 2022 | 1.4151 | 0.0005946 | Sustained | FALSE | FALSE | TMED_Event | 873
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:10 | 1261 | 052:27 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3147 | 2022-04-06 | 3968367 | keep | 0 | Apr | 2022 | 2.7028 | 0.00085886 | Sustained | FALSE | FALSE | TMED_Event | 1261
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 16:55 | 2713 | 044:12 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2652 | 2022-04-06 | 7194876 | keep | 0 | Apr | 2022 | 4.9004 | 0.0018478 | Sustained | FALSE | FALSE | TMED_Event | 2713
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:10 | 51 | 052:27 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3147 | 2022-04-06 | 160497 | keep | 0 | Apr | 2022 | 0.10931 | 3.4736e-05 | Sustained | FALSE | FALSE | TMED_Event | 51
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:10 | 285 | 052:27 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3147 | 2022-04-06 | 896895 | keep | 0 | Apr | 2022 | 0.61087 | 0.00019411 | Sustained | FALSE | FALSE | TMED_Event | 285
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 04:17 | 192 | 007:34 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 454 | 2022-04-06 | 87168 | keep | 0 | Apr | 2022 | 0.05937 | 0.00013077 | Sustained | FALSE | FALSE | TMED_Event | 192
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 04:18 | 20 | 007:35 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 455 | 2022-04-06 | 9100 | keep | 0 | Apr | 2022 | 0.006198 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 04:18 | 406 | 007:35 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 455 | 2022-04-06 | 184730 | keep | 0 | Apr | 2022 | 0.12582 | 0.00027652 | Sustained | FALSE | FALSE | TMED_Event | 406
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 04:18 | 793 | 007:35 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 455 | 2022-04-06 | 360815 | keep | 0 | Apr | 2022 | 0.24575 | 0.00054011 | Sustained | FALSE | FALSE | TMED_Event | 793
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 04:18 | 1509 | 007:35 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 455 | 2022-04-06 | 686595 | keep | 0 | Apr | 2022 | 0.46764 | 0.0010278 | Sustained | FALSE | FALSE | TMED_Event | 1509
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 13:42 | 824 | 016:59 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1019 | 2022-04-06 | 839656 | keep | 0 | Apr | 2022 | 0.57189 | 0.00056122 | Sustained | FALSE | FALSE | TMED_Event | 824
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 13:42 | 146 | 016:59 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1019 | 2022-04-06 | 148774 | keep | 0 | Apr | 2022 | 0.10133 | 9.944e-05 | Sustained | FALSE | FALSE | TMED_Event | 146
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 13:42 | 667 | 016:59 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1019 | 2022-04-06 | 679673 | keep | 0 | Apr | 2022 | 0.46292 | 0.00045429 | Sustained | FALSE | FALSE | TMED_Event | 667
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:12 | 1142 | 052:29 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3149 | 2022-04-06 | 3596158 | keep | 0 | Apr | 2022 | 2.4493 | 0.00077781 | Sustained | FALSE | FALSE | TMED_Event | 1142
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:12 | 409 | 052:29 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3149 | 2022-04-06 | 1287941 | keep | 0 | Apr | 2022 | 0.87721 | 0.00027857 | Sustained | FALSE | FALSE | TMED_Event | 409
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:12 | 424 | 052:29 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3149 | 2022-04-06 | 1335176 | keep | 0 | Apr | 2022 | 0.90938 | 0.00028878 | Sustained | FALSE | FALSE | TMED_Event | 424
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 03:59 | 1145 | 007:16 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 436 | 2022-04-06 | 499220 | keep | 0 | Apr | 2022 | 0.34002 | 0.00077985 | Sustained | FALSE | FALSE | TMED_Event | 1145
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 03:59 | 1889 | 007:16 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 436 | 2022-04-06 | 823604 | keep | 0 | Apr | 2022 | 0.56095 | 0.0012866 | Sustained | FALSE | FALSE | TMED_Event | 1889
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 02:03 | 888 | 053:20 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3200 | 2022-04-06 | 2841600 | keep | 0 | Apr | 2022 | 1.9354 | 0.00060481 | Sustained | FALSE | FALSE | TMED_Event | 888
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 02:03 | 393 | 053:20 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3200 | 2022-04-06 | 1257600 | keep | 0 | Apr | 2022 | 0.85655 | 0.00026767 | Sustained | FALSE | FALSE | TMED_Event | 393
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 02:03 | 4 | 053:20 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3200 | 2022-04-06 | 12800 | keep | 0 | Apr | 2022 | 0.008718 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 09:26 | 372 | 012:43 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 763 | 2022-04-06 | 283836 | keep | 0 | Apr | 2022 | 0.19332 | 0.00025337 | Sustained | FALSE | FALSE | TMED_Event | 372
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:12 | 2530 | 052:29 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR TRNSFERIDO AL 6004-05 | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3149 | 2022-04-06 | 7966970 | keep | 0 | Apr | 2022 | 5.4263 | 0.0017232 | Sustained | FALSE | FALSE | TMED_Event | 2530
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 09:26 | 199 | 012:43 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 763 | 2022-04-06 | 151837 | keep | 0 | Apr | 2022 | 0.10342 | 0.00013554 | Sustained | FALSE | FALSE | TMED_Event | 199
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 15:40 | 1253 | 066:57 | S | LINEA DE TRANSMISION | DISPARO DE UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4017 | 2022-04-06 | 5033301 | keep | 0 | Apr | 2022 | 3.4282 | 0.00085341 | Sustained | FALSE | FALSE | TMED_Event | 1253
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 15:40 | 1266 | 066:57 | S | LINEA DE TRANSMISION | DISPARO DE UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4017 | 2022-04-06 | 5085522 | keep | 0 | Apr | 2022 | 3.4637 | 0.00086227 | Sustained | FALSE | FALSE | TMED_Event | 1266
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 15:40 | 411 | 066:57 | S | LINEA DE TRANSMISION | DISPARO DE UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4017 | 2022-04-06 | 1650987 | keep | 0 | Apr | 2022 | 1.1245 | 0.00027993 | Sustained | FALSE | FALSE | TMED_Event | 411
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 02:23 | 528 | 005:40 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 340 | 2022-04-06 | 179520 | keep | 0 | Apr | 2022 | 0.12227 | 0.00035962 | Sustained | FALSE | FALSE | TMED_Event | 528
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 00:43 | 4664 | 004:00 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 240 | 2022-04-06 | 1119360 | keep | 0 | Apr | 2022 | 0.76239 | 0.0031766 | Sustained | FALSE | FALSE | TMED_Event | 4664
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 00:37 | 2067 | 003:54 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 234 | 2022-04-06 | 483678 | keep | 0 | Apr | 2022 | 0.32943 | 0.0014078 | Sustained | FALSE | FALSE | TMED_Event | 2067
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 00:44 | 1352 | 004:01 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR LLEVA LA CARGA DEL 6014-03 | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 241 | 2022-04-06 | 325832 | keep | 0 | Apr | 2022 | 0.22192 | 0.00092084 | Sustained | FALSE | FALSE | TMED_Event | 1352
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 17:49 | 1444 | 045:06 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR SU CARGA POR EL 6014-02 | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2706 | 2022-04-06 | 3907464 | keep | 0 | Apr | 2022 | 2.6614 | 0.0009835 | Sustained | FALSE | FALSE | TMED_Event | 1444
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 17:49 | 3630 | 045:06 | T | LINEA DE TRANSMISION | AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2706 | 2022-04-06 | 9822780 | keep | 0 | Apr | 2022 | 6.6903 | 0.0024724 | Sustained | FALSE | FALSE | TMED_Event | 3630
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 00:44 | 871 | 004:01 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR LA CARGA POR 6012-05 | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 241 | 2022-04-06 | 209911 | keep | 0 | Apr | 2022 | 0.14297 | 0.00059323 | Sustained | FALSE | FALSE | TMED_Event | 871
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 13:42 | 312 | 016:59 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1019 | 2022-04-06 | 317928 | keep | 0 | Apr | 2022 | 0.21654 | 0.0002125 | Sustained | FALSE | FALSE | TMED_Event | 312
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 13:42 | 4641 | 016:59 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1019 | 2022-04-06 | 4729179 | keep | 0 | Apr | 2022 | 3.221 | 0.003161 | Sustained | FALSE | FALSE | TMED_Event | 4641
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 03:25 | 810 | 006:42 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 402 | 2022-04-06 | 325620 | keep | 0 | Apr | 2022 | 0.22178 | 0.00055169 | Sustained | FALSE | FALSE | TMED_Event | 810
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 03:25 | 1235 | 006:42 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 402 | 2022-04-06 | 496470 | keep | 0 | Apr | 2022 | 0.33814 | 0.00084115 | Sustained | FALSE | FALSE | TMED_Event | 1235
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 03:25 | 93 | 006:42 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 402 | 2022-04-06 | 37386 | keep | 0 | Apr | 2022 | 0.025463 | 6.3342e-05 | Sustained | FALSE | FALSE | TMED_Event | 93
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 03:25 | 1825 | 006:42 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 402 | 2022-04-06 | 733650 | keep | 0 | Apr | 2022 | 0.49969 | 0.001243 | Sustained | FALSE | FALSE | TMED_Event | 1825
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 03:25 | 3230 | 006:42 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 402 | 2022-04-06 | 1298460 | keep | 0 | Apr | 2022 | 0.88438 | 0.0021999 | Sustained | FALSE | FALSE | TMED_Event | 3230
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 15:40 | 863 | 066:57 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4017 | 2022-04-06 | 3466671 | keep | 0 | Apr | 2022 | 2.3611 | 0.00058779 | Sustained | FALSE | FALSE | TMED_Event | 863
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 15:40 | 309 | 066:57 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4017 | 2022-04-06 | 1241253 | keep | 0 | Apr | 2022 | 0.84541 | 0.00021046 | Sustained | FALSE | FALSE | TMED_Event | 309
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 15:40 | 176 | 066:57 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4017 | 2022-04-06 | 706992 | keep | 0 | Apr | 2022 | 0.48153 | 0.00011987 | Sustained | FALSE | FALSE | TMED_Event | 176
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 18:47 | 108 | 046:04 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2764 | 2022-04-06 | 298512 | keep | 0 | Apr | 2022 | 0.20332 | 7.3558e-05 | Sustained | FALSE | FALSE | TMED_Event | 108
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:50 | 281 | 053:07 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3187 | 2022-04-06 | 895547 | keep | 0 | Apr | 2022 | 0.60995 | 0.00019139 | Sustained | FALSE | FALSE | TMED_Event | 281
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:50 | 1252 | 053:07 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3187 | 2022-04-06 | 3990124 | keep | 0 | Apr | 2022 | 2.7177 | 0.00085273 | Sustained | FALSE | FALSE | TMED_Event | 1252
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 15:40 | 974 | 066:57 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4017 | 2022-04-06 | 3912558 | keep | 0 | Apr | 2022 | 2.6648 | 0.00066339 | Sustained | FALSE | FALSE | TMED_Event | 974
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:18 | 11 | 052:35 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3155 | 2022-04-06 | 34705 | keep | 0 | Apr | 2022 | 0.023637 | 7.492e-06 | Sustained | FALSE | FALSE | TMED_Event | 11
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 12:23 | 2077 | 039:40 | T | LINEA DE TRANSMISION | RELEVO DE CARGA POR AVERIA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 4943260 | keep | 0 | Apr | 2022 | 3.3668 | 0.0014146 | Sustained | FALSE | FALSE | TMED_Event | 2077
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:18 | 2 | 052:35 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3155 | 2022-04-06 | 6310 | keep | 0 | Apr | 2022 | 0.0042977 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:19 | 2560 | 052:36 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3156 | 2022-04-06 | 8079360 | keep | 0 | Apr | 2022 | 5.5028 | 0.0017436 | Sustained | FALSE | FALSE | TMED_Event | 2560
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:19 | 117 | 052:36 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3156 | 2022-04-06 | 369252 | keep | 0 | Apr | 2022 | 0.2515 | 7.9688e-05 | Sustained | FALSE | FALSE | TMED_Event | 117
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:19 | 1671 | 052:36 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3156 | 2022-04-06 | 5273676 | keep | 0 | Apr | 2022 | 3.5919 | 0.0011381 | Sustained | FALSE | FALSE | TMED_Event | 1671
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 12:23 | 527 | 039:40 | T | LINEA DE TRANSMISION | RELEVO DE CARGA POR AVERIA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 1254260 | keep | 0 | Apr | 2022 | 0.85427 | 0.00035894 | Sustained | FALSE | FALSE | TMED_Event | 527
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 12:23 | 671 | 039:40 | T | LINEA DE TRANSMISION | RELEVO DE CARGA POR AVERIA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 1596980 | keep | 0 | Apr | 2022 | 1.0877 | 0.00045702 | Sustained | FALSE | FALSE | TMED_Event | 671
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 12:23 | 2999 | 039:40 | T | LINEA DE TRANSMISION | RELEVO DE CARGA POR AVERIA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2380 | 2022-04-06 | 7137620 | keep | 0 | Apr | 2022 | 4.8614 | 0.0020426 | Sustained | FALSE | FALSE | TMED_Event | 2999
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 12:24 | 1597 | 039:41 | T | LINEA DE TRANSMISION | AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2381 | 2022-04-06 | 3802457 | keep | 0 | Apr | 2022 | 2.5898 | 0.0010877 | Sustained | FALSE | FALSE | TMED_Event | 1597
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:13 | 1268 | 052:30 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3150 | 2022-04-06 | 3994200 | keep | 0 | Apr | 2022 | 2.7204 | 0.00086363 | Sustained | FALSE | FALSE | TMED_Event | 1268
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:13 | 2064 | 052:30 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3150 | 2022-04-06 | 6501600 | keep | 0 | Apr | 2022 | 4.4282 | 0.0014058 | Sustained | FALSE | FALSE | TMED_Event | 2064
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:13 | 3036 | 052:30 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3150 | 2022-04-06 | 9563400 | keep | 0 | Apr | 2022 | 6.5136 | 0.0020678 | Sustained | FALSE | FALSE | TMED_Event | 3036
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 14:22 | 2952 | 017:39 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1059 | 2022-04-06 | 3126168 | keep | 0 | Apr | 2022 | 2.1292 | 0.0020106 | Sustained | FALSE | FALSE | TMED_Event | 2952
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 22:46 | 1339 | 026:03 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1563 | 2022-04-06 | 2092857 | keep | 0 | Apr | 2022 | 1.4254 | 0.00091199 | Sustained | FALSE | FALSE | TMED_Event | 1339
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 22:46 | 470 | 026:03 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1563 | 2022-04-06 | 734610 | keep | 0 | Apr | 2022 | 0.50034 | 0.00032011 | Sustained | FALSE | FALSE | TMED_Event | 470
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 22:46 | 2483 | 026:03 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1563 | 2022-04-06 | 3880929 | keep | 0 | Apr | 2022 | 2.6433 | 0.0016912 | Sustained | FALSE | FALSE | TMED_Event | 2483
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 22:46 | 2190 | 026:03 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1563 | 2022-04-06 | 3422970 | keep | 0 | Apr | 2022 | 2.3314 | 0.0014916 | Sustained | FALSE | FALSE | TMED_Event | 2190
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 03:14 | 3006 | 054:31 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3271 | 2022-04-06 | 9832626 | keep | 0 | Apr | 2022 | 6.697 | 0.0020474 | Sustained | FALSE | FALSE | TMED_Event | 3006
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 03:15 | 179 | 054:32 | T | LINEA DE TRANSMISION | DISPARO UNIDAD 5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3272 | 2022-04-06 | 585688 | keep | 0 | Apr | 2022 | 0.39891 | 0.00012192 | Sustained | FALSE | FALSE | TMED_Event | 179
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 03:19 | 107 | 030:36 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1836 | 2022-04-06 | 196452 | keep | 0 | Apr | 2022 | 0.1338 | 7.2877e-05 | Sustained | FALSE | FALSE | TMED_Event | 107
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 02:30 | 1666 | 053:47 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3227 | 2022-04-06 | 5376182 | keep | 0 | Apr | 2022 | 3.6617 | 0.0011347 | Sustained | FALSE | FALSE | TMED_Event | 1666
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 02:29 | 4387 | 053:46 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3226 | 2022-04-06 | 14152462 | keep | 0 | Apr | 2022 | 9.6392 | 0.002988 | Sustained | FALSE | FALSE | TMED_Event | 4387
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:57 | 2073 | 053:14 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3194 | 2022-04-06 | 6621162 | keep | 0 | Apr | 2022 | 4.5096 | 0.0014119 | Sustained | FALSE | FALSE | TMED_Event | 2073
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 13:22 | 637 | 040:39 | T | LINEA DE TRANSMISION | AVERIA EN CENTRAL COSTA SUR | M21040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2439 | 2022-04-06 | 1553643 | keep | 0 | Apr | 2022 | 1.0582 | 0.00043386 | Sustained | FALSE | FALSE | TMED_Event | 637
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 13:22 | 1491 | 040:39 | T | LINEA DE TRANSMISION | AVERIA EN CENTRAL COSTA SUR | M21040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2439 | 2022-04-06 | 3636549 | keep | 0 | Apr | 2022 | 2.4768 | 0.0010155 | Sustained | FALSE | FALSE | TMED_Event | 1491
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 02:40 | 3147 | 029:57 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1797 | 2022-04-06 | 5655159 | keep | 0 | Apr | 2022 | 3.8517 | 0.0021434 | Sustained | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 02:40 | 4304 | 029:57 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1797 | 2022-04-06 | 7734288 | keep | 0 | Apr | 2022 | 5.2678 | 0.0029314 | Sustained | FALSE | FALSE | TMED_Event | 4304
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 22:46 | 4892 | 026:03 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1563 | 2022-04-06 | 7646196 | keep | 0 | Apr | 2022 | 5.2078 | 0.0033319 | Sustained | FALSE | FALSE | TMED_Event | 4892
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-07 22:46 | 160 | 026:03 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1563 | 2022-04-06 | 250080 | keep | 0 | Apr | 2022 | 0.17033 | 0.00010898 | Sustained | FALSE | FALSE | TMED_Event | 160
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 01:50 | 1185 | 029:07 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1747 | 2022-04-06 | 2070195 | keep | 0 | Apr | 2022 | 1.41 | 0.0008071 | Sustained | FALSE | FALSE | TMED_Event | 1185
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 01:50 | 1584 | 029:07 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1747 | 2022-04-06 | 2767248 | keep | 0 | Apr | 2022 | 1.8848 | 0.0010789 | Sustained | FALSE | FALSE | TMED_Event | 1584
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 01:50 | 1818 | 029:07 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1747 | 2022-04-06 | 3176046 | keep | 0 | Apr | 2022 | 2.1632 | 0.0012382 | Sustained | FALSE | FALSE | TMED_Event | 1818
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:39 | 1097 | 052:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3176 | 2022-04-06 | 3484072 | keep | 0 | Apr | 2022 | 2.373 | 0.00074716 | Sustained | FALSE | FALSE | TMED_Event | 1097
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 01:50 | 3458 | 029:07 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES 6802-2,5 (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1747 | 2022-04-06 | 6041126 | keep | 0 | Apr | 2022 | 4.1146 | 0.0023552 | Sustained | FALSE | FALSE | TMED_Event | 3458
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:38 | 4381 | 052:55 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3175 | 2022-04-06 | 13909675 | keep | 0 | Apr | 2022 | 9.4738 | 0.0029839 | Sustained | FALSE | FALSE | TMED_Event | 4381
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 01:50 | 990 | 029:07 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES 6802-2,5 (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1747 | 2022-04-06 | 1729530 | keep | 0 | Apr | 2022 | 1.178 | 0.00067428 | Sustained | FALSE | FALSE | TMED_Event | 990
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 693 | 031:25 | S | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 1306305 | keep | 0 | Apr | 2022 | 0.88972 | 0.000472 | Sustained | FALSE | FALSE | TMED_Event | 693
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 47 | 031:25 | S | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 88595 | keep | 0 | Apr | 2022 | 0.060342 | 3.2011e-05 | Sustained | FALSE | FALSE | TMED_Event | 47
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 1256 | 031:25 | S | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 2367560 | keep | 0 | Apr | 2022 | 1.6125 | 0.00085546 | Sustained | FALSE | FALSE | TMED_Event | 1256
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 558 | 031:25 | S | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 1051830 | keep | 0 | Apr | 2022 | 0.7164 | 0.00038005 | Sustained | FALSE | FALSE | TMED_Event | 558
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 470 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 885950 | keep | 0 | Apr | 2022 | 0.60342 | 0.00032011 | Sustained | FALSE | FALSE | TMED_Event | 470
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 1345 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 2535325 | keep | 0 | Apr | 2022 | 1.7268 | 0.00091607 | Sustained | FALSE | FALSE | TMED_Event | 1345
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 00:58 | 2946 | 052:15 | T | LINEA DE TRANSMISION | AVERIA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3135 | 2022-04-06 | 9235710 | keep | 0 | Apr | 2022 | 6.2904 | 0.0020065 | Sustained | FALSE | FALSE | TMED_Event | 2946
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 103 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 194155 | keep | 0 | Apr | 2022 | 0.13224 | 7.0153e-05 | Sustained | FALSE | FALSE | TMED_Event | 103
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 00:59 | 1057 | 052:16 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3136 | 2022-04-06 | 3314752 | keep | 0 | Apr | 2022 | 2.2577 | 0.00071992 | Sustained | FALSE | FALSE | TMED_Event | 1057
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 99 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 186615 | keep | 0 | Apr | 2022 | 0.1271 | 6.7428e-05 | Sustained | FALSE | FALSE | TMED_Event | 99
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 52 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 98020 | keep | 0 | Apr | 2022 | 0.066761 | 3.5417e-05 | Sustained | FALSE | FALSE | TMED_Event | 52
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 32 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 60320 | keep | 0 | Apr | 2022 | 0.041084 | 2.1795e-05 | Sustained | FALSE | FALSE | TMED_Event | 32
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 129 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 243165 | keep | 0 | Apr | 2022 | 0.16562 | 8.7861e-05 | Sustained | FALSE | FALSE | TMED_Event | 129
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 146 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 275210 | keep | 0 | Apr | 2022 | 0.18744 | 9.944e-05 | Sustained | FALSE | FALSE | TMED_Event | 146
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 69 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 130065 | keep | 0 | Apr | 2022 | 0.088587 | 4.6996e-05 | Sustained | FALSE | FALSE | TMED_Event | 69
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 15 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 28275 | keep | 0 | Apr | 2022 | 0.019258 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 132 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 248820 | keep | 0 | Apr | 2022 | 0.16947 | 8.9905e-05 | Sustained | FALSE | FALSE | TMED_Event | 132
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 1157 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 2180945 | keep | 0 | Apr | 2022 | 1.4854 | 0.00078803 | Sustained | FALSE | FALSE | TMED_Event | 1157
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 376 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 708760 | keep | 0 | Apr | 2022 | 0.48273 | 0.00025609 | Sustained | FALSE | FALSE | TMED_Event | 376
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 1943 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 3662555 | keep | 0 | Apr | 2022 | 2.4945 | 0.0013234 | Sustained | FALSE | FALSE | TMED_Event | 1943
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 04:08 | 5 | 031:25 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1885 | 2022-04-06 | 9425 | keep | 0 | Apr | 2022 | 0.0064193 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
AGUADILLA | 2022-04-06 20:43 | 2022-04-08 23:01 | 1024 | 050:18 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3018 | 2022-04-06 | 3090432 | keep | 0 | Apr | 2022 | 2.1049 | 0.00069744 | Sustained | FALSE | FALSE | TMED_Event | 1024
AGUADILLA | 2022-04-06 20:43 | 2022-04-07 12:34 | 1192 | 015:51 | T | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | M20040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 951 | 2022-04-06 | 1133592 | keep | 0 | Apr | 2022 | 0.77208 | 0.00081187 | Sustained | FALSE | FALSE | TMED_Event | 1192
AGUADILLA | 2022-04-06 20:43 | 2022-04-07 12:28 | 3041 | 015:45 | T | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 945 | 2022-04-06 | 2873745 | keep | 0 | Apr | 2022 | 1.9573 | 0.0020712 | Sustained | FALSE | FALSE | TMED_Event | 3041
AGUADILLA | 2022-04-06 20:43 | 2022-04-07 13:41 | 390 | 016:58 | T | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1018 | 2022-04-06 | 397020 | keep | 0 | Apr | 2022 | 0.27041 | 0.00026563 | Sustained | FALSE | FALSE | TMED_Event | 390
AGUADILLA | 2022-04-06 20:43 | 2022-04-07 13:41 | 650 | 016:58 | T | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1018 | 2022-04-06 | 661700 | keep | 0 | Apr | 2022 | 0.45068 | 0.00044271 | Sustained | FALSE | FALSE | TMED_Event | 650
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 00:57 | 1827 | 052:14 | S | LINEA DE TRANSMISION | AVERIA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3134 | 2022-04-06 | 5725818 | keep | 0 | Apr | 2022 | 3.8998 | 0.0012444 | Sustained | FALSE | FALSE | TMED_Event | 1827
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 00:58 | 1047 | 052:15 | S | LINEA DE TRANSMISION | AVERIA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3135 | 2022-04-06 | 3282345 | keep | 0 | Apr | 2022 | 2.2356 | 0.00071311 | Sustained | FALSE | FALSE | TMED_Event | 1047
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 00:57 | 4882 | 052:14 | S | LINEA DE TRANSMISION | AVERIA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3134 | 2022-04-06 | 15300188 | keep | 0 | Apr | 2022 | 10.4209 | 0.0033251 | Sustained | FALSE | FALSE | TMED_Event | 4882
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 00:49 | 1485 | 052:06 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3126 | 2022-04-06 | 4642110 | keep | 0 | Apr | 2022 | 3.1617 | 0.0010114 | Sustained | FALSE | FALSE | TMED_Event | 1485
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 00:49 | 543 | 052:06 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3126 | 2022-04-06 | 1697418 | keep | 0 | Apr | 2022 | 1.1561 | 0.00036983 | Sustained | FALSE | FALSE | TMED_Event | 543
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 03:25 | 569 | 054:42 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3282 | 2022-04-06 | 1867458 | keep | 0 | Apr | 2022 | 1.2719 | 0.00038754 | Sustained | FALSE | FALSE | TMED_Event | 569
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 01:59 | 1245 | 053:16 | T | LINEA DE TRANSMISION | DISPARO EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3196 | 2022-04-06 | 3979020 | keep | 0 | Apr | 2022 | 2.7101 | 0.00084796 | Sustained | FALSE | FALSE | TMED_Event | 1245
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 01:59 | 1155 | 053:16 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3196 | 2022-04-06 | 3691380 | keep | 0 | Apr | 2022 | 2.5142 | 0.00078667 | Sustained | FALSE | FALSE | TMED_Event | 1155
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 04:18 | 867 | 055:35 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3335 | 2022-04-06 | 2891445 | keep | 0 | Apr | 2022 | 1.9694 | 0.00059051 | Sustained | FALSE | FALSE | TMED_Event | 867
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 04:18 | 257 | 055:35 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3335 | 2022-04-06 | 857095 | keep | 0 | Apr | 2022 | 0.58376 | 0.00017504 | Sustained | FALSE | FALSE | TMED_Event | 257
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 04:18 | 1336 | 055:35 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3335 | 2022-04-06 | 4455560 | keep | 0 | Apr | 2022 | 3.0347 | 0.00090994 | Sustained | FALSE | FALSE | TMED_Event | 1336
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 03:31 | 3315 | 054:48 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3288 | 2022-04-06 | 10899720 | keep | 0 | Apr | 2022 | 7.4237 | 0.0022578 | Sustained | FALSE | FALSE | TMED_Event | 3315
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 03:33 | 1718 | 054:50 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3290 | 2022-04-06 | 5652220 | keep | 0 | Apr | 2022 | 3.8497 | 0.0011701 | Sustained | FALSE | FALSE | TMED_Event | 1718
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 01:07 | 154 | 052:24 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3144 | 2022-04-06 | 484176 | keep | 0 | Apr | 2022 | 0.32977 | 0.00010489 | Sustained | FALSE | FALSE | TMED_Event | 154
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 04:43 | 1261 | 055:60 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3360 | 2022-04-06 | 4236960 | keep | 0 | Apr | 2022 | 2.8858 | 0.00085886 | Sustained | FALSE | FALSE | TMED_Event | 1261
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 01:07 | 3894 | 052:24 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3144 | 2022-04-06 | 12242736 | keep | 0 | Apr | 2022 | 8.3385 | 0.0026522 | Sustained | FALSE | FALSE | TMED_Event | 3894
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 04:44 | 997 | 056:01 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3361 | 2022-04-06 | 3350917 | keep | 0 | Apr | 2022 | 2.2823 | 0.00067905 | Sustained | FALSE | FALSE | TMED_Event | 997
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 01:08 | 1497 | 052:25 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3145 | 2022-04-06 | 4708065 | keep | 0 | Apr | 2022 | 3.2066 | 0.0010196 | Sustained | FALSE | FALSE | TMED_Event | 1497
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 05:07 | 574 | 056:24 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3384 | 2022-04-06 | 1942416 | keep | 0 | Apr | 2022 | 1.323 | 0.00039095 | Sustained | FALSE | FALSE | TMED_Event | 574
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 05:17 | 2493 | 056:34 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3394 | 2022-04-06 | 8461242 | keep | 0 | Apr | 2022 | 5.7629 | 0.001698 | Sustained | FALSE | FALSE | TMED_Event | 2493
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 05:17 | 1415 | 056:34 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3394 | 2022-04-06 | 4802510 | keep | 0 | Apr | 2022 | 3.271 | 0.00096375 | Sustained | FALSE | FALSE | TMED_Event | 1415
AGUADILLA | 2022-04-06 20:43 | 2022-04-10 00:13 | 1428 | 075:30 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4530 | 2022-04-06 | 6468840 | keep | 0 | Apr | 2022 | 4.4059 | 0.0009726 | Sustained | FALSE | FALSE | TMED_Event | 1428
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 05:17 | 1036 | 056:34 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3394 | 2022-04-06 | 3516184 | keep | 0 | Apr | 2022 | 2.3949 | 0.00070561 | Sustained | FALSE | FALSE | TMED_Event | 1036
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 05:17 | 382 | 056:34 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3394 | 2022-04-06 | 1296508 | keep | 0 | Apr | 2022 | 0.88305 | 0.00026018 | Sustained | FALSE | FALSE | TMED_Event | 382
AGUADILLA | 2022-04-06 20:43 | 2022-04-09 05:17 | 39 | 056:34 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3394 | 2022-04-06 | 132366 | keep | 0 | Apr | 2022 | 0.090154 | 2.6563e-05 | Sustained | FALSE | FALSE | TMED_Event | 39
AGUADILLA | 2022-04-06 20:43 | 2022-04-10 22:59 | 2366 | 098:16 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5896 | 2022-04-06 | 13949936 | keep | 0 | Apr | 2022 | 9.5012 | 0.0016115 | Sustained | FALSE | FALSE | TMED_Event | 2366
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 11:09 | 1337 | 062:26 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3746 | 2022-04-06 | 5008402 | keep | 0 | Apr | 2022 | 3.4112 | 0.00091062 | Sustained | FALSE | FALSE | TMED_Event | 1337
AGUADILLA | 2022-04-06 20:43 | 2022-04-10 22:59 | 709 | 098:16 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5896 | 2022-04-06 | 4180264 | keep | 0 | Apr | 2022 | 2.8472 | 0.0004829 | Sustained | FALSE | FALSE | TMED_Event | 709
ARECIBO | 2022-04-06 20:43 | 2022-04-09 09:51 | 3396 | 061:08 | T | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3668 | 2022-04-06 | 12456528 | keep | 0 | Apr | 2022 | 8.4841 | 0.002313 | Sustained | FALSE | FALSE | TMED_Event | 3396
ARECIBO | 2022-04-06 20:43 | 2022-04-09 11:57 | 1720 | 063:14 | T | LINEA DE TRANSMISION | DISPARO EN UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3794 | 2022-04-06 | 6525680 | keep | 0 | Apr | 2022 | 4.4446 | 0.0011715 | Sustained | FALSE | FALSE | TMED_Event | 1720
ARECIBO | 2022-04-06 20:43 | 2022-04-09 11:57 | 207 | 063:14 | T | LINEA DE TRANSMISION | DISPARO EN UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3794 | 2022-04-06 | 785358 | keep | 0 | Apr | 2022 | 0.5349 | 0.00014099 | Sustained | FALSE | FALSE | TMED_Event | 207
ARECIBO | 2022-04-06 20:43 | 2022-04-09 11:57 | 2785 | 063:14 | T | LINEA DE TRANSMISION | DISPARO EN UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3794 | 2022-04-06 | 10566290 | keep | 0 | Apr | 2022 | 7.1967 | 0.0018969 | Sustained | FALSE | FALSE | TMED_Event | 2785
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:49 | 1 | 031:06 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1866 | 2022-04-06 | 1866 | keep | 0 | Apr | 2022 | 0.0012709 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:49 | 2266 | 031:06 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1866 | 2022-04-06 | 4228356 | keep | 0 | Apr | 2022 | 2.8799 | 0.0015434 | Sustained | FALSE | FALSE | TMED_Event | 2266
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:49 | 1399 | 031:06 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1866 | 2022-04-06 | 2610534 | keep | 0 | Apr | 2022 | 1.778 | 0.00095285 | Sustained | FALSE | FALSE | TMED_Event | 1399
ARECIBO | 2022-04-06 20:43 | 2022-04-09 09:41 | 2379 | 060:58 | T | LINEA DE TRANSMISION | DISPARO DE UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3658 | 2022-04-06 | 8702382 | keep | 0 | Apr | 2022 | 5.9272 | 0.0016203 | Sustained | FALSE | FALSE | TMED_Event | 2379
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 1798 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 3434180 | keep | 0 | Apr | 2022 | 2.339 | 0.0012246 | Sustained | FALSE | FALSE | TMED_Event | 1798
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 3309 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 6320190 | keep | 0 | Apr | 2022 | 4.3047 | 0.0022537 | Sustained | FALSE | FALSE | TMED_Event | 3309
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 713 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 1361830 | keep | 0 | Apr | 2022 | 0.92754 | 0.00048562 | Sustained | FALSE | FALSE | TMED_Event | 713
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 1628 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 3109480 | keep | 0 | Apr | 2022 | 2.1179 | 0.0011088 | Sustained | FALSE | FALSE | TMED_Event | 1628
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 1541 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 2943310 | keep | 0 | Apr | 2022 | 2.0047 | 0.0010496 | Sustained | FALSE | FALSE | TMED_Event | 1541
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 307 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 586370 | keep | 0 | Apr | 2022 | 0.39937 | 0.0002091 | Sustained | FALSE | FALSE | TMED_Event | 307
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 1277 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 2439070 | keep | 0 | Apr | 2022 | 1.6612 | 0.00086976 | Sustained | FALSE | FALSE | TMED_Event | 1277
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 1831 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 3497210 | keep | 0 | Apr | 2022 | 2.3819 | 0.0012471 | Sustained | FALSE | FALSE | TMED_Event | 1831
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 1483 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 2832530 | keep | 0 | Apr | 2022 | 1.9292 | 0.0010101 | Sustained | FALSE | FALSE | TMED_Event | 1483
ARECIBO | 2022-04-06 20:43 | 2022-04-08 04:33 | 89 | 031:50 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1910 | 2022-04-06 | 169990 | keep | 0 | Apr | 2022 | 0.11578 | 6.0617e-05 | Sustained | FALSE | FALSE | TMED_Event | 89
ARECIBO | 2022-04-06 20:43 | 2022-04-10 00:49 | 1 | 076:06 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR LLEVA CARGA DE 7505-05 | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4566 | 2022-04-06 | 4566 | keep | 0 | Apr | 2022 | 0.0031099 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2022-04-06 20:43 | 2022-04-10 00:49 | 1 | 076:06 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR CARGA POR 7505-01 | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4566 | 2022-04-06 | 4566 | keep | 0 | Apr | 2022 | 0.0031099 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 1222 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 2276586 | keep | 0 | Apr | 2022 | 1.5506 | 0.0008323 | Sustained | FALSE | FALSE | TMED_Event | 1222
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 2756 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 5134428 | keep | 0 | Apr | 2022 | 3.497 | 0.0018771 | Sustained | FALSE | FALSE | TMED_Event | 2756
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 2833 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 5277879 | keep | 0 | Apr | 2022 | 3.5947 | 0.0019295 | Sustained | FALSE | FALSE | TMED_Event | 2833
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 1218 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 2269134 | keep | 0 | Apr | 2022 | 1.5455 | 0.00082957 | Sustained | FALSE | FALSE | TMED_Event | 1218
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 1345 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 2505735 | keep | 0 | Apr | 2022 | 1.7066 | 0.00091607 | Sustained | FALSE | FALSE | TMED_Event | 1345
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 1265 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 2356695 | keep | 0 | Apr | 2022 | 1.6051 | 0.00086159 | Sustained | FALSE | FALSE | TMED_Event | 1265
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 2071 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 3858273 | keep | 0 | Apr | 2022 | 2.6279 | 0.0014105 | Sustained | FALSE | FALSE | TMED_Event | 2071
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 760 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD 5 COSTA SUR CERRADOS LOS INTERRUPTORES (MANUAL NO RTU) | M22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 1415880 | keep | 0 | Apr | 2022 | 0.96435 | 0.00051763 | Sustained | FALSE | FALSE | TMED_Event | 760
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 509 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 948267 | keep | 0 | Apr | 2022 | 0.64586 | 0.00034668 | Sustained | FALSE | FALSE | TMED_Event | 509
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 2620 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 4881060 | keep | 0 | Apr | 2022 | 3.3245 | 0.0017845 | Sustained | FALSE | FALSE | TMED_Event | 2620
ARECIBO | 2022-04-06 20:43 | 2022-04-08 03:46 | 1916 | 031:03 | S | LINEA DE TRANSMISION | UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1863 | 2022-04-06 | 3569508 | keep | 0 | Apr | 2022 | 2.4312 | 0.001305 | Sustained | FALSE | FALSE | TMED_Event | 1916
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:04 | 3087 | 052:21 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3141 | 2022-04-06 | 9696267 | keep | 0 | Apr | 2022 | 6.6041 | 0.0021025 | Sustained | FALSE | FALSE | TMED_Event | 3087
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:04 | 770 | 052:21 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3141 | 2022-04-06 | 2418570 | keep | 0 | Apr | 2022 | 1.6473 | 0.00052444 | Sustained | FALSE | FALSE | TMED_Event | 770
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:04 | 1192 | 052:21 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3141 | 2022-04-06 | 3744072 | keep | 0 | Apr | 2022 | 2.5501 | 0.00081187 | Sustained | FALSE | FALSE | TMED_Event | 1192
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:04 | 1772 | 052:21 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3141 | 2022-04-06 | 5565852 | keep | 0 | Apr | 2022 | 3.7909 | 0.0012069 | Sustained | FALSE | FALSE | TMED_Event | 1772
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:05 | 2174 | 052:22 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3142 | 2022-04-06 | 6830708 | keep | 0 | Apr | 2022 | 4.6524 | 0.0014807 | Sustained | FALSE | FALSE | TMED_Event | 2174
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:05 | 64 | 052:22 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3142 | 2022-04-06 | 201088 | keep | 0 | Apr | 2022 | 0.13696 | 4.359e-05 | Sustained | FALSE | FALSE | TMED_Event | 64
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 04:03 | 2658 | 031:20 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1880 | 2022-04-06 | 4997040 | keep | 0 | Apr | 2022 | 3.4035 | 0.0018104 | Sustained | FALSE | FALSE | TMED_Event | 2658
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 22:16 | 6285 | 049:33 | T | LINEA DE TRANSMISION | AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2973 | 2022-04-06 | 18685305 | keep | 0 | Apr | 2022 | 12.7265 | 0.0042807 | Sustained | FALSE | FALSE | TMED_Event | 6285
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 01:02 | 2225 | 052:19 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3139 | 2022-04-06 | 6984275 | keep | 0 | Apr | 2022 | 4.757 | 0.0015154 | Sustained | FALSE | FALSE | TMED_Event | 2225
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 18:39 | 3522 | 045:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2756 | 2022-04-06 | 9706632 | keep | 0 | Apr | 2022 | 6.6111 | 0.0023988 | Sustained | FALSE | FALSE | TMED_Event | 3522
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 18:39 | 1337 | 045:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2756 | 2022-04-06 | 3684772 | keep | 0 | Apr | 2022 | 2.5097 | 0.00091062 | Sustained | FALSE | FALSE | TMED_Event | 1337
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 18:39 | 2825 | 045:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2756 | 2022-04-06 | 7785700 | keep | 0 | Apr | 2022 | 5.3028 | 0.0019241 | Sustained | FALSE | FALSE | TMED_Event | 2825
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 18:39 | 1287 | 045:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2756 | 2022-04-06 | 3546972 | keep | 0 | Apr | 2022 | 2.4158 | 0.00087657 | Sustained | FALSE | FALSE | TMED_Event | 1287
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 10:30 | 595 | 061:47 | T | LINEA DE TRANSMISION | AVERIA EN CENTRAL COSTA SUR SE CERRARON LOS INTERRUPTORES EN LA SUBESTACION | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3707 | 2022-04-06 | 2205665 | keep | 0 | Apr | 2022 | 1.5023 | 0.00040525 | Sustained | FALSE | FALSE | TMED_Event | 595
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-09 10:30 | 51 | 061:47 | T | LINEA DE TRANSMISION | RELEVO DE CARGA AUTOMATICO AVERIA EN CENTRAL COSTA SUR SE CERRARON LOS INTERRUPTORES EN LA SUBESTACION | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3707 | 2022-04-06 | 189057 | keep | 0 | Apr | 2022 | 0.12877 | 3.4736e-05 | Sustained | FALSE | FALSE | TMED_Event | 51
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 18:23 | 721 | 045:40 | T | LINEA DE TRANSMISION | AVERIA EN CENTRAL COSTA SUR SE CERRARON LOS INTERRUPTORES EN LA SUBESTACION | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2740 | 2022-04-06 | 1975540 | keep | 0 | Apr | 2022 | 1.3455 | 0.00049107 | Sustained | FALSE | FALSE | TMED_Event | 721
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 18:39 | 1417 | 045:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2756 | 2022-04-06 | 3905252 | keep | 0 | Apr | 2022 | 2.6598 | 0.00096511 | Sustained | FALSE | FALSE | TMED_Event | 1417
MAYAGÃœEZ | 2022-04-06 20:43 | 2022-04-08 18:39 | 80 | 045:56 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2756 | 2022-04-06 | 220480 | keep | 0 | Apr | 2022 | 0.15017 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:29 | 1548 | 007:46 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 466 | 2022-04-06 | 721368 | keep | 0 | Apr | 2022 | 0.49132 | 0.0010543 | Sustained | FALSE | FALSE | TMED_Event | 1548
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:29 | 274 | 007:46 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 466 | 2022-04-06 | 127684 | keep | 0 | Apr | 2022 | 0.086965 | 0.00018662 | Sustained | FALSE | FALSE | TMED_Event | 274
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:29 | 185 | 007:46 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 466 | 2022-04-06 | 86210 | keep | 0 | Apr | 2022 | 0.058717 | 0.000126 | Sustained | FALSE | FALSE | TMED_Event | 185
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:29 | 9 | 007:46 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 466 | 2022-04-06 | 4194 | keep | 0 | Apr | 2022 | 0.0028565 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:31 | 458 | 007:48 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 468 | 2022-04-06 | 214344 | keep | 0 | Apr | 2022 | 0.14599 | 0.00031194 | Sustained | FALSE | FALSE | TMED_Event | 458
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:31 | 437 | 007:48 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 468 | 2022-04-06 | 204516 | keep | 0 | Apr | 2022 | 0.13929 | 0.00029764 | Sustained | FALSE | FALSE | TMED_Event | 437
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:31 | 1185 | 007:48 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 468 | 2022-04-06 | 554580 | keep | 0 | Apr | 2022 | 0.37772 | 0.0008071 | Sustained | FALSE | FALSE | TMED_Event | 1185
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:31 | 63 | 007:48 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 468 | 2022-04-06 | 29484 | keep | 0 | Apr | 2022 | 0.020081 | 4.2909e-05 | Sustained | FALSE | FALSE | TMED_Event | 63
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:31 | 232 | 007:48 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 468 | 2022-04-06 | 108576 | keep | 0 | Apr | 2022 | 0.073951 | 0.00015801 | Sustained | FALSE | FALSE | TMED_Event | 232
ARECIBO | 2022-04-06 20:43 | 2022-04-07 03:27 | 1022 | 006:44 | S | LINEA DE TRANSMISION | DISPARO UNIDAD #5 COSTA SUR | A22040600100 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 404 | 2022-04-06 | 412888 | keep | 0 | Apr | 2022 | 0.28122 | 0.00069608 | Sustained | FALSE | FALSE | TMED_Event | 1022
ARECIBO | 2022-04-06 20:43 | 2022-04-07 03:26 | 2407 | 006:43 | S | LINEA DE TRANSMISION | DISPARO UNIDAD #5 COSTA SUR | A22040600100 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 403 | 2022-04-06 | 970021 | keep | 0 | Apr | 2022 | 0.66068 | 0.0016394 | Sustained | FALSE | FALSE | TMED_Event | 2407
ARECIBO | 2022-04-06 20:43 | 2022-04-07 03:26 | 2558 | 006:43 | S | LINEA DE TRANSMISION | DISPARO UNIDAD #5 COSTA SUR | A22040600100 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 403 | 2022-04-06 | 1030874 | keep | 0 | Apr | 2022 | 0.70212 | 0.0017422 | Sustained | FALSE | FALSE | TMED_Event | 2558
ARECIBO | 2022-04-06 20:43 | 2022-04-07 03:27 | 830 | 006:44 | T | LINEA DE TRANSMISION | DISPARO UNIDAD #5 COSTA SUR | A22040600100 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 404 | 2022-04-06 | 335320 | keep | 0 | Apr | 2022 | 0.22838 | 0.00056531 | Sustained | FALSE | FALSE | TMED_Event | 830
ARECIBO | 2022-04-06 20:43 | 2022-04-07 05:38 | 1105 | 008:55 | T | LINEA DE TRANSMISION | DISPARO UNIDAD #5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 535 | 2022-04-06 | 591175 | keep | 0 | Apr | 2022 | 0.40265 | 0.00075261 | Sustained | FALSE | FALSE | TMED_Event | 1105
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:35 | 2694 | 007:52 | T | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 472 | 2022-04-06 | 1271568 | keep | 0 | Apr | 2022 | 0.86606 | 0.0018349 | Sustained | FALSE | FALSE | TMED_Event | 2694
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:35 | 2228 | 007:52 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 472 | 2022-04-06 | 1051616 | keep | 0 | Apr | 2022 | 0.71625 | 0.0015175 | Sustained | FALSE | FALSE | TMED_Event | 2228
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:35 | 438 | 007:52 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 472 | 2022-04-06 | 206736 | keep | 0 | Apr | 2022 | 0.14081 | 0.00029832 | Sustained | FALSE | FALSE | TMED_Event | 438
ARECIBO | 2022-04-06 20:43 | 2022-04-07 05:38 | 385 | 008:55 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 535 | 2022-04-06 | 205975 | keep | 0 | Apr | 2022 | 0.14029 | 0.00026222 | Sustained | FALSE | FALSE | TMED_Event | 385
ARECIBO | 2022-04-06 20:43 | 2022-04-07 05:38 | 264 | 008:55 | S | LINEA DE TRANSMISION | ADISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 535 | 2022-04-06 | 141240 | keep | 0 | Apr | 2022 | 0.096198 | 0.00017981 | Sustained | FALSE | FALSE | TMED_Event | 264
ARECIBO | 2022-04-06 20:43 | 2022-04-08 21:24 | 5042 | 048:41 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2921 | 2022-04-06 | 14727682 | keep | 0 | Apr | 2022 | 10.031 | 0.0034341 | Sustained | FALSE | FALSE | TMED_Event | 5042
ARECIBO | 2022-04-06 20:43 | 2022-04-08 21:24 | 2720 | 048:41 | T | LINEA DE TRANSMISION | DISPARO UNIDA COSTA SUR | A22040900000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2921 | 2022-04-06 | 7945120 | keep | 0 | Apr | 2022 | 5.4114 | 0.0018526 | Sustained | FALSE | FALSE | TMED_Event | 2720
ARECIBO | 2022-04-06 20:43 | 2022-04-09 00:25 | 1883 | 051:42 | T | LINEA DE TRANSMISION | DISPAR0 UNIDA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3102 | 2022-04-06 | 5841066 | keep | 0 | Apr | 2022 | 3.9783 | 0.0012825 | Sustained | FALSE | FALSE | TMED_Event | 1883
ARECIBO | 2022-04-06 20:43 | 2022-04-07 05:07 | 2523 | 008:24 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 504 | 2022-04-06 | 1271592 | keep | 0 | Apr | 2022 | 0.86608 | 0.0017184 | Sustained | FALSE | FALSE | TMED_Event | 2523
ARECIBO | 2022-04-06 20:43 | 2022-04-07 05:07 | 1607 | 008:24 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 504 | 2022-04-06 | 809928 | keep | 0 | Apr | 2022 | 0.55164 | 0.0010945 | Sustained | FALSE | FALSE | TMED_Event | 1607
ARECIBO | 2022-04-06 20:43 | 2022-04-07 05:07 | 1722 | 008:24 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 504 | 2022-04-06 | 867888 | keep | 0 | Apr | 2022 | 0.59111 | 0.0011728 | Sustained | FALSE | FALSE | TMED_Event | 1722
ARECIBO | 2022-04-06 20:43 | 2022-04-09 00:31 | 2201 | 051:48 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3108 | 2022-04-06 | 6840708 | keep | 0 | Apr | 2022 | 4.6592 | 0.0014991 | Sustained | FALSE | FALSE | TMED_Event | 2201
ARECIBO | 2022-04-06 20:43 | 2022-04-09 00:32 | 1986 | 051:49 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3109 | 2022-04-06 | 6174474 | keep | 0 | Apr | 2022 | 4.2054 | 0.0013527 | Sustained | FALSE | FALSE | TMED_Event | 1986
ARECIBO | 2022-04-06 20:43 | 2022-04-09 00:32 | 199 | 051:49 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3109 | 2022-04-06 | 618691 | keep | 0 | Apr | 2022 | 0.42139 | 0.00013554 | Sustained | FALSE | FALSE | TMED_Event | 199
ARECIBO | 2022-04-06 20:43 | 2022-04-09 00:33 | 24 | 051:50 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3110 | 2022-04-06 | 74640 | keep | 0 | Apr | 2022 | 0.050837 | 1.6346e-05 | Sustained | FALSE | FALSE | TMED_Event | 24
ARECIBO | 2022-04-06 20:43 | 2022-04-07 05:18 | 619 | 008:35 | T | LINEA DE TRANSMISION | DISPARO UNIDAD #5 COSTA SUR | A22040600096 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 515 | 2022-04-06 | 318785 | keep | 0 | Apr | 2022 | 0.21712 | 0.0004216 | Sustained | FALSE | FALSE | TMED_Event | 619
ARECIBO | 2022-04-06 20:43 | 2022-04-07 05:18 | 243 | 008:35 | T | LINEA DE TRANSMISION | DISPARO UNIDAD #5 COSTA SUR | A22040600096 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 515 | 2022-04-06 | 125145 | keep | 0 | Apr | 2022 | 0.085236 | 0.00016551 | Sustained | FALSE | FALSE | TMED_Event | 243
ARECIBO | 2022-04-06 20:43 | 2022-04-07 05:18 | 2703 | 008:35 | S | LINEA DE TRANSMISION | DISPARO UNIDAD #5 COSTA SUR | A22040600096 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 515 | 2022-04-06 | 1392045 | keep | 0 | Apr | 2022 | 0.94812 | 0.001841 | Sustained | FALSE | FALSE | TMED_Event | 2703
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:29 | 316 | 007:46 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 466 | 2022-04-06 | 147256 | keep | 0 | Apr | 2022 | 0.1003 | 0.00021523 | Sustained | FALSE | FALSE | TMED_Event | 316
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:29 | 1227 | 007:46 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 466 | 2022-04-06 | 571782 | keep | 0 | Apr | 2022 | 0.38944 | 0.0008357 | Sustained | FALSE | FALSE | TMED_Event | 1227
ARECIBO | 2022-04-06 20:43 | 2022-04-07 04:29 | 3431 | 007:46 | S | LINEA DE TRANSMISION | DISPARO UNIDAD # 5 COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 466 | 2022-04-06 | 1598846 | keep | 0 | Apr | 2022 | 1.089 | 0.0023368 | Sustained | FALSE | FALSE | TMED_Event | 3431
UTUADO | 2022-04-06 20:43 | 2022-04-07 22:58 | 1405 | 026:15 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1575 | 2022-04-06 | 2212875 | keep | 0 | Apr | 2022 | 1.5072 | 0.00095694 | Sustained | FALSE | FALSE | TMED_Event | 1405
UTUADO | 2022-04-06 20:43 | 2022-04-07 22:58 | 669 | 026:15 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1575 | 2022-04-06 | 1053675 | keep | 0 | Apr | 2022 | 0.71765 | 0.00045565 | Sustained | FALSE | FALSE | TMED_Event | 669
UTUADO | 2022-04-06 20:43 | 2022-04-07 22:58 | 1527 | 026:15 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1575 | 2022-04-06 | 2405025 | keep | 0 | Apr | 2022 | 1.6381 | 0.00104 | Sustained | FALSE | FALSE | TMED_Event | 1527
UTUADO | 2022-04-06 20:43 | 2022-04-07 22:58 | 1054 | 026:15 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1575 | 2022-04-06 | 1660050 | keep | 0 | Apr | 2022 | 1.1307 | 0.00071787 | Sustained | FALSE | FALSE | TMED_Event | 1054
UTUADO | 2022-04-06 20:43 | 2022-04-07 22:58 | 932 | 026:15 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1575 | 2022-04-06 | 1467900 | keep | 0 | Apr | 2022 | 0.99978 | 0.00063478 | Sustained | FALSE | FALSE | TMED_Event | 932
UTUADO | 2022-04-06 20:43 | 2022-04-08 03:20 | 1633 | 030:37 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1837 | 2022-04-06 | 2999821 | keep | 0 | Apr | 2022 | 2.0432 | 0.0011122 | Sustained | FALSE | FALSE | TMED_Event | 1633
UTUADO | 2022-04-06 20:43 | 2022-04-08 03:20 | 1624 | 030:37 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1837 | 2022-04-06 | 2983288 | keep | 0 | Apr | 2022 | 2.0319 | 0.0011061 | Sustained | FALSE | FALSE | TMED_Event | 1624
UTUADO | 2022-04-06 20:43 | 2022-04-07 22:58 | 705 | 026:15 | S | LINEA DE TRANSMISION | DISPARO UNIDA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1575 | 2022-04-06 | 1110375 | keep | 0 | Apr | 2022 | 0.75627 | 0.00048017 | Sustained | FALSE | FALSE | TMED_Event | 705
UTUADO | 2022-04-06 20:43 | 2022-04-07 22:58 | 1521 | 026:15 | S | LINEA DE TRANSMISION | DISPARO UNIDA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1575 | 2022-04-06 | 2395575 | keep | 0 | Apr | 2022 | 1.6316 | 0.0010359 | Sustained | FALSE | FALSE | TMED_Event | 1521
UTUADO | 2022-04-06 20:43 | 2022-04-07 22:58 | 882 | 026:15 | S | LINEA DE TRANSMISION | DISPARO UNIDA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1575 | 2022-04-06 | 1389150 | keep | 0 | Apr | 2022 | 0.94614 | 0.00060073 | Sustained | FALSE | FALSE | TMED_Event | 882
UTUADO | 2022-04-06 20:43 | 2022-04-09 00:27 | 3502 | 051:44 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3104 | 2022-04-06 | 10870208 | keep | 0 | Apr | 2022 | 7.4036 | 0.0023852 | Sustained | FALSE | FALSE | TMED_Event | 3502
UTUADO | 2022-04-06 20:43 | 2022-04-09 00:27 | 1241 | 051:44 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3104 | 2022-04-06 | 3852064 | keep | 0 | Apr | 2022 | 2.6236 | 0.00084524 | Sustained | FALSE | FALSE | TMED_Event | 1241
UTUADO | 2022-04-06 20:43 | 2022-04-09 00:27 | 650 | 051:44 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3104 | 2022-04-06 | 2017600 | keep | 0 | Apr | 2022 | 1.3742 | 0.00044271 | Sustained | FALSE | FALSE | TMED_Event | 650
UTUADO | 2022-04-06 20:43 | 2022-04-09 04:13 | 1382 | 055:30 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3330 | 2022-04-06 | 4602060 | keep | 0 | Apr | 2022 | 3.1344 | 0.00094127 | Sustained | FALSE | FALSE | TMED_Event | 1382
UTUADO | 2022-04-06 20:43 | 2022-04-09 04:13 | 654 | 055:30 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3330 | 2022-04-06 | 2177820 | keep | 0 | Apr | 2022 | 1.4833 | 0.00044544 | Sustained | FALSE | FALSE | TMED_Event | 654
UTUADO | 2022-04-06 20:43 | 2022-04-08 00:50 | 934 | 028:07 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1687 | 2022-04-06 | 1575658 | keep | 0 | Apr | 2022 | 1.0732 | 0.00063614 | Sustained | FALSE | FALSE | TMED_Event | 934
UTUADO | 2022-04-06 20:43 | 2022-04-08 00:50 | 4 | 028:07 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1687 | 2022-04-06 | 6748 | keep | 0 | Apr | 2022 | 0.004596 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
UTUADO | 2022-04-06 20:43 | 2022-04-08 00:50 | 1479 | 028:07 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1687 | 2022-04-06 | 2495073 | keep | 0 | Apr | 2022 | 1.6994 | 0.0010073 | Sustained | FALSE | FALSE | TMED_Event | 1479
UTUADO | 2022-04-06 20:43 | 2022-04-08 00:50 | 1841 | 028:07 | S | LINEA DE TRANSMISION | DISPARO UNIDA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1687 | 2022-04-06 | 3105767 | keep | 0 | Apr | 2022 | 2.1153 | 0.0012539 | Sustained | FALSE | FALSE | TMED_Event | 1841
UTUADO | 2022-04-06 20:43 | 2022-04-08 00:50 | 1950 | 028:07 | S | LINEA DE TRANSMISION | DISPARO UNIDA COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1687 | 2022-04-06 | 3289650 | keep | 0 | Apr | 2022 | 2.2406 | 0.0013281 | Sustained | FALSE | FALSE | TMED_Event | 1950
ARECIBO | 2022-04-06 20:43 | 2022-04-08 13:48 | 2231 | 041:05 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2465 | 2022-04-06 | 5499415 | keep | 0 | Apr | 2022 | 3.7456 | 0.0015195 | Sustained | FALSE | FALSE | TMED_Event | 2231
ARECIBO | 2022-04-06 20:43 | 2022-04-08 17:56 | 1923 | 045:13 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2713 | 2022-04-06 | 5217099 | keep | 0 | Apr | 2022 | 3.5533 | 0.0013097 | Sustained | FALSE | FALSE | TMED_Event | 1923
ARECIBO | 2022-04-06 20:43 | 2022-04-08 13:48 | 1066 | 041:05 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2465 | 2022-04-06 | 2627690 | keep | 0 | Apr | 2022 | 1.7897 | 0.00072605 | Sustained | FALSE | FALSE | TMED_Event | 1066
ARECIBO | 2022-04-06 20:43 | 2022-04-08 13:48 | 141 | 041:05 | S | LINEA DE TRANSMISION | DISAPRO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2465 | 2022-04-06 | 347565 | keep | 0 | Apr | 2022 | 0.23672 | 9.6034e-05 | Sustained | FALSE | FALSE | TMED_Event | 141
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:43 | 425 | 010:00 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 600 | 2022-04-06 | 255000 | keep | 0 | Apr | 2022 | 0.17368 | 0.00028947 | Sustained | FALSE | FALSE | TMED_Event | 425
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:43 | 1494 | 010:00 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 600 | 2022-04-06 | 896400 | keep | 0 | Apr | 2022 | 0.61053 | 0.0010176 | Sustained | FALSE | FALSE | TMED_Event | 1494
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:43 | 3654 | 010:00 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 600 | 2022-04-06 | 2192400 | keep | 0 | Apr | 2022 | 1.4932 | 0.0024887 | Sustained | FALSE | FALSE | TMED_Event | 3654
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:44 | 2888 | 010:01 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 601 | 2022-04-06 | 1735688 | keep | 0 | Apr | 2022 | 1.1822 | 0.001967 | Sustained | FALSE | FALSE | TMED_Event | 2888
ARECIBO | 2022-04-06 20:43 | 2022-04-08 21:25 | 2107 | 048:42 | T | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2922 | 2022-04-06 | 6156654 | keep | 0 | Apr | 2022 | 4.1933 | 0.0014351 | Sustained | FALSE | FALSE | TMED_Event | 2107
ARECIBO | 2022-04-06 20:43 | 2022-04-09 12:04 | 308 | 063:21 | T | LINEA DE TRANSMISION | DISPARO EN UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3801 | 2022-04-06 | 1170708 | keep | 0 | Apr | 2022 | 0.79736 | 0.00020978 | Sustained | FALSE | FALSE | TMED_Event | 308
ARECIBO | 2022-04-06 20:43 | 2022-04-08 22:14 | 2697 | 049:31 | T | LINEA DE TRANSMISION | DISPARO EN UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2971 | 2022-04-06 | 8012787 | keep | 0 | Apr | 2022 | 5.4575 | 0.0018369 | Sustained | FALSE | FALSE | TMED_Event | 2697
ARECIBO | 2022-04-06 20:43 | 2022-04-09 12:04 | 67 | 063:21 | T | LINEA DE TRANSMISION | DISPARO EN UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3801 | 2022-04-06 | 254667 | keep | 0 | Apr | 2022 | 0.17345 | 4.5633e-05 | Sustained | FALSE | FALSE | TMED_Event | 67
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:11 | 1879 | 009:28 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 568 | 2022-04-06 | 1067272 | keep | 0 | Apr | 2022 | 0.72691 | 0.0012798 | Sustained | FALSE | FALSE | TMED_Event | 1879
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:11 | 2777 | 009:28 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 568 | 2022-04-06 | 1577336 | keep | 0 | Apr | 2022 | 1.0743 | 0.0018914 | Sustained | FALSE | FALSE | TMED_Event | 2777
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:11 | 2 | 009:28 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 568 | 2022-04-06 | 1136 | keep | 0 | Apr | 2022 | 0.00077372 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:11 | 2839 | 009:28 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 568 | 2022-04-06 | 1612552 | keep | 0 | Apr | 2022 | 1.0983 | 0.0019336 | Sustained | FALSE | FALSE | TMED_Event | 2839
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:11 | 1160 | 009:28 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 568 | 2022-04-06 | 658880 | keep | 0 | Apr | 2022 | 0.44876 | 0.00079007 | Sustained | FALSE | FALSE | TMED_Event | 1160
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:11 | 1860 | 009:28 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 568 | 2022-04-06 | 1056480 | keep | 0 | Apr | 2022 | 0.71956 | 0.0012668 | Sustained | FALSE | FALSE | TMED_Event | 1860
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:02 | 3157 | 009:19 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 559 | 2022-04-06 | 1764763 | keep | 0 | Apr | 2022 | 1.202 | 0.0021502 | Sustained | FALSE | FALSE | TMED_Event | 3157
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:02 | 35 | 009:19 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 559 | 2022-04-06 | 19565 | keep | 0 | Apr | 2022 | 0.013326 | 2.3838e-05 | Sustained | FALSE | FALSE | TMED_Event | 35
ARECIBO | 2022-04-06 20:43 | 2022-04-07 06:02 | 2916 | 009:19 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | A22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 559 | 2022-04-06 | 1630044 | keep | 0 | Apr | 2022 | 1.1102 | 0.0019861 | Sustained | FALSE | FALSE | TMED_Event | 2916
ARECIBO | 2022-04-06 20:43 | 2022-04-07 23:48 | 2791 | 027:05 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1625 | 2022-04-06 | 4535375 | keep | 0 | Apr | 2022 | 3.089 | 0.0019009 | Sustained | FALSE | FALSE | TMED_Event | 2791
ARECIBO | 2022-04-06 20:43 | 2022-04-07 23:48 | 1464 | 027:05 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1625 | 2022-04-06 | 2379000 | keep | 0 | Apr | 2022 | 1.6203 | 0.00099712 | Sustained | FALSE | FALSE | TMED_Event | 1464
ARECIBO | 2022-04-06 20:43 | 2022-04-07 23:48 | 759 | 027:05 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1625 | 2022-04-06 | 1233375 | keep | 0 | Apr | 2022 | 0.84005 | 0.00051695 | Sustained | FALSE | FALSE | TMED_Event | 759
ARECIBO | 2022-04-06 20:43 | 2022-04-07 23:48 | 1500 | 027:05 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1625 | 2022-04-06 | 2437500 | keep | 0 | Apr | 2022 | 1.6602 | 0.0010216 | Sustained | FALSE | FALSE | TMED_Event | 1500
ARECIBO | 2022-04-06 20:43 | 2022-04-07 23:40 | 2132 | 026:57 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1617 | 2022-04-06 | 3447444 | keep | 0 | Apr | 2022 | 2.348 | 0.0014521 | Sustained | FALSE | FALSE | TMED_Event | 2132
ARECIBO | 2022-04-06 20:43 | 2022-04-07 23:40 | 2366 | 026:57 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1617 | 2022-04-06 | 3825822 | keep | 0 | Apr | 2022 | 2.6057 | 0.0016115 | Sustained | FALSE | FALSE | TMED_Event | 2366
ARECIBO | 2022-04-06 20:43 | 2022-04-07 23:40 | 1976 | 026:57 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1617 | 2022-04-06 | 3195192 | keep | 0 | Apr | 2022 | 2.1762 | 0.0013458 | Sustained | FALSE | FALSE | TMED_Event | 1976
ARECIBO | 2022-04-06 20:43 | 2022-04-07 23:40 | 3688 | 026:57 | S | LINEA DE TRANSMISION | DISPARO UNIDAD COSTA SUR | M22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1617 | 2022-04-06 | 5963496 | keep | 0 | Apr | 2022 | 4.0617 | 0.0025119 | Sustained | FALSE | FALSE | TMED_Event | 3688
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 23:36 | 776 | 026:53 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1613 | 2022-04-06 | 1251688 | keep | 0 | Apr | 2022 | 0.85252 | 0.00052853 | Sustained | FALSE | FALSE | TMED_Event | 776
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 23:48 | 2216 | 027:05 | T | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1625 | 2022-04-06 | 3601000 | keep | 0 | Apr | 2022 | 2.4526 | 0.0015093 | Sustained | FALSE | FALSE | TMED_Event | 2216
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 12:59 | 3000 | 064:16 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3856 | 2022-04-06 | 11568000 | keep | 0 | Apr | 2022 | 7.8789 | 0.0020433 | Sustained | FALSE | FALSE | TMED_Event | 3000
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 12:59 | 908 | 064:16 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3856 | 2022-04-06 | 3501248 | keep | 0 | Apr | 2022 | 2.3847 | 0.00061843 | Sustained | FALSE | FALSE | TMED_Event | 908
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 12:59 | 3332 | 064:16 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3856 | 2022-04-06 | 12848192 | keep | 0 | Apr | 2022 | 8.7508 | 0.0022694 | Sustained | FALSE | FALSE | TMED_Event | 3332
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 11:50 | 2610 | 063:07 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3787 | 2022-04-06 | 9884070 | keep | 0 | Apr | 2022 | 6.732 | 0.0017777 | Sustained | FALSE | FALSE | TMED_Event | 2610
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 23:57 | 3076 | 027:14 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1634 | 2022-04-06 | 5026184 | keep | 0 | Apr | 2022 | 3.4233 | 0.002095 | Sustained | FALSE | FALSE | TMED_Event | 3076
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 06:14 | 3387 | 057:31 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3451 | 2022-04-06 | 11688537 | keep | 0 | Apr | 2022 | 7.961 | 0.0023069 | Sustained | FALSE | FALSE | TMED_Event | 3387
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 22:25 | 4702 | 025:42 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1542 | 2022-04-06 | 7250484 | keep | 0 | Apr | 2022 | 4.9383 | 0.0032025 | Sustained | FALSE | FALSE | TMED_Event | 4702
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 06:14 | 377 | 057:31 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3451 | 2022-04-06 | 1301027 | keep | 0 | Apr | 2022 | 0.88612 | 0.00025677 | Sustained | FALSE | FALSE | TMED_Event | 377
VEGA BAJA | 2022-04-06 20:43 | 2022-04-08 00:09 | 4027 | 027:26 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1646 | 2022-04-06 | 6628442 | keep | 0 | Apr | 2022 | 4.5146 | 0.0027428 | Sustained | FALSE | FALSE | TMED_Event | 4027
VEGA BAJA | 2022-04-06 20:43 | 2022-04-08 00:09 | 2468 | 027:26 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1646 | 2022-04-06 | 4062328 | keep | 0 | Apr | 2022 | 2.7668 | 0.0016809 | Sustained | FALSE | FALSE | TMED_Event | 2468
VEGA BAJA | 2022-04-06 20:43 | 2022-04-08 00:09 | 1494 | 027:26 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1646 | 2022-04-06 | 2459124 | keep | 0 | Apr | 2022 | 1.6749 | 0.0010176 | Sustained | FALSE | FALSE | TMED_Event | 1494
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 23:59 | 2368 | 027:16 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1636 | 2022-04-06 | 3874048 | keep | 0 | Apr | 2022 | 2.6386 | 0.0016128 | Sustained | FALSE | FALSE | TMED_Event | 2368
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 23:59 | 538 | 027:16 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1636 | 2022-04-06 | 880168 | keep | 0 | Apr | 2022 | 0.59948 | 0.00036643 | Sustained | FALSE | FALSE | TMED_Event | 538
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 23:59 | 1284 | 027:16 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1636 | 2022-04-06 | 2100624 | keep | 0 | Apr | 2022 | 1.4307 | 0.00087453 | Sustained | FALSE | FALSE | TMED_Event | 1284
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 04:26 | 1310 | 055:43 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3343 | 2022-04-06 | 4379330 | keep | 0 | Apr | 2022 | 2.9827 | 0.00089224 | Sustained | FALSE | FALSE | TMED_Event | 1310
VEGA BAJA | 2022-04-06 20:43 | 2022-04-08 23:46 | 215 | 051:03 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3063 | 2022-04-06 | 658545 | keep | 0 | Apr | 2022 | 0.44853 | 0.00014644 | Sustained | FALSE | FALSE | TMED_Event | 215
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 04:26 | 1 | 055:43 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3343 | 2022-04-06 | 3343 | keep | 0 | Apr | 2022 | 0.0022769 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 20:22 | 652 | 071:39 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4299 | 2022-04-06 | 2802948 | keep | 0 | Apr | 2022 | 1.9091 | 0.00044407 | Sustained | FALSE | FALSE | TMED_Event | 652
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 20:22 | 2704 | 071:39 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4299 | 2022-04-06 | 11624496 | keep | 0 | Apr | 2022 | 7.9174 | 0.0018417 | Sustained | FALSE | FALSE | TMED_Event | 2704
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 18:52 | 1526 | 022:09 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1329 | 2022-04-06 | 2028054 | keep | 0 | Apr | 2022 | 1.3813 | 0.0010394 | Sustained | FALSE | FALSE | TMED_Event | 1526
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 18:28 | 308 | 021:45 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1305 | 2022-04-06 | 401940 | keep | 0 | Apr | 2022 | 0.27376 | 0.00020978 | Sustained | FALSE | FALSE | TMED_Event | 308
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 18:28 | 1397 | 021:45 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1305 | 2022-04-06 | 1823085 | keep | 0 | Apr | 2022 | 1.2417 | 0.00095149 | Sustained | FALSE | FALSE | TMED_Event | 1397
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 18:28 | 2926 | 021:45 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1305 | 2022-04-06 | 3818430 | keep | 0 | Apr | 2022 | 2.6007 | 0.0019929 | Sustained | FALSE | FALSE | TMED_Event | 2926
BAYAMON | 2022-04-06 20:43 | 2022-04-07 13:34 | 1834 | 016:51 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1011 | 2022-04-06 | 1854174 | keep | 0 | Apr | 2022 | 1.2629 | 0.0012491 | Sustained | FALSE | FALSE | TMED_Event | 1834
BAYAMON | 2022-04-06 20:43 | 2022-04-09 04:26 | 2324 | 055:43 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3343 | 2022-04-06 | 7769132 | keep | 0 | Apr | 2022 | 5.2915 | 0.0015829 | Sustained | FALSE | FALSE | TMED_Event | 2324
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 13:34 | 1570 | 016:51 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1011 | 2022-04-06 | 1587270 | keep | 0 | Apr | 2022 | 1.0811 | 0.0010693 | Sustained | FALSE | FALSE | TMED_Event | 1570
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 12:24 | 27 | 063:41 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3821 | 2022-04-06 | 103167 | keep | 0 | Apr | 2022 | 0.070267 | 1.839e-05 | Sustained | FALSE | FALSE | TMED_Event | 27
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 20:52 | 603 | 024:09 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1449 | 2022-04-06 | 873747 | keep | 0 | Apr | 2022 | 0.59511 | 0.0004107 | Sustained | FALSE | FALSE | TMED_Event | 603
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 20:52 | 6 | 024:09 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1449 | 2022-04-06 | 8694 | keep | 0 | Apr | 2022 | 0.0059214 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 11:50 | 325 | 063:07 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3787 | 2022-04-06 | 1230775 | keep | 0 | Apr | 2022 | 0.83828 | 0.00022136 | Sustained | FALSE | FALSE | TMED_Event | 325
VEGA BAJA | 2022-04-06 20:43 | 2022-04-09 05:08 | 172 | 056:25 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3385 | 2022-04-06 | 582220 | keep | 0 | Apr | 2022 | 0.39655 | 0.00011715 | Sustained | FALSE | FALSE | TMED_Event | 172
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 13:34 | 31 | 016:51 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1011 | 2022-04-06 | 31341 | keep | 0 | Apr | 2022 | 0.021346 | 2.1114e-05 | Sustained | FALSE | FALSE | TMED_Event | 31
BAYAMON | 2022-04-06 20:43 | 2022-04-07 13:34 | 1859 | 016:51 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1011 | 2022-04-06 | 1879449 | keep | 0 | Apr | 2022 | 1.2801 | 0.0012662 | Sustained | FALSE | FALSE | TMED_Event | 1859
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 13:34 | 7 | 016:51 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1011 | 2022-04-06 | 7077 | keep | 0 | Apr | 2022 | 0.0048201 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BAYAMON | 2022-04-06 20:43 | 2022-04-07 13:36 | 2861 | 016:53 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1013 | 2022-04-06 | 2898193 | keep | 0 | Apr | 2022 | 1.9739 | 0.0019486 | Sustained | FALSE | FALSE | TMED_Event | 2861
BAYAMON | 2022-04-06 20:43 | 2022-04-07 13:36 | 2096 | 016:53 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1013 | 2022-04-06 | 2123248 | keep | 0 | Apr | 2022 | 1.4461 | 0.0014276 | Sustained | FALSE | FALSE | TMED_Event | 2096
BAYAMON | 2022-04-06 20:43 | 2022-04-07 13:36 | 493 | 016:53 | S | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1013 | 2022-04-06 | 499409 | keep | 0 | Apr | 2022 | 0.34015 | 0.00033578 | Sustained | FALSE | FALSE | TMED_Event | 493
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:30 | 941 | 014:47 | T | LINEA DE TRANSMISION | APAGON GENERAL - LLEVA CARGA DEL 9405-09 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 887 | 2022-04-06 | 834667 | keep | 0 | Apr | 2022 | 0.56849 | 0.00064091 | Sustained | FALSE | FALSE | TMED_Event | 941
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:15 | 1 | 014:32 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 872 | 2022-04-06 | 872 | keep | 0 | Apr | 2022 | 0.00059392 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:32 | 2678 | 014:49 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 889 | 2022-04-06 | 2380742 | keep | 0 | Apr | 2022 | 1.6215 | 0.001824 | Sustained | FALSE | FALSE | TMED_Event | 2678
VEGA BAJA | 2022-04-06 20:43 | 2022-04-07 23:58 | 425 | 027:15 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1635 | 2022-04-06 | 694875 | keep | 0 | Apr | 2022 | 0.47328 | 0.00028947 | Sustained | FALSE | FALSE | TMED_Event | 425
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:29 | 3511 | 014:46 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 886 | 2022-04-06 | 3110746 | keep | 0 | Apr | 2022 | 2.1187 | 0.0023913 | Sustained | FALSE | FALSE | TMED_Event | 3511
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:15 | 1 | 014:32 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 872 | 2022-04-06 | 872 | keep | 0 | Apr | 2022 | 0.00059392 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-06 20:43 | 2022-04-07 11:30 | 136 | 014:47 | T | LINEA DE TRANSMISION | APAGON GENERAL - CARGA TRANSFERIDA AL 9403-01 | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 887 | 2022-04-06 | 120632 | keep | 0 | Apr | 2022 | 0.082162 | 9.2629e-05 | Sustained | FALSE | FALSE | TMED_Event | 136
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:40 | 3070 | 026:57 | S | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1617 | 2022-04-06 | 4964190 | keep | 0 | Apr | 2022 | 3.3811 | 0.002091 | Sustained | FALSE | FALSE | TMED_Event | 3070
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:40 | 2735 | 026:57 | S | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1617 | 2022-04-06 | 4422495 | keep | 0 | Apr | 2022 | 3.0121 | 0.0018628 | Sustained | FALSE | FALSE | TMED_Event | 2735
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:40 | 1070 | 026:57 | S | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1617 | 2022-04-06 | 1730190 | keep | 0 | Apr | 2022 | 1.1784 | 0.00072877 | Sustained | FALSE | FALSE | TMED_Event | 1070
BAYAMON | 2022-04-06 20:43 | 2022-04-08 04:55 | 1647 | 032:12 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1932 | 2022-04-06 | 3182004 | keep | 0 | Apr | 2022 | 2.1672 | 0.0011218 | Sustained | FALSE | FALSE | TMED_Event | 1647
BAYAMON | 2022-04-06 20:43 | 2022-04-08 04:55 | 3295 | 032:12 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1932 | 2022-04-06 | 6365940 | keep | 0 | Apr | 2022 | 4.3358 | 0.0022442 | Sustained | FALSE | FALSE | TMED_Event | 3295
BAYAMON | 2022-04-06 20:43 | 2022-04-08 04:55 | 1180 | 032:12 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1932 | 2022-04-06 | 2279760 | keep | 0 | Apr | 2022 | 1.5527 | 0.00080369 | Sustained | FALSE | FALSE | TMED_Event | 1180
BAYAMON | 2022-04-06 20:43 | 2022-04-08 04:55 | 320 | 032:12 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1932 | 2022-04-06 | 618240 | keep | 0 | Apr | 2022 | 0.42108 | 0.00021795 | Sustained | FALSE | FALSE | TMED_Event | 320
BAYAMON | 2022-04-06 20:43 | 2022-04-08 04:55 | 2234 | 032:12 | T | LINEA DE TRANSMISION | APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1932 | 2022-04-06 | 4316088 | keep | 0 | Apr | 2022 | 2.9397 | 0.0015216 | Sustained | FALSE | FALSE | TMED_Event | 2234
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-09 04:51 | 2192 | 056:08 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040900000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3368 | 2022-04-06 | 7382656 | keep | 0 | Apr | 2022 | 5.0283 | 0.001493 | Sustained | FALSE | FALSE | TMED_Event | 2192
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 01:01 | 3296 | 028:18 | T | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1698 | 2022-04-06 | 5596608 | keep | 0 | Apr | 2022 | 3.8118 | 0.0022449 | Sustained | FALSE | FALSE | TMED_Event | 3296
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 04:51 | 1364 | 032:08 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040900000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1928 | 2022-04-06 | 2629792 | keep | 0 | Apr | 2022 | 1.7911 | 0.00092901 | Sustained | FALSE | FALSE | TMED_Event | 1364
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 04:52 | 2937 | 032:09 | T | LINEA DE TRANSMISION | APAGON GENERAL | R22040900000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1929 | 2022-04-06 | 5665473 | keep | 0 | Apr | 2022 | 3.8587 | 0.0020004 | Sustained | FALSE | FALSE | TMED_Event | 2937
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 01:02 | 2410 | 028:19 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1699 | 2022-04-06 | 4094590 | keep | 0 | Apr | 2022 | 2.7888 | 0.0016414 | Sustained | FALSE | FALSE | TMED_Event | 2410
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 01:02 | 2826 | 028:19 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1699 | 2022-04-06 | 4801374 | keep | 0 | Apr | 2022 | 3.2702 | 0.0019248 | Sustained | FALSE | FALSE | TMED_Event | 2826
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 01:01 | 1604 | 028:18 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1698 | 2022-04-06 | 2723592 | keep | 0 | Apr | 2022 | 1.855 | 0.0010925 | Sustained | FALSE | FALSE | TMED_Event | 1604
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 01:01 | 1131 | 028:18 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1698 | 2022-04-06 | 1920438 | keep | 0 | Apr | 2022 | 1.308 | 0.00077032 | Sustained | FALSE | FALSE | TMED_Event | 1131
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 01:01 | 2362 | 028:18 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1698 | 2022-04-06 | 4010676 | keep | 0 | Apr | 2022 | 2.7317 | 0.0016087 | Sustained | FALSE | FALSE | TMED_Event | 2362
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:28 | 4176 | 026:45 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1605 | 2022-04-06 | 6702480 | keep | 0 | Apr | 2022 | 4.565 | 0.0028443 | Sustained | FALSE | FALSE | TMED_Event | 4176
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:35 | 252 | 026:52 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1612 | 2022-04-06 | 406224 | keep | 0 | Apr | 2022 | 0.27668 | 0.00017164 | Sustained | FALSE | FALSE | TMED_Event | 252
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:35 | 2147 | 026:52 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1612 | 2022-04-06 | 3460964 | keep | 0 | Apr | 2022 | 2.3572 | 0.0014623 | Sustained | FALSE | FALSE | TMED_Event | 2147
BAYAMON | 2022-04-06 20:43 | 2022-04-07 23:35 | 2858 | 026:52 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL | B22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1612 | 2022-04-06 | 4607096 | keep | 0 | Apr | 2022 | 3.1379 | 0.0019466 | Sustained | FALSE | FALSE | TMED_Event | 2858
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-09 04:55 | 229 | 056:12 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3372 | 2022-04-06 | 772188 | keep | 0 | Apr | 2022 | 0.52593 | 0.00015597 | Sustained | FALSE | FALSE | TMED_Event | 229
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-09 04:55 | 1246 | 056:12 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 3372 | 2022-04-06 | 4201512 | keep | 0 | Apr | 2022 | 2.8616 | 0.00084864 | Sustained | FALSE | FALSE | TMED_Event | 1246
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 00:38 | 2635 | 027:55 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1675 | 2022-04-06 | 4413625 | keep | 0 | Apr | 2022 | 3.0061 | 0.0017947 | Sustained | FALSE | FALSE | TMED_Event | 2635
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 00:38 | 2280 | 027:55 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1675 | 2022-04-06 | 3819000 | keep | 0 | Apr | 2022 | 2.6011 | 0.0015529 | Sustained | FALSE | FALSE | TMED_Event | 2280
BARRANQUITAS | 2022-04-06 20:43 | 2022-04-08 00:38 | 1617 | 027:55 | S | LINEA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1675 | 2022-04-06 | 2708475 | keep | 0 | Apr | 2022 | 1.8447 | 0.0011013 | Sustained | FALSE | FALSE | TMED_Event | 1617
MAYAGÃœEZ | 2022-04-07 02:23 | 2022-04-07 09:56 | 60 | 007:33 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR POR PARRARAYO CRUZADO EVENTO ANTES DE LA AVERIA DE COSTA SUR | M22040600022 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 453 | 2022-04-07 | 27180 | keep | 0 | Apr | 2022 | 0.018512 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-07 04:47 | 2022-04-08 19:34 | 300 | 038:47 | P | LINEA DE TRANSMISION | APAGON GENERAL SE CERRO INTERRUPTOR 1206-01 LLEVA CARGA 1206-02 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S2204060000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 2327 | 2022-04-07 | 698100 | keep | 0 | Apr | 2022 | 0.47547 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-07 05:25 | 2022-04-07 05:51 | 4098 | 000:26 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | R22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 26 | 2022-04-07 | 106548 | keep | 0 | Apr | 2022 | 0.072569 | 0.0027911 | Sustained | FALSE | FALSE | Not_TMED_Event | 4098
SAN JUAN | 2022-04-07 05:43 | 2022-04-07 17:55 | 137 | 012:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 732 | 2022-04-07 | 100284 | keep | 0 | Apr | 2022 | 0.068303 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2022-04-07 05:43 | 2022-04-07 17:55 | 457 | 012:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 732 | 2022-04-07 | 334524 | keep | 0 | Apr | 2022 | 0.22784 | 0.00031126 | Sustained | FALSE | FALSE | Not_TMED_Event | 457
FAJARDO | 2022-04-07 05:51 | 2022-04-07 11:23 | 956 | 005:32 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | R22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 332 | 2022-04-07 | 317392 | keep | 0 | Apr | 2022 | 0.21617 | 0.00065113 | Sustained | FALSE | FALSE | Not_TMED_Event | 956
ARECIBO | 2022-04-07 06:31 | 2022-04-07 06:32 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22040700081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-07 | 1227 | keep | 0 | Apr | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-04-07 06:32 | 2022-04-07 14:42 | 150 | 008:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARO LINEAS CRUZADAS | A22040700225 | New_Event | Wire Down | Include | Include | Equipment | 490 | 2022-04-07 | 73500 | keep | 0 | Apr | 2022 | 0.050061 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-04-07 07:06 | 2022-04-07 11:23 | 500 | 004:17 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO 0082 COSTA SUR APAGON GENERAL 20% POR 1118-10 | S22040600000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 257 | 2022-04-07 | 128500 | keep | 0 | Apr | 2022 | 0.087521 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-04-07 07:06 | 2022-04-07 14:13 | 823 | 007:07 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR 5 APAGON GENERAL SE CERRO INTERRUPTOR 1111-01 CARGA POR 1111-01 Y 1119-04 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 427 | 2022-04-07 | 351421 | keep | 0 | Apr | 2022 | 0.23935 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-07 07:07 | 2022-04-08 03:44 | 218 | 020:37 | S | LINEA DE TRANSMISION | APAGON GENERAL | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1237 | 2022-04-07 | 269666 | keep | 0 | Apr | 2022 | 0.18367 | 0.00014848 | Sustained | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2022-04-07 07:14 | 2022-04-08 12:28 | 17 | 029:14 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO AL PROBAR 1111-01 | S22040600000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1754 | 2022-04-07 | 29818 | keep | 0 | Apr | 2022 | 0.020309 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2022-04-07 07:49 | 2022-04-07 10:26 | 4664 | 002:37 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M22040700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-04-07 | 732248 | keep | 0 | Apr | 2022 | 0.49873 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
SAN JUAN | 2022-04-07 08:04 | 2022-04-07 11:18 | 1191 | 003:14 | T | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 194 | 2022-04-07 | 231054 | keep | 0 | Apr | 2022 | 0.15737 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-07 08:04 | 2022-04-07 11:17 | 60 | 003:13 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 193 | 2022-04-07 | 11580 | keep | 0 | Apr | 2022 | 0.0078871 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-07 08:04 | 2022-04-07 11:17 | 449 | 003:13 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 193 | 2022-04-07 | 86657 | keep | 0 | Apr | 2022 | 0.059022 | 0.00030581 | Sustained | FALSE | FALSE | Not_TMED_Event | 449
BAYAMON | 2022-04-07 08:04 | 2022-04-07 10:49 | 727 | 002:45 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 165 | 2022-04-07 | 119955 | keep | 0 | Apr | 2022 | 0.081701 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-07 08:04 | 2022-04-07 10:49 | 1420 | 002:45 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 165 | 2022-04-07 | 234300 | keep | 0 | Apr | 2022 | 0.15958 | 0.00096716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-04-07 08:04 | 2022-04-07 10:49 | 290 | 002:45 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 165 | 2022-04-07 | 47850 | keep | 0 | Apr | 2022 | 0.03259 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-07 08:04 | 2022-04-07 10:49 | 610 | 002:45 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 165 | 2022-04-07 | 100650 | keep | 0 | Apr | 2022 | 0.068552 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-07 08:04 | 2022-04-07 10:49 | 842 | 002:45 | S | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 165 | 2022-04-07 | 138930 | keep | 0 | Apr | 2022 | 0.094625 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-07 08:41 | 2022-04-07 11:19 | 9 | 002:38 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 158 | 2022-04-07 | 1422 | keep | 0 | Apr | 2022 | 0.00096852 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-04-07 09:07 | 2022-04-07 15:00 | 761 | 005:53 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 353 | 2022-04-07 | 268633 | keep | 0 | Apr | 2022 | 0.18296 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2022-04-07 09:08 | 2022-04-07 11:21 | 293 | 002:13 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 133 | 2022-04-07 | 38969 | keep | 0 | Apr | 2022 | 0.026542 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2022-04-07 10:49 | 2022-04-09 06:26 | 1420 | 043:37 | T | LINEA DE TRANSMISION | APAGON GENERAL CARGA POR EL 1530-07 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 2617 | 2022-04-07 | 3716140 | keep | 0 | Apr | 2022 | 2.531 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-07 10:56 | 2022-04-07 11:09 | 1839 | 000:13 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | R22040700101 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2022-04-07 | 23907 | keep | 0 | Apr | 2022 | 0.016283 | 0.0012525 | Sustained | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2022-04-07 10:56 | 2022-04-07 11:09 | 1376 | 000:13 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | R22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2022-04-07 | 17888 | keep | 0 | Apr | 2022 | 0.012183 | 0.00093719 | Sustained | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2022-04-07 10:57 | 2022-04-07 11:08 | 4098 | 000:11 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | R22040700106 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2022-04-07 | 45078 | keep | 0 | Apr | 2022 | 0.030702 | 0.0027911 | Sustained | FALSE | FALSE | Not_TMED_Event | 4098
FAJARDO | 2022-04-07 10:57 | 2022-04-07 11:08 | 293 | 000:11 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | R22040700103 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2022-04-07 | 3223 | keep | 0 | Apr | 2022 | 0.0021952 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2022-04-07 10:59 | 2022-04-07 11:07 | 1778 | 000:08 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | R22040700108 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-04-07 | 14224 | keep | 0 | Apr | 2022 | 0.0096879 | 0.001211 | Sustained | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2022-04-07 10:59 | 2022-04-07 11:07 | 1215 | 000:08 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | R22040700107 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-04-07 | 9720 | keep | 0 | Apr | 2022 | 0.0066202 | 0.00082753 | Sustained | FALSE | FALSE | Not_TMED_Event | 1215
SAN JUAN | 2022-04-07 11:23 | 2022-04-07 14:16 | 2566 | 002:53 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO AL PROBAR 1111-02 BARRA QUEMADA EN SU-20 | S22040700000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 173 | 2022-04-07 | 443918 | keep | 0 | Apr | 2022 | 0.30235 | 0.0017477 | Sustained | FALSE | FALSE | Not_TMED_Event | 2566
ARECIBO | 2022-04-07 11:35 | 2022-04-07 12:11 | 1227 | 000:36 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO CAUSA EL CCE AUTORIZO CERRAR EL INTERRUPTOR | A22040700196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2022-04-07 | 44172 | keep | 0 | Apr | 2022 | 0.030085 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
SAN JUAN | 2022-04-07 12:30 | 2022-04-07 13:18 | 67 | 000:48 | P | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL 10% DE LA CARGA POR 1418-02 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 48 | 2022-04-07 | 3216 | keep | 0 | Apr | 2022 | 0.0021904 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
ARECIBO | 2022-04-07 12:31 | 2022-04-07 14:29 | 20 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A22040700220 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2022-04-07 | 2360 | keep | 0 | Apr | 2022 | 0.0016074 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-07 12:36 | 2022-04-07 15:13 | 80 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22040700223 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2022-04-07 | 12560 | keep | 0 | Apr | 2022 | 0.0085546 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-07 12:44 | 2022-04-08 09:09 | 1106 | 020:25 | P | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL 60% POR 1529-15 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 1225 | 2022-04-07 | 1354850 | keep | 0 | Apr | 2022 | 0.92278 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-07 12:46 | 2022-04-07 23:48 | 2070 | 011:02 | T | LINEA DE TRANSMISION | APAGON GENERAL DISPARO 0082 COSTA SUR BKR 1718-03 LLEVA 40% 1710-05 | B22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 662 | 2022-04-07 | 1370340 | keep | 0 | Apr | 2022 | 0.93333 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-07 12:50 | 2022-04-07 14:14 | 1000 | 001:24 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 84 | 2022-04-07 | 84000 | keep | 0 | Apr | 2022 | 0.057212 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-04-07 12:50 | 2022-04-07 14:14 | 278 | 001:24 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 84 | 2022-04-07 | 23352 | keep | 0 | Apr | 2022 | 0.015905 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2022-04-07 12:50 | 2022-04-07 14:14 | 2203 | 001:24 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 84 | 2022-04-07 | 185052 | keep | 0 | Apr | 2022 | 0.12604 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-04-07 12:50 | 2022-04-07 14:14 | 9 | 001:24 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 84 | 2022-04-07 | 756 | keep | 0 | Apr | 2022 | 0.00051491 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-04-07 13:37 | 2022-04-09 04:09 | 500 | 038:32 | P | LINEA DE TRANSMISION | APAGON GENERAL 1343-05 LLEVA CARGA DEL 1908-3 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 2312 | 2022-04-07 | 1156000 | keep | 0 | Apr | 2022 | 0.78735 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-07 13:37 | 2022-04-09 03:41 | 500 | 038:04 | P | LINEA DE TRANSMISION | APAGON GENERAL 1343-03 LLEVA CARGA CONVERTIDOR 1908-03 | S22040600000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2284 | 2022-04-07 | 1142000 | keep | 0 | Apr | 2022 | 0.77781 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-04-07 13:50 | 2022-04-07 21:36 | 8711 | 007:46 | P | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL PARTE POR 1206-3 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 466 | 2022-04-07 | 4059326 | keep | 0 | Apr | 2022 | 2.7648 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-07 13:50 | 2022-04-07 14:14 | 1500 | 000:24 | P | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR APAGON GENERAL | S22040700000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-04-07 | 36000 | keep | 0 | Apr | 2022 | 0.024519 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-04-07 13:56 | 2022-04-08 04:07 | 5630 | 014:11 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | C22040600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 851 | 2022-04-07 | 4791130 | keep | 0 | Apr | 2022 | 3.2632 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
SAN JUAN | 2022-04-07 14:38 | 2022-04-08 06:28 | 399 | 015:50 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S22040700568 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 950 | 2022-04-07 | 379050 | keep | 0 | Apr | 2022 | 0.25817 | 0.00027176 | Sustained | FALSE | FALSE | Not_TMED_Event | 399
BAYAMON | 2022-04-07 14:52 | 2022-04-07 23:10 | 40 | 008:18 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO Y TRANSFORMADOR | S22040700642 | New_Event | Defective Pole | Include | Include | Equipment | 498 | 2022-04-07 | 19920 | keep | 0 | Apr | 2022 | 0.013567 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-07 16:03 | 2022-04-07 20:03 | 30 | 004:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040700325 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-04-07 | 7200 | keep | 0 | Apr | 2022 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-07 16:10 | 2022-04-07 18:04 | 120 | 001:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A22040700329 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-04-07 | 13680 | keep | 0 | Apr | 2022 | 0.0093174 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-04-07 22:02 | 2022-04-08 16:53 | 552 | 018:51 | P | LINEA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL SE CERRO INTERRUPTOR 1204-01 QUE LLEVA EL 40% DEL 1204-03 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 1131 | 2022-04-07 | 624312 | keep | 0 | Apr | 2022 | 0.42522 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-07 22:33 | 2022-04-07 22:34 | 2000 | 000:01 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO 0082 COSTA SUR. APAGON GENERAL INTERRUPTOR 1206-04 LLEVA 40% 1204-04 Y 60% 1204-03 | S22040600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-04-07 | 2000 | keep | 0 | Apr | 2022 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2022-04-07 22:46 | 2022-04-07 22:52 | 19 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1512-05 | S22040700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-04-07 | 114 | keep | 0 | Apr | 2022 | 7.7645e-05 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-04-07 23:53 | 2022-04-09 04:10 | 39 | 028:17 | P | LINEA DE TRANSMISION | APAGON GENERAL EL 80% DEL 1519-03 ESTA POR EL 1910-01 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 1697 | 2022-04-07 | 66183 | keep | 0 | Apr | 2022 | 0.045077 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-04-08 00:42 | 2022-04-08 08:13 | 40 | 007:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE AJUSTO CAJA PRIMARIA | C22040800014 | New_Event | Cutout Failure | Include | Include | Equipment | 451 | 2022-04-08 | 18040 | keep | 0 | Apr | 2022 | 0.012287 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-08 00:46 | 2022-04-08 06:32 | 125 | 005:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22040800015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 346 | 2022-04-08 | 43250 | keep | 0 | Apr | 2022 | 0.029457 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-04-08 01:50 | 2022-04-08 07:00 | 40 | 005:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA PUNTE ABIERTO AFECTO MAS CLIENTES | M22040600211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-04-08 | 12400 | keep | 0 | Apr | 2022 | 0.0084456 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-08 01:50 | 2022-04-10 07:00 | 40 | 053:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESAGNCHE | M22040600211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3190 | 2022-04-08 | 127600 | keep | 0 | Apr | 2022 | 0.086908 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-04-08 06:29 | 2022-04-08 10:24 | 8 | 003:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN TRANSFORMADOR CLIENTE INSTALANDO GENERADOR ELECTRICO | A22040800094 | New_Event |  |  | Include | Wildlife | 235 | 2022-04-08 | 1880 | keep | 0 | Apr | 2022 | 0.0012805 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-08 06:53 | 2022-04-09 19:17 | 91 | 036:24 | P | DESGANCHE | 2 X 100 EN C/L DESGACHE SE REEMPLAZO CAJA PRIMARIA Y BAJANTE PRIMARIO | S22040800160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2184 | 2022-04-08 | 198744 | keep | 0 | Apr | 2022 | 0.13536 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
PONCE | 2022-04-08 06:59 | 2022-04-08 07:03 | 2113 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE CERRO Y QUEDO EN SERVICIO NO SE REPORTO CAUSA | P22010800177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-08 | 8452 | keep | 0 | Apr | 2022 | 0.0057566 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
CAGUAS | 2022-04-08 07:19 | 2022-04-08 11:18 | 64 | 003:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50, 1 X 40 Y 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22040408001 | New_Event | Cutout Failure | Include | Include | Equipment | 239 | 2022-04-08 | 15296 | keep | 0 | Apr | 2022 | 0.010418 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
HUMACAO | 2022-04-08 07:48 | 2022-04-08 11:20 | 28 | 003:32 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORAMDOR SE ELIMINO PARARRAYOS | C22040800167 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 212 | 2022-04-08 | 5936 | keep | 0 | Apr | 2022 | 0.004043 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
FAJARDO | 2022-04-08 07:56 | 2022-04-08 09:21 | 11 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22040800100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-04-08 | 935 | keep | 0 | Apr | 2022 | 0.00063682 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-04-08 07:58 | 2022-04-08 11:07 | 4 | 003:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A TRANSFORMADOR | C22040800173 | New_Event | Wire Down | Include | Include | Equipment | 189 | 2022-04-08 | 756 | keep | 0 | Apr | 2022 | 0.00051491 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-04-08 08:56 | 2022-04-09 10:47 | 528 | 025:51 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR POR SALIDA SOTERRADA AVERIADA SE TRANSFIRIO LA CARGA AL 6012-02 | M22040800169 | New_Event | UG Cable Fault | Include | Include | Equipment | 1551 | 2022-04-08 | 818928 | keep | 0 | Apr | 2022 | 0.55777 | 0.00035962 | Sustained | FALSE | FALSE | Not_TMED_Event | 528
SAN JUAN | 2022-04-08 09:14 | 2022-04-08 09:16 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVA PARTE 1206-3 | S22040800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-08 | 3230 | keep | 0 | Apr | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
BAYAMON | 2022-04-08 09:22 | 2022-04-08 10:55 | 1 | 001:33 | P | NO SE REPORTO CAUSA | 2 X 25 EN CORTE DE LINEA | B22040800283 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-04-08 | 93 | keep | 0 | Apr | 2022 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-08 09:26 | 2022-04-08 09:29 | 1984 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1911-7 | S2204080000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-08 | 5952 | keep | 0 | Apr | 2022 | 0.0040539 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-04-08 09:26 | 2022-04-08 09:29 | 577 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1911-7 | S2204080000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-08 | 1731 | keep | 0 | Apr | 2022 | 0.001179 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
UTUADO | 2022-04-08 09:42 | 2022-04-08 10:05 | 15 | 000:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22040800171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-04-08 | 345 | keep | 0 | Apr | 2022 | 0.00023498 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-04-08 09:58 | 2022-04-08 14:56 | 10 | 004:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN XMR SE REEMPLAZO SECUNDARIA | C22040800237 | New_Event | Secondary Wire Down | Include | Include | Equipment | 298 | 2022-04-08 | 2980 | keep | 0 | Apr | 2022 | 0.0020297 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-08 10:15 | 2022-04-08 10:16 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-08 | 959 | keep | 0 | Apr | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-04-08 10:15 | 2022-04-08 10:31 | 5809 | 000:16 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR - SE CERRO POR CONTROL - CARGA TRANSFERIDA AL 1710-02 | B22040800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2022-04-08 | 92944 | keep | 0 | Apr | 2022 | 0.063304 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
ARECIBO | 2022-04-08 10:22 | 2022-04-09 20:24 | 1879 | 034:02 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETES PARA SECCIONALIZAR Y CERRAR EL INTERRUPTOR CONTINUA LA INTERRUPCION CON UNA PARCIAL | A22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2042 | 2022-04-08 | 3836918 | keep | 0 | Apr | 2022 | 2.6133 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
BAYAMON | 2022-04-08 10:35 | 2022-04-08 10:36 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-08 | 4431 | keep | 0 | Apr | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
VEGA BAJA | 2022-04-08 10:38 | 2022-04-08 10:40 | 31 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B22040800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-08 | 62 | keep | 0 | Apr | 2022 | 4.2228e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
VEGA BAJA | 2022-04-08 10:39 | 2022-04-08 10:40 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-08 | 7 | keep | 0 | Apr | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-04-08 11:00 | 2022-04-08 13:07 | 8 | 002:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | A22040800243 | New_Event | Wire Down | Include | Include | Equipment | 127 | 2022-04-08 | 1016 | keep | 0 | Apr | 2022 | 0.00069199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-08 11:07 | 2022-04-08 11:08 | 1825 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22040800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-08 | 1825 | keep | 0 | Apr | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2022-04-08 11:45 | 2022-04-08 13:50 | 100 | 002:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22040800325 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-04-08 | 12500 | keep | 0 | Apr | 2022 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-08 11:46 | 2022-04-08 12:37 | 50 | 000:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR PALOMA | A22040800022 | New_Event |  |  | Include | Wildlife | 51 | 2022-04-08 | 2550 | keep | 0 | Apr | 2022 | 0.0017368 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-08 11:53 | 2022-04-08 15:25 | 12 | 003:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO CAJA | B22040800394 | New_Event | Cutout Failure | Include | Include | Equipment | 212 | 2022-04-08 | 2544 | keep | 0 | Apr | 2022 | 0.0017327 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-04-08 11:54 | 2022-04-08 12:38 | 100 | 000:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040800221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-04-08 | 4400 | keep | 0 | Apr | 2022 | 0.0029968 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-08 12:28 | 2022-04-08 12:37 | 2077 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR | M22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-04-08 | 18693 | keep | 0 | Apr | 2022 | 0.012732 | 0.0014146 | Sustained | FALSE | FALSE | Not_TMED_Event | 2077
CANOVANAS | 2022-04-08 12:42 | 2022-04-08 12:48 | 1894 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA CANOVANAS SECT | R22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-08 | 11364 | keep | 0 | Apr | 2022 | 0.00774 | 0.00129 | Sustained | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2022-04-08 12:42 | 2022-04-08 12:48 | 4154 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA CANOVANAS SECT | R22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-08 | 24924 | keep | 0 | Apr | 2022 | 0.016976 | 0.0028293 | Sustained | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2022-04-08 12:42 | 2022-04-08 12:48 | 424 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA CANOVANAS SECT | R22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-08 | 2544 | keep | 0 | Apr | 2022 | 0.0017327 | 0.00028878 | Sustained | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2022-04-08 12:42 | 2022-04-08 12:48 | 2708 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA CANOVANAS SECT | R22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-08 | 16248 | keep | 0 | Apr | 2022 | 0.011066 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-04-08 12:42 | 2022-04-08 12:48 | 2524 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA CANOVANAS SECT | R22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-08 | 15144 | keep | 0 | Apr | 2022 | 0.010315 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-04-08 12:42 | 2022-04-08 12:48 | 1648 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA CANOVANAS SECT | R22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-04-08 | 9888 | keep | 0 | Apr | 2022 | 0.0067347 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-04-08 12:42 | 2022-04-08 12:47 | 3838 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA CANOVANAS SECT | R22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-08 | 19190 | keep | 0 | Apr | 2022 | 0.01307 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
CANOVANAS | 2022-04-08 12:42 | 2022-04-08 12:47 | 817 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA CANOVANAS SECT | R22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-08 | 4085 | keep | 0 | Apr | 2022 | 0.0027823 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CANOVANAS | 2022-04-08 12:42 | 2022-04-08 12:47 | 1124 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA CANOVANAS SECT | R22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-08 | 5620 | keep | 0 | Apr | 2022 | 0.0038278 | 0.00076555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1124
SAN JUAN | 2022-04-08 12:52 | 2022-04-08 16:47 | 50 | 003:55 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO TERMINACION | S22040800606 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 235 | 2022-04-08 | 11750 | keep | 0 | Apr | 2022 | 0.0080029 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-08 12:52 | 2022-04-08 13:54 | 1894 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2022-04-08 | 117428 | keep | 0 | Apr | 2022 | 0.07998 | 0.00129 | Sustained | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2022-04-08 12:52 | 2022-04-08 13:54 | 4154 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2022-04-08 | 257548 | keep | 0 | Apr | 2022 | 0.17541 | 0.0028293 | Sustained | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2022-04-08 12:52 | 2022-04-08 13:54 | 424 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2022-04-08 | 26288 | keep | 0 | Apr | 2022 | 0.017905 | 0.00028878 | Sustained | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2022-04-08 12:52 | 2022-04-08 13:54 | 2708 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2022-04-08 | 167896 | keep | 0 | Apr | 2022 | 0.11435 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-04-08 12:52 | 2022-04-08 13:54 | 2524 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2022-04-08 | 156488 | keep | 0 | Apr | 2022 | 0.10658 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-04-08 12:52 | 2022-04-08 13:54 | 1648 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2022-04-08 | 102176 | keep | 0 | Apr | 2022 | 0.069592 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-04-08 12:52 | 2022-04-08 13:20 | 3838 | 000:28 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE CANOVANAS SECT | R22040800000 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 28 | 2022-04-08 | 107464 | keep | 0 | Apr | 2022 | 0.073193 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-08 12:52 | 2022-04-08 13:20 | 817 | 000:28 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE CANOVANAS SECT | R22040800000 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 28 | 2022-04-08 | 22876 | keep | 0 | Apr | 2022 | 0.015581 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-08 12:52 | 2022-04-08 13:20 | 1124 | 000:28 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE CANOVANAS SECT | R22040800000 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 28 | 2022-04-08 | 31472 | keep | 0 | Apr | 2022 | 0.021435 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-08 12:54 | 2022-04-09 03:39 | 445 | 014:45 | P | LINEA DE TRANSMISION | APAGON GENERAL SE CERRO INTERRUPTOR 1301-02. 1335-05 LLEVA 40% DEL 1301-02 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 885 | 2022-04-08 | 393825 | keep | 0 | Apr | 2022 | 0.26823 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-08 12:55 | 2022-04-08 12:56 | 135 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO AL CERRAR N/O SE VERIFICO Y SE CERRO LOCAMENTE 100% EN SERVICIO 1401-8 Y 1346-5 | S22040600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-08 | 135 | keep | 0 | Apr | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2022-04-08 13:17 | 2022-04-08 16:38 | 2077 | 003:21 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR SE PATRULLO Y NO SE ENCONTRO CAUSA SE CERRO POR SCADA | M22040800312 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 201 | 2022-04-08 | 417477 | keep | 0 | Apr | 2022 | 0.28434 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-08 13:33 | 2022-04-08 14:15 | 5 | 000:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22040800276 | New_Event | Wire Down | Include | Include | Equipment | 42 | 2022-04-08 | 210 | keep | 0 | Apr | 2022 | 0.00014303 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-04-08 13:51 | 2022-04-08 14:09 | 922 | 000:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO N/O PARA RETIRAR PUENTE SAFADO COLGANDO | S22040800000 | New_Event | Wire Down | Include | Include | Equipment | 18 | 2022-04-08 | 16596 | keep | 0 | Apr | 2022 | 0.011303 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
PONCE | 2022-04-08 14:41 | 2022-04-08 15:45 | 250 | 001:04 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | P22040800223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-04-08 | 16000 | keep | 0 | Apr | 2022 | 0.010898 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
HUMACAO | 2022-04-08 15:00 | 2022-04-08 17:09 | 1 | 002:09 | P | NO SE REPORTO CAUSA | 2 X 25 SMU | C22040800373 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2022-04-08 | 129 | keep | 0 | Apr | 2022 | 8.7861e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-08 15:00 | 2022-04-08 16:45 | 12 | 001:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON PROBLEMAS DE VOLTAJE | B22040800000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 105 | 2022-04-08 | 1260 | keep | 0 | Apr | 2022 | 0.00085818 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-08 15:05 | 2022-04-08 18:09 | 40 | 003:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA QUEMADA | C22040800378 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2022-04-08 | 7360 | keep | 0 | Apr | 2022 | 0.0050129 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-08 15:13 | 2022-04-08 16:17 | 30 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22040800735 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-04-08 | 1920 | keep | 0 | Apr | 2022 | 0.0013077 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-08 15:19 | 2022-04-08 16:49 | 5 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | A22040800286 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-04-08 | 450 | keep | 0 | Apr | 2022 | 0.00030649 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-04-08 15:31 | 2022-04-08 15:40 | 1894 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-04-08 | 17046 | keep | 0 | Apr | 2022 | 0.01161 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-08 15:31 | 2022-04-08 15:40 | 4154 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-04-08 | 37386 | keep | 0 | Apr | 2022 | 0.025463 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-08 15:31 | 2022-04-08 15:40 | 424 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-04-08 | 3816 | keep | 0 | Apr | 2022 | 0.0025991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-08 15:31 | 2022-04-08 16:29 | 3838 | 000:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 58 | 2022-04-08 | 222604 | keep | 0 | Apr | 2022 | 0.15161 | 0.002614 | Sustained | FALSE | FALSE | Not_TMED_Event | 3838
CANOVANAS | 2022-04-08 15:31 | 2022-04-08 16:29 | 817 | 000:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 58 | 2022-04-08 | 47386 | keep | 0 | Apr | 2022 | 0.032274 | 0.00055645 | Sustained | FALSE | FALSE | Not_TMED_Event | 817
CANOVANAS | 2022-04-08 15:31 | 2022-04-08 16:29 | 1124 | 000:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22040800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 58 | 2022-04-08 | 65192 | keep | 0 | Apr | 2022 | 0.044402 | 0.00076555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1124
HUMACAO | 2022-04-08 16:00 | 2022-04-08 20:59 | 10 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22040800399 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2022-04-08 | 2990 | keep | 0 | Apr | 2022 | 0.0020365 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-08 16:19 | 2022-04-08 17:27 | 40 | 001:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22040800322 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-04-08 | 2720 | keep | 0 | Apr | 2022 | 0.0018526 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-08 16:19 | 2022-04-08 21:30 | 50 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22040800404 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2022-04-08 | 15550 | keep | 0 | Apr | 2022 | 0.010591 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-08 16:40 | 2022-04-08 18:37 | 15 | 001:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22040800822 | New_Event | Secondary Wire Down | Include | Include | Equipment | 117 | 2022-04-08 | 1755 | keep | 0 | Apr | 2022 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-08 17:28 | 2022-04-08 22:30 | 100 | 005:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R22040800284 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2022-04-08 | 30200 | keep | 0 | Apr | 2022 | 0.020569 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-08 17:45 | 2022-04-09 06:57 | 30 | 013:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA | B22040800634 | New_Event | Cutout Failure | Include | Include | Equipment | 792 | 2022-04-08 | 23760 | keep | 0 | Apr | 2022 | 0.016183 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-04-08 17:46 | 2022-04-08 18:37 | 36 | 000:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L SE RETIRO CULEBRA | R22040800296 | New_Event |  |  | Include | Wildlife | 51 | 2022-04-08 | 1836 | keep | 0 | Apr | 2022 | 0.0012505 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-04-08 17:59 | 2022-04-09 03:24 | 4481 | 009:25 | P | LINEA DE TRANSMISION | APAGON GENERAL CERRADO POR SCADA 30% POR 1619-02 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 565 | 2022-04-08 | 2531765 | keep | 0 | Apr | 2022 | 1.7244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-08 17:59 | 2022-04-09 06:16 | 46 | 012:17 | P | LINEA DE TRANSMISION | APAGON GENERAL SE CERRO INTERRUPTOR 1717-02 95% DE LA CARGA TRANSFERIDA AL 1713-05 | B22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 737 | 2022-04-08 | 33902 | keep | 0 | Apr | 2022 | 0.02309 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-08 18:08 | 2022-04-08 18:13 | 327 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KV / 38KV COMERIO TC | C22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-08 | 1635 | keep | 0 | Apr | 2022 | 0.0011136 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
CAGUAS | 2022-04-08 18:08 | 2022-04-08 18:13 | 1843 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KV / 38KV COMERIO TC | C22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-08 | 9215 | keep | 0 | Apr | 2022 | 0.0062763 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
CAGUAS | 2022-04-08 18:08 | 2022-04-08 18:13 | 2203 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KV / 38KV COMERIO TC | C22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-08 | 11015 | keep | 0 | Apr | 2022 | 0.0075023 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
CAGUAS | 2022-04-08 18:08 | 2022-04-08 18:13 | 2457 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KV / 38KV COMERIO TC | C22040800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-08 | 12285 | keep | 0 | Apr | 2022 | 0.0083673 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
BAYAMON | 2022-04-08 18:32 | 2022-04-08 18:34 | 1812 | 000:02 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETE QUEMADO | B22040800000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-04-08 | 3624 | keep | 0 | Apr | 2022 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2022-04-08 18:34 | 2022-04-08 20:36 | 900 | 002:02 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO Y SE CERRO POR SCADA | B22040800000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 122 | 2022-04-08 | 109800 | keep | 0 | Apr | 2022 | 0.074784 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
FAJARDO | 2022-04-08 19:03 | 2022-04-08 19:04 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | R22040800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-08 | 1234 | keep | 0 | Apr | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
BAYAMON | 2022-04-08 19:15 | 2022-04-08 19:17 | 320 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22040800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-08 | 640 | keep | 0 | Apr | 2022 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2022-04-08 19:58 | 2022-04-08 20:17 | 108 | 000:19 | S | LINEA DE TRANSMISION 115KV | SE ABRIO LINEA 36200 PARA CERRAR CAMARA DE MOD NO CERRO BIEN | S22040800000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-04-08 | 2052 | keep | 0 | Apr | 2022 | 0.0013976 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2022-04-08 19:58 | 2022-04-08 20:17 | 1368 | 000:19 | S | LINEA DE TRANSMISION 115KV | SE ABRIO LINEA 36200 PARA CERRAR CAMARA DE MOD NO CERRO BIEN | S22040800000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-04-08 | 25992 | keep | 0 | Apr | 2022 | 0.017703 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2022-04-08 19:58 | 2022-04-08 20:17 | 2064 | 000:19 | S | LINEA DE TRANSMISION 115KV | SE ABRIO LINEA 36200 PARA CERRAR CAMARA DE MOD NO CERRO BIEN | S22040800000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-04-08 | 39216 | keep | 0 | Apr | 2022 | 0.02671 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2022-04-08 20:17 | 2022-04-08 21:16 | 36 | 000:59 | P | DESGANCHE | 2 X 40 EN C/L SE DESGANCHO | R22040800343 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-04-08 | 2124 | keep | 0 | Apr | 2022 | 0.0014466 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2022-04-08 20:36 | 2022-04-08 20:38 | 1812 | 000:02 | T | DESCONECTIVO DEFECTUOSO | NORMALIZANDO CARGA DISPARO ALIMENTADOR | B22040800000 | Additional_clients | Switch Failure | Include | Include | Equipment | 2 | 2022-04-08 | 3624 | keep | 0 | Apr | 2022 | 0.0024683 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-08 20:38 | 2022-04-08 21:16 | 900 | 000:38 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y SE CERRO MACHETES | B22040800000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 38 | 2022-04-08 | 34200 | keep | 0 | Apr | 2022 | 0.023293 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
ARECIBO | 2022-04-08 20:39 | 2022-04-09 18:30 | 12 | 021:51 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A22040800411 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1311 | 2022-04-08 | 15732 | keep | 0 | Apr | 2022 | 0.010715 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-08 20:43 | 2022-04-08 23:45 | 4634 | 003:02 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | C22040000240 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 182 | 2022-04-08 | 843388 | keep | 0 | Apr | 2022 | 0.57443 | 0.0031562 | Sustained | FALSE | FALSE | Not_TMED_Event | 4634
ARECIBO | 2022-04-08 20:43 | 2022-04-08 20:50 | 100 | 000:07 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040800403 | New_Event | Bad Weather | Include | Include | Weather | 7 | 2022-04-08 | 700 | keep | 0 | Apr | 2022 | 0.00047677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-08 20:45 | 2022-04-09 13:08 | 3000 | 016:23 | P | DESGANCHE | SE CERRO MACHETES Y SE REALIZO DESGANCHE | M22040800561 | New_Event | Vegetation Contact | Include | Include | Vegetation | 983 | 2022-04-08 | 2949000 | keep | 0 | Apr | 2022 | 2.0086 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
FAJARDO | 2022-04-08 20:48 | 2022-04-08 21:28 | 40 | 000:40 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION EN EL RISER Y SE CERRO | R22040800356 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 40 | 2022-04-08 | 1600 | keep | 0 | Apr | 2022 | 0.0010898 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-08 20:49 | 2022-04-09 02:58 | 25 | 006:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040800415 | New_Event | Bad Weather | Include | Include | Weather | 369 | 2022-04-08 | 9225 | keep | 0 | Apr | 2022 | 0.0062831 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-08 20:57 | 2022-04-09 03:38 | 766 | 006:41 | P | LINEA DE TRANSMISION | APAGON GENERAL 50% POR 1909-07 | S22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 401 | 2022-04-08 | 307166 | keep | 0 | Apr | 2022 | 0.20921 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-08 21:16 | 2022-04-10 02:44 | 91 | 029:28 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETES 100% EN SERVICIO | B22040800000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 1768 | 2022-04-08 | 160888 | keep | 0 | Apr | 2022 | 0.10958 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-04-08 21:18 | 2022-04-09 01:08 | 4 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A22040800425 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2022-04-08 | 920 | keep | 0 | Apr | 2022 | 0.00062661 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2022-04-08 22:00 | 2022-04-08 22:09 | 100 | 000:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R22040800398 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-04-08 | 900 | keep | 0 | Apr | 2022 | 0.00061299 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-08 22:13 | 2022-04-09 00:06 | 200 | 001:53 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | R22040800404 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-04-08 | 22600 | keep | 0 | Apr | 2022 | 0.015393 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-04-08 23:20 | 2022-04-08 23:22 | 551 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR CONTROL | C22040800602 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-04-08 | 1102 | keep | 0 | Apr | 2022 | 0.00075057 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2022-04-08 23:22 | 2022-04-09 01:26 | 36 | 002:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PARTIDA SOBRE TRANSFORMADOR | C22040900008 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 124 | 2022-04-08 | 4464 | keep | 0 | Apr | 2022 | 0.0030404 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2022-04-08 23:25 | 2022-04-09 02:10 | 100 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040800459 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2022-04-08 | 16500 | keep | 0 | Apr | 2022 | 0.011238 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-08 23:30 | 2022-04-09 00:40 | 40 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22040800608 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2022-04-08 | 2800 | keep | 0 | Apr | 2022 | 0.0019071 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-08 23:42 | 2022-04-09 03:43 | 120 | 004:01 | P | DESGANCHE | 2 X 80 EN C/L SE REALIZO DESGANCHE | B22040800828 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-04-08 | 28920 | keep | 0 | Apr | 2022 | 0.019697 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-04-09 00:04 | 2022-04-09 00:08 | 476 | 000:04 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | C22040800003 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-04-09 | 1904 | keep | 0 | Apr | 2022 | 0.0012968 | 0.0003242 | Momentary | FALSE | FALSE | TMED_Event | 476
CAGUAS | 2022-04-09 00:05 | 2022-04-09 00:08 | 2842 | 000:03 | T | DISPARO DE BARRA DE TRANSMISION | APAGON GENERAL | C22040800004 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-09 | 8526 | keep | 0 | Apr | 2022 | 0.005807 | 0.0019357 | Momentary | FALSE | FALSE | TMED_Event | 2842
BAYAMON | 2022-04-09 00:21 | 2022-04-09 00:46 | 350 | 000:25 | P | LINEA DE TRANSMISION | APAGON GENERAL PARTE POR 1708-03 | B22040600000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 25 | 2022-04-09 | 8750 | keep | 0 | Apr | 2022 | 0.0059596 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
AGUADILLA | 2022-04-09 01:35 | 2022-04-09 18:02 | 50 | 016:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040900022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 987 | 2022-04-09 | 49350 | keep | 0 | Apr | 2022 | 0.033612 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
CAGUAS | 2022-04-09 01:45 | 2022-04-09 11:50 | 1342 | 010:05 | T | CABLE SOTERRADO AVERIADO | DISPARO | C22040900000 | New_Event | UG Cable Fault | Include | Include | Equipment | 605 | 2022-04-09 | 811910 | keep | 0 | Apr | 2022 | 0.55299 | 0.00091403 | Sustained | FALSE | FALSE | TMED_Event | 1342
BAYAMON | 2022-04-09 02:10 | 2022-04-09 02:17 | 748 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-04-09 | 5236 | keep | 0 | Apr | 2022 | 0.0035662 | 0.00050946 | Sustained | FALSE | FALSE | TMED_Event | 748
BAYAMON | 2022-04-09 02:10 | 2022-04-09 02:17 | 33 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-04-09 | 231 | keep | 0 | Apr | 2022 | 0.00015733 | 2.2476e-05 | Sustained | FALSE | FALSE | TMED_Event | 33
HUMACAO | 2022-04-09 02:15 | 2022-04-09 02:18 | 1835 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | C22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-09 | 5505 | keep | 0 | Apr | 2022 | 0.0037494 | 0.0012498 | Momentary | FALSE | FALSE | TMED_Event | 1835
ARECIBO | 2022-04-09 02:40 | 2022-04-09 06:48 | 20 | 004:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJAS QUEMADAS | A22040900033 | New_Event | Cutout Failure | Include | Include | Equipment | 248 | 2022-04-09 | 4960 | keep | 0 | Apr | 2022 | 0.0033782 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
HUMACAO | 2022-04-09 02:57 | 2022-04-09 03:48 | 80 | 000:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO. | C22040900070 | New_Event | Wire Down | Include | Include | Equipment | 51 | 2022-04-09 | 4080 | keep | 0 | Apr | 2022 | 0.0027789 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
AGUADILLA | 2022-04-09 03:48 | 2022-04-09 11:25 | 35 | 007:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2022-04-09 | 15995 | keep | 0 | Apr | 2022 | 0.010894 | 2.3838e-05 | Sustained | FALSE | FALSE | TMED_Event | 35
BAYAMON | 2022-04-09 04:29 | 2022-04-09 12:08 | 1825 | 007:39 | T | NO SE REPORTO CAUSA | DISPARO 1118-09 LLEVA 1118-08 | B22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 459 | 2022-04-09 | 837675 | keep | 0 | Apr | 2022 | 0.57054 | 0.001243 | Sustained | FALSE | FALSE | TMED_Event | 1825
BAYAMON | 2022-04-09 04:29 | 2022-04-09 12:08 | 4398 | 007:39 | T | NO SE REPORTO CAUSA | DISPARO 1118-09 LLEVA 1118-08 | B22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 459 | 2022-04-09 | 2018682 | keep | 0 | Apr | 2022 | 1.3749 | 0.0029955 | Sustained | FALSE | FALSE | TMED_Event | 4398
CAGUAS | 2022-04-09 05:21 | 2022-04-09 06:14 | 110 | 000:53 | P | NO SE REPORTO CAUSA | 2 X 80 EN RISER | C22040900123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2022-04-09 | 5830 | keep | 0 | Apr | 2022 | 0.0039708 | 7.492e-05 | Sustained | FALSE | FALSE | TMED_Event | 110
HUMACAO | 2022-04-09 05:28 | 2022-04-09 07:05 | 60 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22040900127 | New_Event |  |  | Include | Wildlife | 97 | 2022-04-09 | 5820 | keep | 0 | Apr | 2022 | 0.003964 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
YAUCO | 2022-04-09 05:31 | 2022-04-09 10:03 | 80 | 004:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22040900089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2022-04-09 | 21760 | keep | 0 | Apr | 2022 | 0.014821 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
SAN JUAN | 2022-04-09 05:50 | 2022-04-09 06:05 | 1 | 000:15 | T | NO SE REPORTO CAUSA | PERSONAL REALIZANDO OPERACIONES LE HABIA PROBADO MALO - SE CERRO POR CONTROL (LUEGO DE CORROBORAR PERSONAL FUERA) | R22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-04-09 | 15 | keep | 0 | Apr | 2022 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-09 06:14 | 2022-04-09 06:16 | 1681 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-04 | S22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-09 | 3362 | keep | 0 | Apr | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | TMED_Event | 1681
SAN JUAN | 2022-04-09 06:14 | 2022-04-09 06:16 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-04 | S22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-09 | 3196 | keep | 0 | Apr | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | TMED_Event | 1598
CANOVANAS | 2022-04-09 06:14 | 2022-04-09 10:09 | 130 | 003:55 | P | NO SE REPORTO CAUSA | 1X65 & 1X50 EN C/L | R22040900078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2022-04-09 | 30550 | keep | 0 | Apr | 2022 | 0.020807 | 8.8542e-05 | Sustained | FALSE | FALSE | TMED_Event | 130
BARRANQUITAS | 2022-04-09 06:15 | 2022-04-09 09:51 | 10 | 003:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22040900149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2022-04-09 | 2160 | keep | 0 | Apr | 2022 | 0.0014712 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
ARECIBO | 2022-04-09 06:20 | 2022-04-09 11:44 | 100 | 005:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA REPARO LINEA PARTIDA | A22040900073 | New_Event | Wire Down | Include | Include | Equipment | 324 | 2022-04-09 | 32400 | keep | 0 | Apr | 2022 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
CAGUAS | 2022-04-09 06:21 | 2022-04-09 11:40 | 30 | 005:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR NO CAUSA | C22040900150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2022-04-09 | 9570 | keep | 0 | Apr | 2022 | 0.0065181 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
AGUADILLA | 2022-04-09 06:55 | 2022-04-09 11:09 | 1337 | 004:14 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE PATRULLO EL ALIMENTADOR Y SE VERIFICO EL INTERRUPTOR Y NO SE ENCONTRO CAUSA PARA EL DISPARO DEL INTERRUPTOR SE CERRO EL INTERRUPTOR EN LA SUBESTACION ESTE NO CIERRA POR SCADA | M22040900069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 254 | 2022-04-09 | 339598 | keep | 0 | Apr | 2022 | 0.2313 | 0.00091062 | Sustained | FALSE | FALSE | TMED_Event | 1337
BAYAMON | 2022-04-09 06:57 | 2022-04-09 13:42 | 80 | 006:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA Y SE CERRO PUENTE ABIERTO | S22040900165 | New_Event | Wire Down | Include | Include | Equipment | 405 | 2022-04-09 | 32400 | keep | 0 | Apr | 2022 | 0.022067 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
BAYAMON | 2022-04-09 07:05 | 2022-04-09 14:30 | 30 | 007:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA | B22040800634 | New_Event | Cutout Failure | Include | Include | Equipment | 445 | 2022-04-09 | 13350 | keep | 0 | Apr | 2022 | 0.0090926 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
BAYAMON | 2022-04-09 07:08 | 2022-04-09 14:31 | 30 | 007:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22040900188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 443 | 2022-04-09 | 13290 | keep | 0 | Apr | 2022 | 0.0090518 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
SAN JUAN | 2022-04-09 07:20 | 2022-04-09 11:08 | 75 | 003:48 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22040900185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2022-04-09 | 17100 | keep | 0 | Apr | 2022 | 0.011647 | 5.1082e-05 | Sustained | FALSE | FALSE | TMED_Event | 75
CAGUAS | 2022-04-09 07:31 | 2022-04-09 07:32 | 4369 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22040900178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 4369 | keep | 0 | Apr | 2022 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | TMED_Event | 4369
PONCE | 2022-04-09 07:34 | 2022-04-09 13:22 | 752 | 005:48 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR POR AVERIA SOTERRADA DE MH-62 A MH-29A SE SECCIONALIZO AVERIA LA CARGA ESTA TRANSFERIDA AL 5018-04 | P22040900132 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 348 | 2022-04-09 | 261696 | keep | 0 | Apr | 2022 | 0.17824 | 0.00051218 | Sustained | FALSE | FALSE | TMED_Event | 752
PONCE | 2022-04-09 07:34 | 2022-04-09 13:22 | 2696 | 005:48 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR POR AVERIA SOTERRADA DE MH-62 A MH-29A SE SECCIONALIZO AVERIA LLEVA LA CARGA DEL 5011-04 | P22040900132 | New_Event | UG Cable Fault | Include | Include | Equipment | 348 | 2022-04-09 | 938208 | keep | 0 | Apr | 2022 | 0.63901 | 0.0018362 | Sustained | FALSE | FALSE | TMED_Event | 2696
BARRANQUITAS | 2022-04-09 08:12 | 2022-04-09 11:05 | 10 | 002:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22040900190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2022-04-09 | 1730 | keep | 0 | Apr | 2022 | 0.0011783 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2022-04-09 08:13 | 2022-04-10 01:14 | 30 | 017:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | B22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1021 | 2022-04-09 | 30630 | keep | 0 | Apr | 2022 | 0.020862 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
CAGUAS | 2022-04-09 08:13 | 2022-04-09 14:16 | 70 | 006:03 | P | DESGANCHE | 1 X 50 1 X 40 EN C/L SE RETIRO RAMA | C22040900192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2022-04-09 | 25410 | keep | 0 | Apr | 2022 | 0.017307 | 4.7677e-05 | Sustained | FALSE | FALSE | TMED_Event | 70
CAGUAS | 2022-04-09 08:17 | 2022-04-09 08:18 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22040900193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | TMED_Event | 1702
CAGUAS | 2022-04-09 08:18 | 2022-04-09 15:19 | 3 | 007:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22040900199 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 421 | 2022-04-09 | 1263 | keep | 0 | Apr | 2022 | 0.00086022 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
CANOVANAS | 2022-04-09 08:21 | 2022-04-09 12:47 | 80 | 004:26 | P | DESGANCHE | 1X65 EN C/L | R22040900091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2022-04-09 | 21280 | keep | 0 | Apr | 2022 | 0.014494 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
MAYAGÃœEZ | 2022-04-09 08:24 | 2022-04-09 16:04 | 16 | 007:40 | P | PARARRAYOS DEFECTUOSO | 2 X 15 EN TRANSFORMADOR SE REMPLAZO PARARRAYOS DEFECTUOSO | M22040900096 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 460 | 2022-04-09 | 7360 | keep | 0 | Apr | 2022 | 0.0050129 | 1.0898e-05 | Sustained | FALSE | FALSE | TMED_Event | 16
CAGUAS | 2022-04-09 08:28 | 2022-04-09 10:12 | 12 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR AVE | C22040900201 | New_Event |  |  | Include | Wildlife | 104 | 2022-04-09 | 1248 | keep | 0 | Apr | 2022 | 0.00085001 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
YAUCO | 2022-04-09 08:30 | 2022-04-09 13:37 | 30 | 005:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22040900154 | New_Event |  |  | Include | Wildlife | 307 | 2022-04-09 | 9210 | keep | 0 | Apr | 2022 | 0.0062729 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
BAYAMON | 2022-04-09 08:37 | 2022-04-09 15:15 | 15 | 006:38 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22040900259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 398 | 2022-04-09 | 5970 | keep | 0 | Apr | 2022 | 0.0040661 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
BAYAMON | 2022-04-09 08:46 | 2022-04-09 08:47 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 73 | keep | 0 | Apr | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | TMED_Event | 73
BAYAMON | 2022-04-09 08:50 | 2022-04-09 18:15 | 80 | 009:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 565 | 2022-04-09 | 45200 | keep | 0 | Apr | 2022 | 0.030786 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
BAYAMON | 2022-04-09 08:58 | 2022-04-10 12:23 | 50 | 027:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 30 EN RISER SE REPARO TERMINACION | B22040900277 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1645 | 2022-04-09 | 82250 | keep | 0 | Apr | 2022 | 0.05602 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
HUMACAO | 2022-04-09 08:58 | 2022-04-09 18:25 | 20 | 009:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5KVA POR UNO DE IGUAL 37.5KVA | C22040900212 | New_Event | Service Transformer Failure | Include | Include | Equipment | 567 | 2022-04-09 | 11340 | keep | 0 | Apr | 2022 | 0.0077236 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
SAN JUAN | 2022-04-09 09:02 | 2022-04-09 14:52 | 40 | 005:50 | P | DESGANCHE | 1X80 EN C/L | R22040900101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2022-04-09 | 14000 | keep | 0 | Apr | 2022 | 0.0095353 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
MAYAGÃœEZ | 2022-04-09 09:12 | 2022-04-10 16:52 | 5 | 031:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REMPLAZO LINEAS SECUNDARIAS AVERIADAS | M22040900111 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1900 | 2022-04-09 | 9500 | keep | 0 | Apr | 2022 | 0.0064704 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2022-04-09 09:21 | 2022-04-10 13:30 | 12 | 028:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22040900287 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1689 | 2022-04-09 | 20268 | keep | 0 | Apr | 2022 | 0.013804 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
MAYAGÃœEZ | 2022-04-09 09:21 | 2022-04-10 01:07 | 40 | 015:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040900114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 946 | 2022-04-09 | 37840 | keep | 0 | Apr | 2022 | 0.025773 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
HUMACAO | 2022-04-09 09:23 | 2022-04-09 11:14 | 45 | 001:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C22040900223 | New_Event |  |  | Include | Wildlife | 111 | 2022-04-09 | 4995 | keep | 0 | Apr | 2022 | 0.0034021 | 3.0649e-05 | Sustained | FALSE | FALSE | TMED_Event | 45
YAUCO | 2022-04-09 09:23 | 2022-04-09 14:43 | 5 | 005:20 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | P22040900178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2022-04-09 | 1600 | keep | 0 | Apr | 2022 | 0.0010898 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
HUMACAO | 2022-04-09 09:26 | 2022-04-09 09:27 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22040900225 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-09 | 2450 | keep | 0 | Apr | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | TMED_Event | 2450
MAYAGÃœEZ | 2022-04-09 09:26 | 2022-04-09 11:40 | 35 | 002:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040900117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-04-09 | 4690 | keep | 0 | Apr | 2022 | 0.0031943 | 2.3838e-05 | Sustained | FALSE | FALSE | TMED_Event | 35
HUMACAO | 2022-04-09 09:27 | 2022-04-09 12:41 | 50 | 003:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22040900234 | 1st_after_momentary |  |  | Include | Wildlife | 194 | 2022-04-09 | 9700 | keep | 0 | Apr | 2022 | 0.0066066 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
CANOVANAS | 2022-04-09 09:32 | 2022-04-09 10:33 | 1 | 001:01 | P | OTRAS CAUSAS | PROA - SE LE ENTREGO AL CLIENTE PARA QUE REPARE | R22040900105 | New_Event | Other Causes | Include | Include | Other | 61 | 2022-04-09 | 61 | keep | 0 | Apr | 2022 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-09 09:34 | 2022-04-10 13:20 | 25 | 027:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22040900300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1666 | 2022-04-09 | 41650 | keep | 0 | Apr | 2022 | 0.028368 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
YAUCO | 2022-04-09 09:35 | 2022-04-09 11:28 | 15 | 001:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | P22040900182 | New_Event | Secondary Wire Down | Include | Include | Equipment | 113 | 2022-04-09 | 1695 | keep | 0 | Apr | 2022 | 0.0011545 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
CAGUAS | 2022-04-09 09:36 | 2022-04-09 12:03 | 4369 | 002:27 | T | CABLE SOTERRADO AVERIADO | SE ABRIO MACHETES EN AVE. DEGETAU FTE. LOMITA DE CHARLIE | C22040900232 | New_Event | UG Cable Fault | Include | Include | Equipment | 147 | 2022-04-09 | 642243 | keep | 0 | Apr | 2022 | 0.43743 | 0.0029757 | Sustained | FALSE | FALSE | TMED_Event | 4369
HUMACAO | 2022-04-09 09:37 | 2022-04-09 13:05 | 110 | 003:28 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | C22040900231 | New_Event | Bad Weather | Include | Include | Weather | 208 | 2022-04-09 | 22880 | keep | 0 | Apr | 2022 | 0.015583 | 7.492e-05 | Sustained | FALSE | FALSE | TMED_Event | 110
UTUADO | 2022-04-09 09:38 | 2022-04-09 11:02 | 25 | 001:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22040900115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-04-09 | 2100 | keep | 0 | Apr | 2022 | 0.0014303 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
MAYAGÃœEZ | 2022-04-09 09:40 | 2022-04-10 12:46 | 40 | 027:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | M22040900125 | New_Event | Cutout Failure | Include | Include | Equipment | 1626 | 2022-04-09 | 65040 | keep | 0 | Apr | 2022 | 0.044298 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
PONCE | 2022-04-09 09:44 | 2022-04-09 14:13 | 30 | 004:29 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REEMPLAZAR POSTE PRIMARIO PARTIDO | P22040900185 | New_Event | Defective Pole | Include | Include | Equipment | 269 | 2022-04-09 | 8070 | keep | 0 | Apr | 2022 | 0.0054964 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
HUMACAO | 2022-04-09 09:46 | 2022-04-09 14:15 | 4 | 004:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22040900244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2022-04-09 | 1076 | keep | 0 | Apr | 2022 | 0.00073286 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
ARECIBO | 2022-04-09 09:54 | 2022-04-09 13:42 | 80 | 003:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | A22040900134 | New_Event | Cutout Failure | Include | Include | Equipment | 228 | 2022-04-09 | 18240 | keep | 0 | Apr | 2022 | 0.012423 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
UTUADO | 2022-04-09 10:07 | 2022-04-09 12:37 | 20 | 002:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22040900141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-04-09 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
MAYAGÃœEZ | 2022-04-09 10:10 | 2022-04-09 10:35 | 12 | 000:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22040900140 | New_Event | Bad Weather | Include | Include | Weather | 25 | 2022-04-09 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
BAYAMON | 2022-04-09 10:28 | 2022-04-09 10:30 | 293 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S22040900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-09 | 586 | keep | 0 | Apr | 2022 | 0.00039912 | 0.00019956 | Momentary | FALSE | FALSE | TMED_Event | 293
BAYAMON | 2022-04-09 10:28 | 2022-04-09 10:30 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S22040900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-09 | 630 | keep | 0 | Apr | 2022 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | TMED_Event | 315
BAYAMON | 2022-04-09 10:28 | 2022-04-09 10:30 | 216 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S22040900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-09 | 432 | keep | 0 | Apr | 2022 | 0.00029423 | 0.00014712 | Momentary | FALSE | FALSE | TMED_Event | 216
BAYAMON | 2022-04-09 10:28 | 2022-04-09 10:30 | 1310 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S22040900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-09 | 2620 | keep | 0 | Apr | 2022 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | TMED_Event | 1310
CAGUAS | 2022-04-09 10:31 | 2022-04-09 10:32 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 2178 | keep | 0 | Apr | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | TMED_Event | 2178
CANOVANAS | 2022-04-09 10:33 | 2022-04-10 17:10 | 1 | 030:37 | P | CABLE SOTERRADO AVERIADO | SE REPARARON/REMPLAZARON TERMINACIONES SOTERRADAS EN EL SU-1 MEDIANTE G.O.I. SJ-220410-51 | R22040900105 | New_Event | UG Cable Fault | Include | Include | Equipment | 1837 | 2022-04-09 | 1837 | keep | 0 | Apr | 2022 | 0.0012512 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
MAYAGÃœEZ | 2022-04-09 10:34 | 2022-04-09 17:26 | 40 | 006:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M22040900145 | New_Event |  |  | Include | Wildlife | 412 | 2022-04-09 | 16480 | keep | 0 | Apr | 2022 | 0.011224 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
MAYAGÃœEZ | 2022-04-09 10:34 | 2022-04-10 11:00 | 150 | 024:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22040900145 | New_Event | Bad Weather | Include | Include | Weather | 1466 | 2022-04-09 | 219900 | keep | 0 | Apr | 2022 | 0.14977 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
ARECIBO | 2022-04-09 10:34 | 2022-04-09 17:05 | 3 | 006:31 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A22040900156 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 391 | 2022-04-09 | 1173 | keep | 0 | Apr | 2022 | 0.00079892 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
MAYAGÃœEZ | 2022-04-09 10:38 | 2022-04-09 10:47 | 4664 | 000:09 | T | CABLE SOTERRADO AVERIADO | SE ABRIO EL INTERRUPTOR 6012-02 PARA PODER CERRAR EL AMARRE DEL 6012-01 CON EL 6012-02 POR AVERIA EN EL RISER DE SALIDA DEL 6012-01 | M22040900147 | New_Event | UG Cable Fault | Include | Include | Equipment | 9 | 2022-04-09 | 41976 | keep | 0 | Apr | 2022 | 0.02859 | 0.0031766 | Sustained | FALSE | FALSE | TMED_Event | 4664
GUAYAMA | 2022-04-09 10:46 | 2022-04-09 13:00 | 50 | 002:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22040900212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-04-09 | 6700 | keep | 0 | Apr | 2022 | 0.0045633 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2022-04-09 10:56 | 2022-04-09 12:30 | 15 | 001:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER @ T-1 | B22040900377 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2022-04-09 | 1410 | keep | 0 | Apr | 2022 | 0.00096034 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
ARECIBO | 2022-04-09 10:56 | 2022-04-09 14:00 | 100 | 003:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS ABIERTOS | A22040900112 | New_Event | Wire Down | Include | Include | Equipment | 184 | 2022-04-09 | 18400 | keep | 0 | Apr | 2022 | 0.012532 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
GUAYAMA | 2022-04-09 11:05 | 2022-04-09 12:39 | 89 | 001:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR AVE CRUZO FASE | P22040900222 | New_Event |  |  | Include | Wildlife | 94 | 2022-04-09 | 8366 | keep | 0 | Apr | 2022 | 0.005698 | 6.0617e-05 | Sustained | FALSE | FALSE | TMED_Event | 89
HUMACAO | 2022-04-09 11:06 | 2022-04-09 13:40 | 11 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22040900286 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-04-09 | 1694 | keep | 0 | Apr | 2022 | 0.0011538 | 7.492e-06 | Sustained | FALSE | FALSE | TMED_Event | 11
MAYAGÃœEZ | 2022-04-09 11:13 | 2022-04-09 19:00 | 30 | 007:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22040900163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 467 | 2022-04-09 | 14010 | keep | 0 | Apr | 2022 | 0.0095421 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
MAYAGÃœEZ | 2022-04-09 11:29 | 2022-04-10 11:02 | 40 | 023:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M22040900173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1413 | 2022-04-09 | 56520 | keep | 0 | Apr | 2022 | 0.038496 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
UTUADO | 2022-04-09 11:29 | 2022-04-09 14:38 | 15 | 003:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22040900172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2022-04-09 | 2835 | keep | 0 | Apr | 2022 | 0.0019309 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
BAYAMON | 2022-04-09 11:30 | 2022-04-10 17:30 | 40 | 030:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S22040900363 | New_Event | Cutout Failure | Include | Include | Equipment | 1800 | 2022-04-09 | 72000 | keep | 0 | Apr | 2022 | 0.049039 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
AGUADILLA | 2022-04-09 11:30 | 2022-04-09 12:20 | 3 | 000:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22040900188 | New_Event |  |  | Include | Wildlife | 50 | 2022-04-09 | 150 | keep | 0 | Apr | 2022 | 0.00010216 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
ARECIBO | 2022-04-09 11:31 | 2022-04-09 12:34 | 25 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22040900173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-04-09 | 1575 | keep | 0 | Apr | 2022 | 0.0010727 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
CAGUAS | 2022-04-09 11:50 | 2022-04-09 14:19 | 1274 | 002:29 | P | CABLE SOTERRADO AVERIADO | PERSONAL LOCALIZANDO AVERIA | C22040900000 | New_Event | UG Cable Fault | Include | Include | Equipment | 149 | 2022-04-09 | 189826 | keep | 0 | Apr | 2022 | 0.12929 | 0.00086772 | Sustained | FALSE | FALSE | TMED_Event | 1274
ARECIBO | 2022-04-09 11:55 | 2022-04-10 00:23 | 12 | 012:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A22040900397 | New_Event | Cutout Failure | Include | Include | Equipment | 748 | 2022-04-09 | 8976 | keep | 0 | Apr | 2022 | 0.0061135 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CAGUAS | 2022-04-09 12:03 | 2022-04-09 12:33 | 2000 | 000:30 | P | CABLE SOTERRADO AVERIADO | PERSONAL LOCALIZANDO AVERIA | C22040900232 | New_Event | UG Cable Fault | Include | Include | Equipment | 30 | 2022-04-09 | 60000 | keep | 0 | Apr | 2022 | 0.040866 | 0.0013622 | Sustained | FALSE | FALSE | TMED_Event | 2000
SAN JUAN | 2022-04-09 12:09 | 2022-04-09 14:58 | 40 | 002:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | S22040900384 | New_Event | Cutout Failure | Include | Include | Equipment | 169 | 2022-04-09 | 6760 | keep | 0 | Apr | 2022 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
ARECIBO | 2022-04-09 12:13 | 2022-04-09 14:49 | 2 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22040900188 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2022-04-09 | 312 | keep | 0 | Apr | 2022 | 0.0002125 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-04-09 12:25 | 2022-04-09 17:00 | 12 | 004:35 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22040900447 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 275 | 2022-04-09 | 3300 | keep | 0 | Apr | 2022 | 0.0022476 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
SAN JUAN | 2022-04-09 12:29 | 2022-04-09 16:59 | 25 | 004:30 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22040900396 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-04-09 | 6750 | keep | 0 | Apr | 2022 | 0.0045974 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
CAGUAS | 2022-04-09 12:33 | 2022-04-09 12:34 | 4369 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO PERSONAL SECCIONALIZANDO TRAMO PROBANDO MALO DEL SU-D @ SU-E | C22040900232 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-04-09 | 4369 | keep | 0 | Apr | 2022 | 0.0029757 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2022-04-09 12:34 | 2022-04-09 12:47 | 2000 | 000:13 | P | CABLE SOTERRADO AVERIADO | PERSONAL LOCALIZANDO AVERIA | C22040900232 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 13 | 2022-04-09 | 26000 | keep | 0 | Apr | 2022 | 0.017708 | 0.0013622 | Sustained | FALSE | FALSE | TMED_Event | 2000
HUMACAO | 2022-04-09 12:41 | 2022-04-09 14:40 | 6 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22040900339 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2022-04-09 | 714 | keep | 0 | Apr | 2022 | 0.0004863 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
CAGUAS | 2022-04-09 12:47 | 2022-04-10 10:41 | 993 | 021:54 | P | CABLE SOTERRADO AVERIADO | SECCIONALIZARON TRAMO PROBANDO MALO DEL SU-D @ SU-E Y TRANSFIRIO PARTE DE LA CARGA DEL 3010-01 AL 3604-06 | C22040900232 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1314 | 2022-04-09 | 1304802 | keep | 0 | Apr | 2022 | 0.88869 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CANOVANAS | 2022-04-09 12:56 | 2022-04-10 13:13 | 17 | 024:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO EL T-54 MEDIANTE G.O.I. SJ-220410-50 | R22040900144 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1457 | 2022-04-09 | 24769 | keep | 0 | Apr | 2022 | 0.01687 | 1.1579e-05 | Sustained | FALSE | FALSE | TMED_Event | 17
ARECIBO | 2022-04-09 13:03 | 2022-04-09 13:12 | 1 | 000:09 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36700 | A22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-04-09 | 9 | keep | 0 | Apr | 2022 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2022-04-09 13:03 | 2022-04-09 13:12 | 2266 | 000:09 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36700 | A22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-04-09 | 20394 | keep | 0 | Apr | 2022 | 0.01389 | 0.0015434 | Sustained | FALSE | FALSE | TMED_Event | 2266
ARECIBO | 2022-04-09 13:03 | 2022-04-09 13:12 | 1399 | 000:09 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36700 | A22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-04-09 | 12591 | keep | 0 | Apr | 2022 | 0.0085757 | 0.00095285 | Sustained | FALSE | FALSE | TMED_Event | 1399
FAJARDO | 2022-04-09 13:04 | 2022-04-09 13:08 | 1394 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16500 | R22040900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-09 | 5576 | keep | 0 | Apr | 2022 | 0.0037978 | 0.00094945 | Momentary | FALSE | FALSE | TMED_Event | 1394
FAJARDO | 2022-04-09 13:04 | 2022-04-09 13:08 | 412 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16500 | R22040900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-09 | 1648 | keep | 0 | Apr | 2022 | 0.0011224 | 0.00028061 | Momentary | FALSE | FALSE | TMED_Event | 412
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 15:44 | 1617 | 002:40 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 160 | 2022-04-09 | 258720 | keep | 0 | Apr | 2022 | 0.17621 | 0.0011013 | Sustained | FALSE | FALSE | TMED_Event | 1617
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 15:44 | 1017 | 002:40 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 160 | 2022-04-09 | 162720 | keep | 0 | Apr | 2022 | 0.11083 | 0.00069267 | Sustained | FALSE | FALSE | TMED_Event | 1017
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 15:44 | 828 | 002:40 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 160 | 2022-04-09 | 132480 | keep | 0 | Apr | 2022 | 0.090232 | 0.00056395 | Sustained | FALSE | FALSE | TMED_Event | 828
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 15:44 | 3087 | 002:40 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 160 | 2022-04-09 | 493920 | keep | 0 | Apr | 2022 | 0.33641 | 0.0021025 | Sustained | FALSE | FALSE | TMED_Event | 3087
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 15:44 | 770 | 002:40 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 160 | 2022-04-09 | 123200 | keep | 0 | Apr | 2022 | 0.083911 | 0.00052444 | Sustained | FALSE | FALSE | TMED_Event | 770
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 15:44 | 1192 | 002:40 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 160 | 2022-04-09 | 190720 | keep | 0 | Apr | 2022 | 0.1299 | 0.00081187 | Sustained | FALSE | FALSE | TMED_Event | 1192
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 15:44 | 1772 | 002:40 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 160 | 2022-04-09 | 283520 | keep | 0 | Apr | 2022 | 0.1931 | 0.0012069 | Sustained | FALSE | FALSE | TMED_Event | 1772
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 15:44 | 2174 | 002:40 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 160 | 2022-04-09 | 347840 | keep | 0 | Apr | 2022 | 0.23691 | 0.0014807 | Sustained | FALSE | FALSE | TMED_Event | 2174
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 21:52 | 64 | 008:48 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 528 | 2022-04-09 | 33792 | keep | 0 | Apr | 2022 | 0.023016 | 4.359e-05 | Sustained | FALSE | FALSE | TMED_Event | 64
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 15:44 | 2658 | 002:40 | T | LINEA DE TRANSMISION 115KV | DSIPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 160 | 2022-04-09 | 425280 | keep | 0 | Apr | 2022 | 0.28966 | 0.0018104 | Sustained | FALSE | FALSE | TMED_Event | 2658
MAYAGÃœEZ | 2022-04-09 13:04 | 2022-04-09 22:18 | 6285 | 009:14 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36700 | M22040900000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 554 | 2022-04-09 | 3481890 | keep | 0 | Apr | 2022 | 2.3715 | 0.0042807 | Sustained | FALSE | FALSE | TMED_Event | 6285
BAYAMON | 2022-04-09 13:11 | 2022-04-10 11:50 | 60 | 022:39 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22040900490 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1359 | 2022-04-09 | 81540 | keep | 0 | Apr | 2022 | 0.055537 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
SAN JUAN | 2022-04-09 13:15 | 2022-04-09 16:42 | 80 | 003:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X100 EN SU-8A & SE RETIRO IGUANA | R22040900154 | New_Event |  |  | Include | Wildlife | 207 | 2022-04-09 | 16560 | keep | 0 | Apr | 2022 | 0.011279 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
PONCE | 2022-04-09 13:22 | 2022-04-11 20:52 | 28 | 055:30 | P | CABLE SOTERRADO AVERIADO | ALAMBRAR CABLE SOTERRADO DESDE MH-29A A MH-62 SE HICIERON REPARACIONES EN MH 28 AVERIA DEL DIA 9 | P22041000210 | New_Event | UG Cable Fault | Include | Include | Equipment | 3330 | 2022-04-09 | 93240 | keep | 0 | Apr | 2022 | 0.063505 | 1.9071e-05 | Sustained | FALSE | FALSE | TMED_Event | 28
ARECIBO | 2022-04-09 13:25 | 2022-04-09 15:07 | 9 | 001:42 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO EL AMARRE CON EL 8001-02 PARA REMPLAZAR LOS MACHETES DE AMARRE | A22040900211 | New_Event | Switch Failure | Include | Include | Equipment | 102 | 2022-04-09 | 918 | keep | 0 | Apr | 2022 | 0.00062525 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
SAN JUAN | 2022-04-09 13:30 | 2022-04-09 13:31 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 SE CERRO POR SCADA LLEVANDO 1303-04 | S22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 225 | keep | 0 | Apr | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | TMED_Event | 225
SAN JUAN | 2022-04-09 13:30 | 2022-04-09 13:31 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 870 | keep | 0 | Apr | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | TMED_Event | 870
MAYAGÃœEZ | 2022-04-09 13:49 | 2022-04-10 17:30 | 40 | 027:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22040900279 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1661 | 2022-04-09 | 66440 | keep | 0 | Apr | 2022 | 0.045252 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
CAGUAS | 2022-04-09 13:51 | 2022-04-09 18:00 | 128 | 004:09 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C22040900370 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-04-09 | 31872 | keep | 0 | Apr | 2022 | 0.021708 | 8.718e-05 | Sustained | FALSE | FALSE | TMED_Event | 128
UTUADO | 2022-04-09 13:53 | 2022-04-09 18:30 | 30 | 004:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22041000110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2022-04-09 | 8310 | keep | 0 | Apr | 2022 | 0.0056599 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
UTUADO | 2022-04-09 13:58 | 2022-04-09 18:43 | 50 | 004:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22040900223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2022-04-09 | 14250 | keep | 0 | Apr | 2022 | 0.0097056 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
ARECIBO | 2022-04-09 14:00 | 2022-04-10 02:00 | 60 | 012:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040900090 | New_Event | Bad Weather | Include | Include | Weather | 720 | 2022-04-09 | 43200 | keep | 0 | Apr | 2022 | 0.029423 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
PONCE | 2022-04-09 14:06 | 2022-04-09 17:29 | 2 | 003:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 6 EN TRANSFORMADOR AVE CRUZO FASE | P22040900305 | New_Event |  |  | Include | Wildlife | 203 | 2022-04-09 | 406 | keep | 0 | Apr | 2022 | 0.00027652 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-04-09 14:11 | 2022-04-09 20:51 | 10 | 006:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA XMR | B22040900519 | New_Event | Wire Down | Include | Include | Equipment | 400 | 2022-04-09 | 4000 | keep | 0 | Apr | 2022 | 0.0027244 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
HUMACAO | 2022-04-09 14:13 | 2022-04-09 20:02 | 25 | 005:49 | P | ESTRUCTURA AVERIADA | 1 X 25 EN C.L 1 X 10 EN XMR SE ABRIO PUENTES HACIA POSTE CON XMR EN EL SUELO | C22040900378 | New_Event | Defective Pole | Include | Include | Equipment | 349 | 2022-04-09 | 8725 | keep | 0 | Apr | 2022 | 0.0059426 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
CAGUAS | 2022-04-09 14:19 | 2022-04-10 09:28 | 1342 | 019:09 | T | OTRAS CAUSAS | DISPARO SE TRANSFIRIO 20% AL 3006-01 | C22040900000 | New_Event | Other Causes | Include | Include | Other | 1149 | 2022-04-09 | 1541958 | keep | 0 | Apr | 2022 | 1.0502 | 0.00091403 | Sustained | FALSE | FALSE | TMED_Event | 1342
PONCE | 2022-04-09 14:19 | 2022-04-11 11:23 | 1 | 045:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN MONTURA TRIFASICA CRUCE POR AVE | P22040900309 | New_Event |  |  | Include | Wildlife | 2704 | 2022-04-09 | 2704 | keep | 0 | Apr | 2022 | 0.0018417 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
PONCE | 2022-04-09 14:20 | 2022-04-10 10:00 | 50 | 019:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR BAMBU | P22040900310 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1180 | 2022-04-09 | 59000 | keep | 0 | Apr | 2022 | 0.040185 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
CANOVANAS | 2022-04-09 14:57 | 2022-04-09 14:58 | 40 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X80 EN C/L (POR CRUCE DE AVE) | R22040900129 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-09 | 40 | keep | 0 | Apr | 2022 | 2.7244e-05 | 2.7244e-05 | Momentary | FALSE | FALSE | TMED_Event | 40
SAN JUAN | 2022-04-09 15:15 | 2022-04-09 20:51 | 10211 | 005:36 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR 1206-03 QUE LLEVA EL 1204-05 A PETICION DE JOSE BURGOS POR MACHETES EN FUEGO. SE DEJO FUERA HASTA QUE EL CCE DIO AUTORAZCION DE CERRARLO DEBIDO AL RELEVO DE CARGA. | S22040900000 | New_Event | Switch Failure | Include | Include | Equipment | 336 | 2022-04-09 | 3430896 | keep | 0 | Apr | 2022 | 2.3368 | 0.0069547 | Sustained | FALSE | FALSE | TMED_Event | 10211
SAN JUAN | 2022-04-09 15:15 | 2022-04-09 20:51 | 4133 | 005:36 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR 1206-03 QUE LLEVA EL 1204-05 A PETICION DE JOSE BURGOS POR MACHETES EN FUEGO. SE DEJO FUERA HASTA QUE EL CCE DIO AUTORAZCION DE CERRARLO DEBIDO AL RELEVO DE CARGA. | S22040900000 | New_Event | Switch Failure | Include | Include | Equipment | 336 | 2022-04-09 | 1388688 | keep | 0 | Apr | 2022 | 0.94583 | 0.002815 | Sustained | FALSE | FALSE | TMED_Event | 4133
CAGUAS | 2022-04-09 15:19 | 2022-04-09 15:20 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | TMED_Event | 1702
CAGUAS | 2022-04-09 15:20 | 2022-04-09 16:24 | 3 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22040900199 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-04-09 | 192 | keep | 0 | Apr | 2022 | 0.00013077 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
ARECIBO | 2022-04-09 15:23 | 2022-04-10 02:45 | 2228 | 011:22 | T | AISLADOR ROTO, PARTIDO O SAFADO | INTERRUPTOR RECERRO TRES VECES, SE PATRULLO AREA Y SE REEMPLAZO AISLADOR LA CARGA ESTA POR 8007-04 | A22040900253 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 682 | 2022-04-09 | 1519496 | keep | 0 | Apr | 2022 | 1.0349 | 0.0015175 | Sustained | FALSE | FALSE | TMED_Event | 2228
ARECIBO | 2022-04-09 15:23 | 2022-04-10 02:45 | 438 | 011:22 | T | AISLADOR ROTO, PARTIDO O SAFADO | INTERRUPTOR RECERRO TRES VECES, SE PATRULLO AREA Y SE REEMPLAZO AISLADOR LLEVA LA CARGA DE 8007-03 | A22040900253 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 682 | 2022-04-09 | 298716 | keep | 0 | Apr | 2022 | 0.20345 | 0.00029832 | Sustained | FALSE | FALSE | TMED_Event | 438
YAUCO | 2022-04-09 15:28 | 2022-04-09 16:47 | 1 | 001:19 | P | OTRAS CAUSAS | 1 X 15 EN MONTURA POR PROBLEMA INTERIOR | P22040900345 | New_Event | Other Causes | Include | Include | Other | 79 | 2022-04-09 | 79 | keep | 0 | Apr | 2022 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-04-09 15:30 | 2022-04-09 21:12 | 225 | 005:42 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 NO SE PUDO PROBAR AL MOMENTO HASTA QUE EL CCE DIO LA AUTORIZACION DEBIDO AL RELEVO DE CARGA LLEVANDO 1303-04 | S22040900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 342 | 2022-04-09 | 76950 | keep | 0 | Apr | 2022 | 0.05241 | 0.00015325 | Sustained | FALSE | FALSE | TMED_Event | 225
SAN JUAN | 2022-04-09 15:30 | 2022-04-09 21:12 | 870 | 005:42 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE PUDO PROBAR AL MOMENTO HASTA QUE EL CCE DIO LA AUTORIZACION DEBIDO AL RELEVO DE CARGA PROBO BUENO | S22040900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 342 | 2022-04-09 | 297540 | keep | 0 | Apr | 2022 | 0.20265 | 0.00059255 | Sustained | FALSE | FALSE | TMED_Event | 870
BAYAMON | 2022-04-09 15:56 | 2022-04-09 21:16 | 427 | 005:20 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE PUDO PROBAR AL MOMENTO HASTA QUE EL CCE DIO LA AUTORIZACION DEBIDO AL RELEVO DE CARGA PROBO BUENO | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 320 | 2022-04-09 | 136640 | keep | 0 | Apr | 2022 | 0.093065 | 0.00029083 | Sustained | FALSE | FALSE | TMED_Event | 427
CAGUAS | 2022-04-09 16:15 | 2022-04-09 18:38 | 46 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22040900438 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2022-04-09 | 6578 | keep | 0 | Apr | 2022 | 0.0044802 | 3.133e-05 | Sustained | FALSE | FALSE | TMED_Event | 46
CAGUAS | 2022-04-09 16:24 | 2022-04-09 16:25 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22040900000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2022-04-09 16:25 | 2022-04-10 01:12 | 3 | 008:47 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22040900199 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 527 | 2022-04-09 | 1581 | keep | 0 | Apr | 2022 | 0.0010768 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
CANOVANAS | 2022-04-09 17:01 | 2022-04-09 17:02 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 1894 | keep | 0 | Apr | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | TMED_Event | 1894
BAYAMON | 2022-04-09 17:28 | 2022-04-09 20:51 | 5809 | 003:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | B22040900000 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2022-04-09 | 1179227 | keep | 0 | Apr | 2022 | 0.80317 | 0.0039565 | Sustained | FALSE | FALSE | TMED_Event | 5809
BAYAMON | 2022-04-09 17:42 | 2022-04-09 17:43 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1909-08 | S22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 2435 | keep | 0 | Apr | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | TMED_Event | 2435
BAYAMON | 2022-04-09 17:42 | 2022-04-09 17:43 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA CARGA 1907-05 | S22040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 2956 | keep | 0 | Apr | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | TMED_Event | 2956
FAJARDO | 2022-04-09 18:22 | 2022-04-10 16:00 | 20 | 021:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X25 EN C/L & SE REMPLAZO CAJA PRIMARIA | R22040900231 | New_Event | Cutout Failure | Include | Include | Equipment | 1298 | 2022-04-09 | 25960 | keep | 0 | Apr | 2022 | 0.017681 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
CANOVANAS | 2022-04-09 18:25 | 2022-04-09 19:26 | 8 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TRAMO SECUNDARIO QUEMADO | R22040900233 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2022-04-09 | 488 | keep | 0 | Apr | 2022 | 0.00033237 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
CANOVANAS | 2022-04-09 18:31 | 2022-04-10 04:20 | 184 | 009:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | R22040900234 | New_Event |  |  | Include | Wildlife | 589 | 2022-04-09 | 108376 | keep | 0 | Apr | 2022 | 0.073814 | 0.00012532 | Sustained | FALSE | FALSE | TMED_Event | 184
MAYAGÃœEZ | 2022-04-09 19:16 | 2022-04-10 19:45 | 5 | 024:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22040900115 | New_Event | Bad Weather | Include | Include | Weather | 1469 | 2022-04-09 | 7345 | keep | 0 | Apr | 2022 | 0.0050026 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2022-04-09 19:36 | 2022-04-10 14:24 | 30 | 018:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA | B22040800634 | New_Event | Cutout Failure | Include | Include | Equipment | 1128 | 2022-04-09 | 33840 | keep | 0 | Apr | 2022 | 0.023048 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
ARECIBO | 2022-04-09 20:24 | 2022-04-10 09:25 | 474 | 013:01 | P | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE ENCONTRO CAUSA SE CERRARON LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR Y CERRAR EL INTERRUPTOR | A22040900312 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 781 | 2022-04-09 | 370194 | keep | 0 | Apr | 2022 | 0.25214 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
ARECIBO | 2022-04-09 20:26 | 2022-04-10 04:24 | 3157 | 007:58 | S | LINEA DE TRANSMISION 38KV | SE REPARO LINEA 11400 Y SE ENERGIZO SUBESTACION MEDIANTE PORTATIL #6 | A22040900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 478 | 2022-04-09 | 1509046 | keep | 0 | Apr | 2022 | 1.0278 | 0.0021502 | Sustained | FALSE | FALSE | TMED_Event | 3157
ARECIBO | 2022-04-09 20:26 | 2022-04-10 04:24 | 35 | 007:58 | S | LINEA DE TRANSMISION 38KV | SE REPARO LINEA 11400 Y SE ENERGIZO SUBESTACION MEDIANTE PORTATIL #6 | A22040900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 478 | 2022-04-09 | 16730 | keep | 0 | Apr | 2022 | 0.011395 | 2.3838e-05 | Sustained | FALSE | FALSE | TMED_Event | 35
ARECIBO | 2022-04-09 20:26 | 2022-04-10 04:24 | 2916 | 007:58 | S | LINEA DE TRANSMISION 38KV | SE REPARO LINEA 11400 Y SE ENERGIZO SUBESTACION MEDIANTE PORTATIL #6 | A22040900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 478 | 2022-04-09 | 1393848 | keep | 0 | Apr | 2022 | 0.94934 | 0.0019861 | Sustained | FALSE | FALSE | TMED_Event | 2916
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 1 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 6 | keep | 0 | Apr | 2022 | 4.0866e-06 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 81 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 486 | keep | 0 | Apr | 2022 | 0.00033101 | 5.5169e-05 | Sustained | FALSE | FALSE | TMED_Event | 81
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 959 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 5754 | keep | 0 | Apr | 2022 | 0.003919 | 0.00065317 | Sustained | FALSE | FALSE | TMED_Event | 959
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 1715 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 10290 | keep | 0 | Apr | 2022 | 0.0070085 | 0.0011681 | Sustained | FALSE | FALSE | TMED_Event | 1715
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 1498 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 8988 | keep | 0 | Apr | 2022 | 0.0061217 | 0.0010203 | Sustained | FALSE | FALSE | TMED_Event | 1498
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 1221 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 7326 | keep | 0 | Apr | 2022 | 0.0049897 | 0.00083162 | Sustained | FALSE | FALSE | TMED_Event | 1221
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 1100 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 6600 | keep | 0 | Apr | 2022 | 0.0044952 | 0.0007492 | Sustained | FALSE | FALSE | TMED_Event | 1100
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 98 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 588 | keep | 0 | Apr | 2022 | 0.00040048 | 6.6747e-05 | Sustained | FALSE | FALSE | TMED_Event | 98
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 74 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 444 | keep | 0 | Apr | 2022 | 0.00030241 | 5.0401e-05 | Sustained | FALSE | FALSE | TMED_Event | 74
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 776 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 4656 | keep | 0 | Apr | 2022 | 0.0031712 | 0.00052853 | Sustained | FALSE | FALSE | TMED_Event | 776
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 4176 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 25056 | keep | 0 | Apr | 2022 | 0.017066 | 0.0028443 | Sustained | FALSE | FALSE | TMED_Event | 4176
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 252 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 1512 | keep | 0 | Apr | 2022 | 0.0010298 | 0.00017164 | Sustained | FALSE | FALSE | TMED_Event | 252
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 2147 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 12882 | keep | 0 | Apr | 2022 | 0.0087739 | 0.0014623 | Sustained | FALSE | FALSE | TMED_Event | 2147
BAYAMON | 2022-04-09 20:51 | 2022-04-09 20:57 | 2858 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | B22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-09 | 17148 | keep | 0 | Apr | 2022 | 0.011679 | 0.0019466 | Sustained | FALSE | FALSE | TMED_Event | 2858
BAYAMON | 2022-04-09 20:57 | 2022-04-10 16:50 | 10 | 019:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA XMR | B22040900519 | Partial_restoration | Wire Down | Include | Include | Equipment | 1193 | 2022-04-09 | 11930 | keep | 0 | Apr | 2022 | 0.0081255 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
VEGA BAJA | 2022-04-09 21:02 | 2022-04-09 21:10 | 776 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 VEGA BAJA | B22040900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-04-09 | 6208 | keep | 0 | Apr | 2022 | 0.0042282 | 0.00052853 | Sustained | FALSE | FALSE | TMED_Event | 776
VEGA BAJA | 2022-04-09 21:02 | 2022-04-09 21:10 | 2216 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 VEGA BAJA | B22040900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-04-09 | 17728 | keep | 0 | Apr | 2022 | 0.012074 | 0.0015093 | Sustained | FALSE | FALSE | TMED_Event | 2216
VEGA BAJA | 2022-04-09 21:02 | 2022-04-09 21:09 | 3000 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 VEGA BAJA | B22040900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-04-09 | 21000 | keep | 0 | Apr | 2022 | 0.014303 | 0.0020433 | Sustained | FALSE | FALSE | TMED_Event | 3000
VEGA BAJA | 2022-04-09 21:02 | 2022-04-09 21:09 | 908 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 VEGA BAJA | B22040900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-04-09 | 6356 | keep | 0 | Apr | 2022 | 0.004329 | 0.00061843 | Sustained | FALSE | FALSE | TMED_Event | 908
VEGA BAJA | 2022-04-09 21:02 | 2022-04-09 21:09 | 3332 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 VEGA BAJA | B22040900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-04-09 | 23324 | keep | 0 | Apr | 2022 | 0.015886 | 0.0022694 | Sustained | FALSE | FALSE | TMED_Event | 3332
VEGA BAJA | 2022-04-09 21:02 | 2022-04-09 21:09 | 2610 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 VEGA BAJA | B22040900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-04-09 | 18270 | keep | 0 | Apr | 2022 | 0.012444 | 0.0017777 | Sustained | FALSE | FALSE | TMED_Event | 2610
VEGA BAJA | 2022-04-09 21:02 | 2022-04-09 21:09 | 3076 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 VEGA BAJA | B22040900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-04-09 | 21532 | keep | 0 | Apr | 2022 | 0.014665 | 0.002095 | Sustained | FALSE | FALSE | TMED_Event | 3076
BAYAMON | 2022-04-09 21:33 | 2022-04-09 21:34 | 169 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1116-05 | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 169 | keep | 0 | Apr | 2022 | 0.00011511 | 0.00011511 | Momentary | FALSE | FALSE | TMED_Event | 169
BAYAMON | 2022-04-09 21:33 | 2022-04-09 21:34 | 5 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 1117-08 Y 1116-04 | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 5 | keep | 0 | Apr | 2022 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2022-04-09 21:33 | 2022-04-09 21:34 | 466 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1116-05 | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-09 | 466 | keep | 0 | Apr | 2022 | 0.00031739 | 0.00031739 | Momentary | FALSE | FALSE | TMED_Event | 466
ARECIBO | 2022-04-09 22:11 | 2022-04-10 04:39 | 20 | 006:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22040900352 | New_Event | Bad Weather | Include | Include | Weather | 388 | 2022-04-09 | 7760 | keep | 0 | Apr | 2022 | 0.0052853 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
BAYAMON | 2022-04-09 22:22 | 2022-04-10 01:41 | 25 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | B22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-04-09 | 4975 | keep | 0 | Apr | 2022 | 0.0033884 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
BAYAMON | 2022-04-09 22:26 | 2022-04-10 11:30 | 60 | 013:04 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22040900887 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 784 | 2022-04-09 | 47040 | keep | 0 | Apr | 2022 | 0.032039 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
MAYAGÃœEZ | 2022-04-09 22:28 | 2022-04-10 11:15 | 25 | 012:47 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22040900489 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 767 | 2022-04-09 | 19175 | keep | 0 | Apr | 2022 | 0.01306 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
FAJARDO | 2022-04-09 22:52 | 2022-04-10 09:49 | 8 | 010:57 | P | DESGANCHE | 1X15 EN XMR & SE LIMPIO ENRREDADERA | R22040900275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 657 | 2022-04-09 | 5256 | keep | 0 | Apr | 2022 | 0.0035798 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
MAYAGÃœEZ | 2022-04-09 23:07 | 2022-04-10 01:31 | 300 | 002:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M22040900498 | New_Event | Cutout Failure | Include | Include | Equipment | 144 | 2022-04-09 | 43200 | keep | 0 | Apr | 2022 | 0.029423 | 0.00020433 | Sustained | FALSE | FALSE | TMED_Event | 300
BAYAMON | 2022-04-09 23:10 | 2022-04-09 23:26 | 150 | 000:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B22040900923 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2022-04-09 | 2400 | keep | 0 | Apr | 2022 | 0.0016346 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
VEGA BAJA | 2022-04-09 23:13 | 2022-04-10 07:02 | 1350 | 007:49 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES EN SWITCH FORM BY-220409-01 | B22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 469 | 2022-04-09 | 633150 | keep | 0 | Apr | 2022 | 0.43124 | 0.00091948 | Sustained | FALSE | FALSE | TMED_Event | 1350
BAYAMON | 2022-04-09 23:54 | 2022-04-10 01:23 | 317 | 001:29 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1711-03, SE SECCIONALIZO VS-DEFENSA CIVIL POR AVERIA SOTERRADA Y SE CERRO INTERRUPTOR 20% POR EL 1711-03 | B22041000000 | New_Event | UG Cable Fault | Include | Include | Equipment | 89 | 2022-04-09 | 28213 | keep | 0 | Apr | 2022 | 0.019216 | 0.00021591 | Sustained | FALSE | FALSE | TMED_Event | 317
BAYAMON | 2022-04-09 23:54 | 2022-04-10 01:23 | 13 | 001:29 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR, SE SECCIONALIZO VS-DEFENSA CIVIL POR AVERIA SOTERRADA Y SE CERRO INTERRUPTOR 100% EN SERVICIO LLEVA 20% 1711-01 | B22041000000 | New_Event | UG Cable Fault | Include | Include | Equipment | 89 | 2022-04-09 | 1157 | keep | 0 | Apr | 2022 | 0.00078803 | 8.8542e-06 | Sustained | FALSE | FALSE | TMED_Event | 13
CANOVANAS | 2022-04-10 00:35 | 2022-04-10 01:19 | 6 | 000:44 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22040900274 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2022-04-10 | 264 | keep | 0 | Apr | 2022 | 0.00017981 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-04-10 00:50 | 2022-04-10 11:45 | 30 | 010:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22041000110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 655 | 2022-04-10 | 19650 | keep | 0 | Apr | 2022 | 0.013384 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-10 00:50 | 2022-04-10 11:06 | 12 | 010:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A22040800411 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 616 | 2022-04-10 | 7392 | keep | 0 | Apr | 2022 | 0.0050347 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-10 01:03 | 2022-04-10 01:04 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 4176 | keep | 0 | Apr | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
PONCE | 2022-04-10 01:08 | 2022-04-10 01:09 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041000017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 3744 | keep | 0 | Apr | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2022-04-10 01:08 | 2022-04-10 01:09 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA TRANSFERIDA AL 5004-06 | P22041000017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 1746 | keep | 0 | Apr | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2022-04-10 01:54 | 2022-04-10 01:58 | 4035 | 000:04 | S | LINEA DE TRANSMISION 38KV | TRABAJOS EN LINEA 4800 | P220410000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-10 | 16140 | keep | 0 | Apr | 2022 | 0.010993 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-04-10 01:54 | 2022-04-10 01:58 | 3718 | 000:04 | S | LINEA DE TRANSMISION 38KV | TRABAJOS EN LINEA 4800 | P220410000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-10 | 14872 | keep | 0 | Apr | 2022 | 0.010129 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
ARECIBO | 2022-04-10 02:28 | 2022-04-10 02:31 | 232 | 000:03 | T | ESTRUCTURA AVERIADA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA | A22041000054 | New_Event | Defective Pole | Include | Include | Equipment | 3 | 2022-04-10 | 696 | keep | 0 | Apr | 2022 | 0.00047404 | 0.00015801 | Momentary | FALSE | FALSE | Not_TMED_Event | 232
ARECIBO | 2022-04-10 02:31 | 2022-04-10 17:10 | 12 | 014:39 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE CERRO CORTE DE LINEA | A22041000095 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 879 | 2022-04-10 | 10548 | keep | 0 | Apr | 2022 | 0.0071842 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-04-10 02:47 | 2022-04-10 03:35 | 100 | 000:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22041000005 | New_Event | Bad Weather | Include | Include | Weather | 48 | 2022-04-10 | 4800 | keep | 0 | Apr | 2022 | 0.0032693 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-04-10 03:18 | 2022-04-10 03:19 | 1284 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 1284 | keep | 0 | Apr | 2022 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
FAJARDO | 2022-04-10 04:01 | 2022-04-10 04:03 | 1394 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22041000031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-10 | 2788 | keep | 0 | Apr | 2022 | 0.0018989 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
VEGA BAJA | 2022-04-10 04:24 | 2022-04-10 04:25 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERURPTOR | B22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 2926 | keep | 0 | Apr | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
VEGA BAJA | 2022-04-10 04:24 | 2022-04-10 04:25 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERURPTOR | B22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 325 | keep | 0 | Apr | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CAGUAS | 2022-04-10 04:25 | 2022-04-10 05:49 | 70 | 001:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22041000122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-04-10 | 5880 | keep | 0 | Apr | 2022 | 0.0040048 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-04-10 05:10 | 2022-04-10 10:02 | 250 | 004:52 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | M22041000072 | New_Event | Bad Weather | Include | Include | Weather | 292 | 2022-04-10 | 73000 | keep | 0 | Apr | 2022 | 0.04972 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-04-10 05:29 | 2022-04-10 05:30 | 61 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 61 | keep | 0 | Apr | 2022 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2022-04-10 05:30 | 2022-04-10 05:33 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-10 | 516 | keep | 0 | Apr | 2022 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
PONCE | 2022-04-10 05:31 | 2022-04-10 05:35 | 1212 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1800 | P22041000097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-10 | 4848 | keep | 0 | Apr | 2022 | 0.003302 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
PONCE | 2022-04-10 05:31 | 2022-04-10 05:35 | 200 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1800 | P22041000097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-10 | 800 | keep | 0 | Apr | 2022 | 0.00054488 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-04-10 05:31 | 2022-04-10 05:35 | 423 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1800 | P22041000097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-10 | 1692 | keep | 0 | Apr | 2022 | 0.0011524 | 0.0002881 | Momentary | FALSE | FALSE | Not_TMED_Event | 423
PONCE | 2022-04-10 05:31 | 2022-04-10 05:35 | 520 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1800 | P22041000097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-10 | 2080 | keep | 0 | Apr | 2022 | 0.0014167 | 0.00035417 | Momentary | FALSE | FALSE | Not_TMED_Event | 520
PONCE | 2022-04-10 05:31 | 2022-04-10 05:35 | 948 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1800 | P22041000097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-10 | 3792 | keep | 0 | Apr | 2022 | 0.0025827 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
PONCE | 2022-04-10 05:31 | 2022-04-10 05:35 | 7 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1800 | P22041000097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-10 | 28 | keep | 0 | Apr | 2022 | 1.9071e-05 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-04-10 05:31 | 2022-04-10 05:35 | 114 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1800 | P22041000097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-10 | 456 | keep | 0 | Apr | 2022 | 0.00031058 | 7.7645e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 114
PONCE | 2022-04-10 05:31 | 2022-04-10 06:49 | 171 | 001:18 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA TRANSFERIDA AL 5016-02 | P22041000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-04-10 | 13338 | keep | 0 | Apr | 2022 | 0.0090845 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
PONCE | 2022-04-10 05:31 | 2022-04-10 06:49 | 120 | 001:18 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA TRANSFERIDA AL 5016-02 | P22041000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-04-10 | 9360 | keep | 0 | Apr | 2022 | 0.0063751 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-04-10 05:31 | 2022-04-10 06:49 | 1478 | 001:18 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 5011-01 Y 5011-02 | P22041000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-04-10 | 115284 | keep | 0 | Apr | 2022 | 0.078519 | 0.0010067 | Sustained | FALSE | FALSE | Not_TMED_Event | 1478
SAN JUAN | 2022-04-10 05:32 | 2022-04-10 05:33 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1206-02 | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-04-10 05:32 | 2022-04-10 05:33 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-01 | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
PONCE | 2022-04-10 05:38 | 2022-04-10 14:12 | 200 | 008:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REMPLAZO CAJA PRIMARIA EN C/L QUEMADA | P22041000096 | New_Event | Cutout Failure | Include | Include | Equipment | 514 | 2022-04-10 | 102800 | keep | 0 | Apr | 2022 | 0.070017 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-04-10 05:39 | 2022-04-11 10:10 | 10 | 028:31 | P | DESGANCHE | 2 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22041000173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1711 | 2022-04-10 | 17110 | keep | 0 | Apr | 2022 | 0.011654 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-10 05:44 | 2022-04-10 18:18 | 40 | 012:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22041000174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 754 | 2022-04-10 | 30160 | keep | 0 | Apr | 2022 | 0.020542 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-04-10 06:00 | 2022-04-10 12:46 | 7 | 006:46 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P22041000343 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 406 | 2022-04-10 | 2842 | keep | 0 | Apr | 2022 | 0.0019357 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-04-10 06:28 | 2022-04-10 08:14 | 90 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22041000154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-04-10 | 9540 | keep | 0 | Apr | 2022 | 0.0064977 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2022-04-10 06:28 | 2022-04-10 15:35 | 10 | 009:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 KVA @ 4160 VOLT POR UNO DE LA MIMA CAPACIDAD QUEMADO | P22041000279 | New_Event | Service Transformer Failure | Include | Include | Equipment | 547 | 2022-04-10 | 5470 | keep | 0 | Apr | 2022 | 0.0037256 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-04-10 06:32 | 2022-04-10 09:07 | 60 | 002:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22041000118 | New_Event |  |  | Include | Wildlife | 155 | 2022-04-10 | 9300 | keep | 0 | Apr | 2022 | 0.0063342 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-04-10 06:49 | 2022-04-10 09:33 | 50 | 002:44 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22041000167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-04-10 | 8200 | keep | 0 | Apr | 2022 | 0.005585 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-04-10 06:54 | 2022-04-10 18:41 | 50 | 011:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22041000193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 707 | 2022-04-10 | 35350 | keep | 0 | Apr | 2022 | 0.024077 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-10 06:56 | 2022-04-11 00:28 | 8 | 017:32 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S22041000205 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1052 | 2022-04-10 | 8416 | keep | 0 | Apr | 2022 | 0.0057321 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-10 06:56 | 2022-04-10 11:29 | 25 | 004:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22041000169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 273 | 2022-04-10 | 6825 | keep | 0 | Apr | 2022 | 0.0046485 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-10 07:00 | 2022-04-10 11:18 | 50 | 004:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | M22041000084 | New_Event | Wire Down | Include | Include | Equipment | 258 | 2022-04-10 | 12900 | keep | 0 | Apr | 2022 | 0.0087861 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-04-10 07:02 | 2022-04-10 08:13 | 650 | 001:11 | P | NO SE REPORTO CAUSA | CON SWITCH FORM BY 220406-01 SE SECCIONALIZO TRAMO QUE CORRE POR EL MONTE Y SE TRANSFIRIO CARGA. TRAMO SECCIONALIZADO PENDIENTE A PATRULLAR | B22040600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2022-04-10 | 46150 | keep | 0 | Apr | 2022 | 0.031433 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
VEGA BAJA | 2022-04-10 07:05 | 2022-04-10 22:53 | 36 | 015:48 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22041000202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 948 | 2022-04-10 | 34128 | keep | 0 | Apr | 2022 | 0.023244 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-04-10 07:17 | 2022-04-10 22:20 | 80 | 015:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L SE RETIRO CULEBRA | S22041000209 | New_Event |  |  | Include | Wildlife | 903 | 2022-04-10 | 72240 | keep | 0 | Apr | 2022 | 0.049202 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-10 07:19 | 2022-04-10 09:15 | 40 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B22041000206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-04-10 | 4640 | keep | 0 | Apr | 2022 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-04-10 07:21 | 2022-04-10 11:15 | 40 | 003:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22041000148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-04-10 | 9360 | keep | 0 | Apr | 2022 | 0.0063751 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-10 07:26 | 2022-04-10 15:15 | 80 | 007:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE ELIMINO CONDUCTOR VACANTE | B22041000211 | New_Event | Wire Down | Include | Include | Equipment | 469 | 2022-04-10 | 37520 | keep | 0 | Apr | 2022 | 0.025555 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-04-10 07:28 | 2022-04-10 15:00 | 30 | 007:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVENTO LINEA PRIMARIA | B22041000213 | New_Event | Wire Down | Include | Include | Equipment | 452 | 2022-04-10 | 13560 | keep | 0 | Apr | 2022 | 0.0092357 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-10 07:30 | 2022-04-11 01:58 | 30 | 018:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S22041000213 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1108 | 2022-04-10 | 33240 | keep | 0 | Apr | 2022 | 0.02264 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-10 07:30 | 2022-04-10 07:31 | 1483 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 30% DE LA CARGA POR EL 1336-08 | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 1483 | keep | 0 | Apr | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-04-10 07:30 | 2022-04-10 07:31 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 30% DEL 1204-04 | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 5290 | keep | 0 | Apr | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
CAGUAS | 2022-04-10 07:52 | 2022-04-10 16:45 | 1 | 008:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR DESGANCHE | C22041000189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 533 | 2022-04-10 | 533 | keep | 0 | Apr | 2022 | 0.00036302 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-04-10 07:58 | 2022-04-10 13:04 | 120 | 005:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN RISER & SE REMPLAZO CAJA PRIMARIA | R22041000052 | New_Event | Cutout Failure | Include | Include | Equipment | 306 | 2022-04-10 | 36720 | keep | 0 | Apr | 2022 | 0.02501 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-04-10 08:05 | 2022-04-10 12:39 | 1 | 004:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X30 EN C/L (POR CRUCE DE AVE) | R22041000054 | New_Event |  |  | Include | Wildlife | 274 | 2022-04-10 | 274 | keep | 0 | Apr | 2022 | 0.00018662 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-04-10 08:06 | 2022-04-10 08:07 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 1827 | keep | 0 | Apr | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2022-04-10 08:26 | 2022-04-10 09:17 | 45 | 000:51 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | S22041000234 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-04-10 | 2295 | keep | 0 | Apr | 2022 | 0.0015631 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-04-10 08:26 | 2022-04-10 13:44 | 10 | 005:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22041000109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 318 | 2022-04-10 | 3180 | keep | 0 | Apr | 2022 | 0.0021659 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-10 08:27 | 2022-04-10 18:27 | 60 | 010:00 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | SS2204100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 600 | 2022-04-10 | 36000 | keep | 0 | Apr | 2022 | 0.024519 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-04-10 08:29 | 2022-04-10 15:15 | 2 | 006:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041000110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 406 | 2022-04-10 | 812 | keep | 0 | Apr | 2022 | 0.00055305 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-04-10 08:42 | 2022-04-10 12:57 | 15 | 004:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR AVE | C22041000224 | New_Event |  |  | Include | Wildlife | 255 | 2022-04-10 | 3825 | keep | 0 | Apr | 2022 | 0.0026052 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-10 08:44 | 2022-04-10 10:25 | 150 | 001:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B22041000000 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2022-04-10 | 15150 | keep | 0 | Apr | 2022 | 0.010319 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-04-10 08:48 | 2022-04-10 08:49 | 603 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE - LLEVA LA CARGA DEL 9206-09 | B22041000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-10 | 603 | keep | 0 | Apr | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-04-10 08:48 | 2022-04-10 08:49 | 6 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE - CARGA TRANSFERIDA AL 9206-08 | B22041000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-10 | 6 | keep | 0 | Apr | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-04-10 08:49 | 2022-04-10 16:35 | 80 | 007:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | B22041000247 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 466 | 2022-04-10 | 37280 | keep | 0 | Apr | 2022 | 0.025391 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-10 08:55 | 2022-04-11 09:29 | 50 | 024:34 | P | HERRAJE ROTO O PODRIDO | SE REEMPLAZO CRUCETA Y 1 X 65 EN C/L | S22041000241 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1474 | 2022-04-10 | 73700 | keep | 0 | Apr | 2022 | 0.050197 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-04-10 08:55 | 2022-04-10 18:15 | 40 | 009:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041000116 | New_Event | Bad Weather | Include | Include | Weather | 560 | 2022-04-10 | 22400 | keep | 0 | Apr | 2022 | 0.015257 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-10 08:56 | 2022-04-11 12:49 | 100 | 027:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJAS PRIMARIAS Y 3 X 10 EN C/L | S22041000242 | New_Event | Cutout Failure | Include | Include | Equipment | 1673 | 2022-04-10 | 167300 | keep | 0 | Apr | 2022 | 0.11395 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-10 09:00 | 2022-04-10 13:56 | 70 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22041000239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2022-04-10 | 20720 | keep | 0 | Apr | 2022 | 0.014112 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-04-10 09:00 | 2022-04-10 16:00 | 3 | 007:00 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR INDICO JOURNEY LINEMAN NO IDENTIFICO CAUSA | A22041000107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 420 | 2022-04-10 | 1260 | keep | 0 | Apr | 2022 | 0.00085818 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2022-04-10 09:01 | 2022-04-10 11:30 | 140 | 002:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR AVERIADO | P22041000214 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 149 | 2022-04-10 | 20860 | keep | 0 | Apr | 2022 | 0.014208 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
GUAYAMA | 2022-04-10 09:03 | 2022-04-10 12:05 | 6 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P22041000217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2022-04-10 | 1092 | keep | 0 | Apr | 2022 | 0.00074376 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-10 09:07 | 2022-04-11 09:27 | 9 | 024:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S22041000245 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1460 | 2022-04-10 | 13140 | keep | 0 | Apr | 2022 | 0.0089496 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2022-04-10 09:16 | 2022-04-10 10:27 | 30 | 001:11 | P | DESGANCHE | 1X65 EN C/L | R22041000058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-04-10 | 2130 | keep | 0 | Apr | 2022 | 0.0014507 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-10 09:18 | 2022-04-10 12:14 | 12 | 002:56 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-1 CON DERRAME DE ACEITE | B22041000261 | New_Event | Service Transformer Failure | Include | Include | Equipment | 176 | 2022-04-10 | 2112 | keep | 0 | Apr | 2022 | 0.0014385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-04-10 09:25 | 2022-04-10 11:48 | 4 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22041000262 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2022-04-10 | 572 | keep | 0 | Apr | 2022 | 0.00038959 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-04-10 09:28 | 2022-04-10 15:45 | 940 | 006:17 | P | OTRAS CAUSAS | SE REALIZARON OPERACIONES CERRANDO RISER 35% EN SERVICIO ATRAVEZ DEL 3006-01 | C22041000000 | New_Event | Other Causes | Include | Include | Other | 377 | 2022-04-10 | 354380 | keep | 0 | Apr | 2022 | 0.24137 | 0.00064023 | Sustained | FALSE | FALSE | Not_TMED_Event | 940
BAYAMON | 2022-04-10 09:30 | 2022-04-10 15:20 | 25 | 005:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | B22041000230 | New_Event | Wire Down | Include | Include | Equipment | 350 | 2022-04-10 | 8750 | keep | 0 | Apr | 2022 | 0.0059596 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-10 09:36 | 2022-04-10 15:52 | 1 | 006:16 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X 20 NX EN TRANSCLOUSURE | S22041000257 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 376 | 2022-04-10 | 376 | keep | 0 | Apr | 2022 | 0.00025609 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-10 09:47 | 2022-04-11 21:24 | 13 | 035:37 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO AVERIADO DE T 203 A T 202 | B22041000277 | New_Event | UG Cable Fault | Include | Include | Equipment | 2137 | 2022-04-10 | 27781 | keep | 0 | Apr | 2022 | 0.018922 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2022-04-10 09:48 | 2022-04-10 10:31 | 1883 | 000:43 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETES Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | A22041000115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 43 | 2022-04-10 | 80969 | keep | 0 | Apr | 2022 | 0.055148 | 0.0012825 | Sustained | FALSE | FALSE | Not_TMED_Event | 1883
SAN JUAN | 2022-04-10 09:55 | 2022-04-10 12:38 | 80 | 002:43 | P | DESGANCHE | 1 X 85 EN C/L SE REALIZO DESGANCHE | S22041000264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-04-10 | 13040 | keep | 0 | Apr | 2022 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-10 09:55 | 2022-04-10 18:02 | 50 | 008:07 | P | NO SE REPORTO CAUSA | 3 X 125 EN SU-1 | S22041000267 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 487 | 2022-04-10 | 24350 | keep | 0 | Apr | 2022 | 0.016585 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-10 10:10 | 2022-04-10 14:13 | 8 | 004:03 | P | DESGANCHE | 1X40 EN C/L SE DESGANCHO | R22041000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2022-04-10 | 1944 | keep | 0 | Apr | 2022 | 0.001324 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-04-10 10:11 | 2022-04-10 18:15 | 30 | 008:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE NO FUSIBLE | P22041000256 | New_Event | Wire Down | Include | Include | Equipment | 484 | 2022-04-10 | 14520 | keep | 0 | Apr | 2022 | 0.0098895 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-10 10:16 | 2022-04-10 18:51 | 1 | 008:35 | P | NO SE REPORTO CAUSA | 2 X 40 EN RISER Y 1 X 150 EN SU | B22041000298 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 515 | 2022-04-10 | 515 | keep | 0 | Apr | 2022 | 0.00035076 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-10 10:18 | 2022-04-10 14:40 | 95 | 004:22 | P | DESGANCHE | 1X80 EN C/L (SE RETIRO PENCA DE PALMA) | S22041000272 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-04-10 | 24890 | keep | 0 | Apr | 2022 | 0.016952 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
SAN JUAN | 2022-04-10 10:24 | 2022-04-10 13:57 | 200 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X100 EN C/L & SE CERRO PUENTE PRIMARIO | R22041000061 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2022-04-10 | 42600 | keep | 0 | Apr | 2022 | 0.029015 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-04-10 10:31 | 2022-04-10 11:00 | 940 | 000:29 | P | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE ENCONTRO CAUSA PARA EL DISPARO DEL INTERRUPTOR SE CERRO LOS MACHETES QUE SE ABRIERON PARA SECCIONALIZAR Y CERRAR EL INTERRUPTOR EN SERVICIO TOTAL | A22041000125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-04-10 | 27260 | keep | 0 | Apr | 2022 | 0.018567 | 0.00064023 | Sustained | FALSE | FALSE | Not_TMED_Event | 940
BARRANQUITAS | 2022-04-10 10:39 | 2022-04-10 15:41 | 32 | 005:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22041000304 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 302 | 2022-04-10 | 9664 | keep | 0 | Apr | 2022 | 0.0065821 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2022-04-10 10:41 | 2022-04-10 10:45 | 4369 | 000:04 | T | CABLE SOTERRADO AVERIADO | PERSONAL REALIZANDO OPERACIONES EN LAZO SOTERRADO PROBANDO MALO DEL SU-D @ SU-E. | C22041000305 | New_Event | UG Cable Fault | Include | Include | Equipment | 4 | 2022-04-10 | 17476 | keep | 0 | Apr | 2022 | 0.011903 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2022-04-10 10:45 | 2022-04-10 12:59 | 993 | 002:14 | P | CABLE SOTERRADO AVERIADO | SECCIONALIZARON TRAMO PROBANDO MALO DEL SU-D @ SU-E Y TRANSFIRIO PARTE DE LA CARGA DEL 3010-01 AL 3604-06 | C22040900232 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 134 | 2022-04-10 | 133062 | keep | 0 | Apr | 2022 | 0.090628 | 0.00067633 | Sustained | FALSE | FALSE | Not_TMED_Event | 993
MAYAGÃœEZ | 2022-04-10 10:45 | 2022-04-10 15:05 | 100 | 004:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041000143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2022-04-10 | 26000 | keep | 0 | Apr | 2022 | 0.017708 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-04-10 10:49 | 2022-04-10 13:59 | 10 | 003:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22041000308 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2022-04-10 | 1900 | keep | 0 | Apr | 2022 | 0.0012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-10 10:51 | 2022-04-10 22:32 | 50 | 011:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22041000276 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 701 | 2022-04-10 | 35050 | keep | 0 | Apr | 2022 | 0.023872 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-10 11:15 | 2022-04-10 20:20 | 50 | 009:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 Y 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22041000150 | New_Event | Cutout Failure | Include | Include | Equipment | 545 | 2022-04-10 | 27250 | keep | 0 | Apr | 2022 | 0.01856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-04-10 11:17 | 2022-04-10 12:18 | 80 | 001:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22041000321 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2022-04-10 | 4880 | keep | 0 | Apr | 2022 | 0.0033237 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-10 11:18 | 2022-04-10 13:06 | 40 | 001:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA PUENTE ABIERTO POR DSGANCHE AFECTO MAS CLIENTES | M22040600211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-04-10 | 4320 | keep | 0 | Apr | 2022 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-10 11:24 | 2022-04-11 10:26 | 1 | 023:02 | P | TRANSFORMADOR AVERIADO | 2 X 10 EN BANCO XMR SE ELIMINO TRANSFORMADOR Y SE CONSTRUYO DELTA ABIERTA | B22041000323 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1382 | 2022-04-10 | 1382 | keep | 0 | Apr | 2022 | 0.00094127 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-10 11:25 | 2022-04-10 13:11 | 15 | 001:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR REPARO SECUNDARIA ROTA POR CLIENTE DESGANCHANDO | C22041000326 | New_Event |  |  | Include | Wildlife | 106 | 2022-04-10 | 1590 | keep | 0 | Apr | 2022 | 0.0010829 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-10 11:35 | 2022-04-11 10:40 | 15 | 023:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22041000326 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1385 | 2022-04-10 | 20775 | keep | 0 | Apr | 2022 | 0.01415 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-04-10 11:44 | 2022-04-10 14:27 | 25 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A22041000132 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2022-04-10 | 4075 | keep | 0 | Apr | 2022 | 0.0027755 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-10 11:47 | 2022-04-10 20:15 | 200 | 008:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE SAFADO Y PEGANDO A POSTE 1 X 140 EN C/L | P22041000134 | New_Event | Wire Down | Include | Include | Equipment | 508 | 2022-04-10 | 101600 | keep | 0 | Apr | 2022 | 0.069199 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-04-10 12:06 | 2022-04-10 12:07 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1909-09 | S22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 222 | keep | 0 | Apr | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-04-10 12:06 | 2022-04-10 12:07 | 4456 | 000:01 | T | TRANSFORMADOR AVERIADO | RECERRO CARGA TRANSFERIDA AL 1907-03 | S22041000000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-04-10 | 4456 | keep | 0 | Apr | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-04-10 12:07 | 2022-04-10 20:05 | 60 | 007:58 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22041000286 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 478 | 2022-04-10 | 28680 | keep | 0 | Apr | 2022 | 0.019534 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-10 12:07 | 2022-04-11 | 59 | 011:53 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO | S22041000354 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 713 | 2022-04-10 | 42067 | keep | 0 | Apr | 2022 | 0.028652 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
SAN JUAN | 2022-04-10 12:33 | 2022-04-10 19:35 | 4 | 007:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN BANCO SE RETIRO NIDO | S22041000297 | New_Event |  |  | Include | Wildlife | 422 | 2022-04-10 | 1688 | keep | 0 | Apr | 2022 | 0.0011497 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-10 12:33 | 2022-04-10 16:50 | 30 | 004:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22041000337 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 257 | 2022-04-10 | 7710 | keep | 0 | Apr | 2022 | 0.0052512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-10 12:44 | 2022-04-11 04:15 | 8 | 015:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO PORTAFUSIBLES | S22041000300 | New_Event | Cutout Failure | Include | Include | Equipment | 931 | 2022-04-10 | 7448 | keep | 0 | Apr | 2022 | 0.0050728 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-10 12:44 | 2022-04-10 18:35 | 4 | 005:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-32 | R22041000072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 351 | 2022-04-10 | 1404 | keep | 0 | Apr | 2022 | 0.00095626 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-10 12:45 | 2022-04-10 20:40 | 5 | 007:55 | P | NO SE REPORTO CAUSA | 3 X 100 EN RISER | S22041000301 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 475 | 2022-04-10 | 2375 | keep | 0 | Apr | 2022 | 0.0016176 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-04-10 12:53 | 2022-04-10 14:38 | 15 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 50 EN RISER NO SE REPORTO CAUSA | M22041000128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-04-10 | 1575 | keep | 0 | Apr | 2022 | 0.0010727 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-04-10 12:59 | 2022-04-10 15:53 | 3496 | 002:54 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO DEJANDO 4 CARGAS TRIFASICAS FUERA 99% EN SERVICIO. | C22041000232 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 174 | 2022-04-10 | 608304 | keep | 0 | Apr | 2022 | 0.41431 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-10 13:17 | 2022-04-10 16:07 | 1984 | 002:50 | T | CABLE SOTERRADO AVERIADO | DISPARO 1529-12 SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 1911-07 | S22041000307 | New_Event | UG Cable Fault | Include | Include | Equipment | 170 | 2022-04-10 | 337280 | keep | 0 | Apr | 2022 | 0.22972 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-04-10 13:17 | 2022-04-10 17:41 | 577 | 004:24 | T | CABLE SOTERRADO AVERIADO | EN DISPARO DEL 1529-12 QUE LLEVA 1911-07, SE SECCIONALIZO AVERIA DE RISER @ SU-1 CALLE PALMASOLA GARDEN HILLS Y SE CERRO MACHETES ABIERTOS SJ-220410-01 97% EN SERVICIO DEL 1529-12 Y 100% EL 1911-07 | S22041000307 | New_Event | UG Cable Fault | Include | Include | Equipment | 264 | 2022-04-10 | 152328 | keep | 0 | Apr | 2022 | 0.10375 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
MAYAGÃœEZ | 2022-04-10 13:20 | 2022-04-11 01:45 | 50 | 012:25 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041000171 | New_Event | Bad Weather | Include | Include | Weather | 745 | 2022-04-10 | 37250 | keep | 0 | Apr | 2022 | 0.025371 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-10 13:31 | 2022-04-11 03:00 | 80 | 013:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S22041000318 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 809 | 2022-04-10 | 64720 | keep | 0 | Apr | 2022 | 0.04408 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-04-10 13:41 | 2022-04-10 17:26 | 130 | 003:45 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041000174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-04-10 | 29250 | keep | 0 | Apr | 2022 | 0.019922 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2022-04-10 13:42 | 2022-04-11 00:45 | 50 | 011:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S22041000325 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 663 | 2022-04-10 | 33150 | keep | 0 | Apr | 2022 | 0.022578 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-04-10 13:52 | 2022-04-10 17:18 | 60 | 003:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A22041000144 | New_Event | Wire Down | Include | Include | Equipment | 206 | 2022-04-10 | 12360 | keep | 0 | Apr | 2022 | 0.0084183 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-10 13:55 | 2022-04-11 10:48 | 30 | 020:53 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B22041000355 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1253 | 2022-04-10 | 37590 | keep | 0 | Apr | 2022 | 0.025602 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-10 14:01 | 2022-04-11 15:02 | 15 | 025:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE LINEA A TRANSFORMADOR | S22041000336 | New_Event | Wire Down | Include | Include | Equipment | 1501 | 2022-04-10 | 22515 | keep | 0 | Apr | 2022 | 0.015335 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-04-10 14:03 | 2022-04-10 15:11 | 10 | 001:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X20 EN RISER & SE REMPLAZO PORTAFUSIBLE | R22041000076 | New_Event | Cutout Failure | Include | Include | Equipment | 68 | 2022-04-10 | 680 | keep | 0 | Apr | 2022 | 0.00046314 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-04-10 14:03 | 2022-04-10 18:25 | 50 | 004:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA, SE REMPLAZO CAJA CAUSA DE CRUCE DE GUY CON CAJA PRIMARIA | B22041000516 | New_Event |  |  | Include | Wildlife | 262 | 2022-04-10 | 13100 | keep | 0 | Apr | 2022 | 0.0089224 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-10 14:19 | 2022-04-10 14:47 | 20 | 000:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L, 1 X 8 Y 1 X 10 EN XMR SE REEMPLAZO CAJA PRIMARIA | C22041000298 | New_Event | Cutout Failure | Include | Include | Equipment | 28 | 2022-04-10 | 560 | keep | 0 | Apr | 2022 | 0.00038141 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-10 14:22 | 2022-04-10 14:23 | 2366 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22041000146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 2366 | keep | 0 | Apr | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2022-04-10 14:53 | 2022-04-11 10:09 | 8 | 019:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22041000180 | New_Event | Bad Weather | Include | Include | Weather | 1156 | 2022-04-10 | 9248 | keep | 0 | Apr | 2022 | 0.0062988 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-04-10 14:54 | 2022-04-10 16:40 | 30 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22041000148 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2022-04-10 | 3180 | keep | 0 | Apr | 2022 | 0.0021659 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-10 14:56 | 2022-04-11 03:23 | 60 | 012:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041000181 | New_Event | Bad Weather | Include | Include | Weather | 747 | 2022-04-10 | 44820 | keep | 0 | Apr | 2022 | 0.030527 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-04-10 14:57 | 2022-04-11 10:00 | 3 | 019:03 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M22041000182 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1143 | 2022-04-10 | 3429 | keep | 0 | Apr | 2022 | 0.0023355 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-04-10 15:00 | 2022-04-10 15:59 | 15 | 000:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L AVE CRUZO LINEAS | P22011000403 | New_Event |  |  | Include | Wildlife | 59 | 2022-04-10 | 885 | keep | 0 | Apr | 2022 | 0.00060277 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-10 15:12 | 2022-04-11 13:22 | 100 | 022:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22041000357 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1330 | 2022-04-10 | 133000 | keep | 0 | Apr | 2022 | 0.090586 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-04-10 15:15 | 2022-04-10 15:20 | 10 | 000:05 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | B22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-04-10 | 50 | keep | 0 | Apr | 2022 | 3.4055e-05 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-04-10 15:16 | 2022-04-10 15:24 | 1 | 000:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN C/L LINEAS ARREADAS Y SE CRUZAN | P22041000407 | New_Event | Wire Down | Include | Include | Equipment | 8 | 2022-04-10 | 8 | keep | 0 | Apr | 2022 | 5.4488e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-10 15:25 | 2022-04-10 15:26 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041000410 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 527 | keep | 0 | Apr | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2022-04-10 15:27 | 2022-04-10 15:28 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041000410 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 527 | keep | 0 | Apr | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CAGUAS | 2022-04-10 15:45 | 2022-04-10 15:48 | 873 | 000:03 | P | OTRAS CAUSAS | SE REALIZARON OPERACIONES CERRANDO RISER 50% EN SERVICIO ATRAVEZ DEL 3006-01 | C22041000000 | New_Event | Other Causes | Include | Include | Other | 3 | 2022-04-10 | 2619 | keep | 0 | Apr | 2022 | 0.0017838 | 0.0005946 | Momentary | FALSE | FALSE | Not_TMED_Event | 873
CAGUAS | 2022-04-10 15:48 | 2022-04-10 15:57 | 671 | 000:09 | P | OTRAS CAUSAS | SE REALIZARON OPERACIONES CERRANDO RISER 60% EN SERVICIO ATRAVEZ DEL 3006-01 | C22041000000 | 1st_after_momentary | Other Causes | Include | Include | Other | 9 | 2022-04-10 | 6039 | keep | 0 | Apr | 2022 | 0.0041131 | 0.00045702 | Sustained | FALSE | FALSE | Not_TMED_Event | 671
CANOVANAS | 2022-04-10 15:52 | 2022-04-10 18:30 | 200 | 002:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X100 EN C/L & SE REPARO LIGADURA PEGADA A CRUCETA | R22041000079 | New_Event | Wire Down | Include | Include | Equipment | 158 | 2022-04-10 | 31600 | keep | 0 | Apr | 2022 | 0.021523 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-04-10 15:53 | 2022-04-10 19:57 | 4 | 004:04 | P | CABLE SOTERRADO AVERIADO | 4 CARGAS TRIFASICAS FUERA DE SERVICIO. | C22041000232 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 244 | 2022-04-10 | 976 | keep | 0 | Apr | 2022 | 0.00066475 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-10 15:57 | 2022-04-10 16:01 | 536 | 000:04 | P | OTRAS CAUSAS | SE SECCIONALIZO POSIBLE AVERIA DE VS-1 HACIA CAJAS SECAS Y SE REALIZARON OPERACIONES CERRANDO MACHETES 95% EN SERVICIO | C22041000000 | Partial_restoration | Other Causes | Include | Include | Other | 4 | 2022-04-10 | 2144 | keep | 0 | Apr | 2022 | 0.0014603 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-04-10 16:00 | 2022-04-10 16:40 | 60 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B22041000000 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2022-04-10 | 2400 | keep | 0 | Apr | 2022 | 0.0016346 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-04-10 16:01 | 2022-04-11 14:55 | 67 | 022:54 | P | OTRAS CAUSAS | PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA SOTERRADA AVERIA EN CAJAS SECAS A ESCUELA LUI RAMOS GONZALEZ | C22041100000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1374 | 2022-04-10 | 92058 | keep | 0 | Apr | 2022 | 0.0627 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-04-10 16:07 | 2022-04-10 16:24 | 1786 | 000:17 | P | CABLE SOTERRADO AVERIADO | HACIENDO PRUEBAS VOLVIO A DISPARAR SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 1911-07 | S22041000307 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 17 | 2022-04-10 | 30362 | keep | 0 | Apr | 2022 | 0.020679 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-10 16:17 | 2022-04-11 15:02 | 80 | 022:45 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S22041000379 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1365 | 2022-04-10 | 109200 | keep | 0 | Apr | 2022 | 0.074376 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-10 16:19 | 2022-04-10 18:00 | 15 | 001:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | M22041000191 | New_Event | Wire Down | Include | Include | Equipment | 101 | 2022-04-10 | 1515 | keep | 0 | Apr | 2022 | 0.0010319 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-10 16:24 | 2022-04-10 16:25 | 1984 | 000:01 | T | CABLE SOTERRADO AVERIADO | HACIENDO PRUEBAS VOLVIO A DISPARAR SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 1911-07 | S22041000307 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-04-10 | 1984 | keep | 0 | Apr | 2022 | 0.0013513 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-10 16:25 | 2022-04-10 17:23 | 1786 | 000:58 | P | CABLE SOTERRADO AVERIADO | HACIENDO PRUEBAS VOLVIO A DISPARAR SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 1911-07 | S22041000307 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 58 | 2022-04-10 | 103588 | keep | 0 | Apr | 2022 | 0.070553 | 0.0012164 | Sustained | FALSE | FALSE | Not_TMED_Event | 1786
FAJARDO | 2022-04-10 16:25 | 2022-04-10 18:11 | 1 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2X20 DE RISER @ TRANSCLOSURE & SE REMPLAZO PERNO & BAJANTE DE CAJA PRIMARIA | R22041000082 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2022-04-10 | 106 | keep | 0 | Apr | 2022 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-04-10 16:40 | 2022-04-10 16:53 | 7 | 000:13 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C22041000365 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-04-10 | 91 | keep | 0 | Apr | 2022 | 6.198e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-04-10 17:10 | 2022-04-11 12:14 | 1 | 019:04 | P | ERROR HUMANO | SE CERRO DEL SU-1 AL T DE SALE CENTER, AYER EN OPERACIONES QUE SE REALIZARON SE DEJARON ABIERTOS | R22040600039 | New_Event | Human Error | Include | Include | Other | 1144 | 2022-04-10 | 1144 | keep | 0 | Apr | 2022 | 0.00077917 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-10 17:17 | 2022-04-10 22:30 | 70 | 005:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22041000388 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2022-04-10 | 21910 | keep | 0 | Apr | 2022 | 0.014923 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-04-10 17:22 | 2022-04-10 18:31 | 1 | 001:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22041000398 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-04-10 | 69 | keep | 0 | Apr | 2022 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-10 17:23 | 2022-04-10 17:35 | 1984 | 000:12 | T | CABLE SOTERRADO AVERIADO | HACIENDO PRUEBAS VOLVIO A DISPARAR SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 1911-07 | S22041000307 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 12 | 2022-04-10 | 23808 | keep | 0 | Apr | 2022 | 0.016216 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-10 17:30 | 2022-04-11 11:51 | 25 | 018:21 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA INTERMEDIO Y 1 X 40 EN CORTE DE LINEA PRINCIPAL SE REALIZO DESGANCHE | B22041000391 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1101 | 2022-04-10 | 27525 | keep | 0 | Apr | 2022 | 0.018747 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-04-10 17:30 | 2022-04-10 20:46 | 25 | 003:16 | P | NO SE REPORTO CAUSA | 1 X 30 C/L | C22041000407 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2022-04-10 | 4900 | keep | 0 | Apr | 2022 | 0.0033374 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-10 17:31 | 2022-04-10 20:53 | 400 | 003:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041000197 | New_Event | Bad Weather | Include | Include | Weather | 202 | 2022-04-10 | 80800 | keep | 0 | Apr | 2022 | 0.055033 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2022-04-10 17:35 | 2022-04-10 17:41 | 1587 | 000:06 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA DE RISER @ SU-1 CALLE PALMASOLA GARDEN HILLS Y SE CERRO MACHETES ABIERTOS SJ-220410-01 97% EN SERVICIO Y 100% EL 1911-07 | S22041000307 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 6 | 2022-04-10 | 9522 | keep | 0 | Apr | 2022 | 0.0064854 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-10 17:39 | 2022-04-10 20:17 | 60 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22041000399 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-04-10 | 9480 | keep | 0 | Apr | 2022 | 0.0064568 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-10 17:41 | 2022-04-11 19:10 | 40 | 025:29 | P | CABLE SOTERRADO AVERIADO | SE REALIZO JUMPER A RISER DE QUE TENIA AVERIA EN UNA DE SUS FASES PARA ENERGIZAR CARGAS MONOFASICAS POR AVERIA EN CABLE SOTERRADO DE RISER A SU 21 EN ALIMENTADOR 1529-12 | S22041000441 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1529 | 2022-04-10 | 61160 | keep | 0 | Apr | 2022 | 0.041656 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-04-10 17:42 | 2022-04-10 19:27 | 30 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B22041000393 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-04-10 | 3150 | keep | 0 | Apr | 2022 | 0.0021455 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-04-10 17:44 | 2022-04-10 18:43 | 30 | 000:59 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22041000400 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-04-10 | 1770 | keep | 0 | Apr | 2022 | 0.0012055 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-04-10 17:53 | 2022-04-10 21:00 | 25 | 003:07 | P | DESGANCHE | 1X40 EN C/L | R22041000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-04-10 | 4675 | keep | 0 | Apr | 2022 | 0.0031841 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-10 17:59 | 2022-04-11 14:57 | 8 | 020:58 | P | DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE | B22041000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1258 | 2022-04-10 | 10064 | keep | 0 | Apr | 2022 | 0.0068545 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-04-10 18:02 | 2022-04-11 09:04 | 15 | 015:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO ZAFADO DE LINEA A CORTE DE LINEA | A22041000154 | New_Event | Wire Down | Include | Include | Equipment | 902 | 2022-04-10 | 13530 | keep | 0 | Apr | 2022 | 0.0092152 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-04-10 18:03 | 2022-04-10 18:29 | 25 | 000:26 | P | DESGANCHE | 1X40 EN C/L | R22041000089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2022-04-10 | 650 | keep | 0 | Apr | 2022 | 0.00044271 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-10 18:13 | 2022-04-10 18:14 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6014-02 NO SE REPORTO CAUSA EL CUAL LLEVA LA CARGA DEL 6014-01 | M22041000204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 1444 | keep | 0 | Apr | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-04-10 18:13 | 2022-04-10 18:14 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-01 | M22041000204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-10 | 3630 | keep | 0 | Apr | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
VEGA BAJA | 2022-04-10 18:25 | 2022-04-10 18:32 | 1284 | 000:07 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR POR GUY CRUZADO CON CAJA PRIMARIA | B22041000000 | Additional_clients |  |  | Include | Wildlife | 7 | 2022-04-10 | 8988 | keep | 0 | Apr | 2022 | 0.0061217 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-04-10 18:32 | 2022-04-10 19:10 | 50 | 000:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA, SE REMPLAZO CAJA CAUSA DE CRUCE DE GUY CON CAJA PRIMARIA | B22041000516 | Partial_restoration |  |  | Include | Wildlife | 38 | 2022-04-10 | 1900 | keep | 0 | Apr | 2022 | 0.0012941 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-10 18:35 | 2022-04-10 21:37 | 240 | 003:02 | T | LINEA DE TRANSMISION 38KV | SE REPARO/LEVANTO FASE DE LA 3100 QUE SE PARTIO A MITAD DE SPAN Y CAYO SOBRE RISER DE SALIDA DEL INTERRUPTOR 2005-08 MEDIANTE G.O.I. SJ-220410-52 | R22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 182 | 2022-04-10 | 43680 | keep | 0 | Apr | 2022 | 0.02975 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
FAJARDO | 2022-04-10 18:35 | 2022-04-10 19:06 | 2286 | 000:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2022-04-10 | 70866 | keep | 0 | Apr | 2022 | 0.048267 | 0.001557 | Sustained | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2022-04-10 18:35 | 2022-04-10 19:06 | 693 | 000:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2022-04-10 | 21483 | keep | 0 | Apr | 2022 | 0.014632 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
VEGA BAJA | 2022-04-10 18:59 | 2022-04-10 21:47 | 1310 | 002:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO 50% EN SERVICIO | B22041000000 | New_Event | Wire Down | Include | Include | Equipment | 168 | 2022-04-10 | 220080 | keep | 0 | Apr | 2022 | 0.1499 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-04-10 19:02 | 2022-04-11 09:55 | 15 | 014:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22041000412 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 893 | 2022-04-10 | 13395 | keep | 0 | Apr | 2022 | 0.0091233 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-04-10 19:39 | 2022-04-10 23:54 | 10 | 004:15 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041000160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2022-04-10 | 2550 | keep | 0 | Apr | 2022 | 0.0017368 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-10 19:51 | 2022-04-10 19:54 | 1403 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-10 | 4209 | keep | 0 | Apr | 2022 | 0.0028667 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
CAGUAS | 2022-04-10 19:57 | 2022-04-10 20:00 | 3496 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 80% DE SU CARGA | C22041000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-10 | 10488 | keep | 0 | Apr | 2022 | 0.0071433 | 0.0023811 | Momentary | FALSE | FALSE | Not_TMED_Event | 3496
CAGUAS | 2022-04-10 20:00 | 2022-04-10 20:10 | 4 | 000:10 | P | CABLE SOTERRADO AVERIADO | 4 CARGAS TRIFASICAS FUERA DE SERVICIO. | C22041000232 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 10 | 2022-04-10 | 40 | keep | 0 | Apr | 2022 | 2.7244e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-10 20:10 | 2022-04-10 20:12 | 3496 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 80% DE SU CARGA | C22041000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-10 | 6992 | keep | 0 | Apr | 2022 | 0.0047622 | 0.0023811 | Momentary | FALSE | FALSE | Not_TMED_Event | 3496
CAGUAS | 2022-04-10 20:12 | 2022-04-12 13:00 | 4 | 040:48 | P | CABLE SOTERRADO AVERIADO | 4 CARGAS TRIFASICAS FUERA DE SERVICIO. | C22041000232 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 2448 | 2022-04-10 | 9792 | keep | 0 | Apr | 2022 | 0.0066693 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-04-10 20:32 | 2022-04-10 20:33 | 2368 | 000:01 | T | ERROR HUMANO | RECERRO PERSONAL REALIZO OPERACIONES EN EL FEEDER INCORRECTO Y EL MISMO RECERRO. | B22041000000 | New_Event | Human Error | Include | Include | Other | 1 | 2022-04-10 | 2368 | keep | 0 | Apr | 2022 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2022-04-10 20:33 | 2022-04-11 02:59 | 1534 | 006:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR DEL 9105-06 Y SE CERRO MACHETES | B22041000000 | New_Event | Wire Down | Include | Include | Equipment | 386 | 2022-04-10 | 592124 | keep | 0 | Apr | 2022 | 0.40329 | 0.0010448 | Sustained | FALSE | FALSE | Not_TMED_Event | 1534
BAYAMON | 2022-04-10 20:38 | 2022-04-10 21:20 | 50 | 000:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22041000478 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 42 | 2022-04-10 | 2100 | keep | 0 | Apr | 2022 | 0.0014303 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-10 20:38 | 2022-04-11 01:24 | 25 | 004:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041000162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2022-04-10 | 7150 | keep | 0 | Apr | 2022 | 0.0048698 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-04-10 20:44 | 2022-04-11 15:42 | 30 | 018:58 | P | NO SE REPORTO CAUSA | 2 X 30 EN CORTE DE LINEA | S22041000465 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1138 | 2022-04-10 | 34140 | keep | 0 | Apr | 2022 | 0.023253 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-04-10 20:49 | 2022-04-10 21:10 | 5 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE ENCONTRO CAUSA | M22041000217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2022-04-10 | 105 | keep | 0 | Apr | 2022 | 7.1515e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-04-10 21:02 | 2022-04-11 15:20 | 18 | 018:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22041000505 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1098 | 2022-04-10 | 19764 | keep | 0 | Apr | 2022 | 0.013461 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2022-04-10 21:38 | 2022-04-11 04:55 | 69 | 007:17 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22041000535 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 437 | 2022-04-10 | 30153 | keep | 0 | Apr | 2022 | 0.020537 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
CAGUAS | 2022-04-10 21:45 | 2022-04-10 23:44 | 100 | 001:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22040900443 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-04-10 | 11900 | keep | 0 | Apr | 2022 | 0.008105 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-04-10 21:47 | 2022-04-11 03:00 | 1048 | 005:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR Y SE ABRIO BKR PARA PODER CERRAR MACHETES POR SEGURIDAD INCOMODOS | B22041000000 | Partial_restoration | Wire Down | Include | Include | Equipment | 313 | 2022-04-10 | 328024 | keep | 0 | Apr | 2022 | 0.22342 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-10 22:05 | 2022-04-10 23:39 | 25 | 001:34 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22041000130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-04-10 | 2350 | keep | 0 | Apr | 2022 | 0.0016006 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-04-10 22:48 | 2022-04-11 09:57 | 45 | 011:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REMPLAZAR DISCO | C22041000460 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 669 | 2022-04-10 | 30105 | keep | 0 | Apr | 2022 | 0.020504 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-04-10 22:58 | 2022-04-10 22:59 | 574 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 574 | keep | 0 | Apr | 2022 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
AGUADILLA | 2022-04-10 22:58 | 2022-04-10 22:59 | 2493 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 2493 | keep | 0 | Apr | 2022 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
AGUADILLA | 2022-04-10 22:58 | 2022-04-10 22:59 | 1415 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 1415 | keep | 0 | Apr | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
AGUADILLA | 2022-04-10 22:58 | 2022-04-10 22:59 | 1428 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 1428 | keep | 0 | Apr | 2022 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
AGUADILLA | 2022-04-10 22:58 | 2022-04-10 22:59 | 1036 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 1036 | keep | 0 | Apr | 2022 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
AGUADILLA | 2022-04-10 22:58 | 2022-04-10 22:59 | 382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 382 | keep | 0 | Apr | 2022 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
AGUADILLA | 2022-04-10 22:58 | 2022-04-10 22:59 | 39 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 39 | keep | 0 | Apr | 2022 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2022-04-10 22:58 | 2022-04-10 22:59 | 2366 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 2366 | keep | 0 | Apr | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2022-04-10 22:58 | 2022-04-10 22:59 | 1337 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 1337 | keep | 0 | Apr | 2022 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-04-10 22:58 | 2022-04-10 22:59 | 709 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 5600 | M22041000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-10 | 709 | keep | 0 | Apr | 2022 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
MAYAGÃœEZ | 2022-04-10 23:34 | 2022-04-11 12:25 | 6 | 012:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 37.5 KVA | M22041000224 | New_Event | Service Transformer Failure | Include | Include | Equipment | 771 | 2022-04-10 | 4626 | keep | 0 | Apr | 2022 | 0.0031507 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-11 | 2022-04-11 00:01 | 222 | 000:01 | T | TRANSFORMADOR AVERIADO | HACIENDO PRUEBA RECERRO 1907-03 QUE LLEVA LA CARGA DEL 1909-09 | S22041000354 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-04-11 | 222 | keep | 0 | Apr | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-04-11 | 2022-04-11 00:01 | 4456 | 000:01 | T | TRANSFORMADOR AVERIADO | HACIENDO PRUEBA RECERRO 1907-03 QUE LLEVA LA CARGA DEL 1909-09 | S22041000354 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-04-11 | 4456 | keep | 0 | Apr | 2022 | 0.003035 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-11 00:01 | 2022-04-11 12:50 | 8 | 012:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRASNFORMADOR DE 100KVA AVERIADO CON GOI BY 220411-01A | S22041100020 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 769 | 2022-04-11 | 6152 | keep | 0 | Apr | 2022 | 0.0041901 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-04-11 00:29 | 2022-04-11 11:37 | 5 | 011:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR AVE CRUZO LINEAS | M22041100001 | New_Event |  |  | Include | Wildlife | 668 | 2022-04-11 | 3340 | keep | 0 | Apr | 2022 | 0.0022749 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-04-11 01:44 | 2022-04-11 01:45 | 1057 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22041100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 1057 | keep | 0 | Apr | 2022 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | Not_TMED_Event | 1057
BAYAMON | 2022-04-11 02:09 | 2022-04-11 04:17 | 863 | 002:08 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO HACIA TRASTALLERES Y SE CERRO POR TRAMO FRENTE A COND. BAHIA ENTRO 20% DEL 1119-04 Y ENTRO 1115-05 QUE ESTA ATRAVEZ DEL 1119-04 | S22041100012 | New_Event | Switch Failure | Include | Include | Equipment | 128 | 2022-04-11 | 110464 | keep | 0 | Apr | 2022 | 0.075237 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
BAYAMON | 2022-04-11 02:09 | 2022-04-11 04:29 | 863 | 002:20 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO HACIA TRASTALLERES Y SE CERRO POR TRAMO HACIA AVE. FDEZ. JUNCOS A ENTRO 98% DEL 1119-04 Y ENTRO 1119-02 | S22041100012 | New_Event | Switch Failure | Include | Include | Equipment | 140 | 2022-04-11 | 120820 | keep | 0 | Apr | 2022 | 0.08229 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
BAYAMON | 2022-04-11 02:09 | 2022-04-11 04:10 | 2720 | 002:01 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALLIZO HACIA TRASTALLERES Y SE CERRO POR SCADA LLEVA 95% DEL 1115-05 Y 1119-02 | S22041100012 | New_Event | Switch Failure | Include | Include | Equipment | 121 | 2022-04-11 | 329120 | keep | 0 | Apr | 2022 | 0.22416 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
CANOVANAS | 2022-04-11 02:52 | 2022-04-11 06:19 | 150 | 003:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON LAGARTO | R22041100002 | New_Event |  |  | Include | Wildlife | 207 | 2022-04-11 | 31050 | keep | 0 | Apr | 2022 | 0.021148 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-04-11 02:52 | 2022-04-11 06:10 | 125 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR IGUANA | R22041100002 | New_Event |  |  | Include | Wildlife | 198 | 2022-04-11 | 24750 | keep | 0 | Apr | 2022 | 0.016857 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2022-04-11 03:00 | 2022-04-11 11:51 | 1 | 008:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN RISER SE REMPLAZO CAJA QUEMADA | A22041100003 | New_Event | Cutout Failure | Include | Include | Equipment | 531 | 2022-04-11 | 531 | keep | 0 | Apr | 2022 | 0.00036166 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-11 03:00 | 2022-04-11 03:06 | 1310 | 000:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR Y SE ABRIO BKR PARA PODER CERRAR MACHETES POR SEGURIDAD INCOMODOS | B22041000000 | Additional_clients | Wire Down | Include | Include | Equipment | 6 | 2022-04-11 | 7860 | keep | 0 | Apr | 2022 | 0.0053534 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-04-11 03:01 | 2022-04-11 03:02 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22041100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 1192 | keep | 0 | Apr | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BAYAMON | 2022-04-11 04:10 | 2022-04-11 04:17 | 2176 | 000:07 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO HACIA TRASTALLERES Y SE CERRO POR TRAMO FRENTE A COND. BAHIA ENTRO 20% DEL 1119-04 Y 95% DEL 1115-05 | S22041100012 | Partial_restoration | Switch Failure | Include | Include | Equipment | 7 | 2022-04-11 | 15232 | keep | 0 | Apr | 2022 | 0.010374 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-11 04:17 | 2022-04-11 04:25 | 1088 | 000:08 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO HACIA TRASTALLERES Y SE CERRO POR TRAMO HACIA AVE. FDEZ. JUNCOS A ENTRO 60% DEL 1119-04 | S22041100012 | Partial_restoration | Switch Failure | Include | Include | Equipment | 8 | 2022-04-11 | 8704 | keep | 0 | Apr | 2022 | 0.0059283 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-11 04:18 | 2022-04-11 10:48 | 80 | 006:30 | P | DESCONECTIVO DEFECTUOSO | SE HIZO BYPASS V.S. MH-1 Y SE PASO AL 1117-7 | S22041100000 | New_Event | Switch Failure | Include | Include | Equipment | 390 | 2022-04-11 | 31200 | keep | 0 | Apr | 2022 | 0.02125 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-11 04:25 | 2022-04-11 04:29 | 500 | 000:04 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO HACIA TRASTALLERES Y SE CERRO POR TRAMO HACIA AVE. FDEZ. JUNCOS A ENTRO 98% DEL 1119-04 Y ENTRO 1119-02 | S22041100012 | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2022-04-11 | 2000 | keep | 0 | Apr | 2022 | 0.0013622 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-04-11 04:26 | 2022-04-11 16:41 | 18 | 012:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22041100018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 735 | 2022-04-11 | 13230 | keep | 0 | Apr | 2022 | 0.0090109 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-04-11 04:45 | 2022-04-11 06:31 | 6 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN XMR HAY QUE RETEZAR NEUTRAL PRIMARIO | C22041100001 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2022-04-11 | 636 | keep | 0 | Apr | 2022 | 0.00043318 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-04-11 05:37 | 2022-04-11 05:39 | 3025 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22041100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-11 | 6050 | keep | 0 | Apr | 2022 | 0.0041206 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
BARRANQUITAS | 2022-04-11 05:38 | 2022-04-11 09:05 | 50 | 003:27 | P | DESGANCHE | 1 X 50 EN C/L | C22041100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-04-11 | 10350 | keep | 0 | Apr | 2022 | 0.0070493 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-11 06:38 | 2022-04-11 10:13 | 50 | 003:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22041100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-04-11 | 10750 | keep | 0 | Apr | 2022 | 0.0073218 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-11 06:49 | 2022-04-11 06:50 | 918 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 918 | keep | 0 | Apr | 2022 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
MAYAGÃœEZ | 2022-04-11 06:54 | 2022-04-11 12:01 | 20 | 005:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22041100006 | New_Event | Bad Weather | Include | Include | Weather | 307 | 2022-04-11 | 6140 | keep | 0 | Apr | 2022 | 0.0041819 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-04-11 07:00 | 2022-04-11 16:30 | 10 | 009:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M22041100023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 570 | 2022-04-11 | 5700 | keep | 0 | Apr | 2022 | 0.0038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-11 07:13 | 2022-04-11 14:50 | 20 | 007:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041100007 | New_Event | Bad Weather | Include | Include | Weather | 457 | 2022-04-11 | 9140 | keep | 0 | Apr | 2022 | 0.0062252 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-04-11 07:14 | 2022-04-11 08:59 | 93 | 001:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y 1 X 65 EN CORTES DE LINEA SE REEMLAZO CAJA PRIMARIA | R22041100013 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2022-04-11 | 9765 | keep | 0 | Apr | 2022 | 0.0066509 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2022-04-11 07:18 | 2022-04-11 21:27 | 4 | 014:09 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER INDICO NO IDENTIFICO CAUSA | M22041100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 849 | 2022-04-11 | 3396 | keep | 0 | Apr | 2022 | 0.002313 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-11 07:23 | 2022-04-11 12:00 | 35 | 004:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X 50 EN C/L SE REPARO BAJANTE LINEA A CAJA EN XMR CRUZADO | B22041100028 | New_Event | Wire Down | Include | Include | Equipment | 277 | 2022-04-11 | 9695 | keep | 0 | Apr | 2022 | 0.0066032 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-04-11 07:30 | 2022-04-11 09:55 | 1 | 002:25 | P | NO SE REPORTO CAUSA | 2 X 30 EN RISER FOREMAN NO NOTIFICO CAUSA | A22041100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-04-11 | 145 | keep | 0 | Apr | 2022 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-11 07:58 | 2022-04-11 11:59 | 40 | 004:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R22041100017 | New_Event |  |  | Include | Wildlife | 241 | 2022-04-11 | 9640 | keep | 0 | Apr | 2022 | 0.0065658 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-11 08:06 | 2022-04-11 16:53 | 75 | 008:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S22041100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 527 | 2022-04-11 | 39525 | keep | 0 | Apr | 2022 | 0.02692 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-04-11 08:08 | 2022-04-11 10:10 | 200 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R22041100020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-04-11 | 24400 | keep | 0 | Apr | 2022 | 0.016619 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-04-11 08:09 | 2022-04-11 14:30 | 1 | 006:21 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN XMR REMPLAZO XMR AVERIADO DE 15 KVA X 15 KVA | C22041100014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 381 | 2022-04-11 | 381 | keep | 0 | Apr | 2022 | 0.0002595 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-11 08:10 | 2022-04-11 20:20 | 12 | 012:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22041100039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 730 | 2022-04-11 | 8760 | keep | 0 | Apr | 2022 | 0.0059664 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-04-11 08:16 | 2022-04-11 08:20 | 403 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1620-03 | S22041100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-11 | 1612 | keep | 0 | Apr | 2022 | 0.0010979 | 0.00027448 | Momentary | FALSE | FALSE | Not_TMED_Event | 403
SAN JUAN | 2022-04-11 08:16 | 2022-04-11 08:20 | 36 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1620-03 | S22041100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-11 | 144 | keep | 0 | Apr | 2022 | 9.8078e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-04-11 08:16 | 2022-04-11 08:20 | 1073 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1620-01 Y 1336-10 | S22041100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-11 | 4292 | keep | 0 | Apr | 2022 | 0.0029233 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
HUMACAO | 2022-04-11 08:19 | 2022-04-11 15:50 | 20 | 007:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C22041100018 | New_Event | Wire Down | Include | Include | Equipment | 451 | 2022-04-11 | 9020 | keep | 0 | Apr | 2022 | 0.0061435 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-11 08:21 | 2022-04-11 12:32 | 80 | 004:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REMPLAZO AISLADOR | C22041100019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 251 | 2022-04-11 | 20080 | keep | 0 | Apr | 2022 | 0.013676 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-11 08:39 | 2022-04-11 14:21 | 50 | 005:42 | P | DESGANCHE | 1 X 50 EN C/L | C22041100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2022-04-11 | 17100 | keep | 0 | Apr | 2022 | 0.011647 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-11 08:54 | 2022-04-12 04:52 | 31 | 019:58 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR | S22041100062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1198 | 2022-04-11 | 37138 | keep | 0 | Apr | 2022 | 0.025295 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
ARECIBO | 2022-04-11 09:07 | 2022-04-11 12:10 | 12 | 003:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE QUEMADO | A22041100007 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2022-04-11 | 2196 | keep | 0 | Apr | 2022 | 0.0014957 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-04-11 09:15 | 2022-04-11 09:16 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A22041100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 308 | keep | 0 | Apr | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
FAJARDO | 2022-04-11 09:17 | 2022-04-11 10:05 | 1 | 000:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | R22041100035 | New_Event | Cutout Failure | Include | Include | Equipment | 48 | 2022-04-11 | 48 | keep | 0 | Apr | 2022 | 3.2693e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-11 09:21 | 2022-04-11 18:20 | 8 | 008:59 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041100010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 539 | 2022-04-11 | 4312 | keep | 0 | Apr | 2022 | 0.0029369 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-04-11 09:25 | 2022-04-11 15:10 | 25 | 005:45 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR INDICO JOURNEYMAN NO IDENTIFICO CAUSA | M22041100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 345 | 2022-04-11 | 8625 | keep | 0 | Apr | 2022 | 0.0058744 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-04-11 09:45 | 2022-04-11 11:03 | 1 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22041100030 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2022-04-11 | 78 | keep | 0 | Apr | 2022 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-11 09:46 | 2022-04-12 11:04 | 1 | 025:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER AVE | S22041100082 | New_Event |  |  | Include | Wildlife | 1518 | 2022-04-11 | 1518 | keep | 0 | Apr | 2022 | 0.0010339 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-04-11 09:46 | 2022-04-11 11:30 | 40 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR Y 1 X 40 EN CORTE DE LINEA POR AVE | P22041100015 | New_Event |  |  | Include | Wildlife | 104 | 2022-04-11 | 4160 | keep | 0 | Apr | 2022 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-04-11 09:55 | 2022-04-11 13:09 | 20 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22041100077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-04-11 | 3880 | keep | 0 | Apr | 2022 | 0.0026427 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-11 10:10 | 2022-04-11 11:55 | 6 | 001:45 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y LEVANTAR SECUNDARIA | C22041100038 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 105 | 2022-04-11 | 630 | keep | 0 | Apr | 2022 | 0.00042909 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-11 10:13 | 2022-04-11 10:14 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO CARGA 1720-08 | B22041100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 2402 | keep | 0 | Apr | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-04-11 10:13 | 2022-04-11 10:14 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO CARGA 1720-08 | B22041100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-11 10:18 | 2022-04-11 14:00 | 50 | 003:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA SE RETIRO PARARRAYO EN SUB DE FIRSTBANK | S22041100095 | New_Event | Wire Down | Include | Include | Equipment | 222 | 2022-04-11 | 11100 | keep | 0 | Apr | 2022 | 0.0075602 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-11 10:24 | 2022-04-12 15:10 | 40 | 028:46 | P | NO SE REPORTO CAUSA | 1 X 80 SUM-20 | S22041100100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1726 | 2022-04-11 | 69040 | keep | 0 | Apr | 2022 | 0.047023 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-11 10:26 | 2022-04-11 10:27 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO Y QUEDO EN SERVICIO | B22041100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 3941 | keep | 0 | Apr | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-04-11 10:27 | 2022-04-11 11:49 | 1 | 001:22 | P | TRANSFORMADOR AVERIADO | 2 X 10 EN BANCO XMR SE ELIMINO TRANSFORMADOR Y SE CONSTRUYO DELTA ABIERTA | B22041000323 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 82 | 2022-04-11 | 82 | keep | 0 | Apr | 2022 | 5.585e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-11 10:27 | 2022-04-12 11:22 | 2 | 024:55 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN BANCO DE TRANSFORMADORES SE RETIRO ENREDADERA | C22041100044 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1495 | 2022-04-11 | 2990 | keep | 0 | Apr | 2022 | 0.0020365 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-04-11 10:41 | 2022-04-11 14:00 | 25 | 003:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | C22041100049 | New_Event |  |  | Include | Wildlife | 199 | 2022-04-11 | 4975 | keep | 0 | Apr | 2022 | 0.0033884 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-11 10:43 | 2022-04-11 13:27 | 12 | 002:44 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22041100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-04-11 | 1968 | keep | 0 | Apr | 2022 | 0.0013404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-11 10:48 | 2022-04-11 11:01 | 740 | 000:13 | T | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO CARGA POR EL 1119-04 SJ-220411-01 | S22041100000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 13 | 2022-04-11 | 9620 | keep | 0 | Apr | 2022 | 0.0065521 | 0.00050401 | Sustained | FALSE | FALSE | Not_TMED_Event | 740
BAYAMON | 2022-04-11 10:48 | 2022-04-11 11:01 | 2720 | 000:13 | T | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO SJ-220411-01 | S22041100000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 13 | 2022-04-11 | 35360 | keep | 0 | Apr | 2022 | 0.024084 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
CAGUAS | 2022-04-11 10:55 | 2022-04-11 14:49 | 40 | 003:54 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22041100054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-04-11 | 9360 | keep | 0 | Apr | 2022 | 0.0063751 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-11 11:01 | 2022-04-11 13:02 | 80 | 002:01 | P | DESCONECTIVO DEFECTUOSO | SE HIZO BYPASS V.S. MH-1 Y SE PASO AL 1117-7 | S22041100000 | New_Event | Switch Failure | Include | Include | Equipment | 121 | 2022-04-11 | 9680 | keep | 0 | Apr | 2022 | 0.006593 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-04-11 11:16 | 2022-04-11 17:14 | 20 | 005:58 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C22041100057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 358 | 2022-04-11 | 7160 | keep | 0 | Apr | 2022 | 0.0048766 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-04-11 11:19 | 2022-04-11 13:27 | 1 | 002:08 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22041100059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2022-04-11 | 128 | keep | 0 | Apr | 2022 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-11 11:44 | 2022-04-11 20:23 | 40 | 008:39 | P | SOBRECARGA | 1 X 10 EN XMR SOBRE CARGA | C22041100061 | New_Event | Trip Due To Overload | Include | Include | Other | 519 | 2022-04-11 | 20760 | keep | 0 | Apr | 2022 | 0.01414 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-04-11 12:31 | 2022-04-11 22:35 | 150 | 010:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE QUEMADO | M22041100051 | New_Event | Cutout Failure | Include | Include | Equipment | 604 | 2022-04-11 | 90600 | keep | 0 | Apr | 2022 | 0.061707 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-04-11 12:33 | 2022-04-11 12:34 | 1 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN BANCO DE XMR'S CRUCE X AVE | C22041100043 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-11 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-11 12:37 | 2022-04-12 02:52 | 179 | 014:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22041100164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 855 | 2022-04-11 | 153045 | keep | 0 | Apr | 2022 | 0.10424 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
YAUCO | 2022-04-11 12:40 | 2022-04-11 15:47 | 40 | 003:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR ARBOL SOBRE LINEA | P22041100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-04-11 | 7480 | keep | 0 | Apr | 2022 | 0.0050946 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-11 12:48 | 2022-04-11 18:56 | 6 | 006:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REMPLAZO TRAMO SECUNDARIO | C22041100095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 368 | 2022-04-11 | 2208 | keep | 0 | Apr | 2022 | 0.0015039 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-04-11 12:57 | 2022-04-11 15:16 | 120 | 002:19 | P | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR POR SEGURIDAD PARA LEVANTAR TRAMO DE ALAMBRE DE LINEA 3100 EL 50% ESTA TRANSFERIDO AL 2003-01 SJ-220411-50 | R22041100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 139 | 2022-04-11 | 16680 | keep | 0 | Apr | 2022 | 0.011361 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2022-04-11 12:59 | 2022-04-11 13:00 | 1467 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041100101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 1467 | keep | 0 | Apr | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BARRANQUITAS | 2022-04-11 13:01 | 2022-04-11 13:02 | 30 | 000:01 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L NO CAUSA | C22041100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 30 | keep | 0 | Apr | 2022 | 2.0433e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-11 13:02 | 2022-04-11 13:03 | 740 | 000:01 | T | DESCONECTIVO DEFECTUOSO | PERSONAR REALIZANDO OPERACIONES BUSCANDO AVERIA SOTERRADA SJ-220411-01 CARGA POR EL 1119-04 | S22041100000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-04-11 | 740 | keep | 0 | Apr | 2022 | 0.00050401 | 0.00050401 | Momentary | FALSE | FALSE | Not_TMED_Event | 740
BAYAMON | 2022-04-11 13:02 | 2022-04-11 13:03 | 2720 | 000:01 | T | DESCONECTIVO DEFECTUOSO | PERSONAR REALIZANDO OPERACIONES BUSCANDO AVERIA SOTERRADA SJ-220411-01 | S22041100000 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2022-04-11 | 2720 | keep | 0 | Apr | 2022 | 0.0018526 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-11 13:03 | 2022-04-11 13:46 | 80 | 000:43 | P | DESCONECTIVO DEFECTUOSO | SE HIZO BYPASS V.S. MH-1 Y SE PASO AL 1117-7 | S22041100000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 43 | 2022-04-11 | 3440 | keep | 0 | Apr | 2022 | 0.002343 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-11 13:04 | 2022-04-11 17:03 | 8 | 003:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | B22041100104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 239 | 2022-04-11 | 1912 | keep | 0 | Apr | 2022 | 0.0013023 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-04-11 13:23 | 2022-04-12 13:18 | 3 | 023:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | P22041100040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1435 | 2022-04-11 | 4305 | keep | 0 | Apr | 2022 | 0.0029321 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-04-11 13:25 | 2022-04-11 21:19 | 25 | 007:54 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION EN RISER HACIA TRANSFORMADOR | B22041100106 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 474 | 2022-04-11 | 11850 | keep | 0 | Apr | 2022 | 0.008071 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-11 13:31 | 2022-04-11 16:08 | 40 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | P22041100041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-04-11 | 6280 | keep | 0 | Apr | 2022 | 0.0042773 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-11 13:37 | 2022-04-12 08:12 | 80 | 018:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE | S22041100185 | New_Event | Wire Down | Include | Include | Equipment | 1115 | 2022-04-11 | 89200 | keep | 0 | Apr | 2022 | 0.060754 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-04-11 13:38 | 2022-04-11 15:30 | 25 | 001:52 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | R22041100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-04-11 | 2800 | keep | 0 | Apr | 2022 | 0.0019071 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-11 13:39 | 2022-04-11 17:06 | 30 | 003:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M22041100065 | New_Event | Wire Down | Include | Include | Equipment | 207 | 2022-04-11 | 6210 | keep | 0 | Apr | 2022 | 0.0042296 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-11 13:46 | 2022-04-11 13:47 | 740 | 000:01 | T | DESCONECTIVO DEFECTUOSO | PERSONAR REALIZANDO OPERACIONES BUSCANDO AVERIA SOTERRADA SJ-220411-01 CARGA POR EL 1119-04 | S22041100000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-04-11 | 740 | keep | 0 | Apr | 2022 | 0.00050401 | 0.00050401 | Momentary | FALSE | FALSE | Not_TMED_Event | 740
BAYAMON | 2022-04-11 13:46 | 2022-04-11 13:47 | 2720 | 000:01 | T | DESCONECTIVO DEFECTUOSO | PERSONAR REALIZANDO OPERACIONES BUSCANDO AVERIA SOTERRADA SJ-220411-01 | S22041100000 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2022-04-11 | 2720 | keep | 0 | Apr | 2022 | 0.0018526 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-11 13:47 | 2022-04-12 19:55 | 80 | 030:08 | P | DESCONECTIVO DEFECTUOSO | SE HIZO BYPASS V.S. MH-1 Y SE PASO AL 1117-7 | S22041100000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1808 | 2022-04-11 | 144640 | keep | 0 | Apr | 2022 | 0.098514 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-11 13:59 | 2022-04-11 19:20 | 2 | 005:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADORES AVERIADOS UNO DE 25 KVA Y UNO DE 50 KVA EN MONTURA DE TRANSFORMADORES POR LA MISMA CAPACIDAD | A22041100035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 321 | 2022-04-11 | 642 | keep | 0 | Apr | 2022 | 0.00043726 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-04-11 14:05 | 2022-04-11 17:44 | 10 | 003:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | M22041100071 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2022-04-11 | 2190 | keep | 0 | Apr | 2022 | 0.0014916 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-04-11 14:08 | 2022-04-11 16:00 | 80 | 001:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L AISLADOR | R22041100054 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 112 | 2022-04-11 | 8960 | keep | 0 | Apr | 2022 | 0.0061026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-11 14:11 | 2022-04-11 15:55 | 10 | 001:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN RISER SE REMPLAZO PORTAFUSIBLES | B22041100109 | New_Event | Cutout Failure | Include | Include | Equipment | 104 | 2022-04-11 | 1040 | keep | 0 | Apr | 2022 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-11 14:16 | 2022-04-12 00:28 | 50 | 010:12 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO PISTOLA 1 X 30 EN CORTE DE LINEA | B22041100133 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 612 | 2022-04-11 | 30600 | keep | 0 | Apr | 2022 | 0.020842 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-11 14:17 | 2022-04-11 14:18 | 4664 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22041100074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 4664 | keep | 0 | Apr | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
ARECIBO | 2022-04-11 14:37 | 2022-04-11 21:30 | 6 | 006:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES AVERIADO | A22041100036 | New_Event | Cutout Failure | Include | Include | Equipment | 413 | 2022-04-11 | 2478 | keep | 0 | Apr | 2022 | 0.0016878 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-04-11 14:39 | 2022-04-11 21:00 | 80 | 006:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22041100075 | New_Event | Bad Weather | Include | Include | Weather | 381 | 2022-04-11 | 30480 | keep | 0 | Apr | 2022 | 0.02076 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-11 14:48 | 2022-04-11 18:53 | 120 | 004:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C22041100144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2022-04-11 | 29400 | keep | 0 | Apr | 2022 | 0.020024 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-04-11 14:52 | 2022-04-12 14:00 | 6 | 023:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R22041100059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1388 | 2022-04-11 | 8328 | keep | 0 | Apr | 2022 | 0.0056722 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-04-11 14:52 | 2022-04-11 14:54 | 3000 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22041100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-11 | 6000 | keep | 0 | Apr | 2022 | 0.0040866 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2022-04-11 14:52 | 2022-04-11 14:54 | 908 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22041100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-11 | 1816 | keep | 0 | Apr | 2022 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
VEGA BAJA | 2022-04-11 14:52 | 2022-04-11 14:54 | 3332 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22041100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-11 | 6664 | keep | 0 | Apr | 2022 | 0.0045388 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
CAGUAS | 2022-04-11 14:53 | 2022-04-11 14:55 | 329 | 000:02 | T | CABLE SOTERRADO AVERIADO | PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA SOTERRADA | C22041100000 | New_Event | UG Cable Fault | Include | Include | Equipment | 2 | 2022-04-11 | 658 | keep | 0 | Apr | 2022 | 0.00044816 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2022-04-11 14:55 | 2022-04-11 19:00 | 10 | 004:05 | P | OTRAS CAUSAS | DESCONECTO ESCUELA GERARDO SELLES SOLA Y FARMACIA CON TOMAS AVERIADAS | C22041100029 | New_Event | Other Causes | Include | Include | Other | 245 | 2022-04-11 | 2450 | keep | 0 | Apr | 2022 | 0.0016687 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-04-11 15:07 | 2022-04-11 15:08 | 2307 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9003-06 CON 25% DE SU CARGA POR 9003-05 | B22041100121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 2307 | keep | 0 | Apr | 2022 | 0.0015713 | 0.0015713 | Momentary | FALSE | FALSE | Not_TMED_Event | 2307
BAYAMON | 2022-04-11 15:14 | 2022-04-11 20:57 | 68 | 005:43 | S | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE L-6700 | S22041100217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 343 | 2022-04-11 | 23324 | keep | 0 | Apr | 2022 | 0.015886 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-04-11 15:14 | 2022-04-11 20:57 | 171 | 005:43 | S | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE L-6700 | S22041100217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 343 | 2022-04-11 | 58653 | keep | 0 | Apr | 2022 | 0.039948 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-04-11 15:14 | 2022-04-11 20:57 | 1837 | 005:43 | S | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE L-6700 | S22041100219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 343 | 2022-04-11 | 630091 | keep | 0 | Apr | 2022 | 0.42915 | 0.0012512 | Sustained | FALSE | FALSE | Not_TMED_Event | 1837
BAYAMON | 2022-04-11 15:14 | 2022-04-11 20:57 | 536 | 005:43 | S | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE L-6700 | S22041100217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 343 | 2022-04-11 | 183848 | keep | 0 | Apr | 2022 | 0.12522 | 0.00036507 | Sustained | FALSE | FALSE | Not_TMED_Event | 536
BAYAMON | 2022-04-11 15:14 | 2022-04-11 20:57 | 348 | 005:43 | S | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE L-6700 | S22041100217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 343 | 2022-04-11 | 119364 | keep | 0 | Apr | 2022 | 0.081298 | 0.00023702 | Sustained | FALSE | FALSE | Not_TMED_Event | 348
SAN JUAN | 2022-04-11 15:14 | 2022-04-11 20:57 | 559 | 005:43 | T | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE L-6700 SU CARGA POR 1102-1 | S22041100217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 343 | 2022-04-11 | 191737 | keep | 0 | Apr | 2022 | 0.13059 | 0.00038073 | Sustained | FALSE | FALSE | Not_TMED_Event | 559
BAYAMON | 2022-04-11 15:14 | 2022-04-11 20:57 | 370 | 005:43 | T | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE L-6700 SU CARGA POR 1102-1 | S22041100217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 343 | 2022-04-11 | 126910 | keep | 0 | Apr | 2022 | 0.086438 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
SAN JUAN | 2022-04-11 15:14 | 2022-04-11 20:58 | 218 | 005:44 | S | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE PRIMARIO L-6700 | S22041100221 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 344 | 2022-04-11 | 74992 | keep | 0 | Apr | 2022 | 0.051077 | 0.00014848 | Sustained | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2022-04-11 15:14 | 2022-04-11 20:58 | 455 | 005:44 | S | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE PRIMARIO L-6700 | S22041100222 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 344 | 2022-04-11 | 156520 | keep | 0 | Apr | 2022 | 0.10661 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2022-04-11 15:14 | 2022-04-11 20:58 | 1526 | 005:44 | S | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE PRIMARIO L-6700 | S22041100221 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 344 | 2022-04-11 | 524944 | keep | 0 | Apr | 2022 | 0.35754 | 0.0010394 | Sustained | FALSE | FALSE | Not_TMED_Event | 1526
SAN JUAN | 2022-04-11 15:14 | 2022-04-11 20:58 | 283 | 005:44 | S | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE PRIMARIO L-6700 | S22041100223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 344 | 2022-04-11 | 97352 | keep | 0 | Apr | 2022 | 0.066306 | 0.00019275 | Sustained | FALSE | FALSE | Not_TMED_Event | 283
BAYAMON | 2022-04-11 15:16 | 2022-04-11 17:23 | 15 | 002:07 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22041100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2022-04-11 | 1905 | keep | 0 | Apr | 2022 | 0.0012975 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-04-11 15:21 | 2022-04-11 17:22 | 120 | 002:01 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN C/L DESGANCHE | R22041100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-04-11 | 14520 | keep | 0 | Apr | 2022 | 0.0098895 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-04-11 15:26 | 2022-04-11 15:27 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 3046 | keep | 0 | Apr | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CAGUAS | 2022-04-11 15:26 | 2022-04-11 15:27 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041100168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
PONCE | 2022-04-11 15:27 | 2022-04-11 17:28 | 3 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTA CAUSA | P22041100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-04-11 | 363 | keep | 0 | Apr | 2022 | 0.00024724 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-04-11 15:43 | 2022-04-11 15:44 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041100050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 215 | keep | 0 | Apr | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2022-04-11 15:44 | 2022-04-11 15:59 | 10 | 000:15 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR | B22041100126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-04-11 | 150 | keep | 0 | Apr | 2022 | 0.00010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-04-11 15:51 | 2022-04-11 17:46 | 120 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L 1 X 65 EN OTRO | R22041100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-04-11 | 13800 | keep | 0 | Apr | 2022 | 0.0093991 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-04-11 15:53 | 2022-04-12 12:30 | 1 | 020:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN RISER CRUCE POR AVE | C22041100172 | New_Event |  |  | Include | Wildlife | 1237 | 2022-04-11 | 1237 | keep | 0 | Apr | 2022 | 0.00084252 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-11 15:55 | 2022-04-12 11:12 | 2 | 019:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C22041100174 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1157 | 2022-04-11 | 2314 | keep | 0 | Apr | 2022 | 0.0015761 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-04-11 15:55 | 2022-04-11 15:56 | 1 | 000:01 | P | NO SE REPORTO CAUSA | 2 X 15 EN BANCO DE XMR'S NO CAUSA | C22041100183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-11 15:57 | 2022-04-11 15:58 | 308 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22041100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-11 | 308 | keep | 0 | Apr | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2022-04-11 15:58 | 2022-04-11 20:55 | 20 | 004:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041100039 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-04-11 | 5940 | keep | 0 | Apr | 2022 | 0.0040457 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-11 16:07 | 2022-04-11 20:06 | 50 | 003:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 Y1 X 30 EN CORTE DE LINEA SE LEVANTO FASE | S22041100263 | New_Event | Wire Down | Include | Include | Equipment | 239 | 2022-04-11 | 11950 | keep | 0 | Apr | 2022 | 0.0081391 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-11 16:15 | 2022-04-11 19:50 | 50 | 003:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L LINEAS CRUZADAS POR IMPACTO DE CAMION | C22041100178 | New_Event |  |  | Include | Wildlife | 215 | 2022-04-11 | 10750 | keep | 0 | Apr | 2022 | 0.0073218 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-11 16:26 | 2022-04-11 20:53 | 300 | 004:27 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN RISER Y 1 X 40 EN SU. AVERIA DE T-2 @ T-3. FUERA T-3, T-4, T-5 Y T-6 | R22041100072 | New_Event | UG Cable Fault | Include | Include | Equipment | 267 | 2022-04-11 | 80100 | keep | 0 | Apr | 2022 | 0.054556 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-04-11 16:34 | 2022-04-11 16:37 | 1106 | 000:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1529-15 QUE LLEVA 60% DEL 1346-02 SE PROBO QUEDO EN SERVICIO | S22041100000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-04-11 | 3318 | keep | 0 | Apr | 2022 | 0.0022599 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-04-11 16:34 | 2022-04-11 16:37 | 1802 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO LLAVA 60% DEL 1346-2 SE PROBO QUEDO EN SERVICIO | S22041100000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-04-11 | 5406 | keep | 0 | Apr | 2022 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-04-11 16:37 | 2022-04-11 23:30 | 164 | 006:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA CERRAR PUENTE PRIMARIO | S22041100464 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 413 | 2022-04-11 | 67732 | keep | 0 | Apr | 2022 | 0.046132 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
SAN JUAN | 2022-04-11 16:37 | 2022-04-11 23:30 | 88 | 006:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA CERRAR PUENTE PRIMARIO | S22041100465 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 413 | 2022-04-11 | 36344 | keep | 0 | Apr | 2022 | 0.024754 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
HUMACAO | 2022-04-11 16:40 | 2022-04-11 19:40 | 6 | 003:00 | P | NO SE REPORTO CAUSA | 1 NX DE 18A EN T - 1 NO CAUSA | C22041100184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2022-04-11 | 1080 | keep | 0 | Apr | 2022 | 0.00073558 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-04-11 16:44 | 2022-04-11 18:10 | 14 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA POR CAMION | C22041100186 | New_Event |  |  | Include | Wildlife | 86 | 2022-04-11 | 1204 | keep | 0 | Apr | 2022 | 0.00082004 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
GUAYAMA | 2022-04-11 16:48 | 2022-04-11 19:00 | 2 | 002:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 15 EN MONTURA TRIFASICA SE SEPARARON PUENTES DE PARARRAYOS | P22041100059 | New_Event | Wire Down | Include | Include | Equipment | 132 | 2022-04-11 | 264 | keep | 0 | Apr | 2022 | 0.00017981 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-04-11 17:14 | 2022-04-12 09:59 | 40 | 016:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR NO FUNDIO | R22041100082 | New_Event | Wire Down | Include | Include | Equipment | 1005 | 2022-04-11 | 40200 | keep | 0 | Apr | 2022 | 0.02738 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-11 17:17 | 2022-04-12 07:46 | 10 | 014:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR CRUCE POR CHANGO | C22041100191 | New_Event |  |  | Include | Wildlife | 869 | 2022-04-11 | 8690 | keep | 0 | Apr | 2022 | 0.0059187 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-11 17:21 | 2022-04-11 19:20 | 352 | 001:59 | P | DESGANCHE | SE RETIRO ARBOL Y SE CERRO MACHETES | R22041100068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-04-11 | 41888 | keep | 0 | Apr | 2022 | 0.02853 | 0.00023975 | Sustained | FALSE | FALSE | Not_TMED_Event | 352
BAYAMON | 2022-04-11 17:23 | 2022-04-11 17:24 | 50 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO AL CERRAR TIE EN SU-3A GANG EN EDIFICIO CENTRAL Y SE ABRIO SE CERRO INTERRUPTOR | S22041100000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-04-11 | 50 | keep | 0 | Apr | 2022 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-11 17:28 | 2022-04-12 02:45 | 80 | 009:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE RETIRO CABLE CRUZANDO FASES | M22041100084 | New_Event | Wire Down | Include | Include | Equipment | 557 | 2022-04-11 | 44560 | keep | 0 | Apr | 2022 | 0.03035 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-11 17:42 | 2022-04-12 00:43 | 1 | 007:01 | P | NO SE REPORTO CAUSA | 2 X 15 EN BANCO DE XMR | B22041100143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 421 | 2022-04-11 | 421 | keep | 0 | Apr | 2022 | 0.00028674 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-04-11 17:49 | 2022-04-12 11:29 | 5 | 017:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X REPTIL | R22041100086 | New_Event |  |  | Include | Wildlife | 1060 | 2022-04-11 | 5300 | keep | 0 | Apr | 2022 | 0.0036098 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-04-11 17:58 | 2022-04-11 20:31 | 2 | 002:33 | P | OTRAS CAUSAS | 1 X 40 EN TRANSFORMADOR POR DEFECTO INTERIOR DE UN CLIENTE | P22041100066 | New_Event | Other Causes | Include | Include | Other | 153 | 2022-04-11 | 306 | keep | 0 | Apr | 2022 | 0.00020842 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-04-11 18:09 | 2022-04-11 23:20 | 30 | 005:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | A22041100047 | New_Event | Wire Down | Include | Include | Equipment | 311 | 2022-04-11 | 9330 | keep | 0 | Apr | 2022 | 0.0063546 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-04-11 18:54 | 2022-04-12 09:58 | 7 | 015:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R22041100097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 904 | 2022-04-11 | 6328 | keep | 0 | Apr | 2022 | 0.00431 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-04-11 19:05 | 2022-04-12 14:34 | 10 | 019:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22041100050 | New_Event | Bad Weather | Include | Include | Weather | 1169 | 2022-04-11 | 11690 | keep | 0 | Apr | 2022 | 0.007962 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-11 19:10 | 2022-04-13 20:48 | 80 | 049:38 | P | CABLE SOTERRADO AVERIADO | SE ALAMBRO RISER A SU-1 | S22041000307 | New_Event | UG Cable Fault | Include | Include | Equipment | 2978 | 2022-04-11 | 238240 | keep | 0 | Apr | 2022 | 0.16226 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-11 19:13 | 2022-04-11 21:53 | 353 | 002:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22041100150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-04-11 | 56480 | keep | 0 | Apr | 2022 | 0.038468 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
MAYAGÃœEZ | 2022-04-11 19:32 | 2022-04-12 17:45 | 25 | 022:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22041100095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1333 | 2022-04-11 | 33325 | keep | 0 | Apr | 2022 | 0.022698 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-04-11 19:40 | 2022-04-12 08:56 | 45 | 013:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22041100153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 796 | 2022-04-11 | 35820 | keep | 0 | Apr | 2022 | 0.024397 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-04-11 19:41 | 2022-04-12 12:10 | 100 | 016:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE Y SE RETIRO GUY | S22041100408 | New_Event | Wire Down | Include | Include | Equipment | 989 | 2022-04-11 | 98900 | keep | 0 | Apr | 2022 | 0.06736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-11 19:56 | 2022-04-12 14:38 | 124 | 018:42 | P | NO SE REPORTO CAUSA | 2 RVAA DE 25 AMP. Y 1 RVA DE 50 AMP. | C22041100212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1122 | 2022-04-11 | 139128 | keep | 0 | Apr | 2022 | 0.094759 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
MAYAGÃœEZ | 2022-04-11 19:56 | 2022-04-11 22:50 | 30 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22041100096 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2022-04-11 | 5220 | keep | 0 | Apr | 2022 | 0.0035553 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-04-11 19:59 | 2022-04-11 22:21 | 50 | 002:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA DEL PISO | P22041100082 | New_Event | Wire Down | Include | Include | Equipment | 142 | 2022-04-11 | 7100 | keep | 0 | Apr | 2022 | 0.0048358 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-11 20:15 | 2022-04-12 09:20 | 16 | 013:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22041100084 | New_Event |  |  | Include | Wildlife | 785 | 2022-04-11 | 12560 | keep | 0 | Apr | 2022 | 0.0085546 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-04-11 20:18 | 2022-04-12 13:00 | 200 | 016:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22041100102 | New_Event | Wire Down | Include | Include | Equipment | 1002 | 2022-04-11 | 200400 | keep | 0 | Apr | 2022 | 0.13649 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-04-11 20:19 | 2022-04-12 12:39 | 16 | 016:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE | B22041100164 | New_Event | Secondary Wire Down | Include | Include | Equipment | 980 | 2022-04-11 | 15680 | keep | 0 | Apr | 2022 | 0.01068 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2022-04-11 20:27 | 2022-04-12 02:14 | 80 | 005:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AUTO IMPACTO TENSOR EN POSTE | C22041200022 | New_Event |  |  | Include | Wildlife | 347 | 2022-04-11 | 27760 | keep | 0 | Apr | 2022 | 0.018907 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-04-11 20:33 | 2022-04-11 20:37 | 1863 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22041100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-11 | 7452 | keep | 0 | Apr | 2022 | 0.0050755 | 0.0012689 | Momentary | FALSE | FALSE | Not_TMED_Event | 1863
PONCE | 2022-04-11 20:33 | 2022-04-11 20:37 | 708 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22041100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-11 | 2832 | keep | 0 | Apr | 2022 | 0.0019289 | 0.00048222 | Momentary | FALSE | FALSE | Not_TMED_Event | 708
YAUCO | 2022-04-11 20:33 | 2022-04-11 20:37 | 508 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22041100088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-11 | 2032 | keep | 0 | Apr | 2022 | 0.001384 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2022-04-11 20:33 | 2022-04-11 20:37 | 64 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22041100088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-11 | 256 | keep | 0 | Apr | 2022 | 0.00017436 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
ARECIBO | 2022-04-11 20:43 | 2022-04-11 22:37 | 120 | 001:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | A22041100054 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2022-04-11 | 13680 | keep | 0 | Apr | 2022 | 0.0093174 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-04-11 20:53 | 2022-04-12 20:05 | 8 | 023:12 | P | CABLE SOTERRADO AVERIADO | CONSTRUYO PROVICIONAL AEREO DEL T - 2 AL T - 3 | R22041200001 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1392 | 2022-04-11 | 11136 | keep | 0 | Apr | 2022 | 0.0075847 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-11 21:25 | 2022-04-12 02:11 | 20 | 004:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA | S22041100458 | New_Event | Cutout Failure | Include | Include | Equipment | 286 | 2022-04-11 | 5720 | keep | 0 | Apr | 2022 | 0.0038959 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-11 22:08 | 2022-04-11 23:24 | 30 | 001:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22041100057 | New_Event | Bad Weather | Include | Include | Weather | 76 | 2022-04-11 | 2280 | keep | 0 | Apr | 2022 | 0.0015529 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-04-11 22:16 | 2022-04-11 22:17 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041100099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-11 | 1352 | keep | 0 | Apr | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
CAGUAS | 2022-04-11 22:17 | 2022-04-12 06:53 | 95 | 008:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22041100230 | New_Event |  |  | Include | Wildlife | 516 | 2022-04-11 | 49020 | keep | 0 | Apr | 2022 | 0.033387 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
MAYAGÃœEZ | 2022-04-11 22:40 | 2022-04-12 09:15 | 4 | 010:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22041100119 | New_Event | Bad Weather | Include | Include | Weather | 635 | 2022-04-11 | 2540 | keep | 0 | Apr | 2022 | 0.00173 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-04-11 22:44 | 2022-04-12 11:39 | 1 | 012:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22041100466 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 775 | 2022-04-11 | 775 | keep | 0 | Apr | 2022 | 0.00052785 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-11 22:50 | 2022-04-11 23:29 | 10 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | B22041100096 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-04-11 | 390 | keep | 0 | Apr | 2022 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-11 23:30 | 2022-04-12 00:58 | 493 | 001:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A MACHETE | S22041100283 | Additional_clients | Wire Down | Include | Include | Equipment | 88 | 2022-04-11 | 43384 | keep | 0 | Apr | 2022 | 0.029549 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-11 23:30 | 2022-04-12 00:58 | 268 | 001:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A MACHETE | S22041100283 | Additional_clients | Wire Down | Include | Include | Equipment | 88 | 2022-04-11 | 23584 | keep | 0 | Apr | 2022 | 0.016063 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-04-12 00:05 | 2022-04-12 04:03 | 40 | 003:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M22041200001 | New_Event | Cutout Failure | Include | Include | Equipment | 238 | 2022-04-12 | 9520 | keep | 0 | Apr | 2022 | 0.006484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-04-12 00:44 | 2022-04-12 00:46 | 1859 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-12 | 3718 | keep | 0 | Apr | 2022 | 0.0025323 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-04-12 01:06 | 2022-04-12 01:07 | 652 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 652 | keep | 0 | Apr | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
BAYAMON | 2022-04-12 01:58 | 2022-04-12 03:56 | 143 | 001:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE DESPEJO LINEA | S22041200008 | New_Event | Wire Down | Include | Include | Equipment | 118 | 2022-04-12 | 16874 | keep | 0 | Apr | 2022 | 0.011493 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
BAYAMON | 2022-04-12 03:23 | 2022-04-12 15:37 | 500 | 012:14 | P | HERRAJE ROTO O PODRIDO | REMPLAZO DE HERRAJE EN CRUCETA | S22041200010 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 734 | 2022-04-12 | 367000 | keep | 0 | Apr | 2022 | 0.24996 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-04-12 04:18 | 2022-04-12 13:49 | 1834 | 009:31 | S | NO SE REPORTO CAUSA | SE INSPECCIONO SUBESTACION Y NO SE ENCONTRO CAUSA. SE REMPLAZARO 2 FUSIBLES EN TRANSFORMADOR SUBESTACION | B22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 571 | 2022-04-12 | 1047214 | keep | 0 | Apr | 2022 | 0.71325 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2022-04-12 04:18 | 2022-04-12 13:49 | 2324 | 009:31 | S | NO SE REPORTO CAUSA | SE INSPECCIONO SUBESTACION Y NO SE ENCONTRO CAUSA. SE REMPLAZARO 2 FUSIBLES EN TRANSFORMADOR SUBESTACION | B22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 571 | 2022-04-12 | 1327004 | keep | 0 | Apr | 2022 | 0.90382 | 0.0015829 | Sustained | FALSE | FALSE | Not_TMED_Event | 2324
VEGA BAJA | 2022-04-12 04:18 | 2022-04-12 13:49 | 1570 | 009:31 | S | NO SE REPORTO CAUSA | SE INSPECCIONO SUBESTACION Y NO SE ENCONTRO CAUSA. SE REMPLAZARO 2 FUSIBLES EN TRANSFORMADOR SUBESTACION | B22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 571 | 2022-04-12 | 896470 | keep | 0 | Apr | 2022 | 0.61058 | 0.0010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 1570
CANOVANAS | 2022-04-12 04:34 | 2022-04-12 04:35 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 4188 | keep | 0 | Apr | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
PONCE | 2022-04-12 04:43 | 2022-04-12 13:45 | 25 | 009:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22041200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 542 | 2022-04-12 | 13550 | keep | 0 | Apr | 2022 | 0.0092288 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-04-12 04:43 | 2022-04-12 10:30 | 50 | 005:47 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041200002 | New_Event | Bad Weather | Include | Include | Weather | 347 | 2022-04-12 | 17350 | keep | 0 | Apr | 2022 | 0.011817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-12 05:05 | 2022-04-12 10:40 | 3006 | 005:35 | S | PARARRAYOS DEFECTUOSO | DISPARO DE LA SUBESTACION DEBIDO A PARARRAYOS DEFECTUOSOS | M22041200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 335 | 2022-04-12 | 1007010 | keep | 0 | Apr | 2022 | 0.68587 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-04-12 05:05 | 2022-04-12 10:40 | 179 | 005:35 | S | PARARRAYOS DEFECTUOSO | DISPARO DE LA SUBESTACION DEBIDO A PARARRAYOS DEFECTUOSOS | M22041200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 335 | 2022-04-12 | 59965 | keep | 0 | Apr | 2022 | 0.040842 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
BAYAMON | 2022-04-12 05:54 | 2022-04-12 09:47 | 127 | 003:53 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22041200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2022-04-12 | 29591 | keep | 0 | Apr | 2022 | 0.020154 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
SAN JUAN | 2022-04-12 06:00 | 2022-04-12 10:22 | 16 | 004:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S22041200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-04-12 | 4192 | keep | 0 | Apr | 2022 | 0.0028552 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2022-04-12 06:02 | 2022-04-12 06:03 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO 65% DE SU CARGA POR 2604-03 | C22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
SAN JUAN | 2022-04-12 06:05 | 2022-04-12 09:56 | 50 | 003:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S22041200015 | New_Event | Wire Down | Include | Include | Equipment | 231 | 2022-04-12 | 11550 | keep | 0 | Apr | 2022 | 0.0078667 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-04-12 06:10 | 2022-04-12 09:24 | 25 | 003:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP Y AISLADOR | C22041200005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 194 | 2022-04-12 | 4850 | keep | 0 | Apr | 2022 | 0.0033033 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-04-12 06:26 | 2022-04-13 16:19 | 20 | 033:53 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO UN AEREO PROVISIONAL DE T-2 @ T-3 Y T-3 @ T-4 | R22041200001 | New_Event | UG Cable Fault | Include | Include | Equipment | 2033 | 2022-04-12 | 40660 | keep | 0 | Apr | 2022 | 0.027693 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-04-12 06:27 | 2022-04-12 06:28 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22041200051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 478 | keep | 0 | Apr | 2022 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-04-12 06:27 | 2022-04-12 06:28 | 854 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22041200051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 854 | keep | 0 | Apr | 2022 | 0.00058166 | 0.00058166 | Momentary | FALSE | FALSE | Not_TMED_Event | 854
BAYAMON | 2022-04-12 06:38 | 2022-04-12 10:53 | 66 | 004:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22041200055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 255 | 2022-04-12 | 16830 | keep | 0 | Apr | 2022 | 0.011463 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
SAN JUAN | 2022-04-12 06:45 | 2022-04-12 06:49 | 302 | 000:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DEL 1620-03 QUE ESTA LLEVANDO 85% DE LA CARGA DEL 1336-10 | S22041200020 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2022-04-12 | 1208 | keep | 0 | Apr | 2022 | 0.00082276 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
SAN JUAN | 2022-04-12 06:45 | 2022-04-12 06:49 | 36 | 000:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1620-01 | S22041200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2022-04-12 | 144 | keep | 0 | Apr | 2022 | 9.8078e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-04-12 06:45 | 2022-04-12 06:49 | 1073 | 000:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1620-01 | S22041200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2022-04-12 | 4292 | keep | 0 | Apr | 2022 | 0.0029233 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
SAN JUAN | 2022-04-12 06:52 | 2022-04-12 07:43 | 302 | 000:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AREA PARA REEMPLAZAR AISLADORES PARTIDOS SJ-220412-01 CARGA POR EL 1620-03 | S22041200020 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 51 | 2022-04-12 | 15402 | keep | 0 | Apr | 2022 | 0.01049 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
SAN JUAN | 2022-04-12 06:52 | 2022-04-12 07:43 | 36 | 000:51 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AREA PARA REEMPLAZAR AISLADORES PARTIDOS SJ-220412-01 CARGA POR EL 1620-03 | S22041200020 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 51 | 2022-04-12 | 1836 | keep | 0 | Apr | 2022 | 0.0012505 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-04-12 06:52 | 2022-04-12 07:43 | 1073 | 000:51 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AREA PARA REEMPLAZAR AISLADORES PARTIDOS SJ-220412-01 LLEVA LA CARGA DEL 1620-01 Y 85% DEL 1336-10 | S22041200020 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 51 | 2022-04-12 | 54723 | keep | 0 | Apr | 2022 | 0.037272 | 0.00073082 | Sustained | FALSE | FALSE | Not_TMED_Event | 1073
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 1798 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 5394 | keep | 0 | Apr | 2022 | 0.0036738 | 0.0012246 | Momentary | FALSE | FALSE | Not_TMED_Event | 1798
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 3309 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 9927 | keep | 0 | Apr | 2022 | 0.0067612 | 0.0022537 | Momentary | FALSE | FALSE | Not_TMED_Event | 3309
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 713 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 2139 | keep | 0 | Apr | 2022 | 0.0014569 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 1628 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 4884 | keep | 0 | Apr | 2022 | 0.0033265 | 0.0011088 | Momentary | FALSE | FALSE | Not_TMED_Event | 1628
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 1541 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 4623 | keep | 0 | Apr | 2022 | 0.0031487 | 0.0010496 | Momentary | FALSE | FALSE | Not_TMED_Event | 1541
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 307 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 921 | keep | 0 | Apr | 2022 | 0.00062729 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 1277 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 3831 | keep | 0 | Apr | 2022 | 0.0026093 | 0.00086976 | Momentary | FALSE | FALSE | Not_TMED_Event | 1277
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 1644 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 4932 | keep | 0 | Apr | 2022 | 0.0033592 | 0.0011197 | Momentary | FALSE | FALSE | Not_TMED_Event | 1644
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 1831 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 5493 | keep | 0 | Apr | 2022 | 0.0037413 | 0.0012471 | Momentary | FALSE | FALSE | Not_TMED_Event | 1831
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 1483 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 4449 | keep | 0 | Apr | 2022 | 0.0030302 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
ARECIBO | 2022-04-12 07:06 | 2022-04-12 07:09 | 89 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13700 | A22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-12 | 267 | keep | 0 | Apr | 2022 | 0.00018185 | 6.0617e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 89
BAYAMON | 2022-04-12 07:15 | 2022-04-12 16:32 | 12 | 009:17 | P | NO SE REPORTO CAUSA | 3 X 100 EN RISER | S22041200030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 557 | 2022-04-12 | 6684 | keep | 0 | Apr | 2022 | 0.0045524 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-12 07:37 | 2022-04-12 14:35 | 50 | 006:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22041200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 418 | 2022-04-12 | 20900 | keep | 0 | Apr | 2022 | 0.014235 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-12 07:39 | 2022-04-12 12:50 | 100 | 005:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041200035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-04-12 | 31100 | keep | 0 | Apr | 2022 | 0.021182 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-12 07:42 | 2022-04-12 10:59 | 45 | 003:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | R22041200007 | New_Event |  |  | Include | Wildlife | 197 | 2022-04-12 | 8865 | keep | 0 | Apr | 2022 | 0.0060379 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-04-12 07:45 | 2022-04-12 07:46 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1206-02 | S22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-04-12 07:45 | 2022-04-12 07:46 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1206-01 | S22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2022-04-12 07:45 | 2022-04-12 07:47 | 320 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22041200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-12 | 640 | keep | 0 | Apr | 2022 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
AGUADILLA | 2022-04-12 07:46 | 2022-04-12 07:47 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22041200039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 390 | keep | 0 | Apr | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
CAGUAS | 2022-04-12 07:48 | 2022-04-12 07:54 | 1261 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | C22041200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-04-12 | 7566 | keep | 0 | Apr | 2022 | 0.0051532 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
CAGUAS | 2022-04-12 07:50 | 2022-04-12 11:45 | 224 | 003:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22041200018 | New_Event |  |  | Include | Wildlife | 235 | 2022-04-12 | 52640 | keep | 0 | Apr | 2022 | 0.035853 | 0.00015257 | Sustained | FALSE | FALSE | Not_TMED_Event | 224
HUMACAO | 2022-04-12 08:05 | 2022-04-12 12:36 | 52 | 004:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA | C22041200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-04-12 | 14092 | keep | 0 | Apr | 2022 | 0.009598 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
MAYAGÃœEZ | 2022-04-12 08:25 | 2022-04-12 11:10 | 1 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22041200047 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2022-04-12 | 165 | keep | 0 | Apr | 2022 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-12 08:30 | 2022-04-12 08:31 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-12 | 1339 | keep | 0 | Apr | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-04-12 08:30 | 2022-04-12 08:31 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-12 | 470 | keep | 0 | Apr | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-04-12 08:30 | 2022-04-12 08:31 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-12 | 2483 | keep | 0 | Apr | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-04-12 08:30 | 2022-04-12 08:31 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-12 | 2190 | keep | 0 | Apr | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-04-12 08:30 | 2022-04-12 08:31 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-12 | 107 | keep | 0 | Apr | 2022 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-04-12 08:30 | 2022-04-12 08:31 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-12 | 1666 | keep | 0 | Apr | 2022 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-04-12 08:30 | 2022-04-12 08:31 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-12 | 4387 | keep | 0 | Apr | 2022 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-04-12 08:30 | 2022-04-12 08:31 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-12 | 3147 | keep | 0 | Apr | 2022 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-04-12 08:30 | 2022-04-12 08:31 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22041200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-12 | 4304 | keep | 0 | Apr | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
YAUCO | 2022-04-12 08:31 | 2022-04-12 11:06 | 15 | 002:35 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22104120002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-04-12 | 2325 | keep | 0 | Apr | 2022 | 0.0015835 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-12 08:39 | 2022-04-12 08:42 | 2000 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DEL 1619-02 | R22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-12 | 6000 | keep | 0 | Apr | 2022 | 0.0040866 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
CAGUAS | 2022-04-12 08:44 | 2022-04-12 10:34 | 1 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO NEUTRAL PRIMARIO EN BANCO DE TRANSFORMADORES | C22041200031 | New_Event | Wire Down | Include | Include | Equipment | 110 | 2022-04-12 | 110 | keep | 0 | Apr | 2022 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-12 08:48 | 2022-04-12 14:05 | 30 | 005:17 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN CORTE DE LINEA PARARRAYO CRUZADO | P22041200027 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 317 | 2022-04-12 | 9510 | keep | 0 | Apr | 2022 | 0.0064772 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-12 08:50 | 2022-04-12 09:17 | 16 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22041100108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2022-04-12 | 432 | keep | 0 | Apr | 2022 | 0.00029423 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2022-04-12 09:06 | 2022-04-12 14:38 | 28 | 005:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR PALOMA | C22041200036 | New_Event |  |  | Include | Wildlife | 332 | 2022-04-12 | 9296 | keep | 0 | Apr | 2022 | 0.0063315 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
CANOVANAS | 2022-04-12 09:09 | 2022-04-12 09:26 | 1 | 000:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN C/L Y 1 X 10 EN BANCO DE XMR'S CRUCE X AVE | R22041200052 | New_Event |  |  | Include | Wildlife | 17 | 2022-04-12 | 17 | keep | 0 | Apr | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-04-12 09:11 | 2022-04-12 17:12 | 100 | 008:01 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P22041200032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 481 | 2022-04-12 | 48100 | keep | 0 | Apr | 2022 | 0.032761 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-04-12 09:13 | 2022-04-12 13:10 | 50 | 003:57 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22041200034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2022-04-12 | 11850 | keep | 0 | Apr | 2022 | 0.008071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-12 09:19 | 2022-04-12 11:50 | 10 | 002:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C22041200039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 151 | 2022-04-12 | 1510 | keep | 0 | Apr | 2022 | 0.0010285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-04-12 09:32 | 2022-04-12 14:14 | 38 | 004:42 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO Y HOT CLAM | C22041200042 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 282 | 2022-04-12 | 10716 | keep | 0 | Apr | 2022 | 0.0072986 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
VEGA BAJA | 2022-04-12 09:39 | 2022-04-12 09:40 | 2307 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 9003-06 CON 25% DE SU CARGA POR 9003-05 | B22041200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-12 | 2307 | keep | 0 | Apr | 2022 | 0.0015713 | 0.0015713 | Momentary | FALSE | FALSE | Not_TMED_Event | 2307
VEGA BAJA | 2022-04-12 09:55 | 2022-04-12 11:20 | 2307 | 001:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 9003-06 CON 25% DE SU CARGA POR 9003-05. QUEDO FUERA. SE SECCIONALIZO ALIMENTADOR POR CONDUCTOR EN EL SUELO. 20% EN SERVICIO | B22041200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 85 | 2022-04-12 | 196095 | keep | 0 | Apr | 2022 | 0.13356 | 0.0015713 | Sustained | FALSE | FALSE | Not_TMED_Event | 2307
ARECIBO | 2022-04-12 09:56 | 2022-04-12 14:29 | 80 | 004:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | A22041200027 | New_Event |  |  | Include | Wildlife | 273 | 2022-04-12 | 21840 | keep | 0 | Apr | 2022 | 0.014875 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-12 10:05 | 2022-04-12 15:38 | 71 | 005:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR CHANGO | C22041200048 | New_Event |  |  | Include | Wildlife | 333 | 2022-04-12 | 23643 | keep | 0 | Apr | 2022 | 0.016103 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
HUMACAO | 2022-04-12 10:06 | 2022-04-12 10:46 | 20 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE CONECTORES EN BAJANTE SECUNDARIO | C22041100217 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-04-12 | 800 | keep | 0 | Apr | 2022 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-04-12 10:25 | 2022-04-12 10:42 | 1 | 000:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | P22041200042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 17 | 2022-04-12 | 17 | keep | 0 | Apr | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-04-12 10:31 | 2022-04-12 16:03 | 6 | 005:32 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R22041200070 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 332 | 2022-04-12 | 1992 | keep | 0 | Apr | 2022 | 0.0013567 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-12 10:58 | 2022-04-12 11:00 | 1106 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1529-15 QUE LLEVA 60% DEL 1346-02 | S22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-12 | 2212 | keep | 0 | Apr | 2022 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
BAYAMON | 2022-04-12 10:58 | 2022-04-12 11:00 | 1802 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1529-15 QUE LLEVA 60% DEL 1346-02 | S22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-12 | 3604 | keep | 0 | Apr | 2022 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-04-12 10:59 | 2022-04-12 11:01 | 300 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO 1620-05 Y SE CERRO POR SCADA LLEVA PARTE DEL 1206-03 | S22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-12 | 600 | keep | 0 | Apr | 2022 | 0.00040866 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-04-12 10:59 | 2022-04-12 11:01 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1620-05 Y SE CERRO POR SCADA LLEVA PARTE DEL 1206-03 | S22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-12 | 3230 | keep | 0 | Apr | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
MAYAGÃœEZ | 2022-04-12 11:03 | 2022-04-12 16:51 | 40 | 005:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA MAQUINARIA LIMPIANDO TERRENO IMPACTO POSTE Y CRUZO LINEAS MOMENTANEAMENTE | M22041200100 | New_Event |  |  | Include | Wildlife | 348 | 2022-04-12 | 13920 | keep | 0 | Apr | 2022 | 0.0094808 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-12 11:08 | 2022-04-12 13:40 | 26 | 002:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 100 KVA AVERIADO | B22041200185 | New_Event | Service Transformer Failure | Include | Include | Equipment | 152 | 2022-04-12 | 3952 | keep | 0 | Apr | 2022 | 0.0026917 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
VEGA BAJA | 2022-04-12 11:20 | 2022-04-12 15:48 | 1846 | 004:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE NORMALIZO LAS CARGAS CON BY-220412-03 | B22041200000 | New_Event | Wire Down | Include | Include | Equipment | 268 | 2022-04-12 | 494728 | keep | 0 | Apr | 2022 | 0.33696 | 0.0012573 | Sustained | FALSE | FALSE | Not_TMED_Event | 1846
PONCE | 2022-04-12 11:27 | 2022-04-12 16:05 | 1 | 004:38 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE HICIERON TRABAJOS SOTERRADOS BAJO GOI PC-220408-01A | P22041200050 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 278 | 2022-04-12 | 278 | keep | 0 | Apr | 2022 | 0.00018934 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-12 11:29 | 2022-04-12 13:01 | 80 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22041200086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2022-04-12 | 7360 | keep | 0 | Apr | 2022 | 0.0050129 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-12 11:31 | 2022-04-12 13:06 | 1 | 001:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REMPLAZO CAJA PRIMARIA AVERIADA | A22041200034 | New_Event | Cutout Failure | Include | Include | Equipment | 95 | 2022-04-12 | 95 | keep | 0 | Apr | 2022 | 6.4704e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-12 11:42 | 2022-04-12 15:03 | 244 | 003:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO DISCO Y LEVENTARON ALAMBRE PRIMARIO | C22041200068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 201 | 2022-04-12 | 49044 | keep | 0 | Apr | 2022 | 0.033404 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
BAYAMON | 2022-04-12 11:43 | 2022-04-12 17:33 | 60 | 005:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | B22041200201 | New_Event | Wire Down | Include | Include | Equipment | 350 | 2022-04-12 | 21000 | keep | 0 | Apr | 2022 | 0.014303 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-12 11:55 | 2022-04-13 14:14 | 1 | 026:19 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22041200076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1579 | 2022-04-12 | 1579 | keep | 0 | Apr | 2022 | 0.0010754 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-12 12:18 | 2022-04-12 14:34 | 80 | 002:16 | P | DESGANCHE | 1 X 100 EN C/L | R22041200080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-04-12 | 10880 | keep | 0 | Apr | 2022 | 0.0074103 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-12 12:21 | 2022-04-12 12:57 | 6 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | S22041200095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-04-12 | 216 | keep | 0 | Apr | 2022 | 0.00014712 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-12 12:22 | 2022-04-12 13:38 | 10 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22041200071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2022-04-12 | 760 | keep | 0 | Apr | 2022 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-12 12:29 | 2022-04-13 10:51 | 35 | 022:22 | P | NO SE REPORTO CAUSA | 1 X 20 Y 1 X 15 EN TRANSFORMADORES | S22041200098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1342 | 2022-04-12 | 46970 | keep | 0 | Apr | 2022 | 0.031991 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-04-12 12:30 | 2022-04-12 13:55 | 15 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22041200013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2022-04-12 | 1275 | keep | 0 | Apr | 2022 | 0.0008684 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-04-12 12:33 | 2022-04-12 13:17 | 2446 | 000:44 | T | PARARRAYOS DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR 5018-03 | P22041200064 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 44 | 2022-04-12 | 107624 | keep | 0 | Apr | 2022 | 0.073302 | 0.001666 | Sustained | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2022-04-12 12:33 | 2022-04-12 13:07 | 5069 | 000:34 | T | PARARRAYOS DEFECTUOSO | DISPARO INTERRUPTOR DEBIDO A PARARRAYO BAJANTE DE PARARRAYO | P22041200064 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 34 | 2022-04-12 | 172346 | keep | 0 | Apr | 2022 | 0.11738 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
SAN JUAN | 2022-04-12 12:34 | 2022-04-12 12:35 | 225 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO POR SCADA CARGA POR EL 1303-05 | S22041200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-12 | 225 | keep | 0 | Apr | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-12 12:34 | 2022-04-12 12:35 | 870 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO POR SCADA LLEVA EL 1303-04 | S22041200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-12 | 870 | keep | 0 | Apr | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-04-12 12:35 | 2022-04-12 20:36 | 175 | 008:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA CERRAR Y FIJAR LINEA | S22041100450 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 481 | 2022-04-12 | 84175 | keep | 0 | Apr | 2022 | 0.057331 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
VEGA BAJA | 2022-04-12 12:43 | 2022-04-12 12:57 | 4027 | 000:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV VEGA ALTA | B22041200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-04-12 | 56378 | keep | 0 | Apr | 2022 | 0.038399 | 0.0027428 | Sustained | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2022-04-12 12:43 | 2022-04-12 12:57 | 2468 | 000:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV VEGA ALTA | B22041200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-04-12 | 34552 | keep | 0 | Apr | 2022 | 0.023533 | 0.0016809 | Sustained | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2022-04-12 12:43 | 2022-04-12 12:57 | 1494 | 000:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV VEGA ALTA | B22041200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-04-12 | 20916 | keep | 0 | Apr | 2022 | 0.014246 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2022-04-12 12:43 | 2022-04-12 12:57 | 1310 | 000:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV VEGA ALTA | B22041200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-04-12 | 18340 | keep | 0 | Apr | 2022 | 0.012491 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2022-04-12 12:43 | 2022-04-12 12:57 | 215 | 000:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV VEGA ALTA | B22041200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-04-12 | 3010 | keep | 0 | Apr | 2022 | 0.0020501 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-04-12 12:43 | 2022-04-12 12:57 | 1 | 000:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV VEGA ALTA | B22041200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-04-12 | 14 | keep | 0 | Apr | 2022 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-12 12:49 | 2022-04-12 14:11 | 315 | 001:22 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SE ENCONTRO CAMION TUMBO LINEA Y POSTE SE ABRIO PUENTE Y SE CERRO INTERRUPTOR SE DEJO FUERA 1 TRANSFORMADOR 3 CLIENTES | S22041200105 | New_Event |  |  | Include | Wildlife | 82 | 2022-04-12 | 25830 | keep | 0 | Apr | 2022 | 0.017593 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-04-12 12:53 | 2022-04-12 15:34 | 77 | 002:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CAMION IMPACTO LINEA | C22041200083 | New_Event |  |  | Include | Wildlife | 161 | 2022-04-12 | 12397 | keep | 0 | Apr | 2022 | 0.0084435 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2022-04-12 12:54 | 2022-04-12 18:50 | 22 | 005:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22041100103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 356 | 2022-04-12 | 7832 | keep | 0 | Apr | 2022 | 0.0053343 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2022-04-12 12:59 | 2022-04-12 14:14 | 25 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22041200266 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-04-12 | 1875 | keep | 0 | Apr | 2022 | 0.0012771 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-04-12 13:00 | 2022-04-12 20:56 | 101 | 007:56 | P | CABLE SOTERRADO AVERIADO | SE ABRIO EN SU-9 HACIA SU-8 CON CG-220409-02A PARA CONSTRUIR AEREO PROVISIONAL TRIFASICO POR AVERIA DEL SU-D AL SU-E | C22041100211 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 476 | 2022-04-12 | 48076 | keep | 0 | Apr | 2022 | 0.032744 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-12 13:04 | 2022-04-12 15:06 | 100 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN RISER AVE CRUZO FASE | S22041200107 | New_Event |  |  | Include | Wildlife | 122 | 2022-04-12 | 12200 | keep | 0 | Apr | 2022 | 0.0083094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-12 13:15 | 2022-04-12 13:39 | 10 | 000:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | R22041200083 | New_Event |  |  | Include | Wildlife | 24 | 2022-04-12 | 240 | keep | 0 | Apr | 2022 | 0.00016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-12 13:21 | 2022-04-13 09:45 | 10 | 020:24 | P | OTRAS CAUSAS | 1 X 20 EN TRANSFORMADOR POR DETERIORO DEL FUSIBLE | A22041200041 | New_Event | Other Causes | Include | Include | Other | 1224 | 2022-04-12 | 12240 | keep | 0 | Apr | 2022 | 0.0083366 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-12 13:24 | 2022-04-12 18:07 | 12 | 004:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041200120 | New_Event | Bad Weather | Include | Include | Weather | 283 | 2022-04-12 | 3396 | keep | 0 | Apr | 2022 | 0.002313 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-12 13:32 | 2022-04-12 16:19 | 242 | 002:47 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22041200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-04-12 | 40414 | keep | 0 | Apr | 2022 | 0.027526 | 0.00016483 | Sustained | FALSE | FALSE | Not_TMED_Event | 242
BARRANQUITAS | 2022-04-12 13:35 | 2022-04-12 13:36 | 1604 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 1604 | keep | 0 | Apr | 2022 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2022-04-12 13:36 | 2022-04-12 16:14 | 371 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22041200097 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-04-12 | 58618 | keep | 0 | Apr | 2022 | 0.039924 | 0.00025269 | Sustained | FALSE | FALSE | Not_TMED_Event | 371
BAYAMON | 2022-04-12 13:41 | 2022-04-12 16:31 | 48 | 002:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S22041200126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-04-12 | 8160 | keep | 0 | Apr | 2022 | 0.0055577 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
SAN JUAN | 2022-04-12 13:46 | 2022-04-12 15:47 | 100 | 002:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA AISLADOR | S22041200129 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 121 | 2022-04-12 | 12100 | keep | 0 | Apr | 2022 | 0.0082413 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-12 13:55 | 2022-04-12 13:56 | 906 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22041200112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 906 | keep | 0 | Apr | 2022 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
AGUADILLA | 2022-04-12 14:00 | 2022-04-13 02:57 | 45 | 012:57 | P | CABLE SOTERRADO AVERIADO | SE CERRO N/O DE PM-11 A PM-10 | M22041200122 | New_Event | UG Cable Fault | Include | Include | Equipment | 777 | 2022-04-12 | 34965 | keep | 0 | Apr | 2022 | 0.023815 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-04-12 14:10 | 2022-04-12 14:26 | 12 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S22041100450 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2022-04-12 | 192 | keep | 0 | Apr | 2022 | 0.00013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-12 14:11 | 2022-04-12 22:42 | 3 | 008:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | REMPLAZO DE POSTE IMPACTADO | S22041200137 | Partial_restoration |  |  | Include | Wildlife | 511 | 2022-04-12 | 1533 | keep | 0 | Apr | 2022 | 0.0010441 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-12 14:15 | 2022-04-12 21:29 | 25 | 007:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REMPLAZO CAJA PRIMARIA | B22041200337 | New_Event | Cutout Failure | Include | Include | Equipment | 434 | 2022-04-12 | 10850 | keep | 0 | Apr | 2022 | 0.0073899 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-04-12 14:16 | 2022-04-12 16:14 | 12 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | R22041200087 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2022-04-12 | 1416 | keep | 0 | Apr | 2022 | 0.00096443 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-04-12 14:17 | 2022-04-12 14:37 | 3 | 000:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE CAJA DE TRANSFORMADOR PARA SEPARARLAS DE LA ESTRUCTURA | P22041200090 | New_Event | Cutout Failure | Include | Include | Equipment | 20 | 2022-04-12 | 60 | keep | 0 | Apr | 2022 | 4.0866e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-04-12 14:43 | 2022-04-12 15:03 | 1444 | 000:20 | T | DESGANCHE | DISPARO DEL INTERRUPTOR 6014-02 EL CUAL LLEVA LA CARGA DEL 6014-01 | M22041200161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-04-12 | 28880 | keep | 0 | Apr | 2022 | 0.01967 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-04-12 14:43 | 2022-04-12 15:03 | 3630 | 000:20 | T | DESGANCHE | DISPARO DEL INTERRUPTOR LLEVA LA CARGA DEL 6014-01 SE RETIRO BAMBUS SOBRE LAS LINEAS | M22041200161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-04-12 | 72600 | keep | 0 | Apr | 2022 | 0.049448 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-04-12 14:43 | 2022-04-12 20:30 | 40 | 005:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M20041200125 | New_Event | Bad Weather | Include | Include | Weather | 347 | 2022-04-12 | 13880 | keep | 0 | Apr | 2022 | 0.0094536 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-12 14:55 | 2022-04-12 22:20 | 82 | 007:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22041200136 | New_Event | Wire Down | Include | Include | Equipment | 445 | 2022-04-12 | 36490 | keep | 0 | Apr | 2022 | 0.024853 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
CANOVANAS | 2022-04-12 14:59 | 2022-04-12 18:21 | 39 | 003:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL, TAMBIEN REMPLAZO PARARRAYO Y CAJA 1 X 65 EN C/L Y 1 X 10 EN XMR | R22041200090 | New_Event | Cutout Failure | Include | Include | Equipment | 202 | 2022-04-12 | 7878 | keep | 0 | Apr | 2022 | 0.0053657 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
SAN JUAN | 2022-04-12 15:09 | 2022-04-12 15:12 | 614 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO | R22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-12 | 1842 | keep | 0 | Apr | 2022 | 0.0012546 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
VEGA BAJA | 2022-04-12 15:10 | 2022-04-12 15:12 | 1859 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-12 | 3718 | keep | 0 | Apr | 2022 | 0.0025323 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-04-12 15:11 | 2022-04-12 19:20 | 80 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN CONVERTIDOR | B22041200302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2022-04-12 | 19920 | keep | 0 | Apr | 2022 | 0.013567 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-04-12 15:31 | 2022-04-12 15:48 | 12 | 000:17 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041200053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2022-04-12 | 204 | keep | 0 | Apr | 2022 | 0.00013894 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-12 15:34 | 2022-04-12 16:30 | 20 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22041200082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2022-04-12 | 1120 | keep | 0 | Apr | 2022 | 0.00076283 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-12 15:36 | 2022-04-12 20:15 | 100 | 004:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22041200056 | New_Event | Bad Weather | Include | Include | Weather | 279 | 2022-04-12 | 27900 | keep | 0 | Apr | 2022 | 0.019003 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-12 15:39 | 2022-04-12 19:26 | 5 | 003:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A22041200057 | New_Event | Wire Down | Include | Include | Equipment | 227 | 2022-04-12 | 1135 | keep | 0 | Apr | 2022 | 0.00077304 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-04-12 15:52 | 2022-04-12 17:37 | 100 | 001:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22041200060 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2022-04-12 | 10500 | keep | 0 | Apr | 2022 | 0.0071515 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-12 15:57 | 2022-04-12 17:51 | 100 | 001:54 | P | DESGANCHE | 1 X 65 EN C/L | R22041200096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-04-12 | 11400 | keep | 0 | Apr | 2022 | 0.0077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-12 15:57 | 2022-04-12 17:00 | 8 | 001:03 | P | DESGANCHE | DESGANCHE Y SE REPARO SECUNDARIA | B22041200199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-04-12 | 504 | keep | 0 | Apr | 2022 | 0.00034327 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-12 16:01 | 2022-04-12 16:53 | 1 | 000:52 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22041200145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-04-12 | 52 | keep | 0 | Apr | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-12 16:01 | 2022-04-12 18:50 | 8 | 002:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA AVE CRUZO LINEAS | A22041200061 | New_Event |  |  | Include | Wildlife | 169 | 2022-04-12 | 1352 | keep | 0 | Apr | 2022 | 0.00092084 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-12 16:03 | 2022-04-13 19:42 | 10 | 027:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50KVA | S22041200160 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1659 | 2022-04-12 | 16590 | keep | 0 | Apr | 2022 | 0.011299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-12 16:19 | 2022-04-12 18:36 | 45 | 002:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO REPORTO CAUSA | A22041200066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-04-12 | 6165 | keep | 0 | Apr | 2022 | 0.004199 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-04-12 16:20 | 2022-04-12 18:52 | 4 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA PRIMARIA DEL TRANSFORMADOR | C22041200148 | New_Event | Wire Down | Include | Include | Equipment | 152 | 2022-04-12 | 608 | keep | 0 | Apr | 2022 | 0.00041411 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-04-12 16:25 | 2022-04-12 18:19 | 20 | 001:54 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA INFORMA REQUIERE DESGANCHE MASIVO | A22041200069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-04-12 | 2280 | keep | 0 | Apr | 2022 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-12 16:28 | 2022-04-12 22:07 | 110 | 005:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN TRONCAL DE ALIMENTADOR | A22041200070 | New_Event | Wire Down | Include | Include | Equipment | 339 | 2022-04-12 | 37290 | keep | 0 | Apr | 2022 | 0.025398 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
SAN JUAN | 2022-04-12 16:42 | 2022-04-12 20:29 | 1 | 003:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L REMPLAZO PIN POLE TOP | R22041200100 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 227 | 2022-04-12 | 227 | keep | 0 | Apr | 2022 | 0.00015461 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-12 16:46 | 2022-04-12 19:16 | 60 | 002:30 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO Y REMPLAZO CAJA QUEMADA | R22041200101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-04-12 | 9000 | keep | 0 | Apr | 2022 | 0.0061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-04-12 16:58 | 2022-04-12 21:15 | 20 | 004:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-04-12 | 5140 | keep | 0 | Apr | 2022 | 0.0035008 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-04-12 17:12 | 2022-04-12 21:07 | 40 | 003:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO ENCONTRO CAUSA | M22041200191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2022-04-12 | 9400 | keep | 0 | Apr | 2022 | 0.0064023 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-12 17:13 | 2022-04-12 17:24 | 1 | 000:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | C22041200154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-04-12 | 11 | keep | 0 | Apr | 2022 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-12 17:41 | 2022-04-12 19:23 | 184 | 001:42 | P | DESGANCHE | 1 X 40 Y 1 X 65 EN CORTES DE LINEA SE RETIRO RAMA DE LA LINEA | C22041200156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-04-12 | 18768 | keep | 0 | Apr | 2022 | 0.012783 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
VEGA BAJA | 2022-04-12 17:58 | 2022-04-12 17:59 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 1310 | keep | 0 | Apr | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-04-12 17:59 | 2022-04-13 12:38 | 50 | 018:39 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S22041200180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1119 | 2022-04-12 | 55950 | keep | 0 | Apr | 2022 | 0.038107 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-12 18:03 | 2022-04-12 18:04 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22041200203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-12 | 863 | keep | 0 | Apr | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
PONCE | 2022-04-12 18:22 | 2022-04-12 18:58 | 50 | 000:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR AVE | P22041200116 | New_Event |  |  | Include | Wildlife | 36 | 2022-04-12 | 1800 | keep | 0 | Apr | 2022 | 0.001226 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-12 18:41 | 2022-04-12 20:48 | 20 | 002:07 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 25 EN C/L REPARO TERMINACION EN T - 57 | R22041200110 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 127 | 2022-04-12 | 2540 | keep | 0 | Apr | 2022 | 0.00173 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-04-12 18:45 | 2022-04-12 18:56 | 1 | 000:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 SMU 20 DE 20 AMP. AISLADOR ROTO | C22041200165 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 11 | 2022-04-12 | 11 | keep | 0 | Apr | 2022 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-12 18:59 | 2022-04-12 22:44 | 1444 | 003:45 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE PATRULLO Y SE ENCONTRO BAMBUAS SOBRE LINEAS SE REMOVIERON Y SE PROCEDIO A CERRAR POR SCADA Y QUEDO EN SERVICIO CARGA POR 6014-02 | M22041200228 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-04-12 | 324900 | keep | 0 | Apr | 2022 | 0.22129 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-12 18:59 | 2022-04-12 22:44 | 3630 | 003:45 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE PATRULLO Y SE ENCONTRO BAMBUAS SOBRE LINEAS SE REMOVIERON Y SE PROCEDIO A CERRAR POR SCADA Y QUEDO EN SERVICIO LLEVA 6014-01 | M22041200228 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-04-12 | 816750 | keep | 0 | Apr | 2022 | 0.55628 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-12 19:03 | 2022-04-12 20:34 | 80 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO IDENTIFICO CAUSA | A22041200096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2022-04-12 | 7280 | keep | 0 | Apr | 2022 | 0.0049584 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-04-12 19:30 | 2022-04-12 22:59 | 90 | 003:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C22041200179 | New_Event | Wire Down | Include | Include | Equipment | 209 | 2022-04-12 | 18810 | keep | 0 | Apr | 2022 | 0.012811 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2022-04-12 19:41 | 2022-04-13 10:14 | 15 | 014:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REEMPLAZO CAJA PRIMARIA | R22041200117 | New_Event | Cutout Failure | Include | Include | Equipment | 873 | 2022-04-12 | 13095 | keep | 0 | Apr | 2022 | 0.0089189 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-04-12 19:44 | 2022-04-13 08:26 | 20 | 012:42 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | CERRO N/O EN T - 3 PISTOLA AVERIADA EN EL T - 1 | C22041200185 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 762 | 2022-04-12 | 15240 | keep | 0 | Apr | 2022 | 0.01038 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-04-12 20:33 | 2022-04-13 10:45 | 205 | 014:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA AVERIADA Y SE CERRO CORTE DE LINEA | P22041200127 | New_Event | Wire Down | Include | Include | Equipment | 852 | 2022-04-12 | 174660 | keep | 0 | Apr | 2022 | 0.11896 | 0.00013962 | Sustained | FALSE | FALSE | Not_TMED_Event | 205
BAYAMON | 2022-04-12 20:39 | 2022-04-12 23:50 | 649 | 003:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ESTABLECE GOI PARA CERRAR PUENTE ABIERTO DE TRONCAL BY-220412-05 | B22041200349 | New_Event | Wire Down | Include | Include | Equipment | 191 | 2022-04-12 | 123959 | keep | 0 | Apr | 2022 | 0.084428 | 0.00044203 | Sustained | FALSE | FALSE | Not_TMED_Event | 649
CAGUAS | 2022-04-12 20:40 | 2022-04-13 09:46 | 54 | 013:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L FIJO CONDUCTOR | C22041200201 | New_Event | Wire Down | Include | Include | Equipment | 786 | 2022-04-12 | 42444 | keep | 0 | Apr | 2022 | 0.028908 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
GUAYAMA | 2022-04-12 21:15 | 2022-04-13 09:30 | 5 | 012:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | P22041200131 | New_Event | Cutout Failure | Include | Include | Equipment | 735 | 2022-04-12 | 3675 | keep | 0 | Apr | 2022 | 0.002503 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-04-12 22:07 | 2022-04-12 23:25 | 425 | 001:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE ABIERTO EN TRONCAL DEL ALIMENTADOR | A22041200112 | Additional_clients | Wire Down | Include | Include | Equipment | 78 | 2022-04-12 | 33150 | keep | 0 | Apr | 2022 | 0.022578 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-12 22:20 | 2022-04-13 02:05 | 1253 | 003:45 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR MANUAL PARA REPARAR LINEA PRIMARIA ROTA LLEVA CARGA DE 6010-02 | M22041200136 | Additional_clients | Wire Down | Include | Include | Equipment | 225 | 2022-04-12 | 281925 | keep | 0 | Apr | 2022 | 0.19202 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-12 22:20 | 2022-04-13 02:05 | 1266 | 003:45 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR MANUAL PARA REPARAR LINEA PRIMARIA ROTA CARGA POR 6010-01 | M22041200136 | New_Event | Wire Down | Include | Include | Equipment | 225 | 2022-04-12 | 284850 | keep | 0 | Apr | 2022 | 0.19401 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
BAYAMON | 2022-04-12 22:29 | 2022-04-12 23:59 | 70 | 001:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | B22041200380 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2022-04-12 | 6300 | keep | 0 | Apr | 2022 | 0.0042909 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-04-12 22:51 | 2022-04-12 23:20 | 13 | 000:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO BAJANTE ABIERTO | B22041200362 | New_Event | Wire Down | Include | Include | Equipment | 29 | 2022-04-12 | 377 | keep | 0 | Apr | 2022 | 0.00025677 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-04-12 23:50 | 2022-04-13 01:00 | 1834 | 001:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ESTABLECE GOI PARA CERRAR PUENTE ABIERTO DE TRONCAL BY-220412-05 | B22041200349 | Additional_clients | Wire Down | Include | Include | Equipment | 70 | 2022-04-12 | 128380 | keep | 0 | Apr | 2022 | 0.087439 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-12 23:56 | 2022-04-13 10:30 | 150 | 010:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22041200286 | New_Event |  |  | Include | Wildlife | 634 | 2022-04-12 | 95100 | keep | 0 | Apr | 2022 | 0.064772 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-04-13 00:02 | 2022-04-13 10:00 | 10 | 009:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | M22041300002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 598 | 2022-04-13 | 5980 | keep | 0 | Apr | 2022 | 0.004073 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-13 02:38 | 2022-04-13 04:35 | 450 | 001:57 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO LLEVA EL 1706-03 | B22041300008 | New_Event | Switch Failure | Include | Include | Equipment | 117 | 2022-04-13 | 52650 | keep | 0 | Apr | 2022 | 0.03586 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
BAYAMON | 2022-04-13 02:38 | 2022-04-13 04:35 | 221 | 001:57 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO CARGA POR EL 1706-02 | B22041300008 | New_Event | Switch Failure | Include | Include | Equipment | 117 | 2022-04-13 | 25857 | keep | 0 | Apr | 2022 | 0.017611 | 0.00015052 | Sustained | FALSE | FALSE | Not_TMED_Event | 221
CANOVANAS | 2022-04-13 02:42 | 2022-04-13 02:43 | 4188 | 000:01 | T | DESGANCHE | RECIERRE | R22041300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-13 | 4188 | keep | 0 | Apr | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-04-13 02:43 | 2022-04-13 16:28 | 71 | 013:45 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R22041300045 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 825 | 2022-04-13 | 58575 | keep | 0 | Apr | 2022 | 0.039895 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
ARECIBO | 2022-04-13 03:45 | 2022-04-13 03:46 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 308 | keep | 0 | Apr | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2022-04-13 03:54 | 2022-04-13 08:30 | 8 | 004:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN CAJA DE TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | A22041300001 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2022-04-13 | 2208 | keep | 0 | Apr | 2022 | 0.0015039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-13 04:35 | 2022-04-13 05:22 | 1382 | 000:47 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE 1706-02 SE ESTABLECE GOI PARA REMPLAZO DE MACHETE QUEMADO. LLEVA 1706-03 | B22041300008 | Additional_clients | Switch Failure | Include | Include | Equipment | 47 | 2022-04-13 | 64954 | keep | 0 | Apr | 2022 | 0.04424 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-13 04:35 | 2022-04-13 05:22 | 663 | 000:47 | T | DESCONECTIVO DEFECTUOSO | DISPARO DEL 1706-02 SE ESTABLECE GOI PARA REMPLAZO DE MACHETE QUEMADO LLEVA 1706-03 | B22041300008 | Additional_clients | Switch Failure | Include | Include | Equipment | 47 | 2022-04-13 | 31161 | keep | 0 | Apr | 2022 | 0.021224 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-13 05:41 | 2022-04-13 11:36 | 80 | 005:55 | P | DESGANCHE | 1 X 100 EN SU SE REALIZO DESGANCHE | B22041300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2022-04-13 | 28400 | keep | 0 | Apr | 2022 | 0.019343 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-13 05:51 | 2022-04-13 10:04 | 30 | 004:13 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22041300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2022-04-13 | 7590 | keep | 0 | Apr | 2022 | 0.0051695 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-13 06:21 | 2022-04-13 06:22 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1713-05 LLEVANDO 95% DEL 1717-02 | B22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 5961 | keep | 0 | Apr | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-04-13 06:21 | 2022-04-13 06:22 | 865 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1713-05 LLEVANDO 95% DEL 1717-02 | B22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 865 | keep | 0 | Apr | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
SAN JUAN | 2022-04-13 06:34 | 2022-04-13 06:35 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-04 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1681 | keep | 0 | Apr | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-13 06:34 | 2022-04-13 06:35 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-04 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1598 | keep | 0 | Apr | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-04-13 06:48 | 2022-04-13 16:53 | 10 | 010:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22041300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 605 | 2022-04-13 | 6050 | keep | 0 | Apr | 2022 | 0.0041206 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-13 06:56 | 2022-04-13 07:48 | 2126 | 000:52 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AISLADOR ROTO | C22041300008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 52 | 2022-04-13 | 110552 | keep | 0 | Apr | 2022 | 0.075296 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
CAGUAS | 2022-04-13 07:28 | 2022-04-13 09:47 | 100 | 002:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22041300024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-04-13 | 13900 | keep | 0 | Apr | 2022 | 0.0094672 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-13 07:30 | 2022-04-13 21:30 | 12 | 014:00 | P | SOBRECARGA | 1 X 30 EN TRANSFORMADOR INFORMA EL JOURNEYMAN QUE PARECE QUE LE HABIAN REMPLAZADO FUSIBLE Y LE HABIAN PUESTO UNO MUY PEQUEÃ‘O DE 8 AMPERES | M22041300015 | New_Event | Trip Due To Overload | Include | Include | Other | 840 | 2022-04-13 | 10080 | keep | 0 | Apr | 2022 | 0.0068654 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-04-13 07:41 | 2022-04-13 11:28 | 12 | 003:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R22041300002 | New_Event |  |  | Include | Wildlife | 227 | 2022-04-13 | 2724 | keep | 0 | Apr | 2022 | 0.0018553 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-04-13 07:44 | 2022-04-13 07:45 | 676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5300 | C22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-13 | 676 | keep | 0 | Apr | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2022-04-13 07:44 | 2022-04-13 07:45 | 2873 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5300 | C22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-13 | 2873 | keep | 0 | Apr | 2022 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2022-04-13 07:44 | 2022-04-13 07:45 | 3902 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5300 | C22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-13 | 3902 | keep | 0 | Apr | 2022 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
BAYAMON | 2022-04-13 07:46 | 2022-04-13 13:30 | 12 | 005:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22041300053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 344 | 2022-04-13 | 4128 | keep | 0 | Apr | 2022 | 0.0028116 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-13 07:46 | 2022-04-13 12:57 | 50 | 005:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22041300056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 311 | 2022-04-13 | 15550 | keep | 0 | Apr | 2022 | 0.010591 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-04-13 07:48 | 2022-04-13 09:50 | 1115 | 002:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR | C22041300008 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 122 | 2022-04-13 | 136030 | keep | 0 | Apr | 2022 | 0.092649 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-13 07:48 | 2022-04-16 14:50 | 40 | 079:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE CLIENTE FUERA DESDE EL DIA 13 SE VERIFICO EN OMS | M22041300039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4742 | 2022-04-13 | 189680 | keep | 0 | Apr | 2022 | 0.12919 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-04-13 07:48 | 2022-04-13 09:57 | 25 | 002:09 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE DE BAMBUS | A22041300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-04-13 | 3225 | keep | 0 | Apr | 2022 | 0.0021965 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-04-13 07:49 | 2022-04-13 10:12 | 112 | 002:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER CRUCE POR CHANGO | R22041300004 | New_Event |  |  | Include | Wildlife | 143 | 2022-04-13 | 16016 | keep | 0 | Apr | 2022 | 0.010908 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
SAN JUAN | 2022-04-13 07:57 | 2022-04-13 07:58 | 828 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 60% POR EL 1206-04 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 828 | keep | 0 | Apr | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-04-13 07:57 | 2022-04-13 07:58 | 1977 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 40% POR EL 1206-04 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1977 | keep | 0 | Apr | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-04-13 07:57 | 2022-04-13 07:58 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 20% DEL 1303-02 40% DEL 1204-04 60% DEL 1204-03 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1799 | keep | 0 | Apr | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-04-13 07:57 | 2022-04-13 07:58 | 487 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1206-04 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 487 | keep | 0 | Apr | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
CANOVANAS | 2022-04-13 08:03 | 2022-04-13 08:04 | 1380 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22041300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1380 | keep | 0 | Apr | 2022 | 0.00093991 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
MAYAGÃœEZ | 2022-04-13 08:12 | 2022-04-13 20:49 | 3 | 012:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA FUERTE VIENTO | M22041300020 | New_Event | Bad Weather | Include | Include | Weather | 757 | 2022-04-13 | 2271 | keep | 0 | Apr | 2022 | 0.0015468 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-04-13 08:23 | 2022-04-13 10:50 | 100 | 002:27 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22041300017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-04-13 | 14700 | keep | 0 | Apr | 2022 | 0.010012 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-13 08:37 | 2022-04-13 12:45 | 40 | 004:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REMPLAZO AISLADOR | B22041300065 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 248 | 2022-04-13 | 9920 | keep | 0 | Apr | 2022 | 0.0067565 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-04-13 08:41 | 2022-04-13 10:53 | 10 | 002:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C22041300051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2022-04-13 | 1320 | keep | 0 | Apr | 2022 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-13 08:50 | 2022-04-13 08:51 | 676 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 676 | keep | 0 | Apr | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
BAYAMON | 2022-04-13 09:02 | 2022-04-13 09:03 | 3597 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | B22041300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-13 | 3597 | keep | 0 | Apr | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
CAGUAS | 2022-04-13 09:02 | 2022-04-13 11:57 | 20 | 002:55 | P | DESGANCHE | 1 X 15 EN C/L | C22041300064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-04-13 | 3500 | keep | 0 | Apr | 2022 | 0.0023838 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-04-13 09:03 | 2022-04-13 15:56 | 45 | 006:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X65 EN C/L (POR AVE EN LA LINEA) | B22041300118 | 1st_after_momentary |  |  | Include | Wildlife | 413 | 2022-04-13 | 18585 | keep | 0 | Apr | 2022 | 0.012658 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-04-13 09:08 | 2022-04-13 13:07 | 20 | 003:59 | P | DESGANCHE | 1 X30 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE LEVANTO CONDUCTOR | B22041300072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-04-13 | 4780 | keep | 0 | Apr | 2022 | 0.0032556 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-04-13 09:20 | 2022-04-13 17:35 | 1 | 008:15 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CONTINUAN TRABAJOS MANANA EN EL SOTERRADO BAJO GOI PC-220408-01A | P22041300015 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 495 | 2022-04-13 | 495 | keep | 0 | Apr | 2022 | 0.00033714 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-04-13 09:25 | 2022-04-13 12:41 | 99 | 003:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R22041300013 | New_Event | Cutout Failure | Include | Include | Equipment | 196 | 2022-04-13 | 19404 | keep | 0 | Apr | 2022 | 0.013216 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
VEGA BAJA | 2022-04-13 09:30 | 2022-04-13 10:04 | 10 | 000:34 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA SECCIONALIZAR POSTE SECUNDARIO PARTIDO 2 CLIENTES FUERA | B22041300048 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 34 | 2022-04-13 | 340 | keep | 0 | Apr | 2022 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-13 09:31 | 2022-04-13 12:25 | 1 | 002:54 | P | DESGANCHE | 2 X 30 EN RISER SE REALIZO DESGANCHE | B22041300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-04-13 | 174 | keep | 0 | Apr | 2022 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-13 09:31 | 2022-04-13 16:39 | 5 | 007:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE FIJO BAJANTE SECUNDARIO & SE INSTALO HOT CLAMP | B22041300077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 428 | 2022-04-13 | 2140 | keep | 0 | Apr | 2022 | 0.0014575 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-04-13 09:41 | 2022-04-13 09:42 | 1835 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041300077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1835 | keep | 0 | Apr | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2022-04-13 09:42 | 2022-04-13 15:15 | 50 | 005:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22041300123 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 333 | 2022-04-13 | 16650 | keep | 0 | Apr | 2022 | 0.01134 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-13 09:43 | 2022-04-13 14:10 | 100 | 004:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE RETEZO LINEA ARREADAS | M22041300029 | New_Event | Wire Down | Include | Include | Equipment | 267 | 2022-04-13 | 26700 | keep | 0 | Apr | 2022 | 0.018185 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-13 09:46 | 2022-04-13 10:45 | 1 | 000:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R22041300015 | New_Event | Cutout Failure | Include | Include | Equipment | 59 | 2022-04-13 | 59 | keep | 0 | Apr | 2022 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-13 09:59 | 2022-04-13 23:41 | 6 | 013:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO DE LINEA A CAJA | B22041300000 | New_Event | Wire Down | Include | Include | Equipment | 822 | 2022-04-13 | 4932 | keep | 0 | Apr | 2022 | 0.0033592 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-04-13 10:02 | 2022-04-13 10:21 | 4369 | 000:19 | T | CABLE SOTERRADO AVERIADO | SE ABRIO EL BKR PARA PERSONAL PODER REALIZAR OPERACIONES EN EL SU - D LLEVA 20% DEL 3604-06 | C22041300081 | New_Event | UG Cable Fault | Include | Include | Equipment | 19 | 2022-04-13 | 83011 | keep | 0 | Apr | 2022 | 0.056538 | 0.0029757 | Sustained | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2022-04-13 10:02 | 2022-04-13 10:21 | 581 | 000:19 | P | CABLE SOTERRADO AVERIADO | SE ABRIO EL BKR 3010-01 PARA PERSONAL PODER REALIZAR OPERACIONES EN EL SU - D | C22041300081 | New_Event | UG Cable Fault | Include | Include | Equipment | 19 | 2022-04-13 | 11039 | keep | 0 | Apr | 2022 | 0.0075186 | 0.00039572 | Sustained | FALSE | FALSE | Not_TMED_Event | 581
SAN JUAN | 2022-04-13 10:07 | 2022-04-13 11:19 | 10 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22041200157 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2022-04-13 | 720 | keep | 0 | Apr | 2022 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-13 10:12 | 2022-04-13 12:17 | 281 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-04-13 | 35125 | keep | 0 | Apr | 2022 | 0.023923 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-04-13 10:12 | 2022-04-13 12:17 | 1252 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-04-13 | 156500 | keep | 0 | Apr | 2022 | 0.10659 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-04-13 10:12 | 2022-04-13 12:17 | 595 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-04-13 | 74375 | keep | 0 | Apr | 2022 | 0.050656 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-04-13 10:12 | 2022-04-13 12:17 | 51 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-04-13 | 6375 | keep | 0 | Apr | 2022 | 0.004342 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-04-13 10:12 | 2022-04-13 12:17 | 721 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-04-13 | 90125 | keep | 0 | Apr | 2022 | 0.061384 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-04-13 10:13 | 2022-04-13 11:43 | 1382 | 001:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-04-13 | 124380 | keep | 0 | Apr | 2022 | 0.084715 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-04-13 10:13 | 2022-04-13 11:43 | 654 | 001:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22041300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-04-13 | 58860 | keep | 0 | Apr | 2022 | 0.040089 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
BAYAMON | 2022-04-13 10:31 | 2022-04-13 15:22 | 5 | 004:51 | P | PARARRAYOS DEFECTUOSO | 1X15 EN XMR & SE REMPLAZO PARARRAYO | B22041300089 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 291 | 2022-04-13 | 1455 | keep | 0 | Apr | 2022 | 0.00099099 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-04-13 10:33 | 2022-04-13 11:16 | 1 | 000:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22041300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 43 | 2022-04-13 | 43 | keep | 0 | Apr | 2022 | 2.9287e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-13 10:39 | 2022-04-13 13:18 | 30 | 002:39 | P | DESGANCHE | 1 X 30 EN C/L | C22041300101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-04-13 | 4770 | keep | 0 | Apr | 2022 | 0.0032488 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-13 10:40 | 2022-04-13 11:56 | 15 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTES SECUNDARIOS | A22041200084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2022-04-13 | 1140 | keep | 0 | Apr | 2022 | 0.00077645 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-13 10:50 | 2022-04-13 10:51 | 3046 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR EN SERVICIO | R22041300019 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-13 | 3046 | keep | 0 | Apr | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-04-13 10:51 | 2022-04-13 13:00 | 69 | 002:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 50 EN CORTES DE LINEA CRUCE POR CHANGO Y SE REEMPLAZO PORTAFUSIBLE | R22041300022 | 1st_after_momentary |  |  | Include | Wildlife | 129 | 2022-04-13 | 8901 | keep | 0 | Apr | 2022 | 0.0060624 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
CAGUAS | 2022-04-13 10:54 | 2022-04-13 10:55 | 40 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22041300047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 40 | keep | 0 | Apr | 2022 | 2.7244e-05 | 2.7244e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-13 10:56 | 2022-04-13 10:57 | 828 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 60% DE LA CARGA POR EL 1206-04 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 828 | keep | 0 | Apr | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-04-13 10:56 | 2022-04-13 10:57 | 1977 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 40% DE LA CARGA POR EL 1206-04 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1977 | keep | 0 | Apr | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-04-13 10:56 | 2022-04-13 10:57 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 20% DEL 1303-02 40% 1204-04 60% 1204-03 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1799 | keep | 0 | Apr | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-04-13 10:56 | 2022-04-13 10:57 | 487 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 20% DE LA CARGA POR EL 1206-04 | S22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 487 | keep | 0 | Apr | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-04-13 11:00 | 2022-04-13 12:55 | 10 | 001:55 | P | SECUNDARIA/DESGANCHE | SE REEMPLAZARON CONECTORES SE RELIZO DESGANCHE Y SE REPARO SECUNDARIA | S22041300041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 115 | 2022-04-13 | 1150 | keep | 0 | Apr | 2022 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-13 11:32 | 2022-04-13 12:54 | 1 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22041300118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-04-13 | 82 | keep | 0 | Apr | 2022 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-13 11:32 | 2022-04-13 19:25 | 1 | 007:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 15 EN BANCO DE TRANSFORMADORES Y 3 X 20 EN RISER IGUANA CRUZO FASES A TIERRA | M22041300061 | New_Event |  |  | Include | Wildlife | 473 | 2022-04-13 | 473 | keep | 0 | Apr | 2022 | 0.00032216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-13 11:41 | 2022-04-13 12:25 | 7 | 000:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO XMR PARA LEVANTAR NEUTRAL PRIMARIO | C22041300121 | New_Event | Wire Down | Include | Include | Equipment | 44 | 2022-04-13 | 308 | keep | 0 | Apr | 2022 | 0.00020978 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-04-13 11:51 | 2022-04-13 15:30 | 60 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R22041300028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-04-13 | 13140 | keep | 0 | Apr | 2022 | 0.0089496 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-04-13 11:57 | 2022-04-13 11:58 | 1 | 000:01 | P | NO SE REPORTO CAUSA | 2 X 30 EN RISER NO CAUSA | C22041300021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-04-13 11:59 | 2022-04-13 22:31 | 400 | 010:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M22041300068 | New_Event | Cutout Failure | Include | Include | Equipment | 632 | 2022-04-13 | 252800 | keep | 0 | Apr | 2022 | 0.17218 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CAGUAS | 2022-04-13 12:17 | 2022-04-13 15:00 | 5 | 002:43 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO Y REPARO SECUNDARIA | C22041300126 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 163 | 2022-04-13 | 815 | keep | 0 | Apr | 2022 | 0.00055509 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-04-13 12:26 | 2022-04-13 14:00 | 1 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A CAJA DE MONTURA TRIFASICA | P22041300026 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2022-04-13 | 94 | keep | 0 | Apr | 2022 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-13 12:27 | 2022-04-13 13:30 | 7 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 20 Y 1 X 100 SU-7 | S22041300051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-04-13 | 441 | keep | 0 | Apr | 2022 | 0.00030036 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-04-13 12:32 | 2022-04-13 14:27 | 25 | 001:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 30 EN CORTE DE LINEA SE REEMPLAZARON DOS AISLADORES | A22041300045 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 115 | 2022-04-13 | 2875 | keep | 0 | Apr | 2022 | 0.0019581 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-04-13 12:39 | 2022-04-13 21:07 | 20 | 008:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A22041300047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 508 | 2022-04-13 | 10160 | keep | 0 | Apr | 2022 | 0.0069199 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-13 12:46 | 2022-04-13 14:29 | 100 | 001:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN C/L FUERTES VIENTOS | C22041300132 | New_Event | Bad Weather | Include | Include | Weather | 103 | 2022-04-13 | 10300 | keep | 0 | Apr | 2022 | 0.0070153 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-04-13 12:48 | 2022-04-13 13:52 | 1340 | 001:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE SEPARO LINEA PRIMARIA CRUZADA | P22041300029 | New_Event | Wire Down | Include | Include | Equipment | 64 | 2022-04-13 | 85760 | keep | 0 | Apr | 2022 | 0.058411 | 0.00091267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1340
HUMACAO | 2022-04-13 12:49 | 2022-04-13 15:54 | 100 | 003:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REMPLAZO CAJA AVERIADA | C22041300133 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2022-04-13 | 18500 | keep | 0 | Apr | 2022 | 0.0126 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-13 13:01 | 2022-04-13 18:47 | 90 | 005:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | A22041300049 | New_Event | Bad Weather | Include | Include | Weather | 346 | 2022-04-13 | 31140 | keep | 0 | Apr | 2022 | 0.021209 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-04-13 13:11 | 2022-04-13 17:08 | 8 | 003:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE X AVE | C22041300140 | New_Event |  |  | Include | Wildlife | 237 | 2022-04-13 | 1896 | keep | 0 | Apr | 2022 | 0.0012914 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-13 13:11 | 2022-04-13 14:14 | 3 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE Y LINEA SECUNDARIA | C22041300138 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2022-04-13 | 189 | keep | 0 | Apr | 2022 | 0.00012873 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-04-13 13:15 | 2022-04-13 14:14 | 1 | 000:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO DOS CAJAS PRIMARIAS | A22041300052 | New_Event | Cutout Failure | Include | Include | Equipment | 59 | 2022-04-13 | 59 | keep | 0 | Apr | 2022 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-13 13:18 | 2022-04-13 14:40 | 10 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22041300055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-04-13 | 820 | keep | 0 | Apr | 2022 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-04-13 13:22 | 2022-04-13 13:47 | 12 | 000:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ENREDADERA | R22041300035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2022-04-13 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-04-13 13:25 | 2022-04-13 18:49 | 1 | 005:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN XMR SE REPARO SECUNDARIA | R22041300036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 324 | 2022-04-13 | 324 | keep | 0 | Apr | 2022 | 0.00022067 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-04-13 13:28 | 2022-04-13 17:07 | 6 | 003:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | A22041300056 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2022-04-13 | 1314 | keep | 0 | Apr | 2022 | 0.00089496 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-04-13 13:31 | 2022-04-13 15:19 | 60 | 001:48 | P | DESGANCHE | 1 X 65 EN C/L | C22041300141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-04-13 | 6480 | keep | 0 | Apr | 2022 | 0.0044135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-13 13:33 | 2022-04-13 20:17 | 1 | 006:44 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR REQUIERE DESGANCHE | A22041300058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 404 | 2022-04-13 | 404 | keep | 0 | Apr | 2022 | 0.00027516 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-13 13:42 | 2022-04-14 10:17 | 50 | 020:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | M22041300106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1235 | 2022-04-13 | 61750 | keep | 0 | Apr | 2022 | 0.042058 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-04-13 13:45 | 2022-04-13 16:20 | 8 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARARON CONEXIONES SECUNDARIAS | A22041300059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2022-04-13 | 1240 | keep | 0 | Apr | 2022 | 0.00084456 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-04-13 13:47 | 2022-04-16 23:22 | 25 | 081:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EVENTO DEL DIA 4/13 | M22041300107 | New_Event | Cutout Failure | Include | Include | Equipment | 4895 | 2022-04-13 | 122375 | keep | 0 | Apr | 2022 | 0.083349 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-13 13:47 | 2022-04-13 18:15 | 100 | 004:28 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | M22041300107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 268 | 2022-04-13 | 26800 | keep | 0 | Apr | 2022 | 0.018253 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-04-13 13:47 | 2022-04-13 13:48 | 776 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | B22041300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-13 | 776 | keep | 0 | Apr | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2022-04-13 13:48 | 2022-04-13 18:44 | 200 | 004:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN C/L & SE CERRO PUENTE PRIMARIO | B22041300145 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 296 | 2022-04-13 | 59200 | keep | 0 | Apr | 2022 | 0.040321 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-04-13 13:50 | 2022-04-13 19:43 | 100 | 005:53 | P | DESGANCHE | 1 X 140 EN C/L DESGANCHE | R22041300038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2022-04-13 | 35300 | keep | 0 | Apr | 2022 | 0.024043 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-13 13:53 | 2022-04-13 13:54 | 424 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 424 | keep | 0 | Apr | 2022 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
MAYAGÃœEZ | 2022-04-13 14:04 | 2022-04-13 14:05 | 1268 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041300116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1268 | keep | 0 | Apr | 2022 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2022-04-13 14:07 | 2022-04-13 14:08 | 637 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | M22041300119 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-13 | 637 | keep | 0 | Apr | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-04-13 14:07 | 2022-04-13 14:08 | 1491 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR 6703-02 QUE ESTA LLEVANDO LA CARGA DEL 6703-03 | M22041300119 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-13 | 1491 | keep | 0 | Apr | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-04-13 14:08 | 2022-04-13 19:05 | 40 | 004:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22041300125 | 1st_after_momentary |  |  | Include | Wildlife | 297 | 2022-04-13 | 11880 | keep | 0 | Apr | 2022 | 0.0080914 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-13 14:11 | 2022-04-13 17:15 | 80 | 003:04 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22041300122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-04-13 | 14720 | keep | 0 | Apr | 2022 | 0.010026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-13 14:17 | 2022-04-13 14:18 | 1268 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041300127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1268 | keep | 0 | Apr | 2022 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
VEGA BAJA | 2022-04-13 14:20 | 2022-04-13 14:22 | 19 | 000:02 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR PARA ABRIR PUENTE Y SECCIONALIZAR POSTE SECUNDARIO PARTIDO SE QUEDARON 5 CLIENTES FUERA | B22041300088 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 2 | 2022-04-13 | 38 | keep | 0 | Apr | 2022 | 2.5882e-05 | 1.2941e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 19
VEGA BAJA | 2022-04-13 14:22 | 2022-04-13 16:50 | 5 | 002:28 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO POSTE SECUNDARIO PARTIDO | B22041300088 | 1st_after_momentary | Secondary Defective Pole | Include | Include | Equipment | 148 | 2022-04-13 | 740 | keep | 0 | Apr | 2022 | 0.00050401 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-04-13 14:25 | 2022-04-13 16:50 | 60 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | A22041300067 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2022-04-13 | 8700 | keep | 0 | Apr | 2022 | 0.0059255 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-04-13 14:27 | 2022-04-13 19:27 | 15 | 005:00 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO POSTES PARTIDOS | M22041300264 | New_Event | Defective Pole | Include | Include | Equipment | 300 | 2022-04-13 | 4500 | keep | 0 | Apr | 2022 | 0.0030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-13 14:35 | 2022-04-13 15:29 | 828 | 000:54 | P | DESGANCHE | DISPARO Y SE PATRULLO EL 1206-04 SE RETIRO BAMBUA CON VARETA CARR.845 KM.4.5 CASI ENTRADA BRISAS DE CARAIZO 60% POR 1206-4 | S22041300068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-04-13 | 44712 | keep | 0 | Apr | 2022 | 0.030453 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-04-13 14:35 | 2022-04-13 15:29 | 1977 | 000:54 | P | DESGANCHE | SE PATRULLO SE RETIRO BAMBUA CON VARETA CARR.845 KM.4.5 CASI ENTRADA BRISAS DE CARAIZO 40% POR 1206-4 | S22041300068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-04-13 | 106758 | keep | 0 | Apr | 2022 | 0.072712 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-04-13 14:35 | 2022-04-13 15:29 | 1799 | 000:54 | T | DESGANCHE | SE PATRULLO SE RETIRO BAMBUA CON VARETA CARR.845 KM.4.5 CASI ENTRADA BRISAS DE CARAIZO LLEVA 40% DEL 1204-4, LLEVA 60% 1204-3 Y 20% DEL 1303-2 | S22041300068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-04-13 | 97146 | keep | 0 | Apr | 2022 | 0.066166 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-04-13 14:35 | 2022-04-13 15:29 | 487 | 000:54 | P | DESGANCHE | SE PATRULLO SE RETIRO BAMBUA CON VARETA CARR.845 KM.4.5 CASI ENTRADA BRISAS DE CARAIZO 20% POR 1206-4 | S22041300068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-04-13 | 26298 | keep | 0 | Apr | 2022 | 0.017911 | 0.00033169 | Sustained | FALSE | FALSE | Not_TMED_Event | 487
FAJARDO | 2022-04-13 14:36 | 2022-04-13 18:29 | 50 | 003:53 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22041300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-04-13 | 11650 | keep | 0 | Apr | 2022 | 0.0079348 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-13 14:43 | 2022-04-13 14:44 | 1262 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041300069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1262 | keep | 0 | Apr | 2022 | 0.00085954 | 0.00085954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1262
VEGA BAJA | 2022-04-13 14:45 | 2022-04-13 17:04 | 200 | 002:19 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | B22041300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-04-13 | 27800 | keep | 0 | Apr | 2022 | 0.018934 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-04-13 14:52 | 2022-04-13 14:53 | 1284 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1284 | keep | 0 | Apr | 2022 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
MAYAGÃœEZ | 2022-04-13 15:00 | 2022-04-14 11:31 | 50 | 020:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA MAQUINA LIMPIANDO CRUZO FASES SIN SERVICIO DEL DIA 13 | M22041400023 | New_Event |  |  | Include | Wildlife | 1231 | 2022-04-13 | 61550 | keep | 0 | Apr | 2022 | 0.041921 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-04-13 15:13 | 2022-04-13 19:35 | 25 | 004:22 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R22041300047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-04-13 | 6550 | keep | 0 | Apr | 2022 | 0.0044612 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-13 15:13 | 2022-04-13 16:07 | 18 | 000:54 | T | DESGANCHE | 1 X 65 EN CORTE DE LINEA. SE PROBO EL INTERRUPTOR MANUALMENTE Y QUEDO EN SERVICIO. POR DESGANCHE | P22041300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-04-13 | 972 | keep | 0 | Apr | 2022 | 0.00066202 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-04-13 15:13 | 2022-04-13 16:07 | 494 | 000:54 | T | DESGANCHE | 1 X 65 EN CORTE DE LINEA. SE PROBO EL INTERRUPTOR MANUALMENTE Y QUEDO EN SERVICIO. POR DESGANCHE | P22041300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-04-13 | 26676 | keep | 0 | Apr | 2022 | 0.018169 | 0.00033646 | Sustained | FALSE | FALSE | Not_TMED_Event | 494
PONCE | 2022-04-13 15:17 | 2022-04-13 15:18 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041300080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 2163 | keep | 0 | Apr | 2022 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
SAN JUAN | 2022-04-13 15:19 | 2022-04-14 13:10 | 80 | 021:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22041300139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1311 | 2022-04-13 | 104880 | keep | 0 | Apr | 2022 | 0.071433 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-13 15:20 | 2022-04-13 15:57 | 7 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22041300126 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-04-13 | 259 | keep | 0 | Apr | 2022 | 0.0001764 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-04-13 15:25 | 2022-04-13 20:05 | 35 | 004:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO LINEA PRIMARIA ROTA | M22041300233 | New_Event | Wire Down | Include | Include | Equipment | 280 | 2022-04-13 | 9800 | keep | 0 | Apr | 2022 | 0.0066747 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2022-04-13 15:40 | 2022-04-13 19:20 | 80 | 003:40 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEAS | A22041300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2022-04-13 | 17600 | keep | 0 | Apr | 2022 | 0.011987 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-13 15:47 | 2022-04-14 01:50 | 50 | 010:03 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22041300167 | New_Event | Bad Weather | Include | Include | Weather | 603 | 2022-04-13 | 30150 | keep | 0 | Apr | 2022 | 0.020535 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-13 15:49 | 2022-04-14 08:05 | 350 | 016:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M22041300168 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 976 | 2022-04-13 | 341600 | keep | 0 | Apr | 2022 | 0.23266 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2022-04-13 16:20 | 2022-04-13 17:05 | 10 | 000:45 | P | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA | S22041300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2022-04-13 | 450 | keep | 0 | Apr | 2022 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-04-13 16:21 | 2022-04-13 17:31 | 5 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE CAJA DE TRANSFORMADOR | P22041300090 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2022-04-13 | 350 | keep | 0 | Apr | 2022 | 0.00023838 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-04-13 16:24 | 2022-04-13 16:45 | 10 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22041300091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2022-04-13 | 210 | keep | 0 | Apr | 2022 | 0.00014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-13 16:32 | 2022-04-13 16:33 | 726 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO LLEVA 1346-4 SE PROBO QUEDO EN SERVICIO | S22041300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-13 | 726 | keep | 0 | Apr | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-04-13 16:32 | 2022-04-13 16:33 | 3932 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1303-3 | S22041300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-13 | 3932 | keep | 0 | Apr | 2022 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
VEGA BAJA | 2022-04-13 16:50 | 2022-04-13 16:54 | 19 | 000:04 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR PARA CERRAR PUENTE SECUNDARIO QUE SE HABIA ABIERTO POR POSTE PARTIDO, EL CUAL SE REMPLAZO | B22041300088 | Additional_clients | Secondary Defective Pole | Include | Include | Equipment | 4 | 2022-04-13 | 76 | keep | 0 | Apr | 2022 | 5.1763e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-13 16:53 | 2022-04-13 18:03 | 50 | 001:10 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 00 EN CONVERTIDOR RELACIONADO A MANIOBRAS DEL SOTERRADO DEL CASCO URBANO EN EVENTO P22041300015 | P22041300100 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 70 | 2022-04-13 | 3500 | keep | 0 | Apr | 2022 | 0.0023838 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-13 16:57 | 2022-04-13 18:39 | 30 | 001:42 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | R22041300059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-04-13 | 3060 | keep | 0 | Apr | 2022 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-04-13 17:00 | 2022-04-13 17:01 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-04-13 17:00 | 2022-04-13 17:01 | 4279 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-04-13 17:00 | 2022-04-13 17:01 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-04-13 17:01 | 2022-04-13 18:53 | 10 | 001:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA POR AVE Y SE REMPLAZO AISALDOR | P22041300106 | New_Event |  |  | Include | Wildlife | 112 | 2022-04-13 | 1120 | keep | 0 | Apr | 2022 | 0.00076283 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-04-13 17:01 | 2022-04-13 18:24 | 5 | 001:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22041300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-04-13 | 415 | keep | 0 | Apr | 2022 | 0.00028265 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-04-13 17:04 | 2022-04-13 21:50 | 400 | 004:46 | P | NO SE REPORTO CAUSA | 2X65 EN RISER | S22041300189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2022-04-13 | 114400 | keep | 0 | Apr | 2022 | 0.077917 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2022-04-13 17:10 | 2022-04-13 22:10 | 100 | 005:00 | P | DESGANCHE | 2 X 50 Y 1 X 80 EN DIFERENTES CORTES DE LINEA SE RETIRO RAMA | M22041300200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-04-13 | 30000 | keep | 0 | Apr | 2022 | 0.020433 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-13 17:21 | 2022-04-13 18:39 | 80 | 001:18 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S22041300191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-04-13 | 6240 | keep | 0 | Apr | 2022 | 0.00425 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-13 17:21 | 2022-04-13 22:04 | 50 | 004:43 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU-A. AVERIA T-4 @ T-5 | C22041300171 | New_Event | UG Cable Fault | Include | Include | Equipment | 283 | 2022-04-13 | 14150 | keep | 0 | Apr | 2022 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-13 17:39 | 2022-04-13 20:25 | 60 | 002:46 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R22041300064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-04-13 | 9960 | keep | 0 | Apr | 2022 | 0.0067837 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-04-13 17:50 | 2022-04-13 20:23 | 1 | 002:33 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | R22041300063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-04-13 | 153 | keep | 0 | Apr | 2022 | 0.00010421 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-04-13 17:53 | 2022-04-13 19:31 | 1144 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES PARA LEVANTAR NEUTRAL PRIMARIO | P22041300114 | New_Event | Wire Down | Include | Include | Equipment | 98 | 2022-04-13 | 112112 | keep | 0 | Apr | 2022 | 0.076359 | 0.00077917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1144
ARECIBO | 2022-04-13 18:01 | 2022-04-13 19:46 | 20 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | A22041300089 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2022-04-13 | 2100 | keep | 0 | Apr | 2022 | 0.0014303 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-04-13 18:32 | 2022-04-13 21:26 | 7 | 002:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | P22041300120 | New_Event | Wire Down | Include | Include | Equipment | 174 | 2022-04-13 | 1218 | keep | 0 | Apr | 2022 | 0.00082957 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-04-13 18:35 | 2022-04-14 09:55 | 70 | 015:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22041300235 | New_Event | Bad Weather | Include | Include | Weather | 920 | 2022-04-13 | 64400 | keep | 0 | Apr | 2022 | 0.043863 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-04-13 18:52 | 2022-04-14 02:09 | 80 | 007:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M22041300243 | New_Event | Cutout Failure | Include | Include | Equipment | 437 | 2022-04-13 | 34960 | keep | 0 | Apr | 2022 | 0.023811 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-13 18:58 | 2022-04-13 18:59 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 3046 | keep | 0 | Apr | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
MAYAGÃœEZ | 2022-04-13 19:08 | 2022-04-13 23:16 | 60 | 004:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | M22041300251 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2022-04-13 | 14880 | keep | 0 | Apr | 2022 | 0.010135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-13 19:23 | 2022-04-13 19:36 | 726 | 000:13 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE INTERRUPTOR A PETICION CELADOR CAMION TUMBO POSTE Y LINEA SE ABRIO PUENTE LLEVA 1346-4 | S22041300203 | 1st_after_momentary |  |  | Include | Wildlife | 13 | 2022-04-13 | 9438 | keep | 0 | Apr | 2022 | 0.0064282 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-04-13 19:23 | 2022-04-13 19:36 | 3932 | 000:13 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE INTERRUPTOR A PETICION CELADOR CAMION TUMBO POSTE Y LINEA SE ABRIO PUENTE SU CARGA POR 1303-3 SE QUEDARON 2 TRANSFORMADORES FUERA FID-16407865 | S22041300203 | 1st_after_momentary |  |  | Include | Wildlife | 13 | 2022-04-13 | 51116 | keep | 0 | Apr | 2022 | 0.034815 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
BAYAMON | 2022-04-13 19:23 | 2022-04-13 23:18 | 150 | 003:55 | P | NO SE REPORTO CAUSA | 1 X 65 C/L | B22041300189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2022-04-13 | 35250 | keep | 0 | Apr | 2022 | 0.024009 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-04-13 19:27 | 2022-04-14 17:51 | 8 | 022:24 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTES PARTIDOS Y SE CERRO LOS PUENTES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR DESDE AYER LA AVERIA | M22041400163 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1344 | 2022-04-13 | 10752 | keep | 0 | Apr | 2022 | 0.0073231 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-13 19:36 | 2022-04-14 15:31 | 20 | 019:55 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO Y SE LEVANTO LINEA SE CONSTRUYO CORTE DE LINEA Y 1 X 20 EN CORTE DE LINEA | S22041300259 | New_Event | Defective Pole | Include | Include | Equipment | 1195 | 2022-04-13 | 23900 | keep | 0 | Apr | 2022 | 0.016278 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-04-13 20:03 | 2022-04-14 09:06 | 18 | 013:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO LINEA A CAJA EN CORTE DE LINEA | B22041300192 | New_Event | Wire Down | Include | Include | Equipment | 783 | 2022-04-13 | 14094 | keep | 0 | Apr | 2022 | 0.0095994 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-04-13 20:09 | 2022-04-13 20:10 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041300136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1478 | keep | 0 | Apr | 2022 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
CAGUAS | 2022-04-13 20:19 | 2022-04-14 12:18 | 5 | 015:59 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C22041300179 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 959 | 2022-04-13 | 4795 | keep | 0 | Apr | 2022 | 0.0032659 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-04-13 20:41 | 2022-04-14 08:22 | 15 | 011:41 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | PUNTO DE CONECTE EN T-3 AVERIADO SE COLOCO PISTOLA EN BUSHING SPARE | P22041300145 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 701 | 2022-04-13 | 10515 | keep | 0 | Apr | 2022 | 0.0071617 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-04-13 22:04 | 2022-04-14 10:18 | 25 | 012:14 | P | CABLE SOTERRADO AVERIADO | SE CERRO FUSIBLE EN T-2 | C22041300171 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 734 | 2022-04-13 | 18350 | keep | 0 | Apr | 2022 | 0.012498 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-13 22:27 | 2022-04-14 11:55 | 51 | 013:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22041300289 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 808 | 2022-04-13 | 41208 | keep | 0 | Apr | 2022 | 0.028067 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
VEGA BAJA | 2022-04-13 22:29 | 2022-04-13 22:30 | 1570 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22040130000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-13 | 1570 | keep | 0 | Apr | 2022 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
MAYAGÃœEZ | 2022-04-13 23:07 | 2022-04-14 09:12 | 14 | 010:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22041300312 | New_Event | Bad Weather | Include | Include | Weather | 605 | 2022-04-13 | 8470 | keep | 0 | Apr | 2022 | 0.0057689 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2022-04-13 23:39 | 2022-04-13 23:42 | 908 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B22041300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-13 | 2724 | keep | 0 | Apr | 2022 | 0.0018553 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
YAUCO | 2022-04-13 23:55 | 2022-04-14 01:00 | 2440 | 001:05 | T | ANIMAL U OBJETO EXTRAÃ‘O | POSTE PRIMARIO PARTIDO POR AUTO | P22041300154 | New_Event |  |  | Include | Wildlife | 65 | 2022-04-13 | 158600 | keep | 0 | Apr | 2022 | 0.10802 | 0.0016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 2440
BAYAMON | 2022-04-14 00:13 | 2022-04-14 00:14 | 1362 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 1362 | keep | 0 | Apr | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2022-04-14 00:14 | 2022-04-14 12:10 | 101 | 011:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN C/L SE LEVANTARON 2 FASES PARTIDAS LINEA PRIMARIA AUTO IMPACTO POSTE | B22041400024 | New_Event |  |  | Include | Wildlife | 716 | 2022-04-14 | 72316 | keep | 0 | Apr | 2022 | 0.049254 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
ARECIBO | 2022-04-14 00:48 | 2022-04-14 00:49 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 2201 | keep | 0 | Apr | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
YAUCO | 2022-04-14 01:00 | 2022-04-14 17:53 | 81 | 016:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE PARTIDO | P22041400001 | Partial_restoration |  |  | Include | Wildlife | 1013 | 2022-04-14 | 82053 | keep | 0 | Apr | 2022 | 0.055886 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-04-14 02:33 | 2022-04-14 10:44 | 129 | 008:11 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHO Y FIJO CONDUCTOR | C22041300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 491 | 2022-04-14 | 63339 | keep | 0 | Apr | 2022 | 0.04314 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
SAN JUAN | 2022-04-14 02:38 | 2022-04-14 13:32 | 35 | 010:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE Y SE CERRO CORTE DE LINEA | S22041400037 | New_Event | Wire Down | Include | Include | Equipment | 654 | 2022-04-14 | 22890 | keep | 0 | Apr | 2022 | 0.01559 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-04-14 02:53 | 2022-04-14 07:47 | 70 | 004:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | B22041400015 | New_Event |  |  | Include | Wildlife | 294 | 2022-04-14 | 20580 | keep | 0 | Apr | 2022 | 0.014017 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-04-14 03:26 | 2022-04-14 10:12 | 30 | 006:46 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | B22041400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 406 | 2022-04-14 | 12180 | keep | 0 | Apr | 2022 | 0.0082957 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-04-14 05:07 | 2022-04-14 06:42 | 51 | 001:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22041400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-04-14 | 4845 | keep | 0 | Apr | 2022 | 0.0032999 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
GUAYAMA | 2022-04-14 05:12 | 2022-04-14 05:44 | 1676 | 000:32 | T | NO SE REPORTO CAUSA | DISPARO DIO FAIL TO OPERATE SE CERRO MANUALMENTE | P22041400038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 32 | 2022-04-14 | 53632 | keep | 0 | Apr | 2022 | 0.036529 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
CAGUAS | 2022-04-14 05:26 | 2022-04-14 09:08 | 141 | 003:42 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22041400039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2022-04-14 | 31302 | keep | 0 | Apr | 2022 | 0.02132 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
VEGA BAJA | 2022-04-14 05:27 | 2022-04-14 23:57 | 19 | 018:30 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN SU-17. AVERIA NUEVA T-19 @ T-18 AVERIA VIEJA T-17 @ T-16 SE QUEDARON FUERA T-18 Y T-17 13 CLIENTES | B22041400018 | New_Event | UG Cable Fault | Include | Include | Equipment | 1110 | 2022-04-14 | 21090 | keep | 0 | Apr | 2022 | 0.014364 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2022-04-14 06:30 | 2022-04-14 10:50 | 14 | 004:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C22041400040 | New_Event |  |  | Include | Wildlife | 260 | 2022-04-14 | 3640 | keep | 0 | Apr | 2022 | 0.0024792 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-04-14 06:33 | 2022-04-14 11:24 | 12 | 004:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 30 EN TRANSFORMADOR SE REPARO SECUNDARIA | S22041400058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 291 | 2022-04-14 | 3492 | keep | 0 | Apr | 2022 | 0.0023784 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-04-14 06:47 | 2022-04-14 08:50 | 60 | 002:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-04-14 | 7380 | keep | 0 | Apr | 2022 | 0.0050265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-04-14 07:05 | 2022-04-14 09:43 | 4 | 002:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | C22041400042 | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2022-04-14 | 632 | keep | 0 | Apr | 2022 | 0.00043045 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-04-14 07:10 | 2022-04-14 10:12 | 175 | 003:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA | P22041400042 | New_Event | Wire Down | Include | Include | Equipment | 182 | 2022-04-14 | 31850 | keep | 0 | Apr | 2022 | 0.021693 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
MAYAGÃœEZ | 2022-04-14 07:10 | 2022-04-14 14:16 | 20 | 007:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTO | M22204140001 | New_Event | Bad Weather | Include | Include | Weather | 426 | 2022-04-14 | 8520 | keep | 0 | Apr | 2022 | 0.0058029 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-14 07:11 | 2022-04-14 09:50 | 40 | 002:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | R22041400031 | New_Event |  |  | Include | Wildlife | 159 | 2022-04-14 | 6360 | keep | 0 | Apr | 2022 | 0.0043318 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-04-14 07:16 | 2022-04-14 09:21 | 8 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22041400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-04-14 | 1000 | keep | 0 | Apr | 2022 | 0.0006811 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-14 07:27 | 2022-04-14 08:15 | 8 | 000:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA VEHICULO IMPACTO TENSOR | C22041400046 | New_Event |  |  | Include | Wildlife | 48 | 2022-04-14 | 384 | keep | 0 | Apr | 2022 | 0.00026154 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-04-14 07:31 | 2022-04-15 10:20 | 1 | 026:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | M22041400015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1609 | 2022-04-14 | 1609 | keep | 0 | Apr | 2022 | 0.0010959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-14 07:42 | 2022-04-14 09:49 | 12 | 002:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C22041400048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2022-04-14 | 1524 | keep | 0 | Apr | 2022 | 0.001038 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-14 07:44 | 2022-04-14 10:33 | 20 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | C22041400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-04-14 | 3380 | keep | 0 | Apr | 2022 | 0.0023021 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-14 07:47 | 2022-04-14 10:55 | 40 | 003:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 100A EN SU - 2B CUCE X AVE | R22041400033 | New_Event |  |  | Include | Wildlife | 188 | 2022-04-14 | 7520 | keep | 0 | Apr | 2022 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-14 08:00 | 2022-04-14 18:45 | 50 | 010:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO PUENTE | S22041400071 | New_Event | Wire Down | Include | Include | Equipment | 645 | 2022-04-14 | 32250 | keep | 0 | Apr | 2022 | 0.021965 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-14 08:26 | 2022-04-14 13:10 | 1 | 004:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN C/L REMPLAZO AISLACION | R22041400034 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 284 | 2022-04-14 | 284 | keep | 0 | Apr | 2022 | 0.00019343 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-14 08:31 | 2022-04-14 10:25 | 12 | 001:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 XMR SE REPARO SECUNDARIA | B22041400029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 114 | 2022-04-14 | 1368 | keep | 0 | Apr | 2022 | 0.00093174 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-04-14 08:32 | 2022-04-14 08:33 | 1131 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22041400055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 1131 | keep | 0 | Apr | 2022 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
BAYAMON | 2022-04-14 08:37 | 2022-04-14 11:22 | 65 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22041400030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-04-14 | 10725 | keep | 0 | Apr | 2022 | 0.0073047 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-04-14 08:47 | 2022-04-14 08:48 | 4089 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22041400031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 4089 | keep | 0 | Apr | 2022 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
CAGUAS | 2022-04-14 08:55 | 2022-04-14 12:00 | 28 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22041400056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-04-14 | 5180 | keep | 0 | Apr | 2022 | 0.0035281 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
CAGUAS | 2022-04-14 08:56 | 2022-04-14 11:05 | 8 | 002:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRA SECUNDARIA | C22041400057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 129 | 2022-04-14 | 1032 | keep | 0 | Apr | 2022 | 0.00070289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-14 09:00 | 2022-04-14 10:46 | 50 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22041400032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-04-14 | 5300 | keep | 0 | Apr | 2022 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-14 09:03 | 2022-04-14 09:04 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22041400058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-04-14 09:04 | 2022-04-14 12:06 | 10 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C22041400078 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 182 | 2022-04-14 | 1820 | keep | 0 | Apr | 2022 | 0.0012396 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-04-14 09:12 | 2022-04-14 12:37 | 100 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22041400028 | New_Event | Bad Weather | Include | Include | Weather | 205 | 2022-04-14 | 20500 | keep | 0 | Apr | 2022 | 0.013962 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-14 09:27 | 2022-04-14 11:00 | 16 | 001:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | C22041400061 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2022-04-14 | 1488 | keep | 0 | Apr | 2022 | 0.0010135 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2022-04-14 09:30 | 2022-04-14 17:11 | 20 | 007:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTES SECUNDARIO | M22041400031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 461 | 2022-04-14 | 9220 | keep | 0 | Apr | 2022 | 0.0062797 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-14 09:36 | 2022-04-14 09:37 | 3432 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 80% DE SU CARGA | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 3432 | keep | 0 | Apr | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
CAGUAS | 2022-04-14 09:50 | 2022-04-14 12:40 | 50 | 002:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22041400066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-04-14 | 8500 | keep | 0 | Apr | 2022 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-14 09:53 | 2022-04-14 13:18 | 60 | 003:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CAMION IMPACTO CABLES DE TELEFONOS | C22041400067 | New_Event |  |  | Include | Wildlife | 205 | 2022-04-14 | 12300 | keep | 0 | Apr | 2022 | 0.0083775 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-04-14 09:58 | 2022-04-14 12:14 | 22 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22041400068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-04-14 | 2992 | keep | 0 | Apr | 2022 | 0.0020378 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
ARECIBO | 2022-04-14 10:00 | 2022-04-14 12:30 | 200 | 002:30 | P | LINEA DE TRANSMISION 38KV | 3 X 100 EN CORTE DE LINEA LINEAS CRUZADAS CON OVERHEAD DE LINEA 38 KV | A22041400014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 150 | 2022-04-14 | 30000 | keep | 0 | Apr | 2022 | 0.020433 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-04-14 10:01 | 2022-04-15 10:00 | 45 | 023:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1439 | 2022-04-14 | 64755 | keep | 0 | Apr | 2022 | 0.044104 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-04-14 10:05 | 2022-04-14 10:06 | 2560 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22041400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-14 | 2560 | keep | 0 | Apr | 2022 | 0.0017436 | 0.0017436 | Momentary | FALSE | FALSE | Not_TMED_Event | 2560
MAYAGÃœEZ | 2022-04-14 10:06 | 2022-04-14 14:56 | 200 | 004:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR VIENTOS | M22041400041 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 290 | 2022-04-14 | 58000 | keep | 0 | Apr | 2022 | 0.039504 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-04-14 10:15 | 2022-04-14 14:01 | 1 | 003:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22041400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2022-04-14 | 226 | keep | 0 | Apr | 2022 | 0.00015393 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-14 10:26 | 2022-04-14 12:40 | 1 | 002:14 | P | TRANSFORMADOR AVERIADO | 1 X 10 SE REEMPLAZO TRANSFORMADOR EN BANCO | C22041400075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 134 | 2022-04-14 | 134 | keep | 0 | Apr | 2022 | 9.1267e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-14 10:31 | 2022-04-14 17:39 | 30 | 007:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22041400097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 428 | 2022-04-14 | 12840 | keep | 0 | Apr | 2022 | 0.0087453 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-14 10:31 | 2022-04-14 14:46 | 2 | 004:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA POR PALOMA | M22041400053 | New_Event |  |  | Include | Wildlife | 255 | 2022-04-14 | 510 | keep | 0 | Apr | 2022 | 0.00034736 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-04-14 10:42 | 2022-04-14 12:05 | 1 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER PERSONAL INDICA NO CAUSA | A22041400037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2022-04-14 | 83 | keep | 0 | Apr | 2022 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-14 10:42 | 2022-04-14 13:58 | 8 | 003:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22041400057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2022-04-14 | 1568 | keep | 0 | Apr | 2022 | 0.001068 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-04-14 10:55 | 2022-04-14 14:20 | 6 | 003:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | A22041400038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 205 | 2022-04-14 | 1230 | keep | 0 | Apr | 2022 | 0.00083775 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-04-14 10:58 | 2022-04-14 14:32 | 40 | 003:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE INSTALO RIGIDO | R22041400042 | New_Event |  |  | Include | Wildlife | 214 | 2022-04-14 | 8560 | keep | 0 | Apr | 2022 | 0.0058302 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-14 11:07 | 2022-04-14 11:10 | 2234 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22041400064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-14 | 6702 | keep | 0 | Apr | 2022 | 0.0045647 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-04-14 11:12 | 2022-04-15 17:30 | 15 | 030:18 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22041400066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1818 | 2022-04-14 | 27270 | keep | 0 | Apr | 2022 | 0.018573 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-14 11:14 | 2022-04-14 11:45 | 8 | 000:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO BUSHING SECUNDARIO | B22041300064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 31 | 2022-04-14 | 248 | keep | 0 | Apr | 2022 | 0.00016891 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-14 11:15 | 2022-04-14 14:33 | 10 | 003:18 | P | NO SE REPORTO CAUSA | 1X10 EN XMER | C22041400081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2022-04-14 | 1980 | keep | 0 | Apr | 2022 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-14 11:21 | 2022-04-14 12:22 | 10 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22041400037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2022-04-14 | 610 | keep | 0 | Apr | 2022 | 0.00041547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-14 11:30 | 2022-04-14 12:28 | 14 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA Y SE REPARO SECUNDARIA | S22041400012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-04-14 | 812 | keep | 0 | Apr | 2022 | 0.00055305 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-04-14 11:40 | 2022-04-14 13:50 | 65 | 002:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A22041400045 | New_Event | Cutout Failure | Include | Include | Equipment | 130 | 2022-04-14 | 8450 | keep | 0 | Apr | 2022 | 0.0057553 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-04-14 11:44 | 2022-04-14 15:14 | 12 | 003:30 | P | OTRAS CAUSAS | 3 X 100 EN RISER SE DEJO FUERA EDIFICIO OCEANIA PROBLEMA INTERNO | S22041400119 | New_Event | Other Causes | Include | Include | Other | 210 | 2022-04-14 | 2520 | keep | 0 | Apr | 2022 | 0.0017164 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-04-14 12:03 | 2022-04-14 13:07 | 110 | 001:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22041400085 | New_Event |  |  | Include | Wildlife | 64 | 2022-04-14 | 7040 | keep | 0 | Apr | 2022 | 0.0047949 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CANOVANAS | 2022-04-14 12:11 | 2022-04-14 13:03 | 26 | 000:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REMPLAZO AISLADOR Y PIN | R22041400048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 52 | 2022-04-14 | 1352 | keep | 0 | Apr | 2022 | 0.00092084 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
AGUADILLA | 2022-04-14 12:15 | 2022-04-14 15:14 | 100 | 002:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA | M22041400066 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2022-04-14 | 17900 | keep | 0 | Apr | 2022 | 0.012192 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-14 12:17 | 2022-04-14 14:15 | 65 | 001:58 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | C22041400088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2022-04-14 | 7670 | keep | 0 | Apr | 2022 | 0.005224 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2022-04-14 12:20 | 2022-04-14 14:42 | 4 | 002:22 | P | NO SE REPORTO CAUSA | 1X10 EN XMER | C22041400089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-04-14 | 568 | keep | 0 | Apr | 2022 | 0.00038686 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-04-14 12:21 | 2022-04-14 13:28 | 40 | 001:07 | P | DESGANCHE | 1 X 100 EN C/L | R22041400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-04-14 | 2680 | keep | 0 | Apr | 2022 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-14 12:43 | 2022-04-14 12:55 | 3 | 000:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | M22041400069 | New_Event | Cutout Failure | Include | Include | Equipment | 12 | 2022-04-14 | 36 | keep | 0 | Apr | 2022 | 2.4519e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-04-14 12:46 | 2022-04-14 15:27 | 10 | 002:41 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | S22041400131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-04-14 | 1610 | keep | 0 | Apr | 2022 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-14 12:51 | 2022-04-14 20:44 | 90 | 007:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22041400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 473 | 2022-04-14 | 42570 | keep | 0 | Apr | 2022 | 0.028994 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-04-14 13:00 | 2022-04-14 13:01 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-02 | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-04-14 13:00 | 2022-04-14 13:01 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1206-1 | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-04-14 13:00 | 2022-04-14 13:07 | 225 | 000:07 | T | DESCONECTIVO DEFECTUOSO | DISPARO SU CARGA POR 1303-05 | S22041400000 | New_Event | Switch Failure | Include | Include | Equipment | 7 | 2022-04-14 | 1575 | keep | 0 | Apr | 2022 | 0.0010727 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-14 13:00 | 2022-04-14 13:07 | 870 | 000:07 | T | DESCONECTIVO DEFECTUOSO | DISPARO LLEVA 1303-04 | S22041400000 | New_Event | Switch Failure | Include | Include | Equipment | 7 | 2022-04-14 | 6090 | keep | 0 | Apr | 2022 | 0.0041479 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-04-14 13:10 | 2022-04-14 13:13 | 225 | 000:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO SU CARGA POR 1303-05 | S22041400000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 3 | 2022-04-14 | 675 | keep | 0 | Apr | 2022 | 0.00045974 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-14 13:10 | 2022-04-14 13:13 | 870 | 000:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO LLEVA 1303-4 | S22041400000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 3 | 2022-04-14 | 2610 | keep | 0 | Apr | 2022 | 0.0017777 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-14 13:10 | 2022-04-14 18:09 | 50 | 004:59 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO NO FUNDIO | B22041300105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 299 | 2022-04-14 | 14950 | keep | 0 | Apr | 2022 | 0.010182 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-14 13:12 | 2022-04-14 14:11 | 3744 | 000:59 | T | DESCONECTIVO DEFECTUOSO | GRAPA EN MACHETES QUEMADA | P22041400076 | New_Event | Switch Failure | Include | Include | Equipment | 59 | 2022-04-14 | 220896 | keep | 0 | Apr | 2022 | 0.15045 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
SAN JUAN | 2022-04-14 13:15 | 2022-04-14 13:27 | 225 | 000:12 | T | DESCONECTIVO DEFECTUOSO | DISPARO SU CARGA POR 1303-5 SE SECCIONALIZO MACHETE QUEMADO ENTRADA CAMINO LOS ROMEROS 99% EN SERVICIO | S22041400000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 12 | 2022-04-14 | 2700 | keep | 0 | Apr | 2022 | 0.001839 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-14 13:15 | 2022-04-14 13:27 | 870 | 000:12 | T | DESCONECTIVO DEFECTUOSO | DISPARO LLEVA 1303-4 | S22041400000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 12 | 2022-04-14 | 10440 | keep | 0 | Apr | 2022 | 0.0071106 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2022-04-14 13:20 | 2022-04-14 16:59 | 1 | 003:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CONECTO BAJANTE PRIMARIO ABIERTO | M22041400079 | New_Event | Wire Down | Include | Include | Equipment | 219 | 2022-04-14 | 219 | keep | 0 | Apr | 2022 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-14 13:24 | 2022-04-14 13:25 | 1061 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 1061 | keep | 0 | Apr | 2022 | 0.00072264 | 0.00072264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1061
SAN JUAN | 2022-04-14 13:27 | 2022-04-14 16:31 | 31 | 003:04 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO 3 MACHETE Y SE REPARO PUENTE DE LINEA A MACHETE 100% EN SERVICIO | S22041400000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 184 | 2022-04-14 | 5704 | keep | 0 | Apr | 2022 | 0.003885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-14 13:28 | 2022-04-14 13:29 | 4085 | 000:01 | T | DESGANCHE | RECIERRE LLEVA LA CARGA DEL 2404-06 | R22041400054 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-14 | 4085 | keep | 0 | Apr | 2022 | 0.0027823 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-14 13:28 | 2022-04-14 13:29 | 7621 | 000:01 | T | DESGANCHE | RECIERRE DEL 2402-03 | R22041400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-14 | 7621 | keep | 0 | Apr | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2022-04-14 13:29 | 2022-04-14 14:00 | 40 | 000:31 | P | DESGANCHE | 1 X 100 EN C/L | R22041400049 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 31 | 2022-04-14 | 1240 | keep | 0 | Apr | 2022 | 0.00084456 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-14 13:35 | 2022-04-14 16:36 | 5 | 003:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE DE NEUTRAL SECUNDARIO EN XMR | C22041400098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 181 | 2022-04-14 | 905 | keep | 0 | Apr | 2022 | 0.00061639 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-04-14 13:36 | 2022-04-14 13:37 | 3871 | 000:01 | T | DESGANCHE | RECIERE DE INTERUPTOR | B22041400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-14 | 3871 | keep | 0 | Apr | 2022 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
CAGUAS | 2022-04-14 13:43 | 2022-04-14 16:27 | 30 | 002:44 | P | DESGANCHE | 1X50 EN C/L & 1X40 EN C/L | C22041400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-04-14 | 4920 | keep | 0 | Apr | 2022 | 0.003351 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-04-14 13:47 | 2022-04-14 16:18 | 60 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA FUERTE | B22041400082 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2022-04-14 | 9060 | keep | 0 | Apr | 2022 | 0.0061707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-14 13:56 | 2022-04-14 14:45 | 2 | 000:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041400067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2022-04-14 | 98 | keep | 0 | Apr | 2022 | 6.6747e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-04-14 13:58 | 2022-04-14 17:09 | 80 | 003:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M22041400093 | New_Event | Bad Weather | Include | Include | Weather | 191 | 2022-04-14 | 15280 | keep | 0 | Apr | 2022 | 0.010407 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-14 14:02 | 2022-04-14 14:03 | 1180 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | B22041400083 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-14 | 1180 | keep | 0 | Apr | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-04-14 14:03 | 2022-04-15 01:12 | 40 | 011:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L SE DESGANCHO Y SE RETIRO AVE DE PARARRAYO | B22041400172 | 1st_after_momentary |  |  | Include | Wildlife | 669 | 2022-04-14 | 26760 | keep | 0 | Apr | 2022 | 0.018226 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-14 14:08 | 2022-04-14 16:40 | 40 | 002:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-04-14 | 6080 | keep | 0 | Apr | 2022 | 0.0041411 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-04-14 14:09 | 2022-04-14 18:15 | 160 | 004:06 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | P22041400103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2022-04-14 | 39360 | keep | 0 | Apr | 2022 | 0.026808 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2022-04-14 14:09 | 2022-04-14 16:59 | 60 | 002:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22041400084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-04-14 | 10200 | keep | 0 | Apr | 2022 | 0.0069472 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-14 14:15 | 2022-04-14 18:22 | 22 | 004:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22041400173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2022-04-14 | 5434 | keep | 0 | Apr | 2022 | 0.0037011 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
PONCE | 2022-04-14 14:29 | 2022-04-14 14:30 | 4035 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P22041400114 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-14 | 4035 | keep | 0 | Apr | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-04-14 14:30 | 2022-04-14 16:29 | 50 | 001:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L AVE CRUZO LINEAS | P22041400115 | 1st_after_momentary |  |  | Include | Wildlife | 119 | 2022-04-14 | 5950 | keep | 0 | Apr | 2022 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-04-14 14:32 | 2022-04-14 14:50 | 6 | 000:18 | P | NO SE REPORTO CAUSA | 2X15 EN XMER | C22041400102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2022-04-14 | 108 | keep | 0 | Apr | 2022 | 7.3558e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-04-14 14:36 | 2022-04-14 16:59 | 6 | 002:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRA EN PEDESTAL SECUNDARIO | P22041400116 | New_Event | Secondary Wire Down | Include | Include | Equipment | 143 | 2022-04-14 | 858 | keep | 0 | Apr | 2022 | 0.00058438 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-04-14 14:38 | 2022-04-14 14:39 | 1047 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | M22041400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-04-14 | 1047 | keep | 0 | Apr | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2022-04-14 14:39 | 2022-04-14 18:35 | 6 | 003:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLES AVERIADO | M22041400115 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 236 | 2022-04-14 | 1416 | keep | 0 | Apr | 2022 | 0.00096443 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-14 14:41 | 2022-04-14 14:42 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO 1720-08 | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 2402 | keep | 0 | Apr | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-04-14 14:41 | 2022-04-14 14:42 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO 1720-08 | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-04-14 14:50 | 2022-04-14 18:00 | 1 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22041400111 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2022-04-14 | 190 | keep | 0 | Apr | 2022 | 0.00012941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-14 14:51 | 2022-04-14 16:16 | 3871 | 001:25 | T | DESGANCHE | SE CERRO POR SCADA SECCIONALIZANDO ALIMENTADOR 75% EN SERVICIO | B22041400098 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-04-14 | 329035 | keep | 0 | Apr | 2022 | 0.2241 | 0.0026365 | Sustained | FALSE | FALSE | Not_TMED_Event | 3871
PONCE | 2022-04-14 14:55 | 2022-04-14 19:31 | 70 | 004:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA CABLES CRUZADOS | P22041400124 | New_Event | Wire Down | Include | Include | Equipment | 276 | 2022-04-14 | 19320 | keep | 0 | Apr | 2022 | 0.013159 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-04-14 14:56 | 2022-04-14 19:43 | 30 | 004:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22041400185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2022-04-14 | 8610 | keep | 0 | Apr | 2022 | 0.0058642 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-14 15:03 | 2022-04-14 16:27 | 143 | 001:24 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 80% DEL 1404-07 SE PATRULLO NO SE ENCOTRO CAUSA SE PROBO QUEDO EN SERVICIO | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-04-14 | 12012 | keep | 0 | Apr | 2022 | 0.0081813 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-04-14 15:03 | 2022-04-14 16:27 | 1085 | 001:24 | P | NO SE REPORTO CAUSA | DISPARO 80 % POR 1404-6 SE PATRULLO NO SE ENCOTRO CAUSA SE PROBO QUEDO EN SERVICIO | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-04-14 | 91140 | keep | 0 | Apr | 2022 | 0.062075 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2022-04-14 15:06 | 2022-04-14 18:47 | 10 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22041400101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-04-14 | 2210 | keep | 0 | Apr | 2022 | 0.0015052 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-14 15:06 | 2022-04-14 18:20 | 60 | 003:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B22041400100 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2022-04-14 | 11640 | keep | 0 | Apr | 2022 | 0.007928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-14 15:20 | 2022-04-14 15:21 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-2 | S22041400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-04-14 15:20 | 2022-04-14 15:21 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1206-1 | S22041400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
MAYAGÃœEZ | 2022-04-14 15:29 | 2022-04-14 17:27 | 1444 | 001:58 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 6014-02 QUE LLEVA LA CARGA DEL 6014-01 SE PATRULLO LOS ALIMENTADORES Y NO SE ENCONTRO CAUSA PARA EL DISPARO SOLO MAL TIEMPO EN EL AREA SE PROBO NUEVAMENTE Y QUEDO EN SERVICIO | M22041400137 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2022-04-14 | 170392 | keep | 0 | Apr | 2022 | 0.11605 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-04-14 15:29 | 2022-04-14 17:27 | 3630 | 001:58 | T | MAL TIEMPO/RAYOS/WET ASH | SE PATRULLO LOS ALIMENTADORES Y NO SE ENCONTRO CAUSA PARA EL DISPARO SOLO MAL TIEMPO EN EL AREA SE PROBO NUEVAMENTE Y QUEDO EN SERVICIO | M22041400137 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2022-04-14 | 428340 | keep | 0 | Apr | 2022 | 0.29174 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
SAN JUAN | 2022-04-14 15:30 | 2022-04-14 15:33 | 1000 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO PARTE POR 1620-2 SE PROBO QUEDO EN SERVICIO | S22041400205 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-14 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-04-14 15:30 | 2022-04-14 15:33 | 3718 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA PARTE 1206-3 SE PROBO QUEDO EN SERVICIO | S22041400205 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-14 | 11154 | keep | 0 | Apr | 2022 | 0.0075969 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
VEGA BAJA | 2022-04-14 15:39 | 2022-04-14 15:40 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 1859 | keep | 0 | Apr | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
PONCE | 2022-04-14 15:48 | 2022-04-14 16:21 | 8 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | P22041400150 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2022-04-14 | 264 | keep | 0 | Apr | 2022 | 0.00017981 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-04-14 16:00 | 2022-04-14 16:01 | 576 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22011400153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 576 | keep | 0 | Apr | 2022 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
SAN JUAN | 2022-04-14 16:02 | 2022-04-14 16:16 | 1397 | 000:14 | T | RELEVO DE CARGA PROGRAMADO - Pending to Clasify | RELEVO POR CAIDA FRECUENCIA | S22041400230 | New_Event | Load Shed (Planned) | Exclude | Exclude | Power Supply | 14 | 2022-04-14 | 19558 | keep | 0 | Apr | 2022 | 0.013321 | 0.00095149 | Sustained | FALSE | FALSE | Not_TMED_Event | 1397
ARECIBO | 2022-04-14 16:13 | 2022-04-14 20:30 | 1 | 004:17 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041400078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-04-14 | 257 | keep | 0 | Apr | 2022 | 0.00017504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-14 16:16 | 2022-04-14 16:32 | 968 | 000:16 | P | DESGANCHE | SE CERRO MACHETES EN CARR 840 ESQ 199 ABRIENDO MACHETES EN CARR 840 85% EN SERVICIO POR IGUANA Y BAMBUA CRUZANDO LINEAS | B22041400098 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 16 | 2022-04-14 | 15488 | keep | 0 | Apr | 2022 | 0.010549 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-14 16:32 | 2022-04-14 17:06 | 861 | 000:34 | P | DESGANCHE | SE RETIRO IGUANA Y BAMBUA CRUZANDO LINEAS SE CERRO MACHETES EN CARR 840 | B22041400098 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 34 | 2022-04-14 | 29274 | keep | 0 | Apr | 2022 | 0.019938 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-04-14 16:45 | 2022-04-14 17:45 | 45 | 001:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22041400085 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2022-04-14 | 2700 | keep | 0 | Apr | 2022 | 0.001839 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-04-14 16:45 | 2022-04-14 18:07 | 50 | 001:22 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | C22041400112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-04-14 | 4100 | keep | 0 | Apr | 2022 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-14 16:54 | 2022-04-14 19:14 | 2 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22041400174 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2022-04-14 | 280 | keep | 0 | Apr | 2022 | 0.00019071 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-04-14 16:55 | 2022-04-14 19:35 | 20 | 002:40 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041400087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-04-14 | 3200 | keep | 0 | Apr | 2022 | 0.0021795 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-04-14 16:55 | 2022-04-14 17:15 | 10 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONECTORES EN BAJANTE SECUNDARIO | C22041400114 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2022-04-14 | 200 | keep | 0 | Apr | 2022 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-04-14 16:58 | 2022-04-14 18:49 | 40 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22041400175 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2022-04-14 | 4440 | keep | 0 | Apr | 2022 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-14 17:03 | 2022-04-14 19:01 | 30 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE REMPLAZO AISLADOR | R22041400099 | New_Event |  |  | Include | Wildlife | 118 | 2022-04-14 | 3540 | keep | 0 | Apr | 2022 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-14 17:06 | 2022-04-14 17:08 | 3871 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE BKR AL CERRAR MACHETES EN CARR 840 BO LA ALDEA. PERSONAL NO SE HABIA PERCATADO DE PUENTE ABIERTO EN URB FLAMINGO TERRACE | B22041400098 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-04-14 | 7742 | keep | 0 | Apr | 2022 | 0.005273 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
MAYAGÃœEZ | 2022-04-14 17:06 | 2022-04-15 01:08 | 125 | 008:02 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22041400177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 482 | 2022-04-14 | 60250 | keep | 0 | Apr | 2022 | 0.041036 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-04-14 17:08 | 2022-04-14 17:44 | 49 | 000:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO MACHETES EN CARR 840 EN BO LA ALDEA SECCIONALIZANDO TRAMO DE PUENTE ABIERTO EN URB FLAMINGO TERRACE. ESTE TRAMO NO TIENE CARGAS | B22041400098 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 36 | 2022-04-14 | 1764 | keep | 0 | Apr | 2022 | 0.0012015 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
MAYAGÃœEZ | 2022-04-14 17:09 | 2022-04-14 20:11 | 80 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M22041400180 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2022-04-14 | 14560 | keep | 0 | Apr | 2022 | 0.0099167 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-14 17:11 | 2022-04-14 21:53 | 50 | 004:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S22041400290 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-04-14 | 14100 | keep | 0 | Apr | 2022 | 0.0096034 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-14 17:17 | 2022-04-14 17:49 | 4 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22041400181 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2022-04-14 | 128 | keep | 0 | Apr | 2022 | 8.718e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-04-14 17:26 | 2022-04-15 10:36 | 6 | 017:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22041400295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1030 | 2022-04-14 | 6180 | keep | 0 | Apr | 2022 | 0.0042092 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-04-14 17:36 | 2022-04-14 19:30 | 300 | 001:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 140 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | A22041400094 | New_Event | Wire Down | Include | Include | Equipment | 114 | 2022-04-14 | 34200 | keep | 0 | Apr | 2022 | 0.023293 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-04-14 17:38 | 2022-04-14 17:39 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22041400000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-14 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-04-14 17:39 | 2022-04-14 18:27 | 60 | 000:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X50 EN C/L (POR AVE EN LA LINEA) | C22041400115 | 1st_after_momentary |  |  | Include | Wildlife | 48 | 2022-04-14 | 2880 | keep | 0 | Apr | 2022 | 0.0019616 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-04-14 17:42 | 2022-04-15 08:01 | 86 | 014:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C22041400116 | New_Event |  |  | Include | Wildlife | 859 | 2022-04-14 | 73874 | keep | 0 | Apr | 2022 | 0.050315 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
BAYAMON | 2022-04-14 17:44 | 2022-04-14 18:06 | 49 | 000:22 | P | NO SE REPORTO CAUSA | SE REPUSO 1 X 80 EN RISER HACIA SU 5 EN ROYAL TOWN | B22041400098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2022-04-14 | 1078 | keep | 0 | Apr | 2022 | 0.00073422 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
MAYAGÃœEZ | 2022-04-14 17:52 | 2022-04-14 22:45 | 150 | 004:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22041400188 | New_Event | Cutout Failure | Include | Include | Equipment | 293 | 2022-04-14 | 43950 | keep | 0 | Apr | 2022 | 0.029934 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-04-14 17:54 | 2022-04-14 19:15 | 6 | 001:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BARRA EN PEDESTAL TIPO MOLE | C22041400119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 81 | 2022-04-14 | 486 | keep | 0 | Apr | 2022 | 0.00033101 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-14 17:56 | 2022-04-14 17:57 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22041400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-14 | 888 | keep | 0 | Apr | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-04-14 17:56 | 2022-04-14 17:57 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22041400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-14 | 393 | keep | 0 | Apr | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-04-14 17:56 | 2022-04-14 17:57 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22041400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-14 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-14 18:04 | 2022-04-14 18:05 | 1860 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO | S22041400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-14 | 1860 | keep | 0 | Apr | 2022 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
BAYAMON | 2022-04-14 18:05 | 2022-04-14 19:35 | 100 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | S22041400310 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 90 | 2022-04-14 | 9000 | keep | 0 | Apr | 2022 | 0.0061299 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-04-14 18:14 | 2022-04-14 18:32 | 1 | 000:18 | P | DESGANCHE | 1X30 EN C/L | C22041400122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2022-04-14 | 18 | keep | 0 | Apr | 2022 | 1.226e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-14 18:33 | 2022-04-15 07:24 | 12 | 012:51 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C22041400123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 771 | 2022-04-14 | 9252 | keep | 0 | Apr | 2022 | 0.0063015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-04-14 18:47 | 2022-04-14 21:06 | 2 | 002:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22041400178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-04-14 | 278 | keep | 0 | Apr | 2022 | 0.00018934 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-04-14 18:50 | 2022-04-14 21:16 | 3332 | 002:26 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO POR SCADA. SE TRABAJO CON GOI BY220414-02A | B22041400183 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 146 | 2022-04-14 | 486472 | keep | 0 | Apr | 2022 | 0.33133 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
MAYAGÃœEZ | 2022-04-14 19:05 | 2022-04-15 08:25 | 20 | 013:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO GLOBO CRUZANDO FASES | M22041400200 | New_Event |  |  | Include | Wildlife | 800 | 2022-04-14 | 16000 | keep | 0 | Apr | 2022 | 0.010898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-14 19:11 | 2022-04-14 19:12 | 3838 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R22041400105 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-14 | 3838 | keep | 0 | Apr | 2022 | 0.002614 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
MAYAGÃœEZ | 2022-04-14 19:11 | 2022-04-15 12:40 | 300 | 017:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | M22041400201 | New_Event | Wire Down | Include | Include | Equipment | 1049 | 2022-04-14 | 314700 | keep | 0 | Apr | 2022 | 0.21434 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-04-14 19:12 | 2022-04-14 22:28 | 5 | 003:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO PUENTE ABIERTO NO FUNDIO FUSIBLE | R22041400108 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 196 | 2022-04-14 | 980 | keep | 0 | Apr | 2022 | 0.00066747 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-04-14 19:15 | 2022-04-14 19:16 | 5668 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22041400106 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-04-14 | 5668 | keep | 0 | Apr | 2022 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2022-04-14 19:16 | 2022-04-14 22:10 | 50 | 002:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | R22041400107 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 174 | 2022-04-14 | 8700 | keep | 0 | Apr | 2022 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-14 19:40 | 2022-04-14 19:42 | 3871 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-14 | 7742 | keep | 0 | Apr | 2022 | 0.005273 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
BAYAMON | 2022-04-14 19:50 | 2022-04-15 10:00 | 110 | 014:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S22041400355 | New_Event | Vegetation Contact | Include | Include | Vegetation | 850 | 2022-04-14 | 93500 | keep | 0 | Apr | 2022 | 0.063682 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2022-04-14 19:50 | 2022-04-14 19:51 | 1647 | 000:01 | T | DESGANCHE | RECIERRE | C22041400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-14 | 1647 | keep | 0 | Apr | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
CAGUAS | 2022-04-14 19:51 | 2022-04-14 23:39 | 549 | 003:48 | P | DESGANCHE | 1 X 140 EN SALIDA DEL CONVERTIDOR Y 1 X 65 EN CORTE DE LINEA RETIRO BAMBUAS Y REEMPLAZO PORTAFUSIBLE QUEMADO | C22041400132 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 228 | 2022-04-14 | 125172 | keep | 0 | Apr | 2022 | 0.085254 | 0.00037392 | Sustained | FALSE | FALSE | Not_TMED_Event | 549
BAYAMON | 2022-04-14 19:59 | 2022-04-14 21:41 | 56 | 001:42 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA RAMA CAYO SOBRE LINEAS | B22041400227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-04-14 | 5712 | keep | 0 | Apr | 2022 | 0.0038904 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2022-04-14 20:00 | 2022-04-14 20:57 | 3511 | 000:57 | T | DESGANCHE | SE RETIRO CON VARETA PALMA CRUZANDO LAS 3 FASES SE CERRO POR SCADA | B22041400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-04-14 | 200127 | keep | 0 | Apr | 2022 | 0.13631 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2022-04-14 20:14 | 2022-04-14 20:15 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO 1720-08 | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 2402 | keep | 0 | Apr | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-04-14 20:14 | 2022-04-14 20:15 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO CARGA 1720-08 | S22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-14 20:30 | 2022-04-14 20:32 | 5809 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1710-02 LLEVANDO CARGA 1710-01 | B22041400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-14 | 11618 | keep | 0 | Apr | 2022 | 0.007913 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-04-14 20:34 | 2022-04-14 23:08 | 5 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22041400341 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-04-14 | 770 | keep | 0 | Apr | 2022 | 0.00052444 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-04-14 20:41 | 2022-04-15 12:35 | 12 | 015:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22041400101 | New_Event | Cutout Failure | Include | Include | Equipment | 954 | 2022-04-14 | 11448 | keep | 0 | Apr | 2022 | 0.0077972 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-04-14 20:46 | 2022-04-15 03:45 | 20 | 006:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | M22041400224 | New_Event | Cutout Failure | Include | Include | Equipment | 419 | 2022-04-14 | 8380 | keep | 0 | Apr | 2022 | 0.0057076 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-04-14 20:50 | 2022-04-15 10:00 | 35 | 013:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE Y REEMPLAZO PORTAFUSIBLE | R22041400115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 790 | 2022-04-14 | 27650 | keep | 0 | Apr | 2022 | 0.018832 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-04-14 20:54 | 2022-04-15 09:30 | 250 | 012:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22041400103 | New_Event | Cutout Failure | Include | Include | Equipment | 756 | 2022-04-14 | 189000 | keep | 0 | Apr | 2022 | 0.12873 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-04-14 21:17 | 2022-04-15 02:54 | 80 | 005:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22041400398 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2022-04-14 | 26960 | keep | 0 | Apr | 2022 | 0.018362 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-14 21:24 | 2022-04-15 12:41 | 29 | 015:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22041400404 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 917 | 2022-04-14 | 26593 | keep | 0 | Apr | 2022 | 0.018112 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
VEGA BAJA | 2022-04-14 21:38 | 2022-04-15 16:44 | 80 | 019:06 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22041400414 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1146 | 2022-04-14 | 91680 | keep | 0 | Apr | 2022 | 0.062443 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-04-14 21:40 | 2022-04-15 10:18 | 28 | 012:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | R22041400118 | New_Event | Secondary Wire Down | Include | Include | Equipment | 758 | 2022-04-14 | 21224 | keep | 0 | Apr | 2022 | 0.014456 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
CAGUAS | 2022-04-14 21:56 | 2022-04-15 10:28 | 12 | 012:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR NO FUNDIO | C22041400162 | New_Event | Wire Down | Include | Include | Equipment | 752 | 2022-04-14 | 9024 | keep | 0 | Apr | 2022 | 0.0061462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-14 21:57 | 2022-04-15 02:04 | 52 | 004:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22041400421 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2022-04-14 | 12844 | keep | 0 | Apr | 2022 | 0.008748 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2022-04-14 22:19 | 2022-04-15 11:04 | 15 | 012:45 | P | DESGANCHE | 1 X 80 EN C/L Y 1 X 30 EN C/L DESGANCHE | S22041400331 | New_Event | Vegetation Contact | Include | Include | Vegetation | 765 | 2022-04-14 | 11475 | keep | 0 | Apr | 2022 | 0.0078156 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-14 22:34 | 2022-04-15 16:30 | 60 | 017:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE, SE REMPLAZO AISLADOR ROTO Y SE REPARO LINEA PRIMARIA ROTA | M22041400238 | New_Event | Wire Down | Include | Include | Equipment | 1076 | 2022-04-14 | 64560 | keep | 0 | Apr | 2022 | 0.043972 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-04-14 23:02 | 2022-04-15 08:40 | 30 | 009:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE. | P22041400210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 578 | 2022-04-14 | 17340 | keep | 0 | Apr | 2022 | 0.01181 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-14 23:30 | 2022-04-15 04:26 | 200 | 004:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22041400245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-04-14 | 59200 | keep | 0 | Apr | 2022 | 0.040321 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-04-14 23:43 | 2022-04-14 23:44 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041400110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-04-14 23:52 | 2022-04-14 23:54 | 3654 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE PROBO Y QUEDO EN SERVICIO | A22041400112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-14 | 7308 | keep | 0 | Apr | 2022 | 0.0049774 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
ARECIBO | 2022-04-14 23:52 | 2022-04-14 23:54 | 2888 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE PROBO Y QUEDO EN SERVICIO | A22041400111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-14 | 5776 | keep | 0 | Apr | 2022 | 0.003934 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
ARECIBO | 2022-04-14 23:56 | 2022-04-14 23:57 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041400113 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-14 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-04-15 01:05 | 2022-04-15 12:23 | 50 | 011:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22041500002 | New_Event | Cutout Failure | Include | Include | Equipment | 678 | 2022-04-15 | 33900 | keep | 0 | Apr | 2022 | 0.023089 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-15 01:20 | 2022-04-15 16:09 | 40 | 014:49 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTES DE LINEA DIFERENTES INFORMA REQUIERE DESGANCHE | M22041500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 889 | 2022-04-15 | 35560 | keep | 0 | Apr | 2022 | 0.02422 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-15 01:36 | 2022-04-15 04:50 | 150 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22041500153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-04-15 | 29100 | keep | 0 | Apr | 2022 | 0.01982 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-04-15 02:06 | 2022-04-15 08:13 | 80 | 006:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REMPLAZO AISLADOR ROTO | C22041500001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 367 | 2022-04-15 | 29360 | keep | 0 | Apr | 2022 | 0.019997 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-15 02:10 | 2022-04-15 09:42 | 70 | 007:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22041500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 452 | 2022-04-15 | 31640 | keep | 0 | Apr | 2022 | 0.02155 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-04-15 02:12 | 2022-04-15 03:40 | 1681 | 001:28 | T | DESGANCHE | SE SECCIONALIZO PARA REALIZAR DESGANCHE CARGA POR EL 1303-04 | S22041500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-04-15 | 147928 | keep | 0 | Apr | 2022 | 0.10075 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-15 02:12 | 2022-04-15 03:40 | 1598 | 001:28 | T | DESGANCHE | SE SECCIONALIZO PARA REALIZAR DESGANCHE CARGA POR EL 1303-04 | S22041500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-04-15 | 140624 | keep | 0 | Apr | 2022 | 0.095778 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2022-04-15 02:24 | 2022-04-15 09:35 | 98 | 007:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B22041500006 | New_Event | Cutout Failure | Include | Include | Equipment | 431 | 2022-04-15 | 42238 | keep | 0 | Apr | 2022 | 0.028768 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
BAYAMON | 2022-04-15 02:31 | 2022-04-15 02:34 | 2617 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-15 | 7851 | keep | 0 | Apr | 2022 | 0.0053473 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2022-04-15 03:33 | 2022-04-15 06:45 | 143 | 003:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B22041500013 | New_Event | Cutout Failure | Include | Include | Equipment | 192 | 2022-04-15 | 27456 | keep | 0 | Apr | 2022 | 0.0187 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-04-15 03:40 | 2022-04-15 06:28 | 340 | 002:48 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETE 100% EN SERVICIO SU CARGA POR 1303-4 | S22041500005 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-04-15 | 57120 | keep | 0 | Apr | 2022 | 0.038904 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-04-15 04:58 | 2022-04-15 08:49 | 44 | 003:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L SE REMPLAZO AISLADOR Y CAJA PRIMARIA | B22041500014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 231 | 2022-04-15 | 10164 | keep | 0 | Apr | 2022 | 0.0069227 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
SAN JUAN | 2022-04-15 06:02 | 2022-04-15 08:45 | 100 | 002:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S22041500046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-04-15 | 16300 | keep | 0 | Apr | 2022 | 0.011102 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-04-15 06:06 | 2022-04-15 06:07 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 1310 | keep | 0 | Apr | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
FAJARDO | 2022-04-15 06:23 | 2022-04-15 08:14 | 15 | 001:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22041500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-04-15 | 1665 | keep | 0 | Apr | 2022 | 0.001134 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-15 07:05 | 2022-04-15 12:15 | 100 | 005:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M22041500007 | New_Event |  |  | Include | Wildlife | 310 | 2022-04-15 | 31000 | keep | 0 | Apr | 2022 | 0.021114 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-15 07:20 | 2022-04-15 09:00 | 1 | 001:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | M22041500009 | New_Event |  |  | Include | Wildlife | 100 | 2022-04-15 | 100 | keep | 0 | Apr | 2022 | 6.811e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-15 07:22 | 2022-04-15 07:23 | 3941 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | B22041500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-15 | 3941 | keep | 0 | Apr | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-04-15 07:23 | 2022-04-15 12:36 | 300 | 005:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A MACHETE | B22041500025 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 313 | 2022-04-15 | 93900 | keep | 0 | Apr | 2022 | 0.063955 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-04-15 07:32 | 2022-04-15 10:50 | 150 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M22041500012 | New_Event |  |  | Include | Wildlife | 198 | 2022-04-15 | 29700 | keep | 0 | Apr | 2022 | 0.020229 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-04-15 07:35 | 2022-04-15 12:24 | 54 | 004:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE POR AVE | B22041500024 | New_Event |  |  | Include | Wildlife | 289 | 2022-04-15 | 15606 | keep | 0 | Apr | 2022 | 0.010629 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
ARECIBO | 2022-04-15 08:07 | 2022-04-15 15:00 | 60 | 006:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 Y 1 X 25 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | A22041500013 | New_Event | Cutout Failure | Include | Include | Equipment | 413 | 2022-04-15 | 24780 | keep | 0 | Apr | 2022 | 0.016878 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-15 08:14 | 2022-04-15 12:40 | 7 | 004:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CLIENTE DESGANCHANDO CRUZO LINEAS CON RAMAS DE ARBOL | A22041500014 | New_Event |  |  | Include | Wildlife | 266 | 2022-04-15 | 1862 | keep | 0 | Apr | 2022 | 0.0012682 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-04-15 08:16 | 2022-04-15 10:18 | 10 | 002:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA PORTAFUSIBLE | S22041500054 | New_Event | Cutout Failure | Include | Include | Equipment | 122 | 2022-04-15 | 1220 | keep | 0 | Apr | 2022 | 0.00083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-04-15 08:22 | 2022-04-15 09:55 | 1 | 001:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN RISER AVE CRUZO FASE | P22041500007 | New_Event |  |  | Include | Wildlife | 93 | 2022-04-15 | 93 | keep | 0 | Apr | 2022 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-15 08:23 | 2022-04-15 10:55 | 137 | 002:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22041500035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-04-15 | 20824 | keep | 0 | Apr | 2022 | 0.014183 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
YAUCO | 2022-04-15 08:29 | 2022-04-15 10:10 | 3 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P22041500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-04-15 | 303 | keep | 0 | Apr | 2022 | 0.00020637 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-04-15 08:34 | 2022-04-15 10:13 | 40 | 001:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | S22041500056 | New_Event |  |  | Include | Wildlife | 99 | 2022-04-15 | 3960 | keep | 0 | Apr | 2022 | 0.0026971 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-15 08:48 | 2022-04-15 10:58 | 60 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A22041500019 | New_Event |  |  | Include | Wildlife | 130 | 2022-04-15 | 7800 | keep | 0 | Apr | 2022 | 0.0053125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-04-15 09:15 | 2022-04-15 10:33 | 576 | 001:18 | T | DESGANCHE | SE ABRE INTERRUPTOR PARA RETIRAR ARBOL DEL TRONCAL DEL ALIMENTADOR | P22041500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-04-15 | 44928 | keep | 0 | Apr | 2022 | 0.0306 | 0.00039231 | Sustained | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-04-15 09:15 | 2022-04-15 10:33 | 2584 | 001:18 | T | DESGANCHE | SE ABRE INTERRUPTOR PARA RETIRAR ARBOL DEL TRONCAL DEL ALIMENTADOR | P22041500018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-04-15 | 201552 | keep | 0 | Apr | 2022 | 0.13728 | 0.00176 | Sustained | FALSE | FALSE | Not_TMED_Event | 2584
BAYAMON | 2022-04-15 09:25 | 2022-04-15 09:26 | 767 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-07 LLEVANDO 50% DE LA CARGA 1709-03 | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 767 | keep | 0 | Apr | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-04-15 09:25 | 2022-04-15 09:26 | 1139 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-07 LLEVANDO 50% DE LA CARGA 1709-03 | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 1139 | keep | 0 | Apr | 2022 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
SAN JUAN | 2022-04-15 09:42 | 2022-04-15 12:54 | 25 | 003:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22041500071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-04-15 | 4800 | keep | 0 | Apr | 2022 | 0.0032693 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-04-15 09:46 | 2022-04-15 13:09 | 40 | 003:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-04-15 | 8120 | keep | 0 | Apr | 2022 | 0.0055305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-04-15 09:51 | 2022-04-15 10:11 | 1 | 000:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER REMPLAZO PORTAFUSIBLE QUEMADO | C22041500013 | New_Event | Cutout Failure | Include | Include | Equipment | 20 | 2022-04-15 | 20 | keep | 0 | Apr | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-15 10:02 | 2022-04-15 12:06 | 138 | 002:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L FIJO CAJA | C22041500016 | New_Event | Cutout Failure | Include | Include | Equipment | 124 | 2022-04-15 | 17112 | keep | 0 | Apr | 2022 | 0.011655 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
AGUADILLA | 2022-04-15 10:03 | 2022-04-15 17:02 | 6 | 006:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22041500022 | New_Event | Bad Weather | Include | Include | Weather | 419 | 2022-04-15 | 2514 | keep | 0 | Apr | 2022 | 0.0017123 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-15 10:15 | 2022-04-15 10:16 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2204150000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 3597 | keep | 0 | Apr | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
CAGUAS | 2022-04-15 10:25 | 2022-04-15 10:45 | 1 | 000:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO CAUSA | C22041500018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-04-15 | 20 | keep | 0 | Apr | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-04-15 10:25 | 2022-04-15 23:56 | 3 | 013:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22041500043 | New_Event | Bad Weather | Include | Include | Weather | 811 | 2022-04-15 | 2433 | keep | 0 | Apr | 2022 | 0.0016571 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-04-15 10:28 | 2022-04-15 10:29 | 1494 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR AVE CRUZO LINEAS | A22041500030 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-15 | 1494 | keep | 0 | Apr | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
MAYAGÃœEZ | 2022-04-15 10:29 | 2022-04-15 10:33 | 1444 | 000:04 | T | NO SE REPORTO CAUSA | SU CARGA TRANSFERIDA AL 6014-02 | M22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-15 | 5776 | keep | 0 | Apr | 2022 | 0.003934 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-04-15 10:29 | 2022-04-15 10:33 | 3630 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 6014-01 | M22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-04-15 | 14520 | keep | 0 | Apr | 2022 | 0.0098895 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
ARECIBO | 2022-04-15 10:29 | 2022-04-15 12:15 | 150 | 001:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA AVES CRUZARON LINEAS | A22041500031 | 1st_after_momentary |  |  | Include | Wildlife | 106 | 2022-04-15 | 15900 | keep | 0 | Apr | 2022 | 0.010829 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-04-15 10:30 | 2022-04-15 10:31 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 478 | keep | 0 | Apr | 2022 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-04-15 10:30 | 2022-04-15 10:31 | 854 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 854 | keep | 0 | Apr | 2022 | 0.00058166 | 0.00058166 | Momentary | FALSE | FALSE | Not_TMED_Event | 854
BARRANQUITAS | 2022-04-15 10:39 | 2022-04-15 12:30 | 1 | 001:51 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR NO CAUSA | C22041500019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-04-15 | 111 | keep | 0 | Apr | 2022 | 7.5602e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-15 10:46 | 2022-04-15 10:47 | 8 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22041500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 8 | keep | 0 | Apr | 2022 | 5.4488e-06 | 5.4488e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-04-15 10:47 | 2022-04-15 11:59 | 30 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 30 EN TRANSFORMADOR AVE CRUZO FASE | P22041500033 | New_Event |  |  | Include | Wildlife | 72 | 2022-04-15 | 2160 | keep | 0 | Apr | 2022 | 0.0014712 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-04-15 10:50 | 2022-04-15 11:27 | 3 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22041500030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-04-15 | 111 | keep | 0 | Apr | 2022 | 7.5602e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-04-15 10:53 | 2022-04-16 05:30 | 3 | 018:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR SE ENCONTRO AVE QUEMADA EN TRANSFORMADOR | M22041500196 | New_Event |  |  | Include | Wildlife | 1117 | 2022-04-15 | 3351 | keep | 0 | Apr | 2022 | 0.0022824 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-04-15 10:56 | 2022-04-15 17:55 | 8 | 006:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA PARTIDA (TRASPATIO) | B22041500059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 419 | 2022-04-15 | 3352 | keep | 0 | Apr | 2022 | 0.002283 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-15 11:01 | 2022-04-15 11:56 | 40 | 000:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L SE RETIRO GLOBO METALICO | B22041500063 | New_Event |  |  | Include | Wildlife | 55 | 2022-04-15 | 2200 | keep | 0 | Apr | 2022 | 0.0014984 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-04-15 11:05 | 2022-04-15 11:26 | 30 | 000:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE CORTE DE LINEA PARA FIJAR AISLADOR A CRUCETA | P22041500039 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 21 | 2022-04-15 | 630 | keep | 0 | Apr | 2022 | 0.00042909 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-15 11:06 | 2022-04-15 11:07 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-2 | S22041500086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-04-15 11:06 | 2022-04-15 11:07 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1206-1 | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2022-04-15 11:06 | 2022-04-16 11:38 | 50 | 024:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA TRASPATIO | B22041500067 | New_Event | Cutout Failure | Include | Include | Equipment | 1472 | 2022-04-15 | 73600 | keep | 0 | Apr | 2022 | 0.050129 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-15 11:12 | 2022-04-15 14:35 | 100 | 003:23 | P | DESGANCHE | 1 X 65 EN C/L | C22041500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-04-15 | 20300 | keep | 0 | Apr | 2022 | 0.013826 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-15 11:55 | 2022-04-15 15:41 | 100 | 003:46 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22041500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-04-15 | 22600 | keep | 0 | Apr | 2022 | 0.015393 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-15 11:57 | 2022-04-15 11:58 | 2402 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO CARGA 1720-08 | S22041500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-15 | 2402 | keep | 0 | Apr | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-04-15 11:57 | 2022-04-15 11:58 | 1 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO CARGA 1720-08 | S22041500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-15 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-15 11:57 | 2022-04-15 11:58 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22041500043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 2697 | keep | 0 | Apr | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
BAYAMON | 2022-04-15 12:00 | 2022-04-16 00:36 | 10 | 012:36 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | S22041500088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 756 | 2022-04-15 | 7560 | keep | 0 | Apr | 2022 | 0.0051491 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-04-15 12:15 | 2022-04-15 14:42 | 20 | 002:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES | M22041500065 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2022-04-15 | 2940 | keep | 0 | Apr | 2022 | 0.0020024 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-04-15 12:16 | 2022-04-15 12:17 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVANDO EL 70% DEL 2402-02 EN SERVICIO | R22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 1648 | keep | 0 | Apr | 2022 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-04-15 12:16 | 2022-04-15 12:17 | 1153 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 2302-03 EN SERVICIO | R22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 1153 | keep | 0 | Apr | 2022 | 0.0007853 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
AGUADILLA | 2022-04-15 12:19 | 2022-04-15 23:09 | 60 | 010:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22041500066 | New_Event | Bad Weather | Include | Include | Weather | 650 | 2022-04-15 | 39000 | keep | 0 | Apr | 2022 | 0.026563 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-04-15 12:19 | 2022-04-15 17:31 | 25 | 005:12 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR BAMBUA | A22041500046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2022-04-15 | 7800 | keep | 0 | Apr | 2022 | 0.0053125 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-15 12:22 | 2022-04-15 16:11 | 10 | 003:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN AEREO PROVISIONAL | B22041500080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-04-15 | 2290 | keep | 0 | Apr | 2022 | 0.0015597 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-15 12:34 | 2022-04-15 14:13 | 2402 | 001:39 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 | S22041500084 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 99 | 2022-04-15 | 237798 | keep | 0 | Apr | 2022 | 0.16196 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-04-15 12:34 | 2022-04-15 14:13 | 1 | 001:39 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - CARGA TRANSFERIDA AL 1709-02 | S22041500084 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 99 | 2022-04-15 | 99 | keep | 0 | Apr | 2022 | 6.7428e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-04-15 12:36 | 2022-04-15 14:29 | 5 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR Y 1 X 20 EN C/L CRUCE POR AVE | R22041500020 | New_Event |  |  | Include | Wildlife | 113 | 2022-04-15 | 565 | keep | 0 | Apr | 2022 | 0.00038482 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-04-15 12:41 | 2022-04-15 12:42 | 519 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 519 | keep | 0 | Apr | 2022 | 0.00035349 | 0.00035349 | Momentary | FALSE | FALSE | Not_TMED_Event | 519
SAN JUAN | 2022-04-15 12:42 | 2022-04-15 15:37 | 10 | 002:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO Y NEUTRAL | S22041500097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 175 | 2022-04-15 | 1750 | keep | 0 | Apr | 2022 | 0.0011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-15 12:45 | 2022-04-15 22:14 | 40 | 009:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22041500069 | New_Event | Bad Weather | Include | Include | Weather | 569 | 2022-04-15 | 22760 | keep | 0 | Apr | 2022 | 0.015502 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-15 12:51 | 2022-04-15 18:05 | 150 | 005:14 | P | DESGANCHE | 3 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22041500053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2022-04-15 | 47100 | keep | 0 | Apr | 2022 | 0.03208 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-04-15 12:59 | 2022-04-15 23:37 | 50 | 010:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041500124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 638 | 2022-04-15 | 31900 | keep | 0 | Apr | 2022 | 0.021727 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-15 13:01 | 2022-04-15 14:45 | 100 | 001:44 | P | NO SE REPORTO CAUSA | 1X100 DE RISER @ SU-5 | B22041500100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-04-15 | 10400 | keep | 0 | Apr | 2022 | 0.0070834 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-15 13:14 | 2022-04-15 23:28 | 100 | 010:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22041500119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 614 | 2022-04-15 | 61400 | keep | 0 | Apr | 2022 | 0.041819 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-15 13:17 | 2022-04-15 16:45 | 50 | 003:28 | P | DESGANCHE | 1 X 30 EN C/L | C22041500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-04-15 | 10400 | keep | 0 | Apr | 2022 | 0.0070834 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-15 13:25 | 2022-04-15 15:43 | 1 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTER DE LINEA POR VIENTOS | A22041500057 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2022-04-15 | 138 | keep | 0 | Apr | 2022 | 9.3991e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-15 13:27 | 2022-04-17 09:00 | 60 | 043:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 30 EN C/L SE REMPLAZO BARRA DE PEDESTAL EN XMR AUTOPROTEGIDO Y SE CERRO CORTE DE LINEA | B22041600089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2613 | 2022-04-15 | 156780 | keep | 0 | Apr | 2022 | 0.10678 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-15 13:30 | 2022-04-15 16:34 | 685 | 003:04 | P | DESGANCHE | 1X100 EN C/L | B22041500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-04-15 | 126040 | keep | 0 | Apr | 2022 | 0.085845 | 0.00046655 | Sustained | FALSE | FALSE | Not_TMED_Event | 685
SAN JUAN | 2022-04-15 13:31 | 2022-04-15 13:32 | 1106 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 60% POR 1529-15 SE PROBO QUEDO EN SERVICIO | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 1106 | keep | 0 | Apr | 2022 | 0.00075329 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
BAYAMON | 2022-04-15 13:31 | 2022-04-15 13:32 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 60% DEL 1346-2 SE PROBO QUEDO EN SERVICIO | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 1802 | keep | 0 | Apr | 2022 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
CAGUAS | 2022-04-15 13:32 | 2022-04-15 16:26 | 6 | 002:54 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C22041500034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 174 | 2022-04-15 | 1044 | keep | 0 | Apr | 2022 | 0.00071106 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-04-15 13:51 | 2022-04-15 13:52 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041500037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 2635 | keep | 0 | Apr | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-04-15 13:52 | 2022-04-15 16:01 | 200 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22041500044 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 129 | 2022-04-15 | 25800 | keep | 0 | Apr | 2022 | 0.017572 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-04-15 14:02 | 2022-04-15 14:03 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE NO SE REPORTO CAUSA | P22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 2163 | keep | 0 | Apr | 2022 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
AGUADILLA | 2022-04-15 14:05 | 2022-04-15 16:38 | 300 | 002:33 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE | M22041500090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-04-15 | 45900 | keep | 0 | Apr | 2022 | 0.031262 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-04-15 14:09 | 2022-04-15 17:46 | 120 | 003:37 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHO | C22041500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-04-15 | 26040 | keep | 0 | Apr | 2022 | 0.017736 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-04-15 14:13 | 2022-04-15 14:33 | 2162 | 000:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 | S22041500084 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 20 | 2022-04-15 | 43240 | keep | 0 | Apr | 2022 | 0.029451 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-15 14:13 | 2022-04-15 14:33 | 1 | 000:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - CARGA TRANSFERIDA AL 1709-02 | S22041500084 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 20 | 2022-04-15 | 20 | keep | 0 | Apr | 2022 | 1.3622e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-04-15 14:13 | 2022-04-15 19:00 | 150 | 004:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22041500094 | New_Event | Bad Weather | Include | Include | Weather | 287 | 2022-04-15 | 43050 | keep | 0 | Apr | 2022 | 0.029321 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-04-15 14:20 | 2022-04-15 19:04 | 15 | 004:44 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR RAMA PARTIO CONEXIONES | A22041500061 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 284 | 2022-04-15 | 4260 | keep | 0 | Apr | 2022 | 0.0029015 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-04-15 14:21 | 2022-04-15 17:21 | 60 | 003:00 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22041500031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-04-15 | 10800 | keep | 0 | Apr | 2022 | 0.0073558 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-04-15 14:27 | 2022-04-15 15:36 | 100 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN C/L LLUVIAS | R22041500032 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2022-04-15 | 6900 | keep | 0 | Apr | 2022 | 0.0046996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-15 14:33 | 2022-04-15 14:34 | 2402 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 | S22041500084 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-15 | 2402 | keep | 0 | Apr | 2022 | 0.001636 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-15 14:33 | 2022-04-15 14:34 | 1 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - CARGA TRANSFERIDA AL 1709-02 | S22041500084 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-15 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-15 14:34 | 2022-04-15 15:11 | 2162 | 000:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 ALIMENTADOR 1720-08 ENTRO 100% EN SERVICIO | S22041500084 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 37 | 2022-04-15 | 79994 | keep | 0 | Apr | 2022 | 0.054484 | 0.0014725 | Sustained | FALSE | FALSE | Not_TMED_Event | 2162
BAYAMON | 2022-04-15 14:34 | 2022-04-15 15:11 | 1 | 000:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - CARGA TRANSFERIDA AL 1709-02 | S22041500084 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 37 | 2022-04-15 | 37 | keep | 0 | Apr | 2022 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-15 14:38 | 2022-04-15 17:42 | 200 | 003:04 | P | DESCONECTIVO DEFECTUOSO | 2 X 100 EN C/L SE REMPLAZO MACHETE QUEMADO Y CAJA QUEMADA | P22041500058 | New_Event | Switch Failure | Include | Include | Equipment | 184 | 2022-04-15 | 36800 | keep | 0 | Apr | 2022 | 0.025064 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-04-15 14:45 | 2022-04-15 16:19 | 50 | 001:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L AVE CRUZO LINEAS | P22041500069 | New_Event |  |  | Include | Wildlife | 94 | 2022-04-15 | 4700 | keep | 0 | Apr | 2022 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-15 14:45 | 2022-04-15 17:41 | 15 | 002:56 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA SOTERADA DEL T-16 @ T-17 | B22041500131 | New_Event | UG Cable Fault | Include | Include | Equipment | 176 | 2022-04-15 | 2640 | keep | 0 | Apr | 2022 | 0.0017981 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-15 14:46 | 2022-04-15 21:14 | 7 | 006:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REALIZO DESGANCHE Y SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M22041500118 | New_Event | Wire Down | Include | Include | Equipment | 388 | 2022-04-15 | 2716 | keep | 0 | Apr | 2022 | 0.0018499 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-04-15 14:53 | 2022-04-15 20:08 | 300 | 005:15 | P | CABLE SOTERRADO AVERIADO | 1X140 EN RISER 1X100 EN SU-3 @ PROVISIONAL AEREO, HAY AVERIA DEL T-31 @ SU-4 (RADIAL DEL SU-2 @ SU-4) INFORMA EL EMPLEADO QUE EL DISTRITO SE HARA CARGO | B22041500135 | New_Event | UG Cable Fault | Include | Include | Equipment | 315 | 2022-04-15 | 94500 | keep | 0 | Apr | 2022 | 0.064364 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-04-15 14:56 | 2022-04-15 14:57 | 601 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1437-2 | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 601 | keep | 0 | Apr | 2022 | 0.00040934 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-04-15 14:56 | 2022-04-15 14:57 | 640 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1437-1 | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 640 | keep | 0 | Apr | 2022 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-04-15 14:57 | 2022-04-16 09:08 | 200 | 018:11 | P | DESGANCHE | 1X100 EN C/L | S22041500161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1091 | 2022-04-15 | 218200 | keep | 0 | Apr | 2022 | 0.14862 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-04-15 15:04 | 2022-04-15 15:05 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 3597 | keep | 0 | Apr | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-04-15 15:11 | 2022-04-15 17:11 | 240 | 002:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 (EL CUAL NO SE AFECTO) | S22041500084 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 120 | 2022-04-15 | 28800 | keep | 0 | Apr | 2022 | 0.019616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-15 15:19 | 2022-04-16 13:25 | 30 | 022:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22041500140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1326 | 2022-04-15 | 39780 | keep | 0 | Apr | 2022 | 0.027094 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-04-15 15:21 | 2022-04-15 21:03 | 66 | 005:42 | P | DESGANCHE | 1 X 30 EN C/L | C22041500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2022-04-15 | 22572 | keep | 0 | Apr | 2022 | 0.015374 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2022-04-15 15:22 | 2022-04-15 15:23 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 1834 | keep | 0 | Apr | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
YAUCO | 2022-04-15 15:23 | 2022-04-15 17:16 | 50 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN C/L AVE CRUZO LINEAS | P22041500086 | New_Event |  |  | Include | Wildlife | 113 | 2022-04-15 | 5650 | keep | 0 | Apr | 2022 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-15 15:24 | 2022-04-15 18:25 | 150 | 003:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22041500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-04-15 | 27150 | keep | 0 | Apr | 2022 | 0.018492 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-04-15 15:25 | 2022-04-15 15:26 | 2722 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R22041500040 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-15 | 2722 | keep | 0 | Apr | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2022-04-15 15:26 | 2022-04-15 17:29 | 200 | 002:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN C/L SE LEVANTO CONDUCTOR PRIMARIO Y REEMPLAZO AISLADOR PARTIDO | R22041500041 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 123 | 2022-04-15 | 24600 | keep | 0 | Apr | 2022 | 0.016755 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-04-15 15:30 | 2022-04-15 15:31 | 1250 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22041500063 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-15 | 1250 | keep | 0 | Apr | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-04-15 15:31 | 2022-04-15 17:10 | 100 | 001:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22041500065 | 1st_after_momentary |  |  | Include | Wildlife | 99 | 2022-04-15 | 9900 | keep | 0 | Apr | 2022 | 0.0067428 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-15 15:31 | 2022-04-16 03:12 | 30 | 011:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22041500132 | New_Event | Bad Weather | Include | Include | Weather | 701 | 2022-04-15 | 21030 | keep | 0 | Apr | 2022 | 0.014323 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-15 15:31 | 2022-04-15 16:11 | 20 | 000:40 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO Y SE CERRO LOS PUENTES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A22041500075 | New_Event | Defective Pole | Include | Include | Equipment | 40 | 2022-04-15 | 800 | keep | 0 | Apr | 2022 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-04-15 15:33 | 2022-04-16 08:40 | 12 | 017:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22041500166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1027 | 2022-04-15 | 12324 | keep | 0 | Apr | 2022 | 0.0083938 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-15 15:38 | 2022-04-18 17:15 | 4 | 073:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR Y PARARRAYOS | B22041500147 | New_Event | Service Transformer Failure | Include | Include | Equipment | 4417 | 2022-04-15 | 17668 | keep | 0 | Apr | 2022 | 0.012034 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-04-15 15:51 | 2022-04-15 15:52 | 727 | 000:01 | P | DESGANCHE | DISPARO PARTE X 1620-2 | S22041500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-15 | 727 | keep | 0 | Apr | 2022 | 0.00049516 | 0.00049516 | Momentary | FALSE | FALSE | Not_TMED_Event | 727
SAN JUAN | 2022-04-15 15:51 | 2022-04-15 15:52 | 3718 | 000:01 | T | DESGANCHE | DISPARO LLEVA PARTE 1206-3 | S22041500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-15 | 3718 | keep | 0 | Apr | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
FAJARDO | 2022-04-15 15:51 | 2022-04-15 16:09 | 5 | 000:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR SE REEMPLAZO 2 TRAMOS DE SECUNDARIA AVERIADOS | R22041500043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 18 | 2022-04-15 | 90 | keep | 0 | Apr | 2022 | 6.1299e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-04-15 16:01 | 2022-04-15 19:25 | 727 | 003:24 | P | DESGANCHE | SE ABRIO N/O CONTRA 1620-2 PARA REPARAR PUENTE ABIERTO Y RETIRAR BAMBUA SOBRE LINEA | S22041500173 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-04-15 | 148308 | keep | 0 | Apr | 2022 | 0.10101 | 0.00049516 | Sustained | FALSE | FALSE | Not_TMED_Event | 727
SAN JUAN | 2022-04-15 16:01 | 2022-04-15 16:53 | 3718 | 000:52 | T | DESGANCHE | DISPARO SE ABRIO N/O 1206-3 QUEBRADA GRANDE Y SE CERRO 1620-2 100% EN SERVICIO CONTNUAN PATRULLANDO | S22041500173 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 52 | 2022-04-15 | 193336 | keep | 0 | Apr | 2022 | 0.13168 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
ARECIBO | 2022-04-15 16:14 | 2022-04-16 13:00 | 20 | 020:46 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO Y SE CERRO LOS PUENTES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A22041500075 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1246 | 2022-04-15 | 24920 | keep | 0 | Apr | 2022 | 0.016973 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-15 16:17 | 2022-04-15 16:18 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-2 | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-04-15 16:17 | 2022-04-15 16:18 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1206-1 | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2022-04-15 16:17 | 2022-04-16 01:25 | 10 | 009:08 | P | NO SE REPORTO CAUSA | 1 X 15 EN AEREO PROVISIONAL | B22041500080 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 548 | 2022-04-15 | 5480 | keep | 0 | Apr | 2022 | 0.0037324 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-15 16:17 | 2022-04-15 19:37 | 5 | 003:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR SE REEMPLAZO 2 TRAMOS DE SECUNDARIA AVERIADOS | R22041500043 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 200 | 2022-04-15 | 1000 | keep | 0 | Apr | 2022 | 0.0006811 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-15 16:33 | 2022-04-16 01:12 | 40 | 008:39 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTES DE LINEA DIFERENTES INFORMA REQUIERE DESGANCHE | M22041500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 519 | 2022-04-15 | 20760 | keep | 0 | Apr | 2022 | 0.01414 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-15 16:37 | 2022-04-15 16:38 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 4431 | keep | 0 | Apr | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2022-04-15 16:41 | 2022-04-15 16:45 | 790 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE PROBO QUEDO EN SERVICIO | S22041500208 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2022-04-15 | 3160 | keep | 0 | Apr | 2022 | 0.0021523 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
BAYAMON | 2022-04-15 16:41 | 2022-04-15 16:44 | 1860 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE PROBO QUEDO EN SERVICIO | S22041500207 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-04-15 | 5580 | keep | 0 | Apr | 2022 | 0.0038005 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
BAYAMON | 2022-04-15 16:48 | 2022-04-16 03:13 | 790 | 010:25 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR CONTROL | S22041500213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 625 | 2022-04-15 | 493750 | keep | 0 | Apr | 2022 | 0.33629 | 0.00053807 | Sustained | FALSE | FALSE | Not_TMED_Event | 790
BAYAMON | 2022-04-15 16:52 | 2022-04-15 16:53 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 5252 | keep | 0 | Apr | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2022-04-15 16:53 | 2022-04-16 00:12 | 10 | 007:19 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B22041500219 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 439 | 2022-04-15 | 4390 | keep | 0 | Apr | 2022 | 0.00299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-15 16:54 | 2022-04-15 16:55 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041500094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 2179 | keep | 0 | Apr | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2022-04-15 16:54 | 2022-04-15 16:55 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041500093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 3046 | keep | 0 | Apr | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
BAYAMON | 2022-04-15 16:59 | 2022-04-15 17:00 | 1501 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | B22041500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-15 | 1501 | keep | 0 | Apr | 2022 | 0.0010223 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-04-15 17:00 | 2022-04-16 22:40 | 60 | 029:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO TRASPATIO | B22041500224 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1780 | 2022-04-15 | 106800 | keep | 0 | Apr | 2022 | 0.072741 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-04-15 17:06 | 2022-04-15 21:49 | 200 | 004:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN C/L Y SE REPARO BAJANTE PRIMARIO | R22041500107 | New_Event | Wire Down | Include | Include | Equipment | 283 | 2022-04-15 | 56600 | keep | 0 | Apr | 2022 | 0.03855 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-04-15 17:11 | 2022-04-15 17:48 | 120 | 000:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 | S22041500084 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 37 | 2022-04-15 | 4440 | keep | 0 | Apr | 2022 | 0.0030241 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-15 17:25 | 2022-04-16 11:09 | 9 | 017:44 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 25KVA X 25KVA | R22041500123 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1064 | 2022-04-15 | 9576 | keep | 0 | Apr | 2022 | 0.0065222 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2022-04-15 17:28 | 2022-04-15 19:06 | 30 | 001:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X30 EN C/L & SE REEMPLAZO AISLADOR & SE LLEVO CONDUCTOR AL AISLADOR | B22041500207 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 98 | 2022-04-15 | 2940 | keep | 0 | Apr | 2022 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-04-15 17:34 | 2022-04-15 18:08 | 20 | 000:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | C22041500136 | New_Event |  |  | Include | Wildlife | 34 | 2022-04-15 | 680 | keep | 0 | Apr | 2022 | 0.00046314 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-04-15 17:39 | 2022-04-15 18:59 | 150 | 001:20 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | P22041500148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-04-15 | 12000 | keep | 0 | Apr | 2022 | 0.0081731 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-04-15 17:47 | 2022-04-15 21:14 | 100 | 003:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L RETIRO GLOBO DE LINEA | C22041500145 | New_Event |  |  | Include | Wildlife | 207 | 2022-04-15 | 20700 | keep | 0 | Apr | 2022 | 0.014099 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-15 17:48 | 2022-04-15 19:54 | 121 | 002:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 (EL CUAL NO SE AFECTO) | S22041500084 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 126 | 2022-04-15 | 15246 | keep | 0 | Apr | 2022 | 0.010384 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-15 17:48 | 2022-04-15 21:17 | 70 | 003:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REEMPLAZO DOS AISLADORES PARTIDOS | A22041500095 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 209 | 2022-04-15 | 14630 | keep | 0 | Apr | 2022 | 0.0099644 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-04-15 17:50 | 2022-04-16 01:21 | 514 | 007:31 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES Y Y SE REALIZO DESGANCHE CARGA POR 1520-05 | S22041500277 | New_Event | Vegetation Contact | Include | Include | Vegetation | 451 | 2022-04-15 | 231814 | keep | 0 | Apr | 2022 | 0.15789 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2022-04-15 17:50 | 2022-04-16 01:12 | 752 | 007:22 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES Y SE REALIZO DESGANCHE CARGA POR 1520-05 | S22041500277 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2022-04-15 | 332384 | keep | 0 | Apr | 2022 | 0.22639 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2022-04-15 17:50 | 2022-04-16 00:51 | 68 | 007:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES Y SE REALIZO DESGANCHE LLEVA EL 1520-04 Y 1520-01 | S22041500277 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2022-04-15 | 28628 | keep | 0 | Apr | 2022 | 0.019498 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2022-04-15 18:02 | 2022-04-16 00:45 | 80 | 006:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN C/L LLUVIAS | B22041500227 | New_Event | Bad Weather | Include | Include | Weather | 403 | 2022-04-15 | 32240 | keep | 0 | Apr | 2022 | 0.021959 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-04-15 18:06 | 2022-04-15 18:20 | 70 | 000:14 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR BAMBUA | A22041500100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-04-15 | 980 | keep | 0 | Apr | 2022 | 0.00066747 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-04-15 18:08 | 2022-04-16 06:30 | 25 | 012:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041500181 | New_Event | Bad Weather | Include | Include | Weather | 742 | 2022-04-15 | 18550 | keep | 0 | Apr | 2022 | 0.012634 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-04-15 18:15 | 2022-04-15 18:18 | 539 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | R22041500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-04-15 | 1617 | keep | 0 | Apr | 2022 | 0.0011013 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
BAYAMON | 2022-04-15 18:15 | 2022-04-16 11:40 | 50 | 017:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22041500233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1045 | 2022-04-15 | 52250 | keep | 0 | Apr | 2022 | 0.035587 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-15 18:18 | 2022-04-15 21:25 | 55 | 003:07 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | R22041500142 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-04-15 | 10285 | keep | 0 | Apr | 2022 | 0.0070051 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2022-04-15 18:24 | 2022-04-15 18:25 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1705-01 LLEVANDO 90% 1705-03 | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 478 | keep | 0 | Apr | 2022 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-04-15 18:24 | 2022-04-15 18:25 | 854 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 854 | keep | 0 | Apr | 2022 | 0.00058166 | 0.00058166 | Momentary | FALSE | FALSE | Not_TMED_Event | 854
SAN JUAN | 2022-04-15 18:28 | 2022-04-15 18:29 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S22041500297 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 172 | keep | 0 | Apr | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2022-04-15 18:38 | 2022-04-15 21:16 | 2324 | 002:38 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO @ SALIDA DE LA SUBESTACION MEDIANTE G.O.I. BY-220415-03 | B22041500251 | New_Event | Wire Down | Include | Include | Equipment | 158 | 2022-04-15 | 367192 | keep | 0 | Apr | 2022 | 0.25009 | 0.0015829 | Sustained | FALSE | FALSE | Not_TMED_Event | 2324
MAYAGÃœEZ | 2022-04-15 18:40 | 2022-04-15 18:41 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041500194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 3458 | keep | 0 | Apr | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
BAYAMON | 2022-04-15 18:43 | 2022-04-15 18:44 | 1085 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 1085 | keep | 0 | Apr | 2022 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2022-04-15 18:55 | 2022-04-15 23:28 | 75 | 004:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22041500253 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 273 | 2022-04-15 | 20475 | keep | 0 | Apr | 2022 | 0.013945 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-04-15 18:58 | 2022-04-15 19:01 | 1500 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR - SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1801-02 | B22041500261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-15 | 4500 | keep | 0 | Apr | 2022 | 0.0030649 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
BAYAMON | 2022-04-15 18:58 | 2022-04-15 19:01 | 186 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR - SE CERRO POR CONTROL LLEVA LA CARGA DEL 1717-01 | B22041500261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-15 | 558 | keep | 0 | Apr | 2022 | 0.00038005 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2022-04-15 18:59 | 2022-04-17 10:28 | 50 | 039:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE PRIMARIO DE LINEA @ CAJA EN C/L (NO FUNDIO) | S22041500311 | New_Event | Wire Down | Include | Include | Equipment | 2369 | 2022-04-15 | 118450 | keep | 0 | Apr | 2022 | 0.080676 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-04-15 18:59 | 2022-04-16 14:45 | 6 | 019:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PRIMARIO PARTIDO NO FUSIBLE | P22041500169 | New_Event | Wire Down | Include | Include | Equipment | 1186 | 2022-04-15 | 7116 | keep | 0 | Apr | 2022 | 0.0048467 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-15 19:07 | 2022-04-16 01:07 | 403 | 006:00 | T | DESGANCHE | SE ABREN MACHETES Y SE CIERRA N/O 1620-03 CONTRA EL 1336-10 5% EN SERVICIO | S22041500319 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2022-04-15 | 145080 | keep | 0 | Apr | 2022 | 0.098813 | 0.00027448 | Sustained | FALSE | FALSE | Not_TMED_Event | 403
SAN JUAN | 2022-04-15 19:07 | 2022-04-16 00:08 | 36 | 005:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR ABRIO AMMARRE CONTRA EL 1336-10 Y SE CERRO POR CONTROL CARGA POR 1620-03 | S22041500319 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2022-04-15 | 10836 | keep | 0 | Apr | 2022 | 0.0073804 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-04-15 19:07 | 2022-04-16 00:08 | 1073 | 005:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR ABRIO AMMARRE CONTRA EL 1336-10 Y SE CERRO POR CONTROL LLEVA EL 1620-01 | S22041500319 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2022-04-15 | 322973 | keep | 0 | Apr | 2022 | 0.21998 | 0.00073082 | Sustained | FALSE | FALSE | Not_TMED_Event | 1073
CANOVANAS | 2022-04-15 19:18 | 2022-04-15 20:29 | 12 | 001:11 | P | OTRAS CAUSAS | SE ABRIO XMR DEBIDO A QUE CONTADOR DE CLIENTE SE PRENDIO EN FUEGO. SE DEJO CLIENTE FUERA Y SE NORMALIZO | R22041500141 | New_Event | Other Causes | Include | Include | Other | 71 | 2022-04-15 | 852 | keep | 0 | Apr | 2022 | 0.00058029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-15 19:20 | 2022-04-16 06:43 | 681 | 011:23 | T | NO SE REPORTO CAUSA | RECERRO 3 VECES QUEDO FUERA, SE VERIFICO SIN PERSONAL PATRULLANDO Y SE LE HIZO PRUEBA Y SE QUEDO EN SERVICIO | S22041500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 683 | 2022-04-15 | 465123 | keep | 0 | Apr | 2022 | 0.31679 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
BAYAMON | 2022-04-15 19:29 | 2022-04-16 11:01 | 80 | 015:32 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | B22041500281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 932 | 2022-04-15 | 74560 | keep | 0 | Apr | 2022 | 0.050782 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-15 19:35 | 2022-04-17 09:45 | 10 | 038:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE XMR | B22041500288 | New_Event | Wire Down | Include | Include | Equipment | 2290 | 2022-04-15 | 22900 | keep | 0 | Apr | 2022 | 0.015597 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-15 19:54 | 2022-04-15 20:11 | 2402 | 000:17 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 | S22041500084 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 17 | 2022-04-15 | 40834 | keep | 0 | Apr | 2022 | 0.027812 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-15 19:54 | 2022-04-15 20:11 | 1 | 000:17 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - CARGA TRANSFERIDA AL 1709-02 | S22041500084 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 17 | 2022-04-15 | 17 | keep | 0 | Apr | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-15 20:08 | 2022-04-16 21:15 | 100 | 025:07 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN CORTE DE LINEA SE PREPARO PROVISIONAL AEREO | B22041500135 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1507 | 2022-04-15 | 150700 | keep | 0 | Apr | 2022 | 0.10264 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-15 20:11 | 2022-04-15 21:03 | 120 | 000:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 | S22041500084 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 52 | 2022-04-15 | 6240 | keep | 0 | Apr | 2022 | 0.00425 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-15 20:13 | 2022-04-17 12:03 | 12 | 039:50 | P | DESGANCHE | 1X30 EN XMER | S22041500370 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2390 | 2022-04-15 | 28680 | keep | 0 | Apr | 2022 | 0.019534 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-04-15 20:22 | 2022-04-15 23:21 | 20 | 002:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZRO CAJA Y PORTAFUSIBLE | B22041500322 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2022-04-15 | 3580 | keep | 0 | Apr | 2022 | 0.0024383 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-04-15 20:38 | 2022-04-16 11:02 | 150 | 014:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA PRIMARIA | B22041500143 | New_Event | Cutout Failure | Include | Include | Equipment | 864 | 2022-04-15 | 129600 | keep | 0 | Apr | 2022 | 0.08827 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-04-15 20:59 | 2022-04-15 21:00 | 27 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22041500347 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 27 | keep | 0 | Apr | 2022 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-04-15 21:03 | 2022-04-15 21:04 | 2402 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - LLEVA LA CARGA DEL 1720-08 | S22041500084 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-15 | 2402 | keep | 0 | Apr | 2022 | 0.001636 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-15 21:03 | 2022-04-15 21:04 | 1 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN FASE DEL MEDIO - CARGA TRANSFERIDA AL 1709-02 | S22041500084 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-15 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-15 21:09 | 2022-04-16 12:51 | 30 | 015:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041500219 | New_Event | Bad Weather | Include | Include | Weather | 942 | 2022-04-15 | 28260 | keep | 0 | Apr | 2022 | 0.019248 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-04-15 21:37 | 2022-04-16 04:52 | 200 | 007:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B22041500380 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 435 | 2022-04-15 | 87000 | keep | 0 | Apr | 2022 | 0.059255 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-04-15 22:47 | 2022-04-15 22:48 | 2178 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C22041500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-15 | 2178 | keep | 0 | Apr | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CAGUAS | 2022-04-15 22:48 | 2022-04-16 07:21 | 80 | 008:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESGANCHO Y SE CERRO PUENTE | C22041500170 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 513 | 2022-04-15 | 41040 | keep | 0 | Apr | 2022 | 0.027952 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-15 22:49 | 2022-04-16 11:00 | 6 | 012:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA EN TRANSFORMADOR | A22041500116 | New_Event | Cutout Failure | Include | Include | Equipment | 731 | 2022-04-15 | 4386 | keep | 0 | Apr | 2022 | 0.0029873 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-04-15 23:04 | 2022-04-15 23:05 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22041500117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-15 | 2201 | keep | 0 | Apr | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-04-16 00:51 | 2022-04-16 09:02 | 300 | 008:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22041600002 | New_Event | Bad Weather | Include | Include | Weather | 491 | 2022-04-16 | 147300 | keep | 0 | Apr | 2022 | 0.10033 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-04-16 00:56 | 2022-04-16 16:14 | 10 | 015:18 | P | ESTRUCTURA AVERIADA | 1 X 20 EN CORTE DE LINEA SE REMPLAZO POSTE DE PROVISIONAL AEREO. | B22041600004 | New_Event | Defective Pole | Include | Include | Equipment | 918 | 2022-04-16 | 9180 | keep | 0 | Apr | 2022 | 0.0062525 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-16 01:07 | 2022-04-16 01:09 | 383 | 000:02 | P | DESGANCHE | SE REALIZA DESGANCHE Y SE REALIZAN OPERACIONES 95% EN SERVICIO | S22041500319 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-04-16 | 766 | keep | 0 | Apr | 2022 | 0.00052172 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-16 01:08 | 2022-04-16 01:12 | 68 | 000:04 | T | DESGANCHE | SE ABRIO BKR A PETICION DE JOSE PARTIDA/BENJAMIN FEBRES POR SEGURIDAD PARA CERRAR LOS MACHETES N/O CONTRA 1520-04 QUE NO ESTABAN EN MUY BUENAS CONDICIONES | S22041500277 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-04-16 | 272 | keep | 0 | Apr | 2022 | 0.00018526 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-16 01:09 | 2022-04-16 02:25 | 20 | 001:16 | P | DESGANCHE | SE REALIZO DESGANCHE YSE CERRARON MACHETES 100% | S22041500319 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-04-16 | 1520 | keep | 0 | Apr | 2022 | 0.0010353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-04-16 01:17 | 2022-04-16 01:21 | 752 | 000:04 | T | DESGANCHE | SE ABRIO BKR A PETICION DE JOSE PARTIDA/BENJAMIN FEBRES POR SEGURIDAD PARA CERRAR LOS MACHETES N/O 1520-01 QUE NO ESTABAN EN MUY BUENAS CONDICIONES CARGA POR EL 1520-05 | S22041500277 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-04-16 | 3008 | keep | 0 | Apr | 2022 | 0.0020487 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-16 01:17 | 2022-04-16 01:21 | 68 | 000:04 | T | DESGANCHE | SE ABRIO BKR A PETICION DE JOSE PARTIDA/BENJAMIN FEBRES POR SEGURIDAD PARA CERRAR LOS MACHETES N/O CONTTRA 1520-01 QUE NO ESTABAN EN MUY BUENAS CONDICIONES | S22041500277 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-04-16 | 272 | keep | 0 | Apr | 2022 | 0.00018526 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
PONCE | 2022-04-16 01:48 | 2022-04-16 10:08 | 50 | 008:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | P22041600004 | New_Event | Cutout Failure | Include | Include | Equipment | 500 | 2022-04-16 | 25000 | keep | 0 | Apr | 2022 | 0.017027 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-04-16 02:27 | 2022-04-16 09:48 | 20 | 007:21 | P | DESGANCHE | 1 X 30 EN CL SE DESGANCHO | C22041600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2022-04-16 | 8820 | keep | 0 | Apr | 2022 | 0.0060073 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-16 03:04 | 2022-04-16 03:05 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 1606 | keep | 0 | Apr | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BAYAMON | 2022-04-16 04:15 | 2022-04-16 05:13 | 790 | 000:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO BKR A PETICION DE JUAN C. RAMOS PARA LEVANTAR CONDUCTOR PRIMARIO EN EL SUELO | S22041600000 | New_Event | Wire Down | Include | Include | Equipment | 58 | 2022-04-16 | 45820 | keep | 0 | Apr | 2022 | 0.031208 | 0.00053807 | Sustained | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2022-04-16 05:17 | 2022-04-16 15:35 | 1058 | 010:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR AVERIA DE PUENTE ABIERTO Y SE ENERGIZO PORTATIL | S22041600032 | New_Event | Wire Down | Include | Include | Equipment | 618 | 2022-04-16 | 653844 | keep | 0 | Apr | 2022 | 0.44533 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2022-04-16 05:17 | 2022-04-16 15:35 | 250 | 010:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR AVERIA DE PUENTE ABIERTO Y SE ENERGIZO PORTATIL | S22041600032 | New_Event | Wire Down | Include | Include | Equipment | 618 | 2022-04-16 | 154500 | keep | 0 | Apr | 2022 | 0.10523 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-04-16 05:17 | 2022-04-16 15:35 | 1290 | 010:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR AVERIA DE PUENTE ABIERTO Y SE ENERGIZO PORTATIL | S22041600032 | New_Event | Wire Down | Include | Include | Equipment | 618 | 2022-04-16 | 797220 | keep | 0 | Apr | 2022 | 0.54298 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
CAGUAS | 2022-04-16 05:43 | 2022-04-16 10:46 | 10 | 005:03 | P | DESGANCHE | 1 X15 EN XMR Y SE REALIZO DESGANCHE | C22041600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2022-04-16 | 3030 | keep | 0 | Apr | 2022 | 0.0020637 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-04-16 05:44 | 2022-04-16 07:14 | 1902 | 001:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 PALMER TC @ FAJARDO TC | R22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-04-16 | 171180 | keep | 0 | Apr | 2022 | 0.11659 | 0.0012954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2022-04-16 05:44 | 2022-04-16 07:14 | 970 | 001:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 PALMER TC @ FAJARDO TC | R22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-04-16 | 87300 | keep | 0 | Apr | 2022 | 0.05946 | 0.00066066 | Sustained | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2022-04-16 05:44 | 2022-04-16 07:14 | 3003 | 001:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 PALMER TC @ FAJARDO TC | R22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-04-16 | 270270 | keep | 0 | Apr | 2022 | 0.18408 | 0.0020453 | Sustained | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2022-04-16 05:44 | 2022-04-16 07:14 | 2343 | 001:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 38KV | R22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-04-16 | 210870 | keep | 0 | Apr | 2022 | 0.14362 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2022-04-16 05:44 | 2022-04-16 07:14 | 1830 | 001:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 38KV | R22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-04-16 | 164700 | keep | 0 | Apr | 2022 | 0.11218 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2022-04-16 05:44 | 2022-04-16 07:14 | 710 | 001:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 38KV CARGA POR EL 2201-04 | R22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-04-16 | 63900 | keep | 0 | Apr | 2022 | 0.043522 | 0.00048358 | Sustained | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2022-04-16 05:44 | 2022-04-16 07:14 | 1197 | 001:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 38KV LLEVA LA CARGA DEL 2201-03 | R22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-04-16 | 107730 | keep | 0 | Apr | 2022 | 0.073374 | 0.00081527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1197
FAJARDO | 2022-04-16 05:45 | 2022-04-16 05:46 | 3012 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO RR/OFF PERMANENTE | R22041600000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-16 | 3012 | keep | 0 | Apr | 2022 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
FAJARDO | 2022-04-16 05:47 | 2022-04-16 05:48 | 3012 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO RR/OFF PERMANENTE | R22041600000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-04-16 | 3012 | keep | 0 | Apr | 2022 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
BAYAMON | 2022-04-16 05:49 | 2022-04-16 05:50 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 222 | keep | 0 | Apr | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-04-16 05:51 | 2022-04-16 07:45 | 80 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22041600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-04-16 | 9120 | keep | 0 | Apr | 2022 | 0.0062116 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-16 05:56 | 2022-04-16 05:57 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22041600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 4381 | keep | 0 | Apr | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2022-04-16 06:01 | 2022-04-16 06:02 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22041600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 3458 | keep | 0 | Apr | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
CANOVANAS | 2022-04-16 06:03 | 2022-04-16 12:30 | 80 | 006:27 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA Y SE REEMPLAZO PARARRAYO | R22041600029 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 387 | 2022-04-16 | 30960 | keep | 0 | Apr | 2022 | 0.021087 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-16 06:24 | 2022-04-16 10:30 | 200 | 004:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041600004 | New_Event | Bad Weather | Include | Include | Weather | 246 | 2022-04-16 | 49200 | keep | 0 | Apr | 2022 | 0.03351 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-04-16 06:31 | 2022-04-16 06:32 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 2379 | keep | 0 | Apr | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2022-04-16 06:34 | 2022-04-18 09:27 | 8 | 050:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER SE REMPLAZO PORTAFUSIBLE | B22041600011 | New_Event | Cutout Failure | Include | Include | Equipment | 3053 | 2022-04-16 | 24424 | keep | 0 | Apr | 2022 | 0.016635 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-04-16 06:37 | 2022-04-16 08:55 | 60 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22041600017 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2022-04-16 | 8280 | keep | 0 | Apr | 2022 | 0.0056395 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-16 06:43 | 2022-04-16 06:45 | 45 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 5% DE SU CARGA | B22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-16 | 90 | keep | 0 | Apr | 2022 | 6.1299e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-04-16 06:47 | 2022-04-16 07:37 | 425 | 000:50 | T | NO SE REPORTO CAUSA | SE NOTIFICO INTERRUPTOR FUERA DE SERVICIO POR DESPACHO DE SERVICIO NO HAY SCADA SE REALIZO PRUEBA MANUAL. | A22041600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2022-04-16 | 21250 | keep | 0 | Apr | 2022 | 0.014473 | 0.00028947 | Sustained | FALSE | FALSE | Not_TMED_Event | 425
SAN JUAN | 2022-04-16 06:56 | 2022-04-16 06:57 | 2245 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTORCARGA POR EL 1658-15 | R22041600000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-16 | 2245 | keep | 0 | Apr | 2022 | 0.0015291 | 0.0015291 | Momentary | FALSE | FALSE | Not_TMED_Event | 2245
SAN JUAN | 2022-04-16 06:56 | 2022-04-16 06:57 | 1 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1658-13 SE CERRO POR SCADA | R22041600000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-16 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-16 06:57 | 2022-04-16 10:59 | 1 | 004:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 SU-15 A RISER AVE | R22041600137 | 1st_after_momentary |  |  | Include | Wildlife | 242 | 2022-04-16 | 242 | keep | 0 | Apr | 2022 | 0.00016483 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-16 07:03 | 2022-04-16 07:04 | 2466 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 2466 | keep | 0 | Apr | 2022 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
GUAYAMA | 2022-04-16 07:19 | 2022-04-16 08:00 | 50 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22041600015 | New_Event |  |  | Include | Wildlife | 41 | 2022-04-16 | 2050 | keep | 0 | Apr | 2022 | 0.0013962 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-16 07:21 | 2022-04-16 07:22 | 2178 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C2204160000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-04-16 | 2178 | keep | 0 | Apr | 2022 | 0.0014834 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-16 07:22 | 2022-04-16 12:26 | 80 | 005:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESGANCHO Y SE CERRO PUENTE | C22041500170 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 304 | 2022-04-16 | 24320 | keep | 0 | Apr | 2022 | 0.016564 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-04-16 07:28 | 2022-04-16 13:07 | 1 | 005:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR Y 1 X 25 EN RISER AVE | C22041600007 | New_Event |  |  | Include | Wildlife | 339 | 2022-04-16 | 339 | keep | 0 | Apr | 2022 | 0.00023089 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-16 07:34 | 2022-04-16 07:35 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 3438 | keep | 0 | Apr | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
MAYAGÃœEZ | 2022-04-16 07:39 | 2022-04-17 09:58 | 80 | 026:19 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22041600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1579 | 2022-04-16 | 126320 | keep | 0 | Apr | 2022 | 0.086036 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-16 07:39 | 2022-04-16 10:34 | 1 | 002:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041600029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-04-16 | 175 | keep | 0 | Apr | 2022 | 0.00011919 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-16 07:46 | 2022-04-16 07:49 | 327 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5200 DE AGUAS BUENAS | C22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-16 | 981 | keep | 0 | Apr | 2022 | 0.00066815 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
CAGUAS | 2022-04-16 07:46 | 2022-04-16 07:49 | 1843 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5200 DE AGUAS BUENAS | C22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-16 | 5529 | keep | 0 | Apr | 2022 | 0.0037658 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
CAGUAS | 2022-04-16 07:46 | 2022-04-16 07:49 | 2203 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5200 DE AGUAS BUENAS | C22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-16 | 6609 | keep | 0 | Apr | 2022 | 0.0045014 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
CAGUAS | 2022-04-16 07:46 | 2022-04-16 07:49 | 2457 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5200 DE AGUAS BUENAS | C22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-04-16 | 7371 | keep | 0 | Apr | 2022 | 0.0050204 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
BAYAMON | 2022-04-16 08:14 | 2022-04-17 13:00 | 12 | 028:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1X20 EN XMR & SE REPARO SECUNDARIA - TRASPATIO | S22041600070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1726 | 2022-04-16 | 20712 | keep | 0 | Apr | 2022 | 0.014107 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-04-16 08:16 | 2022-04-16 17:22 | 16 | 009:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARARON VARIAS CONDICIONES EN LA LINEA | R22041600129 | New_Event | Secondary Wire Down | Include | Include | Equipment | 546 | 2022-04-16 | 8736 | keep | 0 | Apr | 2022 | 0.00595 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-04-16 08:21 | 2022-04-17 01:23 | 6 | 017:02 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU | B22041600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1022 | 2022-04-16 | 6132 | keep | 0 | Apr | 2022 | 0.0041765 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-04-16 08:30 | 2022-04-16 14:35 | 1 | 006:05 | P | NO SE REPORTO CAUSA | 1 X 20 EN MONTURA DE XMR | B22041600022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 365 | 2022-04-16 | 365 | keep | 0 | Apr | 2022 | 0.0002486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-16 08:44 | 2022-04-16 11:00 | 8 | 002:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR REPARAR LINEA SECUNDARIA | A22041600038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 136 | 2022-04-16 | 1088 | keep | 0 | Apr | 2022 | 0.00074103 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-16 08:47 | 2022-04-18 11:08 | 2 | 050:21 | P | DESGANCHE | 2 X 10 EN XMR Y SE REALIZO DESGANCHE | B22041600027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3021 | 2022-04-16 | 6042 | keep | 0 | Apr | 2022 | 0.0041152 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-04-16 09:05 | 2022-04-17 07:25 | 12 | 022:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN SU-10A | B22041600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1340 | 2022-04-16 | 16080 | keep | 0 | Apr | 2022 | 0.010952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 594 | 000:03 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1437-04 LLEVA 60% DEL 1301-02 | S22041600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 1782 | keep | 0 | Apr | 2022 | 0.0012137 | 0.00040457 | Momentary | FALSE | FALSE | Not_TMED_Event | 594
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 849 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 2547 | keep | 0 | Apr | 2022 | 0.0017348 | 0.00057825 | Momentary | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 893 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1418-02 LLEVA 10% DEL 1422-02 | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 2679 | keep | 0 | Apr | 2022 | 0.0018247 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 602 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 1806 | keep | 0 | Apr | 2022 | 0.0012301 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 43 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 129 | keep | 0 | Apr | 2022 | 8.7861e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 1389 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 4167 | keep | 0 | Apr | 2022 | 0.0028381 | 0.00094604 | Momentary | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 67 | 000:03 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1418-02 LLEVA 10% DEL 1422-02 | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 201 | keep | 0 | Apr | 2022 | 0.0001369 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 605 | 000:03 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1423-04 LLEVA 90% 1422-02 | S22041600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 1815 | keep | 0 | Apr | 2022 | 0.0012362 | 0.00041206 | Momentary | FALSE | FALSE | Not_TMED_Event | 605
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 372 | 000:03 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1423-04 LLEVA 1422-03 | S22041600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 1116 | keep | 0 | Apr | 2022 | 0.0007601 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 732 | 000:03 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1423-04 LLEVA 1422-04 | S22041600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 2196 | keep | 0 | Apr | 2022 | 0.0014957 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 721 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 2163 | keep | 0 | Apr | 2022 | 0.0014732 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 325 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 975 | keep | 0 | Apr | 2022 | 0.00066407 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 600 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 1800 | keep | 0 | Apr | 2022 | 0.001226 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 267 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1423-04 LLEVA 1422-04 , 1422-03 Y 90% 1422-02 | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 801 | keep | 0 | Apr | 2022 | 0.00054556 | 0.00018185 | Momentary | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 621 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 1863 | keep | 0 | Apr | 2022 | 0.0012689 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 2203 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 6609 | keep | 0 | Apr | 2022 | 0.0045014 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 246 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 738 | keep | 0 | Apr | 2022 | 0.00050265 | 0.00016755 | Momentary | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 9 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1424-08 LLEVA 1348-07, 80% DEL 1348-06 Y PARTE DEL 1336-08 | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 27 | keep | 0 | Apr | 2022 | 1.839e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 601 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1437-01 LLEVA 1437-02 | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 1803 | keep | 0 | Apr | 2022 | 0.001228 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 640 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC CARGA POR EL 1437-01 | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 1920 | keep | 0 | Apr | 2022 | 0.0013077 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 1699 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 5097 | keep | 0 | Apr | 2022 | 0.0034715 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 892 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1437-04 LLEVA 60% DEL 1301-02 | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 2676 | keep | 0 | Apr | 2022 | 0.0018226 | 0.00060754 | Momentary | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-04-16 09:08 | 2022-04-16 09:11 | 1066 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC | S22051600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-04-16 | 3198 | keep | 0 | Apr | 2022 | 0.0021781 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
SAN JUAN | 2022-04-16 09:11 | 2022-04-16 19:16 | 200 | 010:05 | P | DESGANCHE | 1X100 EN C/L | S22041500161 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 605 | 2022-04-16 | 121000 | keep | 0 | Apr | 2022 | 0.082413 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-04-16 09:15 | 2022-04-16 10:52 | 15 | 001:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041600038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-04-16 | 1455 | keep | 0 | Apr | 2022 | 0.00099099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-16 09:29 | 2022-04-16 09:30 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 5961 | keep | 0 | Apr | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
ARECIBO | 2022-04-16 09:41 | 2022-04-17 14:50 | 12 | 029:09 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22041600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1749 | 2022-04-16 | 20988 | keep | 0 | Apr | 2022 | 0.014295 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-04-16 09:47 | 2022-04-16 12:37 | 30 | 002:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22041600030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-04-16 | 5100 | keep | 0 | Apr | 2022 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-16 10:01 | 2022-04-16 10:02 | 500 | 000:01 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1424-08 LLEVA PARTE DEL 1336-08 | S22041600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-04-16 | 500 | keep | 0 | Apr | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-04-16 10:01 | 2022-04-16 10:02 | 1001 | 000:01 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1424-08 LLEVA 80% DEL 1348-06 | S22041600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-04-16 | 1001 | keep | 0 | Apr | 2022 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2022-04-16 10:01 | 2022-04-16 10:02 | 278 | 000:01 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE HATO REY TC 1424-08 LLEVA 1348-07 | S22041600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-04-16 | 278 | keep | 0 | Apr | 2022 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
BAYAMON | 2022-04-16 10:01 | 2022-04-16 12:20 | 10 | 002:19 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR PARA REPARAR PEDESTAL | B22041200300 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 139 | 2022-04-16 | 1390 | keep | 0 | Apr | 2022 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-04-16 10:10 | 2022-04-16 13:00 | 200 | 002:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22041600058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2022-04-16 | 34000 | keep | 0 | Apr | 2022 | 0.023157 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-04-16 10:20 | 2022-04-16 12:12 | 150 | 001:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO POSTE IMPACTADO POR VEHICULO PRIVADO | R22041600003 | New_Event |  |  | Include | Wildlife | 112 | 2022-04-16 | 16800 | keep | 0 | Apr | 2022 | 0.011442 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-04-16 10:20 | 2022-04-16 12:12 | 1 | 001:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO POSTE IMPACTADO POR VEHICULO PRIVADO | R22041600003 | New_Event |  |  | Include | Wildlife | 112 | 2022-04-16 | 112 | keep | 0 | Apr | 2022 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-16 10:21 | 2022-04-16 11:29 | 4 | 001:08 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y SE REALIZO DESGANCHE | C22041600015 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 68 | 2022-04-16 | 272 | keep | 0 | Apr | 2022 | 0.00018526 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-16 10:24 | 2022-04-16 14:23 | 315 | 003:59 | T | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PRIMARIO PARTIDO 40% EN SERVICIO | S22041600000 | New_Event | Defective Pole | Include | Include | Equipment | 239 | 2022-04-16 | 75285 | keep | 0 | Apr | 2022 | 0.051276 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-04-16 10:32 | 2022-04-16 21:25 | 80 | 010:53 | P | DESGANCHE | 1X100 EN C/L | S22041500149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2022-04-16 | 52240 | keep | 0 | Apr | 2022 | 0.03558 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-16 10:51 | 2022-04-16 10:52 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
HUMACAO | 2022-04-16 10:56 | 2022-04-16 14:01 | 40 | 003:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN C/L AVE | C22041600024 | New_Event |  |  | Include | Wildlife | 185 | 2022-04-16 | 7400 | keep | 0 | Apr | 2022 | 0.0050401 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-16 11:15 | 2022-04-16 14:11 | 3433 | 002:56 | P | DESGANCHE | SE RETIRO BAMBUA DEL 13KV Y SE CERRO POR CONTROL - 80% DEL INTERRUPTOR EN SERVICIO, EL OTRO 20% NO SE AFECTO DEBIDO A QUE ESTA TRANSFERIDO AL 1303-02 | S22041600175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-04-16 | 604208 | keep | 0 | Apr | 2022 | 0.41152 | 0.0023382 | Sustained | FALSE | FALSE | Not_TMED_Event | 3433
HUMACAO | 2022-04-16 11:17 | 2022-04-16 12:02 | 23 | 000:45 | P | DESGANCHE | 2 X 50 EN C/L SE REALIZO DESGANCHE | C22041600028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2022-04-16 | 1035 | keep | 0 | Apr | 2022 | 0.00070493 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
PONCE | 2022-04-16 11:19 | 2022-04-16 13:55 | 100 | 002:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22041600038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-04-16 | 15600 | keep | 0 | Apr | 2022 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-16 11:31 | 2022-04-17 14:48 | 80 | 027:17 | P | DESGANCHE | 1X80 EN C/L & SE RETIRO BAMBUA DEL 4KV | S22041600188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1637 | 2022-04-16 | 130960 | keep | 0 | Apr | 2022 | 0.089196 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-04-16 11:50 | 2022-04-16 12:56 | 14 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REEMPLAZAR LINEA SECUNDARIA QUEMADA | P22041600031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2022-04-16 | 924 | keep | 0 | Apr | 2022 | 0.00062933 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-04-16 12:07 | 2022-04-16 13:55 | 50 | 001:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | R22041600176 | New_Event | Cutout Failure | Include | Include | Equipment | 108 | 2022-04-16 | 5400 | keep | 0 | Apr | 2022 | 0.0036779 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-16 12:08 | 2022-04-16 12:10 | 824 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO 1119-04 Y SE CERRO POR SCADA LLEVA 95% DEL 1115-05 | S22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-16 | 1648 | keep | 0 | Apr | 2022 | 0.0011224 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-04-16 12:08 | 2022-04-16 12:10 | 750 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO 1119-04 QUE LLEVA PARTE DEL 1119-02 | S22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-16 | 1500 | keep | 0 | Apr | 2022 | 0.0010216 | 0.00051082 | Momentary | FALSE | FALSE | Not_TMED_Event | 750
BAYAMON | 2022-04-16 12:08 | 2022-04-16 12:10 | 2720 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1119-04 Y SE CERRO POR SCADA LLEVA 95% DEL 1115-05 Y PARTE DEL 1119-02 | S22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-16 | 5440 | keep | 0 | Apr | 2022 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2022-04-16 12:12 | 2022-04-16 14:55 | 1240 | 002:43 | P | DESGANCHE | SE SECCIONALIZO POR DESGANCHE DE BAMBUAS 60% DE LA CARGA TRANSFERIDO AL 1620-02 - AUN QUEDA EL 30% DEL 1206-03 FUERA DE SERVICIO | S22041600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-04-16 | 202120 | keep | 0 | Apr | 2022 | 0.13766 | 0.00084456 | Sustained | FALSE | FALSE | Not_TMED_Event | 1240
SAN JUAN | 2022-04-16 12:12 | 2022-04-16 14:55 | 3718 | 002:43 | T | DESGANCHE | SE SECCIONALIZO POR DESGANCHE DE BAMBUA LLEVA 60% DEL 1206-03 | S22041600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-04-16 | 606034 | keep | 0 | Apr | 2022 | 0.41277 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2022-04-16 12:12 | 2022-04-16 17:20 | 250 | 005:08 | P | DESGANCHE | 2 X 100 Y 1 X 20 EN C/L SE REALIZO DESGANCHE | B22041600079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2022-04-16 | 77000 | keep | 0 | Apr | 2022 | 0.052444 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2022-04-16 12:19 | 2022-04-16 18:08 | 60 | 005:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M22041600076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2022-04-16 | 20940 | keep | 0 | Apr | 2022 | 0.014262 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-04-16 12:20 | 2022-04-16 13:57 | 50 | 001:37 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA | M22041600077 | New_Event | Trip Due To Overload | Include | Include | Other | 97 | 2022-04-16 | 4850 | keep | 0 | Apr | 2022 | 0.0033033 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-16 12:24 | 2022-04-16 12:25 | 376 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1011-04 Y SE CERRO POR SCADA LLEVA 95% DEL 1011-01 | S22041600246 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 376 | keep | 0 | Apr | 2022 | 0.00025609 | 0.00025609 | Momentary | FALSE | FALSE | Not_TMED_Event | 376
BAYAMON | 2022-04-16 12:24 | 2022-04-16 12:25 | 390 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1011-04 Y SE CERRO POR SCADA LLEVA 95% DEL 1011-01 | S22041600246 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 390 | keep | 0 | Apr | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
PONCE | 2022-04-16 12:30 | 2022-04-16 12:31 | 1093 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 200 | P22041600048 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-16 | 1093 | keep | 0 | Apr | 2022 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
PONCE | 2022-04-16 12:30 | 2022-04-16 12:31 | 1067 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 200 | P22041600048 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-16 | 1067 | keep | 0 | Apr | 2022 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2022-04-16 12:30 | 2022-04-16 12:31 | 836 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 200 | P22041600048 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-16 | 836 | keep | 0 | Apr | 2022 | 0.0005694 | 0.0005694 | Momentary | FALSE | FALSE | Not_TMED_Event | 836
PONCE | 2022-04-16 12:30 | 2022-04-16 12:31 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 200 | P22041600048 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-16 | 1339 | keep | 0 | Apr | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
PONCE | 2022-04-16 12:30 | 2022-04-16 12:31 | 1295 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 200 | P22041600048 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-16 | 1295 | keep | 0 | Apr | 2022 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
BAYAMON | 2022-04-16 12:33 | 2022-04-16 18:30 | 40 | 005:57 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22041600082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 357 | 2022-04-16 | 14280 | keep | 0 | Apr | 2022 | 0.009726 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-16 12:47 | 2022-04-16 12:48 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | SE DISPARO LINEA 1600 SE CERRO POR SCADA EN CENTRO DE TRANSMISION | M22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-16 | 888 | keep | 0 | Apr | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-04-16 12:47 | 2022-04-16 12:48 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | SE DISPARO LINEA 1600 SE CERRO POR SCADA EN CENTRO DE TRANSMISION | M22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-16 | 393 | keep | 0 | Apr | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-04-16 12:47 | 2022-04-16 12:48 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | SE DISPARO LINEA 1600 SE CERRO POR SCADA EN CENTRO DE TRANSMISION | M22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-16 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-04-16 12:48 | 2022-04-16 17:39 | 3157 | 004:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CARGA ATRAVES DE PORTATIL 6 AISLADOR PARTIDO | A22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 291 | 2022-04-16 | 918687 | keep | 0 | Apr | 2022 | 0.62571 | 0.0021502 | Sustained | FALSE | FALSE | Not_TMED_Event | 3157
ARECIBO | 2022-04-16 12:48 | 2022-04-16 17:39 | 35 | 004:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 291 | 2022-04-16 | 10185 | keep | 0 | Apr | 2022 | 0.006937 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-04-16 12:48 | 2022-04-16 17:39 | 2916 | 004:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22041600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 291 | 2022-04-16 | 848556 | keep | 0 | Apr | 2022 | 0.57795 | 0.0019861 | Sustained | FALSE | FALSE | Not_TMED_Event | 2916
MAYAGÃœEZ | 2022-04-16 12:50 | 2022-04-16 16:02 | 25 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN TRANSFORMADOR POR RAYOS | M22041600082 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2022-04-16 | 4800 | keep | 0 | Apr | 2022 | 0.0032693 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-04-16 12:55 | 2022-04-17 15:50 | 26 | 026:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 SE REMPLAZO CAJA PRIMARIA | R22041600189 | New_Event | Cutout Failure | Include | Include | Equipment | 1615 | 2022-04-16 | 41990 | keep | 0 | Apr | 2022 | 0.028599 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2022-04-16 12:56 | 2022-04-16 16:04 | 90 | 003:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO | C22041600042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-04-16 | 16920 | keep | 0 | Apr | 2022 | 0.011524 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 1222 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 43992 | keep | 0 | Apr | 2022 | 0.029963 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 2756 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 99216 | keep | 0 | Apr | 2022 | 0.067576 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 2833 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 101988 | keep | 0 | Apr | 2022 | 0.069464 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 1218 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 43848 | keep | 0 | Apr | 2022 | 0.029865 | 0.00082957 | Sustained | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 1345 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 48420 | keep | 0 | Apr | 2022 | 0.032979 | 0.00091607 | Sustained | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 1265 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 45540 | keep | 0 | Apr | 2022 | 0.031017 | 0.00086159 | Sustained | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 2071 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 74556 | keep | 0 | Apr | 2022 | 0.05078 | 0.0014105 | Sustained | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 760 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 27360 | keep | 0 | Apr | 2022 | 0.018635 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 509 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 18324 | keep | 0 | Apr | 2022 | 0.01248 | 0.00034668 | Sustained | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 2620 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 94320 | keep | 0 | Apr | 2022 | 0.064241 | 0.0017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:36 | 1916 | 000:36 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 36 | 2022-04-16 | 68976 | keep | 0 | Apr | 2022 | 0.046979 | 0.001305 | Sustained | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 1548 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 58824 | keep | 0 | Apr | 2022 | 0.040065 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 274 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 10412 | keep | 0 | Apr | 2022 | 0.0070916 | 0.00018662 | Sustained | FALSE | FALSE | Not_TMED_Event | 274
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 185 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 7030 | keep | 0 | Apr | 2022 | 0.0047881 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 9 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 342 | keep | 0 | Apr | 2022 | 0.00023293 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 458 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 17404 | keep | 0 | Apr | 2022 | 0.011854 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 437 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 16606 | keep | 0 | Apr | 2022 | 0.01131 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 1185 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 45030 | keep | 0 | Apr | 2022 | 0.03067 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 63 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 2394 | keep | 0 | Apr | 2022 | 0.0016305 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 232 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 8816 | keep | 0 | Apr | 2022 | 0.0060045 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 1022 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 38836 | keep | 0 | Apr | 2022 | 0.026451 | 0.00069608 | Sustained | FALSE | FALSE | Not_TMED_Event | 1022
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 2407 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 91466 | keep | 0 | Apr | 2022 | 0.062297 | 0.0016394 | Sustained | FALSE | FALSE | Not_TMED_Event | 2407
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 2558 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 97204 | keep | 0 | Apr | 2022 | 0.066205 | 0.0017422 | Sustained | FALSE | FALSE | Not_TMED_Event | 2558
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 830 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 31540 | keep | 0 | Apr | 2022 | 0.021482 | 0.00056531 | Sustained | FALSE | FALSE | Not_TMED_Event | 830
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 2694 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 102372 | keep | 0 | Apr | 2022 | 0.069725 | 0.0018349 | Sustained | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 2228 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 84664 | keep | 0 | Apr | 2022 | 0.057664 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 438 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 16644 | keep | 0 | Apr | 2022 | 0.011336 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 385 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 14630 | keep | 0 | Apr | 2022 | 0.0099644 | 0.00026222 | Sustained | FALSE | FALSE | Not_TMED_Event | 385
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 264 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 10032 | keep | 0 | Apr | 2022 | 0.0068327 | 0.00017981 | Sustained | FALSE | FALSE | Not_TMED_Event | 264
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 5042 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 191596 | keep | 0 | Apr | 2022 | 0.1305 | 0.0034341 | Sustained | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 2720 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 103360 | keep | 0 | Apr | 2022 | 0.070398 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 1883 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 71554 | keep | 0 | Apr | 2022 | 0.048735 | 0.0012825 | Sustained | FALSE | FALSE | Not_TMED_Event | 1883
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:39 | 2523 | 000:39 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-04-16 | 98397 | keep | 0 | Apr | 2022 | 0.067018 | 0.0017184 | Sustained | FALSE | FALSE | Not_TMED_Event | 2523
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:39 | 1607 | 000:39 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-04-16 | 62673 | keep | 0 | Apr | 2022 | 0.042686 | 0.0010945 | Sustained | FALSE | FALSE | Not_TMED_Event | 1607
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:39 | 1722 | 000:39 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-04-16 | 67158 | keep | 0 | Apr | 2022 | 0.045741 | 0.0011728 | Sustained | FALSE | FALSE | Not_TMED_Event | 1722
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 2201 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 83638 | keep | 0 | Apr | 2022 | 0.056965 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 1986 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 75468 | keep | 0 | Apr | 2022 | 0.051401 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 199 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 7562 | keep | 0 | Apr | 2022 | 0.0051504 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 24 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 912 | keep | 0 | Apr | 2022 | 0.00062116 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:39 | 619 | 000:39 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-04-16 | 24141 | keep | 0 | Apr | 2022 | 0.016442 | 0.0004216 | Sustained | FALSE | FALSE | Not_TMED_Event | 619
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:39 | 243 | 000:39 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-04-16 | 9477 | keep | 0 | Apr | 2022 | 0.0064547 | 0.00016551 | Sustained | FALSE | FALSE | Not_TMED_Event | 243
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:39 | 2703 | 000:39 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-04-16 | 105417 | keep | 0 | Apr | 2022 | 0.071799 | 0.001841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2703
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 316 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 12008 | keep | 0 | Apr | 2022 | 0.0081786 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 1227 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 46626 | keep | 0 | Apr | 2022 | 0.031757 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-04-16 13:00 | 2022-04-16 13:38 | 3431 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 CAUSO SE APAGARA BARRA ARECIBO SECT Y CAMBALACHE | A22041600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-04-16 | 130378 | keep | 0 | Apr | 2022 | 0.0888 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
GUAYAMA | 2022-04-16 13:05 | 2022-04-16 14:55 | 6 | 001:50 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | P22041600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-04-16 | 660 | keep | 0 | Apr | 2022 | 0.00044952 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-04-16 13:05 | 2022-04-16 14:59 | 30 | 001:54 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | P22041600046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-04-16 | 3420 | keep | 0 | Apr | 2022 | 0.0023293 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-16 13:07 | 2022-04-16 15:00 | 60 | 001:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22041600088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-04-16 | 6780 | keep | 0 | Apr | 2022 | 0.0046178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-04-16 13:22 | 2022-04-16 19:37 | 60 | 006:15 | P | DESGANCHE | SE DESGANCHO Y 2 X 65 EN C/L | C22041600044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2022-04-16 | 22500 | keep | 0 | Apr | 2022 | 0.015325 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-16 13:37 | 2022-04-17 18:21 | 2 | 028:44 | P | NO SE REPORTO CAUSA | 1 X 140 EN RISER NO ENCONTRO CAUSA | A22041600208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1724 | 2022-04-16 | 3448 | keep | 0 | Apr | 2022 | 0.0023484 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-04-16 13:38 | 2022-04-16 16:50 | 20 | 003:12 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO Y SE CERRO LOS PUENTES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A22041500075 | Partial_restoration | Defective Pole | Include | Include | Equipment | 192 | 2022-04-16 | 3840 | keep | 0 | Apr | 2022 | 0.0026154 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-16 13:43 | 2022-04-16 17:32 | 45 | 003:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22041600093 | New_Event | Bad Weather | Include | Include | Weather | 229 | 2022-04-16 | 10305 | keep | 0 | Apr | 2022 | 0.0070187 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-04-16 13:44 | 2022-04-16 15:34 | 6 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AUTO IMPACTO POSTE | R22041600175 | New_Event |  |  | Include | Wildlife | 110 | 2022-04-16 | 660 | keep | 0 | Apr | 2022 | 0.00044952 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-16 13:49 | 2022-04-17 15:17 | 22 | 025:28 | P | DESGANCHE | 1X20 EN XMER, SE DESGANCHO & SE REMPLAZO PORTAFUSIBLE | S22041600310 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1528 | 2022-04-16 | 33616 | keep | 0 | Apr | 2022 | 0.022896 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2022-04-16 13:49 | 2022-04-16 18:58 | 35 | 005:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M22041600095 | New_Event | Bad Weather | Include | Include | Weather | 309 | 2022-04-16 | 10815 | keep | 0 | Apr | 2022 | 0.007366 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-04-16 13:50 | 2022-04-16 18:43 | 150 | 004:53 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 200 EN CORTE DE LINEA POR MAL TIEMPO | M22041600097 | New_Event | Bad Weather | Include | Include | Weather | 293 | 2022-04-16 | 43950 | keep | 0 | Apr | 2022 | 0.029934 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-04-16 13:50 | 2022-04-16 17:07 | 100 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 200 EN CORTE DE LINEA POR MAL TIEMPO | M22041600098 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2022-04-16 | 19700 | keep | 0 | Apr | 2022 | 0.013418 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-16 13:57 | 2022-04-16 16:35 | 20 | 002:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARARON CONEXIONES | M22041600104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 158 | 2022-04-16 | 3160 | keep | 0 | Apr | 2022 | 0.0021523 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-04-16 14:02 | 2022-04-17 00:45 | 3 | 010:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22041600107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 643 | 2022-04-16 | 1929 | keep | 0 | Apr | 2022 | 0.0013138 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-04-16 14:21 | 2022-04-17 01:39 | 52 | 011:18 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | S22041600329 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 678 | 2022-04-16 | 35256 | keep | 0 | Apr | 2022 | 0.024013 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2022-04-16 14:23 | 2022-04-16 17:06 | 189 | 002:43 | P | ESTRUCTURA AVERIADA | SE CERRO N/O CONTRA 1924-01 95% EN SERVICIO | S22041600000 | Partial_restoration | Defective Pole | Include | Include | Equipment | 163 | 2022-04-16 | 30807 | keep | 0 | Apr | 2022 | 0.020983 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-16 14:27 | 2022-04-16 14:28 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
BARRANQUITAS | 2022-04-16 14:32 | 2022-04-17 09:01 | 90 | 018:29 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | C22041600081 | New_Event | Bad Weather | Include | Include | Weather | 1109 | 2022-04-16 | 99810 | keep | 0 | Apr | 2022 | 0.06798 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-04-16 14:33 | 2022-04-16 16:34 | 200 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | R22041600197 | New_Event |  |  | Include | Wildlife | 121 | 2022-04-16 | 24200 | keep | 0 | Apr | 2022 | 0.016483 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-04-16 14:44 | 2022-04-16 18:21 | 25 | 003:37 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22041600053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-04-16 | 5425 | keep | 0 | Apr | 2022 | 0.0036949 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-04-16 14:51 | 2022-04-16 14:52 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 1606 | keep | 0 | Apr | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
ARECIBO | 2022-04-16 14:52 | 2022-04-16 22:15 | 60 | 007:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22041600391 | New_Event | Wire Down | Include | Include | Equipment | 443 | 2022-04-16 | 26580 | keep | 0 | Apr | 2022 | 0.018104 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-16 14:53 | 2022-04-16 14:54 | 1227 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22041600400 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-16 | 1227 | keep | 0 | Apr | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-04-16 14:54 | 2022-04-16 20:48 | 50 | 005:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A22041600712 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 354 | 2022-04-16 | 17700 | keep | 0 | Apr | 2022 | 0.012055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-16 14:55 | 2022-04-16 16:20 | 2480 | 001:25 | P | DESGANCHE | SE SECCIONALIZO POR DESGANCHE DE BAMBUAS 60% DE LA CARGA TRANSFERIDO AL 1620-02 - EN SERVICIO TOTAL | S22041600000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-04-16 | 210800 | keep | 0 | Apr | 2022 | 0.14357 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-16 14:55 | 2022-04-16 14:56 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041600407 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2022-04-16 14:57 | 2022-04-16 17:07 | 200 | 002:10 | P | DESGANCHE | SE DESGANCHO 2 X 100 EN C/L | C22041600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-04-16 | 26000 | keep | 0 | Apr | 2022 | 0.017708 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-04-16 15:01 | 2022-04-17 13:30 | 50 | 022:29 | P | DESGANCHE | 1X80 EN C/L | S22041600353 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1349 | 2022-04-16 | 67450 | keep | 0 | Apr | 2022 | 0.04594 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-04-16 15:03 | 2022-04-16 16:18 | 4 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A22041600430 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2022-04-16 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-04-16 15:09 | 2022-04-16 15:10 | 2107 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A22041600454 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-16 | 2107 | keep | 0 | Apr | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2022-04-16 15:10 | 2022-04-16 17:12 | 702 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO EN EL TRONCAL DEL ALIMENTADOR | A22041600478 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 122 | 2022-04-16 | 85644 | keep | 0 | Apr | 2022 | 0.058332 | 0.00047813 | Sustained | FALSE | FALSE | Not_TMED_Event | 702
MAYAGÃœEZ | 2022-04-16 15:26 | 2022-04-17 05:40 | 80 | 014:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22041600154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 854 | 2022-04-16 | 68320 | keep | 0 | Apr | 2022 | 0.046532 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-16 15:27 | 2022-04-16 20:37 | 250 | 005:10 | P | DESGANCHE | 1 X 100 Y 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22041600156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-04-16 | 77500 | keep | 0 | Apr | 2022 | 0.052785 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2022-04-16 15:32 | 2022-04-16 21:24 | 10 | 005:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADO SE REMPLAZO PROTAFUSIBLE AVERIADO | M22041600160 | New_Event | Cutout Failure | Include | Include | Equipment | 352 | 2022-04-16 | 3520 | keep | 0 | Apr | 2022 | 0.0023975 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-16 15:35 | 2022-04-16 17:49 | 129 | 002:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR AVERIA, SE CERRO PUENTE ABIERTO,SE ENERGIZO PORTATIL, SE REALIZO DESGANCHE Y SE VOLVIERON A CERRAR LOS MACHETES 100% EN SERVICIO | S22041600032 | New_Event | Wire Down | Include | Include | Equipment | 134 | 2022-04-16 | 17286 | keep | 0 | Apr | 2022 | 0.011773 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
ARECIBO | 2022-04-16 15:40 | 2022-04-16 20:08 | 50 | 004:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A22041600530 | New_Event | Wire Down | Include | Include | Equipment | 268 | 2022-04-16 | 13400 | keep | 0 | Apr | 2022 | 0.0091267 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-16 15:51 | 2022-04-16 15:52 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041600567 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2022-04-16 16:01 | 2022-04-17 02:27 | 45 | 010:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22041600102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 626 | 2022-04-16 | 28170 | keep | 0 | Apr | 2022 | 0.019186 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-04-16 16:03 | 2022-04-17 03:11 | 40 | 011:08 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | B22041600104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 668 | 2022-04-16 | 26720 | keep | 0 | Apr | 2022 | 0.018199 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-04-16 16:31 | 2022-04-16 17:26 | 60 | 000:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A22041600637 | New_Event | Bad Weather | Include | Include | Weather | 55 | 2022-04-16 | 3300 | keep | 0 | Apr | 2022 | 0.0022476 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-16 16:41 | 2022-04-18 13:44 | 6 | 045:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L 1 X65 EN RISER HACIA SU4 Y 1 X25 SMU 20 EN SU 4 | B22041600108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2703 | 2022-04-16 | 16218 | keep | 0 | Apr | 2022 | 0.011046 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-16 16:45 | 2022-04-16 16:48 | 2245 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22041600209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-16 | 6735 | keep | 0 | Apr | 2022 | 0.0045872 | 0.0015291 | Momentary | FALSE | FALSE | Not_TMED_Event | 2245
SAN JUAN | 2022-04-16 16:45 | 2022-04-16 16:48 | 1 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22041600209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-16 | 3 | keep | 0 | Apr | 2022 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-16 16:51 | 2022-04-16 16:52 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22041600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 1606 | keep | 0 | Apr | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2022-04-16 16:56 | 2022-04-16 16:57 | 1378 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 1378 | keep | 0 | Apr | 2022 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
PONCE | 2022-04-16 16:56 | 2022-04-16 17:00 | 14 | 000:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P22041600057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 4 | 2022-04-16 | 56 | keep | 0 | Apr | 2022 | 3.8141e-05 | 9.5353e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-04-16 17:06 | 2022-04-17 21:43 | 16 | 028:37 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO Y SE ABRIO MACHETES PARA CERRAR PUENTES | S22041700000 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1717 | 2022-04-16 | 27472 | keep | 0 | Apr | 2022 | 0.018711 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-16 17:09 | 2022-04-17 09:40 | 25 | 016:31 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN CORTE DE LINEA TRANSFORMADOR 25 KVA AVERIADO | M22041600203 | New_Event | Service Transformer Failure | Include | Include | Equipment | 991 | 2022-04-16 | 24775 | keep | 0 | Apr | 2022 | 0.016874 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-04-16 17:12 | 2022-04-16 17:25 | 2107 | 000:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO ABIERTO EN EL TRONCAL DEL ALIMENTADOR | A22041600682 | Additional_clients | Wire Down | Include | Include | Equipment | 13 | 2022-04-16 | 27391 | keep | 0 | Apr | 2022 | 0.018656 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-16 17:14 | 2022-04-16 19:30 | 150 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE DE MADERA IMPACTADO POR UNO DE METAL | R22041600003 | New_Event |  |  | Include | Wildlife | 136 | 2022-04-16 | 20400 | keep | 0 | Apr | 2022 | 0.013894 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-04-16 17:14 | 2022-04-16 19:32 | 200 | 002:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 40 EN CORTES DE LINEA CRUCE CON AVE | R22041600013 | New_Event |  |  | Include | Wildlife | 138 | 2022-04-16 | 27600 | keep | 0 | Apr | 2022 | 0.018798 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-04-16 17:20 | 2022-04-17 10:53 | 1 | 017:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22041600687 | New_Event | Bad Weather | Include | Include | Weather | 1053 | 2022-04-16 | 1053 | keep | 0 | Apr | 2022 | 0.00071719 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-16 17:21 | 2022-04-17 11:47 | 10 | 018:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22041600207 | New_Event | Bad Weather | Include | Include | Weather | 1106 | 2022-04-16 | 11060 | keep | 0 | Apr | 2022 | 0.0075329 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-16 17:45 | 2022-04-16 17:47 | 485 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR - SE CERRO POR CONTROL - LLEVA LA CARGA DEL 1420-05 | S22041600452 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-16 | 970 | keep | 0 | Apr | 2022 | 0.00066066 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
SAN JUAN | 2022-04-16 17:45 | 2022-04-16 17:47 | 4 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR - SE CERRO POR CONTROL - CARGA TRANSFERIDA AL 1404-09 | S22041600452 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-16 | 8 | keep | 0 | Apr | 2022 | 5.4488e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-04-16 17:49 | 2022-04-16 19:15 | 10 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NUETRAL ABIERTO EN LINEA SECUNDARIA EN TRONCAL | R22041600231 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2022-04-16 | 860 | keep | 0 | Apr | 2022 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-16 17:58 | 2022-04-16 20:05 | 15 | 002:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL DE LAS LINEAS | A22041600700 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-04-16 | 1905 | keep | 0 | Apr | 2022 | 0.0012975 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-16 18:06 | 2022-04-17 17:40 | 1 | 023:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO | B22041600105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1414 | 2022-04-16 | 1414 | keep | 0 | Apr | 2022 | 0.00096307 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-16 18:07 | 2022-04-17 18:18 | 40 | 024:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22041600227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1451 | 2022-04-16 | 58040 | keep | 0 | Apr | 2022 | 0.039531 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-16 18:11 | 2022-04-17 14:06 | 50 | 019:55 | P | NO SE REPORTO CAUSA | 1X80 EN RISER @ 1X40 EN SU-3 | S22041600460 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1195 | 2022-04-16 | 59750 | keep | 0 | Apr | 2022 | 0.040695 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-16 18:15 | 2022-04-17 08:58 | 8 | 014:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X20 EN XMER & SE RETIRO SERPIENTE DEL BAJANTE PRIMARIO | S22041600641 | New_Event |  |  | Include | Wildlife | 883 | 2022-04-16 | 7064 | keep | 0 | Apr | 2022 | 0.0048113 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-16 18:17 | 2022-04-16 18:18 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 95% DEL 1717-02 | B22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 5961 | keep | 0 | Apr | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-04-16 18:17 | 2022-04-16 18:18 | 860 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1713-05 LLEVANDO 95% DEL 1717-02 | B22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 860 | keep | 0 | Apr | 2022 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
BAYAMON | 2022-04-16 18:21 | 2022-04-16 19:28 | 1 | 001:07 | P | OTRAS CAUSAS | 1X25 EN SU - PRIVADO (NO IDENTIFICADO) POR CONTAMINACION EN LAS FACILIDADES DEL CLIENTE - SE LES ORIENTO EN EL LUGAR | S22041600462 | New_Event | Other Causes | Include | Include | Other | 67 | 2022-04-16 | 67 | keep | 0 | Apr | 2022 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-16 18:21 | 2022-04-16 19:22 | 45 | 001:01 | P | DESGANCHE | 1 X 50 Y 2 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22041600239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-04-16 | 2745 | keep | 0 | Apr | 2022 | 0.0018696 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-04-16 18:22 | 2022-04-17 00:29 | 200 | 006:07 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | B22041600123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 367 | 2022-04-16 | 73400 | keep | 0 | Apr | 2022 | 0.049992 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-04-16 18:23 | 2022-04-17 17:07 | 50 | 022:44 | P | NO SE REPORTO CAUSA | 1X80 EN C/L & 1X50 EN C/L | S22041600463 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1364 | 2022-04-16 | 68200 | keep | 0 | Apr | 2022 | 0.046451 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-04-16 18:37 | 2022-04-17 02:03 | 1 | 007:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | R22041600237 | New_Event | Wire Down | Include | Include | Equipment | 446 | 2022-04-16 | 446 | keep | 0 | Apr | 2022 | 0.00030377 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-16 18:46 | 2022-04-16 19:02 | 80 | 000:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A22041600705 | New_Event | Bad Weather | Include | Include | Weather | 16 | 2022-04-16 | 1280 | keep | 0 | Apr | 2022 | 0.0008718 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-16 18:55 | 2022-04-16 18:56 | 767 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 50% X 1909-07 & LLEVA 100% DEL 1709-05 | S22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 767 | keep | 0 | Apr | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-04-16 18:55 | 2022-04-16 18:56 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1709-03 100% DE LA CARGA TRANSFERIDA AL 1709-03 | S22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 2364 | keep | 0 | Apr | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
VEGA BAJA | 2022-04-16 18:55 | 2022-04-16 18:56 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 4702 | keep | 0 | Apr | 2022 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
ARECIBO | 2022-04-16 19:07 | 2022-04-17 12:26 | 16 | 017:19 | P | SECUNDARIA/DESGANCHE | SE REPARO LINEA SECUNDARIA ZAFADA SE DESGANCHO EN LINEA SECUNDARIAS | A22041600707 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1039 | 2022-04-16 | 16624 | keep | 0 | Apr | 2022 | 0.011323 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-04-16 19:10 | 2022-04-16 19:11 | 638 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 638 | keep | 0 | Apr | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
SAN JUAN | 2022-04-16 19:14 | 2022-04-17 14:45 | 50 | 019:31 | P | NO SE REPORTO CAUSA | 1X80 EN SU-10 | S22041600479 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1171 | 2022-04-16 | 58550 | keep | 0 | Apr | 2022 | 0.039878 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-16 19:28 | 2022-04-17 08:42 | 30 | 013:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AUTOMOVIL IMPACTO POSTE SECUNDARIO Y CRUZO LINEA | P22041600109 | New_Event |  |  | Include | Wildlife | 794 | 2022-04-16 | 23820 | keep | 0 | Apr | 2022 | 0.016224 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-16 19:40 | 2022-04-16 19:56 | 15 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22041600489 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2022-04-16 | 240 | keep | 0 | Apr | 2022 | 0.00016346 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-16 19:49 | 2022-04-17 11:12 | 60 | 015:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22041600262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 923 | 2022-04-16 | 55380 | keep | 0 | Apr | 2022 | 0.037719 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-16 20:03 | 2022-04-16 21:31 | 1 | 001:28 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA EN RISER A SU15 SE NORMALIZO CARGA DEL 1658-14 CERRANDO RISER DE SU14 AL SU15 | R22041600229 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2022-04-16 | 88 | keep | 0 | Apr | 2022 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-16 20:15 | 2022-04-16 20:53 | 40 | 000:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA | M22041600270 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2022-04-16 | 1520 | keep | 0 | Apr | 2022 | 0.0010353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-16 20:44 | 2022-04-17 15:52 | 12 | 019:08 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING DE XMR - TRASPATIO - (NO FUNDIO) | S22041600500 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1148 | 2022-04-16 | 13776 | keep | 0 | Apr | 2022 | 0.0093828 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-04-16 20:47 | 2022-04-16 20:48 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041600134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-16 | 1945 | keep | 0 | Apr | 2022 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
SAN JUAN | 2022-04-16 20:49 | 2022-04-17 10:20 | 7 | 013:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR Y CAJA PRIMARIA | R22041600246 | New_Event | Cutout Failure | Include | Include | Equipment | 811 | 2022-04-16 | 5677 | keep | 0 | Apr | 2022 | 0.0038666 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-04-16 21:12 | 2022-04-17 05:32 | 5 | 008:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22041600284 | New_Event | Wire Down | Include | Include | Equipment | 500 | 2022-04-16 | 2500 | keep | 0 | Apr | 2022 | 0.0017027 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-04-16 21:19 | 2022-04-17 12:21 | 180 | 015:02 | P | DESGANCHE | 2X100 EN C/L & 2X65 EN OTRO C/L | S22041600512 | New_Event | Vegetation Contact | Include | Include | Vegetation | 902 | 2022-04-16 | 162360 | keep | 0 | Apr | 2022 | 0.11058 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CAGUAS | 2022-04-16 21:22 | 2022-04-16 21:48 | 2900 | 000:26 | T | DESGANCHE | SECCIONALIZO INTERRUPTOR CG-220416-01 | C22041600097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2022-04-16 | 75400 | keep | 0 | Apr | 2022 | 0.051355 | 0.0019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 2900
CAGUAS | 2022-04-16 21:30 | 2022-04-16 21:32 | 1001 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22041600000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-04-16 | 2002 | keep | 0 | Apr | 2022 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2022-04-16 21:33 | 2022-04-17 08:46 | 150 | 011:13 | P | DESGANCHE | 1X100 EN C/L | S22041600516 | New_Event | Vegetation Contact | Include | Include | Vegetation | 673 | 2022-04-16 | 100950 | keep | 0 | Apr | 2022 | 0.068757 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-04-16 21:34 | 2022-04-17 11:12 | 50 | 013:38 | P | DESGANCHE | SE REPARO LINEA ZAFADA DE AISLADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22041600733 | New_Event | Vegetation Contact | Include | Include | Vegetation | 818 | 2022-04-16 | 40900 | keep | 0 | Apr | 2022 | 0.027857 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-16 21:37 | 2022-04-16 21:38 | 1001 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22041600000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-04-16 | 1001 | keep | 0 | Apr | 2022 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
CAGUAS | 2022-04-16 21:41 | 2022-04-16 23:11 | 1001 | 001:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZARON CONDUCTOR ROTO CG-220416-02 | C22041600163 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 90 | 2022-04-16 | 90090 | keep | 0 | Apr | 2022 | 0.06136 | 0.00068178 | Sustained | FALSE | FALSE | Not_TMED_Event | 1001
GUAYAMA | 2022-04-16 21:45 | 2022-04-16 23:42 | 584 | 001:57 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22041600237 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 117 | 2022-04-16 | 68328 | keep | 0 | Apr | 2022 | 0.046538 | 0.00039776 | Sustained | FALSE | FALSE | Not_TMED_Event | 584
GUAYAMA | 2022-04-16 21:45 | 2022-04-16 23:42 | 1658 | 001:57 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22041600237 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 117 | 2022-04-16 | 193986 | keep | 0 | Apr | 2022 | 0.13212 | 0.0011293 | Sustained | FALSE | FALSE | Not_TMED_Event | 1658
GUAYAMA | 2022-04-16 21:45 | 2022-04-16 23:42 | 630 | 001:57 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22041600237 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 117 | 2022-04-16 | 73710 | keep | 0 | Apr | 2022 | 0.050204 | 0.00042909 | Sustained | FALSE | FALSE | Not_TMED_Event | 630
GUAYAMA | 2022-04-16 21:45 | 2022-04-17 08:46 | 4132 | 011:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 LA CARGA DEL 4003-01 Y DEL 4003-02 ESTAN TRANSFERIDAS AL 4006-05 | P22041600238 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 661 | 2022-04-16 | 2731252 | keep | 0 | Apr | 2022 | 1.8602 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-04-16 21:45 | 2022-04-17 08:46 | 4279 | 011:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 LA CARGA DEL 4003-01 Y DEL 4003-02 ESTAN TRANSFERIDAS AL 4006-05 | P22041600238 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 661 | 2022-04-16 | 2828419 | keep | 0 | Apr | 2022 | 1.9264 | 0.0029144 | Sustained | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-04-16 21:45 | 2022-04-17 08:46 | 1945 | 011:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 LA CARGA DEL 4003-03 ESTA TRANSFERIDA AL 4006-04 | P22041600238 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 661 | 2022-04-16 | 1285645 | keep | 0 | Apr | 2022 | 0.87565 | 0.0013247 | Sustained | FALSE | FALSE | Not_TMED_Event | 1945
GUAYAMA | 2022-04-16 21:45 | 2022-04-17 08:46 | 1173 | 011:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22041600241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 661 | 2022-04-16 | 775353 | keep | 0 | Apr | 2022 | 0.52809 | 0.00079892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2022-04-16 21:45 | 2022-04-17 08:46 | 215 | 011:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 EL 4006-04 LLEVA LA CARGA DEL 4003-03 | P22041600241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 661 | 2022-04-16 | 142115 | keep | 0 | Apr | 2022 | 0.096794 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
GUAYAMA | 2022-04-16 21:45 | 2022-04-17 08:46 | 464 | 011:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 EL 4006-05 LLEVA LA CARGA DEL 4003-01 Y DEL 4003-02 | P22041600241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 661 | 2022-04-16 | 306704 | keep | 0 | Apr | 2022 | 0.20889 | 0.00031603 | Sustained | FALSE | FALSE | Not_TMED_Event | 464
CAGUAS | 2022-04-16 21:48 | 2022-04-16 23:35 | 1147 | 001:47 | P | DESGANCHE | SE TRANSFIRIO CARGA DEL CONVERTIDOR 3103-04 AL 3301-01 CG-220416-01 | C22041600097 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-04-16 | 122729 | keep | 0 | Apr | 2022 | 0.08359 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-16 22:40 | 2022-04-16 22:49 | 1501 | 000:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO BKR A PETICION DE GIOVANNIE RIVERA PARA CERRAR PUENTE ABIERTO TRASPATIO | B22041600000 | Additional_clients | Wire Down | Include | Include | Equipment | 9 | 2022-04-16 | 13509 | keep | 0 | Apr | 2022 | 0.0092009 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-16 23:11 | 2022-04-17 12:32 | 73 | 013:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO CG-220416-02 | C22041600163 | Partial_restoration | Wire Down | Include | Include | Equipment | 801 | 2022-04-16 | 58473 | keep | 0 | Apr | 2022 | 0.039826 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-16 23:13 | 2022-04-17 21:38 | 2 | 022:25 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | R22041600256 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1345 | 2022-04-16 | 2690 | keep | 0 | Apr | 2022 | 0.0018321 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-04-16 23:35 | 2022-04-17 10:39 | 703 | 011:04 | P | DESGANCHE | BAMBUAS SOBRE LINEAS Y AISLADOR QUEMADO CG-220416-01 | C22041600097 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 664 | 2022-04-16 | 466792 | keep | 0 | Apr | 2022 | 0.31793 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-17 02:03 | 2022-04-17 02:04 | 1902 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 1902 | keep | 0 | Apr | 2022 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2022-04-17 02:03 | 2022-04-17 02:04 | 970 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 970 | keep | 0 | Apr | 2022 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2022-04-17 02:03 | 2022-04-17 02:04 | 3003 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 3003 | keep | 0 | Apr | 2022 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2022-04-17 02:03 | 2022-04-17 02:04 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 2343 | keep | 0 | Apr | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2022-04-17 02:03 | 2022-04-17 02:04 | 1830 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 1830 | keep | 0 | Apr | 2022 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2022-04-17 02:03 | 2022-04-17 02:04 | 710 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 710 | keep | 0 | Apr | 2022 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2022-04-17 02:03 | 2022-04-17 02:04 | 1197 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 1197 | keep | 0 | Apr | 2022 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
FAJARDO | 2022-04-17 02:04 | 2022-04-17 17:57 | 1 | 015:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | R22041600237 | New_Event | Wire Down | Include | Include | Equipment | 953 | 2022-04-17 | 953 | keep | 0 | Apr | 2022 | 0.00064908 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-17 02:08 | 2022-04-17 09:17 | 8 | 007:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C22041700020 | New_Event | Bad Weather | Include | Include | Weather | 429 | 2022-04-17 | 3432 | keep | 0 | Apr | 2022 | 0.0023375 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-17 02:28 | 2022-04-17 13:15 | 40 | 010:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L & SE REMPLAZO AISLADOR | S22041700009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 647 | 2022-04-17 | 25880 | keep | 0 | Apr | 2022 | 0.017627 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-17 03:58 | 2022-04-17 03:59 | 553 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 40% POR EL 1204-01 | S22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 553 | keep | 0 | Apr | 2022 | 0.00037665 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2022-04-17 04:53 | 2022-04-17 13:45 | 50 | 008:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE | S22041700015 | New_Event |  |  | Include | Wildlife | 532 | 2022-04-17 | 26600 | keep | 0 | Apr | 2022 | 0.018117 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-04-17 05:03 | 2022-04-17 05:04 | 327 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 327 | keep | 0 | Apr | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
BAYAMON | 2022-04-17 05:08 | 2022-04-17 15:00 | 30 | 009:52 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22041700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 592 | 2022-04-17 | 17760 | keep | 0 | Apr | 2022 | 0.012096 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-17 06:13 | 2022-04-17 06:14 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 888 | keep | 0 | Apr | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-04-17 06:13 | 2022-04-17 06:14 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 393 | keep | 0 | Apr | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-04-17 06:13 | 2022-04-17 06:14 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22041700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-17 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-04-17 06:36 | 2022-04-17 08:32 | 40 | 001:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X80 EN C/L (POR AVE EN EL 13KV) | S22041700021 | New_Event |  |  | Include | Wildlife | 116 | 2022-04-17 | 4640 | keep | 0 | Apr | 2022 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-04-17 06:40 | 2022-04-18 07:09 | 8 | 024:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M22041700025 | New_Event | Wire Down | Include | Include | Equipment | 1469 | 2022-04-17 | 11752 | keep | 0 | Apr | 2022 | 0.0080042 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-17 06:42 | 2022-04-17 08:16 | 60 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22041700052 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2022-04-17 | 5640 | keep | 0 | Apr | 2022 | 0.0038414 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-04-17 06:48 | 2022-04-17 13:51 | 95 | 007:03 | P | DESGANCHE | 1X50 EN C/L & 1X30 EN C/L (SE DESGANCHO) | R22041700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 423 | 2022-04-17 | 40185 | keep | 0 | Apr | 2022 | 0.02737 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
ARECIBO | 2022-04-17 06:58 | 2022-04-17 15:01 | 125 | 008:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 Y 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A22041700010 | New_Event | Wire Down | Include | Include | Equipment | 483 | 2022-04-17 | 60375 | keep | 0 | Apr | 2022 | 0.041121 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
UTUADO | 2022-04-17 07:06 | 2022-04-17 09:14 | 100 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE AVERIADO | A22041700011 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2022-04-17 | 12800 | keep | 0 | Apr | 2022 | 0.008718 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-04-17 07:12 | 2022-04-17 10:12 | 25 | 003:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN TRANSFORMADOR | P22041700125 | New_Event | Wire Down | Include | Include | Equipment | 180 | 2022-04-17 | 4500 | keep | 0 | Apr | 2022 | 0.0030649 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-04-17 07:14 | 2022-04-17 08:08 | 30 | 000:54 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R22041700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-04-17 | 1620 | keep | 0 | Apr | 2022 | 0.0011034 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-04-17 07:15 | 2022-04-17 07:16 | 3005 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041700060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 3005 | keep | 0 | Apr | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
PONCE | 2022-04-17 07:15 | 2022-04-17 15:30 | 30 | 008:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22041700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 495 | 2022-04-17 | 14850 | keep | 0 | Apr | 2022 | 0.010114 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-17 07:22 | 2022-04-17 15:32 | 50 | 008:10 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22041700024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 490 | 2022-04-17 | 24500 | keep | 0 | Apr | 2022 | 0.016687 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-17 07:34 | 2022-04-17 22:45 | 7 | 015:11 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22041700015 | New_Event | Bad Weather | Include | Include | Weather | 911 | 2022-04-17 | 6377 | keep | 0 | Apr | 2022 | 0.0043433 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-04-17 07:36 | 2022-04-17 14:00 | 6 | 006:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22041700026 | New_Event | Bad Weather | Include | Include | Weather | 384 | 2022-04-17 | 2304 | keep | 0 | Apr | 2022 | 0.0015692 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-17 07:44 | 2022-04-17 07:45 | 1106 | 000:01 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL - 60% DE SU CARGA TRANSFERIDA AL 1529-15 | S22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1106 | keep | 0 | Apr | 2022 | 0.00075329 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
BAYAMON | 2022-04-17 07:44 | 2022-04-17 07:45 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA - 60% DE LA CARGA DEL 1346-02 | S22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1802 | keep | 0 | Apr | 2022 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
MAYAGÃœEZ | 2022-04-17 07:48 | 2022-04-17 12:46 | 30 | 004:58 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22041700029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2022-04-17 | 8940 | keep | 0 | Apr | 2022 | 0.006089 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-17 07:48 | 2022-04-17 11:52 | 65 | 004:04 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22041700027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2022-04-17 | 15860 | keep | 0 | Apr | 2022 | 0.010802 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2022-04-17 07:58 | 2022-04-17 11:07 | 15 | 003:09 | P | SOBRECARGA | 1 X 30 EN CONVERTIDOR SE REALIZO PRUEBAS Y SE SOLICITAR CAMBIO DE EQUIPO | A22041700017 | New_Event | Trip Due To Overload | Include | Include | Other | 189 | 2022-04-17 | 2835 | keep | 0 | Apr | 2022 | 0.0019309 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-04-17 08:08 | 2022-04-17 08:30 | 100 | 000:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22041700090 | New_Event | Bad Weather | Include | Include | Weather | 22 | 2022-04-17 | 2200 | keep | 0 | Apr | 2022 | 0.0014984 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-17 08:09 | 2022-04-17 14:14 | 21 | 006:05 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN C/L SE RETIRO PENCAS | R22071700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2022-04-17 | 7665 | keep | 0 | Apr | 2022 | 0.0052206 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2022-04-17 08:11 | 2022-04-17 16:33 | 150 | 008:22 | P | NO SE REPORTO CAUSA | 1X80 EN AEREO PROVISIONAL | S22041700039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 502 | 2022-04-17 | 75300 | keep | 0 | Apr | 2022 | 0.051286 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-04-17 08:14 | 2022-04-17 12:00 | 50 | 003:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22041700183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-04-17 | 11300 | keep | 0 | Apr | 2022 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-04-17 08:16 | 2022-04-18 09:44 | 2 | 025:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | C22041700094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1528 | 2022-04-17 | 3056 | keep | 0 | Apr | 2022 | 0.0020814 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-04-17 08:18 | 2022-04-17 15:25 | 1 | 007:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22041700030 | New_Event | Bad Weather | Include | Include | Weather | 427 | 2022-04-17 | 427 | keep | 0 | Apr | 2022 | 0.00029083 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-04-17 08:22 | 2022-04-17 11:32 | 20 | 003:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO DE SU- 2 @ SU-1. PENDIENTE CAJA A REMPLAZAR | R22041700010 | New_Event | Cutout Failure | Include | Include | Equipment | 190 | 2022-04-17 | 3800 | keep | 0 | Apr | 2022 | 0.0025882 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-04-17 08:22 | 2022-04-17 10:07 | 40 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA LLUVIAS | C22041700098 | New_Event |  |  | Include | Wildlife | 105 | 2022-04-17 | 4200 | keep | 0 | Apr | 2022 | 0.0028606 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-17 08:26 | 2022-04-17 22:41 | 1 | 014:15 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S22041700043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 855 | 2022-04-17 | 855 | keep | 0 | Apr | 2022 | 0.00058234 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-17 08:49 | 2022-04-17 19:16 | 7 | 010:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M22041700037 | New_Event | Wire Down | Include | Include | Equipment | 627 | 2022-04-17 | 4389 | keep | 0 | Apr | 2022 | 0.0029893 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-04-17 08:52 | 2022-04-17 09:54 | 20 | 001:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C22041700114 | New_Event | Bad Weather | Include | Include | Weather | 62 | 2022-04-17 | 1240 | keep | 0 | Apr | 2022 | 0.00084456 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-04-17 08:59 | 2022-04-17 14:57 | 4 | 005:58 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22041700015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 358 | 2022-04-17 | 1432 | keep | 0 | Apr | 2022 | 0.00097533 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-04-17 09:04 | 2022-04-18 11:57 | 50 | 026:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22041700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1613 | 2022-04-17 | 80650 | keep | 0 | Apr | 2022 | 0.05493 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-17 09:06 | 2022-04-17 14:40 | 80 | 005:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTE VIENTO | M22041700041 | New_Event | Bad Weather | Include | Include | Weather | 334 | 2022-04-17 | 26720 | keep | 0 | Apr | 2022 | 0.018199 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-17 09:16 | 2022-04-17 09:17 | 2825 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22041700044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 2825 | keep | 0 | Apr | 2022 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
HUMACAO | 2022-04-17 09:17 | 2022-04-17 12:57 | 20 | 003:40 | P | CABLE SOTERRADO AVERIADO | TRAMO AVERIADO DEL SU 4B7 AL T SE DEJO SECCIONALIZADO Y SE CERRO N/O SU4B7A AL T3 | C22041700127 | New_Event | UG Cable Fault | Include | Include | Equipment | 220 | 2022-04-17 | 4400 | keep | 0 | Apr | 2022 | 0.0029968 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-04-17 09:22 | 2022-04-17 09:23 | 80 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M22041700046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 80 | keep | 0 | Apr | 2022 | 5.4488e-05 | 5.4488e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-17 09:26 | 2022-04-17 09:27 | 80 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M22041700048 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 80 | keep | 0 | Apr | 2022 | 5.4488e-05 | 5.4488e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-17 09:32 | 2022-04-17 12:15 | 600 | 002:43 | P | NO SE REPORTO CAUSA | 1X100 DE RISER @ SU-2 1X80 DE SU-6 @ SU-7 | S22041700063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2022-04-17 | 97800 | keep | 0 | Apr | 2022 | 0.066611 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
MAYAGÃœEZ | 2022-04-17 09:32 | 2022-04-17 09:33 | 2825 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M22041700050 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 2825 | keep | 0 | Apr | 2022 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
BAYAMON | 2022-04-17 09:33 | 2022-04-17 09:34 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 3597 | keep | 0 | Apr | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-04-17 09:34 | 2022-04-17 14:00 | 250 | 004:26 | P | NO SE REPORTO CAUSA | 2 X 140 EN CORTE DE LINEA | B22041700031 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 266 | 2022-04-17 | 66500 | keep | 0 | Apr | 2022 | 0.045293 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-04-17 09:36 | 2022-04-17 09:37 | 2324 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 2324 | keep | 0 | Apr | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
MAYAGÃœEZ | 2022-04-17 09:37 | 2022-04-17 09:38 | 637 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 6703-03 | M22041700052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-17 | 637 | keep | 0 | Apr | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-04-17 09:37 | 2022-04-17 09:38 | 1491 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR 6703-02 | M22041700052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-17 | 1491 | keep | 0 | Apr | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-04-17 09:38 | 2022-04-17 10:35 | 150 | 000:57 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22041700058 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-04-17 | 8550 | keep | 0 | Apr | 2022 | 0.0058234 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-04-17 09:42 | 2022-04-17 14:59 | 70 | 005:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22041700142 | New_Event | Bad Weather | Include | Include | Weather | 317 | 2022-04-17 | 22190 | keep | 0 | Apr | 2022 | 0.015114 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-04-17 09:47 | 2022-04-17 18:46 | 80 | 008:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22041700056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 539 | 2022-04-17 | 43120 | keep | 0 | Apr | 2022 | 0.029369 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-17 09:52 | 2022-04-17 13:15 | 50 | 003:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22041700060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-04-17 | 10150 | keep | 0 | Apr | 2022 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-17 09:55 | 2022-04-17 09:56 | 34 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 34 | keep | 0 | Apr | 2022 | 2.3157e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
MAYAGÃœEZ | 2022-04-17 09:56 | 2022-04-17 09:57 | 1117 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041700195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1117 | keep | 0 | Apr | 2022 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-04-17 09:56 | 2022-04-17 09:57 | 1671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR LLEVA LA CARGA DEL 6404-01 | M22041700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1671 | keep | 0 | Apr | 2022 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
UTUADO | 2022-04-17 09:56 | 2022-04-17 17:30 | 250 | 007:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA Y SE CERRO CORTE DE LINEA | A22041700045 | New_Event | Wire Down | Include | Include | Equipment | 454 | 2022-04-17 | 113500 | keep | 0 | Apr | 2022 | 0.077304 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2022-04-17 09:57 | 2022-04-18 10:43 | 1 | 024:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22041700061 | New_Event | Bad Weather | Include | Include | Weather | 1486 | 2022-04-17 | 1486 | keep | 0 | Apr | 2022 | 0.0010121 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-04-17 10:00 | 2022-04-17 12:25 | 15 | 002:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041700046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-04-17 | 2175 | keep | 0 | Apr | 2022 | 0.0014814 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-04-17 10:09 | 2022-04-17 15:19 | 50 | 005:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE ON AVE | C22041700160 | New_Event |  |  | Include | Wildlife | 310 | 2022-04-17 | 15500 | keep | 0 | Apr | 2022 | 0.010557 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-17 10:14 | 2022-04-18 09:01 | 26 | 022:47 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | S22041700067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1367 | 2022-04-17 | 35542 | keep | 0 | Apr | 2022 | 0.024207 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2022-04-17 10:19 | 2022-04-17 16:09 | 90 | 005:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22041700166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2022-04-17 | 31500 | keep | 0 | Apr | 2022 | 0.021455 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-04-17 10:23 | 2022-04-17 13:53 | 40 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22041700053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2022-04-17 | 8400 | keep | 0 | Apr | 2022 | 0.0057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-04-17 10:32 | 2022-04-17 11:28 | 250 | 000:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABREN MACHETES PARA REEMPLAZAR AISLADOR ROTO | P22041700216 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 56 | 2022-04-17 | 14000 | keep | 0 | Apr | 2022 | 0.0095353 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2022-04-17 10:33 | 2022-04-17 13:53 | 80 | 003:20 | P | DESGANCHE | 2 X 40 Y 1 X 50 EN CORTES DE LINEA SE REALIZO DESGANCHE | M22041700073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2022-04-17 | 16000 | keep | 0 | Apr | 2022 | 0.010898 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-17 10:35 | 2022-04-17 10:36 | 637 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 6703-03 | M22041700075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-17 | 637 | keep | 0 | Apr | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-04-17 10:35 | 2022-04-17 10:36 | 1491 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR 6703-02 | M22041700075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-17 | 1491 | keep | 0 | Apr | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-04-17 10:36 | 2022-04-17 17:23 | 150 | 006:47 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22041700058 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 407 | 2022-04-17 | 61050 | keep | 0 | Apr | 2022 | 0.041581 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-04-17 10:39 | 2022-04-17 10:43 | 1752 | 000:04 | P | DESGANCHE | DISPARO SE VERIFICO PERSONAL FUERA CG-220416-01 CARGA DEL CONVERTIDOR DEL 3103-04 POR EL 3301-01 | C22041600097 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-04-17 | 7008 | keep | 0 | Apr | 2022 | 0.0047731 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-17 10:43 | 2022-04-17 12:20 | 703 | 001:37 | P | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEA Y SE REEMPLAZO DISCO QUEMADO CG-220416-01 | C22041600097 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-04-17 | 68191 | keep | 0 | Apr | 2022 | 0.046445 | 0.00047881 | Sustained | FALSE | FALSE | Not_TMED_Event | 703
CAGUAS | 2022-04-17 10:48 | 2022-04-17 14:49 | 14 | 004:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22041700174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2022-04-17 | 3374 | keep | 0 | Apr | 2022 | 0.002298 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2022-04-17 10:49 | 2022-04-17 13:08 | 50 | 002:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22041700223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-04-17 | 6950 | keep | 0 | Apr | 2022 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-04-17 10:50 | 2022-04-17 10:51 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1310 | keep | 0 | Apr | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
MAYAGÃœEZ | 2022-04-17 10:52 | 2022-04-17 18:55 | 100 | 008:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22041700086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 483 | 2022-04-17 | 48300 | keep | 0 | Apr | 2022 | 0.032897 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-17 10:58 | 2022-04-17 14:44 | 90 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22041700177 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2022-04-17 | 20340 | keep | 0 | Apr | 2022 | 0.013853 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-04-17 11:01 | 2022-04-17 21:20 | 60 | 010:19 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22041700095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 619 | 2022-04-17 | 37140 | keep | 0 | Apr | 2022 | 0.025296 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-17 11:07 | 2022-04-17 11:08 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M22041700108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 863 | keep | 0 | Apr | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
ARECIBO | 2022-04-17 11:18 | 2022-04-17 11:19 | 3654 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A22041700060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 3654 | keep | 0 | Apr | 2022 | 0.0024887 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
FAJARDO | 2022-04-17 11:24 | 2022-04-17 14:13 | 100 | 002:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN RISER 2 X 65 EN C/L SE REMPLAZO AISLADORES DISCO Y SE SUBIO PRIMARIA | R22041700027 | New_Event | Wire Down | Include | Include | Equipment | 169 | 2022-04-17 | 16900 | keep | 0 | Apr | 2022 | 0.011511 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-17 11:30 | 2022-04-17 11:31 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR - LLEVA LA CARGA DEL 1206-02 | S22041700087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-04-17 11:30 | 2022-04-17 11:31 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR - CARGA TRANSFERIDA AL 1206-01 | S22041700087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
MAYAGÃœEZ | 2022-04-17 11:48 | 2022-04-17 17:22 | 25 | 005:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22041700122 | New_Event | Wire Down | Include | Include | Equipment | 334 | 2022-04-17 | 8350 | keep | 0 | Apr | 2022 | 0.0056871 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-04-17 11:48 | 2022-04-18 10:42 | 10 | 022:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA | A22041700063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1374 | 2022-04-17 | 13740 | keep | 0 | Apr | 2022 | 0.0093583 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-17 11:50 | 2022-04-17 14:42 | 29 | 002:52 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22041700192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-04-17 | 4988 | keep | 0 | Apr | 2022 | 0.0033973 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CAGUAS | 2022-04-17 11:56 | 2022-04-17 12:05 | 1590 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-04-17 | 14310 | keep | 0 | Apr | 2022 | 0.0097465 | 0.0010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 1590
SAN JUAN | 2022-04-17 12:11 | 2022-04-17 12:12 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR - LLEVA LA CARGA DEL 1206-02 | S22041700095 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-04-17 12:11 | 2022-04-17 12:12 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR - CARGA TRANSFERIDA AL 1206-01 | S22041700095 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
FAJARDO | 2022-04-17 12:16 | 2022-04-17 15:16 | 12 | 003:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN C/L SE RETIRO LAGARTO | R22041700037 | New_Event |  |  | Include | Wildlife | 180 | 2022-04-17 | 2160 | keep | 0 | Apr | 2022 | 0.0014712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-17 12:21 | 2022-04-17 17:01 | 60 | 004:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON LAGARTO | C22041700214 | New_Event |  |  | Include | Wildlife | 280 | 2022-04-17 | 16800 | keep | 0 | Apr | 2022 | 0.011442 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-17 12:41 | 2022-04-18 13:45 | 20 | 025:04 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22041700075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1504 | 2022-04-17 | 30080 | keep | 0 | Apr | 2022 | 0.020487 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-17 12:44 | 2022-04-17 12:45 | 2124 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | S22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 2124 | keep | 0 | Apr | 2022 | 0.0014466 | 0.0014466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2124
AGUADILLA | 2022-04-17 12:48 | 2022-04-17 18:40 | 200 | 005:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO EN MACHETES | M22041700147 | New_Event | Wire Down | Include | Include | Equipment | 352 | 2022-04-17 | 70400 | keep | 0 | Apr | 2022 | 0.047949 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-04-17 12:52 | 2022-04-17 16:46 | 100 | 003:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22041700226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-04-17 | 23400 | keep | 0 | Apr | 2022 | 0.015938 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-04-17 13:01 | 2022-04-17 13:02 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1234 | keep | 0 | Apr | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
HUMACAO | 2022-04-17 13:02 | 2022-04-18 12:20 | 10 | 023:18 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR T - 4 | C22041700230 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1398 | 2022-04-17 | 13980 | keep | 0 | Apr | 2022 | 0.0095217 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-04-17 13:21 | 2022-04-17 13:45 | 6 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA Y SE REGULO VOLTAGE DEL TAP 1 AL 3 124V | C22041700236 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2022-04-17 | 144 | keep | 0 | Apr | 2022 | 9.8078e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-04-17 13:23 | 2022-04-17 13:24 | 458 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE INTERRUPTOR POSTE PARTIDO | A22041700083 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2022-04-17 | 458 | keep | 0 | Apr | 2022 | 0.00031194 | 0.00031194 | Momentary | FALSE | FALSE | Not_TMED_Event | 458
BAYAMON | 2022-04-17 13:26 | 2022-04-17 16:15 | 40 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22041700107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-04-17 | 6760 | keep | 0 | Apr | 2022 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-17 13:27 | 2022-04-17 20:33 | 100 | 007:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | A22041700084 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 426 | 2022-04-17 | 42600 | keep | 0 | Apr | 2022 | 0.029015 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-17 13:31 | 2022-04-17 13:32 | 458 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE INTERRUPTOR POSTE PARTIDO | A22041700086 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 1 | 2022-04-17 | 458 | keep | 0 | Apr | 2022 | 0.00031194 | 0.00031194 | Momentary | FALSE | FALSE | Not_TMED_Event | 458
GUAYAMA | 2022-04-17 13:32 | 2022-04-17 14:46 | 30 | 001:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22041700259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-04-17 | 2220 | keep | 0 | Apr | 2022 | 0.001512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-17 13:40 | 2022-04-17 15:51 | 458 | 002:11 | T | ESTRUCTURA AVERIADA | SE ABRIO PUENTE PARA SECCIONALIZAR AVERIA DE POSTE PARTIDO Y SE CERRO INTERRUPTOR | A22041700087 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 131 | 2022-04-17 | 59998 | keep | 0 | Apr | 2022 | 0.040864 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
ARECIBO | 2022-04-17 13:49 | 2022-04-17 13:50 | 1986 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR RAMA DE PALMA CRUZANDO LINEAS PRIMARIAS | A22041700088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-17 | 1986 | keep | 0 | Apr | 2022 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2022-04-17 13:50 | 2022-04-17 17:17 | 10 | 003:27 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE PALMA CRUZADO LINEA | A22041700111 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-04-17 | 2070 | keep | 0 | Apr | 2022 | 0.0014099 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-04-17 13:51 | 2022-04-17 13:52 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1859 | keep | 0 | Apr | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2022-04-17 13:57 | 2022-04-17 17:45 | 40 | 003:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO | B22041700053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2022-04-17 | 9120 | keep | 0 | Apr | 2022 | 0.0062116 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-04-17 13:59 | 2022-04-17 20:00 | 30 | 006:01 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR RAMA | P22041700243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2022-04-17 | 10830 | keep | 0 | Apr | 2022 | 0.0073763 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-17 14:01 | 2022-04-17 19:10 | 50 | 005:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22041700055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2022-04-17 | 15450 | keep | 0 | Apr | 2022 | 0.010523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-17 14:13 | 2022-04-17 14:14 | 1117 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6404-02 QUE ESTA LLEVANDO LA CARGA POR 6404-01 | M22041700195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1117 | keep | 0 | Apr | 2022 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-04-17 14:13 | 2022-04-17 14:14 | 1671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041700195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1671 | keep | 0 | Apr | 2022 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
SAN JUAN | 2022-04-17 14:17 | 2022-04-17 20:49 | 200 | 006:32 | P | DESGANCHE | 1X80 EN C/L & 1X65 EN C/L | S22041700114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-04-17 | 78400 | keep | 0 | Apr | 2022 | 0.053398 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-04-17 14:26 | 2022-04-18 01:45 | 150 | 011:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22041700191 | New_Event | Bad Weather | Include | Include | Weather | 679 | 2022-04-17 | 101850 | keep | 0 | Apr | 2022 | 0.06937 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-04-17 14:28 | 2022-04-17 18:00 | 15 | 003:32 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22041700097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-04-17 | 3180 | keep | 0 | Apr | 2022 | 0.0021659 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-04-17 14:32 | 2022-04-17 14:33 | 274 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 274 | keep | 0 | Apr | 2022 | 0.00018662 | 0.00018662 | Momentary | FALSE | FALSE | Not_TMED_Event | 274
BAYAMON | 2022-04-17 14:35 | 2022-04-17 14:36 | 1079 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1079 | keep | 0 | Apr | 2022 | 0.0007349 | 0.0007349 | Momentary | FALSE | FALSE | Not_TMED_Event | 1079
PONCE | 2022-04-17 14:37 | 2022-04-17 16:30 | 35 | 001:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22041700260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-04-17 | 3955 | keep | 0 | Apr | 2022 | 0.0026937 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-04-17 14:38 | 2022-04-17 16:35 | 80 | 001:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 Y 1 X 30 EN CORTE DE LINEA SE REEMPLAZO DOS AISLADORES PARTIDOS | A22041700101 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 117 | 2022-04-17 | 9360 | keep | 0 | Apr | 2022 | 0.0063751 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-17 14:41 | 2022-04-17 16:50 | 80 | 002:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22041700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-04-17 | 10320 | keep | 0 | Apr | 2022 | 0.0070289 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-17 14:41 | 2022-04-17 14:42 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA CARGA DEL 1909-09 | S22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 222 | keep | 0 | Apr | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-04-17 14:41 | 2022-04-17 14:42 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1907-03 | S22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 4456 | keep | 0 | Apr | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-04-17 14:44 | 2022-04-17 21:09 | 50 | 006:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L & SE REMPLAZO CAJA PRIMARIA | B22041700062 | New_Event | Cutout Failure | Include | Include | Equipment | 385 | 2022-04-17 | 19250 | keep | 0 | Apr | 2022 | 0.013111 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-04-17 14:50 | 2022-04-17 19:09 | 30 | 004:19 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS | A22041700104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-04-17 | 7770 | keep | 0 | Apr | 2022 | 0.0052921 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-04-17 14:57 | 2022-04-17 17:32 | 100 | 002:35 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR RAMA | P22041700262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-04-17 | 15500 | keep | 0 | Apr | 2022 | 0.010557 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-17 15:03 | 2022-04-18 18:31 | 1 | 027:28 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | B22041700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1648 | 2022-04-17 | 1648 | keep | 0 | Apr | 2022 | 0.0011224 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-17 15:07 | 2022-04-17 15:08 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22041700266 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 527 | keep | 0 | Apr | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
BAYAMON | 2022-04-17 15:11 | 2022-04-17 19:20 | 200 | 004:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA @ CAJA EN C/L (NO FUNDIO) | S22041700127 | New_Event | Wire Down | Include | Include | Equipment | 249 | 2022-04-17 | 49800 | keep | 0 | Apr | 2022 | 0.033919 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-04-17 15:16 | 2022-04-17 20:37 | 4 | 005:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | A22041700110 | New_Event | Bad Weather | Include | Include | Weather | 321 | 2022-04-17 | 1284 | keep | 0 | Apr | 2022 | 0.00087453 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-17 15:20 | 2022-04-17 15:21 | 1079 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22041700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1079 | keep | 0 | Apr | 2022 | 0.0007349 | 0.0007349 | Momentary | FALSE | FALSE | Not_TMED_Event | 1079
VEGA BAJA | 2022-04-17 15:29 | 2022-04-17 22:21 | 220 | 006:52 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22041700070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 412 | 2022-04-17 | 90640 | keep | 0 | Apr | 2022 | 0.061734 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
MAYAGÃœEZ | 2022-04-17 15:30 | 2022-04-19 01:17 | 2 | 033:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA INDICO REQUIERE DESGANCHE | M22041700207 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2027 | 2022-04-17 | 4054 | keep | 0 | Apr | 2022 | 0.0027612 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-04-17 15:35 | 2022-04-17 18:23 | 100 | 002:48 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEA | C22041700250 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-04-17 | 16800 | keep | 0 | Apr | 2022 | 0.011442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-17 15:51 | 2022-04-17 21:10 | 100 | 005:19 | P | ESTRUCTURA AVERIADA | POSTE Y CRUCETAS PARTIDAS SE SECCIONALIZO AVERIA | A22041700132 | Partial_restoration | Defective Pole | Include | Include | Equipment | 319 | 2022-04-17 | 31900 | keep | 0 | Apr | 2022 | 0.021727 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-17 15:57 | 2022-04-17 18:07 | 30 | 002:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C22041700269 | New_Event | Wire Down | Include | Include | Equipment | 130 | 2022-04-17 | 3900 | keep | 0 | Apr | 2022 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-17 16:05 | 2022-04-17 18:41 | 6 | 002:36 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | M22041700215 | New_Event | Service Transformer Failure | Include | Include | Equipment | 156 | 2022-04-17 | 936 | keep | 0 | Apr | 2022 | 0.00063751 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-04-17 16:16 | 2022-04-17 16:17 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2022-04-17 16:22 | 2022-04-17 18:45 | 40 | 002:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE DE XMR | B22041700076 | New_Event | Wire Down | Include | Include | Equipment | 143 | 2022-04-17 | 5720 | keep | 0 | Apr | 2022 | 0.0038959 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-17 16:31 | 2022-04-17 16:32 | 199 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 199 | keep | 0 | Apr | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2022-04-17 16:31 | 2022-04-17 16:32 | 24 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 24 | keep | 0 | Apr | 2022 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2022-04-17 16:33 | 2022-04-17 20:15 | 40 | 003:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22041700080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 222 | 2022-04-17 | 8880 | keep | 0 | Apr | 2022 | 0.0060481 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-04-17 16:34 | 2022-04-18 07:17 | 1 | 014:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22041700282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 883 | 2022-04-17 | 883 | keep | 0 | Apr | 2022 | 0.00060141 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-17 16:35 | 2022-04-17 22:21 | 30 | 005:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22041700122 | New_Event | Bad Weather | Include | Include | Weather | 346 | 2022-04-17 | 10380 | keep | 0 | Apr | 2022 | 0.0070698 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-04-17 16:37 | 2022-04-18 14:21 | 150 | 021:44 | P | DESGANCHE | 2 X 80 EN C/L SE RETIRO BAMBUAS DE LA LINEA | C22041700278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1304 | 2022-04-17 | 195600 | keep | 0 | Apr | 2022 | 0.13322 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-04-17 16:44 | 2022-04-18 09:16 | 35 | 016:32 | P | DESGANCHE | 1 X 50 EN C/L | C22041700280 | New_Event | Vegetation Contact | Include | Include | Vegetation | 992 | 2022-04-17 | 34720 | keep | 0 | Apr | 2022 | 0.023648 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-04-17 17:23 | 2022-04-17 21:01 | 75 | 003:38 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22041700118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2022-04-17 | 16350 | keep | 0 | Apr | 2022 | 0.011136 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-04-17 17:38 | 2022-04-18 05:48 | 65 | 012:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE AVERIADO | M22041700238 | New_Event | Cutout Failure | Include | Include | Equipment | 730 | 2022-04-17 | 47450 | keep | 0 | Apr | 2022 | 0.032318 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-04-17 17:59 | 2022-04-17 18:00 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 TRANSFERIDO AL 1303-05, Y LLEVA TRANSFERIDA LA CARGA DEL 1303-01 Y DEL 1346-06 | S22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1681 | keep | 0 | Apr | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-17 17:59 | 2022-04-17 18:00 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 TRANSFERIDO AL 1303-05, Y LLEVA TRANSFERIDA LA CARGA DEL 1303-01 Y DEL 1346-06 | S22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1598 | keep | 0 | Apr | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
UTUADO | 2022-04-17 18:05 | 2022-04-17 20:32 | 40 | 002:27 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR BAMBUAS CRUZANDO LINEAS | A22041700142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-04-17 | 5880 | keep | 0 | Apr | 2022 | 0.0040048 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-17 18:17 | 2022-04-18 14:18 | 12 | 020:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22041700095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1201 | 2022-04-17 | 14412 | keep | 0 | Apr | 2022 | 0.0098159 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-04-17 18:18 | 2022-04-17 18:19 | 2141 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C22041700299 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-04-17 | 2141 | keep | 0 | Apr | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-04-17 18:19 | 2022-04-18 17:03 | 37 | 022:44 | P | CABLE SOTERRADO AVERIADO | 1 SMU 20 DE 25A EN SU - 1 Y 1 X 30 EN RISER AVERIA SOTERRADA DEL T - 18 @ T - 17 | C22041700337 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1364 | 2022-04-17 | 50468 | keep | 0 | Apr | 2022 | 0.034374 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
MAYAGÃœEZ | 2022-04-17 18:33 | 2022-04-18 02:03 | 80 | 007:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22041700247 | New_Event | Bad Weather | Include | Include | Weather | 450 | 2022-04-17 | 36000 | keep | 0 | Apr | 2022 | 0.024519 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-17 18:33 | 2022-04-18 | 10 | 005:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22041700148 | New_Event | Wire Down | Include | Include | Equipment | 327 | 2022-04-17 | 3270 | keep | 0 | Apr | 2022 | 0.0022272 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-17 18:39 | 2022-04-17 22:33 | 60 | 003:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22041700149 | New_Event | Bad Weather | Include | Include | Weather | 234 | 2022-04-17 | 14040 | keep | 0 | Apr | 2022 | 0.0095626 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-17 18:52 | 2022-04-19 13:16 | 3 | 042:24 | P | ERROR HUMANO | YA SE HABIA REEMPLAZADO POSTE Y SE CERRO TRANSFORMADOR QUE SE QUEDO ABIERTO | M22041700199 | New_Event | Human Error | Include | Include | Other | 2544 | 2022-04-17 | 7632 | keep | 0 | Apr | 2022 | 0.0051981 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-04-17 18:54 | 2022-04-17 20:15 | 50 | 001:21 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | R22041700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-04-17 | 4050 | keep | 0 | Apr | 2022 | 0.0027584 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-04-17 19:03 | 2022-04-17 19:04 | 4132 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR CARGA POR 4006-05 | P22041700288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-17 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-04-17 19:03 | 2022-04-17 19:04 | 4279 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR CARGA POR 4006-05 | P22041700288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-17 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-04-17 19:03 | 2022-04-17 19:04 | 464 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22041700288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-17 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-04-17 19:04 | 2022-04-17 21:50 | 40 | 002:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22041700291 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-04-17 | 6640 | keep | 0 | Apr | 2022 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-17 19:12 | 2022-04-17 21:21 | 25 | 002:09 | P | DESGANCHE | 1X65 EN C/L | S22041700157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-04-17 | 3225 | keep | 0 | Apr | 2022 | 0.0021965 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-04-17 19:14 | 2022-04-18 10:30 | 50 | 015:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 Y 2 X 50 C/L SE REMPLAZO PORTAFUSIBLES | S22041700158 | New_Event | Cutout Failure | Include | Include | Equipment | 916 | 2022-04-17 | 45800 | keep | 0 | Apr | 2022 | 0.031194 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-04-17 19:24 | 2022-04-17 19:25 | 1457 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22041700295 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1457 | keep | 0 | Apr | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
MAYAGÃœEZ | 2022-04-17 19:26 | 2022-04-18 02:50 | 100 | 007:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22041700253 | New_Event | Bad Weather | Include | Include | Weather | 444 | 2022-04-17 | 44400 | keep | 0 | Apr | 2022 | 0.030241 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-04-17 19:28 | 2022-04-17 23:50 | 279 | 004:22 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B22041700103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-04-17 | 73098 | keep | 0 | Apr | 2022 | 0.049787 | 0.00019003 | Sustained | FALSE | FALSE | Not_TMED_Event | 279
UTUADO | 2022-04-17 19:42 | 2022-04-17 22:14 | 150 | 002:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22041700162 | New_Event | Bad Weather | Include | Include | Weather | 152 | 2022-04-17 | 22800 | keep | 0 | Apr | 2022 | 0.015529 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-04-17 19:48 | 2022-04-18 12:56 | 44 | 017:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REEMPLAZO AISLADOR ROTO | C22041700308 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1028 | 2022-04-17 | 45232 | keep | 0 | Apr | 2022 | 0.030807 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
HUMACAO | 2022-04-17 20:06 | 2022-04-18 11:04 | 15 | 014:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE PRIMARIO | C22041700301 | New_Event | Wire Down | Include | Include | Equipment | 898 | 2022-04-17 | 13470 | keep | 0 | Apr | 2022 | 0.0091744 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-17 21:04 | 2022-04-17 21:06 | 520 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL SOLO LLEVA 80% DE LA CARGA | B22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-17 | 1040 | keep | 0 | Apr | 2022 | 0.00070834 | 0.00035417 | Momentary | FALSE | FALSE | Not_TMED_Event | 520
MAYAGÃœEZ | 2022-04-17 21:08 | 2022-04-17 21:15 | 125 | 000:07 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22041700156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-04-17 | 875 | keep | 0 | Apr | 2022 | 0.00059596 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2022-04-17 21:10 | 2022-04-17 21:52 | 458 | 000:42 | T | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE SE ABRIO INTERRUPTOR PARA CERRAR PUENTES | A22041700197 | Additional_clients | Defective Pole | Include | Include | Equipment | 42 | 2022-04-17 | 19236 | keep | 0 | Apr | 2022 | 0.013102 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-17 21:18 | 2022-04-18 08:05 | 35 | 010:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTE VIENTO | P22041700303 | New_Event | Bad Weather | Include | Include | Weather | 647 | 2022-04-17 | 22645 | keep | 0 | Apr | 2022 | 0.015423 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-04-17 21:21 | 2022-04-17 21:22 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 1648 | keep | 0 | Apr | 2022 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-04-17 21:21 | 2022-04-17 21:22 | 2094 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE | R22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 2094 | keep | 0 | Apr | 2022 | 0.0014262 | 0.0014262 | Momentary | FALSE | FALSE | Not_TMED_Event | 2094
CAGUAS | 2022-04-17 21:25 | 2022-04-18 23:55 | 52 | 026:30 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL HACIA T-NO ROTULADO HASTA T-14 | C22041700330 | New_Event | UG Cable Fault | Include | Include | Equipment | 1590 | 2022-04-17 | 82680 | keep | 0 | Apr | 2022 | 0.056313 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2022-04-17 21:43 | 2022-04-17 22:00 | 238 | 000:17 | P | ESTRUCTURA AVERIADA | SE CERRO MACHETES 100% EN SERVICIO | S22041700000 | Additional_clients | Defective Pole | Include | Include | Equipment | 17 | 2022-04-17 | 4046 | keep | 0 | Apr | 2022 | 0.0027557 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-17 21:52 | 2022-04-18 09:06 | 10 | 011:14 | P | DESCONECTIVO DEFECTUOSO | AUXILIAR DE BARRA QUEMADO SE TRANSFIRIO CARGA AL 8002-05 DESPUES DEL REMPLAZO DEL POSTE SE ENCONTRO MACHETES DE BARRA QUEMADOS POR ESO SE UTILIZA ESA FECHA | A22041800027 | New_Event | Switch Failure | Include | Include | Equipment | 674 | 2022-04-17 | 6740 | keep | 0 | Apr | 2022 | 0.0045906 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-17 22:08 | 2022-04-17 23:14 | 40 | 001:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22041700205 | New_Event | Bad Weather | Include | Include | Weather | 66 | 2022-04-17 | 2640 | keep | 0 | Apr | 2022 | 0.0017981 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-17 22:43 | 2022-04-18 07:45 | 10 | 009:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041700360 | New_Event | Vegetation Contact | Include | Include | Vegetation | 542 | 2022-04-17 | 5420 | keep | 0 | Apr | 2022 | 0.0036915 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-17 23:02 | 2022-04-18 20:20 | 23 | 021:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | C22041700339 | New_Event |  |  | Include | Wildlife | 1278 | 2022-04-17 | 29394 | keep | 0 | Apr | 2022 | 0.02002 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2022-04-17 23:33 | 2022-04-17 23:34 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22041700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-17 | 2178 | keep | 0 | Apr | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
ARECIBO | 2022-04-17 23:33 | 2022-04-18 15:39 | 15 | 016:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 75KVA X 75KVA | A22041700212 | New_Event | Service Transformer Failure | Include | Include | Equipment | 966 | 2022-04-17 | 14490 | keep | 0 | Apr | 2022 | 0.0098691 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-18 00:03 | 2022-04-18 06:20 | 225 | 006:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO DEL 1303-05 Y SE CERRO N/O CONTRA 1908-03 99% EN SERVICIO LLEVA 1303-04 SJ-220418-01 | S22041800001 | New_Event | Wire Down | Include | Include | Equipment | 377 | 2022-04-18 | 84825 | keep | 0 | Apr | 2022 | 0.057774 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-18 00:03 | 2022-04-18 06:20 | 870 | 006:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO N/O CONTRA 1908-03 99% EN SERVICIO LLEVA 1303-04 SJ-220418-01 | S22041800001 | New_Event | Wire Down | Include | Include | Equipment | 377 | 2022-04-18 | 327990 | keep | 0 | Apr | 2022 | 0.22339 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2022-04-18 00:45 | 2022-04-18 02:50 | 100 | 002:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE ABRIO CORTE DE LINEA NO IDENTIFICADO (COORDENADAS +18.264817N, -67.117888W) PARA SECCIONALIZAR LINEA PIRMARIA PARTIDA EEVENTO | M22041800004 | New_Event | Wire Down | Include | Include | Equipment | 125 | 2022-04-18 | 12500 | keep | 0 | Apr | 2022 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-18 02:39 | 2022-04-18 02:40 | 1565 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22041800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-18 | 1565 | keep | 0 | Apr | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
MAYAGÃœEZ | 2022-04-18 02:50 | 2022-04-18 15:12 | 70 | 012:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | M22041800004 | Partial_restoration | Wire Down | Include | Include | Equipment | 742 | 2022-04-18 | 51940 | keep | 0 | Apr | 2022 | 0.035376 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-18 03:17 | 2022-04-18 03:18 | 638 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22041800010 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-18 | 638 | keep | 0 | Apr | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2022-04-18 03:18 | 2022-04-18 14:41 | 80 | 011:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22041800065 | 1st_after_momentary |  |  | Include | Wildlife | 683 | 2022-04-18 | 54640 | keep | 0 | Apr | 2022 | 0.037215 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-18 05:26 | 2022-04-18 09:58 | 50 | 004:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA Y PARARRAYO | S22041800091 | New_Event | Cutout Failure | Include | Include | Equipment | 272 | 2022-04-18 | 13600 | keep | 0 | Apr | 2022 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-18 05:56 | 2022-04-18 06:06 | 2858 | 000:10 | T | DESGANCHE | DISPARO DE INTERRUPTOR CERRADO POR SCADA | B22041800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 10 | 2022-04-18 | 28580 | keep | 0 | Apr | 2022 | 0.019466 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
PONCE | 2022-04-18 06:04 | 2022-04-18 06:05 | 234 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 200 | P22041800016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 234 | keep | 0 | Apr | 2022 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2022-04-18 06:04 | 2022-04-18 06:05 | 2468 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 200 | P22041800016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 2468 | keep | 0 | Apr | 2022 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
BAYAMON | 2022-04-18 06:08 | 2022-04-18 08:36 | 2858 | 002:28 | T | DESGANCHE | DISPARO DE INTERRUPTOR CERRADO POR SCADA SE SECCIONALIZO ALIMENTADOR POR ARBOL EN LA LINEA 75% EN SERVICIO TRABAJANDOSE CON GOI BY220418-01A | B22041800000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-04-18 | 422984 | keep | 0 | Apr | 2022 | 0.28809 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-18 06:20 | 2022-04-18 09:32 | 100 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO N/O CONTRA 1908-03 99% EN SERVICIO LLEVA 1303-04 SJ-220418-01 | S22041800001 | Partial_restoration | Wire Down | Include | Include | Equipment | 192 | 2022-04-18 | 19200 | keep | 0 | Apr | 2022 | 0.013077 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-18 06:27 | 2022-04-18 19:30 | 30 | 013:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041800022 | New_Event | Bad Weather | Include | Include | Weather | 783 | 2022-04-18 | 23490 | keep | 0 | Apr | 2022 | 0.015999 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-04-18 06:44 | 2022-04-18 09:02 | 100 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041800026 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2022-04-18 | 13800 | keep | 0 | Apr | 2022 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-18 06:45 | 2022-04-18 13:01 | 40 | 006:16 | P | DESGANCHE | 1 X 50 EN C/L | C22041800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2022-04-18 | 15040 | keep | 0 | Apr | 2022 | 0.010244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-04-18 06:50 | 2022-04-18 08:46 | 3502 | 001:56 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR RTU DOWN CERRADO MANUAL ELECTRICO | A22041800013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-04-18 | 406232 | keep | 0 | Apr | 2022 | 0.27668 | 0.0023852 | Sustained | FALSE | FALSE | Not_TMED_Event | 3502
CANOVANAS | 2022-04-18 06:55 | 2022-04-18 09:29 | 53 | 002:34 | P | DESGANCHE | 1 X 65 EN C/L | R22041800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-04-18 | 8162 | keep | 0 | Apr | 2022 | 0.0055591 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2022-04-18 07:06 | 2022-04-18 14:37 | 100 | 007:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041800030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 451 | 2022-04-18 | 45100 | keep | 0 | Apr | 2022 | 0.030717 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-04-18 07:12 | 2022-04-19 07:59 | 1 | 024:47 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22041800026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1487 | 2022-04-18 | 1487 | keep | 0 | Apr | 2022 | 0.0010128 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-18 07:47 | 2022-04-18 15:38 | 200 | 007:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041800033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2022-04-18 | 94200 | keep | 0 | Apr | 2022 | 0.064159 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-04-18 07:49 | 2022-04-18 14:27 | 20 | 006:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 20 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | P22041800034 | New_Event | Wire Down | Include | Include | Equipment | 398 | 2022-04-18 | 7960 | keep | 0 | Apr | 2022 | 0.0054215 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-04-18 07:53 | 2022-04-18 12:00 | 1 | 004:07 | P | PARARRAYOS DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZO DE PARARRAYOS DEFECTUOSO | M22041800035 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 247 | 2022-04-18 | 247 | keep | 0 | Apr | 2022 | 0.00016823 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-18 07:56 | 2022-04-18 12:00 | 1 | 004:04 | P | NO SE REPORTO CAUSA | 3 X 100 EN SU-3 SMU | S22041800122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2022-04-18 | 244 | keep | 0 | Apr | 2022 | 0.00016619 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-18 08:12 | 2022-04-18 10:37 | 38 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA POR FUERTE VIENTO | P22041800041 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2022-04-18 | 5510 | keep | 0 | Apr | 2022 | 0.0037528 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
SAN JUAN | 2022-04-18 08:17 | 2022-04-18 15:20 | 1 | 007:03 | P | NO SE REPORTO CAUSA | 2 X 20 TRANSFORMADORES | S22041800124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 423 | 2022-04-18 | 423 | keep | 0 | Apr | 2022 | 0.0002881 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-18 08:36 | 2022-04-18 16:30 | 714 | 007:54 | P | DESGANCHE | SE CERRARON MACHETES AL RETIRAR ARBOL DE LA LINEA Y CERRAR PUENTES PRIMARIOS EN VARIOS PUNTOS | B22041800044 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 474 | 2022-04-18 | 338436 | keep | 0 | Apr | 2022 | 0.23051 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-18 08:38 | 2022-04-18 14:14 | 150 | 005:36 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | S22041800126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 336 | 2022-04-18 | 50400 | keep | 0 | Apr | 2022 | 0.034327 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-04-18 08:44 | 2022-04-18 13:58 | 8 | 005:14 | P | PARARRAYOS DEFECTUOSO | 3 X 100 EN C/L SE ELIMINO PARARRAYO AVERIADO EN BANCO DE TRANSFORMADORES Y SE DEJO FUERA OTRO TRANSCLOSURE PRIVADO POR PARARRAYO AVERIADO | B22041800043 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 314 | 2022-04-18 | 2512 | keep | 0 | Apr | 2022 | 0.0017109 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-04-18 08:44 | 2022-04-18 19:42 | 4 | 010:58 | P | ESTRUCTURA AVERIADA | SE REEMPLAZARON 3 POSTES PARTIDOS | R22041800007 | New_Event | Defective Pole | Include | Include | Equipment | 658 | 2022-04-18 | 2632 | keep | 0 | Apr | 2022 | 0.0017926 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-04-18 08:45 | 2022-04-18 09:22 | 8 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO QUEMADO | P22041800006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-04-18 | 296 | keep | 0 | Apr | 2022 | 0.0002016 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-04-18 08:45 | 2022-04-18 13:50 | 1 | 005:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN MONTURA TRIFASICA POR FUERTE VIENTO | P22041800045 | New_Event | Bad Weather | Include | Include | Weather | 305 | 2022-04-18 | 305 | keep | 0 | Apr | 2022 | 0.00020773 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-18 08:51 | 2022-04-18 19:35 | 300 | 010:44 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041800046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 644 | 2022-04-18 | 193200 | keep | 0 | Apr | 2022 | 0.13159 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
UTUADO | 2022-04-18 08:51 | 2022-04-18 17:50 | 100 | 008:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | A22041800038 | New_Event | Wire Down | Include | Include | Equipment | 539 | 2022-04-18 | 53900 | keep | 0 | Apr | 2022 | 0.036711 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-18 08:56 | 2022-04-18 17:03 | 54 | 008:07 | P | DESGANCHE | 2 X 50 Y 1 X 40 EN CORTES DE LINEA | C22041800041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2022-04-18 | 26298 | keep | 0 | Apr | 2022 | 0.017911 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
MAYAGÃœEZ | 2022-04-18 09:24 | 2022-04-19 03:39 | 1 | 018:15 | P | SOBRECARGA | 1 X 8 EN TRANSFORMADOR INDICA SOBRECARGA | M22041800052 | New_Event | Trip Due To Overload | Include | Include | Other | 1095 | 2022-04-18 | 1095 | keep | 0 | Apr | 2022 | 0.0007458 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-18 09:32 | 2022-04-18 11:20 | 225 | 001:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE VOLVIO A CERRAR N/O CONTRA 1908-03 | S22041800001 | Partial_restoration | Wire Down | Include | Include | Equipment | 108 | 2022-04-18 | 24300 | keep | 0 | Apr | 2022 | 0.016551 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-18 09:32 | 2022-04-18 11:20 | 870 | 001:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE VOLVIO A CERRAR N/O CONTRA 1908-03 | S22041800001 | Additional_clients | Wire Down | Include | Include | Equipment | 108 | 2022-04-18 | 93960 | keep | 0 | Apr | 2022 | 0.063996 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-18 09:32 | 2022-04-18 10:22 | 3957 | 000:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO AMARRE CONTRA 1303-05 Y SE CERRO POR SCADA | S22041800136 | New_Event | Wire Down | Include | Include | Equipment | 50 | 2022-04-18 | 197850 | keep | 0 | Apr | 2022 | 0.13475 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
MAYAGÃœEZ | 2022-04-18 09:47 | 2022-04-18 16:50 | 1 | 007:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS PRIMARIAS QUEMADAS | M22041800058 | New_Event | Cutout Failure | Include | Include | Equipment | 423 | 2022-04-18 | 423 | keep | 0 | Apr | 2022 | 0.0002881 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-18 10:13 | 2022-04-18 15:01 | 33 | 004:48 | P | DESGANCHE | 1 X 80 EN C/L | C22041800084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-04-18 | 9504 | keep | 0 | Apr | 2022 | 0.0064731 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
ARECIBO | 2022-04-18 10:13 | 2022-04-18 11:45 | 35 | 001:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A22041800058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-04-18 | 3220 | keep | 0 | Apr | 2022 | 0.0021931 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-04-18 10:14 | 2022-04-18 10:15 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | B22041800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-18 | 222 | keep | 0 | Apr | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-04-18 10:14 | 2022-04-18 10:15 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | B22041800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-18 | 4456 | keep | 0 | Apr | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
HUMACAO | 2022-04-18 10:21 | 2022-04-20 07:10 | 10 | 044:49 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22041800089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2689 | 2022-04-18 | 26890 | keep | 0 | Apr | 2022 | 0.018315 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-18 10:22 | 2022-04-18 18:37 | 40 | 008:15 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041800065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 495 | 2022-04-18 | 19800 | keep | 0 | Apr | 2022 | 0.013486 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-18 10:23 | 2022-04-18 16:01 | 1 | 005:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADORES CRUCE CON AVE | R22041800015 | New_Event |  |  | Include | Wildlife | 338 | 2022-04-18 | 338 | keep | 0 | Apr | 2022 | 0.00023021 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-18 10:41 | 2022-04-18 18:08 | 1 | 007:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO XMR | B22041800069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 447 | 2022-04-18 | 447 | keep | 0 | Apr | 2022 | 0.00030445 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-18 10:49 | 2022-04-18 10:50 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22041800221 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-18 | 3957 | keep | 0 | Apr | 2022 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
UTUADO | 2022-04-18 10:51 | 2022-04-18 15:31 | 60 | 004:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22041800073 | New_Event | Bad Weather | Include | Include | Weather | 280 | 2022-04-18 | 16800 | keep | 0 | Apr | 2022 | 0.011442 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-18 10:53 | 2022-04-18 22:20 | 150 | 011:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041800074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 687 | 2022-04-18 | 103050 | keep | 0 | Apr | 2022 | 0.070187 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-04-18 10:58 | 2022-04-19 14:04 | 20 | 027:06 | P | DESGANCHE | DESGANCHO Y SE REEMPLAZO HOT CLAMP | C22041800099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1626 | 2022-04-18 | 32520 | keep | 0 | Apr | 2022 | 0.022149 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-18 11:05 | 2022-04-18 11:06 | 1 | 000:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO SECUNDARIA NO FUNDIO | C22041700310 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2022-04-18 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-18 11:06 | 2022-04-18 14:18 | 13 | 003:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22041800101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-04-18 | 2496 | keep | 0 | Apr | 2022 | 0.0017 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2022-04-18 11:11 | 2022-04-18 13:20 | 1 | 002:09 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN XMR | R22041800016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 129 | 2022-04-18 | 129 | keep | 0 | Apr | 2022 | 8.7861e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-18 11:19 | 2022-04-18 20:17 | 112 | 008:58 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22041800080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 538 | 2022-04-18 | 60256 | keep | 0 | Apr | 2022 | 0.04104 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
CAGUAS | 2022-04-18 11:29 | 2022-04-18 14:12 | 50 | 002:43 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | C22041800106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-04-18 | 8150 | keep | 0 | Apr | 2022 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-04-18 11:37 | 2022-04-18 13:58 | 100 | 002:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22041800071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2022-04-18 | 14100 | keep | 0 | Apr | 2022 | 0.0096034 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-18 11:37 | 2022-04-18 13:24 | 50 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041800093 | New_Event | Bad Weather | Include | Include | Weather | 107 | 2022-04-18 | 5350 | keep | 0 | Apr | 2022 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-18 11:47 | 2022-04-18 13:50 | 2 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO SE DEJO FUERA LA PANADERIA ESPAÃ‘A POR PROA | R22041800018 | New_Event | Wire Down | Include | Include | Equipment | 123 | 2022-04-18 | 246 | keep | 0 | Apr | 2022 | 0.00016755 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-04-18 11:57 | 2022-04-18 14:48 | 1 | 002:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REMPLAZO PORTAFUSIBLE AVERIADO | A22041800084 | New_Event | Cutout Failure | Include | Include | Equipment | 171 | 2022-04-18 | 171 | keep | 0 | Apr | 2022 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-18 12:09 | 2022-04-18 14:30 | 1 | 002:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN RISER Y 1 X 15 EN BANCO DE XMR'S CRUCE X AVE | C22041800114 | New_Event |  |  | Include | Wildlife | 141 | 2022-04-18 | 141 | keep | 0 | Apr | 2022 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-18 12:10 | 2022-04-18 13:06 | 15 | 000:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA POR CAMION | P22041800076 | New_Event |  |  | Include | Wildlife | 56 | 2022-04-18 | 840 | keep | 0 | Apr | 2022 | 0.00057212 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-18 12:14 | 2022-04-18 18:57 | 70 | 006:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INDICA REQUIERE DESGANCHE | M22041800122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 403 | 2022-04-18 | 28210 | keep | 0 | Apr | 2022 | 0.019214 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-04-18 12:20 | 2022-04-18 14:47 | 10 | 002:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA ROTA | M22041800129 | New_Event | Secondary Wire Down | Include | Include | Equipment | 147 | 2022-04-18 | 1470 | keep | 0 | Apr | 2022 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-04-18 12:22 | 2022-04-18 17:07 | 6 | 004:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO TOMA ZULFATADA | R22041800021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 285 | 2022-04-18 | 1710 | keep | 0 | Apr | 2022 | 0.0011647 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-04-18 12:29 | 2022-04-18 19:55 | 150 | 007:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE REEMPLAZO AISLADORES Y SE LEVANTO LINEA PRIMARIA | M22041800131 | New_Event | Wire Down | Include | Include | Equipment | 446 | 2022-04-18 | 66900 | keep | 0 | Apr | 2022 | 0.045565 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-04-18 12:29 | 2022-04-18 23:24 | 25 | 010:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22041800093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 655 | 2022-04-18 | 16375 | keep | 0 | Apr | 2022 | 0.011153 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-18 12:30 | 2022-04-18 15:03 | 200 | 002:33 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR RAMA | P22041800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-04-18 | 30600 | keep | 0 | Apr | 2022 | 0.020842 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-04-18 12:33 | 2022-04-18 16:15 | 80 | 003:42 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22041800134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2022-04-18 | 17760 | keep | 0 | Apr | 2022 | 0.012096 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-18 12:35 | 2022-04-18 13:02 | 1 | 000:27 | P | DESGANCHE | 1 X 40 EN RISER SE REALIZO DESGANCHE | B22041800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2022-04-18 | 27 | keep | 0 | Apr | 2022 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-18 12:51 | 2022-04-18 12:52 | 1671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 6404-01 | M22041800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-18 | 1671 | keep | 0 | Apr | 2022 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
BAYAMON | 2022-04-18 13:02 | 2022-04-18 13:58 | 35 | 000:56 | P | CABLE SOTERRADO AVERIADO | 1X 25 EN SU 2A AVERIA NUEVA DE T13 @ T12 Y AVERIA VIEJA DE T11@ T12 | B22041800098 | New_Event | UG Cable Fault | Include | Include | Equipment | 56 | 2022-04-18 | 1960 | keep | 0 | Apr | 2022 | 0.0013349 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-04-18 13:02 | 2022-04-19 09:31 | 9 | 020:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | P22041800084 | New_Event | Wire Down | Include | Include | Equipment | 1229 | 2022-04-18 | 11061 | keep | 0 | Apr | 2022 | 0.0075336 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2022-04-18 13:07 | 2022-04-18 13:08 | 3973 | 000:01 | T | DESGANCHE | RECIERRE AUN NO SE HAN DETERMINADO LAS CAUSAS | P22041800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-18 | 3973 | keep | 0 | Apr | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
AGUADILLA | 2022-04-18 13:08 | 2022-04-18 23:42 | 2 | 010:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA PARTIDA | M22041800161 | New_Event | Wire Down | Include | Include | Equipment | 634 | 2022-04-18 | 1268 | keep | 0 | Apr | 2022 | 0.00086363 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2022-04-18 13:09 | 2022-04-18 13:10 | 3973 | 000:01 | T | DESGANCHE | RECIERRE AUN NO SE HAN DETERMINADO LAS CAUSAS | P22041800087 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-18 | 3973 | keep | 0 | Apr | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-04-18 13:15 | 2022-04-18 17:13 | 3973 | 003:58 | T | DESGANCHE | DISPARO INTERRUPTOR SE RETIRO RAMAS Y REMPLAZO AISLADORES EN TRONCAL PRIMARIO Y SE COLOCO INTERRUPTOR EN SERVICIO | P22041800089 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 238 | 2022-04-18 | 945574 | keep | 0 | Apr | 2022 | 0.64403 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
ARECIBO | 2022-04-18 13:20 | 2022-04-18 13:21 | 63 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR PUENTE ABIERTO CARGA DEL 8002-03 | A22041800174 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-18 | 63 | keep | 0 | Apr | 2022 | 4.2909e-05 | 4.2909e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 63
CANOVANAS | 2022-04-18 13:34 | 2022-04-18 19:07 | 100 | 005:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22041800024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2022-04-18 | 33300 | keep | 0 | Apr | 2022 | 0.02268 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-18 13:36 | 2022-04-18 14:06 | 2 | 000:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22041800110 | New_Event | Bad Weather | Include | Include | Weather | 30 | 2022-04-18 | 60 | keep | 0 | Apr | 2022 | 4.0866e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-04-18 13:45 | 2022-04-18 13:46 | 4 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR LA CARGA DE 6007-05 | M22041800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-18 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-04-18 13:45 | 2022-04-18 13:46 | 4 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6007-04 | M22041800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-18 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-04-18 13:45 | 2022-04-18 16:10 | 705 | 002:25 | T | DESGANCHE | DISPARO DE BREAKER PORTATIL EN LA SUBESTACION SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041800113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-04-18 | 102225 | keep | 0 | Apr | 2022 | 0.069625 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2022-04-18 13:45 | 2022-04-18 16:10 | 1521 | 002:25 | T | DESGANCHE | DISPARO DE BREAKER PORTATIL EN LA SUBESTACION SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041800113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-04-18 | 220545 | keep | 0 | Apr | 2022 | 0.15021 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2022-04-18 13:45 | 2022-04-18 16:10 | 882 | 002:25 | T | DESGANCHE | DISPARO DE BREAKER PORTATIL EN LA SUBESTACION SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041800113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-04-18 | 127890 | keep | 0 | Apr | 2022 | 0.087105 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
MAYAGÃœEZ | 2022-04-18 13:46 | 2022-04-18 16:35 | 393 | 002:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS LLEVA LA CARGA POR 6007-05 | M22041800186 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 169 | 2022-04-18 | 66417 | keep | 0 | Apr | 2022 | 0.045236 | 0.00026767 | Sustained | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-04-18 13:46 | 2022-04-18 13:47 | 4 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS LLEVA LA CARGA DEL 6007-04 | M22041800186 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-04-18 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-04-18 13:49 | 2022-04-19 12:47 | 30 | 022:58 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22041800103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1378 | 2022-04-18 | 41340 | keep | 0 | Apr | 2022 | 0.028156 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-18 13:54 | 2022-04-19 05:40 | 50 | 015:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA INFORMA REQUIERE DESGANCHE | M22041800191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 946 | 2022-04-18 | 47300 | keep | 0 | Apr | 2022 | 0.032216 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-18 13:54 | 2022-04-18 14:11 | 1 | 000:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN BANCO TRANSFORMADORES SE RETIRO AVE | B22041800104 | New_Event |  |  | Include | Wildlife | 17 | 2022-04-18 | 17 | keep | 0 | Apr | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-18 13:58 | 2022-04-18 14:00 | 1983 | 000:02 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 1711-04 Y PARTE DE 1717-01 DISPARO INTERRUPTOR AL HACER PRUEBA EN C/L | B22041800106 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2022-04-18 | 3966 | keep | 0 | Apr | 2022 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-04-18 13:58 | 2022-04-18 14:00 | 1500 | 000:02 | P | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 1711-04 Y PARTE DE 1717-01 AL HACER PRUEBA EN C/L POR PARARRAYO DEFECTUOSO | B22041800106 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2022-04-18 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
BAYAMON | 2022-04-18 13:58 | 2022-04-18 14:00 | 186 | 000:02 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 1711-04 Y PARTE DE 1717-01 AL HACER PRUEBA DISPARO INTERRUPTOR | B22041800106 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2022-04-18 | 372 | keep | 0 | Apr | 2022 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
MAYAGÃœEZ | 2022-04-18 13:58 | 2022-04-18 19:09 | 100 | 005:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041800196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-04-18 | 31100 | keep | 0 | Apr | 2022 | 0.021182 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-18 14:00 | 2022-04-18 17:58 | 35 | 003:58 | P | CABLE SOTERRADO AVERIADO | 1X 25 EN SU 2A AVERIA NUEVA DE T13 @ T12 Y AVERIA VIEJA DE T11@ T12 | B22041800098 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 238 | 2022-04-18 | 8330 | keep | 0 | Apr | 2022 | 0.0056735 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-18 14:00 | 2022-04-18 14:53 | 8 | 000:53 | P | PARARRAYOS DEFECTUOSO | 3 X 100 EN C/L SE ELIMINO PARARRAYO AVERIADO EN BANCO DE TRANSFORMADORES Y SE DEJO FUERA OTRO TRANSCLOSURE PRIVADO POR PARARRAYO AVERIADO | B22041800043 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 53 | 2022-04-18 | 424 | keep | 0 | Apr | 2022 | 0.00028878 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-18 14:09 | 2022-04-18 14:10 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22041800030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-18 | 1026 | keep | 0 | Apr | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
MAYAGÃœEZ | 2022-04-18 14:09 | 2022-04-18 19:26 | 50 | 005:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041800205 | New_Event | Bad Weather | Include | Include | Weather | 317 | 2022-04-18 | 15850 | keep | 0 | Apr | 2022 | 0.010795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-18 14:12 | 2022-04-18 14:13 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 1565 | keep | 0 | Apr | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-04-18 14:12 | 2022-04-18 14:13 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 976 | keep | 0 | Apr | 2022 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-04-18 14:12 | 2022-04-18 14:13 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 548 | keep | 0 | Apr | 2022 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-04-18 14:12 | 2022-04-18 14:13 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 315 | keep | 0 | Apr | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-04-18 14:12 | 2022-04-18 14:13 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 870 | keep | 0 | Apr | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-04-18 14:12 | 2022-04-18 14:13 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 2906 | keep | 0 | Apr | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-04-18 14:12 | 2022-04-18 14:13 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 2343 | keep | 0 | Apr | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
CAGUAS | 2022-04-18 14:13 | 2022-04-18 17:23 | 50 | 003:10 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | C22041800106 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-04-18 | 9500 | keep | 0 | Apr | 2022 | 0.0064704 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-18 14:16 | 2022-04-18 14:17 | 1117 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 6404-01 | M22041800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-18 | 1117 | keep | 0 | Apr | 2022 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-04-18 14:31 | 2022-04-18 18:21 | 100 | 003:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22041800218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-04-18 | 23000 | keep | 0 | Apr | 2022 | 0.015665 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-18 14:32 | 2022-04-18 18:53 | 14 | 004:21 | P | DESGANCHE | 1 X 50 EN C/L | C22041800143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2022-04-18 | 3654 | keep | 0 | Apr | 2022 | 0.0024887 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2022-04-18 14:34 | 2022-04-18 17:49 | 60 | 003:15 | P | DESGANCHE | 1 X 100 EN C/L | C22041800145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-04-18 | 11700 | keep | 0 | Apr | 2022 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-18 14:41 | 2022-04-19 04:00 | 50 | 013:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE TRANSFORMADOR | S22041800003 | New_Event | Wire Down | Include | Include | Equipment | 799 | 2022-04-18 | 39950 | keep | 0 | Apr | 2022 | 0.02721 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-18 14:41 | 2022-04-19 02:07 | 100 | 011:26 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 50 EN CORTE DE LINEA | S22041800272 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 686 | 2022-04-18 | 68600 | keep | 0 | Apr | 2022 | 0.046723 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-18 14:47 | 2022-04-19 16:20 | 3 | 025:33 | P | DESGANCHE | 1 X 20 EN XMR Y DESGANCHE | S22041800274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1533 | 2022-04-18 | 4599 | keep | 0 | Apr | 2022 | 0.0031324 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-04-18 14:51 | 2022-04-18 18:28 | 14 | 003:37 | P | DESGANCHE | 1 X 40 EN C/L SE RETEZO LINEA Y DESGANCHE | B22041800064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-04-18 | 3038 | keep | 0 | Apr | 2022 | 0.0020692 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-04-18 14:55 | 2022-04-19 10:08 | 12 | 019:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | A22041800165 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1153 | 2022-04-18 | 13836 | keep | 0 | Apr | 2022 | 0.0094236 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-04-18 14:56 | 2022-04-18 15:54 | 100 | 000:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22041800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-04-18 | 5800 | keep | 0 | Apr | 2022 | 0.0039504 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-18 15:01 | 2022-04-18 20:11 | 80 | 005:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | M22041800230 | New_Event | Wire Down | Include | Include | Equipment | 310 | 2022-04-18 | 24800 | keep | 0 | Apr | 2022 | 0.016891 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-18 15:03 | 2022-04-18 17:58 | 15 | 002:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE RETEZO LINEA Y SE REALIZO DESGANCHE | B22041700065 | New_Event | Wire Down | Include | Include | Equipment | 175 | 2022-04-18 | 2625 | keep | 0 | Apr | 2022 | 0.0017879 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-04-18 15:06 | 2022-04-18 19:29 | 309 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | P22041800115 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2022-04-18 | 81267 | keep | 0 | Apr | 2022 | 0.055351 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
ARECIBO | 2022-04-18 15:11 | 2022-04-18 15:15 | 458 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | CARGA POR 8002-05 | A22041800173 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2022-04-18 | 1832 | keep | 0 | Apr | 2022 | 0.0012478 | 0.00031194 | Momentary | FALSE | FALSE | Not_TMED_Event | 458
ARECIBO | 2022-04-18 15:11 | 2022-04-18 15:15 | 1185 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR PUENTE ABIERTO LLEVA LA CARGA DEL 8002-04 | A22041800174 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2022-04-18 | 4740 | keep | 0 | Apr | 2022 | 0.0032284 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2022-04-18 15:11 | 2022-04-18 15:15 | 63 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA POR 8002-03 | A22041800174 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 4 | 2022-04-18 | 252 | keep | 0 | Apr | 2022 | 0.00017164 | 4.2909e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 63
ARECIBO | 2022-04-18 15:11 | 2022-04-18 15:15 | 232 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR MAL TIEMPO VIENTOS FUERTES LLEVA LA CARGA DEL 8002-01 | A22041800173 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2022-04-18 | 928 | keep | 0 | Apr | 2022 | 0.00063206 | 0.00015801 | Momentary | FALSE | FALSE | Not_TMED_Event | 232
ARECIBO | 2022-04-18 15:14 | 2022-04-18 15:15 | 1227 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR AISLADOR PARTIDO | A22041800178 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-18 | 1227 | keep | 0 | Apr | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
VEGA BAJA | 2022-04-18 15:15 | 2022-04-18 18:50 | 100 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | B22041800131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2022-04-18 | 21500 | keep | 0 | Apr | 2022 | 0.014644 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-18 15:16 | 2022-04-18 21:51 | 30 | 006:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22041800281 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 395 | 2022-04-18 | 11850 | keep | 0 | Apr | 2022 | 0.008071 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-18 15:34 | 2022-04-18 15:35 | 1227 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR AISLADOR PARTIDO | A22041800186 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-18 | 1227 | keep | 0 | Apr | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-04-18 15:42 | 2022-04-18 18:40 | 100 | 002:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A22041800188 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2022-04-18 | 17800 | keep | 0 | Apr | 2022 | 0.012123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-04-18 15:42 | 2022-04-18 17:16 | 100 | 001:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041800188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-04-18 | 9400 | keep | 0 | Apr | 2022 | 0.0064023 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-18 15:46 | 2022-04-18 18:06 | 65 | 002:20 | P | DESGANCHE | 1 X 100 EN C/L | C22041800178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-04-18 | 9100 | keep | 0 | Apr | 2022 | 0.006198 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-04-18 15:47 | 2022-04-18 16:55 | 80 | 001:08 | P | DESGANCHE | 1 X 80 EN C/L | C22041800179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-04-18 | 5440 | keep | 0 | Apr | 2022 | 0.0037052 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-18 15:54 | 2022-04-18 15:55 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1206-02 | S22041800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-18 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-04-18 15:54 | 2022-04-18 15:55 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1206-01 | S22041800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-18 | 733 | keep | 0 | Apr | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
ARECIBO | 2022-04-18 16:01 | 2022-04-18 20:11 | 50 | 004:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041800194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2022-04-18 | 12500 | keep | 0 | Apr | 2022 | 0.0085137 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-18 16:02 | 2022-04-18 20:44 | 70 | 004:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22041800043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-04-18 | 19740 | keep | 0 | Apr | 2022 | 0.013445 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-04-18 16:10 | 2022-04-18 18:50 | 20 | 002:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041800231 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-04-18 | 3200 | keep | 0 | Apr | 2022 | 0.0021795 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-18 16:12 | 2022-04-18 16:17 | 1185 | 000:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR PUENTE ABIERTO LLEVA LA CARGA DEL 8002-04 | A22041800198 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 5 | 2022-04-18 | 5925 | keep | 0 | Apr | 2022 | 0.0040355 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2022-04-18 16:12 | 2022-04-18 16:17 | 63 | 000:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA POR 8002-03 | A22041800198 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 5 | 2022-04-18 | 315 | keep | 0 | Apr | 2022 | 0.00021455 | 4.2909e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 63
ARECIBO | 2022-04-18 16:17 | 2022-04-18 21:31 | 395 | 005:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE ABRIO INTERRUPTOR PARA REPARAR | A22041800190 | Partial_restoration | Wire Down | Include | Include | Equipment | 314 | 2022-04-18 | 124030 | keep | 0 | Apr | 2022 | 0.084476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-18 16:31 | 2022-04-19 12:19 | 75 | 019:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S22041800296 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1188 | 2022-04-18 | 89100 | keep | 0 | Apr | 2022 | 0.060686 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-04-18 16:57 | 2022-04-18 19:05 | 163 | 002:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22041800146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2022-04-18 | 20864 | keep | 0 | Apr | 2022 | 0.01421 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
HUMACAO | 2022-04-18 17:03 | 2022-04-19 16:14 | 19 | 023:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESCRUZO Y REPARO LINEAS NO FUNDIO | C22041700337 | New_Event | Wire Down | Include | Include | Equipment | 1391 | 2022-04-18 | 26429 | keep | 0 | Apr | 2022 | 0.018001 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2022-04-18 17:03 | 2022-04-19 02:06 | 150 | 009:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA INDICO REQUIERE DESGANCHE | M22041800288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 543 | 2022-04-18 | 81450 | keep | 0 | Apr | 2022 | 0.055475 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-04-18 17:06 | 2022-04-19 07:28 | 23 | 014:22 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | C22041800212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 862 | 2022-04-18 | 19826 | keep | 0 | Apr | 2022 | 0.013503 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
UTUADO | 2022-04-18 17:12 | 2022-04-18 18:27 | 150 | 001:15 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041800209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-04-18 | 11250 | keep | 0 | Apr | 2022 | 0.0076623 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-04-18 17:18 | 2022-04-19 13:55 | 25 | 020:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S22041800302 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1237 | 2022-04-18 | 30925 | keep | 0 | Apr | 2022 | 0.021063 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-18 17:18 | 2022-04-18 20:01 | 80 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | M22041800296 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2022-04-18 | 13040 | keep | 0 | Apr | 2022 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-18 17:20 | 2022-04-19 05:49 | 100 | 012:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B22041800304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 749 | 2022-04-18 | 74900 | keep | 0 | Apr | 2022 | 0.051014 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-04-18 17:43 | 2022-04-19 07:10 | 19 | 013:27 | P | DESGANCHE | 1 X 50 EN C/L | C22041800226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 807 | 2022-04-18 | 15333 | keep | 0 | Apr | 2022 | 0.010443 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2022-04-18 17:57 | 2022-04-18 21:32 | 9 | 003:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA CRUCE CON AVE | R22041800052 | New_Event |  |  | Include | Wildlife | 215 | 2022-04-18 | 1935 | keep | 0 | Apr | 2022 | 0.0013179 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-04-18 18:13 | 2022-04-18 19:17 | 90 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041800314 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2022-04-18 | 5760 | keep | 0 | Apr | 2022 | 0.0039231 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2022-04-18 18:18 | 2022-04-20 06:00 | 1 | 035:42 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR (2) AVERIADO DE 25 KVA X 25 KVA | R22041800058 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2142 | 2022-04-18 | 2142 | keep | 0 | Apr | 2022 | 0.0014589 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-18 18:20 | 2022-04-18 19:53 | 1 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | S22041800325 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-04-18 | 93 | keep | 0 | Apr | 2022 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-04-18 18:36 | 2022-04-18 19:06 | 4 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22041800241 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-04-18 | 120 | keep | 0 | Apr | 2022 | 8.1731e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-04-18 18:49 | 2022-04-18 23:12 | 40 | 004:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO RIGIDO | R22041800063 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 263 | 2022-04-18 | 10520 | keep | 0 | Apr | 2022 | 0.0071651 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-04-18 18:53 | 2022-04-18 23:14 | 50 | 004:21 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE INSTALO POSTE PRIMARIO PARTIDO | P22041800169 | New_Event | Defective Pole | Include | Include | Equipment | 261 | 2022-04-18 | 13050 | keep | 0 | Apr | 2022 | 0.0088883 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-04-18 19:10 | 2022-04-19 11:44 | 25 | 016:34 | P | DESGANCHE | 1 X 25 EN C/L | R22041800067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 994 | 2022-04-18 | 24850 | keep | 0 | Apr | 2022 | 0.016925 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-04-18 19:13 | 2022-04-19 11:52 | 26 | 016:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L FUERTES VIENTOS | C22041800248 | New_Event | Bad Weather | Include | Include | Weather | 999 | 2022-04-18 | 25974 | keep | 0 | Apr | 2022 | 0.017691 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2022-04-18 19:15 | 2022-04-18 20:48 | 1 | 001:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L REEMPLAZO CAJA QUEMADA | C22041800249 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2022-04-18 | 93 | keep | 0 | Apr | 2022 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-18 19:31 | 2022-04-19 16:12 | 80 | 020:41 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B22041800168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1241 | 2022-04-18 | 99280 | keep | 0 | Apr | 2022 | 0.067619 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-04-18 19:34 | 2022-04-18 23:58 | 137 | 004:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22041800256 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2022-04-18 | 36168 | keep | 0 | Apr | 2022 | 0.024634 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
MAYAGÃœEZ | 2022-04-18 19:51 | 2022-04-19 09:57 | 200 | 014:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA Y 1 X 140 EN CONVERTIDOR MAL TIEMPO VIENTOS FUERTES | M22041800374 | New_Event | Bad Weather | Include | Include | Weather | 846 | 2022-04-18 | 169200 | keep | 0 | Apr | 2022 | 0.11524 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-04-18 19:55 | 2022-04-19 12:28 | 50 | 016:33 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22041800353 | New_Event | Vegetation Contact | Include | Include | Vegetation | 993 | 2022-04-18 | 49650 | keep | 0 | Apr | 2022 | 0.033816 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-18 20:08 | 2022-04-19 08:46 | 120 | 012:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22041800240 | New_Event | Bad Weather | Include | Include | Weather | 758 | 2022-04-18 | 90960 | keep | 0 | Apr | 2022 | 0.061952 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-04-18 20:15 | 2022-04-19 21:15 | 5 | 025:00 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | B22041800171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1500 | 2022-04-18 | 7500 | keep | 0 | Apr | 2022 | 0.0051082 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-04-18 20:17 | 2022-04-19 10:41 | 51 | 014:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P22041800186 | New_Event | Bad Weather | Include | Include | Weather | 864 | 2022-04-18 | 44064 | keep | 0 | Apr | 2022 | 0.030012 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
UTUADO | 2022-04-18 20:23 | 2022-04-19 08:50 | 2 | 012:27 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22041800255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 747 | 2022-04-18 | 1494 | keep | 0 | Apr | 2022 | 0.0010176 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-04-18 20:32 | 2022-04-19 13:24 | 50 | 016:52 | P | DESGANCHE | 1 X 40 C/L | C22041800274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1012 | 2022-04-18 | 50600 | keep | 0 | Apr | 2022 | 0.034463 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-04-18 21:00 | 2022-04-18 21:16 | 45 | 000:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22041800280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2022-04-18 | 720 | keep | 0 | Apr | 2022 | 0.00049039 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-04-18 21:31 | 2022-04-19 00:35 | 1185 | 003:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO EN TRONCAL DEL ALIMENTADOR SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 8002-04 | A22041800270 | Additional_clients | Wire Down | Include | Include | Equipment | 184 | 2022-04-18 | 218040 | keep | 0 | Apr | 2022 | 0.14851 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-18 21:31 | 2022-04-19 00:35 | 63 | 003:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA POR 8002-03 | A22041800270 | New_Event | Wire Down | Include | Include | Equipment | 184 | 2022-04-18 | 11592 | keep | 0 | Apr | 2022 | 0.0078953 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
CAGUAS | 2022-04-18 21:43 | 2022-04-18 21:45 | 1565 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | C22041800285 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-18 | 3130 | keep | 0 | Apr | 2022 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
ARECIBO | 2022-04-18 21:56 | 2022-04-19 00:20 | 1227 | 002:24 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES PARTIDOS SE CERRO INTERRUPTOR | A22041800274 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 144 | 2022-04-18 | 176688 | keep | 0 | Apr | 2022 | 0.12034 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
PONCE | 2022-04-18 22:09 | 2022-04-19 06:04 | 15 | 007:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | P22041800010 | New_Event | Wire Down | Include | Include | Equipment | 475 | 2022-04-18 | 7125 | keep | 0 | Apr | 2022 | 0.0048528 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-18 22:22 | 2022-04-18 22:24 | 1000 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1424-8 SE PROBO QUEDO EN SERVICIO | S22041800402 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-18 | 2000 | keep | 0 | Apr | 2022 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-04-18 22:22 | 2022-04-18 22:24 | 1000 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1424-8 SE PROBO QUEDO EN SERVICIO | S22041800402 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-18 | 2000 | keep | 0 | Apr | 2022 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-04-18 22:22 | 2022-04-18 22:24 | 278 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1424-8 SE PROBO QUEDO EN SERVICIO | S22041800402 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-18 | 556 | keep | 0 | Apr | 2022 | 0.00037869 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2022-04-18 22:22 | 2022-04-18 22:24 | 9 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1348-7 LLEVA 80% 1348-6 Y PARTE DEL 1336-8 SE PROBO QUEDO EN SERVICIO | S22041800402 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-18 | 18 | keep | 0 | Apr | 2022 | 1.226e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-04-18 22:22 | 2022-04-19 08:39 | 1 | 010:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN BANCO XMR CRUCE X AVE | C22041800289 | New_Event |  |  | Include | Wildlife | 617 | 2022-04-18 | 617 | keep | 0 | Apr | 2022 | 0.00042024 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-18 22:25 | 2022-04-18 22:26 | 1879 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2200 | A22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 1879 | keep | 0 | Apr | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
ARECIBO | 2022-04-18 22:25 | 2022-04-18 22:26 | 2777 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2200 | A22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 2777 | keep | 0 | Apr | 2022 | 0.0018914 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
ARECIBO | 2022-04-18 22:25 | 2022-04-18 22:26 | 2 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2200 | A22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 2 | keep | 0 | Apr | 2022 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-04-18 22:25 | 2022-04-18 22:26 | 2839 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2200 | A22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 2839 | keep | 0 | Apr | 2022 | 0.0019336 | 0.0019336 | Momentary | FALSE | FALSE | Not_TMED_Event | 2839
ARECIBO | 2022-04-18 22:25 | 2022-04-18 22:26 | 1160 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2200 | A22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 1160 | keep | 0 | Apr | 2022 | 0.00079007 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
ARECIBO | 2022-04-18 22:25 | 2022-04-18 22:26 | 1860 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2200 | A22041800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-18 | 1860 | keep | 0 | Apr | 2022 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
CANOVANAS | 2022-04-18 23:01 | 2022-04-19 10:02 | 4 | 011:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR Y REEMPLAZO BARRA EN PEDESTAL | R22041800083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 661 | 2022-04-18 | 2644 | keep | 0 | Apr | 2022 | 0.0018008 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-04-18 23:48 | 2022-04-19 10:45 | 300 | 010:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A22041800294 | New_Event | Wire Down | Include | Include | Equipment | 657 | 2022-04-18 | 197100 | keep | 0 | Apr | 2022 | 0.13424 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-04-19 01:43 | 2022-04-19 01:44 | 817 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22041900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 817 | keep | 0 | Apr | 2022 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
BAYAMON | 2022-04-19 03:34 | 2022-04-20 13:25 | 13 | 033:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA | B22041900001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2031 | 2022-04-19 | 26403 | keep | 0 | Apr | 2022 | 0.017983 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2022-04-19 05:36 | 2022-04-19 11:50 | 10 | 006:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041900039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2022-04-19 | 3740 | keep | 0 | Apr | 2022 | 0.0025473 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-04-19 05:37 | 2022-04-19 21:47 | 1 | 016:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22041900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 970 | 2022-04-19 | 970 | keep | 0 | Apr | 2022 | 0.00066066 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-19 05:37 | 2022-04-19 14:12 | 155 | 008:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22041900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 515 | 2022-04-19 | 79825 | keep | 0 | Apr | 2022 | 0.054368 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
BAYAMON | 2022-04-19 06:19 | 2022-04-19 11:55 | 5 | 005:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | B22041900002 | New_Event |  |  | Include | Wildlife | 336 | 2022-04-19 | 1680 | keep | 0 | Apr | 2022 | 0.0011442 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-04-19 06:33 | 2022-04-19 06:34 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 3973 | keep | 0 | Apr | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
CAGUAS | 2022-04-19 06:38 | 2022-04-19 06:39 | 3005 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 3005 | keep | 0 | Apr | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
ARECIBO | 2022-04-19 06:53 | 2022-04-19 12:15 | 5 | 005:22 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO | A22041900073 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 322 | 2022-04-19 | 1610 | keep | 0 | Apr | 2022 | 0.0010966 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-04-19 07:09 | 2022-04-19 12:15 | 8 | 005:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | P22041900009 | New_Event | Cutout Failure | Include | Include | Equipment | 306 | 2022-04-19 | 2448 | keep | 0 | Apr | 2022 | 0.0016673 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-04-19 07:20 | 2022-04-19 11:36 | 35 | 004:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22041900011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-04-19 | 8960 | keep | 0 | Apr | 2022 | 0.0061026 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-04-19 07:22 | 2022-04-19 16:31 | 10 | 009:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | R22041900003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 549 | 2022-04-19 | 5490 | keep | 0 | Apr | 2022 | 0.0037392 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-19 07:34 | 2022-04-19 07:35 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041900013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 2697 | keep | 0 | Apr | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
MAYAGÃœEZ | 2022-04-19 07:40 | 2022-04-19 11:35 | 15 | 003:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041900010 | New_Event | Bad Weather | Include | Include | Weather | 235 | 2022-04-19 | 3525 | keep | 0 | Apr | 2022 | 0.0024009 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-04-19 07:48 | 2022-04-19 14:59 | 150 | 007:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 Y 1 X 100 EN CORTES DE LINEAS DISTINTOS MAL TIEMPO DESCARGAS ELECTRICAS | A22041900016 | New_Event | Bad Weather | Include | Include | Weather | 431 | 2022-04-19 | 64650 | keep | 0 | Apr | 2022 | 0.044033 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-04-19 07:56 | 2022-04-19 09:05 | 3 | 001:09 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYOS | S22041900008 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 69 | 2022-04-19 | 207 | keep | 0 | Apr | 2022 | 0.00014099 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-04-19 07:59 | 2022-04-19 10:33 | 1 | 002:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22041900012 | New_Event | Bad Weather | Include | Include | Weather | 154 | 2022-04-19 | 154 | keep | 0 | Apr | 2022 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-19 08:05 | 2022-04-19 11:27 | 15 | 003:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P22041900018 | New_Event |  |  | Include | Wildlife | 202 | 2022-04-19 | 3030 | keep | 0 | Apr | 2022 | 0.0020637 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-04-19 08:12 | 2022-04-19 13:34 | 65 | 005:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22041900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2022-04-19 | 20930 | keep | 0 | Apr | 2022 | 0.014255 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-04-19 08:29 | 2022-04-19 09:41 | 1 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C22041900013 | New_Event |  |  | Include | Wildlife | 72 | 2022-04-19 | 72 | keep | 0 | Apr | 2022 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-19 08:34 | 2022-04-19 12:43 | 69 | 004:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22041900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-04-19 | 17181 | keep | 0 | Apr | 2022 | 0.011702 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2022-04-19 08:36 | 2022-04-20 12:57 | 5 | 028:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO VARIAS CONDICIONES EN LA LINEA. | S22041900010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1701 | 2022-04-19 | 8505 | keep | 0 | Apr | 2022 | 0.0057927 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-04-19 08:37 | 2022-04-19 11:51 | 1 | 003:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L SE REMPLAZO CAJA | S22041900011 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2022-04-19 | 194 | keep | 0 | Apr | 2022 | 0.00013213 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-04-19 08:37 | 2022-04-19 15:00 | 35 | 006:23 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | A22041900028 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 383 | 2022-04-19 | 13405 | keep | 0 | Apr | 2022 | 0.0091301 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-04-19 08:38 | 2022-04-19 14:46 | 8 | 006:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S22041900012 | New_Event | Wire Down | Include | Include | Equipment | 368 | 2022-04-19 | 2944 | keep | 0 | Apr | 2022 | 0.0020051 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-19 08:39 | 2022-04-19 11:23 | 1 | 002:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE CERRO PUENTE PRIMARIO LINEA A CAJA | S22041900013 | New_Event | Wire Down | Include | Include | Equipment | 164 | 2022-04-19 | 164 | keep | 0 | Apr | 2022 | 0.0001117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-19 08:43 | 2022-04-19 10:24 | 30 | 001:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22041900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-04-19 | 3030 | keep | 0 | Apr | 2022 | 0.0020637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-19 08:49 | 2022-04-19 14:47 | 12 | 005:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REMPLAZO AISLADORES Y SE REALIZO DESGANCHE | B22041900010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 358 | 2022-04-19 | 4296 | keep | 0 | Apr | 2022 | 0.002926 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-04-19 08:51 | 2022-04-19 15:56 | 1 | 007:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22041900031 | New_Event | Wire Down | Include | Include | Equipment | 425 | 2022-04-19 | 425 | keep | 0 | Apr | 2022 | 0.00028947 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-19 08:52 | 2022-04-19 08:53 | 5668 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 5668 | keep | 0 | Apr | 2022 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
BAYAMON | 2022-04-19 08:54 | 2022-04-19 14:30 | 1 | 005:36 | P | NO SE REPORTO CAUSA | 2 X 20 EN BANCO XMR Y 2 X 30 EN RISER | S22041900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 336 | 2022-04-19 | 336 | keep | 0 | Apr | 2022 | 0.00022885 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-04-19 08:57 | 2022-04-19 15:30 | 50 | 006:33 | P | ESTRUCTURA AVERIADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | A22041900034 | New_Event | Defective Pole | Include | Include | Equipment | 393 | 2022-04-19 | 19650 | keep | 0 | Apr | 2022 | 0.013384 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-19 09:05 | 2022-04-19 09:06 | 1483 | 000:01 | P | PARARRAYOS DEFECTUOSO | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA 30% DEL 1204-04 | S22041900000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-04-19 | 1483 | keep | 0 | Apr | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-04-19 09:05 | 2022-04-19 09:06 | 1000 | 000:01 | P | PARARRAYOS DEFECTUOSO | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA PARTE DEL 1204-05 | S22041900000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-04-19 | 1000 | keep | 0 | Apr | 2022 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-04-19 09:05 | 2022-04-19 09:06 | 5290 | 000:01 | T | PARARRAYOS DEFECTUOSO | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA 30% DEL 1204-04 Y PARTE DEL 1204-05 | S22041900000 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-04-19 | 5290 | keep | 0 | Apr | 2022 | 0.003603 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-19 09:06 | 2022-04-19 13:20 | 3 | 004:14 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYOS | S22041900008 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 254 | 2022-04-19 | 762 | keep | 0 | Apr | 2022 | 0.00051899 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-04-19 09:08 | 2022-04-19 13:39 | 100 | 004:31 | P | DESGANCHE | 1 X 100 EN C/L | S22041900019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-04-19 | 27100 | keep | 0 | Apr | 2022 | 0.018458 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-19 09:16 | 2022-04-20 15:49 | 12 | 030:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M22041900021 | New_Event | Wire Down | Include | Include | Equipment | 1833 | 2022-04-19 | 21996 | keep | 0 | Apr | 2022 | 0.014981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-04-19 09:16 | 2022-04-19 12:35 | 4 | 003:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22041900039 | New_Event | Bad Weather | Include | Include | Weather | 199 | 2022-04-19 | 796 | keep | 0 | Apr | 2022 | 0.00054215 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-04-19 09:30 | 2022-04-19 12:32 | 30 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P22041900035 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2022-04-19 | 5460 | keep | 0 | Apr | 2022 | 0.0037188 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-04-19 09:34 | 2022-04-19 13:30 | 1 | 003:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A22041900044 | New_Event | Cutout Failure | Include | Include | Equipment | 236 | 2022-04-19 | 236 | keep | 0 | Apr | 2022 | 0.00016074 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-19 09:47 | 2022-04-19 09:48 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22041900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 4035 | keep | 0 | Apr | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-04-19 09:49 | 2022-04-19 18:05 | 5 | 008:16 | P | ESTRUCTURA AVERIADA | POSTE PRIMARIO QUEMADO CON TRANSFORMADOR SE TRANSFIRIO CARGA A TRANSFORMADOR ALEDAÃ‘O | P22041900031 | New_Event | Defective Pole | Include | Include | Equipment | 496 | 2022-04-19 | 2480 | keep | 0 | Apr | 2022 | 0.0016891 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-04-19 09:53 | 2022-04-19 18:00 | 1 | 008:07 | P | DESGANCHE | SE DESGANCHO Y SE REPUSO 1X30 EN C/L | S22041900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2022-04-19 | 487 | keep | 0 | Apr | 2022 | 0.00033169 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-19 09:54 | 2022-04-19 13:20 | 20 | 003:26 | P | DESGANCHE | 2X 50 C/L | C22041900019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2022-04-19 | 4120 | keep | 0 | Apr | 2022 | 0.0028061 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-04-19 09:58 | 2022-04-19 13:19 | 1 | 003:21 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRE DE MH-4 A MH-6 PARA REEMPLAZAR TERMINACIONES EN EL MH-6 | P22041900034 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 201 | 2022-04-19 | 201 | keep | 0 | Apr | 2022 | 0.0001369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-19 10:03 | 2022-04-19 10:04 | 37 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L REEMPLAZO 2 CAJAS QUEMADAS DEJO FUERA EL RISER DE MARSHALL | C22041900002 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-04-19 | 37 | keep | 0 | Apr | 2022 | 2.5201e-05 | 2.5201e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2022-04-19 10:03 | 2022-04-19 10:40 | 10 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE | B22041800027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-04-19 | 370 | keep | 0 | Apr | 2022 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-19 10:05 | 2022-04-19 14:58 | 100 | 004:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 C/L MAL TIEMPO | C22041900024 | New_Event | Bad Weather | Include | Include | Weather | 293 | 2022-04-19 | 29300 | keep | 0 | Apr | 2022 | 0.019956 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-19 10:07 | 2022-04-19 20:20 | 30 | 010:13 | P | DESGANCHE | 1 X 40 EN RISER SE RETIRO RAMAS SOBRE LAS LINEAS | M22041900031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 613 | 2022-04-19 | 18390 | keep | 0 | Apr | 2022 | 0.012525 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-04-19 10:15 | 2022-04-19 11:30 | 50 | 001:15 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P22041900049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-04-19 | 3750 | keep | 0 | Apr | 2022 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-19 10:17 | 2022-04-19 12:15 | 100 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | P22041900050 | New_Event |  |  | Include | Wildlife | 118 | 2022-04-19 | 11800 | keep | 0 | Apr | 2022 | 0.0080369 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-19 10:22 | 2022-04-19 17:19 | 1 | 006:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO NIDO DE AVE | B22041900023 | New_Event |  |  | Include | Wildlife | 417 | 2022-04-19 | 417 | keep | 0 | Apr | 2022 | 0.00028402 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-04-19 10:24 | 2022-04-19 12:30 | 90 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22041900055 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2022-04-19 | 11340 | keep | 0 | Apr | 2022 | 0.0077236 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-04-19 10:27 | 2022-04-19 15:40 | 1 | 005:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR INDICO NO IDENTIFICO CAUSA | A22041900056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2022-04-19 | 313 | keep | 0 | Apr | 2022 | 0.00021318 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-19 10:32 | 2022-04-19 18:07 | 18 | 007:35 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO 25 KVA X 37.5 KVA | C22041900033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 455 | 2022-04-19 | 8190 | keep | 0 | Apr | 2022 | 0.0055782 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-04-19 10:34 | 2022-04-19 10:35 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 2608 | keep | 0 | Apr | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
BAYAMON | 2022-04-19 11:01 | 2022-04-19 15:34 | 249 | 004:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X65 EN C/L Y SE REMPLAZO AILADOR | B22041900030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 273 | 2022-04-19 | 67977 | keep | 0 | Apr | 2022 | 0.046299 | 0.00016959 | Sustained | FALSE | FALSE | Not_TMED_Event | 249
SAN JUAN | 2022-04-19 11:04 | 2022-04-19 11:05 | 1000 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1206-03 PARTE POR 1620-05 LLEVA PARTE DEL 1204-05 | S22041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 1000 | keep | 0 | Apr | 2022 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-04-19 11:04 | 2022-04-19 11:05 | 3800 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1206-03 PARTE POR 1620-05 LLEVA PARTE DEL 1204-05 | S22041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 3800 | keep | 0 | Apr | 2022 | 0.0025882 | 0.0025882 | Momentary | FALSE | FALSE | Not_TMED_Event | 3800
FAJARDO | 2022-04-19 11:10 | 2022-04-19 11:11 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 1234 | keep | 0 | Apr | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
MAYAGÃœEZ | 2022-04-19 11:18 | 2022-04-19 11:19 | 411 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041900040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 411 | keep | 0 | Apr | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
HUMACAO | 2022-04-19 11:20 | 2022-04-19 12:28 | 11 | 001:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO XMR Y REPARO SECUNDARIA AVERIADA POR PERSONAL PRIVADO | C22041900048 | New_Event |  |  | Include | Wildlife | 68 | 2022-04-19 | 748 | keep | 0 | Apr | 2022 | 0.00050946 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-04-19 11:23 | 2022-04-19 19:32 | 52 | 008:09 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN SU 1 AVERIA DE SU1 A SU2 SE QUEDO FUERA IGLESIA Y CENTRO COMUNAL | B22041900037 | New_Event | UG Cable Fault | Include | Include | Equipment | 489 | 2022-04-19 | 25428 | keep | 0 | Apr | 2022 | 0.017319 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 16:07 | 1339 | 004:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 273 | 2022-04-19 | 365547 | keep | 0 | Apr | 2022 | 0.24897 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 16:07 | 470 | 004:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 273 | 2022-04-19 | 128310 | keep | 0 | Apr | 2022 | 0.087391 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 16:07 | 2483 | 004:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 273 | 2022-04-19 | 677859 | keep | 0 | Apr | 2022 | 0.46169 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 16:07 | 2190 | 004:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 273 | 2022-04-19 | 597870 | keep | 0 | Apr | 2022 | 0.40721 | 0.0014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 16:07 | 3006 | 004:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 273 | 2022-04-19 | 820638 | keep | 0 | Apr | 2022 | 0.55893 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 16:07 | 179 | 004:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 273 | 2022-04-19 | 48867 | keep | 0 | Apr | 2022 | 0.033283 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 14:48 | 107 | 003:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2022-04-19 | 20758 | keep | 0 | Apr | 2022 | 0.014138 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 14:48 | 1666 | 003:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2022-04-19 | 323204 | keep | 0 | Apr | 2022 | 0.22013 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 14:48 | 4387 | 003:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2022-04-19 | 851078 | keep | 0 | Apr | 2022 | 0.57967 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 14:48 | 3147 | 003:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2022-04-19 | 610518 | keep | 0 | Apr | 2022 | 0.41582 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-04-19 11:34 | 2022-04-19 14:48 | 4304 | 003:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2022-04-19 | 834976 | keep | 0 | Apr | 2022 | 0.5687 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2022-04-19 11:35 | 2022-04-19 12:52 | 80 | 001:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041900017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-04-19 | 6160 | keep | 0 | Apr | 2022 | 0.0041955 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-19 11:42 | 2022-04-19 12:21 | 1 | 000:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | S22041900041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-04-19 | 39 | keep | 0 | Apr | 2022 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-04-19 11:49 | 2022-04-19 15:35 | 10 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA FUERTES VIENTOS | P22041900066 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2022-04-19 | 2260 | keep | 0 | Apr | 2022 | 0.0015393 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-19 11:52 | 2022-04-20 09:16 | 80 | 021:24 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | C22041900053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1284 | 2022-04-19 | 102720 | keep | 0 | Apr | 2022 | 0.069962 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-04-19 12:03 | 2022-04-19 12:04 | 1352 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | P22041900068 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-04-19 | 1352 | keep | 0 | Apr | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2022-04-19 12:07 | 2022-04-19 15:05 | 1352 | 002:58 | T | PARARRAYOS DEFECTUOSO | DISPARO INTERRUPTOR SE REMPLAZARON DOS PARARRAYOS EN MONTURA TRIFASICA | P22041900069 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 178 | 2022-04-19 | 240656 | keep | 0 | Apr | 2022 | 0.16391 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
HUMACAO | 2022-04-19 12:11 | 2022-04-19 16:47 | 20 | 004:36 | P | ESTRUCTURA AVERIADA | 1 X 40 C/L SE ELIMINO EL POSTE PARTIDO Y SE RELOCALIZO LINEA | C22041900057 | New_Event | Defective Pole | Include | Include | Equipment | 276 | 2022-04-19 | 5520 | keep | 0 | Apr | 2022 | 0.0037596 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-04-19 12:13 | 2022-04-19 21:00 | 8 | 008:47 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041900049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 527 | 2022-04-19 | 4216 | keep | 0 | Apr | 2022 | 0.0028715 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-19 12:15 | 2022-04-19 16:39 | 95 | 004:24 | P | DESGANCHE | 2 X 50 C/L | C22041900058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2022-04-19 | 25080 | keep | 0 | Apr | 2022 | 0.017082 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
MAYAGÃœEZ | 2022-04-19 12:18 | 2022-04-19 14:37 | 30 | 002:19 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22041900051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-04-19 | 4170 | keep | 0 | Apr | 2022 | 0.0028402 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-19 12:25 | 2022-04-19 14:45 | 80 | 002:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22041900059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-04-19 | 11200 | keep | 0 | Apr | 2022 | 0.0076283 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-19 12:27 | 2022-04-19 14:25 | 15 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AVE CRUZO BUSHING | A22041900078 | New_Event |  |  | Include | Wildlife | 118 | 2022-04-19 | 1770 | keep | 0 | Apr | 2022 | 0.0012055 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-04-19 12:28 | 2022-04-19 12:30 | 906 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22041900059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-19 | 1812 | keep | 0 | Apr | 2022 | 0.0012341 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
BAYAMON | 2022-04-19 12:31 | 2022-04-19 14:16 | 1 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE TRANSFORMADORES | B22041900046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-04-19 | 105 | keep | 0 | Apr | 2022 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-04-19 12:32 | 2022-04-19 12:33 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22041900019 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 1234 | keep | 0 | Apr | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
CAGUAS | 2022-04-19 12:34 | 2022-04-19 16:34 | 150 | 004:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 80 C/L CRUCE POR AVE | C22041900061 | New_Event |  |  | Include | Wildlife | 240 | 2022-04-19 | 36000 | keep | 0 | Apr | 2022 | 0.024519 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-04-19 12:35 | 2022-04-19 13:20 | 12 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22041900047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-04-19 | 540 | keep | 0 | Apr | 2022 | 0.00036779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-19 12:39 | 2022-04-19 12:40 | 1084 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 1084 | keep | 0 | Apr | 2022 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
ARECIBO | 2022-04-19 12:45 | 2022-04-19 13:14 | 20 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22041900002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2022-04-19 | 580 | keep | 0 | Apr | 2022 | 0.00039504 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-04-19 12:54 | 2022-04-19 12:55 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041900121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 863 | keep | 0 | Apr | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2022-04-19 13:00 | 2022-04-19 15:03 | 39 | 002:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | R22021900021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 123 | 2022-04-19 | 4797 | keep | 0 | Apr | 2022 | 0.0032672 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2022-04-19 13:07 | 2022-04-19 16:22 | 44 | 003:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22041900067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2022-04-19 | 8580 | keep | 0 | Apr | 2022 | 0.0058438 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BARRANQUITAS | 2022-04-19 13:08 | 2022-04-19 13:30 | 6 | 000:22 | P | HERRAJE ROTO O PODRIDO | ABRIO XMR PARA REEMPLAZO DE HOT CLAMP | C22041900072 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 22 | 2022-04-19 | 132 | keep | 0 | Apr | 2022 | 8.9905e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-19 13:12 | 2022-04-19 16:40 | 30 | 003:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRAR PUENTE ABIERTO Y REPARAR NEUTRAL | S22041900063 | New_Event | Wire Down | Include | Include | Equipment | 208 | 2022-04-19 | 6240 | keep | 0 | Apr | 2022 | 0.00425 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-19 13:12 | 2022-04-19 15:10 | 50 | 001:58 | P | DESGANCHE | 1X 65 EN C/L | S22041900069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-04-19 | 5900 | keep | 0 | Apr | 2022 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-19 13:22 | 2022-04-19 14:33 | 312 | 001:11 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO MANUALMENTE EN SUB | S22041900074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2022-04-19 | 22152 | keep | 0 | Apr | 2022 | 0.015088 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2022-04-19 13:24 | 2022-04-19 15:55 | 30 | 002:31 | P | DESGANCHE | SE REALIZO DESGANCHE 2 X 50 EN C/L Y SE RETEZO ALAMBRE | S22041900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-04-19 | 4530 | keep | 0 | Apr | 2022 | 0.0030854 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-19 13:29 | 2022-04-19 17:46 | 21 | 004:17 | P | DESGANCHE | 2 X 100 EN C/L Y SE RETIRO RAMA DE LINEA | B22041900059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-04-19 | 5397 | keep | 0 | Apr | 2022 | 0.0036759 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-04-19 13:31 | 2022-04-19 19:00 | 17 | 005:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22041900060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 329 | 2022-04-19 | 5593 | keep | 0 | Apr | 2022 | 0.0038094 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2022-04-19 13:32 | 2022-04-19 13:33 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22041900086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
PONCE | 2022-04-19 13:42 | 2022-04-19 14:14 | 2 | 000:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA DE MONTURA TRIFASICA | P22041900086 | New_Event | Wire Down | Include | Include | Equipment | 32 | 2022-04-19 | 64 | keep | 0 | Apr | 2022 | 4.359e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2022-04-19 13:43 | 2022-04-19 15:24 | 10 | 001:41 | P | DESGANCHE | 1 X 30 C/L | C22041900081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-04-19 | 1010 | keep | 0 | Apr | 2022 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-04-19 13:48 | 2022-04-19 16:18 | 55 | 002:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22041900083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2022-04-19 | 8250 | keep | 0 | Apr | 2022 | 0.005619 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2022-04-19 14:01 | 2022-04-19 14:02 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 222 | keep | 0 | Apr | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-04-19 14:01 | 2022-04-19 14:02 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 4456 | keep | 0 | Apr | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-04-19 14:01 | 2022-04-19 18:44 | 100 | 004:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22041900073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2022-04-19 | 28300 | keep | 0 | Apr | 2022 | 0.019275 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-19 14:12 | 2022-04-21 12:16 | 25 | 046:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMER 37.5KVA X 37.5KVA @ 13KV | B22041900108 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2764 | 2022-04-19 | 69100 | keep | 0 | Apr | 2022 | 0.047064 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-19 14:18 | 2022-04-20 03:30 | 30 | 013:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22041900275 | New_Event | Wire Down | Include | Include | Equipment | 792 | 2022-04-19 | 23760 | keep | 0 | Apr | 2022 | 0.016183 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-19 14:20 | 2022-04-19 19:01 | 30 | 004:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A22041900092 | New_Event | Wire Down | Include | Include | Equipment | 281 | 2022-04-19 | 8430 | keep | 0 | Apr | 2022 | 0.0057416 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-04-19 14:32 | 2022-04-19 17:44 | 1 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C22041900093 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2022-04-19 | 192 | keep | 0 | Apr | 2022 | 0.00013077 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-19 14:41 | 2022-04-19 14:42 | 2825 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22041900313 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 2825 | keep | 0 | Apr | 2022 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
MAYAGÃœEZ | 2022-04-19 14:45 | 2022-04-19 16:46 | 30 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M22041900319 | New_Event |  |  | Include | Wildlife | 121 | 2022-04-19 | 3630 | keep | 0 | Apr | 2022 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-04-19 14:57 | 2022-04-19 17:02 | 69 | 002:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22041900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-04-19 | 8625 | keep | 0 | Apr | 2022 | 0.0058744 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
MAYAGÃœEZ | 2022-04-19 15:09 | 2022-04-19 16:41 | 60 | 001:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22041900350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-04-19 | 5520 | keep | 0 | Apr | 2022 | 0.0037596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-19 15:12 | 2022-04-19 15:13 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22041900099 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
PONCE | 2022-04-19 15:13 | 2022-04-19 17:00 | 50 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA FUERTES VIENTOS | P22041900116 | New_Event | Bad Weather | Include | Include | Weather | 107 | 2022-04-19 | 5350 | keep | 0 | Apr | 2022 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-19 15:16 | 2022-04-19 15:17 | 513 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 20% DE SU CARGA POR 1118-10 | S22041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 513 | keep | 0 | Apr | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-04-19 15:16 | 2022-04-19 15:17 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 20% DEL 1111-1 | S22041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 2782 | keep | 0 | Apr | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CANOVANAS | 2022-04-19 15:16 | 2022-04-19 18:29 | 220 | 003:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R22041900027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-04-19 | 42460 | keep | 0 | Apr | 2022 | 0.028919 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
BAYAMON | 2022-04-19 15:21 | 2022-04-19 17:16 | 201 | 001:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | B22041900097 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2022-04-19 | 23115 | keep | 0 | Apr | 2022 | 0.015744 | 0.0001369 | Sustained | FALSE | FALSE | Not_TMED_Event | 201
MAYAGÃœEZ | 2022-04-19 15:29 | 2022-04-19 18:48 | 12 | 003:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M22041900371 | New_Event |  |  | Include | Wildlife | 199 | 2022-04-19 | 2388 | keep | 0 | Apr | 2022 | 0.0016265 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-19 15:30 | 2022-04-19 17:14 | 85 | 001:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B22041900101 | New_Event | Cutout Failure | Include | Include | Equipment | 104 | 2022-04-19 | 8840 | keep | 0 | Apr | 2022 | 0.0060209 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
MAYAGÃœEZ | 2022-04-19 15:40 | 2022-04-20 04:30 | 15 | 012:50 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22041900376 | New_Event | Vegetation Contact | Include | Include | Vegetation | 770 | 2022-04-19 | 11550 | keep | 0 | Apr | 2022 | 0.0078667 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-04-19 15:49 | 2022-04-19 17:12 | 133 | 001:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C22041900105 | New_Event | Cutout Failure | Include | Include | Equipment | 83 | 2022-04-19 | 11039 | keep | 0 | Apr | 2022 | 0.0075186 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
ARECIBO | 2022-04-19 15:49 | 2022-04-19 17:42 | 50 | 001:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A22041900102 | New_Event | Wire Down | Include | Include | Equipment | 113 | 2022-04-19 | 5650 | keep | 0 | Apr | 2022 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-04-19 15:56 | 2022-04-19 17:40 | 40 | 001:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041900104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-04-19 | 4160 | keep | 0 | Apr | 2022 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-04-19 16:01 | 2022-04-19 20:12 | 48 | 004:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L REEMPLAZO CAJA QUEMADA | C22041900106 | New_Event | Cutout Failure | Include | Include | Equipment | 251 | 2022-04-19 | 12048 | keep | 0 | Apr | 2022 | 0.0082058 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2022-04-19 16:18 | 2022-04-19 16:26 | 1 | 000:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN RISER AVE CRUZO LINEAS | B22041900124 | New_Event |  |  | Include | Wildlife | 8 | 2022-04-19 | 8 | keep | 0 | Apr | 2022 | 5.4488e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-19 16:28 | 2022-04-19 20:03 | 8 | 003:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE AVERIADO | A22041900109 | New_Event | Cutout Failure | Include | Include | Equipment | 215 | 2022-04-19 | 1720 | keep | 0 | Apr | 2022 | 0.0011715 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-04-19 16:35 | 2022-04-19 16:42 | 2 | 000:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO HOT CLAMP EN BAJANTE PRIMARIO DE RISER | P22041900042 | New_Event | Wire Down | Include | Include | Equipment | 7 | 2022-04-19 | 14 | keep | 0 | Apr | 2022 | 9.5353e-06 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-04-19 16:46 | 2022-04-21 18:04 | 13 | 049:18 | P | ESTRUCTURA AVERIADA | REEMPLAZO POSTE PARTIDO, INSTALO 2 POSTES | C22041900119 | New_Event | Defective Pole | Include | Include | Equipment | 2958 | 2022-04-19 | 38454 | keep | 0 | Apr | 2022 | 0.026191 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2022-04-19 17:12 | 2022-04-19 17:13 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 2725 | keep | 0 | Apr | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-04-19 17:12 | 2022-04-19 17:13 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 1834 | keep | 0 | Apr | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-04-19 17:12 | 2022-04-19 17:13 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 1437 | keep | 0 | Apr | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-04-19 17:12 | 2022-04-19 17:13 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 2565 | keep | 0 | Apr | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-04-19 17:12 | 2022-04-19 17:13 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22041900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 3565 | keep | 0 | Apr | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-04-19 17:12 | 2022-04-19 17:13 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22041900141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 2751 | keep | 0 | Apr | 2022 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-04-19 17:12 | 2022-04-19 17:13 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22041900141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 576 | keep | 0 | Apr | 2022 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-04-19 17:12 | 2022-04-19 17:13 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22041900141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 2584 | keep | 0 | Apr | 2022 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-04-19 17:12 | 2022-04-19 17:13 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22041900141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 1606 | keep | 0 | Apr | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-04-19 17:12 | 2022-04-19 17:13 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22041900141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 29 | keep | 0 | Apr | 2022 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2022-04-19 17:12 | 2022-04-19 17:13 | 4035 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22041900141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 4035 | keep | 0 | Apr | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-04-19 17:12 | 2022-04-19 17:13 | 3718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22041900141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-19 | 3718 | keep | 0 | Apr | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BARRANQUITAS | 2022-04-19 17:13 | 2022-04-20 08:58 | 133 | 015:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C22041900105 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 945 | 2022-04-19 | 125685 | keep | 0 | Apr | 2022 | 0.085603 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-19 17:25 | 2022-04-20 06:00 | 35 | 012:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22041900127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 755 | 2022-04-19 | 26425 | keep | 0 | Apr | 2022 | 0.017998 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-04-19 17:31 | 2022-04-20 20:18 | 7 | 026:47 | P | TRANSFORMADOR AVERIADO | 1 X 5 EN XMR REEMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | R22041900058 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1607 | 2022-04-19 | 11249 | keep | 0 | Apr | 2022 | 0.0076616 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-04-19 17:36 | 2022-04-19 21:21 | 80 | 003:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22041900421 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2022-04-19 | 18000 | keep | 0 | Apr | 2022 | 0.01226 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-04-19 17:41 | 2022-04-19 22:29 | 201 | 004:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO | B22041900158 | New_Event | Wire Down | Include | Include | Equipment | 288 | 2022-04-19 | 57888 | keep | 0 | Apr | 2022 | 0.039427 | 0.0001369 | Sustained | FALSE | FALSE | Not_TMED_Event | 201
BARRANQUITAS | 2022-04-19 17:51 | 2022-04-19 19:34 | 6 | 001:43 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C22041900132 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 103 | 2022-04-19 | 618 | keep | 0 | Apr | 2022 | 0.00042092 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-19 17:53 | 2022-04-19 21:52 | 80 | 003:59 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22041900425 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-04-19 | 19120 | keep | 0 | Apr | 2022 | 0.013023 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-04-19 17:55 | 2022-04-19 19:08 | 19 | 001:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | B22041900114 | New_Event | Secondary Wire Down | Include | Include | Equipment | 73 | 2022-04-19 | 1387 | keep | 0 | Apr | 2022 | 0.00094468 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2022-04-19 18:19 | 2022-04-19 18:20 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 2608 | keep | 0 | Apr | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2022-04-19 18:20 | 2022-04-19 20:35 | 35 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | C22041900138 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 135 | 2022-04-19 | 4725 | keep | 0 | Apr | 2022 | 0.0032182 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-04-19 18:29 | 2022-04-19 19:17 | 150 | 000:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR AVE | P22041900157 | New_Event |  |  | Include | Wildlife | 48 | 2022-04-19 | 7200 | keep | 0 | Apr | 2022 | 0.0049039 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-04-19 18:51 | 2022-04-19 20:56 | 100 | 002:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA Y PARARRAYO | R22041900068 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2022-04-19 | 12500 | keep | 0 | Apr | 2022 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-19 19:31 | 2022-04-19 21:57 | 200 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 65 EN CORTES DE LINEA | S22041900154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-04-19 | 29200 | keep | 0 | Apr | 2022 | 0.019888 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-04-19 19:32 | 2022-04-22 09:32 | 2 | 061:60 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU-1 AL SU-2 SE DEJO SECCIONALIZADO | B22041900037 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 3720 | 2022-04-19 | 7440 | keep | 0 | Apr | 2022 | 0.0050674 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-19 19:42 | 2022-04-20 13:05 | 15 | 017:23 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA POR DESGANCHE | P22041900165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1043 | 2022-04-19 | 15645 | keep | 0 | Apr | 2022 | 0.010656 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-19 19:54 | 2022-04-20 12:02 | 230 | 016:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO Y SE CERRO C/L | B22041900177 | New_Event | Wire Down | Include | Include | Equipment | 968 | 2022-04-19 | 222640 | keep | 0 | Apr | 2022 | 0.15164 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
AGUADILLA | 2022-04-19 19:55 | 2022-04-19 20:52 | 3 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22041900311 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-04-19 | 171 | keep | 0 | Apr | 2022 | 0.00011647 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-04-19 19:59 | 2022-04-19 23:09 | 30 | 003:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE CAJA DE CORTE DE LINEA | P22041900167 | New_Event | Wire Down | Include | Include | Equipment | 190 | 2022-04-19 | 5700 | keep | 0 | Apr | 2022 | 0.0038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-04-19 20:04 | 2022-04-20 08:50 | 46 | 012:46 | P | HERRAJE ROTO O PODRIDO | SE SECCIONALIZO AVERIA DE CRUZETA PARTIDA Y SE CERRO N/O CON 5401-02 | P22041900169 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 766 | 2022-04-19 | 35236 | keep | 0 | Apr | 2022 | 0.023999 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
MAYAGÃœEZ | 2022-04-19 20:54 | 2022-04-19 22:27 | 15 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR NO IDENTIFICO CAUSA | M22041900455 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-04-19 | 1395 | keep | 0 | Apr | 2022 | 0.00095013 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-04-19 21:01 | 2022-04-19 23:17 | 60 | 002:16 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22041900119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-04-19 | 8160 | keep | 0 | Apr | 2022 | 0.0055577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-19 22:01 | 2022-04-20 06:25 | 80 | 008:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES AVERIADO | M22041900462 | New_Event | Cutout Failure | Include | Include | Equipment | 504 | 2022-04-19 | 40320 | keep | 0 | Apr | 2022 | 0.027462 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-19 22:31 | 2022-04-20 12:37 | 114 | 014:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L PORTAFUSIBLES | S22041900172 | New_Event | Cutout Failure | Include | Include | Equipment | 846 | 2022-04-19 | 96444 | keep | 0 | Apr | 2022 | 0.065688 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
SAN JUAN | 2022-04-19 22:34 | 2022-04-20 13:36 | 49 | 015:02 | P | OTRAS CAUSAS | 1 X 100 RBA EN EN SU, 1X 65 PROVISIONAL Y PROBO MALO HACIA PISO 9 Y ADEMAS SE QUEDO FUERA PARA PERITO PISO 12 PROA | S22041900170 | New_Event | Other Causes | Include | Include | Other | 902 | 2022-04-19 | 44198 | keep | 0 | Apr | 2022 | 0.030103 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
CANOVANAS | 2022-04-19 23:51 | 2022-04-20 12:20 | 54 | 012:29 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL T - 30 @ T - 31, CERRO N/O EN T - 32 @ T - 31 | R22041900090 | New_Event | UG Cable Fault | Include | Include | Equipment | 749 | 2022-04-19 | 40446 | keep | 0 | Apr | 2022 | 0.027548 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
GUAYAMA | 2022-04-19 23:58 | 2022-04-19 23:59 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 4006-05 | P22042000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-04-19 23:58 | 2022-04-19 23:59 | 4279 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 4006-05 | P22042000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-04-19 23:58 | 2022-04-19 23:59 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 4003-01 Y N4003-02 | P22042000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-19 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
CAGUAS | 2022-04-20 00:58 | 2022-04-20 00:59 | 638 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22042000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 638 | keep | 0 | Apr | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2022-04-20 01:12 | 2022-04-20 01:13 | 2457 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22042000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 2457 | keep | 0 | Apr | 2022 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
VEGA BAJA | 2022-04-20 01:19 | 2022-04-20 03:55 | 10 | 002:36 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22042000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2022-04-20 | 1560 | keep | 0 | Apr | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-04-20 02:18 | 2022-04-20 08:50 | 50 | 006:32 | P | DESGANCHE | SE RETIRO BAMBUA Y 1 X 65 EN CORTE DE LINEA | P22042000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-04-20 | 19600 | keep | 0 | Apr | 2022 | 0.013349 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-20 02:25 | 2022-04-20 02:26 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 3458 | keep | 0 | Apr | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2022-04-20 02:37 | 2022-04-20 02:38 | 1017 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22042000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 1017 | keep | 0 | Apr | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
ARECIBO | 2022-04-20 03:07 | 2022-04-20 07:52 | 100 | 004:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22042000002 | New_Event | Bad Weather | Include | Include | Weather | 285 | 2022-04-20 | 28500 | keep | 0 | Apr | 2022 | 0.019411 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-20 03:25 | 2022-04-20 13:55 | 80 | 010:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22042000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 630 | 2022-04-20 | 50400 | keep | 0 | Apr | 2022 | 0.034327 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-20 03:28 | 2022-04-20 03:29 | 3295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | B22042000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 3295 | keep | 0 | Apr | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-04-20 03:38 | 2022-04-20 03:39 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22042000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 3941 | keep | 0 | Apr | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
PONCE | 2022-04-20 04:10 | 2022-04-20 14:45 | 70 | 010:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22042000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 635 | 2022-04-20 | 44450 | keep | 0 | Apr | 2022 | 0.030275 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2022-04-20 04:44 | 2022-04-20 04:45 | 1394 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22042000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 1394 | keep | 0 | Apr | 2022 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
ARECIBO | 2022-04-20 05:00 | 2022-04-20 11:17 | 25 | 006:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA | A22042000005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 377 | 2022-04-20 | 9425 | keep | 0 | Apr | 2022 | 0.0064193 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-04-20 05:13 | 2022-04-20 11:36 | 100 | 006:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22042000007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2022-04-20 | 38300 | keep | 0 | Apr | 2022 | 0.026086 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-04-20 05:38 | 2022-04-20 07:46 | 2484 | 002:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | ALIMENTADOR FUERA DE SERVICIO POR AISLADOR ROTO | P22042000004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 128 | 2022-04-20 | 317952 | keep | 0 | Apr | 2022 | 0.21656 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
PONCE | 2022-04-20 05:51 | 2022-04-20 05:52 | 2446 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 2446 | keep | 0 | Apr | 2022 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2022-04-20 05:51 | 2022-04-20 05:52 | 5069 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 5011-03 | P22042000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 5069 | keep | 0 | Apr | 2022 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
BAYAMON | 2022-04-20 05:58 | 2022-04-20 19:13 | 67 | 013:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8200 | S22042000217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 795 | 2022-04-20 | 53265 | keep | 0 | Apr | 2022 | 0.036279 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-04-20 05:58 | 2022-04-20 19:13 | 1587 | 013:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8200 | S22042000217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 795 | 2022-04-20 | 1261665 | keep | 0 | Apr | 2022 | 0.85931 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
BAYAMON | 2022-04-20 05:58 | 2022-04-20 19:13 | 521 | 013:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8200 | S22042000217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 795 | 2022-04-20 | 414195 | keep | 0 | Apr | 2022 | 0.28211 | 0.00035485 | Sustained | FALSE | FALSE | Not_TMED_Event | 521
BAYAMON | 2022-04-20 05:58 | 2022-04-20 19:13 | 1307 | 013:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8200 | S22042000217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 795 | 2022-04-20 | 1039065 | keep | 0 | Apr | 2022 | 0.7077 | 0.00089019 | Sustained | FALSE | FALSE | Not_TMED_Event | 1307
MAYAGÃœEZ | 2022-04-20 06:00 | 2022-04-20 06:01 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042000033 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 3458 | keep | 0 | Apr | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2022-04-20 06:03 | 2022-04-20 07:57 | 35 | 001:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22041900127 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-04-20 | 3990 | keep | 0 | Apr | 2022 | 0.0027176 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-20 06:06 | 2022-04-20 06:07 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042000036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 4304 | keep | 0 | Apr | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
ARECIBO | 2022-04-20 06:25 | 2022-04-20 09:48 | 50 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN RISER LLUVIA Y FUERTES VIENTOS | A22042000056 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2022-04-20 | 10150 | keep | 0 | Apr | 2022 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-04-20 06:26 | 2022-04-20 15:39 | 1 | 009:13 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR (2) AVERIADO DE 25 KVA X 25 KVA | R22041800058 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 553 | 2022-04-20 | 553 | keep | 0 | Apr | 2022 | 0.00037665 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-20 06:59 | 2022-04-20 07:00 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M2204200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 888 | keep | 0 | Apr | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-04-20 06:59 | 2022-04-20 07:00 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M2204200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 393 | keep | 0 | Apr | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-04-20 06:59 | 2022-04-20 07:00 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M2204200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-04-20 06:59 | 2022-04-20 07:00 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M2204200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 312 | keep | 0 | Apr | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-04-20 06:59 | 2022-04-20 07:00 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M2204200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 4641 | keep | 0 | Apr | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
CANOVANAS | 2022-04-20 07:03 | 2022-04-20 09:53 | 12 | 002:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | C22042000063 | New_Event |  |  | Include | Wildlife | 170 | 2022-04-20 | 2040 | keep | 0 | Apr | 2022 | 0.0013894 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-04-20 07:12 | 2022-04-20 09:24 | 50 | 002:12 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBU | A22042000036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-04-20 | 6600 | keep | 0 | Apr | 2022 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-20 07:14 | 2022-04-20 08:51 | 75 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22042000037 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2022-04-20 | 7275 | keep | 0 | Apr | 2022 | 0.004955 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-04-20 07:19 | 2022-04-20 08:22 | 170 | 001:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 100 EN CORTES DE LINEA CRUCE CON AVE | C22042000086 | New_Event |  |  | Include | Wildlife | 63 | 2022-04-20 | 10710 | keep | 0 | Apr | 2022 | 0.0072945 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
UTUADO | 2022-04-20 07:23 | 2022-04-20 09:30 | 25 | 002:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBU | A22042000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-04-20 | 3175 | keep | 0 | Apr | 2022 | 0.0021625 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-20 07:45 | 2022-04-20 15:50 | 80 | 008:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042000028 | New_Event | Bad Weather | Include | Include | Weather | 485 | 2022-04-20 | 38800 | keep | 0 | Apr | 2022 | 0.026427 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-04-20 07:46 | 2022-04-20 08:50 | 1919 | 001:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABREN MACHETES PARA SECCIONALIZAR AISLADOR ROTO | P22042000070 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 64 | 2022-04-20 | 122816 | keep | 0 | Apr | 2022 | 0.083649 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-20 08:05 | 2022-04-20 16:39 | 16 | 008:34 | P | DESGANCHE | 1 X 25 EN C/L | C22042000109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 514 | 2022-04-20 | 8224 | keep | 0 | Apr | 2022 | 0.0056013 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-04-20 08:11 | 2022-04-20 09:19 | 3458 | 001:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ROTA SE SECCIONALIZO PARA CERRAR EL INTERRUPTOR | M22042000041 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-04-20 | 235144 | keep | 0 | Apr | 2022 | 0.16016 | 0.0023552 | Sustained | FALSE | FALSE | Not_TMED_Event | 3458
SAN JUAN | 2022-04-20 08:22 | 2022-04-20 16:15 | 5 | 007:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO AISLADOR Y DISCOS | S22042000122 | New_Event | Wire Down | Include | Include | Equipment | 473 | 2022-04-20 | 2365 | keep | 0 | Apr | 2022 | 0.0016108 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-04-20 08:22 | 2022-04-20 08:23 | 2302 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22042000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 2302 | keep | 0 | Apr | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
SAN JUAN | 2022-04-20 08:24 | 2022-04-20 12:46 | 17 | 004:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | R22042000112 | New_Event |  |  | Include | Wildlife | 262 | 2022-04-20 | 4454 | keep | 0 | Apr | 2022 | 0.0030336 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-04-20 08:43 | 2022-04-20 17:22 | 10 | 008:39 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S22042000130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 519 | 2022-04-20 | 5190 | keep | 0 | Apr | 2022 | 0.0035349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-04-20 08:48 | 2022-04-20 10:42 | 9 | 001:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON BAJANTES DE TRANSFORMADOR Y LINEA PRINCIPAL SECUNDARIA | C22042000151 | New_Event | Secondary Wire Down | Include | Include | Equipment | 114 | 2022-04-20 | 1026 | keep | 0 | Apr | 2022 | 0.0006988 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-04-20 08:50 | 2022-04-20 14:35 | 40 | 005:45 | P | DESGANCHE | 1 X 65 EN C/L | R22042000115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2022-04-20 | 13800 | keep | 0 | Apr | 2022 | 0.0093991 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-04-20 08:50 | 2022-04-21 14:37 | 3 | 029:47 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA Y SE NORMALIZARON LAS CARGAS GOI PC-220420-01A | P22042100085 | Partial_restoration | Broken / Rusty Hardware | Include | Include | Equipment | 1787 | 2022-04-20 | 5361 | keep | 0 | Apr | 2022 | 0.0036514 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-04-20 08:50 | 2022-04-20 10:10 | 83 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE LLUVIA | P22042000133 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2022-04-20 | 6640 | keep | 0 | Apr | 2022 | 0.0045225 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
BARRANQUITAS | 2022-04-20 08:51 | 2022-04-20 14:44 | 20 | 005:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS QUEMADAS | C22042000154 | New_Event | Cutout Failure | Include | Include | Equipment | 353 | 2022-04-20 | 7060 | keep | 0 | Apr | 2022 | 0.0048085 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-20 08:54 | 2022-04-20 12:48 | 25 | 003:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO NEUTRAL PARTIDO | A22042000053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 234 | 2022-04-20 | 5850 | keep | 0 | Apr | 2022 | 0.0039844 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-04-20 09:00 | 2022-04-20 16:55 | 50 | 007:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL Y REALIZAR DESGANCHE | M22042000011 | New_Event | Wire Down | Include | Include | Equipment | 475 | 2022-04-20 | 23750 | keep | 0 | Apr | 2022 | 0.016176 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-20 09:03 | 2022-04-20 11:20 | 145 | 002:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10O EN C/L AVE CRUZO LINEAS | B22042000070 | New_Event |  |  | Include | Wildlife | 137 | 2022-04-20 | 19865 | keep | 0 | Apr | 2022 | 0.01353 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
AGUADILLA | 2022-04-20 09:03 | 2022-04-20 09:04 | 3315 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042000065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 3315 | keep | 0 | Apr | 2022 | 0.0022578 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
MAYAGÃœEZ | 2022-04-20 09:19 | 2022-04-20 13:52 | 50 | 004:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA SE CERRO MACHETES | M22042000077 | Partial_restoration | Wire Down | Include | Include | Equipment | 273 | 2022-04-20 | 13650 | keep | 0 | Apr | 2022 | 0.009297 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-04-20 09:30 | 2022-04-20 17:28 | 250 | 007:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 80 EN CORTE DE LINEA SE REMPLAZARON CAJAS PRIMARIAS AVERIADAS Y SE REALIZO DESGANCHE | A22042000057 | New_Event | Cutout Failure | Include | Include | Equipment | 478 | 2022-04-20 | 119500 | keep | 0 | Apr | 2022 | 0.081391 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-04-20 09:35 | 2022-04-20 14:53 | 3 | 005:18 | P | ESTRUCTURA AVERIADA | SE REPARO POSTE Y 3 TOMAS | S22042000143 | New_Event | Defective Pole | Include | Include | Equipment | 318 | 2022-04-20 | 954 | keep | 0 | Apr | 2022 | 0.00064977 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-04-20 09:44 | 2022-04-20 12:24 | 109 | 002:40 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE ARBOL | P22042000123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-04-20 | 17440 | keep | 0 | Apr | 2022 | 0.011878 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
CANOVANAS | 2022-04-20 09:57 | 2022-04-20 12:30 | 12 | 002:33 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 75 KVA X 75 KVA | R22042000125 | New_Event | Service Transformer Failure | Include | Include | Equipment | 153 | 2022-04-20 | 1836 | keep | 0 | Apr | 2022 | 0.0012505 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-04-20 10:08 | 2022-04-20 22:49 | 85 | 012:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22042000084 | New_Event | Bad Weather | Include | Include | Weather | 761 | 2022-04-20 | 64685 | keep | 0 | Apr | 2022 | 0.044057 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2022-04-20 10:11 | 2022-04-20 14:36 | 6 | 004:25 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REPARO SECUNDARIA Y SE DESGANCHO | S22041000028 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 265 | 2022-04-20 | 1590 | keep | 0 | Apr | 2022 | 0.0010829 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-04-20 10:14 | 2022-04-20 10:15 | 329 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA 90% DE LA CARGA DEL 3015-06 | C22042000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 329 | keep | 0 | Apr | 2022 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2022-04-20 10:14 | 2022-04-20 10:15 | 1207 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 90% DE LA CARGA POR EL 3006-01 | C22042000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 1207 | keep | 0 | Apr | 2022 | 0.00082208 | 0.00082208 | Momentary | FALSE | FALSE | Not_TMED_Event | 1207
ARECIBO | 2022-04-20 10:25 | 2022-04-20 11:29 | 15 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A22041900124 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2022-04-20 | 960 | keep | 0 | Apr | 2022 | 0.00065385 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-04-20 10:28 | 2022-04-20 17:57 | 10 | 007:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO TRAMO DE 75' DETERIORADO | C22042000175 | New_Event | Secondary Wire Down | Include | Include | Equipment | 449 | 2022-04-20 | 4490 | keep | 0 | Apr | 2022 | 0.0030581 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-20 10:33 | 2022-04-20 12:27 | 9 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22042000176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-04-20 | 1026 | keep | 0 | Apr | 2022 | 0.0006988 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-04-20 10:33 | 2022-04-20 14:05 | 8 | 003:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | P22042000142 | New_Event | Secondary Wire Down | Include | Include | Equipment | 212 | 2022-04-20 | 1696 | keep | 0 | Apr | 2022 | 0.0011551 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-04-20 10:46 | 2022-04-20 15:01 | 6 | 004:15 | P | NO SE REPORTO CAUSA | SE ENCONTRO CAJA EN TRANSFORMADOR ABIERTA | P22042000146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 255 | 2022-04-20 | 1530 | keep | 0 | Apr | 2022 | 0.0010421 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-04-20 10:49 | 2022-04-20 16:30 | 40 | 005:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR AVE | P22042000179 | New_Event |  |  | Include | Wildlife | 341 | 2022-04-20 | 13640 | keep | 0 | Apr | 2022 | 0.0092901 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-20 11:03 | 2022-04-20 17:00 | 6 | 005:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR EN SU # 01 PARA RELOCALIZAR LINEA SECUNDARIA | M22042000098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 357 | 2022-04-20 | 2142 | keep | 0 | Apr | 2022 | 0.0014589 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-20 11:10 | 2022-04-20 17:00 | 12 | 005:50 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE XMR AVERIADO DE 25 KVA X 25 KVA | M22042000106 | New_Event | Service Transformer Failure | Include | Include | Equipment | 350 | 2022-04-20 | 4200 | keep | 0 | Apr | 2022 | 0.0028606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-04-20 11:12 | 2022-04-20 11:23 | 4 | 000:11 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA | C22042000189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 11 | 2022-04-20 | 44 | keep | 0 | Apr | 2022 | 2.9968e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-04-20 11:16 | 2022-04-20 15:40 | 40 | 004:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22042000191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2022-04-20 | 10560 | keep | 0 | Apr | 2022 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-04-20 11:20 | 2022-04-20 14:15 | 6 | 002:55 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5 X 37.5 KVA | M22042000061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 175 | 2022-04-20 | 1050 | keep | 0 | Apr | 2022 | 0.00071515 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-20 11:21 | 2022-04-20 14:31 | 22 | 003:10 | P | DESGANCHE | DESGANCHO Y CERRO PUENTE NO FUNDIO | R22042000133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-04-20 | 4180 | keep | 0 | Apr | 2022 | 0.002847 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
HUMACAO | 2022-04-20 11:30 | 2022-04-20 11:34 | 3701 | 000:04 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE VERIFICO PERSONAL FUERA | C22042000000 | New_Event |  |  | Include | Wildlife | 4 | 2022-04-20 | 14804 | keep | 0 | Apr | 2022 | 0.010083 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-04-20 11:34 | 2022-04-20 14:03 | 300 | 002:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CRUCE CON AVE | C22042000195 | 1st_after_momentary |  |  | Include | Wildlife | 149 | 2022-04-20 | 44700 | keep | 0 | Apr | 2022 | 0.030445 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2022-04-20 11:34 | 2022-04-20 14:03 | 300 | 002:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA | C22042000195 | New_Event |  |  | Include | Wildlife | 149 | 2022-04-20 | 44700 | keep | 0 | Apr | 2022 | 0.030445 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2022-04-20 11:57 | 2022-04-20 12:05 | 1 | 000:08 | P | NO SE REPORTO CAUSA | 2 X 15 EN BANCO XMR | B22042000107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-04-20 | 8 | keep | 0 | Apr | 2022 | 5.4488e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-20 12:01 | 2022-04-20 12:16 | 1 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | B22042000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-04-20 | 15 | keep | 0 | Apr | 2022 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-20 12:03 | 2022-04-20 14:40 | 17 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S22042000182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-04-20 | 2669 | keep | 0 | Apr | 2022 | 0.0018178 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2022-04-20 12:15 | 2022-04-20 18:29 | 40 | 006:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22042000066 | New_Event | Bad Weather | Include | Include | Weather | 374 | 2022-04-20 | 14960 | keep | 0 | Apr | 2022 | 0.010189 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-20 12:26 | 2022-04-20 14:37 | 80 | 002:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22042000216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-04-20 | 10480 | keep | 0 | Apr | 2022 | 0.0071379 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-20 12:29 | 2022-04-21 01:22 | 25 | 012:53 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22042000113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 773 | 2022-04-20 | 19325 | keep | 0 | Apr | 2022 | 0.013162 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-04-20 12:45 | 2022-04-21 07:05 | 5 | 018:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA VEHICULO IMPACTO POSTE Y CAUSO QUE FUNDIERA FUSIBLE | A22042000072 | New_Event |  |  | Include | Wildlife | 1100 | 2022-04-20 | 5500 | keep | 0 | Apr | 2022 | 0.003746 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-04-20 12:47 | 2022-04-20 21:00 | 6 | 008:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | M22042000110 | New_Event | Secondary Wire Down | Include | Include | Equipment | 493 | 2022-04-20 | 2958 | keep | 0 | Apr | 2022 | 0.0020147 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-20 13:03 | 2022-04-20 15:09 | 10 | 002:06 | P | NO SE REPORTO CAUSA | SE RESETEO TRANSFORMADOR AUTO PROTEGIDO | B22041900100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-04-20 | 1260 | keep | 0 | Apr | 2022 | 0.00085818 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-20 13:04 | 2022-04-20 17:55 | 200 | 004:51 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22042000225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2022-04-20 | 58200 | keep | 0 | Apr | 2022 | 0.03964 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-04-20 13:05 | 2022-04-20 16:35 | 50 | 003:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L CAJA PRIMARIA | S22042000193 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2022-04-20 | 10500 | keep | 0 | Apr | 2022 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-04-20 13:05 | 2022-04-20 19:23 | 40 | 006:18 | P | ESTRUCTURA AVERIADA | ABRIR C/L PARA RELOCALIZAR POSTE Y XMR POR DERRUMBE | R22042000126 | New_Event | Defective Pole | Include | Include | Equipment | 378 | 2022-04-20 | 15120 | keep | 0 | Apr | 2022 | 0.010298 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-20 13:06 | 2022-04-20 15:15 | 6 | 002:09 | P | OTRAS CAUSAS | SE ABRIO XMR Y SE SUBIO XMR PARA MEJORAR EL CLEARANCE | S22042000193 | New_Event | Other Causes | Include | Include | Other | 129 | 2022-04-20 | 774 | keep | 0 | Apr | 2022 | 0.00052717 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-20 13:07 | 2022-04-20 15:30 | 350 | 002:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ROTA TRONCAL | M22042000112 | New_Event | Wire Down | Include | Include | Equipment | 143 | 2022-04-20 | 50050 | keep | 0 | Apr | 2022 | 0.034089 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
PONCE | 2022-04-20 13:13 | 2022-04-20 18:13 | 12 | 005:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA A 4.16 KV AVERIADO | P22042000163 | New_Event | Service Transformer Failure | Include | Include | Equipment | 300 | 2022-04-20 | 3600 | keep | 0 | Apr | 2022 | 0.0024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-20 13:27 | 2022-04-20 14:44 | 200 | 001:17 | P | DESGANCHE | 1 X 100 Y 1 X 50 EN CORTES DE LINEA | C22042000239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-04-20 | 15400 | keep | 0 | Apr | 2022 | 0.010489 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2022-04-20 13:27 | 2022-04-20 17:55 | 3 | 004:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22042000164 | New_Event |  |  | Include | Wildlife | 268 | 2022-04-20 | 804 | keep | 0 | Apr | 2022 | 0.0005476 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-04-20 13:38 | 2022-04-20 16:40 | 55 | 003:02 | P | DESGANCHE | 1 X 65 EN C/L | R22042000154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-04-20 | 10010 | keep | 0 | Apr | 2022 | 0.0068178 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
YAUCO | 2022-04-20 13:39 | 2022-04-20 18:02 | 15 | 004:23 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR RAMA | P22042000173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2022-04-20 | 3945 | keep | 0 | Apr | 2022 | 0.0026869 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-04-20 13:42 | 2022-04-20 15:50 | 1 | 002:08 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN RISER MAL TIEMPO VIENTOS FUERTES | A22042000077 | New_Event | Bad Weather | Include | Include | Weather | 128 | 2022-04-20 | 128 | keep | 0 | Apr | 2022 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-20 13:47 | 2022-04-20 13:48 | 33 | 000:01 | T | ERROR HUMANO | DISPARO DE BKR AL PERSONAL EN SUBESTACION TRATAR DE PONER RR EN OFF DEL 1802-01 | B22042000127 | New_Event | Human Error | Include | Include | Other | 1 | 2022-04-20 | 33 | keep | 0 | Apr | 2022 | 2.2476e-05 | 2.2476e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2022-04-20 13:51 | 2022-04-21 01:15 | 60 | 011:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M22042000121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 684 | 2022-04-20 | 41040 | keep | 0 | Apr | 2022 | 0.027952 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-20 13:51 | 2022-04-20 18:59 | 73 | 005:08 | P | PARARRAYOS DEFECTUOSO | 1 X 40 Y 1 X 30 EN CORTES DE LINEAS SE REMPLAZO PARARRAYOS | B22042000130 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 308 | 2022-04-20 | 22484 | keep | 0 | Apr | 2022 | 0.015314 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
FAJARDO | 2022-04-20 13:56 | 2022-04-20 16:40 | 1 | 002:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN C/L REEMPLAZO CAJA QUEMADA | R22042000158 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2022-04-20 | 164 | keep | 0 | Apr | 2022 | 0.0001117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-20 14:11 | 2022-04-21 16:44 | 1 | 026:33 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22042000131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1593 | 2022-04-20 | 1593 | keep | 0 | Apr | 2022 | 0.001085 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-20 14:15 | 2022-04-20 15:00 | 10 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO Y CONECTORES | M22042000102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-04-20 | 450 | keep | 0 | Apr | 2022 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-20 14:27 | 2022-04-21 13:07 | 5 | 022:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO QUEMADO | B22042000138 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1360 | 2022-04-20 | 6800 | keep | 0 | Apr | 2022 | 0.0046314 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-04-20 15:16 | 2022-04-20 15:18 | 1827 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2800 | M22042000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-20 | 3654 | keep | 0 | Apr | 2022 | 0.0024887 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-04-20 15:16 | 2022-04-20 15:18 | 1047 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2800 | M22042000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-20 | 2094 | keep | 0 | Apr | 2022 | 0.0014262 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2022-04-20 15:16 | 2022-04-20 15:18 | 4882 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2800 | M22042000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-20 | 9764 | keep | 0 | Apr | 2022 | 0.0066502 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
MAYAGÃœEZ | 2022-04-20 15:30 | 2022-04-20 17:22 | 974 | 001:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR LINEA PRIMARIA A LA SALIDA DEL ALIMENTADOR | M22042000112 | Additional_clients | Wire Down | Include | Include | Equipment | 112 | 2022-04-20 | 109088 | keep | 0 | Apr | 2022 | 0.074299 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-20 15:33 | 2022-04-20 19:10 | 80 | 003:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22042000147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-04-20 | 17360 | keep | 0 | Apr | 2022 | 0.011824 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-20 15:39 | 2022-04-20 15:59 | 1 | 000:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22042000095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-04-20 | 20 | keep | 0 | Apr | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-20 15:43 | 2022-04-20 15:44 | 810 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22042000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 810 | keep | 0 | Apr | 2022 | 0.00055169 | 0.00055169 | Momentary | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2022-04-20 15:43 | 2022-04-20 15:44 | 1235 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22042000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 1235 | keep | 0 | Apr | 2022 | 0.00084115 | 0.00084115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2022-04-20 15:43 | 2022-04-20 15:44 | 93 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22042000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 93 | keep | 0 | Apr | 2022 | 6.3342e-05 | 6.3342e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2022-04-20 15:43 | 2022-04-20 15:44 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22042000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 1825 | keep | 0 | Apr | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2022-04-20 15:43 | 2022-04-20 15:44 | 3230 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22042000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 3230 | keep | 0 | Apr | 2022 | 0.0021999 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
FAJARDO | 2022-04-20 15:51 | 2022-04-20 17:36 | 17 | 001:45 | P | NO SE REPORTO CAUSA | 1 NX 50A EN EL T - 17 | R22042000167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-04-20 | 1785 | keep | 0 | Apr | 2022 | 0.0012158 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-04-20 15:56 | 2022-04-20 15:57 | 60 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22042000109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 60 | keep | 0 | Apr | 2022 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-20 16:02 | 2022-04-20 16:20 | 16 | 000:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | B22042000159 | New_Event | Secondary Wire Down | Include | Include | Equipment | 18 | 2022-04-20 | 288 | keep | 0 | Apr | 2022 | 0.00019616 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2022-04-20 16:06 | 2022-04-20 16:11 | 1827 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2800 | M22042000000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-04-20 | 9135 | keep | 0 | Apr | 2022 | 0.0062218 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-04-20 16:06 | 2022-04-20 16:11 | 1047 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2800 | M22042000000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-04-20 | 5235 | keep | 0 | Apr | 2022 | 0.0035655 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2022-04-20 16:06 | 2022-04-20 16:11 | 4882 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2800 | M22042000000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-04-20 | 24410 | keep | 0 | Apr | 2022 | 0.016626 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
CAGUAS | 2022-04-20 16:19 | 2022-04-21 09:36 | 32 | 017:17 | P | DESGANCHE | 1 X 25 EN C/ L DESGANCHO Y REEMPLAZO DE CAJA | C22042000301 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1037 | 2022-04-20 | 33184 | keep | 0 | Apr | 2022 | 0.022601 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2022-04-20 16:40 | 2022-04-20 17:20 | 14 | 000:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO XMR Y SE REMPLAZO AISLADOR | S22042000222 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 40 | 2022-04-20 | 560 | keep | 0 | Apr | 2022 | 0.00038141 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-04-20 16:40 | 2022-04-20 23:24 | 1 | 006:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A22042000103 | New_Event | Bad Weather | Include | Include | Weather | 404 | 2022-04-20 | 404 | keep | 0 | Apr | 2022 | 0.00027516 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-20 16:51 | 2022-04-20 17:58 | 2 | 001:07 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22042000202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-04-20 | 134 | keep | 0 | Apr | 2022 | 9.1267e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-04-20 17:04 | 2022-04-20 22:20 | 15 | 005:16 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE RETIRO ARBOL SOBRE SECUNDARIA | A22042000105 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 316 | 2022-04-20 | 4740 | keep | 0 | Apr | 2022 | 0.0032284 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-04-20 17:13 | 2022-04-20 17:50 | 934 | 000:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22042000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 37 | 2022-04-20 | 34558 | keep | 0 | Apr | 2022 | 0.023537 | 0.00063614 | Sustained | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-04-20 17:13 | 2022-04-20 17:50 | 4 | 000:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22042000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 37 | 2022-04-20 | 148 | keep | 0 | Apr | 2022 | 0.0001008 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-04-20 17:13 | 2022-04-20 17:50 | 1479 | 000:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22042000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 37 | 2022-04-20 | 54723 | keep | 0 | Apr | 2022 | 0.037272 | 0.0010073 | Sustained | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-04-20 17:13 | 2022-04-20 17:50 | 1841 | 000:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22042000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 37 | 2022-04-20 | 68117 | keep | 0 | Apr | 2022 | 0.046394 | 0.0012539 | Sustained | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-04-20 17:13 | 2022-04-20 17:50 | 1950 | 000:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22042000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 37 | 2022-04-20 | 72150 | keep | 0 | Apr | 2022 | 0.049141 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
BAYAMON | 2022-04-20 17:21 | 2022-04-20 18:14 | 1 | 000:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN C/L CRUCE POR AVE | B22042000176 | New_Event |  |  | Include | Wildlife | 53 | 2022-04-20 | 53 | keep | 0 | Apr | 2022 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-20 17:32 | 2022-04-20 18:56 | 33 | 001:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22042000311 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-04-20 | 2772 | keep | 0 | Apr | 2022 | 0.001888 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2022-04-20 17:47 | 2022-04-21 02:09 | 40 | 008:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR ARBOL SOBRE LINEA | M22042000184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 502 | 2022-04-20 | 20080 | keep | 0 | Apr | 2022 | 0.013676 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-20 17:55 | 2022-04-20 19:28 | 40 | 001:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042000187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-04-20 | 3720 | keep | 0 | Apr | 2022 | 0.0025337 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-20 18:00 | 2022-04-20 18:45 | 1 | 000:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22042000190 | New_Event | Bad Weather | Include | Include | Weather | 45 | 2022-04-20 | 45 | keep | 0 | Apr | 2022 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-04-20 18:12 | 2022-04-20 21:12 | 46 | 003:00 | P | DESGANCHE | 1 X 65 EN C/L | R22042000174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-04-20 | 8280 | keep | 0 | Apr | 2022 | 0.0056395 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
FAJARDO | 2022-04-20 18:13 | 2022-04-20 20:28 | 1 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L Y 1 X 30 EN EQUIPO DE MEDICION MAL TIEMPO | R22042000175 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2022-04-20 | 135 | keep | 0 | Apr | 2022 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-20 18:47 | 2022-04-20 21:32 | 204 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22042000187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-04-20 | 33660 | keep | 0 | Apr | 2022 | 0.022926 | 0.00013894 | Sustained | FALSE | FALSE | Not_TMED_Event | 204
SAN JUAN | 2022-04-20 18:59 | 2022-04-20 21:10 | 9 | 002:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22042000236 | New_Event | Secondary Wire Down | Include | Include | Equipment | 131 | 2022-04-20 | 1179 | keep | 0 | Apr | 2022 | 0.00080301 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-04-20 19:01 | 2022-04-20 19:02 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22042000189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 4176 | keep | 0 | Apr | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-04-20 19:44 | 2022-04-20 22:23 | 20 | 002:39 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | B22042000195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-04-20 | 3180 | keep | 0 | Apr | 2022 | 0.0021659 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-04-20 20:01 | 2022-04-20 20:02 | 1070 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042000198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 1070 | keep | 0 | Apr | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
CANOVANAS | 2022-04-20 20:10 | 2022-04-20 22:18 | 188 | 002:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE DE RAMAS | R22042000180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-04-20 | 24064 | keep | 0 | Apr | 2022 | 0.01639 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
PONCE | 2022-04-20 20:28 | 2022-04-20 22:54 | 25 | 002:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22042000210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2022-04-20 | 3650 | keep | 0 | Apr | 2022 | 0.002486 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-04-20 20:28 | 2022-04-21 11:58 | 70 | 015:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE RETEZO LINEA PRIMARIA | A22042000151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 930 | 2022-04-20 | 65100 | keep | 0 | Apr | 2022 | 0.044339 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-04-20 20:49 | 2022-04-20 22:55 | 17 | 002:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER HACIA SU-1 SE REEMPLAZO PORTAFUSIBLE | R22042000183 | New_Event | Cutout Failure | Include | Include | Equipment | 126 | 2022-04-20 | 2142 | keep | 0 | Apr | 2022 | 0.0014589 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2022-04-20 20:56 | 2022-04-20 20:57 | 1057 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M22042000196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 1057 | keep | 0 | Apr | 2022 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | Not_TMED_Event | 1057
AGUADILLA | 2022-04-20 21:01 | 2022-04-20 21:02 | 1057 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M22042000196 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 1057 | keep | 0 | Apr | 2022 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | Not_TMED_Event | 1057
AGUADILLA | 2022-04-20 21:01 | 2022-04-20 21:02 | 1827 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2800 | M22042000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 1827 | keep | 0 | Apr | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-04-20 21:01 | 2022-04-20 21:02 | 1047 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2800 | M22042000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 1047 | keep | 0 | Apr | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2022-04-20 21:01 | 2022-04-20 21:02 | 4882 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2800 | M22042000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-20 | 4882 | keep | 0 | Apr | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
YAUCO | 2022-04-20 21:02 | 2022-04-21 14:19 | 50 | 017:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO BAJANTE PRIMARIO A CAJA DE CORTE DE LINEA AVERIADO | P22042000215 | New_Event | Wire Down | Include | Include | Equipment | 1037 | 2022-04-20 | 51850 | keep | 0 | Apr | 2022 | 0.035315 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-04-20 21:07 | 2022-04-20 21:08 | 1057 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M22042000198 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 1057 | keep | 0 | Apr | 2022 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | Not_TMED_Event | 1057
AGUADILLA | 2022-04-20 21:07 | 2022-04-20 21:22 | 1827 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2800 AL OPERAR INTERRUPTOR 7011-1 Y 7003-05 AJUSTES EL 2820 ERAN MAS ALTOS QUE LOS ALIMENTADORES RELES TRABAJO CON LOS 2820 | M21042000203 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-04-20 | 27405 | keep | 0 | Apr | 2022 | 0.018665 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-04-20 21:07 | 2022-04-20 21:22 | 1047 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2800 AL OPERAR INTERRUPTOR 7011-1 Y 7003-05 AJUSTES EL 2820 ERAN MAS ALTOS QUE LOS ALIMENTADORES RELES TRABAJO CON LOS DE 2820 | M21042000203 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-04-20 | 15705 | keep | 0 | Apr | 2022 | 0.010697 | 0.00071311 | Sustained | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2022-04-20 21:07 | 2022-04-20 21:22 | 4882 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2800 AL OPERAR INTERRUPTOR 7011-1 Y 7003-05 AJUSTES EL 2820 ERAN MAS ALTOS QUE LOS ALIMENTADORES RELES TRABJO CON ELLOS | M21042000203 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-04-20 | 73230 | keep | 0 | Apr | 2022 | 0.049877 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
BAYAMON | 2022-04-20 21:21 | 2022-04-21 12:10 | 100 | 014:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO EN TRONCAL DEL 4KV MEDIANTE G.O.I. BY-220421-01 | B22042000205 | New_Event | Wire Down | Include | Include | Equipment | 889 | 2022-04-20 | 88900 | keep | 0 | Apr | 2022 | 0.060549 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-04-20 21:22 | 2022-04-20 22:34 | 1827 | 001:12 | T | LINEA DE TRANSMISION 38KV | SE RETIRO PROTECCION 2820 QUE OPERA COMO MOD INFORMA GILBERTO RIVERA SE DEJO EN SERVICIO | M22042000203 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-04-20 | 131544 | keep | 0 | Apr | 2022 | 0.089594 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-04-20 22:25 | 2022-04-20 22:26 | 4098 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISAPRO DE BARRA DE 38 KV DE DAGUAO TC | R22042000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-04-20 | 4098 | keep | 0 | Apr | 2022 | 0.0027911 | 0.0027911 | Momentary | FALSE | FALSE | Not_TMED_Event | 4098
FAJARDO | 2022-04-20 22:25 | 2022-04-20 22:26 | 956 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISAPRO DE BARRA DE 38 KV DE DAGUAO TC | R22042000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-04-20 | 956 | keep | 0 | Apr | 2022 | 0.00065113 | 0.00065113 | Momentary | FALSE | FALSE | Not_TMED_Event | 956
PONCE | 2022-04-20 22:53 | 2022-04-20 22:54 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042000231 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 2113 | keep | 0 | Apr | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2022-04-20 23:06 | 2022-04-20 23:07 | 1979 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042000234 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 1979 | keep | 0 | Apr | 2022 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
BARRANQUITAS | 2022-04-20 23:21 | 2022-04-20 23:22 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22042000333 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-20 | 2635 | keep | 0 | Apr | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
VEGA BAJA | 2022-04-20 23:28 | 2022-04-21 13:29 | 12 | 014:01 | P | NO SE REPORTO CAUSA | 1X15 EN XMER | B22042000208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 841 | 2022-04-20 | 10092 | keep | 0 | Apr | 2022 | 0.0068736 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-04-20 23:45 | 2022-04-21 04:16 | 1835 | 004:31 | S | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE 38 KV 65E VERY SLOW | C22042000342 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2022-04-20 | 497285 | keep | 0 | Apr | 2022 | 0.3387 | 0.0012498 | Sustained | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2022-04-20 23:45 | 2022-04-21 04:16 | 71 | 004:31 | S | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE 38 KV 65E VERY SLOW | C22042000342 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2022-04-20 | 19241 | keep | 0 | Apr | 2022 | 0.013105 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
MAYAGÃœEZ | 2022-04-20 23:53 | 2022-04-21 02:50 | 2 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042000239 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2022-04-20 | 354 | keep | 0 | Apr | 2022 | 0.00024111 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-04-20 23:55 | 2022-04-21 02:55 | 418 | 003:00 | P | LINEA DE TRANSMISION 38KV | DISPARO INTERRUPTOR OVERHEAD DE LINEA 38KV SOBRE EL ALIMENTADOR 2402-02 SOLO TIENE EL 10% DE SU CARGA SE SECCIONALIZO CON SJ-220420-50 | R22042000193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-04-20 | 75240 | keep | 0 | Apr | 2022 | 0.051246 | 0.0002847 | Sustained | FALSE | FALSE | Not_TMED_Event | 418
CANOVANAS | 2022-04-20 23:55 | 2022-04-21 02:55 | 2078 | 003:00 | P | LINEA DE TRANSMISION 38KV | DISPARO INTERRUPTOR CARGA POR EL 2402-02 OVERHEAD DE LINEA 38KV SOBRE EL ALIMENTADOR 2402-02 SE SECCIONALIZO CON SJ-220420-50 | R22042000193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-04-20 | 374040 | keep | 0 | Apr | 2022 | 0.25476 | 0.0014153 | Sustained | FALSE | FALSE | Not_TMED_Event | 2078
CANOVANAS | 2022-04-20 23:55 | 2022-04-21 02:55 | 2675 | 003:00 | T | LINEA DE TRANSMISION 38KV | DISPARO INTERRUPTOR CARGA POR EL 2402-02 OVERHEAD DE LINEA 38KV SOBRE EL ALIMENTADOR 2402-02 SE SECCIONALIZO CON SJ-220420-50 | R22042000193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-04-20 | 481500 | keep | 0 | Apr | 2022 | 0.32795 | 0.0018219 | Sustained | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2022-04-21 01:03 | 2022-04-21 01:04 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22042100084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 2039 | keep | 0 | Apr | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
BAYAMON | 2022-04-21 02:22 | 2022-04-21 11:45 | 60 | 009:23 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22042100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 563 | 2022-04-21 | 33780 | keep | 0 | Apr | 2022 | 0.023007 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-04-21 02:55 | 2022-04-21 07:20 | 12 | 004:25 | P | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD DE LINEA 38 KV QUE CAYO SOBRE ALIMENTADOR | R22042000193 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 265 | 2022-04-21 | 3180 | keep | 0 | Apr | 2022 | 0.0021659 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-21 02:56 | 2022-04-21 09:08 | 100 | 006:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L REEMPLAZO CAJA QUEMADA | C22042100005 | New_Event | Cutout Failure | Include | Include | Equipment | 372 | 2022-04-21 | 37200 | keep | 0 | Apr | 2022 | 0.025337 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-04-21 02:57 | 2022-04-21 02:58 | 3003 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22042100110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 3003 | keep | 0 | Apr | 2022 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
VEGA BAJA | 2022-04-21 03:07 | 2022-04-21 03:08 | 31 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | B22042100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 31 | keep | 0 | Apr | 2022 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
HUMACAO | 2022-04-21 04:30 | 2022-04-21 09:30 | 125 | 005:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN C/L REPARO CONDUCTOR | C22042100007 | New_Event | Wire Down | Include | Include | Equipment | 300 | 2022-04-21 | 37500 | keep | 0 | Apr | 2022 | 0.025541 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-04-21 04:52 | 2022-04-21 18:11 | 200 | 013:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERO PUENTE | M22042100003 | New_Event | Wire Down | Include | Include | Equipment | 799 | 2022-04-21 | 159800 | keep | 0 | Apr | 2022 | 0.10884 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-04-21 05:04 | 2022-04-21 06:58 | 2580 | 001:54 | S | LINEA DE TRANSMISION 38KV | CCE RETIRO CARGA DE SUBESTACION PARA RETIRAR CONDUCTOR LINEA 11100 | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2022-04-21 | 294120 | keep | 0 | Apr | 2022 | 0.20032 | 0.0017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2022-04-21 05:04 | 2022-04-21 06:58 | 500 | 001:54 | S | LINEA DE TRANSMISION 38KV | CCE RETIRO CARGA DE SUBESTACION PARA RETIRAR CONDUCTOR LINEA 11100 | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2022-04-21 | 57000 | keep | 0 | Apr | 2022 | 0.038822 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
FAJARDO | 2022-04-21 05:32 | 2022-04-21 05:36 | 1902 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO TC | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-21 | 7608 | keep | 0 | Apr | 2022 | 0.0051818 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2022-04-21 05:32 | 2022-04-21 05:36 | 970 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO TC | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-21 | 3880 | keep | 0 | Apr | 2022 | 0.0026427 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2022-04-21 05:32 | 2022-04-21 05:36 | 3003 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO TC | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-21 | 12012 | keep | 0 | Apr | 2022 | 0.0081813 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2022-04-21 05:32 | 2022-04-21 05:36 | 2343 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO TC | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-21 | 9372 | keep | 0 | Apr | 2022 | 0.0063832 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2022-04-21 05:32 | 2022-04-21 05:36 | 1830 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO TC | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-21 | 7320 | keep | 0 | Apr | 2022 | 0.0049856 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2022-04-21 05:32 | 2022-04-21 05:36 | 710 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO TC | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-21 | 2840 | keep | 0 | Apr | 2022 | 0.0019343 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2022-04-21 05:32 | 2022-04-21 05:36 | 1197 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO TC | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-04-21 | 4788 | keep | 0 | Apr | 2022 | 0.0032611 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
CANOVANAS | 2022-04-21 05:32 | 2022-04-21 05:37 | 3012 | 000:05 | T | LINEA DE TRANSMISION 38KV | DISPARO INTERRUPTOR AL MISMO TIEMPO QUE LA LINEA 3100 DE PALMER TC A FAJARDO TC | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-04-21 | 15060 | keep | 0 | Apr | 2022 | 0.010257 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
BARRANQUITAS | 2022-04-21 06:01 | 2022-04-21 07:50 | 2635 | 001:49 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO EL ALIMENTADOR | C22042100014 | New_Event | Wire Down | Include | Include | Equipment | 109 | 2022-04-21 | 287215 | keep | 0 | Apr | 2022 | 0.19562 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
BAYAMON | 2022-04-21 06:08 | 2022-04-21 17:38 | 10 | 011:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L SE RETIRO IGUANA CRUZANDO LINEAS | B22042100010 | New_Event |  |  | Include | Wildlife | 690 | 2022-04-21 | 6900 | keep | 0 | Apr | 2022 | 0.0046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-04-21 06:49 | 2022-04-21 06:51 | 1380 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO CAUSA | R22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-21 | 2760 | keep | 0 | Apr | 2022 | 0.0018798 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
CAGUAS | 2022-04-21 06:55 | 2022-04-21 11:22 | 4 | 004:27 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REPARAR PEDESTAL | C22042100028 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 267 | 2022-04-21 | 1068 | keep | 0 | Apr | 2022 | 0.00072741 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-04-21 07:05 | 2022-04-21 08:02 | 10 | 000:57 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P22042100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-04-21 | 570 | keep | 0 | Apr | 2022 | 0.00038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-04-21 07:18 | 2022-04-21 10:45 | 100 | 003:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22042100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-04-21 | 20700 | keep | 0 | Apr | 2022 | 0.014099 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-21 07:19 | 2022-04-21 07:20 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22042100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 1227 | keep | 0 | Apr | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
SAN JUAN | 2022-04-21 07:20 | 2022-04-21 07:23 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22042100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-21 | 516 | keep | 0 | Apr | 2022 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
ARECIBO | 2022-04-21 07:20 | 2022-04-21 09:22 | 60 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22042100005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-04-21 | 7320 | keep | 0 | Apr | 2022 | 0.0049856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-21 07:29 | 2022-04-21 11:20 | 1 | 003:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M22042100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2022-04-21 | 231 | keep | 0 | Apr | 2022 | 0.00015733 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-21 07:47 | 2022-04-21 13:22 | 25 | 005:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X30 EN C/L & SE INSTALO AISLADOR EN LA FASE DEL MEDIO | B22042100032 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 335 | 2022-04-21 | 8375 | keep | 0 | Apr | 2022 | 0.0057042 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-04-21 07:50 | 2022-04-21 08:42 | 2371 | 000:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO EL ALIMENTADOR | C22042100043 | Partial_restoration | Wire Down | Include | Include | Equipment | 52 | 2022-04-21 | 123292 | keep | 0 | Apr | 2022 | 0.083974 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-21 07:52 | 2022-04-21 10:51 | 2 | 002:59 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | B22042100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2022-04-21 | 358 | keep | 0 | Apr | 2022 | 0.00024383 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-04-21 07:57 | 2022-04-21 12:08 | 94 | 004:11 | P | DESGANCHE | 1 X 15 Y 1X 25 EN CORTES DE LINEA SE REALIZO DESGANCHE | R22042100150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-04-21 | 23594 | keep | 0 | Apr | 2022 | 0.01607 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
SAN JUAN | 2022-04-21 07:58 | 2022-04-21 11:04 | 30 | 003:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR AVE | S22042100006 | New_Event |  |  | Include | Wildlife | 186 | 2022-04-21 | 5580 | keep | 0 | Apr | 2022 | 0.0038005 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 1093 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1093 | keep | 0 | Apr | 2022 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 1067 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1067 | keep | 0 | Apr | 2022 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 836 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 836 | keep | 0 | Apr | 2022 | 0.0005694 | 0.0005694 | Momentary | FALSE | FALSE | Not_TMED_Event | 836
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1339 | keep | 0 | Apr | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 1295 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1295 | keep | 0 | Apr | 2022 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 978 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 978 | keep | 0 | Apr | 2022 | 0.00066611 | 0.00066611 | Momentary | FALSE | FALSE | Not_TMED_Event | 978
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 1730 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1730 | keep | 0 | Apr | 2022 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 891 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 891 | keep | 0 | Apr | 2022 | 0.00060686 | 0.00060686 | Momentary | FALSE | FALSE | Not_TMED_Event | 891
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 527 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 527 | keep | 0 | Apr | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2022-04-21 08:07 | 2022-04-21 08:08 | 542 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22042100035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 542 | keep | 0 | Apr | 2022 | 0.00036915 | 0.00036915 | Momentary | FALSE | FALSE | Not_TMED_Event | 542
PONCE | 2022-04-21 08:11 | 2022-04-21 09:05 | 1093 | 000:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100040 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-04-21 | 59022 | keep | 0 | Apr | 2022 | 0.0402 | 0.00074444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1093
PONCE | 2022-04-21 08:11 | 2022-04-21 09:05 | 1067 | 000:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100040 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-04-21 | 57618 | keep | 0 | Apr | 2022 | 0.039243 | 0.00072673 | Sustained | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2022-04-21 08:11 | 2022-04-21 09:05 | 836 | 000:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100040 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-04-21 | 45144 | keep | 0 | Apr | 2022 | 0.030747 | 0.0005694 | Sustained | FALSE | FALSE | Not_TMED_Event | 836
PONCE | 2022-04-21 08:11 | 2022-04-21 09:05 | 1339 | 000:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100040 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-04-21 | 72306 | keep | 0 | Apr | 2022 | 0.049247 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
PONCE | 2022-04-21 08:11 | 2022-04-21 09:05 | 1295 | 000:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100040 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-04-21 | 69930 | keep | 0 | Apr | 2022 | 0.047629 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
PONCE | 2022-04-21 08:11 | 2022-04-21 09:05 | 978 | 000:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100043 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-04-21 | 52812 | keep | 0 | Apr | 2022 | 0.03597 | 0.00066611 | Sustained | FALSE | FALSE | Not_TMED_Event | 978
PONCE | 2022-04-21 08:11 | 2022-04-21 09:05 | 1730 | 000:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100043 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-04-21 | 93420 | keep | 0 | Apr | 2022 | 0.063628 | 0.0011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 1730
PONCE | 2022-04-21 08:11 | 2022-04-21 11:53 | 891 | 003:42 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100045 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 222 | 2022-04-21 | 197802 | keep | 0 | Apr | 2022 | 0.13472 | 0.00060686 | Sustained | FALSE | FALSE | Not_TMED_Event | 891
PONCE | 2022-04-21 08:11 | 2022-04-21 11:56 | 527 | 003:45 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100045 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 225 | 2022-04-21 | 118575 | keep | 0 | Apr | 2022 | 0.080761 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2022-04-21 08:11 | 2022-04-21 11:49 | 542 | 003:38 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22042100045 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 218 | 2022-04-21 | 118156 | keep | 0 | Apr | 2022 | 0.080476 | 0.00036915 | Sustained | FALSE | FALSE | Not_TMED_Event | 542
GUAYAMA | 2022-04-21 08:18 | 2022-04-21 08:19 | 4132 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P22042100049 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-21 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-04-21 08:18 | 2022-04-21 08:19 | 4279 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P22042100049 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-21 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-04-21 08:18 | 2022-04-21 08:19 | 464 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P22042100049 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-21 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
BARRANQUITAS | 2022-04-21 08:42 | 2022-04-21 11:00 | 264 | 002:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESCRUZO Y RETEZO LINEAS | C22042100043 | Partial_restoration | Wire Down | Include | Include | Equipment | 138 | 2022-04-21 | 36432 | keep | 0 | Apr | 2022 | 0.024814 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-21 08:55 | 2022-04-21 14:40 | 50 | 005:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE REPARO PUENTES PRIMARIOS | A22042100014 | New_Event | Wire Down | Include | Include | Equipment | 345 | 2022-04-21 | 17250 | keep | 0 | Apr | 2022 | 0.011749 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-21 08:56 | 2022-04-21 11:38 | 70 | 002:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042100059 | New_Event | Bad Weather | Include | Include | Weather | 162 | 2022-04-21 | 11340 | keep | 0 | Apr | 2022 | 0.0077236 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-04-21 09:03 | 2022-04-21 09:04 | 1268 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1200 | M22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1268 | keep | 0 | Apr | 2022 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2022-04-21 09:03 | 2022-04-21 09:04 | 2064 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1200 | M22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 2064 | keep | 0 | Apr | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2022-04-21 09:03 | 2022-04-21 09:04 | 3036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1200 | M22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 3036 | keep | 0 | Apr | 2022 | 0.0020678 | 0.0020678 | Momentary | FALSE | FALSE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2022-04-21 09:03 | 2022-04-21 09:04 | 2952 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1200 | M22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 2952 | keep | 0 | Apr | 2022 | 0.0020106 | 0.0020106 | Momentary | FALSE | FALSE | Not_TMED_Event | 2952
FAJARDO | 2022-04-21 09:04 | 2022-04-21 10:20 | 10 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R22042100154 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2022-04-21 | 760 | keep | 0 | Apr | 2022 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-04-21 09:04 | 2022-04-21 09:05 | 688 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042100069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 688 | keep | 0 | Apr | 2022 | 0.00046859 | 0.00046859 | Momentary | FALSE | FALSE | Not_TMED_Event | 688
SAN JUAN | 2022-04-21 09:05 | 2022-04-21 12:29 | 1 | 003:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R22042100155 | New_Event |  |  | Include | Wildlife | 204 | 2022-04-21 | 204 | keep | 0 | Apr | 2022 | 0.00013894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-21 09:21 | 2022-04-21 11:56 | 1 | 002:35 | P | DESGANCHE | 1 X 10 EN XMR Y 1 X 15 EN C/L DESGANCHE | S22042100010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-04-21 | 155 | keep | 0 | Apr | 2022 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-21 09:30 | 2022-04-21 14:30 | 10 | 005:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE MONTURA PARA REMPLAZAR POSTE SECUNDARIO Y SECUNDARIA | S22042100011 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 300 | 2022-04-21 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-04-21 09:30 | 2022-04-21 10:10 | 15 | 000:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE CAJA DE TRANSFORMADOR | P22042100080 | New_Event | Wire Down | Include | Include | Equipment | 40 | 2022-04-21 | 600 | keep | 0 | Apr | 2022 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-04-21 09:31 | 2022-04-21 17:16 | 1 | 007:45 | P | NO SE REPORTO CAUSA | 1 X 20 EN MONTURA TRIFASICA NO SE ENCONTRO CAUSA | P22042100081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 465 | 2022-04-21 | 465 | keep | 0 | Apr | 2022 | 0.00031671 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-21 09:39 | 2022-04-21 09:40 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 308 | keep | 0 | Apr | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-04-21 09:40 | 2022-04-21 15:42 | 272 | 006:02 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L PRINCIPAL | B22042100053 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 362 | 2022-04-21 | 98464 | keep | 0 | Apr | 2022 | 0.067063 | 0.00018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 272
SAN JUAN | 2022-04-21 09:50 | 2022-04-21 09:51 | 291 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1345-02 | S22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 291 | keep | 0 | Apr | 2022 | 0.0001982 | 0.0001982 | Momentary | FALSE | FALSE | Not_TMED_Event | 291
SAN JUAN | 2022-04-21 09:50 | 2022-04-21 09:51 | 435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1342-05 | S22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 435 | keep | 0 | Apr | 2022 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
MAYAGÃœEZ | 2022-04-21 10:00 | 2022-04-21 18:45 | 150 | 008:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M22042100100 | New_Event | Wire Down | Include | Include | Equipment | 525 | 2022-04-21 | 78750 | keep | 0 | Apr | 2022 | 0.053636 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-04-21 10:03 | 2022-04-21 10:04 | 8711 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE CARGA POR 1206-03 | S22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 8711 | keep | 0 | Apr | 2022 | 0.005933 | 0.005933 | Momentary | FALSE | FALSE | Not_TMED_Event | 8711
SAN JUAN | 2022-04-21 10:03 | 2022-04-21 10:04 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 1204-05 | S22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 4133 | keep | 0 | Apr | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-04-21 10:11 | 2022-04-21 11:05 | 26 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA Y SE REALIZO PODA | R22042100156 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-04-21 | 1404 | keep | 0 | Apr | 2022 | 0.00095626 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
MAYAGÃœEZ | 2022-04-21 10:19 | 2022-04-21 10:40 | 2 | 000:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN RISER MAL TIEMPO VIENTOS FUERTES | M22042100071 | New_Event | Bad Weather | Include | Include | Weather | 21 | 2022-04-21 | 42 | keep | 0 | Apr | 2022 | 2.8606e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-04-21 10:23 | 2022-04-21 10:24 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 2203 | keep | 0 | Apr | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-04-21 10:24 | 2022-04-21 12:43 | 17 | 002:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22042100027 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-04-21 | 2363 | keep | 0 | Apr | 2022 | 0.0016094 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2022-04-21 10:35 | 2022-04-21 13:50 | 10 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE ZAFADO EN TRANSFORMADOR | M22042100075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2022-04-21 | 1950 | keep | 0 | Apr | 2022 | 0.0013281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-21 10:44 | 2022-04-22 13:36 | 1 | 026:52 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | B22042100060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1612 | 2022-04-21 | 1612 | keep | 0 | Apr | 2022 | 0.0010979 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-21 11:01 | 2022-04-21 17:15 | 8 | 006:14 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REMPLAZARON CONECTORES Y SE DESGANCHO | A22042100029 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 374 | 2022-04-21 | 2992 | keep | 0 | Apr | 2022 | 0.0020378 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-21 11:09 | 2022-04-21 15:00 | 19 | 003:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO PM-43 PARA REEMPLAZAR BARRA EN PEDESTAL | R22042100165 | New_Event | Secondary Wire Down | Include | Include | Equipment | 231 | 2022-04-21 | 4389 | keep | 0 | Apr | 2022 | 0.0029893 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-04-21 11:10 | 2022-04-21 13:15 | 3 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B22042100062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2022-04-21 | 375 | keep | 0 | Apr | 2022 | 0.00025541 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-04-21 11:17 | 2022-04-21 15:22 | 40 | 004:05 | P | DESGANCHE | 1 X 65 EN RISER DESGANCHO | C22042100085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-04-21 | 9800 | keep | 0 | Apr | 2022 | 0.0066747 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-21 11:28 | 2022-04-21 14:08 | 50 | 002:40 | P | DESGANCHE | 1 X 50 EN C/L | C22042100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-04-21 | 8000 | keep | 0 | Apr | 2022 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-04-21 11:33 | 2022-04-21 18:17 | 40 | 006:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22042100169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 404 | 2022-04-21 | 16160 | keep | 0 | Apr | 2022 | 0.011007 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-21 11:43 | 2022-04-21 16:09 | 13 | 004:26 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | S22042100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2022-04-21 | 3458 | keep | 0 | Apr | 2022 | 0.0023552 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2022-04-21 11:51 | 2022-04-21 11:53 | 906 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22042100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-21 | 1812 | keep | 0 | Apr | 2022 | 0.0012341 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
AGUADILLA | 2022-04-21 12:00 | 2022-04-21 12:01 | 1057 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22042100108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 1057 | keep | 0 | Apr | 2022 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | Not_TMED_Event | 1057
AGUADILLA | 2022-04-21 12:00 | 2022-04-21 12:01 | 4882 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE DE INTERRUPTOR | M22042100109 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-04-21 | 4882 | keep | 0 | Apr | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2022-04-21 12:01 | 2022-04-21 13:52 | 10 | 001:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA | M22042100031 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 111 | 2022-04-21 | 1110 | keep | 0 | Apr | 2022 | 0.00075602 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-21 12:08 | 2022-04-22 10:00 | 80 | 021:52 | P | DESGANCHE | 1X65 EN C/L & SE RETIRO ARBOL DEL TENDIDO ELECTRICO | B22042100072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1312 | 2022-04-21 | 104960 | keep | 0 | Apr | 2022 | 0.071488 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-04-21 12:08 | 2022-04-21 15:34 | 50 | 003:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE LEVANTO CONDUCTOR | B22042100071 | New_Event | Wire Down | Include | Include | Equipment | 206 | 2022-04-21 | 10300 | keep | 0 | Apr | 2022 | 0.0070153 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-04-21 12:19 | 2022-04-21 16:00 | 80 | 003:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA FASE PRIMARIA CRUZADA CON LINEA SECUNDARIA | P22042100120 | New_Event | Wire Down | Include | Include | Equipment | 221 | 2022-04-21 | 17680 | keep | 0 | Apr | 2022 | 0.012042 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-21 12:38 | 2022-04-21 16:40 | 10 | 004:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 C/L CRUCE POR AVE | C22042100091 | New_Event |  |  | Include | Wildlife | 242 | 2022-04-21 | 2420 | keep | 0 | Apr | 2022 | 0.0016483 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-21 12:40 | 2022-04-21 13:56 | 10 | 001:16 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | S22042100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-04-21 | 760 | keep | 0 | Apr | 2022 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-21 12:40 | 2022-04-21 13:42 | 6 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REEMPLAZAR SECUNDARIA | C22042100092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2022-04-21 | 372 | keep | 0 | Apr | 2022 | 0.00025337 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-21 12:52 | 2022-04-21 13:09 | 1 | 000:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR AVE | S22042100042 | New_Event |  |  | Include | Wildlife | 17 | 2022-04-21 | 17 | keep | 0 | Apr | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-21 12:56 | 2022-04-21 13:28 | 50 | 000:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 5 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22042100051 | New_Event | Bad Weather | Include | Include | Weather | 32 | 2022-04-21 | 1600 | keep | 0 | Apr | 2022 | 0.0010898 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-04-21 13:00 | 2022-04-21 14:20 | 25 | 001:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA ZAFADA DE AISLADOR | A22042100031 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 80 | 2022-04-21 | 2000 | keep | 0 | Apr | 2022 | 0.0013622 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-04-21 13:04 | 2022-04-21 13:05 | 1827 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M22042100125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-21 | 1827 | keep | 0 | Apr | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-04-21 13:05 | 2022-04-21 16:05 | 30 | 003:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M22042100128 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-04-21 | 5400 | keep | 0 | Apr | 2022 | 0.0036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-04-21 13:07 | 2022-04-21 15:03 | 140 | 001:56 | P | DESGANCHE | 1 X 80 Y 2 X 50 EN CORTES DE LINEAS RETIRO BAMBUAS SOBRE LINEAS | R22042100173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-04-21 | 16240 | keep | 0 | Apr | 2022 | 0.011061 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
FAJARDO | 2022-04-21 13:10 | 2022-04-21 15:18 | 16 | 002:08 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE ROTO | R22042100175 | New_Event | Defective Pole | Include | Include | Equipment | 128 | 2022-04-21 | 2048 | keep | 0 | Apr | 2022 | 0.0013949 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-04-21 13:21 | 2022-04-21 18:28 | 7 | 005:07 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22042100095 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 307 | 2022-04-21 | 2149 | keep | 0 | Apr | 2022 | 0.0014637 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-04-21 13:23 | 2022-04-21 17:42 | 12 | 004:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA ABIERTA | R22042100179 | New_Event | Secondary Wire Down | Include | Include | Equipment | 259 | 2022-04-21 | 3108 | keep | 0 | Apr | 2022 | 0.0021168 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-04-21 13:32 | 2022-04-21 19:00 | 5 | 005:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M22042100129 | New_Event | Cutout Failure | Include | Include | Equipment | 328 | 2022-04-21 | 1640 | keep | 0 | Apr | 2022 | 0.001117 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-04-21 13:33 | 2022-04-21 22:14 | 40 | 008:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA | M22042100130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2022-04-21 | 20840 | keep | 0 | Apr | 2022 | 0.014194 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-21 13:47 | 2022-04-21 19:39 | 104 | 005:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO SE ENCONTRO PUENTE ABIERTO 2 FASES EN MACHETE NO DIGITALIZADOS Y SE HIZO DESGANCHE Y SE REMPLAZO PUENTE PORTATIL | S22042100044 | New_Event | Wire Down | Include | Include | Equipment | 352 | 2022-04-21 | 36608 | keep | 0 | Apr | 2022 | 0.024934 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
BAYAMON | 2022-04-21 13:50 | 2022-04-21 14:48 | 681 | 000:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESENREDO LINEA CON VARETA SE CERRO INTERRUPTOR QUEDO EN SERVICIO | S22042100045 | New_Event | Wire Down | Include | Include | Equipment | 58 | 2022-04-21 | 39498 | keep | 0 | Apr | 2022 | 0.026902 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-04-21 13:58 | 2022-04-21 17:15 | 50 | 003:17 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S22042100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-04-21 | 9850 | keep | 0 | Apr | 2022 | 0.0067088 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-21 14:04 | 2022-04-21 14:05 | 686 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22042100055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 686 | keep | 0 | Apr | 2022 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
CANOVANAS | 2022-04-21 14:08 | 2022-04-21 17:17 | 11 | 003:09 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTES DE LINEAS | R22042100182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2022-04-21 | 2079 | keep | 0 | Apr | 2022 | 0.001416 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-04-21 14:10 | 2022-04-21 19:25 | 194 | 005:15 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22042100063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 315 | 2022-04-21 | 61110 | keep | 0 | Apr | 2022 | 0.041622 | 0.00013213 | Sustained | FALSE | FALSE | Not_TMED_Event | 194
SAN JUAN | 2022-04-21 14:11 | 2022-04-21 14:12 | 8711 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO PARTE 1206-03 | S22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 8711 | keep | 0 | Apr | 2022 | 0.005933 | 0.005933 | Momentary | FALSE | FALSE | Not_TMED_Event | 8711
SAN JUAN | 2022-04-21 14:11 | 2022-04-21 14:12 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA PARTE 1204-5 | S22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 4133 | keep | 0 | Apr | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
AGUADILLA | 2022-04-21 14:25 | 2022-04-21 18:55 | 150 | 004:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M22042100148 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 270 | 2022-04-21 | 40500 | keep | 0 | Apr | 2022 | 0.027584 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-04-21 14:25 | 2022-04-21 15:25 | 15 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A22042100036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-04-21 | 900 | keep | 0 | Apr | 2022 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-04-21 14:29 | 2022-04-21 15:12 | 1 | 000:43 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R22042100184 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 43 | 2022-04-21 | 43 | keep | 0 | Apr | 2022 | 2.9287e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-21 14:52 | 2022-04-21 17:24 | 681 | 002:32 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESENREDO LINEA SE HIZO DESGANCHE Y SE CERRO PUENTE PRIMARIO | S22042100084 | Partial_restoration | Wire Down | Include | Include | Equipment | 152 | 2022-04-21 | 103512 | keep | 0 | Apr | 2022 | 0.070502 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-21 15:00 | 2022-04-21 15:30 | 15 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR NEUTRAL Y SECUNDARIA | S22042100041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-04-21 | 450 | keep | 0 | Apr | 2022 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-21 15:01 | 2022-04-21 15:11 | 5191 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1710-05 LLEVANDO 40% DEL 1718-03 SE CERRO POR SCADA | B22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-04-21 | 51910 | keep | 0 | Apr | 2022 | 0.035356 | 0.0035356 | Sustained | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2022-04-21 15:01 | 2022-04-21 15:11 | 1042 | 000:10 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1710-05 LLEVANDO 40% DEL 1718-03 SE CERRO POR SCADA | B22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-04-21 | 10420 | keep | 0 | Apr | 2022 | 0.007097 | 0.0007097 | Sustained | FALSE | FALSE | Not_TMED_Event | 1042
MAYAGÃœEZ | 2022-04-21 15:13 | 2022-04-21 15:14 | 6285 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M22042100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-21 | 6285 | keep | 0 | Apr | 2022 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
BAYAMON | 2022-04-21 15:13 | 2022-04-21 17:53 | 11 | 002:40 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO ARBOL SOBRE LINEAS | B22042100108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-04-21 | 1760 | keep | 0 | Apr | 2022 | 0.0011987 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-04-21 15:14 | 2022-04-22 00:40 | 90 | 009:26 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR RAMAS SOBRE LINEA | M22042100177 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 566 | 2022-04-21 | 50940 | keep | 0 | Apr | 2022 | 0.034695 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-04-21 15:15 | 2022-04-21 17:49 | 173 | 002:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO DE LINEA @ CAJA PRIMARIA. NO FUNDIO | S22042100115 | New_Event | Wire Down | Include | Include | Equipment | 154 | 2022-04-21 | 26642 | keep | 0 | Apr | 2022 | 0.018146 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
PONCE | 2022-04-21 15:25 | 2022-04-21 16:27 | 30 | 001:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA FASE PRIMARIA CRUZADA POR CONTACTO CON TENSOR | P22042100118 | New_Event | Wire Down | Include | Include | Equipment | 62 | 2022-04-21 | 1860 | keep | 0 | Apr | 2022 | 0.0012668 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-04-21 15:31 | 2022-04-21 16:31 | 21 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22042100101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-04-21 | 1260 | keep | 0 | Apr | 2022 | 0.00085818 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-04-21 15:34 | 2022-04-21 16:38 | 8 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REALIZAR DESGANCHE | B22042100083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2022-04-21 | 512 | keep | 0 | Apr | 2022 | 0.00034872 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-21 15:38 | 2022-04-22 12:44 | 7 | 021:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE INSTALO HERRAJE NUEVO & SE REMPLAZO BAJANTE PRIMARIO | B22042100114 | New_Event | Wire Down | Include | Include | Equipment | 1266 | 2022-04-21 | 8862 | keep | 0 | Apr | 2022 | 0.0060359 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-04-21 15:42 | 2022-04-21 19:28 | 90 | 003:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22042100115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2022-04-21 | 20340 | keep | 0 | Apr | 2022 | 0.013853 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-04-21 16:06 | 2022-04-21 23:29 | 30 | 007:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CONVERTIDOS POR MAL TIEMPO | M22042100170 | New_Event | Bad Weather | Include | Include | Weather | 443 | 2022-04-21 | 13290 | keep | 0 | Apr | 2022 | 0.0090518 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-21 16:09 | 2022-04-22 02:45 | 92 | 010:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-5A | S22042100123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 636 | 2022-04-21 | 58512 | keep | 0 | Apr | 2022 | 0.039852 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
CAGUAS | 2022-04-21 16:32 | 2022-04-22 06:45 | 1 | 014:13 | P | DESGANCHE | 1 X 40 EN C/L | C22042100104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 853 | 2022-04-21 | 853 | keep | 0 | Apr | 2022 | 0.00058097 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-21 16:35 | 2022-04-21 21:52 | 71 | 005:17 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN SU-3 AVERIA NUEVA T-32 A T-31 AVERIA VIEJA T-28 A SU-28 ( NO HAY CABLE) | S22042100139 | New_Event | UG Cable Fault | Include | Include | Equipment | 317 | 2022-04-21 | 22507 | keep | 0 | Apr | 2022 | 0.015329 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
GUAYAMA | 2022-04-21 16:50 | 2022-04-21 17:16 | 10 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONEXIONES SECUNDARIAS | P22042100082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-04-21 | 260 | keep | 0 | Apr | 2022 | 0.00017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-04-21 16:57 | 2022-04-21 16:58 | 1839 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1839 | keep | 0 | Apr | 2022 | 0.0012525 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2022-04-21 16:57 | 2022-04-21 16:58 | 1778 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1778 | keep | 0 | Apr | 2022 | 0.001211 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2022-04-21 16:57 | 2022-04-21 16:58 | 1376 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1376 | keep | 0 | Apr | 2022 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
HUMACAO | 2022-04-21 16:57 | 2022-04-21 16:58 | 3701 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 5400 | C22042100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 3701 | keep | 0 | Apr | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-04-21 16:57 | 2022-04-21 16:58 | 989 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 5400 | C22042100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 989 | keep | 0 | Apr | 2022 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2022-04-21 16:57 | 2022-04-21 16:58 | 1467 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 5400 | C22042100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1467 | keep | 0 | Apr | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
FAJARDO | 2022-04-21 16:57 | 2022-04-21 16:58 | 293 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 293 | keep | 0 | Apr | 2022 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2022-04-21 16:57 | 2022-04-21 16:58 | 1215 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22042100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-21 | 1215 | keep | 0 | Apr | 2022 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
UTUADO | 2022-04-21 17:11 | 2022-04-22 13:04 | 4 | 019:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE EN VARIOS PUNTOS | A22042100052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1193 | 2022-04-21 | 4772 | keep | 0 | Apr | 2022 | 0.0032502 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-04-21 17:13 | 2022-04-21 20:39 | 30 | 003:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M22042100186 | New_Event |  |  | Include | Wildlife | 206 | 2022-04-21 | 6180 | keep | 0 | Apr | 2022 | 0.0042092 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-21 17:24 | 2022-04-21 17:25 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 4176 | keep | 0 | Apr | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
HUMACAO | 2022-04-21 17:25 | 2022-04-21 17:26 | 327 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 2603-06 QUE LLEVA LA CARGA DEL 2603-07 | C22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 327 | keep | 0 | Apr | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
CAGUAS | 2022-04-21 17:32 | 2022-04-22 11:30 | 1 | 017:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 2 SMU 20 DE 30A EN SU - 3 | C22042100105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1078 | 2022-04-21 | 1078 | keep | 0 | Apr | 2022 | 0.00073422 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-21 17:46 | 2022-04-21 17:47 | 5668 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R22042100196 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-04-21 | 5668 | keep | 0 | Apr | 2022 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2022-04-21 17:47 | 2022-04-21 19:31 | 1889 | 001:44 | P | DESCONECTIVO DEFECTUOSO | SE REPARO FASE CON MACHETE QUEMADO | R22042100206 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 104 | 2022-04-21 | 196456 | keep | 0 | Apr | 2022 | 0.13381 | 0.0012866 | Sustained | FALSE | FALSE | Not_TMED_Event | 1889
GUAYAMA | 2022-04-21 18:05 | 2022-04-21 19:15 | 1 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22042100137 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-04-21 | 70 | keep | 0 | Apr | 2022 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-21 18:08 | 2022-04-21 22:04 | 356 | 003:56 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA | B22042100146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-04-21 | 84016 | keep | 0 | Apr | 2022 | 0.057223 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
ARECIBO | 2022-04-21 18:17 | 2022-04-21 18:18 | 1628 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A22042100054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 1628 | keep | 0 | Apr | 2022 | 0.0011088 | 0.0011088 | Momentary | FALSE | FALSE | Not_TMED_Event | 1628
BAYAMON | 2022-04-21 18:44 | 2022-04-21 22:00 | 125 | 003:16 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 65 EN CORTE DE LINEA | S22042100164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2022-04-21 | 24500 | keep | 0 | Apr | 2022 | 0.016687 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
FAJARDO | 2022-04-21 19:18 | 2022-04-21 20:39 | 8 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR REEMPLAZO SECUNDARIA Y BAJANTE SECUNDARIO XMR AVERIADO POR VEHICULO | R22042100244 | New_Event |  |  | Include | Wildlife | 81 | 2022-04-21 | 648 | keep | 0 | Apr | 2022 | 0.00044135 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-04-21 19:22 | 2022-04-21 21:55 | 35 | 002:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUAS Y PENCAS DE PALMAS | A22042100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-04-21 | 5355 | keep | 0 | Apr | 2022 | 0.0036473 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-04-21 19:31 | 2022-04-21 19:32 | 5668 | 000:01 | T | ERROR HUMANO | DISPARO PERSONAL REALIZANDO OPERACIONES ABRIENDO MACHETE CON FASE AVERIADA, SE ABRIO LA FASE EQUIVOCADA. | R22042100257 | New_Event | Human Error | Include | Include | Other | 1 | 2022-04-21 | 5668 | keep | 0 | Apr | 2022 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2022-04-21 19:32 | 2022-04-21 19:37 | 1889 | 000:05 | P | DESCONECTIVO DEFECTUOSO | SE REPARO FASE CON MACHETE QUEMADO | R22042100206 | Partial_restoration | Switch Failure | Include | Include | Equipment | 5 | 2022-04-21 | 9445 | keep | 0 | Apr | 2022 | 0.0064329 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-21 19:37 | 2022-04-21 19:50 | 716 | 000:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO AL CERRAR N/O CON 1359-7 SE ENCONTRO FASE ABIERTA | S22042100174 | New_Event | Wire Down | Include | Include | Equipment | 13 | 2022-04-21 | 9308 | keep | 0 | Apr | 2022 | 0.0063396 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
SAN JUAN | 2022-04-21 19:37 | 2022-04-21 19:38 | 5668 | 000:01 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA QUE PERSONAL ABRIERA LA FASE DEL MACHETE AVERIADA. | R22042100266 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2022-04-21 | 5668 | keep | 0 | Apr | 2022 | 0.0038604 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-21 19:38 | 2022-04-21 21:47 | 1889 | 002:09 | P | DESCONECTIVO DEFECTUOSO | SE REPARO FASE CON MACHETE QUEMADO | R22042100206 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 129 | 2022-04-21 | 243681 | keep | 0 | Apr | 2022 | 0.16597 | 0.0012866 | Sustained | FALSE | FALSE | Not_TMED_Event | 1889
BAYAMON | 2022-04-21 19:39 | 2022-04-21 22:06 | 312 | 002:27 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE ENCONTRO 2 FASES ABIERTA SE REPARO SE HIZO DESGANCHE Y SE INSTALO PORTATIL MACHETE EN SALIDA INTERRUPTOR | S22042100174 | Additional_clients | Wire Down | Include | Include | Equipment | 147 | 2022-04-21 | 45864 | keep | 0 | Apr | 2022 | 0.031238 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-21 19:56 | 2022-04-21 19:57 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22042100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-21 | 990 | keep | 0 | Apr | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
AGUADILLA | 2022-04-21 20:09 | 2022-04-22 03:37 | 10 | 007:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN TRANSFORMADOR POR CAJA PRIMARIA QUEMADA | M22042100236 | New_Event | Cutout Failure | Include | Include | Equipment | 448 | 2022-04-21 | 4480 | keep | 0 | Apr | 2022 | 0.0030513 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-21 20:10 | 2022-04-22 15:30 | 8 | 019:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR CHANGO | S22042100163 | New_Event |  |  | Include | Wildlife | 1160 | 2022-04-21 | 9280 | keep | 0 | Apr | 2022 | 0.0063206 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-21 20:38 | 2022-04-22 10:20 | 6 | 013:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22042100111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 822 | 2022-04-21 | 4932 | keep | 0 | Apr | 2022 | 0.0033592 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-04-21 21:09 | 2022-04-22 07:20 | 11 | 010:11 | P | PARARRAYOS DEFECTUOSO | 1 X 30 C/L REEMPLAZO PARARRAYO | C22042100112 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 611 | 2022-04-21 | 6721 | keep | 0 | Apr | 2022 | 0.0045776 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2022-04-21 21:13 | 2022-04-22 01:00 | 60 | 003:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA PARTIDA | A22042100067 | New_Event | Cutout Failure | Include | Include | Equipment | 227 | 2022-04-21 | 13620 | keep | 0 | Apr | 2022 | 0.0092765 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-21 21:39 | 2022-04-22 20:49 | 25 | 023:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR CRUCE POR IGUANA | B22042100170 | New_Event |  |  | Include | Wildlife | 1390 | 2022-04-21 | 34750 | keep | 0 | Apr | 2022 | 0.023668 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-04-21 21:43 | 2022-04-21 23:21 | 300 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN CORTE DE LINEA POR FUERTES LLUVIAS | A22042100074 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2022-04-21 | 29400 | keep | 0 | Apr | 2022 | 0.020024 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2022-04-21 21:44 | 2022-04-22 10:36 | 30 | 012:52 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22042100172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 772 | 2022-04-21 | 23160 | keep | 0 | Apr | 2022 | 0.015774 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-21 21:45 | 2022-04-22 04:49 | 15 | 007:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22042100173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 424 | 2022-04-21 | 6360 | keep | 0 | Apr | 2022 | 0.0043318 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-04-21 21:47 | 2022-04-21 21:48 | 5668 | 000:01 | T | DESCONECTIVO DEFECTUOSO | ABRIR INTERRUPTOR PARA QUE PERSONAL PUEDA CERRAR MACHETES INCOMODO PARA OPERAR. | R22042100379 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2022-04-21 | 5668 | keep | 0 | Apr | 2022 | 0.0038604 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-21 21:52 | 2022-04-22 13:06 | 51 | 015:14 | P | CABLE SOTERRADO AVERIADO | SE REEMPLAZO CABLE SOTERRADO DE T-32 @ T-31 | S22042100139 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 914 | 2022-04-21 | 46614 | keep | 0 | Apr | 2022 | 0.031749 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-21 22:24 | 2022-04-22 09:48 | 72 | 011:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L SE RETIRO IGUANA | R22042100383 | New_Event |  |  | Include | Wildlife | 684 | 2022-04-21 | 49248 | keep | 0 | Apr | 2022 | 0.033543 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2022-04-21 22:52 | 2022-04-21 23:07 | 11 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S22042100133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-04-21 | 165 | keep | 0 | Apr | 2022 | 0.00011238 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-04-21 23:20 | 2022-04-22 00:20 | 12 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA LEVANTAR SECUNDARIA | S22042100194 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-04-21 | 720 | keep | 0 | Apr | 2022 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-22 00:36 | 2022-04-22 00:37 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 1834 | keep | 0 | Apr | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-04-22 00:37 | 2022-04-22 17:48 | 21 | 017:11 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | C22042200001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1031 | 2022-04-22 | 21651 | keep | 0 | Apr | 2022 | 0.014746 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-04-22 01:47 | 2022-04-22 01:49 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO | B22042200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-22 | 4468 | keep | 0 | Apr | 2022 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-04-22 01:54 | 2022-04-22 01:56 | 169 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1116-5 SE PROBO QUEDO EN SERVICIO | S22042200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-22 | 338 | keep | 0 | Apr | 2022 | 0.00023021 | 0.00011511 | Momentary | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-04-22 01:54 | 2022-04-22 01:56 | 5 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1117-8 Y 1116-4 SE PROBO QUEDO EN SERVICIO | S22042200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-22 | 10 | keep | 0 | Apr | 2022 | 6.811e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-04-22 01:54 | 2022-04-22 01:56 | 466 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1116-5 SE PROBO QUEDO EN SERVICIO | S22042200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-22 | 932 | keep | 0 | Apr | 2022 | 0.00063478 | 0.00031739 | Momentary | FALSE | FALSE | Not_TMED_Event | 466
BAYAMON | 2022-04-22 01:56 | 2022-04-22 14:23 | 1 | 012:27 | P | NO SE REPORTO CAUSA | 1 SMU-20 X 25 AMP | S22042200100 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 747 | 2022-04-22 | 747 | keep | 0 | Apr | 2022 | 0.00050878 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-22 01:57 | 2022-04-22 04:33 | 10 | 002:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REEMPLAZO PORTAFUSIBLE | M22042200002 | New_Event | Cutout Failure | Include | Include | Equipment | 156 | 2022-04-22 | 1560 | keep | 0 | Apr | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-22 03:38 | 2022-04-22 05:17 | 50 | 001:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEAS | M22042200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-04-22 | 4950 | keep | 0 | Apr | 2022 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-22 03:41 | 2022-04-22 03:44 | 514 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1520-5 | S22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-22 | 1542 | keep | 0 | Apr | 2022 | 0.0010502 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2022-04-22 03:41 | 2022-04-22 03:44 | 752 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1520-5 | S22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-22 | 2256 | keep | 0 | Apr | 2022 | 0.0015366 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2022-04-22 03:41 | 2022-04-22 03:44 | 68 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1520-4 Y 1 | S22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-22 | 204 | keep | 0 | Apr | 2022 | 0.00013894 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-04-22 04:04 | 2022-04-22 12:35 | 18 | 008:31 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 Y 1 X20 EN C/L SE REPARO TERMINACION SOTERRADA | R22042200001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 511 | 2022-04-22 | 9198 | keep | 0 | Apr | 2022 | 0.0062647 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-04-22 04:17 | 2022-04-22 13:32 | 32 | 009:15 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 100 SE REPARO TERMINACION EN AEREO PROVISIONAL | R22042200003 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 555 | 2022-04-22 | 17760 | keep | 0 | Apr | 2022 | 0.012096 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2022-04-22 04:48 | 2022-04-22 04:50 | 143 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 80% DEL 1404-07 | S22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-22 | 286 | keep | 0 | Apr | 2022 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-04-22 04:48 | 2022-04-22 04:50 | 1085 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 80% POR 1404-6 | S22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-22 | 2170 | keep | 0 | Apr | 2022 | 0.001478 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
CAGUAS | 2022-04-22 04:49 | 2022-04-22 04:50 | 2281 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22042200003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2281 | keep | 0 | Apr | 2022 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
BAYAMON | 2022-04-22 04:50 | 2022-04-22 04:51 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 3511 | keep | 0 | Apr | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
SAN JUAN | 2022-04-22 04:53 | 2022-04-22 10:54 | 194 | 006:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE REPARO PUENTE PRIMARIO QUEMADO | R22042200007 | New_Event | Wire Down | Include | Include | Equipment | 361 | 2022-04-22 | 70034 | keep | 0 | Apr | 2022 | 0.0477 | 0.00013213 | Sustained | FALSE | FALSE | Not_TMED_Event | 194
CANOVANAS | 2022-04-22 04:55 | 2022-04-22 10:06 | 60 | 005:11 | P | DESGANCHE | 2 X 10 EN C/L SE REALIZO DESGANCHE | R22042200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-04-22 | 18660 | keep | 0 | Apr | 2022 | 0.012709 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-22 05:02 | 2022-04-22 07:11 | 82 | 002:09 | P | DESGANCHE | 1X65 EN PROVISIONAL AEREO | B22042200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-04-22 | 10578 | keep | 0 | Apr | 2022 | 0.0072046 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
BAYAMON | 2022-04-22 05:17 | 2022-04-22 05:20 | 946 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1525-5 | S22042200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-22 | 2838 | keep | 0 | Apr | 2022 | 0.0019329 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
BAYAMON | 2022-04-22 05:17 | 2022-04-22 05:20 | 937 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1525-2 | S22042200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-22 | 2811 | keep | 0 | Apr | 2022 | 0.0019146 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
BAYAMON | 2022-04-22 05:20 | 2022-04-22 14:01 | 18 | 008:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22042200038 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 521 | 2022-04-22 | 9378 | keep | 0 | Apr | 2022 | 0.0063873 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2022-04-22 05:24 | 2022-04-22 09:05 | 154 | 003:41 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22042200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-04-22 | 34034 | keep | 0 | Apr | 2022 | 0.02318 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
CAGUAS | 2022-04-22 05:26 | 2022-04-22 05:27 | 1084 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 1084 | keep | 0 | Apr | 2022 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
BAYAMON | 2022-04-22 05:37 | 2022-04-22 06:55 | 1860 | 001:18 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO PARA PROBAR TRAMO 95% EN SERVICIO | S22042200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-04-22 | 145080 | keep | 0 | Apr | 2022 | 0.098813 | 0.0012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 1860
HUMACAO | 2022-04-22 05:37 | 2022-04-22 08:21 | 6 | 002:44 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN C/L ELIMINO XMR VACANTE | C22042200005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 164 | 2022-04-22 | 984 | keep | 0 | Apr | 2022 | 0.0006702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-04-22 05:56 | 2022-04-22 07:49 | 75 | 001:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22042200001 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2022-04-22 | 8475 | keep | 0 | Apr | 2022 | 0.0057723 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-04-22 06:00 | 2022-04-22 09:24 | 33 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN AEREO PROVISIONAL | S22042200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2022-04-22 | 6732 | keep | 0 | Apr | 2022 | 0.0045851 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2022-04-22 06:24 | 2022-04-22 16:20 | 234 | 009:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | B22042200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 596 | 2022-04-22 | 139464 | keep | 0 | Apr | 2022 | 0.094988 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
MAYAGÃœEZ | 2022-04-22 06:25 | 2022-04-22 07:57 | 50 | 001:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042200005 | New_Event | Bad Weather | Include | Include | Weather | 92 | 2022-04-22 | 4600 | keep | 0 | Apr | 2022 | 0.003133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-22 06:34 | 2022-04-22 06:35 | 325 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | S22042200015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-22 | 325 | keep | 0 | Apr | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-04-22 06:35 | 2022-04-22 12:19 | 215 | 005:44 | P | DESGANCHE | 2 X 80 EN RISER 1 BAJANTE PRIMARIO Y PARARRAYO DESGANCHE | S22042200030 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 344 | 2022-04-22 | 73960 | keep | 0 | Apr | 2022 | 0.050374 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2022-04-22 06:38 | 2022-04-22 06:39 | 1270 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO - 20% DE SU CARGA ESTA TRANSFERIDA AL 1711-03 | B22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 1270 | keep | 0 | Apr | 2022 | 0.00086499 | 0.00086499 | Momentary | FALSE | FALSE | Not_TMED_Event | 1270
ARECIBO | 2022-04-22 06:42 | 2022-04-22 11:52 | 25 | 005:10 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYO CRUZADO | A22042200003 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 310 | 2022-04-22 | 7750 | keep | 0 | Apr | 2022 | 0.0052785 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-04-22 06:45 | 2022-04-22 06:46 | 1384 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 1000 OPERO EL BKR 1060 Y 1040 | S22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-22 | 1384 | keep | 0 | Apr | 2022 | 0.00094264 | 0.00094264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1384
SAN JUAN | 2022-04-22 06:45 | 2022-04-22 06:46 | 869 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 1000 OPERO EL BKR 1060 Y 1040 | S22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-22 | 869 | keep | 0 | Apr | 2022 | 0.00059187 | 0.00059187 | Momentary | FALSE | FALSE | Not_TMED_Event | 869
CAGUAS | 2022-04-22 06:50 | 2022-04-22 06:51 | 131 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22042200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 131 | keep | 0 | Apr | 2022 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
BAYAMON | 2022-04-22 06:55 | 2022-04-22 07:25 | 93 | 000:30 | P | DESGANCHE | SE CERRARON MACHETES 100% EN SERVICIO DESGANCHE Y MAL TIEMPO | S22042200007 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-04-22 | 2790 | keep | 0 | Apr | 2022 | 0.0019003 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-04-22 07:01 | 2022-04-22 07:02 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22042200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 1047 | keep | 0 | Apr | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
SAN JUAN | 2022-04-22 07:07 | 2022-04-22 07:10 | 726 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 1346-04 | S22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-22 | 2178 | keep | 0 | Apr | 2022 | 0.0014834 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-04-22 07:07 | 2022-04-22 07:10 | 3932 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR 1303-03 | S22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-22 | 11796 | keep | 0 | Apr | 2022 | 0.0080342 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
CAGUAS | 2022-04-22 07:16 | 2022-04-22 11:18 | 17 | 004:02 | P | DESGANCHE | 1 X 30 EN C/L | C22042200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-04-22 | 4114 | keep | 0 | Apr | 2022 | 0.002802 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2022-04-22 07:24 | 2022-04-22 08:12 | 71 | 000:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C22042200012 | New_Event | Bad Weather | Include | Include | Weather | 48 | 2022-04-22 | 3408 | keep | 0 | Apr | 2022 | 0.0023212 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
BAYAMON | 2022-04-22 07:37 | 2022-04-22 08:55 | 80 | 001:18 | P | DESGANCHE | 1X50 EN C/L | B22042200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-04-22 | 6240 | keep | 0 | Apr | 2022 | 0.00425 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-22 07:57 | 2022-04-22 18:15 | 125 | 010:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO PALMA EN CONTACTO CON LA LINEA | B22042200030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 618 | 2022-04-22 | 77250 | keep | 0 | Apr | 2022 | 0.052615 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-04-22 08:00 | 2022-04-22 17:22 | 45 | 009:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | S22042200041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 562 | 2022-04-22 | 25290 | keep | 0 | Apr | 2022 | 0.017225 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2022-04-22 08:03 | 2022-04-22 08:44 | 1405 | 000:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-04-22 | 57605 | keep | 0 | Apr | 2022 | 0.039235 | 0.00095694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2022-04-22 08:03 | 2022-04-22 08:44 | 669 | 000:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-04-22 | 27429 | keep | 0 | Apr | 2022 | 0.018682 | 0.00045565 | Sustained | FALSE | FALSE | Not_TMED_Event | 669
UTUADO | 2022-04-22 08:03 | 2022-04-22 08:44 | 1527 | 000:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-04-22 | 62607 | keep | 0 | Apr | 2022 | 0.042641 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2022-04-22 08:03 | 2022-04-22 08:44 | 1054 | 000:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-04-22 | 43214 | keep | 0 | Apr | 2022 | 0.029433 | 0.00071787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2022-04-22 08:03 | 2022-04-22 08:44 | 932 | 000:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-04-22 | 38212 | keep | 0 | Apr | 2022 | 0.026026 | 0.00063478 | Sustained | FALSE | FALSE | Not_TMED_Event | 932
UTUADO | 2022-04-22 08:03 | 2022-04-22 08:44 | 705 | 000:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-04-22 | 28905 | keep | 0 | Apr | 2022 | 0.019687 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2022-04-22 08:03 | 2022-04-22 08:44 | 1521 | 000:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-04-22 | 62361 | keep | 0 | Apr | 2022 | 0.042474 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2022-04-22 08:03 | 2022-04-22 08:44 | 882 | 000:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A22042200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-04-22 | 36162 | keep | 0 | Apr | 2022 | 0.02463 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
FAJARDO | 2022-04-22 08:11 | 2022-04-22 10:13 | 10 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR AVE | R22042200033 | New_Event |  |  | Include | Wildlife | 122 | 2022-04-22 | 1220 | keep | 0 | Apr | 2022 | 0.00083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-22 08:12 | 2022-04-22 13:45 | 1 | 005:33 | P | OTRAS CAUSAS | 1 X 40 EN RISER CLIENTE TIENE CONTAMINACION EN TRANSCLOSURE SE LE ORIENTO | B22042200033 | New_Event | Other Causes | Include | Include | Other | 333 | 2022-04-22 | 333 | keep | 0 | Apr | 2022 | 0.0002268 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-22 08:14 | 2022-04-22 15:05 | 60 | 006:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A22042200025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2022-04-22 | 24660 | keep | 0 | Apr | 2022 | 0.016796 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-04-22 08:22 | 2022-04-22 10:31 | 2 | 002:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L SE RETIRO AVE | R22042200029 | New_Event |  |  | Include | Wildlife | 129 | 2022-04-22 | 258 | keep | 0 | Apr | 2022 | 0.00017572 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-04-22 08:22 | 2022-04-22 10:56 | 1 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22042200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-04-22 | 154 | keep | 0 | Apr | 2022 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-22 08:25 | 2022-04-22 08:26 | 2446 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2446 | keep | 0 | Apr | 2022 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2022-04-22 08:25 | 2022-04-22 08:26 | 5069 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 5069 | keep | 0 | Apr | 2022 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
BAYAMON | 2022-04-22 08:34 | 2022-04-22 19:36 | 40 | 011:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO Y SE ELIMINO PARARRAYO AVERIADO | S22042200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 662 | 2022-04-22 | 26480 | keep | 0 | Apr | 2022 | 0.018035 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-04-22 08:34 | 2022-04-22 11:52 | 100 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN C/L MAL TIEMPO | C22042200023 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2022-04-22 | 19800 | keep | 0 | Apr | 2022 | 0.013486 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-22 08:40 | 2022-04-22 15:18 | 20 | 006:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO Y SE REEMPLAZO 20 PIES DE SECUNDARIA | S22042200053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 398 | 2022-04-22 | 7960 | keep | 0 | Apr | 2022 | 0.0054215 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-22 08:46 | 2022-04-22 08:48 | 143 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22042200000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-04-22 | 286 | keep | 0 | Apr | 2022 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-04-22 08:46 | 2022-04-22 08:48 | 1086 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 80% DE LA CARGA POR EL 1404-06 | S22042200000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-04-22 | 2172 | keep | 0 | Apr | 2022 | 0.0014793 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
SAN JUAN | 2022-04-22 08:48 | 2022-04-22 17:36 | 1 | 008:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN RISER Y SE CERRO PUENTE DE LINEA A CAJA | S22042200096 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 528 | 2022-04-22 | 528 | keep | 0 | Apr | 2022 | 0.00035962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-22 09:04 | 2022-04-22 13:26 | 30 | 004:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | A22042200057 | New_Event | Wire Down | Include | Include | Equipment | 262 | 2022-04-22 | 7860 | keep | 0 | Apr | 2022 | 0.0053534 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-04-22 09:12 | 2022-04-22 14:49 | 8 | 005:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO EN XMR Y REPARAR SECUNDARIA AVERIADA. | R22042200059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 337 | 2022-04-22 | 2696 | keep | 0 | Apr | 2022 | 0.0018362 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-22 09:13 | 2022-04-22 11:15 | 1 | 002:02 | P | NO SE REPORTO CAUSA | 2 X 80 EN RISER NO CAUSA | C22042200034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-04-22 | 122 | keep | 0 | Apr | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-22 09:16 | 2022-04-22 11:02 | 60 | 001:46 | P | DESGANCHE | 2X65 EN C/L & SE RETIRO BAMBUA DE LAS LINEAS | B22042200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-04-22 | 6360 | keep | 0 | Apr | 2022 | 0.0043318 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-04-22 09:30 | 2022-04-22 10:00 | 8 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22042200147 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-04-22 | 240 | keep | 0 | Apr | 2022 | 0.00016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-22 09:32 | 2022-04-22 16:00 | 70 | 006:28 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO DEL SU-1 AL SU-2 | B22041900037 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 388 | 2022-04-22 | 27160 | keep | 0 | Apr | 2022 | 0.018499 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-04-22 09:39 | 2022-04-22 16:32 | 100 | 006:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 50 C/L REEMPLAZO 3 CAJAS Y PARARRAYOS | C22042200040 | New_Event | Cutout Failure | Include | Include | Equipment | 413 | 2022-04-22 | 41300 | keep | 0 | Apr | 2022 | 0.028129 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-22 09:40 | 2022-04-22 09:45 | 164 | 000:05 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL CARGA POR EL 1531-02 | S22042200066 | New_Event |  |  | Include | Wildlife | 5 | 2022-04-22 | 820 | keep | 0 | Apr | 2022 | 0.0005585 | 0.0001117 | Momentary | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2022-04-22 09:40 | 2022-04-22 09:45 | 716 | 000:05 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA EL 1421-02 | S22042200066 | New_Event |  |  | Include | Wildlife | 5 | 2022-04-22 | 3580 | keep | 0 | Apr | 2022 | 0.0024383 | 0.00048766 | Momentary | FALSE | FALSE | Not_TMED_Event | 716
BAYAMON | 2022-04-22 09:45 | 2022-04-22 16:00 | 55 | 006:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIERON MACHETES Y SE SECCIONALIZO EL 1531-02 PARA REALIZAR DESGANCHE, REEMPLAZAR 3 JUEGOS DE DISCOS Y CERRAR PUENTE EN EL TRONCAL A CAUSA DE CRUCE POR IGUANA CARGA POR EL 1531-02 | S22042200066 | Partial_restoration |  |  | Include | Wildlife | 375 | 2022-04-22 | 20625 | keep | 0 | Apr | 2022 | 0.014048 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-22 09:45 | 2022-04-22 16:00 | 174 | 006:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIERON MACHETES Y SE SECCIONALIZO EL 1531-02 PARA REALIZAR DESGANCHE, REEMPLAZAR 3 JUEGOS DE DISCOS Y CERRAR PUENTE EN EL TRONCAL A CAUSA DE CRUCE POR IGUANA LLEVA EL 1421-02 | S22042200066 | Partial_restoration |  |  | Include | Wildlife | 375 | 2022-04-22 | 65250 | keep | 0 | Apr | 2022 | 0.044441 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-04-22 09:48 | 2022-04-22 09:49 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042200052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2926 | keep | 0 | Apr | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
CANOVANAS | 2022-04-22 09:50 | 2022-04-22 14:38 | 65 | 004:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22042200069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-04-22 | 18720 | keep | 0 | Apr | 2022 | 0.01275 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-04-22 09:50 | 2022-04-22 11:25 | 35 | 001:35 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22042200015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-04-22 | 3325 | keep | 0 | Apr | 2022 | 0.0022646 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-04-22 09:51 | 2022-04-22 12:47 | 162 | 002:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S22042200061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2022-04-22 | 28512 | keep | 0 | Apr | 2022 | 0.019419 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
BAYAMON | 2022-04-22 09:51 | 2022-04-22 14:30 | 244 | 004:39 | P | ESTRUCTURA AVERIADA | 3 X 50 EN CORTE DE LINEA HACIA BOMBA DE AAA Y 1 X 100 EN CORTE DE LINEA PRINCIPAL SE DEJO POSTE PRIMARIO PODRIDO PARTIDO EN EL MONTE SECCIONALIZADO | B22042200053 | New_Event | Defective Pole | Include | Include | Equipment | 279 | 2022-04-22 | 68076 | keep | 0 | Apr | 2022 | 0.046366 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
VEGA BAJA | 2022-04-22 09:59 | 2022-04-22 11:47 | 6 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1X30 EN C/L MAL TIEMPO | B22042200056 | New_Event | Bad Weather | Include | Include | Weather | 108 | 2022-04-22 | 648 | keep | 0 | Apr | 2022 | 0.00044135 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-04-22 10:05 | 2022-04-22 12:46 | 6 | 002:41 | P | DESGANCHE | 1 X 10 EN XMR SE REALIZO DESGANCHE DE PALMA | R22042200071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-04-22 | 966 | keep | 0 | Apr | 2022 | 0.00065794 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-04-22 10:05 | 2022-04-22 13:00 | 10 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | P22042200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2022-04-22 | 1750 | keep | 0 | Apr | 2022 | 0.0011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-04-22 10:08 | 2022-04-22 12:41 | 3 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA Y SE REPARO BAJANTE PRIMARIO | R22042200073 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2022-04-22 | 459 | keep | 0 | Apr | 2022 | 0.00031262 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-04-22 10:24 | 2022-04-22 11:47 | 117 | 001:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P22042200020 | New_Event |  |  | Include | Wildlife | 83 | 2022-04-22 | 9711 | keep | 0 | Apr | 2022 | 0.0066141 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
BARRANQUITAS | 2022-04-22 10:27 | 2022-04-22 11:18 | 4 | 000:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN XMR MAL TEMPO | C22042200051 | New_Event | Bad Weather | Include | Include | Weather | 51 | 2022-04-22 | 204 | keep | 0 | Apr | 2022 | 0.00013894 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-04-22 10:40 | 2022-04-22 13:30 | 35 | 002:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P22042200024 | New_Event |  |  | Include | Wildlife | 170 | 2022-04-22 | 5950 | keep | 0 | Apr | 2022 | 0.0040525 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-04-22 10:45 | 2022-04-22 10:46 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042200064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 4702 | keep | 0 | Apr | 2022 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
CAGUAS | 2022-04-22 10:49 | 2022-04-22 14:02 | 8 | 003:13 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHAR Y REPARAR BAJANTE SECUNDARIO | C22042200059 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 193 | 2022-04-22 | 1544 | keep | 0 | Apr | 2022 | 0.0010516 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-04-22 10:50 | 2022-04-22 16:27 | 80 | 005:37 | P | DESGANCHE | 1 X 65 EN C/L | C22042200060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2022-04-22 | 26960 | keep | 0 | Apr | 2022 | 0.018362 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-04-22 10:53 | 2022-04-23 10:47 | 1 | 023:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C22042200061 | New_Event |  |  | Include | Wildlife | 1434 | 2022-04-22 | 1434 | keep | 0 | Apr | 2022 | 0.00097669 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-22 11:09 | 2022-04-22 11:10 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR - LLEVA 95% DEL 1717-02 | B22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 5961 | keep | 0 | Apr | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-04-22 11:09 | 2022-04-22 11:10 | 865 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE - 95% DE SU CARGA TRANSFERIDA AL 1713-05 | B22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 865 | keep | 0 | Apr | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
MAYAGÃœEZ | 2022-04-22 11:21 | 2022-04-23 10:35 | 50 | 023:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22042200029 | New_Event | Cutout Failure | Include | Include | Equipment | 1394 | 2022-04-22 | 69700 | keep | 0 | Apr | 2022 | 0.047472 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-04-22 11:30 | 2022-04-22 14:50 | 21 | 003:20 | P | ERROR HUMANO | ALAMBRE PRIMARIO EN EL PISO COMPAÃ‘IA PRIVADA XPERT REALIZANDO DESGANCHE TUMBARON LINEA PRIMARIA | P22042200037 | New_Event | Human Error | Include | Include | Other | 200 | 2022-04-22 | 4200 | keep | 0 | Apr | 2022 | 0.0028606 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CAGUAS | 2022-04-22 11:32 | 2022-04-22 16:45 | 40 | 005:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22042200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2022-04-22 | 12520 | keep | 0 | Apr | 2022 | 0.0085273 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-04-22 11:34 | 2022-04-22 15:00 | 1 | 003:26 | P | PARARRAYOS DEFECTUOSO | 2 X 10 C/L SE REEMPLAZO 2 PARARRAYOS | C22042200073 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 206 | 2022-04-22 | 206 | keep | 0 | Apr | 2022 | 0.00014031 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-22 11:45 | 2022-04-22 15:00 | 1 | 003:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042200030 | New_Event | Bad Weather | Include | Include | Weather | 195 | 2022-04-22 | 195 | keep | 0 | Apr | 2022 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-22 11:56 | 2022-04-22 15:00 | 103 | 003:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22042200082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-04-22 | 18952 | keep | 0 | Apr | 2022 | 0.012908 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
BAYAMON | 2022-04-22 12:10 | 2022-04-22 12:11 | 3597 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | B22042200000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-22 | 3597 | keep | 0 | Apr | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
UTUADO | 2022-04-22 12:10 | 2022-04-22 14:15 | 25 | 002:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE VIENTO | A22042200067 | New_Event | Bad Weather | Include | Include | Weather | 125 | 2022-04-22 | 3125 | keep | 0 | Apr | 2022 | 0.0021284 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-22 12:11 | 2022-04-22 15:16 | 175 | 003:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1 X 30 EN CORTES DE LINEA CRUCE POR AVE | B22042200083 | 1st_after_momentary |  |  | Include | Wildlife | 185 | 2022-04-22 | 32375 | keep | 0 | Apr | 2022 | 0.02205 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
SAN JUAN | 2022-04-22 12:14 | 2022-04-22 19:02 | 70 | 006:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINA A CAJA | S22042200084 | New_Event | Wire Down | Include | Include | Equipment | 408 | 2022-04-22 | 28560 | keep | 0 | Apr | 2022 | 0.019452 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-04-22 12:22 | 2022-04-22 14:28 | 5 | 002:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 XMR CRUCE POR AVE | C22042200084 | New_Event |  |  | Include | Wildlife | 126 | 2022-04-22 | 630 | keep | 0 | Apr | 2022 | 0.00042909 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-04-22 12:28 | 2022-04-22 14:02 | 8 | 001:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR AVE | C22042200089 | New_Event |  |  | Include | Wildlife | 94 | 2022-04-22 | 752 | keep | 0 | Apr | 2022 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-04-22 12:29 | 2022-04-22 13:23 | 2039 | 000:54 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA EN EL PISO | P22042200035 | New_Event | Wire Down | Include | Include | Equipment | 54 | 2022-04-22 | 110106 | keep | 0 | Apr | 2022 | 0.074993 | 0.0013888 | Sustained | FALSE | FALSE | Not_TMED_Event | 2039
BAYAMON | 2022-04-22 12:49 | 2022-04-22 15:23 | 7 | 002:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA QUEMADO | B22042200092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 154 | 2022-04-22 | 1078 | keep | 0 | Apr | 2022 | 0.00073422 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-04-22 13:16 | 2022-04-22 13:17 | 1084 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 1084 | keep | 0 | Apr | 2022 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
CAGUAS | 2022-04-22 13:20 | 2022-04-22 13:21 | 1084 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22042200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 1084 | keep | 0 | Apr | 2022 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
HUMACAO | 2022-04-22 13:21 | 2022-04-22 13:22 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | NO CAUSA | C22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 3025 | keep | 0 | Apr | 2022 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
CAGUAS | 2022-04-22 13:21 | 2022-04-22 15:13 | 1084 | 001:52 | T | NO SE REPORTO CAUSA | EN SERVICIO, SE PATRULLO Y NO SE ENCONTRO CAUSA | C22042200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 112 | 2022-04-22 | 121408 | keep | 0 | Apr | 2022 | 0.08269 | 0.00073831 | Sustained | FALSE | FALSE | Not_TMED_Event | 1084
PONCE | 2022-04-22 13:23 | 2022-04-23 15:44 | 3 | 026:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA DEL PISO Y SE REEMPLAZO MACHETE AVERIADO | P22042200061 | Partial_restoration | Wire Down | Include | Include | Equipment | 1581 | 2022-04-22 | 4743 | keep | 0 | Apr | 2022 | 0.0032304 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-22 13:24 | 2022-04-22 14:03 | 15 | 000:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22042200100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2022-04-22 | 585 | keep | 0 | Apr | 2022 | 0.00039844 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-04-22 13:29 | 2022-04-22 15:30 | 80 | 002:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22042200101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-04-22 | 9680 | keep | 0 | Apr | 2022 | 0.006593 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-22 13:33 | 2022-04-22 19:46 | 55 | 006:13 | P | DESGANCHE | 1 X 50 Y 2 X 40 EN CORTES DE LINEA SE RETIRO BAMBUAS DE LA LINEA | B22042200099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2022-04-22 | 20515 | keep | 0 | Apr | 2022 | 0.013973 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2022-04-22 13:35 | 2022-04-22 15:41 | 200 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 Y 2 X 50 EN CORTES DE LINEA POR FUERTE VIENTO | A22042200077 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2022-04-22 | 25200 | keep | 0 | Apr | 2022 | 0.017164 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-04-22 13:42 | 2022-04-22 17:18 | 7 | 003:36 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 10 EN XMR REEMPLAZO POSTE SECUNDARIO PARTIDO | C22042200086 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 216 | 2022-04-22 | 1512 | keep | 0 | Apr | 2022 | 0.0010298 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-04-22 13:53 | 2022-04-22 16:37 | 3 | 002:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | A22042200083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 164 | 2022-04-22 | 492 | keep | 0 | Apr | 2022 | 0.0003351 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2022-04-22 13:55 | 2022-04-22 14:35 | 8 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO DE CONEXIONES EN BARRA SECUNDARIA TIPO PEDESTAL | P22042200050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-04-22 | 320 | keep | 0 | Apr | 2022 | 0.00021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-04-22 13:57 | 2022-04-23 00:16 | 35 | 010:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M22042200044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 619 | 2022-04-22 | 21665 | keep | 0 | Apr | 2022 | 0.014756 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2022-04-22 14:02 | 2022-04-22 16:00 | 13 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X15 EN TRANSFORMADOR PAJARO CRUZO FASE | P22042200058 | New_Event |  |  | Include | Wildlife | 118 | 2022-04-22 | 1534 | keep | 0 | Apr | 2022 | 0.0010448 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2022-04-22 14:08 | 2022-04-22 18:20 | 35 | 004:12 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO PARTIDO | A22042200088 | New_Event | Defective Pole | Include | Include | Equipment | 252 | 2022-04-22 | 8820 | keep | 0 | Apr | 2022 | 0.0060073 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-04-22 14:20 | 2022-04-22 14:45 | 1 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M22042200037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2022-04-22 | 25 | keep | 0 | Apr | 2022 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-22 14:22 | 2022-04-23 12:51 | 7 | 022:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARRO BAJANTE SECUNDARIO ABIERTO | S22042200102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1349 | 2022-04-22 | 9443 | keep | 0 | Apr | 2022 | 0.0064316 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-04-22 14:30 | 2022-04-23 20:38 | 6 | 030:08 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B22042200142 | New_Event | Defective Pole | Include | Include | Equipment | 1808 | 2022-04-22 | 10848 | keep | 0 | Apr | 2022 | 0.0073885 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-22 14:34 | 2022-04-22 18:30 | 50 | 003:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042200073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-04-22 | 11800 | keep | 0 | Apr | 2022 | 0.0080369 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-22 14:36 | 2022-04-23 08:41 | 1 | 018:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN CORTE DE LINEA AVE CRUZO LINEAS | M22042200047 | New_Event |  |  | Include | Wildlife | 1085 | 2022-04-22 | 1085 | keep | 0 | Apr | 2022 | 0.00073899 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-22 14:43 | 2022-04-22 14:45 | 906 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | C22042200118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-22 | 1812 | keep | 0 | Apr | 2022 | 0.0012341 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
AGUADILLA | 2022-04-22 15:10 | 2022-04-23 00:52 | 100 | 009:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES LLUVIA | M22042200052 | New_Event | Bad Weather | Include | Include | Weather | 582 | 2022-04-22 | 58200 | keep | 0 | Apr | 2022 | 0.03964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-22 15:12 | 2022-04-22 15:13 | 3005 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22042200125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 3005 | keep | 0 | Apr | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
PONCE | 2022-04-22 15:12 | 2022-04-22 20:45 | 8 | 005:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P22042200070 | New_Event | Cutout Failure | Include | Include | Equipment | 333 | 2022-04-22 | 2664 | keep | 0 | Apr | 2022 | 0.0018144 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-04-22 15:13 | 2022-04-22 19:02 | 487 | 003:49 | P | NO SE REPORTO CAUSA | CERRO I/R 3006-3F NO CAUSA | C22042200148 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-04-22 | 111523 | keep | 0 | Apr | 2022 | 0.075958 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-22 15:32 | 2022-04-22 18:36 | 40 | 003:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | C22042200133 | New_Event |  |  | Include | Wildlife | 184 | 2022-04-22 | 7360 | keep | 0 | Apr | 2022 | 0.0050129 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-22 15:33 | 2022-04-22 15:34 | 614 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | R22042200114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 614 | keep | 0 | Apr | 2022 | 0.00041819 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
CAGUAS | 2022-04-22 15:33 | 2022-04-23 12:05 | 16 | 020:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON 100'DE LINEA ZULFATADA | C22042200135 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1232 | 2022-04-22 | 19712 | keep | 0 | Apr | 2022 | 0.013426 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2022-04-22 15:36 | 2022-04-22 18:20 | 26 | 002:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M22042200057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 164 | 2022-04-22 | 4264 | keep | 0 | Apr | 2022 | 0.0029042 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2022-04-22 15:51 | 2022-04-22 16:36 | 3046 | 000:45 | T | TRANSFORMADOR AVERIADO | SE ABRIO MACHETES EN AVE. MONSERRATE ESQ CARR 190 | R22042200111 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2022-04-22 | 137070 | keep | 0 | Apr | 2022 | 0.093358 | 0.0020746 | Sustained | FALSE | FALSE | Not_TMED_Event | 3046
PONCE | 2022-04-22 15:56 | 2022-04-22 15:57 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2113 | keep | 0 | Apr | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2022-04-22 15:59 | 2022-04-22 17:53 | 2113 | 001:54 | T | OTRAS CAUSAS | FUERTE LLUVIA | P22042200073 | New_Event | Other Causes | Include | Include | Other | 114 | 2022-04-22 | 240882 | keep | 0 | Apr | 2022 | 0.16406 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
BAYAMON | 2022-04-22 16:00 | 2022-04-22 17:29 | 164 | 001:29 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE CERRARON MACHETES 100% EN SERVICIO CARGA POR EL 1531-02 | S22042200066 | New_Event |  |  | Include | Wildlife | 89 | 2022-04-22 | 14596 | keep | 0 | Apr | 2022 | 0.0099413 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2022-04-22 16:00 | 2022-04-22 17:29 | 645 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE CERRARON MACHETES 100% EN SERVICIO LLEVA EL 1421-02 | S22042200066 | New_Event |  |  | Include | Wildlife | 89 | 2022-04-22 | 57405 | keep | 0 | Apr | 2022 | 0.039098 | 0.00043931 | Sustained | FALSE | FALSE | Not_TMED_Event | 645
CANOVANAS | 2022-04-22 16:01 | 2022-04-22 16:02 | 418 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 2402-02 SOLO CON 10% DE SU CARGA, PERO LLEVANDO 60% DEL 2404-05 Y 100% 2404-08 | R22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 418 | keep | 0 | Apr | 2022 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
CANOVANAS | 2022-04-22 16:01 | 2022-04-22 16:02 | 2078 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 2402-02 SOLO CON 10% DE SU CARGA, PERO LLEVANDO 60% DEL 2404-05 Y 100% 2404-08 | R22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2078 | keep | 0 | Apr | 2022 | 0.0014153 | 0.0014153 | Momentary | FALSE | FALSE | Not_TMED_Event | 2078
CANOVANAS | 2022-04-22 16:01 | 2022-04-22 16:02 | 2675 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2402-02 SOLO CON 10% DE SU CARGA, PERO LLEVANDO 60% DEL 2404-05 Y 100% 2404-08 | R22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2675 | keep | 0 | Apr | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2022-04-22 16:02 | 2022-04-22 20:56 | 150 | 004:54 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | R22042200200 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 294 | 2022-04-22 | 44100 | keep | 0 | Apr | 2022 | 0.030036 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-04-22 16:07 | 2022-04-23 01:05 | 15 | 008:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1X25 EN TRANSFORMADOR POR MAL TIEMPO | M22047220006 | New_Event | Bad Weather | Include | Include | Weather | 538 | 2022-04-22 | 8070 | keep | 0 | Apr | 2022 | 0.0054964 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-04-22 16:13 | 2022-04-22 20:07 | 253 | 003:54 | T | MAL TIEMPO/RAYOS/WET ASH | BREAKER FUERA DE SERVICIO FUERTE LLUVIA | P22042200078 | New_Event | Bad Weather | Include | Include | Weather | 234 | 2022-04-22 | 59202 | keep | 0 | Apr | 2022 | 0.040322 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
MAYAGÃœEZ | 2022-04-22 16:32 | 2022-04-22 23:25 | 60 | 006:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR LLUVIA | M22042200064 | New_Event | Bad Weather | Include | Include | Weather | 413 | 2022-04-22 | 24780 | keep | 0 | Apr | 2022 | 0.016878 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-22 16:36 | 2022-04-22 17:39 | 1523 | 001:03 | P | TRANSFORMADOR AVERIADO | SECCIONALIZARON TRAMO DEL SU-22A @ PROVISONAL AEREO CON FUSIBLE FUNDIDO. | R22042200111 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 63 | 2022-04-22 | 95949 | keep | 0 | Apr | 2022 | 0.06535 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-22 16:43 | 2022-04-22 18:22 | 22 | 001:39 | P | DESGANCHE | 1 X 30 EN C/L | C22042200155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-04-22 | 2178 | keep | 0 | Apr | 2022 | 0.0014834 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2022-04-22 16:48 | 2022-04-22 16:49 | 1185 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6801-02 QUE ESTA LLEVANDO LA CARGA DEL 6801-01 | M22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 1185 | keep | 0 | Apr | 2022 | 0.0008071 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
MAYAGÃœEZ | 2022-04-22 16:48 | 2022-04-22 16:49 | 1584 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 1584 | keep | 0 | Apr | 2022 | 0.0010789 | 0.0010789 | Momentary | FALSE | FALSE | Not_TMED_Event | 1584
ARECIBO | 2022-04-22 16:50 | 2022-04-22 19:40 | 100 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | A22042200099 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2022-04-22 | 17000 | keep | 0 | Apr | 2022 | 0.011579 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 2100 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 14700 | keep | 0 | Apr | 2022 | 0.010012 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 922 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 6454 | keep | 0 | Apr | 2022 | 0.0043958 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 1676 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 11732 | keep | 0 | Apr | 2022 | 0.0079906 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 2844 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 19908 | keep | 0 | Apr | 2022 | 0.013559 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 2775 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 19425 | keep | 0 | Apr | 2022 | 0.01323 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 1457 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 10199 | keep | 0 | Apr | 2022 | 0.0069465 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 1086 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 7602 | keep | 0 | Apr | 2022 | 0.0051777 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 2134 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 14938 | keep | 0 | Apr | 2022 | 0.010174 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 1464 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 10248 | keep | 0 | Apr | 2022 | 0.0069799 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 1833 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 12831 | keep | 0 | Apr | 2022 | 0.0087391 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 1565 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 10955 | keep | 0 | Apr | 2022 | 0.0074614 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-04-22 17:06 | 2022-04-22 17:13 | 977 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042200107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-04-22 | 6839 | keep | 0 | Apr | 2022 | 0.004658 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
CAGUAS | 2022-04-22 17:09 | 2022-04-22 19:49 | 50 | 002:40 | P | NO SE REPORTO CAUSA | X 65 EN C/L | C22042200161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2022-04-22 | 8000 | keep | 0 | Apr | 2022 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-04-22 17:11 | 2022-04-22 21:04 | 60 | 003:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR CRUCE POR CHANGO | B22042200125 | New_Event |  |  | Include | Wildlife | 233 | 2022-04-22 | 13980 | keep | 0 | Apr | 2022 | 0.0095217 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-04-22 17:24 | 2022-04-23 06:08 | 9 | 012:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | C22042200184 | New_Event |  |  | Include | Wildlife | 764 | 2022-04-22 | 6876 | keep | 0 | Apr | 2022 | 0.0046832 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-04-22 17:28 | 2022-04-23 10:40 | 1 | 017:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE PRIMARIO PARTIDO EN MONTURA DE TRANSFORMADOR Y 1 X 15 EN MONTURA | P22042200112 | New_Event | Wire Down | Include | Include | Equipment | 1032 | 2022-04-22 | 1032 | keep | 0 | Apr | 2022 | 0.00070289 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-04-22 17:29 | 2022-04-22 19:55 | 250 | 002:26 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | C22042200164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-04-22 | 36500 | keep | 0 | Apr | 2022 | 0.02486 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
HUMACAO | 2022-04-22 17:31 | 2022-04-22 18:52 | 60 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 Y 1 X 30 EN C/L CRUCE X AVE | C22042200166 | New_Event |  |  | Include | Wildlife | 81 | 2022-04-22 | 4860 | keep | 0 | Apr | 2022 | 0.0033101 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-22 17:34 | 2022-04-22 17:39 | 164 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA CARGA POR EL 1531-02 | S22042200134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-04-22 | 820 | keep | 0 | Apr | 2022 | 0.0005585 | 0.0001117 | Momentary | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2022-04-22 17:34 | 2022-04-22 17:39 | 716 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA LLEVA 1421-02 | S22042200134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-04-22 | 3580 | keep | 0 | Apr | 2022 | 0.0024383 | 0.00048766 | Momentary | FALSE | FALSE | Not_TMED_Event | 716
SAN JUAN | 2022-04-22 17:39 | 2022-04-22 18:22 | 50 | 000:43 | P | TRANSFORMADOR AVERIADO | REEMPLAZO 1 X 40 EN SU-22A @ PROVISIONAL Y SECCIONALIZO T-242 AVERIADO. | R22042200111 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 43 | 2022-04-22 | 2150 | keep | 0 | Apr | 2022 | 0.0014644 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-04-22 17:51 | 2022-04-22 18:54 | 5 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | B22042200135 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2022-04-22 | 315 | keep | 0 | Apr | 2022 | 0.00021455 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-04-22 17:53 | 2022-04-22 18:25 | 1697 | 000:32 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | MACHETES ABIERTOS SECCIONALIZANDO AVERIA EN VS#16 | P22042200122 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 32 | 2022-04-22 | 54304 | keep | 0 | Apr | 2022 | 0.036986 | 0.0011558 | Sustained | FALSE | FALSE | Not_TMED_Event | 1697
SAN JUAN | 2022-04-22 17:58 | 2022-04-22 18:52 | 10 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA TRASPATIO | R22042200196 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-04-22 | 540 | keep | 0 | Apr | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-22 18:01 | 2022-04-23 13:22 | 90 | 019:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22042200172 | New_Event | Bad Weather | Include | Include | Weather | 1161 | 2022-04-22 | 104490 | keep | 0 | Apr | 2022 | 0.071168 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-04-22 18:03 | 2022-04-22 20:38 | 50 | 002:35 | P | DESGANCHE | 1 X 25 EN RISER Y 1 X 50 EN C/L DESGANCHE | S22042200137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-04-22 | 7750 | keep | 0 | Apr | 2022 | 0.0052785 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-22 18:06 | 2022-04-22 20:09 | 50 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE SALIDA EN CAJA DEL PROVISIONAL AEREO | R22042200198 | New_Event | Wire Down | Include | Include | Equipment | 123 | 2022-04-22 | 6150 | keep | 0 | Apr | 2022 | 0.0041887 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-22 18:12 | 2022-04-22 18:34 | 1 | 000:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A RISER | S22042200138 | New_Event | Wire Down | Include | Include | Equipment | 22 | 2022-04-22 | 22 | keep | 0 | Apr | 2022 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-22 18:15 | 2022-04-22 21:55 | 105 | 003:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22042200138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2022-04-22 | 23100 | keep | 0 | Apr | 2022 | 0.015733 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
ARECIBO | 2022-04-22 18:20 | 2022-04-22 18:55 | 10 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | A22042200065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-04-22 | 350 | keep | 0 | Apr | 2022 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-22 18:22 | 2022-04-22 21:55 | 20 | 003:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO T-242 AVERIADO Y CERRO PUENTE EN PROVISIONAL AEREO @ T-242 | R22042200111 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 213 | 2022-04-22 | 4260 | keep | 0 | Apr | 2022 | 0.0029015 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-22 18:25 | 2022-04-22 18:42 | 4 | 000:17 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | AVERIA EN VS#16 | P22042200126 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 17 | 2022-04-22 | 68 | keep | 0 | Apr | 2022 | 4.6314e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-22 18:30 | 2022-04-22 20:15 | 67 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P22042200127 | New_Event |  |  | Include | Wildlife | 105 | 2022-04-22 | 7035 | keep | 0 | Apr | 2022 | 0.0047915 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
PONCE | 2022-04-22 18:42 | 2022-04-22 18:44 | 2113 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ENCONTRO AVERIA EN VS#16 | P22042200133 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2022-04-22 | 4226 | keep | 0 | Apr | 2022 | 0.0028783 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-22 18:44 | 2022-04-23 13:07 | 3 | 018:23 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZARON TRES TERMINACIONES TIPO PISTOLAS UNA BARRA SECA Y PARARRAYO EN RISER EN MH#16 | P22042200126 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1103 | 2022-04-22 | 3309 | keep | 0 | Apr | 2022 | 0.0022537 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-04-22 18:55 | 2022-04-23 17:09 | 1 | 022:14 | P | CABLE SOTERRADO AVERIADO | SE ABRE RISER PARA RETIRAR CARGA A LA LINEA PARA REPARAR AVERIA SOTERRADA | P22042200134 | New_Event | UG Cable Fault | Include | Include | Equipment | 1334 | 2022-04-22 | 1334 | keep | 0 | Apr | 2022 | 0.00090858 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-04-22 18:58 | 2022-04-22 22:40 | 1877 | 003:42 | P | ESTRUCTURA AVERIADA | CON EL CG-220422-01 SE REEMPLAZO 2 POSTES PRIMARIOS APROVECHANDO LA VIA LIBRE DE LA SUBESTACION | C22042200065 | New_Event | Defective Pole | Include | Include | Equipment | 222 | 2022-04-22 | 416694 | keep | 0 | Apr | 2022 | 0.28381 | 0.0012784 | Sustained | FALSE | FALSE | Not_TMED_Event | 1877
MAYAGÃœEZ | 2022-04-22 19:04 | 2022-04-23 02:23 | 100 | 007:19 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR LLUVIAS | M22042200081 | New_Event | Bad Weather | Include | Include | Weather | 439 | 2022-04-22 | 43900 | keep | 0 | Apr | 2022 | 0.0299 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-04-22 19:18 | 2022-04-22 21:45 | 650 | 002:27 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | A22042200122 | New_Event | Bad Weather | Include | Include | Weather | 147 | 2022-04-22 | 95550 | keep | 0 | Apr | 2022 | 0.065079 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
BAYAMON | 2022-04-22 19:28 | 2022-04-23 12:43 | 1 | 017:15 | P | OTRAS CAUSAS | PROA - SE DESCONECTO Y SE ENTREGO AL CLIENTE PARA QUE REPARE/CERTIFIQUE | B22042200149 | New_Event | Other Causes | Include | Include | Other | 1035 | 2022-04-22 | 1035 | keep | 0 | Apr | 2022 | 0.00070493 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-22 19:28 | 2022-04-23 01:54 | 8 | 006:26 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | B22042200148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2022-04-22 | 3088 | keep | 0 | Apr | 2022 | 0.0021032 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-04-22 20:17 | 2022-04-23 10:47 | 8 | 014:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR IGUANA CRUZO LINEAS | M22042200088 | New_Event |  |  | Include | Wildlife | 870 | 2022-04-22 | 6960 | keep | 0 | Apr | 2022 | 0.0047404 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-04-22 20:40 | 2022-04-22 20:41 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 1859 | keep | 0 | Apr | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
CANOVANAS | 2022-04-22 20:56 | 2022-04-22 20:57 | 418 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 2402-02 SOLO CON 10% DE SU CARGA, PERO LLEVANDO 60% DEL 2404-05 Y 100% 2404-08 | R22042200000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 418 | keep | 0 | Apr | 2022 | 0.0002847 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-22 20:56 | 2022-04-22 20:57 | 2078 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 2402-02 SOLO CON 10% DE SU CARGA, PERO LLEVANDO 60% DEL 2404-05 Y 100% 2404-08 | R22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2078 | keep | 0 | Apr | 2022 | 0.0014153 | 0.0014153 | Momentary | FALSE | FALSE | Not_TMED_Event | 2078
CANOVANAS | 2022-04-22 20:56 | 2022-04-22 20:57 | 2675 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2402-02 SOLO CON 10% DE SU CARGA, PERO LLEVANDO 60% DEL 2404-05 Y 100% 2404-08 | R22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2675 | keep | 0 | Apr | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2022-04-22 20:57 | 2022-04-22 21:36 | 150 | 000:39 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | R22042200200 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-04-22 | 5850 | keep | 0 | Apr | 2022 | 0.0039844 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-04-22 21:02 | 2022-04-22 22:33 | 22 | 001:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22045220013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-04-22 | 2002 | keep | 0 | Apr | 2022 | 0.0013636 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CANOVANAS | 2022-04-22 21:51 | 2022-04-22 21:52 | 418 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 2402-02 SOLO CON 10% DE SU CARGA, PERO LLEVANDO 60% DEL 2404-05 Y 100% 2404-08 | R22042200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 418 | keep | 0 | Apr | 2022 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
CANOVANAS | 2022-04-22 21:51 | 2022-04-22 21:52 | 2078 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 2402-02 SOLO CON 10% DE SU CARGA, PERO LLEVANDO 60% DEL 2404-05 Y 100% 2404-08 | R22042200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2078 | keep | 0 | Apr | 2022 | 0.0014153 | 0.0014153 | Momentary | FALSE | FALSE | Not_TMED_Event | 2078
CANOVANAS | 2022-04-22 21:51 | 2022-04-22 21:52 | 2675 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2402-02 SOLO CON 10% DE SU CARGA, PERO LLEVANDO 60% DEL 2404-05 Y 100% 2404-08 | R22042200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-22 | 2675 | keep | 0 | Apr | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2022-04-22 21:57 | 2022-04-22 23:11 | 311 | 001:14 | P | DESGANCHE | 2 X 100 EN RISER SE REALIZO DESGANCH Y SE RETIRO CULEBRA DE PARARRAYO | R22042200221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-04-22 | 23014 | keep | 0 | Apr | 2022 | 0.015675 | 0.00021182 | Sustained | FALSE | FALSE | Not_TMED_Event | 311
SAN JUAN | 2022-04-22 22:10 | 2022-04-23 00:14 | 176 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22042200157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-04-22 | 21824 | keep | 0 | Apr | 2022 | 0.014864 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
BARRANQUITAS | 2022-04-22 22:18 | 2022-04-23 10:14 | 3 | 011:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C22042200193 | New_Event | Bad Weather | Include | Include | Weather | 716 | 2022-04-22 | 2148 | keep | 0 | Apr | 2022 | 0.001463 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-04-22 22:23 | 2022-04-23 08:37 | 8 | 010:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X15 EN XMER POR AVE EN LA PRIMARIA | S22042200159 | New_Event |  |  | Include | Wildlife | 614 | 2022-04-22 | 4912 | keep | 0 | Apr | 2022 | 0.0033455 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-04-22 23:41 | 2022-04-23 14:16 | 40 | 014:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22042200160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 875 | 2022-04-22 | 35000 | keep | 0 | Apr | 2022 | 0.023838 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-04-23 00:58 | 2022-04-23 23:48 | 50 | 022:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN C/L SE REPARO ALAMBRE PRIMARIO PARTIDO | P22042300007 | New_Event | Wire Down | Include | Include | Equipment | 1370 | 2022-04-23 | 68500 | keep | 0 | Apr | 2022 | 0.046655 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-23 02:32 | 2022-04-23 11:18 | 45 | 008:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P22042300009 | New_Event |  |  | Include | Wildlife | 526 | 2022-04-23 | 23670 | keep | 0 | Apr | 2022 | 0.016122 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2022-04-23 02:58 | 2022-04-23 09:15 | 650 | 006:17 | T | DESGANCHE | SE CERRO INTERRUPTOR MANUAL NO RTU SE RETIRO BAMBUS SOBRE LAS LINEAS | A22042300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2022-04-23 | 245050 | keep | 0 | Apr | 2022 | 0.1669 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
MAYAGÃœEZ | 2022-04-23 04:49 | 2022-04-23 10:03 | 20 | 005:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2022-04-23 | 6280 | keep | 0 | Apr | 2022 | 0.0042773 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-04-23 05:32 | 2022-04-23 09:22 | 12 | 003:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO ZULFATADO | C22042300001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 230 | 2022-04-23 | 2760 | keep | 0 | Apr | 2022 | 0.0018798 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-04-23 06:41 | 2022-04-23 13:03 | 1 | 006:22 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22042300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2022-04-23 | 382 | keep | 0 | Apr | 2022 | 0.00026018 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-23 06:42 | 2022-04-23 12:17 | 200 | 005:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22042300010 | New_Event | Bad Weather | Include | Include | Weather | 335 | 2022-04-23 | 67000 | keep | 0 | Apr | 2022 | 0.045633 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-04-23 06:51 | 2022-04-23 22:05 | 7 | 015:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 37.5 KVA | A22042300012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 914 | 2022-04-23 | 6398 | keep | 0 | Apr | 2022 | 0.0043576 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-04-23 06:54 | 2022-04-23 06:55 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-23 | 2379 | keep | 0 | Apr | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
CANOVANAS | 2022-04-23 07:04 | 2022-04-23 07:05 | 3699 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO CARGA A TRAVES DEL 2402-04 | C22042300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-23 | 3699 | keep | 0 | Apr | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
BARRANQUITAS | 2022-04-23 07:16 | 2022-04-23 17:11 | 50 | 009:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP PARTIDO | C22042300003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 595 | 2022-04-23 | 29750 | keep | 0 | Apr | 2022 | 0.020263 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-23 07:21 | 2022-04-23 10:20 | 100 | 002:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22042300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-04-23 | 17900 | keep | 0 | Apr | 2022 | 0.012192 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-23 07:24 | 2022-04-23 12:13 | 1 | 004:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA INDICO NO IDENTIFICO CAUSA | M22042300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 289 | 2022-04-23 | 289 | keep | 0 | Apr | 2022 | 0.00019684 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-23 07:28 | 2022-04-23 11:56 | 100 | 004:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X80 EN C/L (POR AVE EN LA PRIMARIA) | B22042300004 | New_Event |  |  | Include | Wildlife | 268 | 2022-04-23 | 26800 | keep | 0 | Apr | 2022 | 0.018253 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-04-23 07:35 | 2022-04-23 09:20 | 25 | 001:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22042300019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-04-23 | 2625 | keep | 0 | Apr | 2022 | 0.0017879 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-23 07:40 | 2022-04-23 09:08 | 1717 | 001:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22042300016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-04-23 | 151096 | keep | 0 | Apr | 2022 | 0.10291 | 0.0011694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1717
PONCE | 2022-04-23 07:40 | 2022-04-23 09:08 | 974 | 001:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22042300016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-04-23 | 85712 | keep | 0 | Apr | 2022 | 0.058378 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
PONCE | 2022-04-23 07:40 | 2022-04-23 09:08 | 1905 | 001:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22042300016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-04-23 | 167640 | keep | 0 | Apr | 2022 | 0.11418 | 0.0012975 | Sustained | FALSE | FALSE | Not_TMED_Event | 1905
PONCE | 2022-04-23 07:40 | 2022-04-23 09:08 | 1262 | 001:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22042300016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-04-23 | 111056 | keep | 0 | Apr | 2022 | 0.07564 | 0.00085954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1262
PONCE | 2022-04-23 07:40 | 2022-04-23 09:08 | 200 | 001:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22042300016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-04-23 | 17600 | keep | 0 | Apr | 2022 | 0.011987 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-04-23 07:40 | 2022-04-23 09:08 | 222 | 001:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22042300017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-04-23 | 19536 | keep | 0 | Apr | 2022 | 0.013306 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
PONCE | 2022-04-23 07:40 | 2022-04-23 09:08 | 537 | 001:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22042300017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-04-23 | 47256 | keep | 0 | Apr | 2022 | 0.032186 | 0.00036575 | Sustained | FALSE | FALSE | Not_TMED_Event | 537
SAN JUAN | 2022-04-23 07:44 | 2022-04-23 07:45 | 2179 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R22042300010 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-23 | 2179 | keep | 0 | Apr | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CAGUAS | 2022-04-23 07:49 | 2022-04-23 11:50 | 99 | 004:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22042300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-04-23 | 23859 | keep | 0 | Apr | 2022 | 0.01625 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
CANOVANAS | 2022-04-23 07:53 | 2022-04-23 07:54 | 3699 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22042300000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-04-23 | 3699 | keep | 0 | Apr | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2022-04-23 07:54 | 2022-04-23 09:12 | 80 | 001:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L Y 1 X 80 EN RISER SE RETIRO AVE | R22042300002 | 1st_after_momentary |  |  | Include | Wildlife | 78 | 2022-04-23 | 6240 | keep | 0 | Apr | 2022 | 0.00425 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-23 08:04 | 2022-04-23 10:51 | 2179 | 002:47 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ALIMENTADOR ENTRO EN SERVICIO 40% | R22042300000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 167 | 2022-04-23 | 363893 | keep | 0 | Apr | 2022 | 0.24785 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2022-04-23 08:05 | 2022-04-23 08:53 | 2708 | 000:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-04-23 | 129984 | keep | 0 | Apr | 2022 | 0.088532 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-04-23 08:05 | 2022-04-23 08:53 | 2524 | 000:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-04-23 | 121152 | keep | 0 | Apr | 2022 | 0.082516 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-04-23 08:05 | 2022-04-23 08:53 | 1648 | 000:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-04-23 | 79104 | keep | 0 | Apr | 2022 | 0.053877 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
MAYAGÃœEZ | 2022-04-23 08:06 | 2022-04-24 14:50 | 232 | 030:44 | P | DESGANCHE | SE REPARO LINEA PRIMARIA ROTA A CAUSA DE DESGANCHE SE RETIRO RAMAS SOBRE LAS LINEAS | M22042300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1844 | 2022-04-23 | 427808 | keep | 0 | Apr | 2022 | 0.29138 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
MAYAGÃœEZ | 2022-04-23 08:07 | 2022-04-23 09:14 | 75 | 001:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22042300005 | New_Event | Wire Down | Include | Include | Equipment | 67 | 2022-04-23 | 5025 | keep | 0 | Apr | 2022 | 0.0034225 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-04-23 08:17 | 2022-04-23 11:20 | 1 | 003:03 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22042300022 | New_Event | Bad Weather | Include | Include | Weather | 183 | 2022-04-23 | 183 | keep | 0 | Apr | 2022 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-23 08:32 | 2022-04-23 13:43 | 300 | 005:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22042300024 | New_Event | Wire Down | Include | Include | Equipment | 311 | 2022-04-23 | 93300 | keep | 0 | Apr | 2022 | 0.063546 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-04-23 08:47 | 2022-04-23 08:48 | 1210 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-23 | 1210 | keep | 0 | Apr | 2022 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
BAYAMON | 2022-04-23 08:50 | 2022-04-23 08:51 | 70 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X65 EN C/L SE RETIRO GLOBO DE HELIO QUE CRUZO LAS LINEAS | B22042300001 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-23 | 70 | keep | 0 | Apr | 2022 | 4.7677e-05 | 4.7677e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-04-23 09:09 | 2022-04-23 09:11 | 1370 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22042300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-23 | 2740 | keep | 0 | Apr | 2022 | 0.0018662 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
CAGUAS | 2022-04-23 09:18 | 2022-04-23 09:19 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-23 | 1565 | keep | 0 | Apr | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-04-23 09:18 | 2022-04-23 09:19 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-23 | 976 | keep | 0 | Apr | 2022 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-04-23 09:18 | 2022-04-23 09:19 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-23 | 548 | keep | 0 | Apr | 2022 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-04-23 09:18 | 2022-04-23 09:19 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-23 | 315 | keep | 0 | Apr | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-04-23 09:18 | 2022-04-23 09:19 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-23 | 870 | keep | 0 | Apr | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-04-23 09:18 | 2022-04-23 09:19 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-23 | 2906 | keep | 0 | Apr | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-04-23 09:18 | 2022-04-23 09:19 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22042300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-23 | 2343 | keep | 0 | Apr | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
CAGUAS | 2022-04-23 09:21 | 2022-04-23 10:34 | 2 | 001:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C22042300037 | New_Event | Cutout Failure | Include | Include | Equipment | 73 | 2022-04-23 | 146 | keep | 0 | Apr | 2022 | 9.944e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-04-23 09:36 | 2022-04-23 10:57 | 308 | 001:21 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETES SECCIONALIZAR Y REALIZAR PRUEBA INTERRUPTOR | A22042300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-04-23 | 24948 | keep | 0 | Apr | 2022 | 0.016992 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:15 | 2100 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-04-23 | 54600 | keep | 0 | Apr | 2022 | 0.037188 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:15 | 922 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-04-23 | 23972 | keep | 0 | Apr | 2022 | 0.016327 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:15 | 1676 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-04-23 | 43576 | keep | 0 | Apr | 2022 | 0.029679 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:15 | 2844 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-04-23 | 73944 | keep | 0 | Apr | 2022 | 0.050363 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:15 | 2775 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-04-23 | 72150 | keep | 0 | Apr | 2022 | 0.049141 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:15 | 1457 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-04-23 | 37882 | keep | 0 | Apr | 2022 | 0.025801 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:15 | 1086 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-04-23 | 28236 | keep | 0 | Apr | 2022 | 0.019231 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:15 | 2134 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-04-23 | 55484 | keep | 0 | Apr | 2022 | 0.03779 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:47 | 1464 | 000:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 58 | 2022-04-23 | 84912 | keep | 0 | Apr | 2022 | 0.057833 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:47 | 1833 | 000:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 58 | 2022-04-23 | 106314 | keep | 0 | Apr | 2022 | 0.07241 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:47 | 1565 | 000:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 58 | 2022-04-23 | 90770 | keep | 0 | Apr | 2022 | 0.061823 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-04-23 09:49 | 2022-04-23 10:47 | 977 | 000:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22042300094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 58 | 2022-04-23 | 56666 | keep | 0 | Apr | 2022 | 0.038595 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
SAN JUAN | 2022-04-23 10:04 | 2022-04-23 12:42 | 11 | 002:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN XMR SE CERRO PUENTE ABIERTO PRIMARIO DE CAJA A LINEA Y CONDUCTOR SECUNDARIO EN EL SUELO A CAUSA DE IMPACTO DE CAMION | C22042300024 | New_Event |  |  | Include | Wildlife | 158 | 2022-04-23 | 1738 | keep | 0 | Apr | 2022 | 0.0011837 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-04-23 10:35 | 2022-04-23 11:59 | 1 | 001:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE CON AVE | C22042300028 | New_Event |  |  | Include | Wildlife | 84 | 2022-04-23 | 84 | keep | 0 | Apr | 2022 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-04-23 10:35 | 2022-04-23 14:10 | 50 | 003:35 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN TRONCAL DEL ALIMENTADOR | M22042300058 | New_Event | Wire Down | Include | Include | Equipment | 215 | 2022-04-23 | 10750 | keep | 0 | Apr | 2022 | 0.0073218 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-04-23 10:36 | 2022-04-23 13:00 | 50 | 002:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR SE REMPLAZO AISLADOR | R22042300245 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 144 | 2022-04-23 | 7200 | keep | 0 | Apr | 2022 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-04-23 10:42 | 2022-04-23 10:44 | 215 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22042300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-23 | 430 | keep | 0 | Apr | 2022 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-04-23 10:44 | 2022-04-23 14:02 | 40 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22042300010 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 198 | 2022-04-23 | 7920 | keep | 0 | Apr | 2022 | 0.0053943 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-23 10:45 | 2022-04-23 11:05 | 1 | 000:20 | P | DESGANCHE | 2 X 50 EN RISER DESGANCHE | S22042300021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-04-23 | 20 | keep | 0 | Apr | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-04-23 10:47 | 2022-04-23 12:40 | 3 | 001:53 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22042300254 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-04-23 | 339 | keep | 0 | Apr | 2022 | 0.00023089 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-04-23 10:51 | 2022-04-23 11:15 | 1305 | 000:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALIEMNTADOR SECCIONALIZADO | R22042300000 | New_Event | Wire Down | Include | Include | Equipment | 24 | 2022-04-23 | 31320 | keep | 0 | Apr | 2022 | 0.021332 | 0.00088883 | Sustained | FALSE | FALSE | Not_TMED_Event | 1305
ARECIBO | 2022-04-23 10:57 | 2022-04-23 12:15 | 150 | 001:18 | P | NO SE REPORTO CAUSA | SE PATRULLO NO SE ENCONTRO CAUSA SE CERRARON LOS MACHETES TODO EN SERVICIO | A22042300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-04-23 | 11700 | keep | 0 | Apr | 2022 | 0.0079688 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-04-23 11:14 | 2022-04-23 11:15 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-23 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
SAN JUAN | 2022-04-23 11:15 | 2022-04-23 11:35 | 2179 | 000:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO ALIMENTADOR SECCIONALIZADO 60% EN SERVICIO | R22042300000 | Additional_clients | Wire Down | Include | Include | Equipment | 20 | 2022-04-23 | 43580 | keep | 0 | Apr | 2022 | 0.029682 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-23 11:27 | 2022-04-23 19:52 | 70 | 008:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042300068 | New_Event | Bad Weather | Include | Include | Weather | 505 | 2022-04-23 | 35350 | keep | 0 | Apr | 2022 | 0.024077 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-04-23 11:32 | 2022-04-23 11:46 | 2450 | 000:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C22042300032 | New_Event |  |  | Include | Wildlife | 14 | 2022-04-23 | 34300 | keep | 0 | Apr | 2022 | 0.023362 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
SAN JUAN | 2022-04-23 11:35 | 2022-04-23 11:47 | 1305 | 000:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALIMENTADOR SECCIONALIZADO | R22042300000 | Partial_restoration | Wire Down | Include | Include | Equipment | 12 | 2022-04-23 | 15660 | keep | 0 | Apr | 2022 | 0.010666 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-23 11:40 | 2022-04-23 15:00 | 21 | 003:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22042300030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2022-04-23 | 4200 | keep | 0 | Apr | 2022 | 0.0028606 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
HUMACAO | 2022-04-23 11:46 | 2022-04-23 11:47 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22042300031 | Partial_restoration |  |  | Include | Wildlife | 1 | 2022-04-23 | 2450 | keep | 0 | Apr | 2022 | 0.0016687 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-23 11:47 | 2022-04-23 12:05 | 2179 | 000:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ALIMENTADOR 50% EN SERVICIO | R22042300000 | Additional_clients | Wire Down | Include | Include | Equipment | 18 | 2022-04-23 | 39222 | keep | 0 | Apr | 2022 | 0.026714 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-04-23 11:47 | 2022-04-23 15:13 | 2450 | 003:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C22042300032 | 1st_after_momentary |  |  | Include | Wildlife | 206 | 2022-04-23 | 504700 | keep | 0 | Apr | 2022 | 0.34375 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
SAN JUAN | 2022-04-23 12:05 | 2022-04-23 13:25 | 1088 | 001:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALIMENTADOR SECCIONALIZADO, SE REALIZARON OPERACIONES EN SERVICIO 80% | R22042300000 | Partial_restoration | Wire Down | Include | Include | Equipment | 80 | 2022-04-23 | 87040 | keep | 0 | Apr | 2022 | 0.059283 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-23 12:20 | 2022-04-24 15:30 | 80 | 027:10 | P | DESGANCHE | 1 X 65 3 X 50 Y 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22042300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1630 | 2022-04-23 | 130400 | keep | 0 | Apr | 2022 | 0.088815 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-04-23 12:25 | 2022-04-23 14:02 | 80 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C22042300037 | New_Event |  |  | Include | Wildlife | 97 | 2022-04-23 | 7760 | keep | 0 | Apr | 2022 | 0.0052853 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-23 12:26 | 2022-04-24 14:10 | 1 | 025:44 | P | HERRAJE ROTO O PODRIDO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | A22042300045 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1544 | 2022-04-23 | 1544 | keep | 0 | Apr | 2022 | 0.0010516 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-23 12:41 | 2022-04-23 13:31 | 1105 | 000:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA ROTA | A22042300046 | New_Event | Wire Down | Include | Include | Equipment | 50 | 2022-04-23 | 55250 | keep | 0 | Apr | 2022 | 0.037631 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
AGUADILLA | 2022-04-23 12:44 | 2022-04-24 05:32 | 100 | 016:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA POR AISLADOR SAFADO | M22042300080 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1008 | 2022-04-23 | 100800 | keep | 0 | Apr | 2022 | 0.068654 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-04-23 12:46 | 2022-04-23 15:55 | 100 | 003:09 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042300081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2022-04-23 | 18900 | keep | 0 | Apr | 2022 | 0.012873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-23 12:47 | 2022-04-23 13:37 | 8 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRA DE PEDESTAL ZAFADA | C22042300040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-04-23 | 400 | keep | 0 | Apr | 2022 | 0.00027244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-04-23 12:55 | 2022-04-23 12:56 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042300086 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-23 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
ARECIBO | 2022-04-23 12:55 | 2022-04-23 14:54 | 12 | 001:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CAUSO AVERIA | A22042300050 | New_Event |  |  | Include | Wildlife | 119 | 2022-04-23 | 1428 | keep | 0 | Apr | 2022 | 0.0009726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-04-23 13:02 | 2022-04-23 18:35 | 25 | 005:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22042300052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2022-04-23 | 8325 | keep | 0 | Apr | 2022 | 0.0056701 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-23 13:07 | 2022-04-23 15:29 | 18 | 002:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042300093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-04-23 | 2556 | keep | 0 | Apr | 2022 | 0.0017409 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2022-04-23 13:24 | 2022-04-23 17:17 | 150 | 003:53 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042300097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-04-23 | 34950 | keep | 0 | Apr | 2022 | 0.023804 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-04-23 13:25 | 2022-04-23 15:55 | 436 | 002:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR SAFADO SOBRE CRUCETA, REEMPLAZO AISLADOR ROTO Y SE CERRO MACHETES. | R22042300014 | Partial_restoration | Wire Down | Include | Include | Equipment | 150 | 2022-04-23 | 65400 | keep | 0 | Apr | 2022 | 0.044544 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-23 13:31 | 2022-04-23 16:23 | 300 | 002:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22042300046 | Partial_restoration | Wire Down | Include | Include | Equipment | 172 | 2022-04-23 | 51600 | keep | 0 | Apr | 2022 | 0.035145 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-23 13:42 | 2022-04-23 14:34 | 20 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA | R22042200213 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2022-04-23 | 1040 | keep | 0 | Apr | 2022 | 0.00070834 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-04-23 13:45 | 2022-04-24 01:28 | 20 | 011:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | M22042300163 | New_Event | Bad Weather | Include | Include | Weather | 703 | 2022-04-23 | 14060 | keep | 0 | Apr | 2022 | 0.0095762 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-23 14:09 | 2022-04-23 15:25 | 20 | 001:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA LLUVIAS | C22042300049 | New_Event | Bad Weather | Include | Include | Weather | 76 | 2022-04-23 | 1520 | keep | 0 | Apr | 2022 | 0.0010353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-04-23 14:10 | 2022-04-23 15:25 | 154 | 001:15 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE ABIERTO EN TRONCAL DEL ALIMENTADOR | M22042300116 | Additional_clients | Wire Down | Include | Include | Equipment | 75 | 2022-04-23 | 11550 | keep | 0 | Apr | 2022 | 0.0078667 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-23 14:27 | 2022-04-23 17:20 | 30 | 002:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22042300121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-04-23 | 5190 | keep | 0 | Apr | 2022 | 0.0035349 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-04-23 14:50 | 2022-04-24 08:07 | 65 | 017:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22042300050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1037 | 2022-04-23 | 67405 | keep | 0 | Apr | 2022 | 0.045909 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-04-23 14:50 | 2022-04-24 14:44 | 100 | 023:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22042300127 | New_Event | Cutout Failure | Include | Include | Equipment | 1434 | 2022-04-23 | 143400 | keep | 0 | Apr | 2022 | 0.097669 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-04-23 15:00 | 2022-04-23 18:10 | 13 | 003:10 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REEMPLAZAR POSTE SECUNDARIO PARTIDO | P22042300141 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 190 | 2022-04-23 | 2470 | keep | 0 | Apr | 2022 | 0.0016823 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2022-04-23 15:01 | 2022-04-23 18:52 | 60 | 003:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | C22042300052 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 231 | 2022-04-23 | 13860 | keep | 0 | Apr | 2022 | 0.00944 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-04-23 15:06 | 2022-04-23 19:40 | 80 | 004:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE DE ARBOL Y RETEZO LINEA | R22042300342 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2022-04-23 | 21920 | keep | 0 | Apr | 2022 | 0.01493 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-23 15:06 | 2022-04-23 18:03 | 100 | 002:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C.L SE CERRO PUENTE | B22042300020 | New_Event | Wire Down | Include | Include | Equipment | 177 | 2022-04-23 | 17700 | keep | 0 | Apr | 2022 | 0.012055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-04-23 15:21 | 2022-04-23 16:56 | 15 | 001:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | P22042300144 | New_Event | Cutout Failure | Include | Include | Equipment | 95 | 2022-04-23 | 1425 | keep | 0 | Apr | 2022 | 0.00097056 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-04-23 15:26 | 2022-04-23 15:27 | 1902 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R22042300000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-04-23 | 1902 | keep | 0 | Apr | 2022 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2022-04-23 15:27 | 2022-04-23 19:37 | 412 | 004:10 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO | R22042300362 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 250 | 2022-04-23 | 103000 | keep | 0 | Apr | 2022 | 0.070153 | 0.00028061 | Sustained | FALSE | FALSE | Not_TMED_Event | 412
CANOVANAS | 2022-04-23 15:41 | 2022-04-23 21:34 | 40 | 005:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22042300347 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2022-04-23 | 14120 | keep | 0 | Apr | 2022 | 0.0096171 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-23 15:56 | 2022-04-23 16:33 | 3 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | C22042300056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-04-23 | 111 | keep | 0 | Apr | 2022 | 7.5602e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-04-23 16:00 | 2022-04-23 17:22 | 1 | 001:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN CORTE DE LINEA | P22042300152 | New_Event | Wire Down | Include | Include | Equipment | 82 | 2022-04-23 | 82 | keep | 0 | Apr | 2022 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-04-23 16:25 | 2022-04-24 10:15 | 10 | 017:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | R22042300359 | New_Event | Cutout Failure | Include | Include | Equipment | 1070 | 2022-04-23 | 10700 | keep | 0 | Apr | 2022 | 0.0072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-23 16:29 | 2022-04-23 16:31 | 329 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVA 90% DE LA CARGA DEL 3015-06 | C22042300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-23 | 658 | keep | 0 | Apr | 2022 | 0.00044816 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2022-04-23 16:29 | 2022-04-23 16:31 | 1207 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL 90% DE LA CARGA POR EL 3006-01 | C22042300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-23 | 2414 | keep | 0 | Apr | 2022 | 0.0016442 | 0.00082208 | Momentary | FALSE | FALSE | Not_TMED_Event | 1207
BAYAMON | 2022-04-23 17:12 | 2022-04-23 17:13 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | 3 RECIERRES EN SERVICIO 1709-01 SPARE LLEVANDO 1720-07 | B22042300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-23 | 6136 | keep | 0 | Apr | 2022 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2022-04-23 17:26 | 2022-04-23 18:50 | 1 | 001:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S22042300039 | New_Event | Wire Down | Include | Include | Equipment | 84 | 2022-04-23 | 84 | keep | 0 | Apr | 2022 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-23 17:29 | 2022-04-23 20:22 | 65 | 002:53 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22042300064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2022-04-23 | 11245 | keep | 0 | Apr | 2022 | 0.0076589 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
GUAYAMA | 2022-04-23 17:30 | 2022-04-23 18:29 | 1 | 000:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P22042300161 | New_Event | Wire Down | Include | Include | Equipment | 59 | 2022-04-23 | 59 | keep | 0 | Apr | 2022 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-23 17:31 | 2022-04-24 09:10 | 20 | 015:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES DE XMR | B22042300038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 939 | 2022-04-23 | 18780 | keep | 0 | Apr | 2022 | 0.012791 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-04-23 17:43 | 2022-04-24 09:08 | 4 | 015:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE X AVE | R22042300373 | New_Event |  |  | Include | Wildlife | 925 | 2022-04-23 | 3700 | keep | 0 | Apr | 2022 | 0.0025201 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-04-23 17:48 | 2022-04-24 15:19 | 1 | 021:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22042300161 | New_Event | Bad Weather | Include | Include | Weather | 1291 | 2022-04-23 | 1291 | keep | 0 | Apr | 2022 | 0.00087929 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-23 17:49 | 2022-04-23 21:39 | 13 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22042300042 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2022-04-23 | 2990 | keep | 0 | Apr | 2022 | 0.0020365 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2022-04-23 17:56 | 2022-04-24 08:14 | 37 | 014:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE ENCONTRO CAUSA | P22042300156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 858 | 2022-04-23 | 31746 | keep | 0 | Apr | 2022 | 0.021622 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
GUAYAMA | 2022-04-23 18:08 | 2022-04-23 19:42 | 40 | 001:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE | P22042300158 | New_Event |  |  | Include | Wildlife | 94 | 2022-04-23 | 3760 | keep | 0 | Apr | 2022 | 0.0025609 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-04-23 19:00 | 2022-04-24 09:28 | 35 | 014:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22042300089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 868 | 2022-04-23 | 30380 | keep | 0 | Apr | 2022 | 0.020692 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-04-23 19:01 | 2022-04-24 04:47 | 150 | 009:46 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA Y SE REEMPLAZO POSTE PARTIDO | WR-6107356 | New_Event | Defective Pole | Include | Include | Equipment | 586 | 2022-04-23 | 87900 | keep | 0 | Apr | 2022 | 0.059868 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-04-23 19:01 | 2022-04-23 21:19 | 200 | 002:18 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PARTIDO ABIENDO PUENTES Y SE CERRO C/L | B22042300044 | New_Event | Defective Pole | Include | Include | Equipment | 138 | 2022-04-23 | 27600 | keep | 0 | Apr | 2022 | 0.018798 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-04-23 19:42 | 2022-04-24 17:01 | 75 | 021:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS ABIERTOS | M22042300177 | New_Event | Wire Down | Include | Include | Equipment | 1279 | 2022-04-23 | 95925 | keep | 0 | Apr | 2022 | 0.065334 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-04-23 19:42 | 2022-04-23 22:21 | 10 | 002:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22042300177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-04-23 | 1590 | keep | 0 | Apr | 2022 | 0.0010829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-23 19:48 | 2022-04-24 19:41 | 1 | 023:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R22042300412 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1433 | 2022-04-23 | 1433 | keep | 0 | Apr | 2022 | 0.00097601 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-04-23 19:48 | 2022-04-24 20:51 | 234 | 025:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA TRONCAL | R22042300414 | New_Event | Wire Down | Include | Include | Equipment | 1503 | 2022-04-23 | 351702 | keep | 0 | Apr | 2022 | 0.23954 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
BARRANQUITAS | 2022-04-23 21:03 | 2022-04-24 11:12 | 100 | 014:09 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C22042300108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 849 | 2022-04-23 | 84900 | keep | 0 | Apr | 2022 | 0.057825 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-04-23 21:10 | 2022-04-24 11:25 | 11 | 014:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER NO CAUSA | P22042300171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 855 | 2022-04-23 | 9405 | keep | 0 | Apr | 2022 | 0.0064057 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2022-04-23 21:19 | 2022-04-24 16:19 | 60 | 019:00 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTE PARTIDO | B22042300044 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1140 | 2022-04-23 | 68400 | keep | 0 | Apr | 2022 | 0.046587 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-23 21:43 | 2022-04-23 21:44 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042300198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-23 | 990 | keep | 0 | Apr | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BAYAMON | 2022-04-23 22:41 | 2022-04-24 09:45 | 300 | 011:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X100 EN RISER & SE RETIRO ROEDOR (RATA) | B22042300044 | New_Event |  |  | Include | Wildlife | 664 | 2022-04-23 | 199200 | keep | 0 | Apr | 2022 | 0.13567 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
UTUADO | 2022-04-23 22:57 | 2022-04-24 08:45 | 15 | 009:48 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22042300087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 588 | 2022-04-23 | 8820 | keep | 0 | Apr | 2022 | 0.0060073 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-04-23 23:05 | 2022-04-24 02:20 | 200 | 003:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN C/L LAGARTO | R22042300421 | New_Event |  |  | Include | Wildlife | 195 | 2022-04-23 | 39000 | keep | 0 | Apr | 2022 | 0.026563 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-04-23 23:08 | 2022-04-24 12:49 | 50 | 013:41 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R22042300422 | New_Event | Vegetation Contact | Include | Include | Vegetation | 821 | 2022-04-23 | 41050 | keep | 0 | Apr | 2022 | 0.027959 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-23 23:15 | 2022-04-24 | 30 | 000:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M22042300205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2022-04-23 | 1350 | keep | 0 | Apr | 2022 | 0.00091948 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-24 01:30 | 2022-04-24 03:25 | 85 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | M22042400001 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2022-04-24 | 9775 | keep | 0 | Apr | 2022 | 0.0066577 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
ARECIBO | 2022-04-24 02:23 | 2022-04-24 02:24 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22042400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
MAYAGÃœEZ | 2022-04-24 02:36 | 2022-04-24 02:37 | 1417 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 1417 | keep | 0 | Apr | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
BAYAMON | 2022-04-24 03:59 | 2022-04-24 07:26 | 65 | 003:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X40 EN C/L & SE REMPLAZO TRAMO PRIMARIO | B22042400008 | New_Event | Wire Down | Include | Include | Equipment | 207 | 2022-04-24 | 13455 | keep | 0 | Apr | 2022 | 0.0091641 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-04-24 04:12 | 2022-04-25 10:17 | 15 | 030:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M22042400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1805 | 2022-04-24 | 27075 | keep | 0 | Apr | 2022 | 0.018441 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-04-24 04:56 | 2022-04-24 11:16 | 45 | 006:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22042400004 | New_Event |  |  | Include | Wildlife | 380 | 2022-04-24 | 17100 | keep | 0 | Apr | 2022 | 0.011647 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
GUAYAMA | 2022-04-24 05:14 | 2022-04-24 06:12 | 60 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE LLEVO LINEA AL AISLADOR 1 X 65 EN CORTE DE LINEA VEHICULO IMPACTO POSTE | P22042400001 | New_Event |  |  | Include | Wildlife | 58 | 2022-04-24 | 3480 | keep | 0 | Apr | 2022 | 0.0023702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-04-24 05:23 | 2022-04-24 09:59 | 18 | 004:36 | P | NO SE REPORTO CAUSA | 1X15 EN XMER | B22042400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2022-04-24 | 4968 | keep | 0 | Apr | 2022 | 0.0033837 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-04-24 05:36 | 2022-04-24 05:37 | 2076 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 1718-03 LLEVA 40% DEL 1710-05 | B22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 2076 | keep | 0 | Apr | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-04-24 05:36 | 2022-04-24 05:37 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1718-03 LLEVA 40% DEL 1710-05 | B22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 2605 | keep | 0 | Apr | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
MAYAGÃœEZ | 2022-04-24 05:54 | 2022-04-24 08:26 | 150 | 002:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 25 EN RISER AVE CRUZO FASE A TIERRA | M22042400005 | New_Event |  |  | Include | Wildlife | 152 | 2022-04-24 | 22800 | keep | 0 | Apr | 2022 | 0.015529 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-04-24 05:59 | 2022-04-24 06:00 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 1310 | keep | 0 | Apr | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
HUMACAO | 2022-04-24 06:10 | 2022-04-24 10:16 | 1 | 004:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER Y 1 X 20 EN EQUIPO DE MEDICION CRUCE POR AVE | C22042400007 | New_Event |  |  | Include | Wildlife | 246 | 2022-04-24 | 246 | keep | 0 | Apr | 2022 | 0.00016755 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-04-24 06:12 | 2022-04-24 06:13 | 4132 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P22042400004 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-24 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-04-24 06:12 | 2022-04-24 06:13 | 4279 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P22042400004 | Additional_clients |  |  | Include | Wildlife | 1 | 2022-04-24 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-04-24 06:12 | 2022-04-24 06:13 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-04-24 06:13 | 2022-04-24 09:52 | 60 | 003:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE LLEVO LINEA AL AISLADOR 1 X 65 EN CORTE DE LINEA VEHICULO IMPACTO POSTE | P22042400001 | 1st_after_momentary |  |  | Include | Wildlife | 219 | 2022-04-24 | 13140 | keep | 0 | Apr | 2022 | 0.0089496 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-24 06:22 | 2022-04-24 06:25 | 199 | 000:03 | T | ERROR HUMANO | DISPARO DE INTERRUPTOR POR ERROR EN OPERACION DE MACHETE DE VIA LIBRE EN BAYAMON D2022-00319 | S22042400003 | New_Event | Human Error | Include | Include | Other | 3 | 2022-04-24 | 597 | keep | 0 | Apr | 2022 | 0.00040661 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2022-04-24 06:25 | 2022-04-24 07:14 | 66 | 000:49 | P | ERROR HUMANO | ERROR EN OPERACION DE MACHETE DE VIA LIBRE EN BAYAMON D2022-00319 | S22042400003 | 1st_after_momentary | Human Error | Include | Include | Other | 49 | 2022-04-24 | 3234 | keep | 0 | Apr | 2022 | 0.0022027 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2022-04-24 06:39 | 2022-04-24 06:40 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 2147 | keep | 0 | Apr | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BARRANQUITAS | 2022-04-24 06:50 | 2022-04-24 12:40 | 100 | 005:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22042400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 350 | 2022-04-24 | 35000 | keep | 0 | Apr | 2022 | 0.023838 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-24 07:08 | 2022-04-24 07:09 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1909-08 | B22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 2435 | keep | 0 | Apr | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-04-24 07:08 | 2022-04-24 07:09 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 1907-05 | B22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 2956 | keep | 0 | Apr | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
YAUCO | 2022-04-24 07:13 | 2022-04-24 07:14 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 1352 | keep | 0 | Apr | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
PONCE | 2022-04-24 07:56 | 2022-04-24 07:57 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 3114 | keep | 0 | Apr | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2022-04-24 07:56 | 2022-04-24 21:30 | 10 | 013:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO QUEMADO | M22042400012 | New_Event | Wire Down | Include | Include | Equipment | 814 | 2022-04-24 | 8140 | keep | 0 | Apr | 2022 | 0.0055441 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-24 08:00 | 2022-04-24 08:01 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 5062 | keep | 0 | Apr | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2022-04-24 08:01 | 2022-04-24 19:00 | 16 | 010:59 | P | NO SE REPORTO CAUSA | 1 X 12 EN TRANSFORMADOR | R22042400013 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 659 | 2022-04-24 | 10544 | keep | 0 | Apr | 2022 | 0.0071815 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
FAJARDO | 2022-04-24 08:24 | 2022-04-24 08:26 | 1839 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | R22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-24 | 3678 | keep | 0 | Apr | 2022 | 0.0025051 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2022-04-24 08:24 | 2022-04-24 08:26 | 1778 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | R22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-24 | 3556 | keep | 0 | Apr | 2022 | 0.002422 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2022-04-24 08:24 | 2022-04-24 08:26 | 1376 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | R22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-24 | 2752 | keep | 0 | Apr | 2022 | 0.0018744 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2022-04-24 08:24 | 2022-04-24 08:26 | 293 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | R22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-24 | 586 | keep | 0 | Apr | 2022 | 0.00039912 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2022-04-24 08:24 | 2022-04-24 08:26 | 1215 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | R22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-24 | 2430 | keep | 0 | Apr | 2022 | 0.0016551 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
SAN JUAN | 2022-04-24 08:44 | 2022-04-24 09:17 | 356 | 000:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN GERARDO | S22042400011 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 33 | 2022-04-24 | 11748 | keep | 0 | Apr | 2022 | 0.0080015 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
SAN JUAN | 2022-04-24 08:44 | 2022-04-24 09:17 | 790 | 000:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN GERARDO | S22042400010 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 33 | 2022-04-24 | 26070 | keep | 0 | Apr | 2022 | 0.017756 | 0.00053807 | Sustained | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2022-04-24 08:44 | 2022-04-24 09:17 | 29 | 000:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN GERARDO | S22042400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 33 | 2022-04-24 | 957 | keep | 0 | Apr | 2022 | 0.00065181 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2022-04-24 08:44 | 2022-04-24 09:17 | 390 | 000:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN GERARDO | S22042400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 33 | 2022-04-24 | 12870 | keep | 0 | Apr | 2022 | 0.0087657 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2022-04-24 08:44 | 2022-04-24 09:17 | 291 | 000:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN GERARDO | S22042400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 33 | 2022-04-24 | 9603 | keep | 0 | Apr | 2022 | 0.0065406 | 0.0001982 | Sustained | FALSE | FALSE | Not_TMED_Event | 291
MAYAGÃœEZ | 2022-04-24 08:46 | 2022-04-24 08:47 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13400 | M22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-24 | 1339 | keep | 0 | Apr | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-04-24 08:46 | 2022-04-24 08:47 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13400 | M22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-24 | 470 | keep | 0 | Apr | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-04-24 08:46 | 2022-04-24 08:47 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13400 | M22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-24 | 2483 | keep | 0 | Apr | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-04-24 08:46 | 2022-04-24 08:47 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13400 | M22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-24 | 2190 | keep | 0 | Apr | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-04-24 08:46 | 2022-04-24 08:47 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13400 | M22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-24 | 3006 | keep | 0 | Apr | 2022 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-04-24 08:46 | 2022-04-24 08:47 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13400 | M22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-24 | 179 | keep | 0 | Apr | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
FAJARDO | 2022-04-24 08:57 | 2022-04-24 08:58 | 2041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22042400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 2041 | keep | 0 | Apr | 2022 | 0.0013901 | 0.0013901 | Momentary | FALSE | FALSE | Not_TMED_Event | 2041
ARECIBO | 2022-04-24 09:00 | 2022-04-24 11:02 | 40 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE DETECTO LA CAUSA | A22042400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-04-24 | 4880 | keep | 0 | Apr | 2022 | 0.0033237 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-24 09:26 | 2022-04-24 18:06 | 60 | 008:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA REPARO CONDUCTOR SAFADO | C22042400028 | New_Event | Wire Down | Include | Include | Equipment | 520 | 2022-04-24 | 31200 | keep | 0 | Apr | 2022 | 0.02125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-24 09:50 | 2022-04-24 09:51 | 179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042400031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 179 | keep | 0 | Apr | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
GUAYAMA | 2022-04-24 09:52 | 2022-04-24 09:53 | 4132 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P22042400023 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-04-24 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-04-24 09:52 | 2022-04-24 09:53 | 4279 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P22042400023 | Additional_clients |  |  | Include | Wildlife | 1 | 2022-04-24 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-04-24 09:52 | 2022-04-24 09:53 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P22042400023 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-24 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-04-24 09:53 | 2022-04-24 11:33 | 60 | 001:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE LLEVO LINEA AL AISLADOR 1 X 65 EN CORTE DE LINEA VEHICULO IMPACTO POSTE | P22042400001 | 1st_after_momentary |  |  | Include | Wildlife | 100 | 2022-04-24 | 6000 | keep | 0 | Apr | 2022 | 0.0040866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-04-24 09:54 | 2022-04-24 12:33 | 110 | 002:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22042400035 | New_Event |  |  | Include | Wildlife | 159 | 2022-04-24 | 17490 | keep | 0 | Apr | 2022 | 0.011912 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
FAJARDO | 2022-04-24 10:00 | 2022-04-24 18:45 | 1 | 008:45 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN BANCO DE TRANSFORMADOR Y SE RETIRO BEJUCO | R22042400012 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 525 | 2022-04-24 | 525 | keep | 0 | Apr | 2022 | 0.00035758 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-24 10:28 | 2022-04-25 08:08 | 200 | 021:40 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22042400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1300 | 2022-04-24 | 260000 | keep | 0 | Apr | 2022 | 0.17708 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-04-24 10:29 | 2022-04-24 13:02 | 1 | 002:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X15 EN XMER (POR AVE EN LAS LINEAS) | B22042400036 | New_Event |  |  | Include | Wildlife | 153 | 2022-04-24 | 153 | keep | 0 | Apr | 2022 | 0.00010421 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-24 10:29 | 2022-04-24 10:30 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042400036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
BAYAMON | 2022-04-24 10:35 | 2022-04-24 15:15 | 75 | 004:40 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ESTABLECIO GOI SJ-220424-01 PARA REPARAR CONDICION DE PUNTO CALIENTE EN EL SU-4 ENCONTRADO MIENTRAS SE TRABAJABA LA VIA LIBRE D2022-00658. | S22042400045 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 280 | 2022-04-24 | 21000 | keep | 0 | Apr | 2022 | 0.014303 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-04-24 10:44 | 2022-04-24 12:18 | 40 | 001:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA QUEMADA EN CORTE DE LINEA RECERRO EL INTERRUPTOR | A22042400006 | New_Event | Cutout Failure | Include | Include | Equipment | 94 | 2022-04-24 | 3760 | keep | 0 | Apr | 2022 | 0.0025609 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-24 10:49 | 2022-04-24 13:28 | 100 | 002:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ROTA SE ABRIO MACHETES PARA REPARAR | A22042400044 | New_Event | Wire Down | Include | Include | Equipment | 159 | 2022-04-24 | 15900 | keep | 0 | Apr | 2022 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-04-24 10:49 | 2022-04-24 13:28 | 250 | 002:39 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO IDENTIFICO CAUSA | A22042400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2022-04-24 | 39750 | keep | 0 | Apr | 2022 | 0.027074 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2022-04-24 11:11 | 2022-04-25 01:23 | 80 | 014:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22042400042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 852 | 2022-04-24 | 68160 | keep | 0 | Apr | 2022 | 0.046423 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-04-24 11:29 | 2022-04-24 11:30 | 2141 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22042400064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 2141 | keep | 0 | Apr | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
SAN JUAN | 2022-04-24 12:17 | 2022-04-24 15:31 | 100 | 003:14 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA. SE REALIZO DESGANCHE Y SE LEVANTO LINEA PRIMARIA. | R22042400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-04-24 | 19400 | keep | 0 | Apr | 2022 | 0.013213 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-24 12:18 | 2022-04-24 18:26 | 20 | 006:08 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO Y SE CERRO PUENTES | B22042400029 | New_Event | Defective Pole | Include | Include | Equipment | 368 | 2022-04-24 | 7360 | keep | 0 | Apr | 2022 | 0.0050129 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-24 12:18 | 2022-04-24 12:19 | 3654 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR CAJA QUEMADA EN CORTE DE LINEA | A22042400021 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-04-24 | 3654 | keep | 0 | Apr | 2022 | 0.0024887 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-24 12:19 | 2022-04-24 12:51 | 40 | 000:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA QUEMADA EN CORTE DE LINEA DISPARO EL INTERRUPTOR | A22042400006 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 32 | 2022-04-24 | 1280 | keep | 0 | Apr | 2022 | 0.0008718 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-04-24 12:25 | 2022-04-24 15:57 | 5 | 003:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22042400022 | New_Event | Wire Down | Include | Include | Equipment | 212 | 2022-04-24 | 1060 | keep | 0 | Apr | 2022 | 0.00072196 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-04-24 12:43 | 2022-04-24 18:32 | 40 | 005:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22042400053 | New_Event | Cutout Failure | Include | Include | Equipment | 349 | 2022-04-24 | 13960 | keep | 0 | Apr | 2022 | 0.0095081 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-24 12:47 | 2022-04-24 12:48 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042400054 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
ARECIBO | 2022-04-24 12:51 | 2022-04-24 12:54 | 3654 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DEL INTERRUPTOR CAJA QUEMADA EN CORTE DE LINEA SE VERIFICO PERSONAL FUERA DE LAS LINEAS SE CERRO INTERRUPTOR | A22042400028 | Additional_clients | Cutout Failure | Include | Include | Equipment | 3 | 2022-04-24 | 10962 | keep | 0 | Apr | 2022 | 0.0074662 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-24 12:54 | 2022-04-24 14:42 | 400 | 001:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA SE REMPLAZO CAJAS PRIMARIAS AVERIADAS | A22042400006 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 108 | 2022-04-24 | 43200 | keep | 0 | Apr | 2022 | 0.029423 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
GUAYAMA | 2022-04-24 13:09 | 2022-04-24 15:35 | 1 | 002:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER AVE CRUZO FASE | P22042400035 | New_Event |  |  | Include | Wildlife | 146 | 2022-04-24 | 146 | keep | 0 | Apr | 2022 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-24 13:15 | 2022-04-24 14:53 | 15 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22042400005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2022-04-24 | 1470 | keep | 0 | Apr | 2022 | 0.0010012 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-04-24 13:24 | 2022-04-24 16:30 | 50 | 003:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22042400036 | New_Event |  |  | Include | Wildlife | 186 | 2022-04-24 | 9300 | keep | 0 | Apr | 2022 | 0.0063342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-24 13:28 | 2022-04-24 13:29 | 830 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR LINEA PRIMARIA ROTA | A22042400038 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-04-24 | 830 | keep | 0 | Apr | 2022 | 0.00056531 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-24 13:29 | 2022-04-24 14:52 | 100 | 001:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ROTA SE ABRIO MACHETES PARA REPARAR | A22042400044 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 83 | 2022-04-24 | 8300 | keep | 0 | Apr | 2022 | 0.0056531 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-24 14:10 | 2022-04-24 14:12 | 514 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 20% POR EL 1118-10 | S22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-24 | 1028 | keep | 0 | Apr | 2022 | 0.00070017 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-04-24 14:10 | 2022-04-24 14:12 | 2782 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 20% 1111-1 | S22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-24 | 5564 | keep | 0 | Apr | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CAGUAS | 2022-04-24 14:19 | 2022-04-24 14:20 | 1084 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 1084 | keep | 0 | Apr | 2022 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
CAGUAS | 2022-04-24 14:19 | 2022-04-24 14:20 | 2907 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22042400083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 2907 | keep | 0 | Apr | 2022 | 0.0019799 | 0.0019799 | Momentary | FALSE | FALSE | Not_TMED_Event | 2907
MAYAGÃœEZ | 2022-04-24 14:21 | 2022-04-24 18:52 | 30 | 004:31 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22042400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-04-24 | 8130 | keep | 0 | Apr | 2022 | 0.0055373 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-04-24 14:32 | 2022-04-24 16:10 | 18 | 001:38 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR POR FUERTE VIENTO. SE CERRO DE FORMA MANUAL(RTU DOWN) Y QUEDO EN SERVICIO SE REEMPLAZARON 2 X 100 Y 1 X 65 EN DISTINTOS CORTE DE LINEA EL 5005-04 LLEVA LA CARGA DEL 5005-05 | P22042400040 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2022-04-24 | 1764 | keep | 0 | Apr | 2022 | 0.0012015 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-04-24 14:32 | 2022-04-24 15:38 | 494 | 001:06 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR POR FUERTE VIENTO. SE CERRO DE FORMA MANUAL(RTU DOWN) Y QUEDO EN SERVICIO SE REEMPLAZARON 2 X 100 Y 1 X 65 EN DISTINTOS CORTE DE LINEA LA CARGA DEL 5005-05 ESTA TRANSFERIDA AL 5005-04 | P22042400040 | New_Event | Bad Weather | Include | Include | Weather | 66 | 2022-04-24 | 32604 | keep | 0 | Apr | 2022 | 0.022206 | 0.00033646 | Sustained | FALSE | FALSE | Not_TMED_Event | 494
SAN JUAN | 2022-04-24 14:37 | 2022-04-25 11:25 | 14 | 020:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE XMR PARA REPARAR BARRA EN PEDESTAL | S22042400054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1248 | 2022-04-24 | 17472 | keep | 0 | Apr | 2022 | 0.0119 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-04-24 14:42 | 2022-04-24 14:43 | 3654 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA FIJAR CAJA PRIMARIA QUE SE ZAFO AL CERRARLA | A22042400049 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-04-24 | 3654 | keep | 0 | Apr | 2022 | 0.0024887 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-24 14:43 | 2022-04-24 14:52 | 400 | 000:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA SE REMPLAZO CAJAS PRIMARIAS AVERIADAS | A22042400006 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 9 | 2022-04-24 | 3600 | keep | 0 | Apr | 2022 | 0.0024519 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2022-04-24 14:46 | 2022-04-24 16:49 | 115 | 002:03 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22042400047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-04-24 | 14145 | keep | 0 | Apr | 2022 | 0.0096341 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
BAYAMON | 2022-04-24 14:48 | 2022-04-24 16:50 | 116 | 002:02 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S22042400055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-04-24 | 14152 | keep | 0 | Apr | 2022 | 0.0096389 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
SAN JUAN | 2022-04-24 14:49 | 2022-04-24 20:25 | 8 | 005:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA | S22042400031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 336 | 2022-04-24 | 2688 | keep | 0 | Apr | 2022 | 0.0018308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-24 14:49 | 2022-04-24 17:23 | 25 | 002:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA Y SE LEVANTO LINEA PRIMARIA | R22042400414 | New_Event | Wire Down | Include | Include | Equipment | 154 | 2022-04-24 | 3850 | keep | 0 | Apr | 2022 | 0.0026222 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-04-24 14:52 | 2022-04-24 16:49 | 150 | 001:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO MACHETES | A22042400044 | Additional_clients | Wire Down | Include | Include | Equipment | 117 | 2022-04-24 | 17550 | keep | 0 | Apr | 2022 | 0.011953 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-24 14:54 | 2022-04-24 16:55 | 10 | 002:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIAS DE TRANSFORMADOR AVERIADAS | A22042400054 | New_Event | Cutout Failure | Include | Include | Equipment | 121 | 2022-04-24 | 1210 | keep | 0 | Apr | 2022 | 0.00082413 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-24 14:55 | 2022-04-24 14:57 | 225 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL EL 1303-05 | S22042400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-04-24 | 450 | keep | 0 | Apr | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-24 14:55 | 2022-04-24 14:57 | 870 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1303-04 | S22042400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-04-24 | 1740 | keep | 0 | Apr | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-04-24 15:09 | 2022-04-24 15:11 | 225 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-5 | S22042400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-04-24 | 450 | keep | 0 | Apr | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-24 15:09 | 2022-04-24 15:11 | 870 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1303-4 | S22042400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-04-24 | 1740 | keep | 0 | Apr | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2022-04-24 15:09 | 2022-04-24 15:10 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042400053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 527 | keep | 0 | Apr | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
SAN JUAN | 2022-04-24 15:20 | 2022-04-24 15:21 | 225 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-5 | S22042400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-24 | 225 | keep | 0 | Apr | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-24 15:20 | 2022-04-24 15:21 | 870 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1303-4 | S22042400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-24 | 870 | keep | 0 | Apr | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-04-24 15:23 | 2022-04-24 16:42 | 225 | 001:19 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE CON BARRETA Y SE CERRO POR SCADA CARGA POR EL 1303-05 | S22042400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-04-24 | 17775 | keep | 0 | Apr | 2022 | 0.012106 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-24 15:23 | 2022-04-24 16:42 | 870 | 001:19 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE CON BARRETA Y SE CERRO POR SCADA LLEVA EL 1303-4 | S22042400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-04-24 | 68730 | keep | 0 | Apr | 2022 | 0.046812 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2022-04-24 15:44 | 2022-04-24 15:51 | 1337 | 000:07 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA NO SE REPORTO CAUSA | M22042400081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-04-24 | 9359 | keep | 0 | Apr | 2022 | 0.0063744 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
CAGUAS | 2022-04-24 15:46 | 2022-04-24 18:06 | 80 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22042400067 | New_Event |  |  | Include | Wildlife | 140 | 2022-04-24 | 11200 | keep | 0 | Apr | 2022 | 0.0076283 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-04-24 15:47 | 2022-04-24 18:44 | 32 | 002:57 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22042400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2022-04-24 | 5664 | keep | 0 | Apr | 2022 | 0.0038577 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
MAYAGÃœEZ | 2022-04-24 15:56 | 2022-04-24 17:55 | 100 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042400087 | New_Event | Bad Weather | Include | Include | Weather | 119 | 2022-04-24 | 11900 | keep | 0 | Apr | 2022 | 0.008105 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-04-24 15:56 | 2022-04-24 16:25 | 10 | 000:29 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR PARA AJUSTAR BUSHING SECUNDARIOS EN XMR | C22042400098 | New_Event | Service Transformer Failure | Include | Include | Equipment | 29 | 2022-04-24 | 290 | keep | 0 | Apr | 2022 | 0.00019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-24 15:57 | 2022-04-24 20:00 | 80 | 004:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042400088 | New_Event | Bad Weather | Include | Include | Weather | 243 | 2022-04-24 | 19440 | keep | 0 | Apr | 2022 | 0.01324 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-04-24 16:14 | 2022-04-24 16:15 | 1089 | 000:01 | S | LINEA DE TRANSMISION 38KV | SE ABRIO 3060 PARA PODER SECCIONALIZAR TRAMO DE LINEA 3000 CON PUENTE ABIERTO. | C22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-24 | 1089 | keep | 0 | Apr | 2022 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-04-24 16:14 | 2022-04-24 16:15 | 3896 | 000:01 | S | LINEA DE TRANSMISION 38KV | SE ABRIO 3060 PARA PODER SECCIONALIZAR TRAMO DE LINEA 3000 CON PUENTE ABIERTO. | C22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-24 | 3896 | keep | 0 | Apr | 2022 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-04-24 16:14 | 2022-04-24 16:15 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | SE ABRIO 3060 PARA PODER SECCIONALIZAR TRAMO DE LINEA 3000 CON PUENTE ABIERTO. | C22042400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-24 | 1467 | keep | 0 | Apr | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
UTUADO | 2022-04-24 16:41 | 2022-04-24 18:40 | 150 | 001:59 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22042400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-04-24 | 17850 | keep | 0 | Apr | 2022 | 0.012158 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-04-24 16:44 | 2022-04-24 22:00 | 15 | 005:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE ABIERTO A LA CAJA | S22042400053 | New_Event | Wire Down | Include | Include | Equipment | 316 | 2022-04-24 | 4740 | keep | 0 | Apr | 2022 | 0.0032284 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-24 16:48 | 2022-04-24 16:49 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042400110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 1192 | keep | 0 | Apr | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
MAYAGÃœEZ | 2022-04-24 17:01 | 2022-04-24 17:02 | 810 | 000:01 | S | LINEA DE TRANSMISION | RECIERRE DE LINEA 5600 | M22042400000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1 | 2022-04-24 | 810 | keep | 0 | Apr | 2022 | 0.00055169 | 0.00055169 | Momentary | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2022-04-24 17:01 | 2022-04-24 17:02 | 1235 | 000:01 | S | LINEA DE TRANSMISION | RECIERRE DE LINEA 5600 | M22042400000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1 | 2022-04-24 | 1235 | keep | 0 | Apr | 2022 | 0.00084115 | 0.00084115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2022-04-24 17:01 | 2022-04-24 17:02 | 93 | 000:01 | S | LINEA DE TRANSMISION | RECIERRE DE LINEA 5600 | M22042400000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1 | 2022-04-24 | 93 | keep | 0 | Apr | 2022 | 6.3342e-05 | 6.3342e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2022-04-24 17:01 | 2022-04-24 17:02 | 1825 | 000:01 | S | LINEA DE TRANSMISION | RECIERRE DE LINEA 5600 | M22042400000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1 | 2022-04-24 | 1825 | keep | 0 | Apr | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2022-04-24 17:01 | 2022-04-24 17:02 | 3230 | 000:01 | S | LINEA DE TRANSMISION | RECIERRE DE LINEA 5600 | M22042400000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1 | 2022-04-24 | 3230 | keep | 0 | Apr | 2022 | 0.0021999 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
MAYAGÃœEZ | 2022-04-24 17:02 | 2022-04-25 18:45 | 75 | 025:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS ABIERTOS | M22042300177 | Partial_restoration | Wire Down | Include | Include | Equipment | 1543 | 2022-04-24 | 115725 | keep | 0 | Apr | 2022 | 0.07882 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-24 17:07 | 2022-04-25 07:46 | 5 | 014:39 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO IDENTIFICO CAUSA | M22042400115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 879 | 2022-04-24 | 4395 | keep | 0 | Apr | 2022 | 0.0029934 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-04-24 17:27 | 2022-04-24 18:26 | 90 | 000:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | C22042400120 | New_Event | Cutout Failure | Include | Include | Equipment | 59 | 2022-04-24 | 5310 | keep | 0 | Apr | 2022 | 0.0036166 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-04-24 18:05 | 2022-04-25 10:35 | 10 | 016:30 | P | DESGANCHE | 1 X 20 EN XMR, SE REALIZO DESGANCHE Y SE REPARO LINEA SECUNDARIA | S22042400129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 990 | 2022-04-24 | 9900 | keep | 0 | Apr | 2022 | 0.0067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-24 18:17 | 2022-04-25 11:55 | 8 | 017:38 | P | DESGANCHE | 1X15 EN XMER | B22042400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1058 | 2022-04-24 | 8464 | keep | 0 | Apr | 2022 | 0.0057648 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-24 18:17 | 2022-04-24 18:54 | 33 | 000:37 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22042400061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2022-04-24 | 1221 | keep | 0 | Apr | 2022 | 0.00083162 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2022-04-24 18:30 | 2022-04-24 22:43 | 100 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22042400136 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2022-04-24 | 25300 | keep | 0 | Apr | 2022 | 0.017232 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-24 18:50 | 2022-04-24 18:51 | 2067 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR | M22042400137 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-04-24 | 2067 | keep | 0 | Apr | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2022-04-24 18:51 | 2022-04-25 10:15 | 1 | 015:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M22042400139 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 924 | 2022-04-24 | 924 | keep | 0 | Apr | 2022 | 0.00062933 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-24 19:00 | 2022-04-24 19:59 | 80 | 000:59 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22042400062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2022-04-24 | 4720 | keep | 0 | Apr | 2022 | 0.0032148 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-24 19:15 | 2022-04-24 20:16 | 521 | 001:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO LAGARTO DE MACHETE A LA SALIDA Y SE CERRO POR SCADA. SOLO 80% POR EL 1716-02 EL RESTO POR 1717-04 | B22042400000 | New_Event |  |  | Include | Wildlife | 61 | 2022-04-24 | 31781 | keep | 0 | Apr | 2022 | 0.021646 | 0.00035485 | Sustained | FALSE | FALSE | Not_TMED_Event | 521
CAGUAS | 2022-04-24 19:26 | 2022-04-25 11:31 | 3 | 016:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | C22042400148 | New_Event |  |  | Include | Wildlife | 965 | 2022-04-24 | 2895 | keep | 0 | Apr | 2022 | 0.0019718 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-04-24 19:35 | 2022-04-25 08:00 | 39 | 012:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X40 EN C/L SE REMPLAZO PORTAFUSIBLE | B22042400083 | New_Event | Cutout Failure | Include | Include | Equipment | 745 | 2022-04-24 | 29055 | keep | 0 | Apr | 2022 | 0.019789 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
SAN JUAN | 2022-04-24 19:47 | 2022-04-24 21:40 | 100 | 001:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y SE REEMPLAZO CAJA PRIMARIA | S22042400135 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2022-04-24 | 11300 | keep | 0 | Apr | 2022 | 0.0076964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-24 20:38 | 2022-04-25 10:24 | 4 | 013:46 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C22042400155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 826 | 2022-04-24 | 3304 | keep | 0 | Apr | 2022 | 0.0022503 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-04-24 20:42 | 2022-04-24 21:43 | 100 | 001:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042400093 | New_Event | Bad Weather | Include | Include | Weather | 61 | 2022-04-24 | 6100 | keep | 0 | Apr | 2022 | 0.0041547 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-24 21:11 | 2022-04-24 21:12 | 686 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-24 | 686 | keep | 0 | Apr | 2022 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
MAYAGÃœEZ | 2022-04-24 22:43 | 2022-04-24 22:44 | 4641 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22042400000 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2022-04-24 | 4641 | keep | 0 | Apr | 2022 | 0.003161 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-24 22:44 | 2022-04-24 23:35 | 100 | 000:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22042400136 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 51 | 2022-04-24 | 5100 | keep | 0 | Apr | 2022 | 0.0034736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-04-24 23:05 | 2022-04-25 11:23 | 6 | 012:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22042400167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 738 | 2022-04-24 | 4428 | keep | 0 | Apr | 2022 | 0.0030159 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-04-24 23:47 | 2022-04-25 08:10 | 170 | 008:23 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA INDICO SOBRECARGA | M22042400173 | New_Event | Trip Due To Overload | Include | Include | Other | 503 | 2022-04-24 | 85510 | keep | 0 | Apr | 2022 | 0.05824 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
PONCE | 2022-04-25 00:52 | 2022-04-25 10:00 | 3 | 009:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA QUEMADA | P22042500001 | New_Event | Cutout Failure | Include | Include | Equipment | 548 | 2022-04-25 | 1644 | keep | 0 | Apr | 2022 | 0.0011197 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-04-25 01:35 | 2022-04-25 01:36 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22042500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2022-04-25 02:18 | 2022-04-25 10:19 | 82 | 008:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO EN RAMAL | B22042500001 | New_Event | Wire Down | Include | Include | Equipment | 481 | 2022-04-25 | 39442 | keep | 0 | Apr | 2022 | 0.026864 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
VEGA BAJA | 2022-04-25 02:23 | 2022-04-25 02:24 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 4702 | keep | 0 | Apr | 2022 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
BAYAMON | 2022-04-25 02:49 | 2022-04-25 11:44 | 10 | 008:55 | P | CABLE SOTERRADO AVERIADO | 1X50 DE RISER @ T-11 AVERIA NUEVA: T-11 @ T-10, AVERIA VIEJA: RISER @ T-6, FUERA DE SERVICIO: T-10, T-9, T-8, T-7 & T-6 | B22042500003 | New_Event | UG Cable Fault | Include | Include | Equipment | 535 | 2022-04-25 | 5350 | keep | 0 | Apr | 2022 | 0.0036439 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-25 03:31 | 2022-04-25 06:10 | 5062 | 002:39 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO Y SE CERRO POR SCADA | R22042500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2022-04-25 | 804858 | keep | 0 | Apr | 2022 | 0.54819 | 0.0034477 | Sustained | FALSE | FALSE | Not_TMED_Event | 5062
UTUADO | 2022-04-25 03:32 | 2022-04-25 10:41 | 50 | 007:09 | P | ESTRUCTURA AVERIADA | 1 X 80 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | A22042500004 | New_Event | Defective Pole | Include | Include | Equipment | 429 | 2022-04-25 | 21450 | keep | 0 | Apr | 2022 | 0.014609 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-04-25 03:32 | 2022-04-25 22:00 | 150 | 018:28 | P | ESTRUCTURA AVERIADA | 3 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | A22042500065 | New_Event | Defective Pole | Include | Include | Equipment | 1108 | 2022-04-25 | 166200 | keep | 0 | Apr | 2022 | 0.1132 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-04-25 05:04 | 2022-04-25 10:15 | 70 | 005:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A22042500005 | New_Event | Cutout Failure | Include | Include | Equipment | 311 | 2022-04-25 | 21770 | keep | 0 | Apr | 2022 | 0.014827 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-04-25 05:11 | 2022-04-25 12:07 | 10 | 006:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO BUSHING | M22042500001 | New_Event |  |  | Include | Wildlife | 416 | 2022-04-25 | 4160 | keep | 0 | Apr | 2022 | 0.0028334 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-04-25 05:14 | 2022-04-25 05:15 | 778 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22042500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 778 | keep | 0 | Apr | 2022 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2022-04-25 05:14 | 2022-04-25 05:15 | 113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 5004-08 CON CARGA DEL 5011-05 | P22042500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 113 | keep | 0 | Apr | 2022 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
FAJARDO | 2022-04-25 05:30 | 2022-04-25 08:50 | 15 | 003:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO PORTAFUSIBLES | R22042500021 | New_Event | Cutout Failure | Include | Include | Equipment | 200 | 2022-04-25 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-04-25 06:03 | 2022-04-25 09:48 | 100 | 003:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22042500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-04-25 | 22500 | keep | 0 | Apr | 2022 | 0.015325 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-04-25 06:07 | 2022-04-25 09:19 | 32 | 003:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C22042500004 | New_Event |  |  | Include | Wildlife | 192 | 2022-04-25 | 6144 | keep | 0 | Apr | 2022 | 0.0041847 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2022-04-25 06:10 | 2022-04-25 06:35 | 4556 | 000:25 | P | NO SE REPORTO CAUSA | SE CONTINUO CORRIENDO LAZO Y SE ENERGIZO UN 10% | R22042500003 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 25 | 2022-04-25 | 113900 | keep | 0 | Apr | 2022 | 0.077577 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-04-25 06:10 | 2022-04-25 06:11 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
CAGUAS | 2022-04-25 06:20 | 2022-04-25 12:29 | 60 | 006:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP PARTIDO | C22042500091 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 369 | 2022-04-25 | 22140 | keep | 0 | Apr | 2022 | 0.015079 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-25 06:35 | 2022-04-25 07:26 | 4303 | 000:51 | P | NO SE REPORTO CAUSA | SE CONTINUO CORRIENDO LAZO Y SE ENERGIZO UN 15% | R22042500003 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-04-25 | 219453 | keep | 0 | Apr | 2022 | 0.14947 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-25 06:46 | 2022-04-25 15:16 | 120 | 008:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22042500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 510 | 2022-04-25 | 61200 | keep | 0 | Apr | 2022 | 0.041683 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-04-25 06:49 | 2022-04-25 10:46 | 200 | 003:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C22042500011 | New_Event | Cutout Failure | Include | Include | Equipment | 237 | 2022-04-25 | 47400 | keep | 0 | Apr | 2022 | 0.032284 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-04-25 07:00 | 2022-04-25 07:01 | 574 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 574 | keep | 0 | Apr | 2022 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
AGUADILLA | 2022-04-25 07:00 | 2022-04-25 07:01 | 2493 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 2493 | keep | 0 | Apr | 2022 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
AGUADILLA | 2022-04-25 07:00 | 2022-04-25 07:01 | 1415 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1415 | keep | 0 | Apr | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
AGUADILLA | 2022-04-25 07:00 | 2022-04-25 07:01 | 1428 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1428 | keep | 0 | Apr | 2022 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
AGUADILLA | 2022-04-25 07:00 | 2022-04-25 07:01 | 1036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1036 | keep | 0 | Apr | 2022 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
CAGUAS | 2022-04-25 07:02 | 2022-04-25 10:21 | 1 | 003:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA | C22042500015 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2022-04-25 | 199 | keep | 0 | Apr | 2022 | 0.00013554 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-04-25 07:11 | 2022-04-25 11:58 | 10 | 004:47 | P | DESGANCHE | 1 X 20 EN C/L Y 1 X 10 EN XMR SE RETIRO ENREDADERAS | R22042500029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2022-04-25 | 2870 | keep | 0 | Apr | 2022 | 0.0019547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-25 07:26 | 2022-04-25 08:45 | 2025 | 001:19 | P | NO SE REPORTO CAUSA | SE CONTINUO CORRIENDO LAZO Y SE ENERGIZO UN 60% | R22042500003 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-04-25 | 159975 | keep | 0 | Apr | 2022 | 0.10896 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-04-25 07:58 | 2022-04-25 07:59 | 569 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2500 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 569 | keep | 0 | Apr | 2022 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2022-04-25 07:58 | 2022-04-25 07:59 | 1245 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2500 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1245 | keep | 0 | Apr | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2022-04-25 07:58 | 2022-04-25 07:59 | 1155 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2500 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1155 | keep | 0 | Apr | 2022 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2022-04-25 07:58 | 2022-04-25 07:59 | 867 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2500 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 867 | keep | 0 | Apr | 2022 | 0.00059051 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2022-04-25 07:58 | 2022-04-25 07:59 | 257 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2500 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 257 | keep | 0 | Apr | 2022 | 0.00017504 | 0.00017504 | Momentary | FALSE | FALSE | Not_TMED_Event | 257
AGUADILLA | 2022-04-25 07:58 | 2022-04-25 07:59 | 1336 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2500 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1336 | keep | 0 | Apr | 2022 | 0.00090994 | 0.00090994 | Momentary | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2022-04-25 07:58 | 2022-04-25 07:59 | 3315 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2500 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 3315 | keep | 0 | Apr | 2022 | 0.0022578 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2022-04-25 07:58 | 2022-04-25 07:59 | 1718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2500 | M22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1718 | keep | 0 | Apr | 2022 | 0.0011701 | 0.0011701 | Momentary | FALSE | FALSE | Not_TMED_Event | 1718
BAYAMON | 2022-04-25 08:14 | 2022-04-25 13:20 | 60 | 005:06 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B22042500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 306 | 2022-04-25 | 18360 | keep | 0 | Apr | 2022 | 0.012505 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-25 08:17 | 2022-04-25 12:07 | 100 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A22042500026 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2022-04-25 | 23000 | keep | 0 | Apr | 2022 | 0.015665 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-25 08:18 | 2022-04-25 09:49 | 100 | 001:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INDICO REQUIERE DESGANCHE | M22041400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-04-25 | 9100 | keep | 0 | Apr | 2022 | 0.006198 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-04-25 08:33 | 2022-04-25 08:34 | 625 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 625 | keep | 0 | Apr | 2022 | 0.00042568 | 0.00042568 | Momentary | FALSE | FALSE | Not_TMED_Event | 625
FAJARDO | 2022-04-25 08:33 | 2022-04-25 08:34 | 76 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 76 | keep | 0 | Apr | 2022 | 5.1763e-05 | 5.1763e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 76
SAN JUAN | 2022-04-25 08:45 | 2022-04-25 09:00 | 1519 | 000:15 | P | NO SE REPORTO CAUSA | SE CONTINUO CORRIENDO LAZO Y SE ENERGIZO UN 85% | R22042500003 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-04-25 | 22785 | keep | 0 | Apr | 2022 | 0.015519 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-25 09:00 | 2022-04-25 09:05 | 506 | 000:05 | P | NO SE REPORTO CAUSA | SE CONTINUO CORRIENDO LAZO Y SE ENERGIZO UN 100% | R22042500003 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-04-25 | 2530 | keep | 0 | Apr | 2022 | 0.0017232 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-25 09:20 | 2022-04-25 14:40 | 55 | 005:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S22042500009 | New_Event | Wire Down | Include | Include | Equipment | 320 | 2022-04-25 | 17600 | keep | 0 | Apr | 2022 | 0.011987 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-04-25 09:25 | 2022-04-25 10:42 | 1 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | R22042500040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2022-04-25 | 77 | keep | 0 | Apr | 2022 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-25 09:28 | 2022-04-25 09:29 | 271 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 271 | keep | 0 | Apr | 2022 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
GUAYAMA | 2022-04-25 09:31 | 2022-04-25 12:51 | 331 | 003:20 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | P22042500019 | New_Event | Switch Failure | Include | Include | Equipment | 200 | 2022-04-25 | 66200 | keep | 0 | Apr | 2022 | 0.045089 | 0.00022544 | Sustained | FALSE | FALSE | Not_TMED_Event | 331
CAGUAS | 2022-04-25 09:36 | 2022-04-25 09:37 | 1228 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1228 | keep | 0 | Apr | 2022 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2022-04-25 09:36 | 2022-04-25 09:37 | 1271 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1271 | keep | 0 | Apr | 2022 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2022-04-25 09:36 | 2022-04-25 09:37 | 1893 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1893 | keep | 0 | Apr | 2022 | 0.0012893 | 0.0012893 | Momentary | FALSE | FALSE | Not_TMED_Event | 1893
CAGUAS | 2022-04-25 09:36 | 2022-04-25 09:37 | 473 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 473 | keep | 0 | Apr | 2022 | 0.00032216 | 0.00032216 | Momentary | FALSE | FALSE | Not_TMED_Event | 473
CAGUAS | 2022-04-25 09:36 | 2022-04-25 09:37 | 1261 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1261 | keep | 0 | Apr | 2022 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
CAGUAS | 2022-04-25 09:36 | 2022-04-25 09:37 | 1922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1922 | keep | 0 | Apr | 2022 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2022-04-25 09:36 | 2022-04-25 09:37 | 853 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 853 | keep | 0 | Apr | 2022 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
CAGUAS | 2022-04-25 09:36 | 2022-04-25 09:37 | 2900 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 2900 | keep | 0 | Apr | 2022 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
CAGUAS | 2022-04-25 09:36 | 2022-04-25 09:37 | 2178 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 2178 | keep | 0 | Apr | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2022-04-25 09:42 | 2022-04-25 09:43 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042500036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 2147 | keep | 0 | Apr | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
MAYAGÃœEZ | 2022-04-25 09:43 | 2022-04-25 19:40 | 30 | 009:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22042500041 | New_Event | Wire Down | Include | Include | Equipment | 597 | 2022-04-25 | 17910 | keep | 0 | Apr | 2022 | 0.012198 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-04-25 10:01 | 2022-04-25 16:51 | 7 | 006:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C22042500067 | New_Event |  |  | Include | Wildlife | 410 | 2022-04-25 | 2870 | keep | 0 | Apr | 2022 | 0.0019547 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-04-25 10:10 | 2022-04-25 13:40 | 6 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22042500069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2022-04-25 | 1260 | keep | 0 | Apr | 2022 | 0.00085818 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-04-25 10:12 | 2022-04-25 10:13 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042500027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 3114 | keep | 0 | Apr | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-04-25 10:12 | 2022-04-25 13:15 | 40 | 003:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN PROVISIONAL AEREO AVE CRUZO FASE | P22042500025 | New_Event |  |  | Include | Wildlife | 183 | 2022-04-25 | 7320 | keep | 0 | Apr | 2022 | 0.0049856 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-04-25 10:19 | 2022-04-25 14:09 | 40 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REEMPLAZO CAJA PRIMARIA QUEMADA EN RISER | P22042500028 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2022-04-25 | 9200 | keep | 0 | Apr | 2022 | 0.0062661 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-25 10:42 | 2022-04-25 15:53 | 70 | 005:11 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA DE RETIRO RAMA | A22042500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-04-25 | 21770 | keep | 0 | Apr | 2022 | 0.014827 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-04-25 11:00 | 2022-04-25 14:30 | 25 | 003:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA POR IGUAL CAPACIDAD | S22042500023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 210 | 2022-04-25 | 5250 | keep | 0 | Apr | 2022 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-04-25 11:15 | 2022-04-25 14:00 | 30 | 002:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22042500071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-04-25 | 4950 | keep | 0 | Apr | 2022 | 0.0033714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-04-25 11:20 | 2022-04-25 15:45 | 3 | 004:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A22042500052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 265 | 2022-04-25 | 795 | keep | 0 | Apr | 2022 | 0.00054147 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-04-25 11:26 | 2022-04-25 13:31 | 5 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON LAS TRES (3) BARRAS EN PEDESTAL TIPO MOLE | B22042500051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2022-04-25 | 625 | keep | 0 | Apr | 2022 | 0.00042568 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-04-25 11:44 | 2022-04-26 15:48 | 53 | 028:04 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DE T-11 @ T-10 Y SE NORMALIZO CON BY-220425-02 | B22042500003 | New_Event | UG Cable Fault | Include | Include | Equipment | 1684 | 2022-04-25 | 89252 | keep | 0 | Apr | 2022 | 0.060789 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2022-04-25 11:45 | 2022-04-25 12:50 | 8 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22042500051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-04-25 | 520 | keep | 0 | Apr | 2022 | 0.00035417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-04-25 11:50 | 2022-04-25 14:51 | 1 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER | B22042500054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-04-25 | 181 | keep | 0 | Apr | 2022 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-25 12:09 | 2022-04-25 15:02 | 80 | 002:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22042500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-04-25 | 13840 | keep | 0 | Apr | 2022 | 0.0094264 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-25 12:14 | 2022-04-26 11:15 | 19 | 023:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22042500078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1381 | 2022-04-25 | 26239 | keep | 0 | Apr | 2022 | 0.017871 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2022-04-25 12:26 | 2022-04-25 12:27 | 4188 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R22042500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-25 | 4188 | keep | 0 | Apr | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-04-25 12:27 | 2022-04-25 14:59 | 47 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN C/L SE CERRO PUENTE ABIERTO CRUZADO SE REMPLAZO CAJA PRIMARIA | R22042500081 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 152 | 2022-04-25 | 7144 | keep | 0 | Apr | 2022 | 0.0048657 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2022-04-25 12:27 | 2022-04-25 19:45 | 1 | 007:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN C/L NO CAUSA | C22042500080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 438 | 2022-04-25 | 438 | keep | 0 | Apr | 2022 | 0.00029832 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-25 13:07 | 2022-04-25 14:26 | 50 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22042500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-04-25 | 3950 | keep | 0 | Apr | 2022 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-25 13:07 | 2022-04-25 14:04 | 9 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA EN VARIOS PUNTOS | C22042500084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-04-25 | 513 | keep | 0 | Apr | 2022 | 0.0003494 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-04-25 13:11 | 2022-04-25 18:35 | 100 | 005:24 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEAS RETIRO RAMAS SOBRE LINEA | B22042500067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2022-04-25 | 32400 | keep | 0 | Apr | 2022 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-04-25 13:12 | 2022-04-25 17:23 | 100 | 004:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER Y 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P22042500039 | New_Event | Bad Weather | Include | Include | Weather | 251 | 2022-04-25 | 25100 | keep | 0 | Apr | 2022 | 0.017095 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-04-25 13:14 | 2022-04-25 15:24 | 150 | 002:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBU DE LINEA | A22042500086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-04-25 | 19500 | keep | 0 | Apr | 2022 | 0.013281 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-04-25 13:16 | 2022-04-25 13:32 | 10 | 000:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER AVE CRUZO LINEAS | M22042500021 | New_Event |  |  | Include | Wildlife | 16 | 2022-04-25 | 160 | keep | 0 | Apr | 2022 | 0.00010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-25 13:37 | 2022-04-25 13:38 | 614 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | R22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 614 | keep | 0 | Apr | 2022 | 0.00041819 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-04-25 13:52 | 2022-04-25 18:30 | 59 | 004:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA Y SE CERRO PUENTE DE LINEA A CAJA. ADEMAS SE REEMPLAZARON DOS CAJAS | S22042500036 | New_Event | Wire Down | Include | Include | Equipment | 278 | 2022-04-25 | 16402 | keep | 0 | Apr | 2022 | 0.011171 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
HUMACAO | 2022-04-25 13:53 | 2022-04-25 16:07 | 80 | 002:14 | P | DESGANCHE | 1 X 65 EN C/L | C22042500088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-04-25 | 10720 | keep | 0 | Apr | 2022 | 0.0073013 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-25 13:59 | 2022-04-25 14:00 | 3871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 3871 | keep | 0 | Apr | 2022 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
SAN JUAN | 2022-04-25 14:01 | 2022-04-25 14:02 | 614 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | R22042500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 614 | keep | 0 | Apr | 2022 | 0.00041819 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
AGUADILLA | 2022-04-25 14:01 | 2022-04-25 17:23 | 100 | 003:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22042500068 | New_Event | Wire Down | Include | Include | Equipment | 202 | 2022-04-25 | 20200 | keep | 0 | Apr | 2022 | 0.013758 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-04-25 14:25 | 2022-04-25 15:11 | 10 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | R22042500054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2022-04-25 | 460 | keep | 0 | Apr | 2022 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-25 14:30 | 2022-04-25 14:31 | 676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5300 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 676 | keep | 0 | Apr | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2022-04-25 14:30 | 2022-04-25 14:31 | 2873 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5300 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 2873 | keep | 0 | Apr | 2022 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2022-04-25 14:30 | 2022-04-25 14:31 | 3902 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5300 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 3902 | keep | 0 | Apr | 2022 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
BAYAMON | 2022-04-25 14:33 | 2022-04-25 14:34 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | NO CAUSA | B22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 5252 | keep | 0 | Apr | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
AGUADILLA | 2022-04-25 14:35 | 2022-04-25 18:45 | 150 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042500080 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2022-04-25 | 37500 | keep | 0 | Apr | 2022 | 0.025541 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-04-25 14:40 | 2022-04-25 14:41 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 1310 | keep | 0 | Apr | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CAGUAS | 2022-04-25 14:46 | 2022-04-25 16:12 | 44 | 001:26 | P | DESGANCHE | 1 X 65 EN C/L | C22042500097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-04-25 | 3784 | keep | 0 | Apr | 2022 | 0.0025773 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
MAYAGÃœEZ | 2022-04-25 14:46 | 2022-04-26 02:29 | 10 | 011:43 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042500081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 703 | 2022-04-25 | 7030 | keep | 0 | Apr | 2022 | 0.0047881 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-25 14:52 | 2022-04-25 15:34 | 18 | 000:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER LLUVIA Y FUERTES VIENTOS | A22042500122 | New_Event | Bad Weather | Include | Include | Weather | 42 | 2022-04-25 | 756 | keep | 0 | Apr | 2022 | 0.00051491 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2022-04-25 14:52 | 2022-04-25 15:34 | 70 | 000:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22042500097 | New_Event | Bad Weather | Include | Include | Weather | 42 | 2022-04-25 | 2940 | keep | 0 | Apr | 2022 | 0.0020024 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-04-25 14:59 | 2022-04-25 15:00 | 4188 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R22042500000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-04-25 | 4188 | keep | 0 | Apr | 2022 | 0.0028524 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-25 15:00 | 2022-04-25 15:01 | 641 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DE LOS ALIMENTADORES 1105-02 Y 1105-01 | S22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 641 | keep | 0 | Apr | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
BAYAMON | 2022-04-25 15:00 | 2022-04-25 15:01 | 308 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DE LOS ALIMENTADORES 1105-02 Y 1105-01 | S22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 308 | keep | 0 | Apr | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2022-04-25 15:00 | 2022-04-25 15:01 | 333 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DE LOS ALIMENTADORES 1105-02 Y 1105-01 | S22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 333 | keep | 0 | Apr | 2022 | 0.0002268 | 0.0002268 | Momentary | FALSE | FALSE | Not_TMED_Event | 333
CANOVANAS | 2022-04-25 15:00 | 2022-04-25 17:32 | 47 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN C/L SE CERRO PUENTE ABIERTO CRUZADO SE REMPLAZO CAJA PRIMARIA | R22042500081 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 152 | 2022-04-25 | 7144 | keep | 0 | Apr | 2022 | 0.0048657 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
MAYAGÃœEZ | 2022-04-25 15:12 | 2022-04-25 16:15 | 200 | 001:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22042500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-04-25 | 12600 | keep | 0 | Apr | 2022 | 0.0085818 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-04-25 15:12 | 2022-04-25 17:49 | 1 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER FOREMAN NO IDENTIFICO CAUSA | A22042500099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-04-25 | 157 | keep | 0 | Apr | 2022 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-25 15:20 | 2022-04-25 18:42 | 33 | 003:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN RISER SE RETIRO IGUANA DE SU | R22042500056 | New_Event |  |  | Include | Wildlife | 202 | 2022-04-25 | 6666 | keep | 0 | Apr | 2022 | 0.0045402 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
VEGA BAJA | 2022-04-25 15:23 | 2022-04-25 18:48 | 50 | 003:25 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU-17. AVERIA VIEJA T-19 @ T-18 Y AVERIA NUEVA T-16 @ T-17. | B22042500080 | New_Event | UG Cable Fault | Include | Include | Equipment | 205 | 2022-04-25 | 10250 | keep | 0 | Apr | 2022 | 0.0069812 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-04-25 15:37 | 2022-04-25 20:22 | 18 | 004:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER LLUVIA Y FUERTES VIENTOS | A22042500122 | Partial_restoration | Bad Weather | Include | Include | Weather | 285 | 2022-04-25 | 5130 | keep | 0 | Apr | 2022 | 0.003494 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-04-25 15:37 | 2022-04-25 17:04 | 70 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22042500097 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2022-04-25 | 6090 | keep | 0 | Apr | 2022 | 0.0041479 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-04-25 15:52 | 2022-04-25 15:53 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 1894 | keep | 0 | Apr | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
BAYAMON | 2022-04-25 15:57 | 2022-04-25 17:22 | 60 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22042500098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-04-25 | 5100 | keep | 0 | Apr | 2022 | 0.0034736 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-25 16:06 | 2022-04-25 16:50 | 790 | 000:44 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA TRABAJOS DE REPARCION DE LINEA PRIMARIA . EVENTO CREADO EMERGENCIA POR DESPACHO | S22042500065 | New_Event | Wire Down | Include | Include | Equipment | 44 | 2022-04-25 | 34760 | keep | 0 | Apr | 2022 | 0.023675 | 0.00053807 | Sustained | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2022-04-25 16:07 | 2022-04-25 16:08 | 6244 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 6244 | keep | 0 | Apr | 2022 | 0.0042528 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
CAGUAS | 2022-04-25 16:43 | 2022-04-25 16:44 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1565 | keep | 0 | Apr | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-04-25 16:43 | 2022-04-25 16:44 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 976 | keep | 0 | Apr | 2022 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-04-25 16:43 | 2022-04-25 16:44 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 548 | keep | 0 | Apr | 2022 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-04-25 16:43 | 2022-04-25 16:44 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 315 | keep | 0 | Apr | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-04-25 16:43 | 2022-04-25 16:44 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 870 | keep | 0 | Apr | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-04-25 16:43 | 2022-04-25 16:44 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 2906 | keep | 0 | Apr | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-04-25 16:43 | 2022-04-25 16:44 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 2343 | keep | 0 | Apr | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
GUAYAMA | 2022-04-25 16:46 | 2022-04-25 16:47 | 4132 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE SU CARGA ESTA TRANSFERIDA AL 4006-05 | P22042500056 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-25 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-04-25 16:46 | 2022-04-25 16:47 | 4279 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE SU CARGA ESTA TRANSFERIDA AL 4006-05 | P22042500056 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-25 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-04-25 16:46 | 2022-04-25 16:47 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL 4006-05 QUE LLEVA LA CARGA DEL 4003-01 Y DEL 4003-02 | P22042500056 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-25 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-04-25 16:47 | 2022-04-25 17:32 | 1 | 000:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN RISER AVE CRUZO FASE | P22042500059 | 1st_after_momentary |  |  | Include | Wildlife | 45 | 2022-04-25 | 45 | keep | 0 | Apr | 2022 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-25 16:49 | 2022-04-25 16:50 | 1089 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1089 | keep | 0 | Apr | 2022 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-04-25 16:49 | 2022-04-25 16:50 | 3896 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 3896 | keep | 0 | Apr | 2022 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-04-25 16:49 | 2022-04-25 16:50 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-25 | 1467 | keep | 0 | Apr | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
VEGA BAJA | 2022-04-25 16:49 | 2022-04-25 17:43 | 25 | 000:54 | P | OTRAS CAUSAS | SE ABRIO EN RISER @ MH-12 PARA QUE PERSONAL PUDIERA RECONECTAR SERVICIO A CLIENTE ALCALDIA #73 | B22042500131 | New_Event | Other Causes | Include | Include | Other | 54 | 2022-04-25 | 1350 | keep | 0 | Apr | 2022 | 0.00091948 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-25 16:55 | 2022-04-26 02:34 | 1 | 009:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042500100 | New_Event | Bad Weather | Include | Include | Weather | 579 | 2022-04-25 | 579 | keep | 0 | Apr | 2022 | 0.00039435 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-25 17:11 | 2022-04-25 17:12 | 2900 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22042500114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 2900 | keep | 0 | Apr | 2022 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
BARRANQUITAS | 2022-04-25 17:20 | 2022-04-26 07:45 | 5 | 014:25 | P | HERRAJE ROTO O PODRIDO | 1 X 10 EN TRANSFORMADOR SE FIJO CRUCETA DEL TRANSFORMADOR | C22042500116 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 865 | 2022-04-25 | 4325 | keep | 0 | Apr | 2022 | 0.0029457 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-04-25 17:22 | 2022-04-25 17:34 | 6 | 000:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22042500065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 12 | 2022-04-25 | 72 | keep | 0 | Apr | 2022 | 4.9039e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-25 17:27 | 2022-04-25 20:00 | 25 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR Y SE REEMPLAZO CAJA | S22042500080 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2022-04-25 | 3825 | keep | 0 | Apr | 2022 | 0.0026052 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-25 17:37 | 2022-04-25 20:38 | 25 | 003:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | M22042500104 | New_Event |  |  | Include | Wildlife | 181 | 2022-04-25 | 4525 | keep | 0 | Apr | 2022 | 0.003082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-04-25 17:46 | 2022-04-26 10:35 | 10 | 016:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22042500116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1009 | 2022-04-25 | 10090 | keep | 0 | Apr | 2022 | 0.0068723 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-25 18:25 | 2022-04-25 18:26 | 3941 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | B22042500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-25 | 3941 | keep | 0 | Apr | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-04-25 18:29 | 2022-04-25 19:31 | 3941 | 001:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR FUEGO. EL FUEGO FUE CAUSADO POR LA EXPLOSION DE LOS FUSIBLES DEL RISER DE PARQUE DE PELOTA RAUL JULIA QUE A SU VEZ ENCENDIERON LA GRAMA. EL FUEGO FUE CAUSADO POR CONDUCTOR EN EL SUELO VIVO | B22042500109 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 62 | 2022-04-25 | 244342 | keep | 0 | Apr | 2022 | 0.16642 | 0.0026842 | Sustained | FALSE | FALSE | Not_TMED_Event | 3941
GUAYAMA | 2022-04-25 18:35 | 2022-04-25 19:28 | 8 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22042500060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2022-04-25 | 424 | keep | 0 | Apr | 2022 | 0.00028878 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-04-25 19:02 | 2022-04-25 19:03 | 1859 | 000:01 | T | DESGANCHE | RECIERRE | B22042500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-25 | 1859 | keep | 0 | Apr | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-04-25 19:03 | 2022-04-25 22:59 | 100 | 003:56 | P | DESGANCHE | 2 X 100 EN C/L | B22042500214 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-04-25 | 23600 | keep | 0 | Apr | 2022 | 0.016074 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-25 19:05 | 2022-04-26 17:46 | 1 | 022:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15KVA POR IGUAL CAPACIDAD | C22042500117 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1361 | 2022-04-25 | 1361 | keep | 0 | Apr | 2022 | 0.00092697 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-25 19:06 | 2022-04-25 21:00 | 25 | 001:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22042500085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-04-25 | 2850 | keep | 0 | Apr | 2022 | 0.0019411 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-25 19:11 | 2022-04-25 22:01 | 8 | 002:50 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR CRUCE DE FASE POR BEJUCO | P22042500073 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 170 | 2022-04-25 | 1360 | keep | 0 | Apr | 2022 | 0.00092629 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-04-25 19:15 | 2022-04-25 21:00 | 35 | 001:45 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR PARA RETIRAR ARBOL DE LA LINEA Y LEVANTAR SECUNDARIA DEL SUELO | P22042500071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 105 | 2022-04-25 | 3675 | keep | 0 | Apr | 2022 | 0.002503 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-04-25 20:02 | 2022-04-25 21:28 | 53 | 001:26 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU-4A @ T-28 | B22042500225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2022-04-25 | 4558 | keep | 0 | Apr | 2022 | 0.0031044 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
SAN JUAN | 2022-04-25 20:03 | 2022-04-26 19:52 | 30 | 023:49 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DEL T33 AL T34 Y AVERIA VIEJA DEL T36 AL T35. SE CONSTRUYO AEREO PROVISIONAL DEL T36 AL T35 | R22042500097 | New_Event | UG Cable Fault | Include | Include | Equipment | 1429 | 2022-04-25 | 42870 | keep | 0 | Apr | 2022 | 0.029199 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:18 | 3833 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HUMACAO SECT | C22042500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-25 | 19165 | keep | 0 | Apr | 2022 | 0.013053 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:18 | 181 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HUMACAO SECT | C22042500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-25 | 905 | keep | 0 | Apr | 2022 | 0.00061639 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:18 | 2299 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HUMACAO SECT | C22042500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-25 | 11495 | keep | 0 | Apr | 2022 | 0.0078292 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:18 | 776 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HUMACAO SECT | C22042500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-04-25 | 3880 | keep | 0 | Apr | 2022 | 0.0026427 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
HUMACAO | 2022-04-25 20:13 | 2022-04-26 02:56 | 551 | 006:43 | T | LINEA DE TRANSMISION 38KV | SE LEVANTO CONDUCTOR DE L-12500 | C22042500123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 403 | 2022-04-25 | 222053 | keep | 0 | Apr | 2022 | 0.15124 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:19 | 3701 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-25 | 22206 | keep | 0 | Apr | 2022 | 0.015124 | 0.0025207 | Sustained | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:19 | 989 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-25 | 5934 | keep | 0 | Apr | 2022 | 0.0040416 | 0.0006736 | Sustained | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:19 | 1467 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C22042500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-25 | 8802 | keep | 0 | Apr | 2022 | 0.005995 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:18 | 1089 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22042500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-04-25 | 5445 | keep | 0 | Apr | 2022 | 0.0037086 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:18 | 3896 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22042500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-04-25 | 19480 | keep | 0 | Apr | 2022 | 0.013268 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-04-25 20:13 | 2022-04-25 20:18 | 1467 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22042500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-04-25 | 7335 | keep | 0 | Apr | 2022 | 0.0049958 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-04-25 20:31 | 2022-04-25 21:46 | 3701 | 001:15 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE ABRIO BKR A PETICION DE J. ALICEA DEL CCE POR SOBRE CARGA DE LA LINEA 3000 | C22042500000 | New_Event |  |  |  |  | 75 | 2022-04-25 | 277575 | keep | 0 | Apr | 2022 | 0.18906 | 0.0025207 | Sustained | FALSE | FALSE | Not_TMED_Event | 3701
MAYAGÃœEZ | 2022-04-25 20:50 | 2022-04-26 15:42 | 300 | 018:52 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA QUE PERSONAL PRIVADO REALIZARA DESGANCHE | M22042500119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1132 | 2022-04-25 | 339600 | keep | 0 | Apr | 2022 | 0.2313 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2022-04-25 21:42 | 2022-04-25 22:30 | 150 | 000:48 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22042500131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2022-04-25 | 7200 | keep | 0 | Apr | 2022 | 0.0049039 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-04-25 22:03 | 2022-04-26 15:19 | 14 | 017:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE SECUNDARIO QUEMADO | R22042500123 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1036 | 2022-04-25 | 14504 | keep | 0 | Apr | 2022 | 0.0098786 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-04-25 23:29 | 2022-04-26 10:47 | 70 | 011:18 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU 1E Y 1 X30 EN AEREO PROVIONAL AVERIA NUEVA DE T632 @ T633 Y AVERIA VIEJA DE T634 A SU2E | B22042500240 | New_Event | UG Cable Fault | Include | Include | Equipment | 678 | 2022-04-25 | 47460 | keep | 0 | Apr | 2022 | 0.032325 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-04-25 23:40 | 2022-04-25 23:41 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22042500147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 3431 | keep | 0 | Apr | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-04-25 23:41 | 2022-04-25 23:42 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22042500149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-25 | 1227 | keep | 0 | Apr | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
CAGUAS | 2022-04-25 23:42 | 2022-04-26 11:22 | 13 | 011:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO HOT CLAMP EN BAJANTE DE LINEA A CAJA DE TRANSFSORMADOR | C22042500247 | New_Event | Wire Down | Include | Include | Equipment | 700 | 2022-04-25 | 9100 | keep | 0 | Apr | 2022 | 0.006198 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-04-26 00:16 | 2022-04-26 00:17 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22042600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 2999 | keep | 0 | Apr | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
BAYAMON | 2022-04-26 00:23 | 2022-04-26 10:19 | 50 | 009:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22042600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 596 | 2022-04-26 | 29800 | keep | 0 | Apr | 2022 | 0.020297 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-04-26 00:59 | 2022-04-26 01:47 | 519 | 000:48 | T | LINEA DE TRANSMISION 38KV | SE ABRIO BKR PARA PODER LEVANTAR CONDUCTOR DE LA LINEA 12500 | C22042600001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-04-26 | 24912 | keep | 0 | Apr | 2022 | 0.016967 | 0.00035349 | Sustained | FALSE | FALSE | Not_TMED_Event | 519
HUMACAO | 2022-04-26 00:59 | 2022-04-26 01:47 | 1117 | 000:48 | T | LINEA DE TRANSMISION 38KV | SE ABRIO BKR PARA PODER LEVANTAR CONDUCTOR DE LA LINEA 12500 | C22042600001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-04-26 | 53616 | keep | 0 | Apr | 2022 | 0.036518 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
PONCE | 2022-04-26 02:01 | 2022-04-26 02:02 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22042600112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 527 | keep | 0 | Apr | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
FAJARDO | 2022-04-26 02:29 | 2022-04-26 08:51 | 36 | 006:22 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R22042600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2022-04-26 | 13752 | keep | 0 | Apr | 2022 | 0.0093664 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2022-04-26 03:31 | 2022-04-26 08:54 | 50 | 005:23 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 50 EN CORTES DE LINEA | S22042600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 323 | 2022-04-26 | 16150 | keep | 0 | Apr | 2022 | 0.011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-26 04:23 | 2022-04-26 05:25 | 100 | 001:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22042600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-04-26 | 6200 | keep | 0 | Apr | 2022 | 0.0042228 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-04-26 05:39 | 2022-04-26 07:21 | 120 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR AVE | P22042600003 | New_Event |  |  | Include | Wildlife | 102 | 2022-04-26 | 12240 | keep | 0 | Apr | 2022 | 0.0083366 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-04-26 05:58 | 2022-04-26 09:06 | 75 | 003:08 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-04-26 | 14100 | keep | 0 | Apr | 2022 | 0.0096034 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-04-26 06:00 | 2022-04-26 07:27 | 40 | 001:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22042600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-04-26 | 3480 | keep | 0 | Apr | 2022 | 0.0023702 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-04-26 06:05 | 2022-04-26 09:22 | 100 | 003:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22042600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-04-26 | 19700 | keep | 0 | Apr | 2022 | 0.013418 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-04-26 06:06 | 2022-04-27 19:30 | 17 | 037:24 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN C/L SE CONSTRUYO PROVICIONAL AEREO DEL T - 16 @ TRONCAL | C22042600004 | New_Event | UG Cable Fault | Include | Include | Equipment | 2244 | 2022-04-26 | 38148 | keep | 0 | Apr | 2022 | 0.025982 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2022-04-26 06:33 | 2022-04-26 06:34 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22042600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 1227 | keep | 0 | Apr | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
CANOVANAS | 2022-04-26 07:00 | 2022-04-26 10:06 | 60 | 003:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | R22042600006 | New_Event |  |  | Include | Wildlife | 186 | 2022-04-26 | 11160 | keep | 0 | Apr | 2022 | 0.007601 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-04-26 07:10 | 2022-04-26 07:11 | 1986 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22042600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 1986 | keep | 0 | Apr | 2022 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
SAN JUAN | 2022-04-26 07:13 | 2022-04-26 07:14 | 1000 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1620-5 SE CERRO POR CONTROL | S22042600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 1000 | keep | 0 | Apr | 2022 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-04-26 07:13 | 2022-04-26 07:14 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA PARTE DEL 1206-3 SE CERRO POR CONTROL | S22042600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 1615 | keep | 0 | Apr | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
MAYAGÃœEZ | 2022-04-26 07:15 | 2022-04-26 07:16 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 990 | keep | 0 | Apr | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
CAGUAS | 2022-04-26 07:24 | 2022-04-26 11:52 | 1 | 004:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22042600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 268 | 2022-04-26 | 268 | keep | 0 | Apr | 2022 | 0.00018253 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-26 07:33 | 2022-04-26 14:45 | 2 | 007:12 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22042600018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 432 | 2022-04-26 | 864 | keep | 0 | Apr | 2022 | 0.00058847 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-04-26 07:34 | 2022-04-26 07:35 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22042600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 1310 | keep | 0 | Apr | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
PONCE | 2022-04-26 07:40 | 2022-04-26 10:15 | 80 | 002:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | P22042600016 | New_Event |  |  | Include | Wildlife | 155 | 2022-04-26 | 12400 | keep | 0 | Apr | 2022 | 0.0084456 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-04-26 08:05 | 2022-04-26 11:05 | 100 | 003:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-04-26 | 18000 | keep | 0 | Apr | 2022 | 0.01226 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-04-26 08:14 | 2022-04-26 08:16 | 2450 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 12600 DE HUMACAO TC A VERDEMAR | C22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-26 | 4900 | keep | 0 | Apr | 2022 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-04-26 08:14 | 2022-04-26 08:16 | 640 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 12600 DE HUMACAO TC A VERDEMAR | C22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-04-26 | 1280 | keep | 0 | Apr | 2022 | 0.0008718 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
YAUCO | 2022-04-26 08:17 | 2022-04-26 08:18 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042600022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 1352 | keep | 0 | Apr | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
ARECIBO | 2022-04-26 08:27 | 2022-04-26 12:45 | 75 | 004:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22042600009 | New_Event | Cutout Failure | Include | Include | Equipment | 258 | 2022-04-26 | 19350 | keep | 0 | Apr | 2022 | 0.013179 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-04-26 08:28 | 2022-04-26 08:29 | 1526 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 1526 | keep | 0 | Apr | 2022 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2022-04-26 08:28 | 2022-04-26 08:29 | 308 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 308 | keep | 0 | Apr | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-04-26 08:28 | 2022-04-26 08:29 | 1397 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 1397 | keep | 0 | Apr | 2022 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2022-04-26 08:28 | 2022-04-26 08:29 | 2926 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 2926 | keep | 0 | Apr | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
VEGA BAJA | 2022-04-26 08:28 | 2022-04-26 08:29 | 27 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 27 | keep | 0 | Apr | 2022 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2022-04-26 08:28 | 2022-04-26 08:29 | 603 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 603 | keep | 0 | Apr | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-04-26 08:28 | 2022-04-26 08:29 | 6 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 6 | keep | 0 | Apr | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-04-26 08:28 | 2022-04-26 08:29 | 325 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 325 | keep | 0 | Apr | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2022-04-26 08:28 | 2022-04-26 08:29 | 172 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 172 | keep | 0 | Apr | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
VEGA BAJA | 2022-04-26 08:31 | 2022-04-26 08:37 | 1526 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600014 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-26 | 9156 | keep | 0 | Apr | 2022 | 0.0062361 | 0.0010394 | Sustained | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2022-04-26 08:31 | 2022-04-26 08:37 | 308 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600014 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-26 | 1848 | keep | 0 | Apr | 2022 | 0.0012587 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-04-26 08:31 | 2022-04-26 08:37 | 1397 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600014 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-26 | 8382 | keep | 0 | Apr | 2022 | 0.0057089 | 0.00095149 | Sustained | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2022-04-26 08:31 | 2022-04-26 08:37 | 2926 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600014 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-26 | 17556 | keep | 0 | Apr | 2022 | 0.011957 | 0.0019929 | Sustained | FALSE | FALSE | Not_TMED_Event | 2926
VEGA BAJA | 2022-04-26 08:31 | 2022-04-26 08:37 | 27 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600014 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-26 | 162 | keep | 0 | Apr | 2022 | 0.00011034 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2022-04-26 08:31 | 2022-04-26 08:37 | 603 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600014 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-26 | 3618 | keep | 0 | Apr | 2022 | 0.0024642 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-04-26 08:31 | 2022-04-26 08:37 | 6 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600014 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-26 | 36 | keep | 0 | Apr | 2022 | 2.4519e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-04-26 08:31 | 2022-04-26 08:37 | 325 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600014 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-26 | 1950 | keep | 0 | Apr | 2022 | 0.0013281 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2022-04-26 08:31 | 2022-04-26 08:37 | 172 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B22042600014 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-04-26 | 1032 | keep | 0 | Apr | 2022 | 0.00070289 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
BARRANQUITAS | 2022-04-26 08:45 | 2022-04-26 18:50 | 25 | 010:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22042600026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 605 | 2022-04-26 | 15125 | keep | 0 | Apr | 2022 | 0.010302 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-26 08:54 | 2022-04-26 08:55 | 686 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S22042600016 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 686 | keep | 0 | Apr | 2022 | 0.00046723 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-26 08:55 | 2022-04-26 12:19 | 50 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 50 EN CORTES DE LINEA | S22042600003 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 204 | 2022-04-26 | 10200 | keep | 0 | Apr | 2022 | 0.0069472 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-26 09:12 | 2022-04-26 12:09 | 192 | 002:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 Y 2 X 100 EN CORTES DE LINEA CRUCE POR PALOMAS | C22042600027 | New_Event |  |  | Include | Wildlife | 177 | 2022-04-26 | 33984 | keep | 0 | Apr | 2022 | 0.023146 | 0.00013077 | Sustained | FALSE | FALSE | Not_TMED_Event | 192
BAYAMON | 2022-04-26 09:23 | 2022-04-26 16:28 | 14 | 007:05 | P | DESGANCHE | 1 X 20 EN C/L SE REALIZO DESGANCHE | B22042600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2022-04-26 | 5950 | keep | 0 | Apr | 2022 | 0.0040525 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-04-26 09:27 | 2022-04-26 10:05 | 11 | 000:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN MONTURA SE REMPLAZO PORTAFUSIBLE | S22042600001 | New_Event | Cutout Failure | Include | Include | Equipment | 38 | 2022-04-26 | 418 | keep | 0 | Apr | 2022 | 0.0002847 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-04-26 09:46 | 2022-04-26 11:00 | 200 | 001:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22042600036 | New_Event | Cutout Failure | Include | Include | Equipment | 74 | 2022-04-26 | 14800 | keep | 0 | Apr | 2022 | 0.01008 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-04-26 09:53 | 2022-04-26 09:56 | 377 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | B22042600031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-26 | 1131 | keep | 0 | Apr | 2022 | 0.00077032 | 0.00025677 | Momentary | FALSE | FALSE | Not_TMED_Event | 377
MAYAGÃœEZ | 2022-04-26 10:13 | 2022-04-26 15:00 | 1 | 004:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22042600041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2022-04-26 | 287 | keep | 0 | Apr | 2022 | 0.00019547 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-26 10:17 | 2022-04-26 10:18 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-04 | S22042600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 1681 | keep | 0 | Apr | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-26 10:17 | 2022-04-26 10:18 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-04 | S22042600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 1598 | keep | 0 | Apr | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
HUMACAO | 2022-04-26 10:19 | 2022-04-26 19:00 | 82 | 008:41 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | C22042600043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2022-04-26 | 42722 | keep | 0 | Apr | 2022 | 0.029098 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
UTUADO | 2022-04-26 10:22 | 2022-04-26 10:59 | 1 | 000:37 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE NECESITA DESGANCHE | A22042600018 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 37 | 2022-04-26 | 37 | keep | 0 | Apr | 2022 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-26 10:33 | 2022-04-26 12:15 | 100 | 001:42 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S22042600030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-04-26 | 10200 | keep | 0 | Apr | 2022 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-26 10:41 | 2022-04-26 12:10 | 50 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | R22042600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2022-04-26 | 4450 | keep | 0 | Apr | 2022 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-26 10:47 | 2022-04-26 20:51 | 20 | 010:04 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DE T-632 @ T-633 Y SE NORMALIZO | B22042600051 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 604 | 2022-04-26 | 12080 | keep | 0 | Apr | 2022 | 0.0082276 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-04-26 10:53 | 2022-04-26 16:17 | 6 | 005:24 | P | ESTRUCTURA AVERIADA | ABRIR CORTE DE LINEA PARA PERSONAL DE INGENIERIA RETIRE POSTE QUE ESTA SOBRE RESIDENCIA | C22042600051 | New_Event | Defective Pole | Include | Include | Equipment | 324 | 2022-04-26 | 1944 | keep | 0 | Apr | 2022 | 0.001324 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-04-26 10:59 | 2022-04-26 13:35 | 2366 | 002:36 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO INTERRUPTOR | M22042600055 | New_Event | Wire Down | Include | Include | Equipment | 156 | 2022-04-26 | 369096 | keep | 0 | Apr | 2022 | 0.25139 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-04-26 11:00 | 2022-04-26 13:25 | 1 | 002:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA | B22042600039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 145 | 2022-04-26 | 145 | keep | 0 | Apr | 2022 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-04-26 11:04 | 2022-04-26 12:00 | 4 | 000:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR 2 AISLADORES PEGADOS A LINEA | P22042600034 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 56 | 2022-04-26 | 224 | keep | 0 | Apr | 2022 | 0.00015257 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-04-26 11:05 | 2022-04-26 13:15 | 100 | 002:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22042600030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-04-26 | 13000 | keep | 0 | Apr | 2022 | 0.0088542 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-26 11:05 | 2022-04-26 11:35 | 60 | 000:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | M22042600068 | New_Event | Wire Down | Include | Include | Equipment | 30 | 2022-04-26 | 1800 | keep | 0 | Apr | 2022 | 0.001226 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-26 11:09 | 2022-04-26 15:30 | 60 | 004:21 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22042600043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2022-04-26 | 15660 | keep | 0 | Apr | 2022 | 0.010666 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-26 11:19 | 2022-04-26 14:51 | 100 | 003:32 | P | TRANSFORMADOR AVERIADO | 1 X 100 Y 1 X80 EN CORTE DE LINEA ABIERTO DE SU-3 A T-50, T-50 AVERIADO | S22042600037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 212 | 2022-04-26 | 21200 | keep | 0 | Apr | 2022 | 0.014439 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-04-26 11:35 | 2022-04-26 12:02 | 100 | 000:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO SE CERRO CORTE DE LINEA | M22042600068 | Additional_clients | Wire Down | Include | Include | Equipment | 27 | 2022-04-26 | 2700 | keep | 0 | Apr | 2022 | 0.001839 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-26 11:37 | 2022-04-26 12:07 | 20 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR SE REPARO SECUNDARIA | C22042600054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-04-26 | 600 | keep | 0 | Apr | 2022 | 0.00040866 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-04-26 11:40 | 2022-04-26 23:46 | 40 | 012:06 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA SOTERRADA BY-220426-01 | B22042600046 | New_Event | UG Cable Fault | Include | Include | Equipment | 726 | 2022-04-26 | 29040 | keep | 0 | Apr | 2022 | 0.019779 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-26 11:45 | 2022-04-26 18:41 | 3 | 006:56 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARO SECUNDARIA Y SE DESGANCHO | B22042600047 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 416 | 2022-04-26 | 1248 | keep | 0 | Apr | 2022 | 0.00085001 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-04-26 11:49 | 2022-04-26 11:50 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042600073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 863 | keep | 0 | Apr | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
VEGA BAJA | 2022-04-26 11:56 | 2022-04-26 13:01 | 5 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | B22042600050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-04-26 | 325 | keep | 0 | Apr | 2022 | 0.00022136 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-04-26 12:00 | 2022-04-26 12:19 | 100 | 000:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R22042600012 | New_Event |  |  | Include | Wildlife | 19 | 2022-04-26 | 1900 | keep | 0 | Apr | 2022 | 0.0012941 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-26 12:02 | 2022-04-26 13:48 | 1 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22042600057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-04-26 | 106 | keep | 0 | Apr | 2022 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-26 12:03 | 2022-04-26 12:04 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042600079 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 863 | keep | 0 | Apr | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2022-04-26 12:05 | 2022-04-26 12:08 | 36 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1620-3 | S22042600048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-26 | 108 | keep | 0 | Apr | 2022 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-04-26 12:05 | 2022-04-26 12:08 | 1073 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1620-01 SE PROBO QUEDO EN SERVICIO | S22042600048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-26 | 3219 | keep | 0 | Apr | 2022 | 0.0021924 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
MAYAGÃœEZ | 2022-04-26 12:06 | 2022-04-26 12:07 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042600080 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 863 | keep | 0 | Apr | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-04-26 12:07 | 2022-04-26 12:09 | 1337 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO SE CERRO POR CONTROL SCADA NO SE REPORTO CAUSA | M22042600081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-26 | 2674 | keep | 0 | Apr | 2022 | 0.0018212 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
FAJARDO | 2022-04-26 12:12 | 2022-04-26 13:35 | 15 | 001:23 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R22042600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-04-26 | 1245 | keep | 0 | Apr | 2022 | 0.00084796 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-26 12:12 | 2022-04-26 17:31 | 80 | 005:19 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22042600085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2022-04-26 | 25520 | keep | 0 | Apr | 2022 | 0.017382 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-04-26 12:18 | 2022-04-26 15:42 | 12 | 003:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE X AVE | C22042600058 | New_Event |  |  | Include | Wildlife | 204 | 2022-04-26 | 2448 | keep | 0 | Apr | 2022 | 0.0016673 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-04-26 12:28 | 2022-04-26 15:32 | 9 | 003:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22042600060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2022-04-26 | 1656 | keep | 0 | Apr | 2022 | 0.0011279 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-04-26 12:30 | 2022-04-26 13:30 | 7 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR NEUTRAL Y CONECTORES SECUNDARIOS | S22042600053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-04-26 | 420 | keep | 0 | Apr | 2022 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-04-26 12:45 | 2022-04-27 12:30 | 1 | 023:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 10 EN RISER SE REMPLAZO CAJA PRIMARIA AVERIADA | M22042600092 | New_Event | Cutout Failure | Include | Include | Equipment | 1425 | 2022-04-26 | 1425 | keep | 0 | Apr | 2022 | 0.00097056 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-26 12:49 | 2022-04-26 15:49 | 63 | 003:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | C22042500064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-04-26 | 11340 | keep | 0 | Apr | 2022 | 0.0077236 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
GUAYAMA | 2022-04-26 12:59 | 2022-04-26 15:00 | 1 | 002:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE RISER PARA REEMPLAZAR AISLADOR | P22042600047 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 121 | 2022-04-26 | 121 | keep | 0 | Apr | 2022 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-26 13:05 | 2022-04-27 16:17 | 40 | 027:12 | P | DESGANCHE | ABRIO C/L PARA CONTRATISTA DESGANCHAR | C22042600067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1632 | 2022-04-26 | 65280 | keep | 0 | Apr | 2022 | 0.044462 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-26 13:07 | 2022-04-26 13:08 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22042600098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
PONCE | 2022-04-26 13:17 | 2022-04-26 14:07 | 25 | 000:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22042600051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2022-04-26 | 1250 | keep | 0 | Apr | 2022 | 0.00085137 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-04-26 13:18 | 2022-04-26 13:19 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 888 | keep | 0 | Apr | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-04-26 13:18 | 2022-04-26 13:19 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 393 | keep | 0 | Apr | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-04-26 13:18 | 2022-04-26 13:19 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-04-26 13:18 | 2022-04-26 13:19 | 372 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 372 | keep | 0 | Apr | 2022 | 0.00025337 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-04-26 13:18 | 2022-04-26 13:19 | 2530 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 2530 | keep | 0 | Apr | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-04-26 13:18 | 2022-04-26 13:19 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 199 | keep | 0 | Apr | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-04-26 13:18 | 2022-04-26 13:19 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 312 | keep | 0 | Apr | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-04-26 13:18 | 2022-04-26 13:19 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 4641 | keep | 0 | Apr | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-04-26 13:18 | 2022-04-26 13:19 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22042600100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 4381 | keep | 0 | Apr | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
SAN JUAN | 2022-04-26 13:21 | 2022-04-26 15:01 | 1681 | 001:40 | T | DESGANCHE | SE ABRIO N/O CONTRA 1346-6 PARA SECCIONALIZAR Y SE CERRO INTERRUPTOR 1303-1 X 1303-4 | S22042600103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-04-26 | 168100 | keep | 0 | Apr | 2022 | 0.11449 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-26 13:21 | 2022-04-26 16:04 | 1598 | 002:43 | T | DESGANCHE | SE ENCONTRO RAMA SOBRE LINEA AVE. VICTOR LABIOSA Y SE CERRO N/O CARR.177 ESQ. 176 | S22042600103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-04-26 | 260474 | keep | 0 | Apr | 2022 | 0.17741 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
PONCE | 2022-04-26 13:26 | 2022-04-26 13:33 | 2235 | 000:07 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CON RR ACTIVADO. SE VERIFICO CON PERSONAL QUE ESTABA EN LA SUBESTACION Y SE LE DIO PRUEBA QUEDANDO EN SERVICIO | P22042600057 | New_Event | Switch Failure | Include | Include | Equipment | 7 | 2022-04-26 | 15645 | keep | 0 | Apr | 2022 | 0.010656 | 0.0015222 | Sustained | FALSE | FALSE | Not_TMED_Event | 2235
PONCE | 2022-04-26 13:26 | 2022-04-26 13:33 | 713 | 000:07 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CON RR ACTIVADO. LLEVA LA CARGA DEL 2. SE VERIFICO CON PERSONAL QUE ESTABA EN LA SUBESTACION Y SE LE DIO PRUEBA QUEDANDO EN SERVICIO | P22042600057 | New_Event | Switch Failure | Include | Include | Equipment | 7 | 2022-04-26 | 4991 | keep | 0 | Apr | 2022 | 0.0033993 | 0.00048562 | Sustained | FALSE | FALSE | Not_TMED_Event | 713
PONCE | 2022-04-26 13:29 | 2022-04-26 15:10 | 10 | 001:41 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN TRANSFORMADOR POR DESGANCHE SECUNDARIO | P22042600055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 101 | 2022-04-26 | 1010 | keep | 0 | Apr | 2022 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-26 13:34 | 2022-04-26 17:45 | 55 | 004:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE RETIRO PENCA | C22042600073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-04-26 | 13805 | keep | 0 | Apr | 2022 | 0.0094025 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
AGUADILLA | 2022-04-26 13:35 | 2022-04-26 15:39 | 100 | 002:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | M22042600078 | Partial_restoration | Wire Down | Include | Include | Equipment | 124 | 2022-04-26 | 12400 | keep | 0 | Apr | 2022 | 0.0084456 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-26 13:38 | 2022-04-26 13:49 | 1 | 000:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA AVE CRUZO LINEAS | M22042600029 | New_Event |  |  | Include | Wildlife | 11 | 2022-04-26 | 11 | keep | 0 | Apr | 2022 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-26 13:44 | 2022-04-26 18:46 | 1 | 005:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER Y 2 X 20 @ BOMBAS | B22042600056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 302 | 2022-04-26 | 302 | keep | 0 | Apr | 2022 | 0.00020569 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-26 13:49 | 2022-04-26 13:50 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 888 | keep | 0 | Apr | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-04-26 13:49 | 2022-04-26 13:50 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 393 | keep | 0 | Apr | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-04-26 13:49 | 2022-04-26 13:50 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-04-26 13:49 | 2022-04-26 13:50 | 372 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 372 | keep | 0 | Apr | 2022 | 0.00025337 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-04-26 13:49 | 2022-04-26 13:50 | 2530 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 2530 | keep | 0 | Apr | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-04-26 13:49 | 2022-04-26 13:50 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 199 | keep | 0 | Apr | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-04-26 13:49 | 2022-04-26 13:50 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 312 | keep | 0 | Apr | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-04-26 13:49 | 2022-04-26 13:50 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 4641 | keep | 0 | Apr | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-04-26 13:50 | 2022-04-26 15:04 | 1 | 001:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA AVE CRUZO LINEAS | M22042600029 | Partial_restoration |  |  | Include | Wildlife | 74 | 2022-04-26 | 74 | keep | 0 | Apr | 2022 | 5.0401e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-26 13:56 | 2022-04-26 15:15 | 15 | 001:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | C22042600079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-04-26 | 1185 | keep | 0 | Apr | 2022 | 0.0008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-04-26 13:56 | 2022-04-26 13:57 | 2235 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042600080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 2235 | keep | 0 | Apr | 2022 | 0.0015222 | 0.0015222 | Momentary | FALSE | FALSE | Not_TMED_Event | 2235
PONCE | 2022-04-26 13:56 | 2022-04-26 13:57 | 713 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | P22042600080 | Partial_restoration | Switch Failure | Include | Include | Equipment | 1 | 2022-04-26 | 713 | keep | 0 | Apr | 2022 | 0.00048562 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-26 13:57 | 2022-04-26 16:18 | 745 | 002:21 | P | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA DE INSPECCION DEL 4401-03 QUEMADO LA CARGA DEL 4401-02 ESTABA TRANSFERIDA AL 4401-03 SE NORMALIZARON LAS CARGAS Y SE REEMPLAZO MACHETE | P22042600058 | New_Event | Switch Failure | Include | Include | Equipment | 141 | 2022-04-26 | 105045 | keep | 0 | Apr | 2022 | 0.071546 | 0.00050742 | Sustained | FALSE | FALSE | Not_TMED_Event | 745
MAYAGÃœEZ | 2022-04-26 14:08 | 2022-04-26 23:00 | 30 | 008:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | M22042600108 | New_Event | Wire Down | Include | Include | Equipment | 532 | 2022-04-26 | 15960 | keep | 0 | Apr | 2022 | 0.01087 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-26 14:13 | 2022-04-26 14:14 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22042600031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 1227 | keep | 0 | Apr | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
MAYAGÃœEZ | 2022-04-26 14:18 | 2022-04-27 02:39 | 80 | 012:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22042600109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 741 | 2022-04-26 | 59280 | keep | 0 | Apr | 2022 | 0.040375 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-26 14:20 | 2022-04-26 15:00 | 12 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C22042600080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-04-26 | 480 | keep | 0 | Apr | 2022 | 0.00032693 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-04-26 14:20 | 2022-04-26 15:51 | 1 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042600032 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2022-04-26 | 91 | keep | 0 | Apr | 2022 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-04-26 14:23 | 2022-04-26 16:54 | 15 | 002:31 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22042600033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-04-26 | 2265 | keep | 0 | Apr | 2022 | 0.0015427 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-04-26 14:24 | 2022-04-26 15:28 | 2 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA NEUTRAL ABIERTA | R22042600041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2022-04-26 | 128 | keep | 0 | Apr | 2022 | 8.718e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-04-26 14:25 | 2022-04-26 15:46 | 30 | 001:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE HABRE RISER PARA REMPLAZAR CAJA PRIMARIA Y CERRAR PUENTE Y NORMALIZAR CARGAS | S22042600101 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2022-04-26 | 2430 | keep | 0 | Apr | 2022 | 0.0016551 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-26 14:25 | 2022-04-26 18:55 | 75 | 004:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA EMPLEADO NO ENCONTRO CAUSA | A22042600035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2022-04-26 | 20250 | keep | 0 | Apr | 2022 | 0.013792 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-04-26 14:30 | 2022-04-26 15:16 | 11 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REMPLAZAR BARRA PEDESTAL | S22042600094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2022-04-26 | 506 | keep | 0 | Apr | 2022 | 0.00034463 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-04-26 14:30 | 2022-04-27 09:17 | 90 | 018:47 | P | DESGANCHE | 1 X 50 Y 1 X 20 EN TRANSFORMADOR | C22042600085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1127 | 2022-04-26 | 101430 | keep | 0 | Apr | 2022 | 0.069084 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-04-26 14:35 | 2022-04-26 18:23 | 20 | 003:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042600110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2022-04-26 | 4560 | keep | 0 | Apr | 2022 | 0.0031058 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-26 14:36 | 2022-04-26 17:30 | 25 | 002:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN PROVISIONAL SE DEJO T-5 CONTRATISTA PARTIO CABLE PROVISIONAL SE DEJO FUERA 4 CLIENTES | S22042600108 | New_Event |  |  | Include | Wildlife | 174 | 2022-04-26 | 4350 | keep | 0 | Apr | 2022 | 0.0029628 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-04-26 14:47 | 2022-04-26 20:04 | 100 | 005:17 | P | DESGANCHE | 3 X 80 EN CONVERTIDOR | S22042600127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2022-04-26 | 31700 | keep | 0 | Apr | 2022 | 0.021591 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-26 14:47 | 2022-04-26 16:27 | 70 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B22042600061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-04-26 | 7000 | keep | 0 | Apr | 2022 | 0.0047677 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-04-26 14:51 | 2022-04-26 21:28 | 9 | 006:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-50 Y 1 X 20 EN SU-3 | S22042600212 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 397 | 2022-04-26 | 3573 | keep | 0 | Apr | 2022 | 0.0024336 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-26 15:00 | 2022-04-26 15:01 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22042600115 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-04-26 15:04 | 2022-04-26 15:05 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 888 | keep | 0 | Apr | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-04-26 15:04 | 2022-04-26 15:05 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 393 | keep | 0 | Apr | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-04-26 15:04 | 2022-04-26 15:05 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 4 | keep | 0 | Apr | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-04-26 15:04 | 2022-04-26 15:05 | 372 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 372 | keep | 0 | Apr | 2022 | 0.00025337 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-04-26 15:04 | 2022-04-26 15:05 | 2530 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 2530 | keep | 0 | Apr | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-04-26 15:04 | 2022-04-26 15:05 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 199 | keep | 0 | Apr | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-04-26 15:04 | 2022-04-26 15:05 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 312 | keep | 0 | Apr | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-04-26 15:04 | 2022-04-26 15:05 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22042600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-26 | 4641 | keep | 0 | Apr | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-04-26 15:05 | 2022-04-26 18:09 | 1 | 003:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA AVE CRUZO LINEAS | M22042600029 | Partial_restoration |  |  | Include | Wildlife | 184 | 2022-04-26 | 184 | keep | 0 | Apr | 2022 | 0.00012532 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-04-26 15:10 | 2022-04-26 17:27 | 10 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE PRIMARIO EN TRANSFORMADOR | P22042600067 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2022-04-26 | 1370 | keep | 0 | Apr | 2022 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-26 15:22 | 2022-04-26 16:45 | 12 | 001:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | C22042600092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-04-26 | 996 | keep | 0 | Apr | 2022 | 0.00067837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-04-26 15:38 | 2022-04-26 18:23 | 50 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 40 EN PROVISIONAL | S22042600137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-04-26 | 8250 | keep | 0 | Apr | 2022 | 0.005619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-26 15:39 | 2022-04-26 15:40 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22042600127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-04-26 15:48 | 2022-04-27 01:25 | 50 | 009:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22042600128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 577 | 2022-04-26 | 28850 | keep | 0 | Apr | 2022 | 0.01965 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-04-26 16:00 | 2022-04-26 16:56 | 7 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22042600049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2022-04-26 | 392 | keep | 0 | Apr | 2022 | 0.00026699 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-04-26 16:01 | 2022-04-26 16:22 | 40 | 000:21 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | C22042600081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 21 | 2022-04-26 | 840 | keep | 0 | Apr | 2022 | 0.00057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-26 16:02 | 2022-04-26 20:15 | 50 | 004:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22042600067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2022-04-26 | 12650 | keep | 0 | Apr | 2022 | 0.0086159 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-26 16:24 | 2022-04-26 17:10 | 713 | 000:46 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA REEMPLAZAR MACHETE DE BARRA DE INSPECION QUEMADO FASE B | P22042600076 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 46 | 2022-04-26 | 32798 | keep | 0 | Apr | 2022 | 0.022339 | 0.00048562 | Sustained | FALSE | FALSE | Not_TMED_Event | 713
SAN JUAN | 2022-04-26 16:38 | 2022-04-26 16:40 | 1681 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-4 | S22042600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-26 | 3362 | keep | 0 | Apr | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-26 16:38 | 2022-04-26 16:40 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-4 | S22042600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-26 | 3196 | keep | 0 | Apr | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2022-04-26 16:40 | 2022-04-26 16:45 | 100 | 000:05 | P | CABLE SOTERRADO AVERIADO | DISPARO PERSONAL SOTERRADO REALIZANDO INSPECCION Y CERRARON MH-3 A MH-4, SE ABRIO DE NUEVO Y SE CERRO INTERRUPTOR | S22042600000 | New_Event | UG Cable Fault | Include | Include | Equipment | 5 | 2022-04-26 | 500 | keep | 0 | Apr | 2022 | 0.00034055 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-26 16:45 | 2022-04-26 23:19 | 45 | 006:34 | P | DESGANCHE | 1 X 65 EN C/L | C22042600098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2022-04-26 | 17730 | keep | 0 | Apr | 2022 | 0.012076 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-04-26 16:48 | 2022-04-26 19:01 | 34 | 002:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA SE REMPLAZO PIN POLE TOP PARTIDO | R22042600046 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 133 | 2022-04-26 | 4522 | keep | 0 | Apr | 2022 | 0.0030799 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2022-04-26 16:58 | 2022-04-26 18:12 | 249 | 001:14 | P | DESGANCHE | 2 X 80 EN CORTE DELINEA Y SE RETRIO RAMA | C22042600099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-04-26 | 18426 | keep | 0 | Apr | 2022 | 0.01255 | 0.00016959 | Sustained | FALSE | FALSE | Not_TMED_Event | 249
MAYAGÃœEZ | 2022-04-26 16:58 | 2022-04-26 20:40 | 80 | 003:42 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22042600139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2022-04-26 | 17760 | keep | 0 | Apr | 2022 | 0.012096 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-04-26 17:00 | 2022-04-26 18:15 | 10 | 001:15 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA POR UNO DE 50KVA | A22042600044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 75 | 2022-04-26 | 750 | keep | 0 | Apr | 2022 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-26 17:30 | 2022-04-27 12:27 | 8 | 018:57 | P | CABLE SOTERRADO AVERIADO | SE TIRO TRAMO PROVISIONAL Y SE REPARO TERMINACION | S22042600165 | New_Event | UG Cable Fault | Include | Include | Equipment | 1137 | 2022-04-26 | 9096 | keep | 0 | Apr | 2022 | 0.0061952 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-04-26 17:33 | 2022-04-27 13:44 | 1 | 020:11 | P | SOBRECARGA | 1 X 15 EN TRANSFORMADOR SOBRE CARGA | A22042600046 | New_Event | Trip Due To Overload | Include | Include | Other | 1211 | 2022-04-26 | 1211 | keep | 0 | Apr | 2022 | 0.00082481 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-26 17:35 | 2022-04-26 21:13 | 304 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S22042600164 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2022-04-26 | 66272 | keep | 0 | Apr | 2022 | 0.045138 | 0.00020705 | Sustained | FALSE | FALSE | Not_TMED_Event | 304
ARECIBO | 2022-04-26 18:10 | 2022-04-26 18:11 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22042600049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 5042 | keep | 0 | Apr | 2022 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
BARRANQUITAS | 2022-04-26 18:34 | 2022-04-26 20:15 | 12 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C22042600121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-04-26 | 1212 | keep | 0 | Apr | 2022 | 0.00082549 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-26 19:02 | 2022-04-26 19:04 | 723 | 000:02 | T | NO SE REPORTO CAUSA | 1711-02 DISPARO Y SE CERRO POR SCADA LLEVA 1711-05 | B22042600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-26 | 1446 | keep | 0 | Apr | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-04-26 19:02 | 2022-04-26 19:04 | 1976 | 000:02 | T | NO SE REPORTO CAUSA | 1711-02 DISPARO Y SE CERRO POR SCADA LLEVA 1711-05 | B22042600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-26 | 3952 | keep | 0 | Apr | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-04-26 19:02 | 2022-04-26 19:04 | 1812 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22042600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-26 | 3624 | keep | 0 | Apr | 2022 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
PONCE | 2022-04-26 19:06 | 2022-04-26 19:07 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042600099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-26 | 4035 | keep | 0 | Apr | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
SAN JUAN | 2022-04-26 19:20 | 2022-04-27 08:28 | 51 | 013:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | S22042600203 | New_Event | Cutout Failure | Include | Include | Equipment | 788 | 2022-04-26 | 40188 | keep | 0 | Apr | 2022 | 0.027372 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
HUMACAO | 2022-04-26 19:44 | 2022-04-27 11:29 | 120 | 015:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22042600140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 945 | 2022-04-26 | 113400 | keep | 0 | Apr | 2022 | 0.077236 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BARRANQUITAS | 2022-04-26 20:21 | 2022-04-27 07:10 | 100 | 010:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C22042600149 | New_Event | Cutout Failure | Include | Include | Equipment | 649 | 2022-04-26 | 64900 | keep | 0 | Apr | 2022 | 0.044203 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-26 20:22 | 2022-04-27 08:24 | 86 | 012:02 | P | HERRAJE ROTO O PODRIDO | SE ELIMINO CRUCETA PARTIDA Y SE INSTALO RIGIDO 2 X 80 EN CORTE DE LINEA | S22042600214 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 722 | 2022-04-26 | 62092 | keep | 0 | Apr | 2022 | 0.042291 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
MAYAGÃœEZ | 2022-04-26 20:25 | 2022-04-26 23:44 | 75 | 003:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042600174 | New_Event | Bad Weather | Include | Include | Weather | 199 | 2022-04-26 | 14925 | keep | 0 | Apr | 2022 | 0.010165 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-04-26 20:35 | 2022-04-27 09:46 | 8 | 013:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MONTURA Y SE CERRO PUENTE DE LINEA A CAJA TRANSFORMADOR | S22042600218 | New_Event | Wire Down | Include | Include | Equipment | 791 | 2022-04-26 | 6328 | keep | 0 | Apr | 2022 | 0.00431 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-04-26 20:42 | 2022-04-27 00:29 | 100 | 003:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE ABRIERON PUENTES PRIMARIOS PARA SECCIONALIZAR AVERIA DE LINEAS PRIMARIAS PARTIDAS NO SE REPARO LA LINEA LA DEJARON PARA EL OTRO DIA | M22042600183 | New_Event | Wire Down | Include | Include | Equipment | 227 | 2022-04-26 | 22700 | keep | 0 | Apr | 2022 | 0.015461 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-04-26 21:38 | 2022-04-27 09:47 | 60 | 012:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22042600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 729 | 2022-04-26 | 43740 | keep | 0 | Apr | 2022 | 0.029791 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-04-26 21:44 | 2022-04-27 09:58 | 80 | 012:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22042600192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 734 | 2022-04-26 | 58720 | keep | 0 | Apr | 2022 | 0.039994 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-04-26 22:02 | 2022-04-27 06:45 | 90 | 008:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22042600109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 523 | 2022-04-26 | 47070 | keep | 0 | Apr | 2022 | 0.032059 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-04-26 22:04 | 2022-04-27 10:02 | 15 | 011:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M22042600200 | New_Event |  |  | Include | Wildlife | 718 | 2022-04-26 | 10770 | keep | 0 | Apr | 2022 | 0.0073354 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-26 23:52 | 2022-04-27 01:02 | 70 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A LINEA | B22042600091 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2022-04-26 | 4900 | keep | 0 | Apr | 2022 | 0.0033374 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2022-04-27 00:02 | 2022-04-27 00:03 | 2722 | 000:01 | T | DESGANCHE | RECIERRE | R22042700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-27 | 2722 | keep | 0 | Apr | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2022-04-27 00:03 | 2022-04-27 08:54 | 223 | 008:51 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO BEJUCO DE LA LINEA | R22042700006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 531 | 2022-04-27 | 118413 | keep | 0 | Apr | 2022 | 0.080651 | 0.00015188 | Sustained | FALSE | FALSE | Not_TMED_Event | 223
MAYAGÃœEZ | 2022-04-27 00:27 | 2022-04-27 03:04 | 50 | 002:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22042700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-04-27 | 7850 | keep | 0 | Apr | 2022 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-27 00:29 | 2022-04-27 19:00 | 150 | 018:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M22042600183 | Additional_clients | Wire Down | Include | Include | Equipment | 1111 | 2022-04-27 | 166650 | keep | 0 | Apr | 2022 | 0.1135 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-27 01:13 | 2022-04-27 16:27 | 17 | 015:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22042700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 914 | 2022-04-27 | 15538 | keep | 0 | Apr | 2022 | 0.010583 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-04-27 01:48 | 2022-04-27 01:49 | 2076 | 000:01 | P | DESGANCHE | RECIERRE DE INTERRUPTOR 40% DE LA CARGA POR EL 1718-03 | B22042700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-27 | 2076 | keep | 0 | Apr | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-04-27 01:48 | 2022-04-27 01:49 | 2605 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR LLEVA 40% DE 1710-05 | B22042700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-27 | 2605 | keep | 0 | Apr | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-04-27 01:49 | 2022-04-27 05:14 | 45 | 003:25 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B22042700004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 205 | 2022-04-27 | 9225 | keep | 0 | Apr | 2022 | 0.0062831 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-04-27 02:53 | 2022-04-27 02:55 | 2888 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR BAJANTE ZAFADO DE LA ENTRADA DE MACHETE | A22042700001 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-04-27 | 5776 | keep | 0 | Apr | 2022 | 0.003934 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
ARECIBO | 2022-04-27 02:55 | 2022-04-27 09:07 | 855 | 006:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE MACHETE | A22042700029 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 372 | 2022-04-27 | 318060 | keep | 0 | Apr | 2022 | 0.21663 | 0.00058234 | Sustained | FALSE | FALSE | Not_TMED_Event | 855
HUMACAO | 2022-04-27 04:43 | 2022-04-27 08:12 | 150 | 003:29 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C22042700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2022-04-27 | 31350 | keep | 0 | Apr | 2022 | 0.021352 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-04-27 05:13 | 2022-04-27 10:50 | 41 | 005:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C22042700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2022-04-27 | 13817 | keep | 0 | Apr | 2022 | 0.0094107 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
ARECIBO | 2022-04-27 06:33 | 2022-04-27 06:34 | 1986 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22042700036 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-04-27 | 1986 | keep | 0 | Apr | 2022 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2022-04-27 06:34 | 2022-04-27 11:27 | 1 | 004:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE RISER | A22042700096 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 293 | 2022-04-27 | 293 | keep | 0 | Apr | 2022 | 0.00019956 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-27 06:58 | 2022-04-27 11:35 | 80 | 004:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22042700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2022-04-27 | 22160 | keep | 0 | Apr | 2022 | 0.015093 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-04-27 07:10 | 2022-04-27 07:11 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
ARECIBO | 2022-04-27 07:17 | 2022-04-27 10:40 | 40 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042700049 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2022-04-27 | 8120 | keep | 0 | Apr | 2022 | 0.0055305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-04-27 07:21 | 2022-04-27 07:22 | 4132 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | P22042700006 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-04-27 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-04-27 07:21 | 2022-04-27 07:22 | 4279 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | P22042700006 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-04-27 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-04-27 07:21 | 2022-04-27 07:22 | 464 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | P22042700006 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-04-27 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-04-27 07:22 | 2022-04-27 08:36 | 20 | 001:14 | P | PARARRAYOS DEFECTUOSO | 2 X 65 EN CORTE DE LINEA PARARRAYO QUEMADO | P22042700007 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 74 | 2022-04-27 | 1480 | keep | 0 | Apr | 2022 | 0.001008 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-27 07:50 | 2022-04-27 07:52 | 172 | 000:02 | T | DESGANCHE | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22042700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-04-27 | 344 | keep | 0 | Apr | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
ARECIBO | 2022-04-27 07:51 | 2022-04-27 09:02 | 15 | 001:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22042700058 | New_Event | Bad Weather | Include | Include | Weather | 71 | 2022-04-27 | 1065 | keep | 0 | Apr | 2022 | 0.00072537 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-04-27 07:51 | 2022-04-27 10:00 | 60 | 002:09 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | A22042700060 | New_Event | Bad Weather | Include | Include | Weather | 129 | 2022-04-27 | 7740 | keep | 0 | Apr | 2022 | 0.0052717 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-27 07:52 | 2022-04-27 10:37 | 8 | 002:45 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | R22042700027 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-04-27 | 1320 | keep | 0 | Apr | 2022 | 0.00089905 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-04-27 08:11 | 2022-04-27 10:42 | 1 | 002:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REEMPLAZO CAJA PRIMARIA Y PORTAFUSIBLE | R22042700025 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2022-04-27 | 151 | keep | 0 | Apr | 2022 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-27 08:16 | 2022-04-27 16:41 | 6 | 008:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR Y RETEZAR SECUNDARIA EN VARIOS PUNTOS | C22042700029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 505 | 2022-04-27 | 3030 | keep | 0 | Apr | 2022 | 0.0020637 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-27 08:26 | 2022-04-27 15:00 | 366 | 006:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO AISLADOR | S22042700011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 394 | 2022-04-27 | 144204 | keep | 0 | Apr | 2022 | 0.098217 | 0.00024928 | Sustained | FALSE | FALSE | Not_TMED_Event | 366
CANOVANAS | 2022-04-27 08:37 | 2022-04-27 10:45 | 1 | 002:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 100 KVA T-22A CON DERRAME DE ACEITE | R22042700029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 128 | 2022-04-27 | 128 | keep | 0 | Apr | 2022 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-27 08:43 | 2022-04-27 08:45 | 1844 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1907-04 LLEVANDO 1346-02, 5% 1346-03 Y 60% 1529-15 POR VIA LIBRE SE CERRO POR SCADA | S22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-27 | 3688 | keep | 0 | Apr | 2022 | 0.0025119 | 0.0012559 | Momentary | FALSE | FALSE | Not_TMED_Event | 1844
BAYAMON | 2022-04-27 08:43 | 2022-04-27 08:45 | 121 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1907-04 LLEVANDO 1346-02, 5% 1346-03 Y 60% 1529-15 POR VIA LIBRE SE CERRO POR SCADA | S22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-27 | 242 | keep | 0 | Apr | 2022 | 0.00016483 | 8.2413e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 121
BAYAMON | 2022-04-27 08:43 | 2022-04-27 08:45 | 1081 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1907-04 LLEVANDO 1346-02, 5% 1346-03 Y 60% 1529-15 POR VIA LIBRE SE CERRO POR SCADA | S22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-27 | 2162 | keep | 0 | Apr | 2022 | 0.0014725 | 0.00073626 | Momentary | FALSE | FALSE | Not_TMED_Event | 1081
BAYAMON | 2022-04-27 08:43 | 2022-04-27 08:45 | 2466 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1907-04 LLEVANDO 1346-02, 5% 1346-03 Y 60% 1529-15 POR VIA LIBRE SE CERRO POR SCADA | S22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-27 | 4932 | keep | 0 | Apr | 2022 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
PONCE | 2022-04-27 08:57 | 2022-04-27 10:00 | 1922 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22042700042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-04-27 | 121086 | keep | 0 | Apr | 2022 | 0.082471 | 0.0013091 | Sustained | FALSE | FALSE | Not_TMED_Event | 1922
PONCE | 2022-04-27 08:57 | 2022-04-27 10:00 | 2235 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 NO HABIA RTU SE ESPERO POR SUBESTACIONES PARA ENERGIZARLA | P22042700042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-04-27 | 140805 | keep | 0 | Apr | 2022 | 0.095902 | 0.0015222 | Sustained | FALSE | FALSE | Not_TMED_Event | 2235
PONCE | 2022-04-27 08:57 | 2022-04-27 10:00 | 713 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22042700042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-04-27 | 44919 | keep | 0 | Apr | 2022 | 0.030594 | 0.00048562 | Sustained | FALSE | FALSE | Not_TMED_Event | 713
PONCE | 2022-04-27 08:57 | 2022-04-27 10:00 | 1067 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22042700042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-04-27 | 67221 | keep | 0 | Apr | 2022 | 0.045784 | 0.00072673 | Sustained | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2022-04-27 08:57 | 2022-04-27 10:00 | 1293 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22042700043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-04-27 | 81459 | keep | 0 | Apr | 2022 | 0.055481 | 0.00088066 | Sustained | FALSE | FALSE | Not_TMED_Event | 1293
PONCE | 2022-04-27 08:57 | 2022-04-27 10:00 | 426 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22042700043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-04-27 | 26838 | keep | 0 | Apr | 2022 | 0.018279 | 0.00029015 | Sustained | FALSE | FALSE | Not_TMED_Event | 426
PONCE | 2022-04-27 08:57 | 2022-04-27 10:00 | 1556 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22042700043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-04-27 | 98028 | keep | 0 | Apr | 2022 | 0.066766 | 0.0010598 | Sustained | FALSE | FALSE | Not_TMED_Event | 1556
BAYAMON | 2022-04-27 08:58 | 2022-04-27 21:44 | 65 | 012:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22042700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 766 | 2022-04-27 | 49790 | keep | 0 | Apr | 2022 | 0.033912 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-04-27 09:13 | 2022-04-27 13:31 | 15 | 004:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | B22042700028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2022-04-27 | 3870 | keep | 0 | Apr | 2022 | 0.0026358 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-04-27 09:26 | 2022-04-27 11:37 | 250 | 002:11 | P | DESGANCHE | 3 X 140 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22042700018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-04-27 | 32750 | keep | 0 | Apr | 2022 | 0.022306 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2022-04-27 09:40 | 2022-04-27 14:00 | 20 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042700035 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2022-04-27 | 5200 | keep | 0 | Apr | 2022 | 0.0035417 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-04-27 09:48 | 2022-04-27 16:10 | 33 | 006:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22042700036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 382 | 2022-04-27 | 12606 | keep | 0 | Apr | 2022 | 0.0085859 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
ARECIBO | 2022-04-27 10:21 | 2022-04-27 12:25 | 30 | 002:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INDICA REQUIERE DESGANCHE DE EMERGENCIA | A22042700093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-04-27 | 3720 | keep | 0 | Apr | 2022 | 0.0025337 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-04-27 10:30 | 2022-04-27 14:14 | 20 | 003:44 | P | DESGANCHE | ABRIO CORTE DE LINEA PARA RETEZAR LINEA AL ALCANCE DE LA MANO, DESGANCHO Y REPARO SECUNDARIA EN VARIOS PUNTOS | C22042700042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-04-27 | 4480 | keep | 0 | Apr | 2022 | 0.0030513 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-04-27 10:38 | 2022-04-27 12:43 | 200 | 002:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042700070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-04-27 | 25000 | keep | 0 | Apr | 2022 | 0.017027 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-04-27 10:45 | 2022-04-27 16:20 | 25 | 005:35 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75KVA POR 100KVA | S22042700042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 335 | 2022-04-27 | 8375 | keep | 0 | Apr | 2022 | 0.0057042 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-27 10:54 | 2022-04-27 17:37 | 25 | 006:43 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22042700045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 403 | 2022-04-27 | 10075 | keep | 0 | Apr | 2022 | 0.006862 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-04-27 11:00 | 2022-04-27 12:23 | 100 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 80 SMU EN SU-2 NO SE ENCONTRO CAUSA | P22042700081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2022-04-27 | 8300 | keep | 0 | Apr | 2022 | 0.0056531 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-27 11:13 | 2022-04-27 11:16 | 1048 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-27 | 3144 | keep | 0 | Apr | 2022 | 0.0021414 | 0.00071379 | Momentary | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2022-04-27 11:15 | 2022-04-27 13:38 | 7 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | S22042700046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2022-04-27 | 1001 | keep | 0 | Apr | 2022 | 0.00068178 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-04-27 11:15 | 2022-04-27 14:13 | 100 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042700085 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2022-04-27 | 17800 | keep | 0 | Apr | 2022 | 0.012123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-27 11:16 | 2022-04-28 09:32 | 6 | 022:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | B22042700047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1336 | 2022-04-27 | 8016 | keep | 0 | Apr | 2022 | 0.0054597 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-04-27 11:19 | 2022-04-27 15:04 | 2 | 003:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A22042700097 | New_Event | Bad Weather | Include | Include | Weather | 225 | 2022-04-27 | 450 | keep | 0 | Apr | 2022 | 0.00030649 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-04-27 11:27 | 2022-04-27 16:37 | 150 | 005:10 | P | DESGANCHE | 3 X 80 EN C/L | C22042700056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-04-27 | 46500 | keep | 0 | Apr | 2022 | 0.031671 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-04-27 11:36 | 2022-04-27 13:25 | 382 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN RISER HACIA SU-1 CRUCE POR PALOMA | R22042700042 | New_Event |  |  | Include | Wildlife | 109 | 2022-04-27 | 41638 | keep | 0 | Apr | 2022 | 0.028359 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
UTUADO | 2022-04-27 11:37 | 2022-04-27 14:25 | 15 | 002:48 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO DOS PARARRAYOS CRUZADOS | A22042700100 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 168 | 2022-04-27 | 2520 | keep | 0 | Apr | 2022 | 0.0017164 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-04-27 11:42 | 2022-04-27 11:43 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042700099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 6285 | keep | 0 | Apr | 2022 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
VEGA BAJA | 2022-04-27 11:49 | 2022-04-27 11:50 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22042700053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
ARECIBO | 2022-04-27 11:58 | 2022-04-27 14:10 | 50 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASES | A22042700105 | New_Event |  |  | Include | Wildlife | 132 | 2022-04-27 | 6600 | keep | 0 | Apr | 2022 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-27 11:59 | 2022-04-27 12:00 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042700105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
BARRANQUITAS | 2022-04-27 12:00 | 2022-04-27 12:27 | 16 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRA EN PEDESTAL | C22042700060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2022-04-27 | 432 | keep | 0 | Apr | 2022 | 0.00029423 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-04-27 12:03 | 2022-04-27 12:04 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042700105 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
SAN JUAN | 2022-04-27 12:06 | 2022-04-27 14:40 | 12 | 002:34 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE SECUNDARIO | S22042700048 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 154 | 2022-04-27 | 1848 | keep | 0 | Apr | 2022 | 0.0012587 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-04-27 12:14 | 2022-04-27 12:15 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22042700114 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 176 | keep | 0 | Apr | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
BAYAMON | 2022-04-27 12:33 | 2022-04-27 18:09 | 300 | 005:36 | P | ESTRUCTURA AVERIADA | 1 X 100 Y 1 X 80 EN C/L SE SECCIONALIZO CONDUCTOR EN EL SUELO PARA LEVANTAR CON GOI BY220427-01 | B22042700056 | New_Event | Defective Pole | Include | Include | Equipment | 336 | 2022-04-27 | 100800 | keep | 0 | Apr | 2022 | 0.068654 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2022-04-27 12:45 | 2022-04-27 12:46 | 1835 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22042700064 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-27 | 1835 | keep | 0 | Apr | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2022-04-27 12:46 | 2022-04-27 16:11 | 80 | 003:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | C22042700065 | 1st_after_momentary |  |  | Include | Wildlife | 205 | 2022-04-27 | 16400 | keep | 0 | Apr | 2022 | 0.01117 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-04-27 12:53 | 2022-04-27 17:44 | 5 | 004:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZAR BARRAS EN PEDESTAL | P22042700086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 291 | 2022-04-27 | 1455 | keep | 0 | Apr | 2022 | 0.00099099 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-04-27 12:54 | 2022-04-27 15:06 | 88 | 002:12 | P | DESGANCHE | 1 X 100 EN C/L | C22042700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-04-27 | 11616 | keep | 0 | Apr | 2022 | 0.0079116 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
MAYAGÃœEZ | 2022-04-27 12:54 | 2022-04-27 17:00 | 50 | 004:06 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042700123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2022-04-27 | 12300 | keep | 0 | Apr | 2022 | 0.0083775 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-27 12:56 | 2022-04-27 13:19 | 30 | 000:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR BAJANTE PRIMARIO | P22042700087 | New_Event | Wire Down | Include | Include | Equipment | 23 | 2022-04-27 | 690 | keep | 0 | Apr | 2022 | 0.00046996 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-04-27 13:08 | 2022-04-27 14:06 | 57 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA CRUCE POR CHANGO | R22042700051 | New_Event |  |  | Include | Wildlife | 58 | 2022-04-27 | 3306 | keep | 0 | Apr | 2022 | 0.0022517 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
ARECIBO | 2022-04-27 13:09 | 2022-04-27 16:10 | 80 | 003:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A22042700113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-04-27 | 14480 | keep | 0 | Apr | 2022 | 0.0098623 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-27 13:15 | 2022-04-27 14:29 | 55 | 001:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22042700058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-04-27 | 4070 | keep | 0 | Apr | 2022 | 0.0027721 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-04-27 13:25 | 2022-04-27 14:02 | 191 | 000:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | POR CRUCE DE PALOMA SE REEMPLAZO CAJA PRIMARIA | R22042700042 | Partial_restoration |  |  | Include | Wildlife | 37 | 2022-04-27 | 7067 | keep | 0 | Apr | 2022 | 0.0048133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-27 13:28 | 2022-04-27 16:33 | 1 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA DE TRANSFORMADOR | P22042700090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-04-27 | 185 | keep | 0 | Apr | 2022 | 0.000126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-27 13:36 | 2022-04-27 14:48 | 4 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR Y REMPLAZO BAJANTE SECUNDARIO | C22042700044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2022-04-27 | 288 | keep | 0 | Apr | 2022 | 0.00019616 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-04-27 13:41 | 2022-04-27 13:42 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1303-4 SE PROBO QUEDO EN SERVICIO | S22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 1681 | keep | 0 | Apr | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-27 13:41 | 2022-04-27 13:42 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1303-4 SE PROBO QUEDO EN SERVICIO | S22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 1598 | keep | 0 | Apr | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
CAGUAS | 2022-04-27 13:43 | 2022-04-27 17:22 | 40 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22042700075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-04-27 | 8760 | keep | 0 | Apr | 2022 | 0.0059664 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-04-27 13:44 | 2022-04-27 15:49 | 1048 | 002:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO EN EL CAMPO DEBIDO A QUE NO CERRABA POR SCADA FAIL TO OPERATE LO CERRO JUAN C. FUENTES DE CDS | B22042700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-04-27 | 131000 | keep | 0 | Apr | 2022 | 0.089224 | 0.00071379 | Sustained | FALSE | FALSE | Not_TMED_Event | 1048
ARECIBO | 2022-04-27 13:53 | 2022-04-27 16:08 | 1 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A22042700118 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2022-04-27 | 135 | keep | 0 | Apr | 2022 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-27 14:02 | 2022-04-27 14:04 | 315 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22042700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-27 | 630 | keep | 0 | Apr | 2022 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
ARECIBO | 2022-04-27 14:13 | 2022-04-27 18:34 | 300 | 004:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22042700120 | New_Event | Bad Weather | Include | Include | Weather | 261 | 2022-04-27 | 78300 | keep | 0 | Apr | 2022 | 0.05333 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2022-04-27 14:25 | 2022-04-27 16:35 | 83 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P22042700095 | New_Event |  |  | Include | Wildlife | 130 | 2022-04-27 | 10790 | keep | 0 | Apr | 2022 | 0.007349 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
SAN JUAN | 2022-04-27 14:46 | 2022-04-27 14:47 | 225 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. SE REPORTA AVERIA POR DESGANCHE DE BAMBUA CARGA TRANSFERIDA AL 1303-05 | S22042700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-27 | 225 | keep | 0 | Apr | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-04-27 14:46 | 2022-04-27 14:47 | 870 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. SE REPORTA AVERIA POR DESGANCHE DE BAMBUA | S22042700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-04-27 | 870 | keep | 0 | Apr | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-04-27 15:04 | 2022-04-27 18:26 | 200 | 003:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN CORTE DE LINEA | S22042700087 | New_Event | Wire Down | Include | Include | Equipment | 202 | 2022-04-27 | 40400 | keep | 0 | Apr | 2022 | 0.027516 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2022-04-27 15:10 | 2022-04-27 16:05 | 10 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | P22042700046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2022-04-27 | 550 | keep | 0 | Apr | 2022 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-27 15:11 | 2022-04-27 19:50 | 10 | 004:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A22042700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-04-27 | 2790 | keep | 0 | Apr | 2022 | 0.0019003 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-27 15:38 | 2022-04-27 19:59 | 100 | 004:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECONECTO BAJANTE DE LINEA A CAJA NO FUNDIO | C22042700116 | New_Event | Wire Down | Include | Include | Equipment | 261 | 2022-04-27 | 26100 | keep | 0 | Apr | 2022 | 0.017777 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-04-27 15:45 | 2022-04-27 16:55 | 569 | 001:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | INTERRUPTOR RECERRO TRES VECES Y QUEDO FUERA DE SERVICIO. SE PATRULLO SE ENCONTRO NEUTRAL ENRREDADO CON UNA FASE Y SE PROCEDIO A DESENREDAR CONDUCTORES Y CERRAR INTERRUPTOR POR SCADA | M22042700152 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2022-04-27 | 39830 | keep | 0 | Apr | 2022 | 0.027128 | 0.00038754 | Sustained | FALSE | FALSE | Not_TMED_Event | 569
ARECIBO | 2022-04-27 15:54 | 2022-04-27 16:44 | 50 | 000:50 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A22042700127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2022-04-27 | 2500 | keep | 0 | Apr | 2022 | 0.0017027 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-27 15:56 | 2022-04-27 17:09 | 5 | 001:13 | P | OTRAS CAUSAS | PROA, ABRIO XMR PARA DESCONECTAR TOMA SOTERRADA AVERIADA | C22042700121 | New_Event | Other Causes | Include | Include | Other | 73 | 2022-04-27 | 365 | keep | 0 | Apr | 2022 | 0.0002486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-04-27 16:32 | 2022-04-27 21:23 | 250 | 004:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22042700165 | New_Event | Cutout Failure | Include | Include | Equipment | 291 | 2022-04-27 | 72750 | keep | 0 | Apr | 2022 | 0.04955 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-04-27 16:36 | 2022-04-27 16:37 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 172 | keep | 0 | Apr | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
MAYAGÃœEZ | 2022-04-27 16:39 | 2022-04-27 19:50 | 135 | 003:11 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22042700170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-04-27 | 25785 | keep | 0 | Apr | 2022 | 0.017562 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-04-27 16:47 | 2022-04-27 16:48 | 12 | 000:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR Y SE REPARO SECUNDARIA | S22042700073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2022-04-27 | 12 | keep | 0 | Apr | 2022 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-04-27 16:53 | 2022-04-28 13:30 | 129 | 020:37 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22042700137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1237 | 2022-04-27 | 159573 | keep | 0 | Apr | 2022 | 0.10868 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
BAYAMON | 2022-04-27 16:53 | 2022-04-27 18:00 | 5 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22042700109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2022-04-27 | 335 | keep | 0 | Apr | 2022 | 0.00022817 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-04-27 16:54 | 2022-04-27 18:40 | 1 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C22042700138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-04-27 | 106 | keep | 0 | Apr | 2022 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-04-27 17:06 | 2022-04-27 20:27 | 15 | 003:21 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A22042700133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-04-27 | 3015 | keep | 0 | Apr | 2022 | 0.0020535 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-27 17:36 | 2022-04-27 18:00 | 1 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22042700140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2022-04-27 | 24 | keep | 0 | Apr | 2022 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-04-27 17:53 | 2022-04-28 10:49 | 1 | 016:56 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22042700114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1016 | 2022-04-27 | 1016 | keep | 0 | Apr | 2022 | 0.00069199 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-27 18:06 | 2022-04-27 19:27 | 200 | 001:21 | P | DESGANCHE | 2 X 80 EN C/L | C22042700144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-04-27 | 16200 | keep | 0 | Apr | 2022 | 0.011034 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-04-27 18:09 | 2022-04-28 04:05 | 100 | 009:56 | P | ESTRUCTURA AVERIADA | SE LEVANTO CONDUCTOR PRIMARIO BY-220427-01 | B22042700056 | Partial_restoration | Defective Pole | Include | Include | Equipment | 596 | 2022-04-27 | 59600 | keep | 0 | Apr | 2022 | 0.040593 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-04-27 18:58 | 2022-04-27 21:22 | 55 | 002:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042700187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-04-27 | 7920 | keep | 0 | Apr | 2022 | 0.0053943 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
FAJARDO | 2022-04-27 19:12 | 2022-04-27 21:30 | 162 | 002:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | R22042700067 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2022-04-27 | 22356 | keep | 0 | Apr | 2022 | 0.015227 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
CAGUAS | 2022-04-27 19:14 | 2022-04-27 23:32 | 65 | 004:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L LEVANTO CONDUCTOR | C22042700159 | New_Event | Wire Down | Include | Include | Equipment | 258 | 2022-04-27 | 16770 | keep | 0 | Apr | 2022 | 0.011422 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-04-27 19:22 | 2022-04-28 10:23 | 6 | 015:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | A22042700138 | New_Event | Cutout Failure | Include | Include | Equipment | 901 | 2022-04-27 | 5406 | keep | 0 | Apr | 2022 | 0.003682 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-04-27 19:46 | 2022-04-27 22:35 | 86 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22042700146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-04-27 | 14534 | keep | 0 | Apr | 2022 | 0.009899 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
SAN JUAN | 2022-04-27 20:23 | 2022-04-27 20:24 | 283 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 283 | keep | 0 | Apr | 2022 | 0.00019275 | 0.00019275 | Momentary | FALSE | FALSE | Not_TMED_Event | 283
SAN JUAN | 2022-04-27 20:24 | 2022-04-27 21:15 | 95 | 000:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | S22042700160 | New_Event | Wire Down | Include | Include | Equipment | 51 | 2022-04-27 | 4845 | keep | 0 | Apr | 2022 | 0.0032999 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
SAN JUAN | 2022-04-27 21:15 | 2022-04-27 23:39 | 283 | 002:24 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR SITUACION DE EMERGENCIA, CONDUCTOR EN EL SUELO. SE SECCIONALIZO Y SE LEVANTO CONDUCTOR SJ-220427-03 | S22042700160 | Additional_clients | Wire Down | Include | Include | Equipment | 144 | 2022-04-27 | 40752 | keep | 0 | Apr | 2022 | 0.027756 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-27 21:35 | 2022-04-27 22:49 | 57 | 001:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 RBA DE 100A EN SU - 3 CRUCE X RATA | R22042700074 | New_Event |  |  | Include | Wildlife | 74 | 2022-04-27 | 4218 | keep | 0 | Apr | 2022 | 0.0028729 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2022-04-27 22:05 | 2022-04-28 00:22 | 80 | 002:17 | P | NO SE REPORTO CAUSA | SE REMPLAZO 1 X 80 EN CL | B22042700144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-04-27 | 10960 | keep | 0 | Apr | 2022 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-27 22:46 | 2022-04-27 22:47 | 4089 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-27 | 4089 | keep | 0 | Apr | 2022 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BAYAMON | 2022-04-27 22:55 | 2022-04-28 00:22 | 6 | 001:27 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22042700144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-04-27 | 522 | keep | 0 | Apr | 2022 | 0.00035553 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-28 01:05 | 2022-04-28 01:07 | 1026 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R22042800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-28 | 2052 | keep | 0 | Apr | 2022 | 0.0013976 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
HUMACAO | 2022-04-28 02:09 | 2022-04-28 09:27 | 372 | 007:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONECTOR AVERIADO EN LA SALIDA DEL ALIMENTADOR SE ABRIO INTERRUPTOR PARA REEMPLAZARLO SE CREO EVENTO C22042800027 | C22042800001 | New_Event | Wire Down | Include | Include | Equipment | 438 | 2022-04-28 | 162936 | keep | 0 | Apr | 2022 | 0.11097 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
CANOVANAS | 2022-04-28 05:05 | 2022-04-28 10:12 | 90 | 005:07 | P | PARARRAYOS DEFECTUOSO | 2 X 65 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R22042800002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 307 | 2022-04-28 | 27630 | keep | 0 | Apr | 2022 | 0.018819 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-04-28 05:23 | 2022-04-28 11:00 | 30 | 005:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22042800002 | New_Event | Bad Weather | Include | Include | Weather | 337 | 2022-04-28 | 10110 | keep | 0 | Apr | 2022 | 0.0068859 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-04-28 06:06 | 2022-04-28 07:44 | 180 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA POR AVE | P22042800002 | New_Event |  |  | Include | Wildlife | 98 | 2022-04-28 | 17640 | keep | 0 | Apr | 2022 | 0.012015 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
AGUADILLA | 2022-04-28 06:11 | 2022-04-28 12:00 | 150 | 005:49 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22042800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2022-04-28 | 52350 | keep | 0 | Apr | 2022 | 0.035655 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-04-28 06:19 | 2022-04-28 13:05 | 1 | 006:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN RISER Y 2 X 15 EN BANCO DE TRANSFORMADORES CRUCE POR CHANGO | C22042800005 | New_Event |  |  | Include | Wildlife | 406 | 2022-04-28 | 406 | keep | 0 | Apr | 2022 | 0.00027652 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-04-28 06:51 | 2022-04-28 15:40 | 2 | 008:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22042800004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 529 | 2022-04-28 | 1058 | keep | 0 | Apr | 2022 | 0.0007206 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-04-28 06:58 | 2022-04-28 07:00 | 1825 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SU CARGA POR 1118-9 SE PROBO QUEDO EN SERVICIO | S22042800000 | New_Event |  |  | Include | Wildlife | 2 | 2022-04-28 | 3650 | keep | 0 | Apr | 2022 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-04-28 06:58 | 2022-04-28 07:00 | 4398 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO LLEVA 1118-8 SE PROBO QUEDO EN SERVICIO | S22042800000 | New_Event |  |  | Include | Wildlife | 2 | 2022-04-28 | 8796 | keep | 0 | Apr | 2022 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
BAYAMON | 2022-04-28 07:00 | 2022-04-28 16:36 | 100 | 009:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L DESGANCHE CRUCE POR AVE | S22042800004 | 1st_after_momentary |  |  | Include | Wildlife | 576 | 2022-04-28 | 57600 | keep | 0 | Apr | 2022 | 0.039231 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-28 07:14 | 2022-04-29 15:30 | 24 | 032:16 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DEL T-648 @ T-647 | B22042800005 | New_Event | UG Cable Fault | Include | Include | Equipment | 1936 | 2022-04-28 | 46464 | keep | 0 | Apr | 2022 | 0.031646 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
FAJARDO | 2022-04-28 07:14 | 2022-04-28 07:15 | 1839 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | R22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 1839 | keep | 0 | Apr | 2022 | 0.0012525 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2022-04-28 07:14 | 2022-04-28 07:15 | 1778 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | R22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 1778 | keep | 0 | Apr | 2022 | 0.001211 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2022-04-28 07:14 | 2022-04-28 07:15 | 1376 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | R22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 1376 | keep | 0 | Apr | 2022 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
HUMACAO | 2022-04-28 07:14 | 2022-04-28 07:15 | 3701 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE DAGUAO A RIO BLANCO | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 3701 | keep | 0 | Apr | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-04-28 07:14 | 2022-04-28 07:15 | 989 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE DAGUAO A RIO BLANCO | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 989 | keep | 0 | Apr | 2022 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2022-04-28 07:14 | 2022-04-28 07:15 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE DAGUAO A RIO BLANCO | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 1467 | keep | 0 | Apr | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
FAJARDO | 2022-04-28 07:14 | 2022-04-28 07:15 | 293 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | R22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 293 | keep | 0 | Apr | 2022 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2022-04-28 07:14 | 2022-04-28 07:15 | 1215 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | R22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 1215 | keep | 0 | Apr | 2022 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
MAYAGÃœEZ | 2022-04-28 07:27 | 2022-04-28 14:50 | 60 | 007:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M22042800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 443 | 2022-04-28 | 26580 | keep | 0 | Apr | 2022 | 0.018104 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-04-28 07:48 | 2022-04-28 10:40 | 80 | 002:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE CAMBIO AISLADOR Y SE FIJO LINEA | P22042800005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 172 | 2022-04-28 | 13760 | keep | 0 | Apr | 2022 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-04-28 08:00 | 2022-04-28 08:01 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 1565 | keep | 0 | Apr | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-04-28 08:00 | 2022-04-28 08:01 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 976 | keep | 0 | Apr | 2022 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-04-28 08:00 | 2022-04-28 08:01 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 548 | keep | 0 | Apr | 2022 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-04-28 08:00 | 2022-04-28 08:01 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 315 | keep | 0 | Apr | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-04-28 08:00 | 2022-04-28 08:01 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 870 | keep | 0 | Apr | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-04-28 08:00 | 2022-04-28 08:01 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 2906 | keep | 0 | Apr | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-04-28 08:00 | 2022-04-28 08:01 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA | C22042800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-28 | 2343 | keep | 0 | Apr | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
MAYAGÃœEZ | 2022-04-28 08:00 | 2022-04-28 19:15 | 30 | 011:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22042800088 | New_Event | Bad Weather | Include | Include | Weather | 675 | 2022-04-28 | 20250 | keep | 0 | Apr | 2022 | 0.013792 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-04-28 08:09 | 2022-04-28 09:40 | 43 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22042800011 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2022-04-28 | 3913 | keep | 0 | Apr | 2022 | 0.0026651 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
AGUADILLA | 2022-04-28 08:30 | 2022-04-28 17:25 | 50 | 008:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22042800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 535 | 2022-04-28 | 26750 | keep | 0 | Apr | 2022 | 0.018219 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-28 08:40 | 2022-04-28 08:41 | 6244 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO | S22042800012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-28 | 6244 | keep | 0 | Apr | 2022 | 0.0042528 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
SAN JUAN | 2022-04-28 08:45 | 2022-04-28 08:46 | 6244 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO | S22042800014 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-28 | 6244 | keep | 0 | Apr | 2022 | 0.0042528 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
HUMACAO | 2022-04-28 08:53 | 2022-04-28 14:14 | 10 | 005:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22042800022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2022-04-28 | 3210 | keep | 0 | Apr | 2022 | 0.0021863 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-04-28 08:56 | 2022-04-28 08:57 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-28 | 1352 | keep | 0 | Apr | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
SAN JUAN | 2022-04-28 09:11 | 2022-04-28 13:56 | 80 | 004:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | S22042800019 | New_Event |  |  | Include | Wildlife | 285 | 2022-04-28 | 22800 | keep | 0 | Apr | 2022 | 0.015529 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-04-28 09:18 | 2022-04-28 12:18 | 4 | 003:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | P22042800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-04-28 | 720 | keep | 0 | Apr | 2022 | 0.00049039 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-04-28 09:27 | 2022-04-28 11:21 | 1117 | 001:54 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REEMPLAZAR CONECTOR PRIMARIO AVERIADO EN LA SALIDA DEL ALIMENTADOR | C22042800027 | Additional_clients | Wire Down | Include | Include | Equipment | 114 | 2022-04-28 | 127338 | keep | 0 | Apr | 2022 | 0.086729 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-28 09:34 | 2022-04-28 12:50 | 110 | 003:16 | P | DESGANCHE | 1 X 40 Y 1 X 65 EN CORTES DE LINEAS | R22042800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-04-28 | 21560 | keep | 0 | Apr | 2022 | 0.014684 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
HUMACAO | 2022-04-28 09:44 | 2022-04-28 15:38 | 6 | 005:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REPARO SECUNDARIA CRUZADA | C22042800030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 354 | 2022-04-28 | 2124 | keep | 0 | Apr | 2022 | 0.0014466 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-04-28 09:50 | 2022-04-28 13:04 | 30 | 003:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50KVA | A22042800006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 194 | 2022-04-28 | 5820 | keep | 0 | Apr | 2022 | 0.003964 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-28 10:00 | 2022-04-28 12:13 | 5 | 002:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA Y TOMA | S22042700122 | New_Event | Secondary Wire Down | Include | Include | Equipment | 133 | 2022-04-28 | 665 | keep | 0 | Apr | 2022 | 0.00045293 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-04-28 10:08 | 2022-04-28 16:47 | 8 | 006:39 | P | DESGANCHE | 2 X 40 EN C/L | C22042800034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 399 | 2022-04-28 | 3192 | keep | 0 | Apr | 2022 | 0.0021741 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-04-28 10:29 | 2022-04-28 11:40 | 8 | 001:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RETEZAR LINEA PRIMARIA | A22042800008 | New_Event | Wire Down | Include | Include | Equipment | 71 | 2022-04-28 | 568 | keep | 0 | Apr | 2022 | 0.00038686 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-04-28 10:35 | 2022-04-28 11:58 | 12 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22042800158 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-04-28 | 996 | keep | 0 | Apr | 2022 | 0.00067837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-04-28 10:44 | 2022-04-28 13:25 | 1 | 002:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE DE TRANSFORMADOR | M22042800048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 161 | 2022-04-28 | 161 | keep | 0 | Apr | 2022 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-28 11:00 | 2022-04-28 16:40 | 12 | 005:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | REMPLAZO DE POSTE AVERIADO POR CAMION | P22042800017 | New_Event |  |  | Include | Wildlife | 340 | 2022-04-28 | 4080 | keep | 0 | Apr | 2022 | 0.0027789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-04-28 11:11 | 2022-04-28 12:40 | 12 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE TRANSFORMADOR PARA RETIRAR PELIGRO DE POSTE IMPACTADO POR CAMION | A22042800014 | New_Event |  |  | Include | Wildlife | 89 | 2022-04-28 | 1068 | keep | 0 | Apr | 2022 | 0.00072741 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-28 11:26 | 2022-04-28 16:16 | 57 | 004:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO LINEA A CAJA EN C/L | B22042800016 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2022-04-28 | 16530 | keep | 0 | Apr | 2022 | 0.011259 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2022-04-28 11:39 | 2022-04-28 12:05 | 4 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE AJUSTARON CONEXIONES EN BARRAS SECUNDARIAS | B22042800017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-04-28 | 104 | keep | 0 | Apr | 2022 | 7.0834e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-04-28 11:42 | 2022-04-28 12:35 | 1066 | 000:53 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR TRAMO EN EL PISO 87% EN SERVICIO | S22042800047 | New_Event | Wire Down | Include | Include | Equipment | 53 | 2022-04-28 | 56498 | keep | 0 | Apr | 2022 | 0.038481 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
ARECIBO | 2022-04-28 11:55 | 2022-04-28 15:57 | 275 | 004:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A22042800018 | New_Event | Wire Down | Include | Include | Equipment | 242 | 2022-04-28 | 66550 | keep | 0 | Apr | 2022 | 0.045327 | 0.0001873 | Sustained | FALSE | FALSE | Not_TMED_Event | 275
ARECIBO | 2022-04-28 11:58 | 2022-04-28 12:50 | 1 | 000:52 | P | OTRAS CAUSAS | SE ABRE MONTURA DE TRANSFORMADOR PARA PERSONAL DE MEDICIONES TRABAJAR EN CT'S | A22042800020 | New_Event | Other Causes | Include | Include | Other | 52 | 2022-04-28 | 52 | keep | 0 | Apr | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-04-28 12:00 | 2022-04-28 18:30 | 3 | 006:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE IMPACTADO | R22042800020 | New_Event |  |  | Include | Wildlife | 390 | 2022-04-28 | 1170 | keep | 0 | Apr | 2022 | 0.00079688 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-04-28 12:25 | 2022-04-28 16:12 | 1 | 003:47 | P | OTRAS CAUSAS | 1 X 80 EN SU-5 Y 1 X 50 EN SUBESTACION DE CLIENTE Y SE REALIZO BYPASS A MEDICION | S22042800056 | New_Event | Other Causes | Include | Include | Other | 227 | 2022-04-28 | 227 | keep | 0 | Apr | 2022 | 0.00015461 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-28 12:35 | 2022-04-28 15:50 | 139 | 003:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE TRABAJO ALAMBRE EN EL SUELO Y SE CERRARON MACHETES 100% EN SERVICIO | S22042800047 | Partial_restoration | Wire Down | Include | Include | Equipment | 195 | 2022-04-28 | 27105 | keep | 0 | Apr | 2022 | 0.018461 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-04-28 12:54 | 2022-04-28 16:53 | 92 | 003:59 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L NO CAUSA | C22042800054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 239 | 2022-04-28 | 21988 | keep | 0 | Apr | 2022 | 0.014976 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
AGUADILLA | 2022-04-28 13:00 | 2022-04-28 19:20 | 30 | 006:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA VIENTOS FUERTES | M22042800090 | New_Event | Bad Weather | Include | Include | Weather | 380 | 2022-04-28 | 11400 | keep | 0 | Apr | 2022 | 0.0077645 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-04-28 13:15 | 2022-04-28 15:20 | 8 | 002:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P22042800026 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2022-04-28 | 1000 | keep | 0 | Apr | 2022 | 0.0006811 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-04-28 13:28 | 2022-04-28 13:29 | 58 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22042800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-28 | 58 | keep | 0 | Apr | 2022 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
FAJARDO | 2022-04-28 13:30 | 2022-04-28 14:49 | 2041 | 001:19 | T | CABLE SOTERRADO AVERIADO | RISER DE SALIDA AVERIADO, SE TRANSFIRIO LA CARGA AL 2001-01 | R22042800065 | New_Event | UG Cable Fault | Include | Include | Equipment | 79 | 2022-04-28 | 161239 | keep | 0 | Apr | 2022 | 0.10982 | 0.0013901 | Sustained | FALSE | FALSE | Not_TMED_Event | 2041
ARECIBO | 2022-04-28 13:33 | 2022-04-28 16:39 | 150 | 003:06 | P | DESGANCHE | 1 X 80 EN CONVERTIDOR ARBOL CAYO Y CRUZO LAS LINEAS | A22042800036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-04-28 | 27900 | keep | 0 | Apr | 2022 | 0.019003 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-04-28 13:41 | 2022-04-28 15:37 | 10 | 001:56 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 50 KVA A 7620 VOLTS CON PERDIDA DE ACEITE | P22042800008 | New_Event | Service Transformer Failure | Include | Include | Equipment | 116 | 2022-04-28 | 1160 | keep | 0 | Apr | 2022 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-04-28 13:52 | 2022-04-28 15:45 | 65 | 001:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | R22042800090 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 113 | 2022-04-28 | 7345 | keep | 0 | Apr | 2022 | 0.0050026 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-04-28 14:22 | 2022-04-28 18:42 | 50 | 004:20 | P | DESGANCHE | 2 X 65 EN C/L SE RETIRO PENCA DE PALMA | S22042800132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2022-04-28 | 13000 | keep | 0 | Apr | 2022 | 0.0088542 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-28 14:22 | 2022-04-29 12:05 | 30 | 021:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA CAJA QUEMADA | S22042800133 | New_Event | Cutout Failure | Include | Include | Equipment | 1303 | 2022-04-28 | 39090 | keep | 0 | Apr | 2022 | 0.026624 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-28 14:38 | 2022-04-28 18:06 | 30 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22042800141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-04-28 | 6240 | keep | 0 | Apr | 2022 | 0.00425 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-28 14:47 | 2022-04-28 17:09 | 4 | 002:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE LINEA A CAJA EN TRANSFORMADOR | B22042800066 | New_Event | Wire Down | Include | Include | Equipment | 142 | 2022-04-28 | 568 | keep | 0 | Apr | 2022 | 0.00038686 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-04-28 14:48 | 2022-04-28 18:53 | 60 | 004:05 | P | DESGANCHE | 1 X 65 EN C/L | S22042800148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-04-28 | 14700 | keep | 0 | Apr | 2022 | 0.010012 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-04-28 15:00 | 2022-04-28 17:18 | 38 | 002:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22042800088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-04-28 | 5244 | keep | 0 | Apr | 2022 | 0.0035717 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2022-04-28 15:02 | 2022-04-28 17:49 | 12 | 002:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR, SE REPARO SECUNDARIO Y SE REMPLAZO BAJANTE SECUNDARIO | S22042700120 | New_Event | Secondary Wire Down | Include | Include | Equipment | 167 | 2022-04-28 | 2004 | keep | 0 | Apr | 2022 | 0.0013649 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-28 16:14 | 2022-04-28 17:39 | 7 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR NEUTRAL Y BAJANTE SECUNDARIO | C22042800204 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2022-04-28 | 595 | keep | 0 | Apr | 2022 | 0.00040525 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-04-28 16:16 | 2022-04-28 20:42 | 14 | 004:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN XMR SE REPARO PUENTE DE CAJA A XMR | S22042800168 | New_Event | Wire Down | Include | Include | Equipment | 266 | 2022-04-28 | 3724 | keep | 0 | Apr | 2022 | 0.0025364 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2022-04-28 16:25 | 2022-04-28 17:53 | 20 | 001:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | C22042800205 | New_Event |  |  | Include | Wildlife | 88 | 2022-04-28 | 1760 | keep | 0 | Apr | 2022 | 0.0011987 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-04-28 16:38 | 2022-04-28 20:03 | 39 | 003:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO GLOBO | B22042800085 | New_Event |  |  | Include | Wildlife | 205 | 2022-04-28 | 7995 | keep | 0 | Apr | 2022 | 0.0054454 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
PONCE | 2022-04-28 17:00 | 2022-04-28 18:15 | 4 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22042800117 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2022-04-28 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-04-28 17:03 | 2022-04-28 19:20 | 35 | 002:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22042800113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-04-28 | 4795 | keep | 0 | Apr | 2022 | 0.0032659 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-04-28 17:10 | 2022-04-28 18:13 | 75 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22042800091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-04-28 | 4725 | keep | 0 | Apr | 2022 | 0.0032182 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2022-04-28 17:16 | 2022-04-28 18:00 | 9 | 000:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 25 KVA X 37.5 KVA | C22042800208 | New_Event | Service Transformer Failure | Include | Include | Equipment | 44 | 2022-04-28 | 396 | keep | 0 | Apr | 2022 | 0.00026971 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2022-04-28 17:18 | 2022-04-29 08:43 | 65 | 015:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | B22042800093 | New_Event | Cutout Failure | Include | Include | Equipment | 925 | 2022-04-28 | 60125 | keep | 0 | Apr | 2022 | 0.040951 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2022-04-28 17:22 | 2022-04-28 17:23 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22042800210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-28 | 5630 | keep | 0 | Apr | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
SAN JUAN | 2022-04-28 17:27 | 2022-04-29 13:16 | 27 | 019:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA 1 X 20 EN TRANSFORMADOR | S22042800182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1189 | 2022-04-28 | 32103 | keep | 0 | Apr | 2022 | 0.021865 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2022-04-28 17:45 | 2022-04-28 21:40 | 70 | 003:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22042800101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-04-28 | 16450 | keep | 0 | Apr | 2022 | 0.011204 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-04-28 18:01 | 2022-04-28 18:02 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22042800120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-28 | 3114 | keep | 0 | Apr | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
CAGUAS | 2022-04-28 18:19 | 2022-04-28 19:22 | 10 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO Y REGULARLO BAJO TAP C AL A QUEDO EN 122/244V | C22042800212 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2022-04-28 | 630 | keep | 0 | Apr | 2022 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-04-28 18:30 | 2022-04-28 20:00 | 12 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO TOMA DE CLIENTE | R22042800129 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-04-28 | 1080 | keep | 0 | Apr | 2022 | 0.00073558 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-04-28 18:35 | 2022-04-29 00:20 | 15 | 005:45 | P | NO SE REPORTO CAUSA | 1 X 12 EN TRANSFORMADOR | B22042800105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 345 | 2022-04-28 | 5175 | keep | 0 | Apr | 2022 | 0.0035247 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-04-28 18:46 | 2022-04-28 20:03 | 12 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES EN BAJANTE SECUNDARIO | B22042800086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2022-04-28 | 924 | keep | 0 | Apr | 2022 | 0.00062933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-04-28 18:52 | 2022-04-28 18:53 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-28 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
SAN JUAN | 2022-04-28 19:02 | 2022-04-28 20:06 | 350 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L Y 1 X 100 EN C/L | S22042800190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-04-28 | 22400 | keep | 0 | Apr | 2022 | 0.015257 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2022-04-28 19:08 | 2022-04-28 22:30 | 500 | 003:22 | P | NO SE REPORTO CAUSA | 1 X 125 EN SU-13 | B22042800113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2022-04-28 | 101000 | keep | 0 | Apr | 2022 | 0.068791 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2022-04-28 19:23 | 2022-04-28 22:20 | 20 | 002:57 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SE NECESITA DESGANCHE | A22042800082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-04-28 | 3540 | keep | 0 | Apr | 2022 | 0.0024111 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-04-28 19:34 | 2022-04-28 21:28 | 7 | 001:54 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 37.5 KV | C22042800211 | New_Event | Service Transformer Failure | Include | Include | Equipment | 114 | 2022-04-28 | 798 | keep | 0 | Apr | 2022 | 0.00054351 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-04-28 19:41 | 2022-04-29 15:34 | 8 | 019:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22042800203 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1193 | 2022-04-28 | 9544 | keep | 0 | Apr | 2022 | 0.0065004 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-04-28 19:45 | 2022-04-28 19:46 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-28 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-04-28 20:04 | 2022-04-28 22:30 | 60 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22042800206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-04-28 | 8760 | keep | 0 | Apr | 2022 | 0.0059664 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-04-28 20:12 | 2022-04-29 06:23 | 25 | 010:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L AVE CRUZO LINEAS | P22042800126 | New_Event |  |  | Include | Wildlife | 611 | 2022-04-28 | 15275 | keep | 0 | Apr | 2022 | 0.010404 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-04-28 20:15 | 2022-04-28 22:44 | 24 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22042800215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-04-28 | 3576 | keep | 0 | Apr | 2022 | 0.0024356 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2022-04-28 20:44 | 2022-04-29 15:45 | 21 | 019:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22042800223 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1141 | 2022-04-28 | 23961 | keep | 0 | Apr | 2022 | 0.01632 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2022-04-28 20:50 | 2022-04-29 00:31 | 2 | 003:41 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22042800110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-04-28 | 442 | keep | 0 | Apr | 2022 | 0.00030104 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-04-28 21:16 | 2022-04-28 21:17 | 590 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22042800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-28 | 590 | keep | 0 | Apr | 2022 | 0.00040185 | 0.00040185 | Momentary | FALSE | FALSE | Not_TMED_Event | 590
GUAYAMA | 2022-04-28 21:54 | 2022-04-29 01:00 | 140 | 003:06 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22042800133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-04-28 | 26040 | keep | 0 | Apr | 2022 | 0.017736 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
MAYAGÃœEZ | 2022-04-28 22:13 | 2022-04-29 08:52 | 25 | 010:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR Y SE REPARA SECUNDARIA ABIERTA | M22042800112 | New_Event | Secondary Wire Down | Include | Include | Equipment | 639 | 2022-04-28 | 15975 | keep | 0 | Apr | 2022 | 0.01088 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-04-29 01:22 | 2022-04-29 01:24 | 68 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 1102-04 & 5 LLEVA 1105-04 & 5 | S22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-29 | 136 | keep | 0 | Apr | 2022 | 9.2629e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-04-29 01:22 | 2022-04-29 01:24 | 536 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR 1102-01 DISPARO Y SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 1102-04 | S22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-29 | 1072 | keep | 0 | Apr | 2022 | 0.00073013 | 0.00036507 | Momentary | FALSE | FALSE | Not_TMED_Event | 536
BAYAMON | 2022-04-29 01:22 | 2022-04-29 01:24 | 348 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR 1102-01 DISPARO Y SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 1102-05 | S22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-29 | 696 | keep | 0 | Apr | 2022 | 0.00047404 | 0.00023702 | Momentary | FALSE | FALSE | Not_TMED_Event | 348
BAYAMON | 2022-04-29 01:22 | 2022-04-29 01:24 | 559 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR 1102-01 DISPARO Y SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 1105-04 | S22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-29 | 1118 | keep | 0 | Apr | 2022 | 0.00076146 | 0.00038073 | Momentary | FALSE | FALSE | Not_TMED_Event | 559
BAYAMON | 2022-04-29 01:22 | 2022-04-29 01:24 | 370 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR 1102-01 DISPARO Y SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 1105-05 | S22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-29 | 740 | keep | 0 | Apr | 2022 | 0.00050401 | 0.00025201 | Momentary | FALSE | FALSE | Not_TMED_Event | 370
FAJARDO | 2022-04-29 02:14 | 2022-04-29 08:48 | 100 | 006:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | R22042900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2022-04-29 | 39400 | keep | 0 | Apr | 2022 | 0.026835 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-29 03:03 | 2022-04-29 09:45 | 104 | 006:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | R22042900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 402 | 2022-04-29 | 41808 | keep | 0 | Apr | 2022 | 0.028475 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
HUMACAO | 2022-04-29 03:04 | 2022-04-29 03:05 | 824 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-29 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
HUMACAO | 2022-04-29 03:10 | 2022-04-29 03:11 | 824 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042900000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-29 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
CAGUAS | 2022-04-29 04:45 | 2022-04-29 04:46 | 1843 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C22042900002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-04-29 | 1843 | keep | 0 | Apr | 2022 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
CAGUAS | 2022-04-29 04:46 | 2022-04-29 13:20 | 100 | 008:34 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA REEMPLAZO PARARRAYO Y BAJANTE HACIA CAJA PRIMARIA | C22042900071 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 514 | 2022-04-29 | 51400 | keep | 0 | Apr | 2022 | 0.035008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-29 05:21 | 2022-04-29 07:45 | 170 | 002:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22042900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-04-29 | 24480 | keep | 0 | Apr | 2022 | 0.016673 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
HUMACAO | 2022-04-29 05:37 | 2022-04-29 05:38 | 824 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042900000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-29 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
HUMACAO | 2022-04-29 05:53 | 2022-04-29 05:54 | 824 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042900000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-29 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
HUMACAO | 2022-04-29 06:26 | 2022-04-29 06:27 | 824 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042900000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-29 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
HUMACAO | 2022-04-29 06:35 | 2022-04-29 09:35 | 180 | 003:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22042900019 | New_Event |  |  | Include | Wildlife | 180 | 2022-04-29 | 32400 | keep | 0 | Apr | 2022 | 0.022067 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
HUMACAO | 2022-04-29 06:46 | 2022-04-29 12:53 | 45 | 006:07 | P | DESGANCHE | 1 X 30 EN CORTE DEL LINEA | C22042900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2022-04-29 | 16515 | keep | 0 | Apr | 2022 | 0.011248 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-04-29 06:52 | 2022-04-29 08:00 | 1 | 001:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA Y 2 X 25 EN RISER GATO CRUZO FASES EN SW | P22042900002 | New_Event |  |  | Include | Wildlife | 68 | 2022-04-29 | 68 | keep | 0 | Apr | 2022 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-29 06:56 | 2022-04-29 06:57 | 824 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 65% DE SU CARGA POR 2604-03 | C22042900000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-29 | 824 | keep | 0 | Apr | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
PONCE | 2022-04-29 07:02 | 2022-04-29 09:00 | 123 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L AVE CRUZO LINEAS | P22042900003 | New_Event |  |  | Include | Wildlife | 118 | 2022-04-29 | 14514 | keep | 0 | Apr | 2022 | 0.0098854 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
HUMACAO | 2022-04-29 07:04 | 2022-04-29 09:29 | 824 | 2:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZARON AISLADOR ROTO Y MACHETE QUEMADO 65% DE SU CARGA POR 2604-03 | C22042900033 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 145 | 2022-04-29 | 119480 | keep | 0 | Apr | 2022 | 0.081377 | 0.00056122 | Sustained | FALSE | FALSE | Not_TMED_Event | 824
SAN JUAN | 2022-04-29 07:15 | 2022-04-29 07:17 | 1483 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 30% POR 1336-08 | S22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-29 | 2966 | keep | 0 | Apr | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-04-29 07:15 | 2022-04-29 07:17 | 1500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE POR 1336-08 | S22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-29 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-04-29 07:15 | 2022-04-29 07:17 | 5290 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 30% 1204-4 Y PARTE DEL 1204-5 | S22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-29 | 10580 | keep | 0 | Apr | 2022 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
CAGUAS | 2022-04-29 07:21 | 2022-04-29 09:08 | 60 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22042900029 | New_Event |  |  | Include | Wildlife | 107 | 2022-04-29 | 6420 | keep | 0 | Apr | 2022 | 0.0043726 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-04-29 07:30 | 2022-04-29 19:05 | 35 | 011:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22042900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 695 | 2022-04-29 | 24325 | keep | 0 | Apr | 2022 | 0.016568 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-04-29 07:50 | 2022-04-29 10:11 | 10 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | M22042900004 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2022-04-29 | 1410 | keep | 0 | Apr | 2022 | 0.00096034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-29 07:56 | 2022-04-29 07:58 | 3798 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO | B22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-29 | 7596 | keep | 0 | Apr | 2022 | 0.0051736 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
GUAYAMA | 2022-04-29 08:07 | 2022-04-29 12:08 | 150 | 004:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L AVE CRUZO LINEAS Y SE REMPLAZO CAJA PRIMARIA CORRIGIO NUM DE CLIENTES | P22042900005 | New_Event |  |  | Include | Wildlife | 241 | 2022-04-29 | 36150 | keep | 0 | Apr | 2022 | 0.024622 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-04-29 08:28 | 2022-04-29 13:24 | 18 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22042900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2022-04-29 | 5328 | keep | 0 | Apr | 2022 | 0.0036289 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-04-29 08:48 | 2022-04-29 14:22 | 3 | 005:34 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 75 KVA A7620VOLTS QUEMADO | P22042900018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 334 | 2022-04-29 | 1002 | keep | 0 | Apr | 2022 | 0.00068246 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-04-29 09:00 | 2022-04-29 09:35 | 5 | 000:35 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO Y REEMPLAZARON CONECTOR ROTO | R22042800136 | New_Event | Service Transformer Failure | Include | Include | Equipment | 35 | 2022-04-29 | 175 | keep | 0 | Apr | 2022 | 0.00011919 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-04-29 09:10 | 2022-04-29 22:00 | 12 | 012:50 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONALA EREO | S22042900021 | New_Event | UG Cable Fault | Include | Include | Equipment | 770 | 2022-04-29 | 9240 | keep | 0 | Apr | 2022 | 0.0062933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-29 09:10 | 2022-04-29 18:09 | 56 | 008:59 | P | DESGANCHE | 1 X 65 EN C/L | C22042900066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 539 | 2022-04-29 | 30184 | keep | 0 | Apr | 2022 | 0.020558 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
HUMACAO | 2022-04-29 09:29 | 2022-04-29 15:16 | 2119 | 005:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO MACHETE QUEMADO Y AISLADOR ROTO | C22042900033 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 347 | 2022-04-29 | 735293 | keep | 0 | Apr | 2022 | 0.5008 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-04-29 09:40 | 2022-04-29 11:05 | 60 | 001:25 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22042900014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-04-29 | 5100 | keep | 0 | Apr | 2022 | 0.0034736 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-04-29 10:00 | 2022-04-29 10:45 | 2 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES Y BAJANTE SECUNDARIO | S22042800008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-04-29 | 90 | keep | 0 | Apr | 2022 | 6.1299e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-04-29 10:11 | 2022-04-29 10:53 | 891 | 000:42 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LINEA DE TRANSMISION 0200 PARA REPARAR # 1 DE CAMPAMENTO SANTIAGO | P22042900025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-04-29 | 37422 | keep | 0 | Apr | 2022 | 0.025488 | 0.00060686 | Sustained | FALSE | FALSE | Not_TMED_Event | 891
PONCE | 2022-04-29 10:11 | 2022-04-29 10:53 | 527 | 000:42 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LINEA DE TRANSMISION 0200 PARA REPARAR # 1 DE CAMPAMENTO SANTIAGO | P22042900025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-04-29 | 22134 | keep | 0 | Apr | 2022 | 0.015075 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2022-04-29 10:11 | 2022-04-29 10:53 | 542 | 000:42 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LINEA DE TRANSMISION 0200 PARA REPARAR # 1 DE CAMPAMENTO SANTIAGO | P22042900025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-04-29 | 22764 | keep | 0 | Apr | 2022 | 0.015504 | 0.00036915 | Sustained | FALSE | FALSE | Not_TMED_Event | 542
BAYAMON | 2022-04-29 10:43 | 2022-04-29 12:15 | 10 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE BAJO DEL TAP 3 AL 1 Y SE REMPLAZARON BAJANTES SECUNDARIOS JUNTO CON 2 TOMAS Y SECUNDARIA | B22042900022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2022-04-29 | 920 | keep | 0 | Apr | 2022 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-29 11:10 | 2022-04-29 15:10 | 40 | 004:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22042900018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-04-29 | 9600 | keep | 0 | Apr | 2022 | 0.0065385 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-04-29 11:20 | 2022-04-29 11:50 | 10 | 000:30 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZO DE BARRA SECUNDARIA | A22042800088 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 30 | 2022-04-29 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-29 11:22 | 2022-04-29 11:23 | 752 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 LLEVANDO 1709-05 Y 50% DE SU CARGA POR 1909-07 | S22042800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-29 | 752 | keep | 0 | Apr | 2022 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2022-04-29 11:22 | 2022-04-29 11:23 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 LLEVANDO 1709-05 Y 50% DE SU CARGA POR 1909-07 | S22042800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-29 | 2364 | keep | 0 | Apr | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
GUAYAMA | 2022-04-29 11:46 | 2022-04-29 15:00 | 40 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA SE CORRIGIO NUM CLIENTES SEGUN INFORMACION DE JOSE T MORALES | P22042900036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-04-29 | 7760 | keep | 0 | Apr | 2022 | 0.0052853 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-04-29 11:47 | 2022-04-29 13:55 | 30 | 002:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | A22042900021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-04-29 | 3840 | keep | 0 | Apr | 2022 | 0.0026154 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-29 11:57 | 2022-04-29 14:06 | 21 | 002:09 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA POSTE PARTIDO | R22042900026 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 129 | 2022-04-29 | 2709 | keep | 0 | Apr | 2022 | 0.0018451 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
FAJARDO | 2022-04-29 12:00 | 2022-04-29 15:05 | 212 | 003:05 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO Y SE LEVANTO NEUTRAL PRIMARIO | R22042900024 | New_Event | Switch Failure | Include | Include | Equipment | 185 | 2022-04-29 | 39220 | keep | 0 | Apr | 2022 | 0.026713 | 0.00014439 | Sustained | FALSE | FALSE | Not_TMED_Event | 212
YAUCO | 2022-04-29 12:08 | 2022-04-29 16:40 | 25 | 004:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22042900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2022-04-29 | 6800 | keep | 0 | Apr | 2022 | 0.0046314 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-04-29 12:34 | 2022-04-29 13:21 | 5 | 000:47 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | S22042900061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-04-29 | 235 | keep | 0 | Apr | 2022 | 0.00016006 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-04-29 12:43 | 2022-04-29 15:20 | 30 | 002:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRA CARGA A TRES TRANSFORMADORES PARA CERRAR PUENTE ABIERTO | P22042900042 | New_Event | Wire Down | Include | Include | Equipment | 157 | 2022-04-29 | 4710 | keep | 0 | Apr | 2022 | 0.003208 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-29 13:00 | 2022-04-29 13:24 | 1 | 000:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE PRIMARIO A MONTURA DE TRANSFORMADOR | M22042900025 | New_Event | Wire Down | Include | Include | Equipment | 24 | 2022-04-29 | 24 | keep | 0 | Apr | 2022 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-04-29 13:14 | 2022-04-29 14:48 | 6 | 001:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22042900099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 94 | 2022-04-29 | 564 | keep | 0 | Apr | 2022 | 0.00038414 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-04-29 13:16 | 2022-04-29 14:45 | 9 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN XMR SE DEJO FUERA EL ALUMBRADO POR AVERIA | S22042900073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 89 | 2022-04-29 | 801 | keep | 0 | Apr | 2022 | 0.00054556 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-04-29 13:29 | 2022-04-29 13:30 | 8711 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO PARTE POR 1206-3 | S22042900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-29 | 8711 | keep | 0 | Apr | 2022 | 0.005933 | 0.005933 | Momentary | FALSE | FALSE | Not_TMED_Event | 8711
SAN JUAN | 2022-04-29 13:29 | 2022-04-29 13:30 | 4133 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO LLEVA PARTE 1204-5 | S22042900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-04-29 | 4133 | keep | 0 | Apr | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-04-29 13:30 | 2022-04-29 19:32 | 124 | 006:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO PARA REZALIZAR REEMPLAZO DE AISLADOR PATRTIDO, PUENTE PRIMARIO Y PETNO PARTIDO. | S22042900075 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 362 | 2022-04-29 | 44888 | keep | 0 | Apr | 2022 | 0.030573 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
MAYAGÃœEZ | 2022-04-29 13:33 | 2022-04-30 04:58 | 50 | 015:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22042900042 | New_Event | Cutout Failure | Include | Include | Equipment | 925 | 2022-04-29 | 46250 | keep | 0 | Apr | 2022 | 0.031501 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-04-29 13:34 | 2022-04-30 10:42 | 53 | 021:08 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LA LINEA | C22042900103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1268 | 2022-04-29 | 67204 | keep | 0 | Apr | 2022 | 0.045772 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
HUMACAO | 2022-04-29 13:40 | 2022-04-29 18:25 | 4 | 004:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C22042900109 | New_Event |  |  | Include | Wildlife | 285 | 2022-04-29 | 1140 | keep | 0 | Apr | 2022 | 0.00077645 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-04-29 13:59 | 2022-04-29 16:30 | 45 | 002:31 | P | DESGANCHE | 1 X 65 EN C/L | C22042900114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-04-29 | 6795 | keep | 0 | Apr | 2022 | 0.004628 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-04-29 14:00 | 2022-04-29 14:26 | 7 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO NEUTRAL Y REGULO EL XMR | C22042900115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-04-29 | 182 | keep | 0 | Apr | 2022 | 0.00012396 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-04-29 14:00 | 2022-04-29 15:10 | 10 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22042900047 | New_Event | Bad Weather | Include | Include | Weather | 70 | 2022-04-29 | 700 | keep | 0 | Apr | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-29 14:02 | 2022-04-29 14:12 | 1337 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M22042900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-04-29 | 13370 | keep | 0 | Apr | 2022 | 0.0091062 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
SAN JUAN | 2022-04-29 14:04 | 2022-04-29 14:23 | 1 | 000:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA VECINO DEJO CAER ARBOL SOBRE LINEA | R22042900037 | New_Event |  |  | Include | Wildlife | 19 | 2022-04-29 | 19 | keep | 0 | Apr | 2022 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-29 14:06 | 2022-04-29 16:13 | 11 | 002:07 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA PARA RELOCALIZAR SECUNDARIA Y TOMAS POSTE PARTIDO | R22042900039 | Partial_restoration | Secondary Defective Pole | Include | Include | Equipment | 127 | 2022-04-29 | 1397 | keep | 0 | Apr | 2022 | 0.00095149 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-29 14:13 | 2022-04-29 16:01 | 30 | 001:48 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22042900076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-04-29 | 3240 | keep | 0 | Apr | 2022 | 0.0022067 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-29 14:16 | 2022-04-29 14:18 | 2888 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR | A22042900033 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-04-29 | 5776 | keep | 0 | Apr | 2022 | 0.003934 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
ARECIBO | 2022-04-29 14:18 | 2022-04-29 16:00 | 20 | 001:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A22042900035 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2022-04-29 | 2040 | keep | 0 | Apr | 2022 | 0.0013894 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-29 14:18 | 2022-04-29 18:20 | 250 | 004:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR Y REPARAR LINEA PRIMARIA | A22042900036 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 242 | 2022-04-29 | 60500 | keep | 0 | Apr | 2022 | 0.041206 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
PONCE | 2022-04-29 14:51 | 2022-04-29 18:20 | 4 | 003:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE SAFADO EN TRANSFORMADOR | P22042900050 | New_Event | Wire Down | Include | Include | Equipment | 209 | 2022-04-29 | 836 | keep | 0 | Apr | 2022 | 0.0005694 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-04-29 14:55 | 2022-04-29 20:22 | 10 | 005:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22042900051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2022-04-29 | 3270 | keep | 0 | Apr | 2022 | 0.0022272 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-29 14:57 | 2022-04-29 17:40 | 23 | 002:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN XMR SE REPARO BAJANTE PRIMARIO | S22042900078 | New_Event | Wire Down | Include | Include | Equipment | 163 | 2022-04-29 | 3749 | keep | 0 | Apr | 2022 | 0.0025534 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
PONCE | 2022-04-29 15:02 | 2022-04-29 17:40 | 55 | 002:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE HIZO DESGANCHE | P22042900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-04-29 | 8690 | keep | 0 | Apr | 2022 | 0.0059187 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2022-04-29 15:08 | 2022-04-29 15:12 | 50 | 000:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REMPLAZO AISLADOR | B22042900031 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2022-04-29 | 200 | keep | 0 | Apr | 2022 | 0.00013622 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-29 15:18 | 2022-04-29 18:00 | 1337 | 002:42 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO BAJANTE DE CORTE DE LINEA FUERA DE SERVICIO CRUZANDO FASES | M22042900056 | New_Event | Wire Down | Include | Include | Equipment | 162 | 2022-04-29 | 216594 | keep | 0 | Apr | 2022 | 0.14752 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-04-29 15:27 | 2022-04-29 19:50 | 100 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | M22042900057 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2022-04-29 | 26300 | keep | 0 | Apr | 2022 | 0.017913 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-04-29 15:32 | 2022-04-29 16:35 | 40 | 001:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L PORTAFUSIBLE QUEMADO | C22042900145 | New_Event | Cutout Failure | Include | Include | Equipment | 63 | 2022-04-29 | 2520 | keep | 0 | Apr | 2022 | 0.0017164 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-04-29 15:35 | 2022-04-29 17:05 | 25 | 001:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22042900059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-04-29 | 2250 | keep | 0 | Apr | 2022 | 0.0015325 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-04-29 15:45 | 2022-04-29 16:48 | 12 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE TRAMO SECUNDARIO | B22042900033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2022-04-29 | 756 | keep | 0 | Apr | 2022 | 0.00051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-04-29 16:01 | 2022-04-29 16:04 | 2782 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22042900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-29 | 8346 | keep | 0 | Apr | 2022 | 0.0056844 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2022-04-29 16:03 | 2022-04-29 19:10 | 80 | 003:07 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S22042900086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-04-29 | 14960 | keep | 0 | Apr | 2022 | 0.010189 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-04-29 16:14 | 2022-04-30 03:00 | 1 | 010:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER NO SE REPORTO CAUSA | M22042900066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 646 | 2022-04-29 | 646 | keep | 0 | Apr | 2022 | 0.00043999 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-29 16:24 | 2022-04-30 09:20 | 68 | 016:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S22042900087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1016 | 2022-04-29 | 69088 | keep | 0 | Apr | 2022 | 0.047056 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2022-04-29 17:12 | 2022-04-29 19:05 | 16 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO | A22042900055 | New_Event |  |  | Include | Wildlife | 113 | 2022-04-29 | 1808 | keep | 0 | Apr | 2022 | 0.0012314 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-04-29 17:33 | 2022-04-29 22:25 | 40 | 004:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE CON URGENCIA | M22042900087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2022-04-29 | 11680 | keep | 0 | Apr | 2022 | 0.0079552 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-04-29 17:48 | 2022-04-29 19:00 | 11 | 001:12 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REEMPLAZO DE SECUNDARIA, DESGANCHE Y REGULAR VOLTAJE | S22042900092 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 72 | 2022-04-29 | 792 | keep | 0 | Apr | 2022 | 0.00053943 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-04-29 17:54 | 2022-04-29 17:55 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DEL BKR 4870 Y RECIERRE DEL BKR 8510 | C22042900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-29 | 2725 | keep | 0 | Apr | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-04-29 17:54 | 2022-04-29 17:55 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DEL BKR 4870 Y RECIERRE DEL BKR 8510 | C22042900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-29 | 1834 | keep | 0 | Apr | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-04-29 17:54 | 2022-04-29 17:55 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DEL BKR 4870 Y RECIERRE DEL BKR 8510 | C22042900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-29 | 1437 | keep | 0 | Apr | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-04-29 17:54 | 2022-04-29 17:55 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DEL BKR 4870 Y RECIERRE DEL BKR 8510 | C22042900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-29 | 2565 | keep | 0 | Apr | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-04-29 17:54 | 2022-04-29 17:55 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DEL BKR 4870 Y RECIERRE DEL BKR 8510 | C22042900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-29 | 3565 | keep | 0 | Apr | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
VEGA BAJA | 2022-04-29 18:00 | 2022-04-29 20:10 | 10 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22042900035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-04-29 | 1300 | keep | 0 | Apr | 2022 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-04-29 18:24 | 2022-04-30 08:29 | 7 | 014:05 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE ELIMINO PARARRAYO | B22042900037 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 845 | 2022-04-29 | 5915 | keep | 0 | Apr | 2022 | 0.0040287 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-04-29 18:36 | 2022-04-29 19:30 | 1 | 000:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO PRIMARIO | S22042900105 | New_Event | Wire Down | Include | Include | Equipment | 54 | 2022-04-29 | 54 | keep | 0 | Apr | 2022 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-04-29 19:09 | 2022-04-29 20:54 | 287 | 001:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | R22042900052 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2022-04-29 | 30135 | keep | 0 | Apr | 2022 | 0.020525 | 0.00019547 | Sustained | FALSE | FALSE | Not_TMED_Event | 287
ARECIBO | 2022-04-29 19:15 | 2022-04-29 19:35 | 12 | 000:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | ABRIR TRANSFORMADOR REMPLAZO DE CAJA EN TRANSFORMADOR CON PUNTO CALIENTE | A22042900064 | New_Event | Cutout Failure | Include | Include | Equipment | 20 | 2022-04-29 | 240 | keep | 0 | Apr | 2022 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-04-29 19:25 | 2022-04-29 21:40 | 175 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22042900075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2022-04-29 | 23625 | keep | 0 | Apr | 2022 | 0.016091 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
SAN JUAN | 2022-04-29 19:29 | 2022-04-29 21:08 | 30 | 001:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A CAJA | S22042900103 | New_Event | Wire Down | Include | Include | Equipment | 99 | 2022-04-29 | 2970 | keep | 0 | Apr | 2022 | 0.0020229 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-29 19:33 | 2022-04-29 21:40 | 400 | 002:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA AVE CRUZO FASES | M22042900097 | New_Event |  |  | Include | Wildlife | 127 | 2022-04-29 | 50800 | keep | 0 | Apr | 2022 | 0.0346 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2022-04-29 19:34 | 2022-04-29 20:14 | 80 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B22042900041 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2022-04-29 | 3200 | keep | 0 | Apr | 2022 | 0.0021795 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-04-29 20:14 | 2022-04-29 20:15 | 4431 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B22042900000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-04-29 | 4431 | keep | 0 | Apr | 2022 | 0.0030179 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-29 20:15 | 2022-04-29 21:05 | 80 | 000:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B22042900041 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 50 | 2022-04-29 | 4000 | keep | 0 | Apr | 2022 | 0.0027244 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-04-29 21:30 | 2022-04-29 21:40 | 5 | 000:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR CONTAMINACION EN CAJA PRIMARIA | R22042900093 | New_Event | Cutout Failure | Include | Include | Equipment | 10 | 2022-04-29 | 50 | keep | 0 | Apr | 2022 | 3.4055e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-04-29 23:08 | 2022-04-30 11:00 | 80 | 011:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22042900098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 712 | 2022-04-29 | 56960 | keep | 0 | Apr | 2022 | 0.038795 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-04-30 00:49 | 2022-04-30 11:00 | 14 | 010:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | P22043000001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 611 | 2022-04-30 | 8554 | keep | 0 | Apr | 2022 | 0.0058261 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2022-04-30 03:19 | 2022-04-30 05:35 | 15 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22043000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-04-30 | 2040 | keep | 0 | Apr | 2022 | 0.0013894 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-04-30 03:54 | 2022-04-30 09:27 | 696 | 005:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C22043000005 | New_Event | Bad Weather | Include | Include | Weather | 333 | 2022-04-30 | 231768 | keep | 0 | Apr | 2022 | 0.15786 | 0.00047404 | Sustained | FALSE | FALSE | Not_TMED_Event | 696
VEGA BAJA | 2022-04-30 03:56 | 2022-04-30 15:28 | 40 | 011:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22043000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 692 | 2022-04-30 | 27680 | keep | 0 | Apr | 2022 | 0.018853 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-30 05:04 | 2022-04-30 05:05 | 2608 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C22043000000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-04-30 | 2608 | keep | 0 | Apr | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2022-04-30 05:05 | 2022-04-30 08:34 | 134 | 003:29 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN RISER HACIA SU-4 LA FASE DE LA IZQUIERDA PROBO MALO SE REFIERE A SOTERRADO | C22043000010 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 209 | 2022-04-30 | 28006 | keep | 0 | Apr | 2022 | 0.019075 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
CAGUAS | 2022-04-30 05:25 | 2022-04-30 05:27 | 1403 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERREA | C22043000016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-04-30 | 2806 | keep | 0 | Apr | 2022 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
CAGUAS | 2022-04-30 05:57 | 2022-04-30 05:58 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22043000021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1342 | keep | 0 | Apr | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
HUMACAO | 2022-04-30 05:59 | 2022-04-30 06:00 | 2450 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR EN SERVICIO | C22043000022 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 2450 | keep | 0 | Apr | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-04-30 06:00 | 2022-04-30 09:40 | 150 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C22043000040 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 220 | 2022-04-30 | 33000 | keep | 0 | Apr | 2022 | 0.022476 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-04-30 06:09 | 2022-04-30 06:10 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2725 | keep | 0 | Apr | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-04-30 06:09 | 2022-04-30 06:10 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1834 | keep | 0 | Apr | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-04-30 06:09 | 2022-04-30 06:10 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABLE A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1437 | keep | 0 | Apr | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-04-30 06:09 | 2022-04-30 06:10 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2565 | keep | 0 | Apr | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-04-30 06:09 | 2022-04-30 06:10 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 3565 | keep | 0 | Apr | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-04-30 06:09 | 2022-04-30 06:10 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2751 | keep | 0 | Apr | 2022 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-04-30 06:09 | 2022-04-30 06:10 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 576 | keep | 0 | Apr | 2022 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-04-30 06:09 | 2022-04-30 06:10 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2584 | keep | 0 | Apr | 2022 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-04-30 06:09 | 2022-04-30 06:10 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1606 | keep | 0 | Apr | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-04-30 06:09 | 2022-04-30 06:10 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 29 | keep | 0 | Apr | 2022 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
FAJARDO | 2022-04-30 06:29 | 2022-04-30 06:30 | 1839 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1839 | keep | 0 | Apr | 2022 | 0.0012525 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2022-04-30 06:29 | 2022-04-30 06:30 | 1778 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1778 | keep | 0 | Apr | 2022 | 0.001211 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2022-04-30 06:29 | 2022-04-30 06:30 | 1376 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1376 | keep | 0 | Apr | 2022 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
HUMACAO | 2022-04-30 06:29 | 2022-04-30 06:30 | 3701 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 5400 DE DAGUAO A RIO BLANCO | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 3701 | keep | 0 | Apr | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-04-30 06:29 | 2022-04-30 06:30 | 989 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 5400 DE DAGUAO A RIO BLANCO | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 989 | keep | 0 | Apr | 2022 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2022-04-30 06:29 | 2022-04-30 06:30 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 5400 DE DAGUAO A RIO BLANCO | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1467 | keep | 0 | Apr | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
FAJARDO | 2022-04-30 06:29 | 2022-04-30 06:30 | 293 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 293 | keep | 0 | Apr | 2022 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2022-04-30 06:29 | 2022-04-30 06:30 | 1215 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1215 | keep | 0 | Apr | 2022 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
PONCE | 2022-04-30 06:42 | 2022-04-30 06:43 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22043000006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 4035 | keep | 0 | Apr | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
SAN JUAN | 2022-04-30 06:44 | 2022-04-30 06:45 | 1051 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22043000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1051 | keep | 0 | Apr | 2022 | 0.00071583 | 0.00071583 | Momentary | FALSE | FALSE | Not_TMED_Event | 1051
PONCE | 2022-04-30 06:51 | 2022-04-30 10:26 | 12 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN RISER FUERTE LLUVIA | P22043000007 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2022-04-30 | 2580 | keep | 0 | Apr | 2022 | 0.0017572 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-04-30 07:00 | 2022-04-30 07:01 | 120 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE SU CARGA ESTA TRANSFERIDA AL 5016-02 | P22043000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 120 | keep | 0 | Apr | 2022 | 8.1731e-05 | 8.1731e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-04-30 07:01 | 2022-04-30 08:51 | 50 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO FASE | P22043000025 | New_Event |  |  | Include | Wildlife | 110 | 2022-04-30 | 5500 | keep | 0 | Apr | 2022 | 0.003746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-04-30 07:05 | 2022-04-30 07:06 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 5011-02 | P22043000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1478 | keep | 0 | Apr | 2022 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
HUMACAO | 2022-04-30 07:19 | 2022-04-30 07:20 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22043000034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 181 | keep | 0 | Apr | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
MAYAGÃœEZ | 2022-04-30 07:22 | 2022-04-30 09:55 | 50 | 002:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22043000012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-04-30 | 7650 | keep | 0 | Apr | 2022 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-30 07:26 | 2022-04-30 13:38 | 40 | 006:12 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 30 EN CORTES DE LINEA | B22043000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 372 | 2022-04-30 | 14880 | keep | 0 | Apr | 2022 | 0.010135 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-04-30 07:27 | 2022-04-30 07:28 | 1702 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR EN SERVICIO MAL TIEMPO | C22043000037 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-04-30 07:28 | 2022-04-30 08:02 | 44 | 000:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22043000072 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 34 | 2022-04-30 | 1496 | keep | 0 | Apr | 2022 | 0.0010189 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
SAN JUAN | 2022-04-30 07:39 | 2022-04-30 12:18 | 100 | 004:39 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-4CA | R22043000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2022-04-30 | 27900 | keep | 0 | Apr | 2022 | 0.019003 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-04-30 07:39 | 2022-04-30 07:40 | 2147 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO | B22043000009 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 2147 | keep | 0 | Apr | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
SAN JUAN | 2022-04-30 07:41 | 2022-04-30 13:48 | 60 | 006:07 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN RISER Y 1 X 20 EN SU-A. SECCIONALIZARON T-24 DE 75KVA AVERIADO | R22043000012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 367 | 2022-04-30 | 22020 | keep | 0 | Apr | 2022 | 0.014998 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-30 07:46 | 2022-04-30 07:47 | 3941 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO | B22043000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 3941 | keep | 0 | Apr | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
GUAYAMA | 2022-04-30 07:46 | 2022-04-30 07:47 | 4279 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE CARGA TRANSFERIDA AL 4006-05 | P22043000020 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-30 | 4279 | keep | 0 | Apr | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-04-30 07:46 | 2022-04-30 07:47 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE LLEVA LA CARGA DEL 4003-01 Y DEL 4003-02 | P22043000020 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-30 | 464 | keep | 0 | Apr | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
HUMACAO | 2022-04-30 07:49 | 2022-04-30 07:50 | 676 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22043000041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 676 | keep | 0 | Apr | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
MAYAGÃœEZ | 2022-04-30 07:50 | 2022-04-30 12:10 | 75 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22043000016 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2022-04-30 | 19500 | keep | 0 | Apr | 2022 | 0.013281 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-04-30 07:56 | 2022-04-30 07:57 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22043000018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1827 | keep | 0 | Apr | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
GUAYAMA | 2022-04-30 07:58 | 2022-04-30 07:59 | 4132 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE CARGA TRANSFERIDA AL 4006-05 | P22043000020 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-30 | 4132 | keep | 0 | Apr | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
BAYAMON | 2022-04-30 07:59 | 2022-04-30 08:01 | 2466 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR ALIMENTADOR AMERITA DESGANCHE MASIVO | S22043000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-04-30 | 4932 | keep | 0 | Apr | 2022 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
GUAYAMA | 2022-04-30 07:59 | 2022-04-30 10:04 | 45 | 002:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P22043000029 | 1st_after_momentary |  |  | Include | Wildlife | 125 | 2022-04-30 | 5625 | keep | 0 | Apr | 2022 | 0.0038312 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-04-30 08:00 | 2022-04-30 08:01 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22043000019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1047 | keep | 0 | Apr | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
BAYAMON | 2022-04-30 08:01 | 2022-04-30 14:38 | 150 | 006:37 | P | DESGANCHE | 2 X 100 EN RISER Y 2 X 65 EN C/L DESGANCHE | S22043000076 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 397 | 2022-04-30 | 59550 | keep | 0 | Apr | 2022 | 0.040559 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-04-30 08:01 | 2022-04-30 08:02 | 676 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22043000042 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 676 | keep | 0 | Apr | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
BAYAMON | 2022-04-30 08:02 | 2022-04-30 11:38 | 2435 | 003:36 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO CONDUCTOR A AISLADOR INTERRUPTOR 1909-08 LLEVA CARGA 1907-05 SE CERRO MACHETES N/O ENTRE 1907-05 Y 1909-08 | S22043000008 | New_Event | Wire Down | Include | Include | Equipment | 216 | 2022-04-30 | 525960 | keep | 0 | Apr | 2022 | 0.35823 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-04-30 08:02 | 2022-04-30 11:30 | 2956 | 003:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO CONDUCTOR A AISLADOR Y SE CERRO POR SCADA. ABRIENDO MACHETES DE AMARRE ENTRE 1909-08 Y 1907-05 INTERRUPTOR 1909-08 LLEVA CARGA 1907-05 | S22043000008 | New_Event | Wire Down | Include | Include | Equipment | 208 | 2022-04-30 | 614848 | keep | 0 | Apr | 2022 | 0.41877 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
CAGUAS | 2022-04-30 08:02 | 2022-04-30 08:03 | 476 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 476 | keep | 0 | Apr | 2022 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2022-04-30 08:02 | 2022-04-30 08:03 | 1655 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1655 | keep | 0 | Apr | 2022 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-04-30 08:02 | 2022-04-30 08:03 | 361 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 361 | keep | 0 | Apr | 2022 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2022-04-30 08:02 | 2022-04-30 08:03 | 2842 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2842 | keep | 0 | Apr | 2022 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-04-30 08:02 | 2022-04-30 08:03 | 1702 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-04-30 08:02 | 2022-04-30 08:03 | 918 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 918 | keep | 0 | Apr | 2022 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2022-04-30 08:03 | 2022-04-30 17:13 | 44 | 009:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22043000072 | Partial_restoration | Bad Weather | Include | Include | Weather | 550 | 2022-04-30 | 24200 | keep | 0 | Apr | 2022 | 0.016483 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-30 08:07 | 2022-04-30 08:09 | 172 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO MAL TIEMPO | S22043000013 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-04-30 | 344 | keep | 0 | Apr | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
HUMACAO | 2022-04-30 08:11 | 2022-04-30 11:46 | 32 | 003:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22043000043 | New_Event |  |  | Include | Wildlife | 215 | 2022-04-30 | 6880 | keep | 0 | Apr | 2022 | 0.0046859 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2022-04-30 08:14 | 2022-04-30 09:48 | 190 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO | C22043000044 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2022-04-30 | 17860 | keep | 0 | Apr | 2022 | 0.012164 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
BAYAMON | 2022-04-30 08:16 | 2022-04-30 08:19 | 723 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 MAL TIEMPO | B22043000000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-04-30 | 2169 | keep | 0 | Apr | 2022 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-04-30 08:16 | 2022-04-30 08:19 | 1976 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 MAL TIEMPO | B22043000000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-04-30 | 5928 | keep | 0 | Apr | 2022 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-04-30 08:17 | 2022-04-30 08:18 | 5961 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR 1713-05 LLEVANDO 95% 1717-02 MAL TIEMPO | B22043000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 5961 | keep | 0 | Apr | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-04-30 08:17 | 2022-04-30 08:18 | 865 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR 1713-05 LLEVANDO 95% 1717-02 MAL TIEMPO | B22043000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 865 | keep | 0 | Apr | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
BAYAMON | 2022-04-30 08:21 | 2022-04-30 10:06 | 29 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22043000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-04-30 | 3045 | keep | 0 | Apr | 2022 | 0.0020739 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2022-04-30 08:23 | 2022-04-30 08:24 | 500 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECERRO PARTE POR 1206-3 | S22043000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 500 | keep | 0 | Apr | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-04-30 08:23 | 2022-04-30 08:24 | 3306 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECERRO LLEVA PARTE 1204-05 MAL TIEMPO | S22043000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 3306 | keep | 0 | Apr | 2022 | 0.0022517 | 0.0022517 | Momentary | FALSE | FALSE | Not_TMED_Event | 3306
BAYAMON | 2022-04-30 08:25 | 2022-04-30 09:18 | 6136 | 000:53 | T | DESGANCHE | SE CERRO POR SCADA SE RETIRO RAMA CON VARETA | S22043000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2022-04-30 | 325208 | keep | 0 | Apr | 2022 | 0.2215 | 0.0041792 | Sustained | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2022-04-30 08:28 | 2022-04-30 20:57 | 1 | 012:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22043000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 749 | 2022-04-30 | 749 | keep | 0 | Apr | 2022 | 0.00051014 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-04-30 08:34 | 2022-04-30 09:15 | 100 | 000:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22043000026 | New_Event | Bad Weather | Include | Include | Weather | 41 | 2022-04-30 | 4100 | keep | 0 | Apr | 2022 | 0.0027925 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-30 08:35 | 2022-04-30 08:36 | 1000 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO SU CARGA POR 1620-05 MAL TIEMPO | S22043000028 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 1000 | keep | 0 | Apr | 2022 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-04-30 08:35 | 2022-04-30 08:36 | 1615 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA PARTE DEL 1206-3 MAL TIEMPO | S22043000028 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 1615 | keep | 0 | Apr | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
BAYAMON | 2022-04-30 08:37 | 2022-04-30 15:37 | 45 | 007:00 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES QUEMADO | S22043000029 | New_Event | Switch Failure | Include | Include | Equipment | 420 | 2022-04-30 | 18900 | keep | 0 | Apr | 2022 | 0.012873 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-04-30 08:44 | 2022-04-30 09:27 | 2451 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZARON CONDUCTOR SAFADO SOBRE CRUCETA DEL 2403-01 95% X 2403-02. ENTRANDO 2403-02 100% Y 60% DE CARGA TRANSFERIDA 2403-01. | R22043000018 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2022-04-30 | 105393 | keep | 0 | Apr | 2022 | 0.071783 | 0.0016694 | Sustained | FALSE | FALSE | Not_TMED_Event | 2451
CANOVANAS | 2022-04-30 08:44 | 2022-04-30 09:27 | 500 | 000:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZARON CONDUCTOR SAFADO SOBRE CRUCETA DEL 2403-01 95% X 2403-02. ENTRANDO 2403-02 100% Y 60% DE CARGA TRANSFERIDA 2403-01. | R22043000018 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2022-04-30 | 21500 | keep | 0 | Apr | 2022 | 0.014644 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BARRANQUITAS | 2022-04-30 08:44 | 2022-04-30 10:13 | 2 | 001:29 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA Y ARBOL | C22043000052 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 89 | 2022-04-30 | 178 | keep | 0 | Apr | 2022 | 0.00012123 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-04-30 08:45 | 2022-04-30 10:22 | 1681 | 001:37 | T | DESGANCHE | DISPARO SE RETIRO CON VARETA BAMBUA SOBRE FASE CAMINO LOS GUANOS Y SE RESETEO BANDERA SE CERRO QUEDO EN SERVICIO SU CARGA POR 1303-4 | S22043000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-04-30 | 163057 | keep | 0 | Apr | 2022 | 0.11106 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-04-30 08:45 | 2022-04-30 10:22 | 1598 | 001:37 | T | DESGANCHE | DISPARO SE RETIRO CON VARETA BAMBUA SOBRE FASE CAMINO LOS GUANOS Y SE RESETEO BANDERA SE CERRO QUEDO EN SERVICIO SU CARGA POR 1303-4 | S22043000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-04-30 | 155006 | keep | 0 | Apr | 2022 | 0.10557 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2022-04-30 08:45 | 2022-04-30 08:46 | 4100 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR CON 10% DE SU CARGA POR 1806-02 | B22043000027 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 4100 | keep | 0 | Apr | 2022 | 0.0027925 | 0.0027925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4100
BAYAMON | 2022-04-30 08:49 | 2022-04-30 21:16 | 100 | 012:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22043000031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 747 | 2022-04-30 | 74700 | keep | 0 | Apr | 2022 | 0.050878 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-30 08:49 | 2022-04-30 12:25 | 117 | 003:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22043000053 | New_Event | Bad Weather | Include | Include | Weather | 216 | 2022-04-30 | 25272 | keep | 0 | Apr | 2022 | 0.017213 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
FAJARDO | 2022-04-30 08:57 | 2022-04-30 10:37 | 90 | 001:40 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1 X 50 EN CORTES DE LINEAS REEMPLAZO PARARRAYO | R22043000021 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 100 | 2022-04-30 | 9000 | keep | 0 | Apr | 2022 | 0.0061299 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-04-30 09:14 | 2022-04-30 09:15 | 4369 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECERRO INTERRUPTOR EN SERVICIO | C22043000063 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2022-04-30 | 4369 | keep | 0 | Apr | 2022 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2022-04-30 09:15 | 2022-04-30 11:35 | 60 | 002:20 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 3 RBA DE 50 AMP. CONTAMINACION EN SU-10 | C22043000066 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 140 | 2022-04-30 | 8400 | keep | 0 | Apr | 2022 | 0.0057212 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-30 09:26 | 2022-04-30 09:28 | 1825 | 000:02 | T | DESGANCHE | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1118-9 | S22043000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-04-30 | 3650 | keep | 0 | Apr | 2022 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-04-30 09:26 | 2022-04-30 09:28 | 4398 | 000:02 | T | DESGANCHE | DISPARO LLEVA 1118-8 SE PROBO QUEDO EN SERVICIO | S22043000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-04-30 | 8796 | keep | 0 | Apr | 2022 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
BAYAMON | 2022-04-30 09:27 | 2022-04-30 09:28 | 222 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 MAL TIEMPO | S22043000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 222 | keep | 0 | Apr | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-04-30 09:27 | 2022-04-30 09:28 | 4456 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 MAL TIEMPO | S22043000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 4456 | keep | 0 | Apr | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
CANOVANAS | 2022-04-30 09:27 | 2022-04-30 12:00 | 980 | 002:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR SAFADO SOBRE CRUCETA Y CERRO MACHETES | R22043000018 | Partial_restoration | Wire Down | Include | Include | Equipment | 153 | 2022-04-30 | 149940 | keep | 0 | Apr | 2022 | 0.10212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-30 09:28 | 2022-04-30 19:42 | 50 | 010:14 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S22043000116 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 614 | 2022-04-30 | 30700 | keep | 0 | Apr | 2022 | 0.02091 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-04-30 09:29 | 2022-04-30 21:32 | 9 | 012:03 | P | DESGANCHE | 1 X 15 EN XMR SE RETIRO ENREDADERA | B22043000059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 723 | 2022-04-30 | 6507 | keep | 0 | Apr | 2022 | 0.0044319 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2022-04-30 09:29 | 2022-04-30 15:04 | 13 | 005:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO | C22043000068 | New_Event | Bad Weather | Include | Include | Weather | 335 | 2022-04-30 | 4355 | keep | 0 | Apr | 2022 | 0.0029662 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2022-04-30 09:35 | 2022-04-30 09:36 | 1717 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 300 | P22043000031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1717 | keep | 0 | Apr | 2022 | 0.0011694 | 0.0011694 | Momentary | FALSE | FALSE | Not_TMED_Event | 1717
PONCE | 2022-04-30 09:35 | 2022-04-30 09:36 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 300 | P22043000031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 974 | keep | 0 | Apr | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
PONCE | 2022-04-30 09:35 | 2022-04-30 09:36 | 1905 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 300 | P22043000031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1905 | keep | 0 | Apr | 2022 | 0.0012975 | 0.0012975 | Momentary | FALSE | FALSE | Not_TMED_Event | 1905
PONCE | 2022-04-30 09:35 | 2022-04-30 09:36 | 1262 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 300 | P22043000031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1262 | keep | 0 | Apr | 2022 | 0.00085954 | 0.00085954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1262
PONCE | 2022-04-30 09:35 | 2022-04-30 09:36 | 200 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 300 | P22043000031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 200 | keep | 0 | Apr | 2022 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-04-30 09:35 | 2022-04-30 09:36 | 222 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 300 | P22043000031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 222 | keep | 0 | Apr | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
PONCE | 2022-04-30 09:35 | 2022-04-30 09:36 | 537 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 300 | P22043000031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 537 | keep | 0 | Apr | 2022 | 0.00036575 | 0.00036575 | Momentary | FALSE | FALSE | Not_TMED_Event | 537
BAYAMON | 2022-04-30 09:46 | 2022-04-30 11:47 | 25 | 002:01 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | B22043000063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-04-30 | 3025 | keep | 0 | Apr | 2022 | 0.0020603 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-04-30 09:47 | 2022-04-30 10:59 | 20 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22043000033 | New_Event |  |  | Include | Wildlife | 72 | 2022-04-30 | 1440 | keep | 0 | Apr | 2022 | 0.00098078 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-04-30 09:57 | 2022-04-30 12:45 | 20 | 002:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA | S22043000131 | New_Event | Bad Weather | Include | Include | Weather | 168 | 2022-04-30 | 3360 | keep | 0 | Apr | 2022 | 0.0022885 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-04-30 10:00 | 2022-04-30 10:01 | 562 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 17900 | P22043000037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 562 | keep | 0 | Apr | 2022 | 0.00038278 | 0.00038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 562
PONCE | 2022-04-30 10:00 | 2022-04-30 10:01 | 688 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 17900 | P22043000037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 688 | keep | 0 | Apr | 2022 | 0.00046859 | 0.00046859 | Momentary | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2022-04-30 10:00 | 2022-04-30 10:01 | 658 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 17900 | P22043000037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 658 | keep | 0 | Apr | 2022 | 0.00044816 | 0.00044816 | Momentary | FALSE | FALSE | Not_TMED_Event | 658
PONCE | 2022-04-30 10:00 | 2022-04-30 10:01 | 4009 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 17900 | P22043000037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 4009 | keep | 0 | Apr | 2022 | 0.0027305 | 0.0027305 | Momentary | FALSE | FALSE | Not_TMED_Event | 4009
YAUCO | 2022-04-30 10:05 | 2022-04-30 11:57 | 10 | 001:52 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR PARA REALIZAR DESGANCHE SECUNDARIO Y LEVANTAR SECUNDARIA DEL PISO | P22043000035 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 112 | 2022-04-30 | 1120 | keep | 0 | Apr | 2022 | 0.00076283 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-04-30 10:08 | 2022-04-30 14:41 | 1 | 004:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER HACIA TRANSCLOSURE MAL TIEMPO | C22043000080 | New_Event | Bad Weather | Include | Include | Weather | 273 | 2022-04-30 | 273 | keep | 0 | Apr | 2022 | 0.00018594 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-04-30 10:13 | 2022-04-30 10:14 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2725 | keep | 0 | Apr | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-04-30 10:13 | 2022-04-30 10:14 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1834 | keep | 0 | Apr | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-04-30 10:13 | 2022-04-30 10:14 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1437 | keep | 0 | Apr | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-04-30 10:13 | 2022-04-30 10:14 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2565 | keep | 0 | Apr | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-04-30 10:13 | 2022-04-30 10:14 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 3565 | keep | 0 | Apr | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-04-30 10:13 | 2022-04-30 10:14 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22043000038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1606 | keep | 0 | Apr | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BARRANQUITAS | 2022-04-30 10:14 | 2022-04-30 12:29 | 2 | 002:15 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA Y ARBOL | C22043000052 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 135 | 2022-04-30 | 270 | keep | 0 | Apr | 2022 | 0.0001839 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-04-30 10:20 | 2022-04-30 19:54 | 6 | 009:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO DE CAJA A LINEA EN XMR | B22043000069 | New_Event | Wire Down | Include | Include | Equipment | 574 | 2022-04-30 | 3444 | keep | 0 | Apr | 2022 | 0.0023457 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-04-30 10:21 | 2022-04-30 14:47 | 140 | 004:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22043000083 | New_Event | Cutout Failure | Include | Include | Equipment | 266 | 2022-04-30 | 37240 | keep | 0 | Apr | 2022 | 0.025364 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
MAYAGÃœEZ | 2022-04-30 10:24 | 2022-04-30 14:35 | 50 | 004:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22043000042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-04-30 | 12550 | keep | 0 | Apr | 2022 | 0.0085477 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-04-30 10:25 | 2022-04-30 11:50 | 8 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22043000043 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2022-04-30 | 680 | keep | 0 | Apr | 2022 | 0.00046314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-04-30 10:28 | 2022-04-30 11:54 | 30 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P22043000041 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2022-04-30 | 2580 | keep | 0 | Apr | 2022 | 0.0017572 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-04-30 10:38 | 2022-04-30 12:58 | 20 | 002:20 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR RAMA CRUZANDO LINEA | A22043000020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-04-30 | 2800 | keep | 0 | Apr | 2022 | 0.0019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-30 10:42 | 2022-04-30 18:35 | 42 | 007:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22043000090 | New_Event | Bad Weather | Include | Include | Weather | 473 | 2022-04-30 | 19866 | keep | 0 | Apr | 2022 | 0.013531 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
FAJARDO | 2022-04-30 10:50 | 2022-04-30 12:10 | 55 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R22043000053 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2022-04-30 | 4400 | keep | 0 | Apr | 2022 | 0.0029968 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
GUAYAMA | 2022-04-30 10:53 | 2022-04-30 12:22 | 100 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P22043000042 | New_Event |  |  | Include | Wildlife | 89 | 2022-04-30 | 8900 | keep | 0 | Apr | 2022 | 0.0060617 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-04-30 10:56 | 2022-04-30 13:20 | 108 | 002:24 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR Y SE ESTABLECE GOI PARA REPARAR ALAMBRE SAFADO ENCIMA CRUCETA | S22043000161 | New_Event | Wire Down | Include | Include | Equipment | 144 | 2022-04-30 | 15552 | keep | 0 | Apr | 2022 | 0.010592 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
CAGUAS | 2022-04-30 10:57 | 2022-04-30 17:54 | 118 | 006:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22043000093 | New_Event | Bad Weather | Include | Include | Weather | 417 | 2022-04-30 | 49206 | keep | 0 | Apr | 2022 | 0.033514 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
CANOVANAS | 2022-04-30 11:07 | 2022-04-30 16:15 | 50 | 005:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22043000058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2022-04-30 | 15400 | keep | 0 | Apr | 2022 | 0.010489 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-30 11:36 | 2022-04-30 13:18 | 10 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR AVE | R22043000064 | New_Event |  |  | Include | Wildlife | 102 | 2022-04-30 | 1020 | keep | 0 | Apr | 2022 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-04-30 11:43 | 2022-04-30 18:11 | 42 | 006:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C22043000112 | New_Event |  |  | Include | Wildlife | 388 | 2022-04-30 | 16296 | keep | 0 | Apr | 2022 | 0.011099 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
MAYAGÃœEZ | 2022-04-30 11:46 | 2022-04-30 15:04 | 45 | 003:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22043000053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2022-04-30 | 8910 | keep | 0 | Apr | 2022 | 0.0060686 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-04-30 11:48 | 2022-04-30 11:50 | 513 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO 20 % POR 1118-10 MAL TIEMPO | S22043000000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-04-30 | 1026 | keep | 0 | Apr | 2022 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-04-30 11:48 | 2022-04-30 11:50 | 2782 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 20 % DEL 1111-1 MAL TIEMPO | S22043000000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-04-30 | 5564 | keep | 0 | Apr | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2022-04-30 11:50 | 2022-04-30 11:52 | 271 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO | S22043000174 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-04-30 | 542 | keep | 0 | Apr | 2022 | 0.00036915 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2022-04-30 12:08 | 2022-04-30 16:44 | 1 | 004:36 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN C/L | R22043000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2022-04-30 | 276 | keep | 0 | Apr | 2022 | 0.00018798 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-04-30 12:10 | 2022-04-30 12:11 | 1067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22043000044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1067 | keep | 0 | Apr | 2022 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
BAYAMON | 2022-04-30 12:12 | 2022-04-30 12:15 | 3798 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO | B22043000079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-30 | 11394 | keep | 0 | Apr | 2022 | 0.0077604 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
BAYAMON | 2022-04-30 12:13 | 2022-04-30 21:45 | 31 | 009:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE INTERRUPTOR PARA REMPLAZO DE CAJA PRIMARIA EN AZOTEA SJ-220430-03 | S22043000185 | New_Event | Cutout Failure | Include | Include | Equipment | 572 | 2022-04-30 | 17732 | keep | 0 | Apr | 2022 | 0.012077 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CANOVANAS | 2022-04-30 12:14 | 2022-04-30 12:56 | 75 | 000:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R22043000071 | New_Event | Bad Weather | Include | Include | Weather | 42 | 2022-04-30 | 3150 | keep | 0 | Apr | 2022 | 0.0021455 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-04-30 12:15 | 2022-04-30 15:04 | 175 | 002:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22043000121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-04-30 | 29575 | keep | 0 | Apr | 2022 | 0.020143 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
AGUADILLA | 2022-04-30 12:17 | 2022-04-30 15:20 | 129 | 003:03 | T | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PRIMARIO PARTIDO Y SE CERRO EL INTERRUPTOR | M22043000058 | New_Event | Defective Pole | Include | Include | Equipment | 183 | 2022-04-30 | 23607 | keep | 0 | Apr | 2022 | 0.016079 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
BAYAMON | 2022-04-30 12:20 | 2022-04-30 22:48 | 52 | 010:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22043000081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 628 | 2022-04-30 | 32656 | keep | 0 | Apr | 2022 | 0.022242 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
ARECIBO | 2022-04-30 12:24 | 2022-04-30 21:10 | 40 | 008:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22043000022 | New_Event | Cutout Failure | Include | Include | Equipment | 526 | 2022-04-30 | 21040 | keep | 0 | Apr | 2022 | 0.01433 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-04-30 12:29 | 2022-04-30 12:30 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2725 | keep | 0 | Apr | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-04-30 12:29 | 2022-04-30 12:30 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1834 | keep | 0 | Apr | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-04-30 12:29 | 2022-04-30 12:30 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1437 | keep | 0 | Apr | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-04-30 12:29 | 2022-04-30 12:30 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2565 | keep | 0 | Apr | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-04-30 12:29 | 2022-04-30 12:30 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C22043000000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 3565 | keep | 0 | Apr | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-04-30 12:29 | 2022-04-30 12:30 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2751 | keep | 0 | Apr | 2022 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-04-30 12:29 | 2022-04-30 12:30 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 576 | keep | 0 | Apr | 2022 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-04-30 12:29 | 2022-04-30 12:30 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2584 | keep | 0 | Apr | 2022 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-04-30 12:29 | 2022-04-30 12:30 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1606 | keep | 0 | Apr | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-04-30 12:29 | 2022-04-30 12:30 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 29 | keep | 0 | Apr | 2022 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2022-04-30 12:29 | 2022-04-30 12:30 | 4035 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 4035 | keep | 0 | Apr | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-04-30 12:29 | 2022-04-30 12:30 | 3718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22043000047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 3718 | keep | 0 | Apr | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BARRANQUITAS | 2022-04-30 12:30 | 2022-04-30 16:07 | 2 | 003:37 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA Y ARBOL | C22043000052 | Partial_restoration | Secondary Vegetation | Include | Include | Vegetation | 217 | 2022-04-30 | 434 | keep | 0 | Apr | 2022 | 0.0002956 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-30 12:30 | 2022-04-30 13:22 | 3 | 000:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | P22043000043 | New_Event | Bad Weather | Include | Include | Weather | 52 | 2022-04-30 | 156 | keep | 0 | Apr | 2022 | 0.00010625 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-04-30 12:31 | 2022-04-30 13:29 | 143 | 000:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C22043000124 | New_Event | Bad Weather | Include | Include | Weather | 58 | 2022-04-30 | 8294 | keep | 0 | Apr | 2022 | 0.005649 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
BAYAMON | 2022-04-30 12:35 | 2022-04-30 12:36 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | S22043000191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 2435 | keep | 0 | Apr | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-04-30 12:35 | 2022-04-30 12:36 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | S22043000191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 2956 | keep | 0 | Apr | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
PONCE | 2022-04-30 12:39 | 2022-04-30 15:08 | 45 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P22043000050 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2022-04-30 | 6705 | keep | 0 | Apr | 2022 | 0.0045667 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-04-30 12:40 | 2022-04-30 14:28 | 19 | 001:48 | P | ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA RELOCALIZARLO POSTE PRIMARIO PODRIDO | C22043000115 | New_Event | Defective Pole | Include | Include | Equipment | 108 | 2022-04-30 | 2052 | keep | 0 | Apr | 2022 | 0.0013976 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2022-04-30 12:52 | 2022-04-30 15:45 | 75 | 002:53 | P | DESGANCHE | 1 X 80 CORTE DE LINEA HAY FASE ABIERTA HAY QUE DESGANCHAR EL DESGANCHE TRABAJRA CON WR 6111721 | M2243000065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-04-30 | 12975 | keep | 0 | Apr | 2022 | 0.0088372 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-04-30 12:53 | 2022-04-30 14:28 | 1356 | 001:35 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE ALIMENTADOR SE SECCIONALIZO 75% EN SERVICIO | S22043000197 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 95 | 2022-04-30 | 128820 | keep | 0 | Apr | 2022 | 0.087739 | 0.00092357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1356
VEGA BAJA | 2022-04-30 12:57 | 2022-04-30 12:58 | 1859 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO | B22043000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 1859 | keep | 0 | Apr | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BARRANQUITAS | 2022-04-30 13:00 | 2022-04-30 17:40 | 10 | 004:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | C22043000130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2022-04-30 | 2800 | keep | 0 | Apr | 2022 | 0.0019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-04-30 13:20 | 2022-04-30 13:21 | 4035 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | P22043000052 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 4035 | keep | 0 | Apr | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
MAYAGÃœEZ | 2022-04-30 13:22 | 2022-04-30 21:01 | 100 | 007:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22043000066 | New_Event | Wire Down | Include | Include | Equipment | 459 | 2022-04-30 | 45900 | keep | 0 | Apr | 2022 | 0.031262 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-04-30 13:29 | 2022-04-30 13:55 | 30 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | R22043000079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-04-30 | 780 | keep | 0 | Apr | 2022 | 0.00053125 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-04-30 13:33 | 2022-04-30 13:34 | 4035 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | P22043000053 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 4035 | keep | 0 | Apr | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
SAN JUAN | 2022-04-30 13:39 | 2022-05-01 13:15 | 22 | 023:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22004300212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1416 | 2022-04-30 | 31152 | keep | 0 | Apr | 2022 | 0.021217 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
FAJARDO | 2022-04-30 13:40 | 2022-04-30 14:40 | 50 | 001:00 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | R22043000080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-04-30 | 3000 | keep | 0 | Apr | 2022 | 0.0020433 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-04-30 13:48 | 2022-04-30 17:28 | 12 | 003:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO PM 100KVA QUEMADO | R22043000012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 220 | 2022-04-30 | 2640 | keep | 0 | Apr | 2022 | 0.0017981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-04-30 13:52 | 2022-04-30 15:49 | 76 | 001:57 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C22043000146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-04-30 | 8892 | keep | 0 | Apr | 2022 | 0.0060563 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
PONCE | 2022-04-30 13:53 | 2022-04-30 16:00 | 75 | 002:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P22043000055 | New_Event |  |  | Include | Wildlife | 127 | 2022-04-30 | 9525 | keep | 0 | Apr | 2022 | 0.0064874 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-04-30 14:03 | 2022-04-30 18:13 | 25 | 004:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22043000071 | New_Event |  |  | Include | Wildlife | 250 | 2022-04-30 | 6250 | keep | 0 | Apr | 2022 | 0.0042568 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-04-30 14:04 | 2022-04-30 14:05 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22043000150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 181 | keep | 0 | Apr | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
MAYAGÃœEZ | 2022-04-30 14:04 | 2022-04-30 18:12 | 80 | 004:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22043000072 | New_Event |  |  | Include | Wildlife | 248 | 2022-04-30 | 19840 | keep | 0 | Apr | 2022 | 0.013513 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-04-30 14:10 | 2022-04-30 14:30 | 5 | 000:20 | P | DESGANCHE | SE ABRIO C/L PARA RETIRAR ARBOL DE LA LINEA | R22043000076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-04-30 | 100 | keep | 0 | Apr | 2022 | 6.811e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-04-30 14:15 | 2022-04-30 14:16 | 1945 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | P22043000056 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 1945 | keep | 0 | Apr | 2022 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
GUAYAMA | 2022-04-30 14:15 | 2022-04-30 14:16 | 215 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | P22043000056 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 215 | keep | 0 | Apr | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
HUMACAO | 2022-04-30 14:22 | 2022-04-30 14:23 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22043000153 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 181 | keep | 0 | Apr | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
BAYAMON | 2022-04-30 14:28 | 2022-04-30 16:42 | 339 | 002:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO PARA REEMPLAZAR 3 CAJAS PRIMARIAS QUEMADAS EN RISER Y SE CERRARON MACHETES. 80% EN SERVICIO | S22043000197 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 134 | 2022-04-30 | 45426 | keep | 0 | Apr | 2022 | 0.030939 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-04-30 14:30 | 2022-04-30 14:40 | 30 | 000:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R22043000083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-04-30 | 300 | keep | 0 | Apr | 2022 | 0.00020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-30 14:32 | 2022-04-30 17:47 | 30 | 003:15 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B22043000098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-04-30 | 5850 | keep | 0 | Apr | 2022 | 0.0039844 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-30 14:48 | 2022-05-01 15:03 | 6 | 024:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO BAJANTE | S22043000222 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1455 | 2022-04-30 | 8730 | keep | 0 | Apr | 2022 | 0.005946 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-04-30 14:52 | 2022-04-30 15:49 | 9 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | LINEA SECUNDARIA AVERIADA | P22043000059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-04-30 | 513 | keep | 0 | Apr | 2022 | 0.0003494 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-04-30 14:55 | 2022-04-30 17:08 | 14 | 002:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | R22043000087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 133 | 2022-04-30 | 1862 | keep | 0 | Apr | 2022 | 0.0012682 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-04-30 15:02 | 2022-04-30 15:03 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 478 | keep | 0 | Apr | 2022 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-04-30 15:02 | 2022-04-30 15:03 | 854 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 854 | keep | 0 | Apr | 2022 | 0.00058166 | 0.00058166 | Momentary | FALSE | FALSE | Not_TMED_Event | 854
BAYAMON | 2022-04-30 15:02 | 2022-04-30 15:05 | 723 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-30 | 2169 | keep | 0 | Apr | 2022 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-04-30 15:02 | 2022-04-30 15:05 | 1976 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-30 | 5928 | keep | 0 | Apr | 2022 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-04-30 15:02 | 2022-04-30 15:17 | 748 | 000:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA AMELIA 38 KV Y LINEA 9700 | B22043000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-04-30 | 11220 | keep | 0 | Apr | 2022 | 0.0076419 | 0.00050946 | Sustained | FALSE | FALSE | Not_TMED_Event | 748
BAYAMON | 2022-04-30 15:02 | 2022-04-30 15:17 | 33 | 000:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA AMELIA 38 KV Y LINEA 9700 | B22043000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-04-30 | 495 | keep | 0 | Apr | 2022 | 0.00033714 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2022-04-30 15:02 | 2022-05-01 01:04 | 67 | 010:02 | S | DISPARO DE BARRA DE TRANSMISION | SE REMPLAZO AISLACION Y BUSHINGS EN BASE DE FUSIBLES DE XMR 1803-00 | B22043000284 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 602 | 2022-04-30 | 40334 | keep | 0 | Apr | 2022 | 0.027471 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-04-30 15:02 | 2022-05-01 01:03 | 1587 | 010:01 | S | DISPARO DE BARRA DE TRANSMISION | SE REMPLAZO AISLACION Y BUSHINGS EN BASE DE FUSIBLES DE XMR 1803-00 | S22043000284 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 601 | 2022-04-30 | 953787 | keep | 0 | Apr | 2022 | 0.64962 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
BAYAMON | 2022-04-30 15:02 | 2022-05-01 01:04 | 521 | 010:02 | S | DISPARO DE BARRA DE TRANSMISION | SE REMPLAZO AISLACION Y BUSHINGS EN BASE DE FUSIBLES DE XMR 1803-00 1803-04 POR 1803-01 | B22043000284 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 602 | 2022-04-30 | 313642 | keep | 0 | Apr | 2022 | 0.21362 | 0.00035485 | Sustained | FALSE | FALSE | Not_TMED_Event | 521
BAYAMON | 2022-04-30 15:02 | 2022-05-01 01:01 | 1307 | 009:59 | S | DISPARO DE BARRA DE TRANSMISION | SE REMPLAZO AISLACION Y BUSHINGS EN BASE DE FUSIBLES DE XMR 1803-00 | B22043000284 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 599 | 2022-04-30 | 782893 | keep | 0 | Apr | 2022 | 0.53322 | 0.00089019 | Sustained | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2022-04-30 15:10 | 2022-04-30 15:53 | 175 | 000:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22043000121 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-04-30 | 7525 | keep | 0 | Apr | 2022 | 0.0051252 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-04-30 15:13 | 2022-04-30 15:23 | 13 | 000:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO | C22043000068 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2022-04-30 | 130 | keep | 0 | Apr | 2022 | 8.8542e-05 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-04-30 15:17 | 2022-04-30 16:00 | 45 | 000:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22043000053 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-04-30 | 1935 | keep | 0 | Apr | 2022 | 0.0013179 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-30 15:17 | 2022-04-30 15:58 | 8 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTE SECUNDARIO | B22042900043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2022-04-30 | 328 | keep | 0 | Apr | 2022 | 0.0002234 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-04-30 15:20 | 2022-05-01 02:30 | 64 | 011:10 | P | ESTRUCTURA AVERIADA | SE REMPLAZO DOS POSTES DE 45 PIES | M22043000058 | Partial_restoration | Defective Pole | Include | Include | Equipment | 670 | 2022-04-30 | 42880 | keep | 0 | Apr | 2022 | 0.029205 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-04-30 15:25 | 2022-04-30 18:50 | 60 | 003:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA | R22043000100 | New_Event | Cutout Failure | Include | Include | Equipment | 205 | 2022-04-30 | 12300 | keep | 0 | Apr | 2022 | 0.0083775 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-04-30 15:33 | 2022-04-30 17:39 | 748 | 002:06 | S | DISPARO DE BARRA DE TRANSMISION | SE INSPECCIONO BARRA DE BAY VIEW Y SE CERRO A TRAVES LINEA 6400 | B22043000000 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-04-30 | 94248 | keep | 0 | Apr | 2022 | 0.064192 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-30 15:33 | 2022-04-30 17:39 | 33 | 002:06 | S | DISPARO DE BARRA DE TRANSMISION | SE INSPECCIONO BARRA DE BAY VIEW Y SE CERRO A TRAVES LINEA 6400 | B22043000000 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-04-30 | 4158 | keep | 0 | Apr | 2022 | 0.002832 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-30 15:45 | 2022-04-30 15:46 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 0800 DE COMSAT A CIDRA | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1565 | keep | 0 | Apr | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-04-30 15:45 | 2022-04-30 15:46 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 0800 DE COMSAT A CIDRA | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 976 | keep | 0 | Apr | 2022 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-04-30 15:45 | 2022-04-30 15:46 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 0800 DE COMSAT A CIDRA | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 548 | keep | 0 | Apr | 2022 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-04-30 15:45 | 2022-04-30 15:46 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 0800 DE COMSAT A CIDRA | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 315 | keep | 0 | Apr | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-04-30 15:45 | 2022-04-30 15:46 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 0800 DE COMSAT A CIDRA | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 870 | keep | 0 | Apr | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-04-30 15:45 | 2022-04-30 15:46 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 0800 DE COMSAT A CIDRA | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2906 | keep | 0 | Apr | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-04-30 15:45 | 2022-04-30 15:46 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 0800 DE COMSAT A CIDRA | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2343 | keep | 0 | Apr | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
MAYAGÃœEZ | 2022-04-30 15:45 | 2022-05-03 17:00 | 20 | 073:15 | P | DESGANCHE | FASE ABIERTA HAY QUE DESGANCHAR EL DESGANCHE TRABAJARA CON WR 6111721 SE LLAMO CLIENTE EL DIA 5/4 2022 INDCO QUE ELSERVICO SE RESTABLECIO COMPLETO EL 5/03 A LA 5:00PM. EMPLEADO NO HA CERRADO ORDENES TODAVIA | M2243000065 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4395 | 2022-04-30 | 87900 | keep | 0 | Apr | 2022 | 0.059868 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-30 16:00 | 2022-05-01 09:10 | 225 | 017:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REPORTA AVERIA POR DESGANCHE | S22043000264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1030 | 2022-04-30 | 231750 | keep | 0 | Apr | 2022 | 0.15784 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
BAYAMON | 2022-04-30 16:05 | 2022-04-30 16:06 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22043000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 478 | keep | 0 | Apr | 2022 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-04-30 16:05 | 2022-04-30 16:06 | 852 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 852 | keep | 0 | Apr | 2022 | 0.00058029 | 0.00058029 | Momentary | FALSE | FALSE | Not_TMED_Event | 852
BAYAMON | 2022-04-30 16:05 | 2022-04-30 16:08 | 723 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B22043000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-30 | 2169 | keep | 0 | Apr | 2022 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-04-30 16:05 | 2022-04-30 16:08 | 1976 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B22043000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-04-30 | 5928 | keep | 0 | Apr | 2022 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
HUMACAO | 2022-04-30 16:06 | 2022-04-30 17:58 | 181 | 001:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR CONDUCTOR PRIMARIO Y DESCRUZAR VIAJERO DE ENTRE LAS FASES CG-220430-01 | C22043000210 | New_Event | Wire Down | Include | Include | Equipment | 112 | 2022-04-30 | 20272 | keep | 0 | Apr | 2022 | 0.013807 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
PONCE | 2022-04-30 16:11 | 2022-04-30 16:50 | 84 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P22043000084 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2022-04-30 | 3276 | keep | 0 | Apr | 2022 | 0.0022313 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
VEGA BAJA | 2022-04-30 16:21 | 2022-04-30 16:51 | 14 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | B22043000033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-04-30 | 420 | keep | 0 | Apr | 2022 | 0.00028606 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-04-30 16:22 | 2022-05-01 10:48 | 1 | 018:26 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER Y 1 X 50 EN TRANSCLOUSURE HACIA BOMBAS DE ACUEDUCTO | S22043000279 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1106 | 2022-04-30 | 1106 | keep | 0 | Apr | 2022 | 0.00075329 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-30 16:25 | 2022-04-30 16:26 | 1342 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO INTERRUPTOR EN SERVICIO | C22043000000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-04-30 | 1342 | keep | 0 | Apr | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2022-04-30 16:26 | 2022-04-30 20:41 | 20 | 004:15 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN CORTE DE LINEA Y 1 X 40 EN RISER CONDUCTOR SOTERRADO AVERIADO SE REFIERE A SOTERRADO PARA QUE LO TRABAJEN MAÃ‘ANA | C22043000231 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 255 | 2022-04-30 | 5100 | keep | 0 | Apr | 2022 | 0.0034736 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-30 16:27 | 2022-04-30 18:00 | 31 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22043000214 | New_Event | Bad Weather | Include | Include | Weather | 93 | 2022-04-30 | 2883 | keep | 0 | Apr | 2022 | 0.0019636 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2022-04-30 16:34 | 2022-04-30 21:33 | 30 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22043000290 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2022-04-30 | 8970 | keep | 0 | Apr | 2022 | 0.0061094 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-04-30 16:42 | 2022-04-30 17:41 | 271 | 000:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO PARA REEMPLAZO DE PIN POLE TOP Y SE CERRARON MACHETES 100% EN SERVICIO | S22043000197 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 59 | 2022-04-30 | 15989 | keep | 0 | Apr | 2022 | 0.01089 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-04-30 16:49 | 2022-05-01 12:46 | 7 | 019:57 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22043000161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1197 | 2022-04-30 | 8379 | keep | 0 | Apr | 2022 | 0.0057069 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-04-30 16:58 | 2022-04-30 18:00 | 3 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22043000080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2022-04-30 | 186 | keep | 0 | Apr | 2022 | 0.00012668 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-04-30 17:09 | 2022-05-01 04:34 | 32 | 011:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22043000169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 685 | 2022-04-30 | 21920 | keep | 0 | Apr | 2022 | 0.01493 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
FAJARDO | 2022-04-30 17:11 | 2022-04-30 17:42 | 30 | 000:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA ELIMINAR BAJANTE PRIMARIO | R22043000084 | New_Event | Wire Down | Include | Include | Equipment | 31 | 2022-04-30 | 930 | keep | 0 | Apr | 2022 | 0.00063342 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-04-30 17:17 | 2022-04-30 17:18 | 1352 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22043000096 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 1352 | keep | 0 | Apr | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-04-30 17:17 | 2022-04-30 17:18 | 871 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22043000096 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 871 | keep | 0 | Apr | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
CAGUAS | 2022-04-30 17:27 | 2022-04-30 17:40 | 49 | 000:13 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL DE LA LINEA QUEMANDO | C22043000227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 13 | 2022-04-30 | 637 | keep | 0 | Apr | 2022 | 0.00043386 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
BAYAMON | 2022-04-30 17:41 | 2022-04-30 17:58 | 1 | 000:17 | P | NO SE REPORTO CAUSA | 1SMU X 20 AMP | S22043000316 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2022-04-30 | 17 | keep | 0 | Apr | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-04-30 17:54 | 2022-04-30 17:55 | 638 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22043000240 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 638 | keep | 0 | Apr | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
PONCE | 2022-04-30 17:59 | 2022-04-30 18:55 | 110 | 000:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P22043000085 | New_Event |  |  | Include | Wildlife | 56 | 2022-04-30 | 6160 | keep | 0 | Apr | 2022 | 0.0041955 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2022-04-30 18:11 | 2022-04-30 18:12 | 476 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 476 | keep | 0 | Apr | 2022 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2022-04-30 18:11 | 2022-04-30 18:12 | 1655 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1655 | keep | 0 | Apr | 2022 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-04-30 18:11 | 2022-04-30 18:12 | 361 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 361 | keep | 0 | Apr | 2022 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2022-04-30 18:11 | 2022-04-30 18:12 | 2842 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 2842 | keep | 0 | Apr | 2022 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-04-30 18:11 | 2022-04-30 18:12 | 1702 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 1702 | keep | 0 | Apr | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-04-30 18:11 | 2022-04-30 18:12 | 918 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3000 DE CAGUAX A JUNCOS | C22043000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-04-30 | 918 | keep | 0 | Apr | 2022 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2022-04-30 18:12 | 2022-04-30 19:35 | 42 | 001:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C22043000112 | Partial_restoration |  |  | Include | Wildlife | 83 | 2022-04-30 | 3486 | keep | 0 | Apr | 2022 | 0.0023743 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-30 18:25 | 2022-04-30 20:28 | 100 | 002:03 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | P22043000088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-04-30 | 12300 | keep | 0 | Apr | 2022 | 0.0083775 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-04-30 18:45 | 2022-04-30 21:15 | 10 | 002:30 | P | PARARRAYOS DEFECTUOSO | 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE ELIMINO PARARRAYO Y DESGANCHO PALMA | C22043000243 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 150 | 2022-04-30 | 1500 | keep | 0 | Apr | 2022 | 0.0010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-04-30 18:50 | 2022-05-01 07:27 | 10 | 012:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X 65 EN C/L SE REMPLAZO AISLADOR | P22043000090 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 757 | 2022-04-30 | 7570 | keep | 0 | Apr | 2022 | 0.0051559 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-04-30 18:52 | 2022-04-30 18:53 | 1352 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22043000101 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 1352 | keep | 0 | Apr | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-04-30 18:52 | 2022-04-30 18:53 | 871 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22043000101 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-04-30 | 871 | keep | 0 | Apr | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-04-30 18:53 | 2022-05-01 01:07 | 500 | 006:14 | P | MAL TIEMPO/RAYOS/WET ASH | SE ABRIO MACHETES PARA SECCIONALIZAR Y SE REMPLAZO 3 X 200 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22043000111 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 374 | 2022-04-30 | 187000 | keep | 0 | Apr | 2022 | 0.12736 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-04-30 19:12 | 2022-04-30 19:13 | 2076 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 | B22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 2076 | keep | 0 | Apr | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-04-30 19:12 | 2022-04-30 19:13 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 | B22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 2605 | keep | 0 | Apr | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
MAYAGÃœEZ | 2022-04-30 19:12 | 2022-05-01 13:13 | 80 | 018:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 80 EN CORTE DE LINEA | M22043000108 | New_Event | Bad Weather | Include | Include | Weather | 1081 | 2022-04-30 | 86480 | keep | 0 | Apr | 2022 | 0.058901 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-04-30 19:22 | 2022-05-01 12:18 | 10 | 016:56 | P | NO SE REPORTO CAUSA | 2 X 10 EN BANCO DE XMR | C22043000249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1016 | 2022-04-30 | 10160 | keep | 0 | Apr | 2022 | 0.0069199 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-04-30 19:48 | 2022-05-01 09:10 | 25 | 013:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22043000030 | New_Event | Bad Weather | Include | Include | Weather | 802 | 2022-04-30 | 20050 | keep | 0 | Apr | 2022 | 0.013656 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-04-30 19:49 | 2022-05-01 09:43 | 15 | 013:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | P22043000102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 834 | 2022-04-30 | 12510 | keep | 0 | Apr | 2022 | 0.0085205 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-04-30 20:00 | 2022-04-30 21:15 | 97 | 001:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE LLEVO LINEA AL AISLADOR FUEGO POR NIDO DE COTORRA | P22043000105 | New_Event |  |  | Include | Wildlife | 75 | 2022-04-30 | 7275 | keep | 0 | Apr | 2022 | 0.004955 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
MAYAGÃœEZ | 2022-04-30 20:06 | 2022-05-01 11:10 | 20 | 015:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22043000115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 904 | 2022-04-30 | 18080 | keep | 0 | Apr | 2022 | 0.012314 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-04-30 20:07 | 2022-05-01 07:55 | 50 | 011:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22043000031 | New_Event | Bad Weather | Include | Include | Weather | 708 | 2022-04-30 | 35400 | keep | 0 | Apr | 2022 | 0.024111 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-04-30 20:20 | 2022-04-30 21:30 | 100 | 001:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22043000121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-04-30 | 7000 | keep | 0 | Apr | 2022 | 0.0047677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-04-30 20:41 | 2022-04-30 20:42 | 1342 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO INTERRUPTOR EN SERVICIO | C22043000263 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-04-30 | 1342 | keep | 0 | Apr | 2022 | 0.00091403 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-30 20:42 | 2022-04-30 21:10 | 20 | 000:28 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN CORTE DE LINEA Y 1 X 40 EN RISER CONDUCTOR SOTERRADO AVERIADO SE REFIERE A SOTERRADO PARA QUE LO TRABAJEN MAÃ‘ANA | C22043000231 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 28 | 2022-04-30 | 560 | keep | 0 | Apr | 2022 | 0.00038141 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-04-30 20:42 | 2022-05-02 12:39 | 35 | 039:57 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA DEL RISER @ T-5. CG-220502-01 | C22043000231 | New_Event | UG Cable Fault | Include | Include | Equipment | 2397 | 2022-04-30 | 83895 | keep | 0 | Apr | 2022 | 0.057141 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-04-30 20:54 | 2022-05-01 06:30 | 30 | 009:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C22043000264 | New_Event | Bad Weather | Include | Include | Weather | 576 | 2022-04-30 | 17280 | keep | 0 | Apr | 2022 | 0.011769 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-04-30 20:56 | 2022-05-01 09:19 | 35 | 012:23 | P | NO SE REPORTO CAUSA | 1 X 30 EN PROVISIONAL AEREO @ T-51 | R22043000124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 743 | 2022-04-30 | 26005 | keep | 0 | Apr | 2022 | 0.017712 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-04-30 21:10 | 2022-04-30 21:11 | 1725 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22043000265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1725 | keep | 0 | Apr | 2022 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
SAN JUAN | 2022-04-30 21:11 | 2022-04-30 23:24 | 500 | 002:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | EN DISPARO DEL 1206-03 QUE ESTA LLEVANDO PARTE DEL 1204-05 SE SECCIONALIZO EL 1206-03 Y SE CERRO POR SCADA SJ-220430-04. | S2204300000 | New_Event | Wire Down | Include | Include | Equipment | 133 | 2022-04-30 | 66500 | keep | 0 | Apr | 2022 | 0.045293 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-04-30 21:11 | 2022-04-30 23:24 | 3306 | 002:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO Y SE CERRO POR SCADA SJ-220430-04. PARTE DE SU CARGA POR 1620-05 Y LLEVA PARTE DEL 1204-05 | S2204300000 | New_Event | Wire Down | Include | Include | Equipment | 133 | 2022-04-30 | 439698 | keep | 0 | Apr | 2022 | 0.29948 | 0.0022517 | Sustained | FALSE | FALSE | Not_TMED_Event | 3306
HUMACAO | 2022-04-30 21:15 | 2022-05-01 11:18 | 20 | 014:03 | P | NO SE REPORTO CAUSA | 1SMU X 40 AMP | C22043000267 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 843 | 2022-04-30 | 16860 | keep | 0 | Apr | 2022 | 0.011483 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-04-30 21:18 | 2022-04-30 21:19 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22043000108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1475 | keep | 0 | Apr | 2022 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
CANOVANAS | 2022-04-30 21:21 | 2022-04-30 21:22 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 2404-06 | R22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 4085 | keep | 0 | Apr | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-04-30 21:21 | 2022-04-30 21:22 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 2402-03 CARGA ESTA TRANSFERIDA | R22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 7621 | keep | 0 | Apr | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CAGUAS | 2022-04-30 21:30 | 2022-05-01 06:47 | 40 | 009:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22043000268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 557 | 2022-04-30 | 22280 | keep | 0 | Apr | 2022 | 0.015175 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-04-30 21:31 | 2022-04-30 21:32 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22043000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-04-30 | 1830 | keep | 0 | Apr | 2022 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
BAYAMON | 2022-04-30 21:45 | 2022-04-30 22:11 | 290 | 000:26 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE INTERRUPTOR PARA REMPLAZO DE CAJA PRIMARIA EN AZOTEA SJ-220430-03 | S22043000185 | Additional_clients | Cutout Failure | Include | Include | Equipment | 26 | 2022-04-30 | 7540 | keep | 0 | Apr | 2022 | 0.0051355 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-04-30 21:52 | 2022-05-01 16:00 | 9 | 018:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22043000116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1088 | 2022-04-30 | 9792 | keep | 0 | Apr | 2022 | 0.0066693 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-04-30 21:55 | 2022-05-01 10:20 | 140 | 012:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65, 2 X 50 Y 1 X 30 EN CORTES DE LINEAS REEMPLAZARON AISLADORES ROTOS | R22043000128 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 745 | 2022-04-30 | 104300 | keep | 0 | Apr | 2022 | 0.071038 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CAGUAS | 2022-04-30 21:57 | 2022-05-01 08:09 | 8 | 010:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR AVE | C22043000273 | New_Event |  |  | Include | Wildlife | 612 | 2022-04-30 | 4896 | keep | 0 | Apr | 2022 | 0.0033346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-04-30 22:01 | 2022-05-01 11:30 | 70 | 013:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R22043000141 | New_Event | Bad Weather | Include | Include | Weather | 809 | 2022-04-30 | 56630 | keep | 0 | Apr | 2022 | 0.03857 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-04-30 22:09 | 2022-05-01 03:31 | 30 | 005:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22043000201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 322 | 2022-04-30 | 9660 | keep | 0 | Apr | 2022 | 0.0065794 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-04-30 22:14 | 2022-04-30 22:15 | 1 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN RISER NIDO DE AVE EN RISER CRUZO LINEAS | M22043000112 | New_Event |  |  | Include | Wildlife | 1 | 2022-04-30 | 1 | keep | 0 | Apr | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-04-30 22:16 | 2022-05-01 13:35 | 85 | 015:19 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 2 X 100 EN CORTE DE LINEA Y 1 X 65 EN CORTE DE LINEA REPARO TERMINACION AVERIADA EN PROVISONAL AEREO @ T-14JC | R22043000145 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 919 | 2022-04-30 | 78115 | keep | 0 | Apr | 2022 | 0.053204 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
PONCE | 2022-04-30 22:17 | 2022-05-01 09:00 | 20 | 010:43 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P22043000118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 643 | 2022-04-30 | 12860 | keep | 0 | Apr | 2022 | 0.0087589 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-04-30 23:17 | 2022-05-01 08:53 | 30 | 009:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22043000285 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 576 | 2022-04-30 | 17280 | keep | 0 | Apr | 2022 | 0.011769 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-04-30 23:24 | 2022-05-01 02:09 | 500 | 002:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO ALAMBRE Y SE NORMALIZO LAS CARGAS SJ-220430-04. | S2204300000 | Partial_restoration | Wire Down | Include | Include | Equipment | 165 | 2022-04-30 | 82500 | keep | 0 | Apr | 2022 | 0.05619 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-04-30 23:29 | 2022-05-01 08:55 | 15 | 009:26 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L Y REEMPLAZO DE PARARRAYO QUEMADO | C22043000287 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 566 | 2022-04-30 | 8490 | keep | 0 | Apr | 2022 | 0.0057825 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-01 00:03 | 2022-05-01 01:46 | 1225 | 001:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTOR VIVO EN EL SUELO SJ-220430-04. 1203-01 LLEVA 1203-03 Y 1602-02 | S22050100000 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-05-01 | 126175 | keep | 0 | May | 2022 | 0.085937 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-05-01 00:03 | 2022-05-01 01:46 | 616 | 001:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTOR VIVO EN EL SUELO SJ-220430-04. 1203-01 LLEVA 1203-03 Y 1602-02 | S22050100000 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-05-01 | 63448 | keep | 0 | May | 2022 | 0.043214 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-05-01 00:03 | 2022-05-01 01:46 | 27 | 001:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTOR VIVO EN EL SUELO SJ-220430-04. 1203-01 LLEVA 1602-02 | S22050100000 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-05-01 | 2781 | keep | 0 | May | 2022 | 0.0018941 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-05-01 00:56 | 2022-05-01 00:58 | 748 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | SE ABRE LINEA 8200 PARA ENERGIZAR AMELIA | B22043000284 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-05-01 | 1496 | keep | 0 | May | 2022 | 0.0010189 | 0.00050946 | Momentary | FALSE | FALSE | Not_TMED_Event | 748
BAYAMON | 2022-05-01 00:56 | 2022-05-01 00:58 | 33 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | SE ABRE LINEA 8200 PARA ENERGIZAR AMELIA | B22043000284 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-05-01 | 66 | keep | 0 | May | 2022 | 4.4952e-05 | 2.2476e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2022-05-01 01:07 | 2022-05-01 15:20 | 200 | 014:13 | P | MAL TIEMPO/RAYOS/WET ASH | SE VERIFICO Y SE CERRO MACHETES MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050100001 | Partial_restoration | Bad Weather | Include | Include | Weather | 853 | 2022-05-01 | 170600 | keep | 0 | May | 2022 | 0.11619 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-01 01:09 | 2022-05-01 01:10 | 1380 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 1380 | keep | 0 | May | 2022 | 0.00093991 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
CAGUAS | 2022-05-01 01:28 | 2022-05-01 16:59 | 17 | 015:31 | P | CABLE SOTERRADO AVERIADO | SE REEMPLAZO CABLE SOTERRADO T-2 @ T-1 | C22040100001 | New_Event | UG Cable Fault | Include | Include | Equipment | 931 | 2022-05-01 | 15827 | keep | 0 | May | 2022 | 0.01078 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2022-05-01 02:25 | 2022-05-01 08:15 | 220 | 005:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 80 EN CORTES DE LINEAS MAL TIEMPO | R22050100005 | New_Event | Bad Weather | Include | Include | Weather | 350 | 2022-05-01 | 77000 | keep | 0 | May | 2022 | 0.052444 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
MAYAGÃœEZ | 2022-05-01 02:37 | 2022-05-01 02:38 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22050100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 863 | keep | 0 | May | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-01 02:39 | 2022-05-01 03:38 | 51 | 000:59 | T | ESTRUCTURA AVERIADA | DISPARO DEL INTERRUPTOR LLEVA LA CARGA DEL 6001-05 EN EL CUAL HAY POSTES PRIMARIOS PARTIDOS SE ABRIO EL AMARRE CON EL 6001-05 | M22050100002 | New_Event | Defective Pole | Include | Include | Equipment | 59 | 2022-05-01 | 3009 | keep | 0 | May | 2022 | 0.0020494 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-05-01 02:39 | 2022-05-01 22:40 | 285 | 020:01 | T | ESTRUCTURA AVERIADA | SE REMPLAZO POSTES PRIMARIOS PARTIDOS | M22050100014 | New_Event | Defective Pole | Include | Include | Equipment | 1201 | 2022-05-01 | 342285 | keep | 0 | May | 2022 | 0.23313 | 0.00019411 | Sustained | FALSE | FALSE | Not_TMED_Event | 285
MAYAGÃœEZ | 2022-05-01 02:40 | 2022-05-01 03:21 | 1444 | 000:41 | T | ANIMAL U OBJETO EXTRAÃ‘O | POSTES PRIMARIOS PARTIDOS EN EL 6014-02 EL CUAL LLEVA LA CARGA DEL 6014-01 POR IMPACTO DE VEHCULO | M22050100014 | New_Event |  |  | Include | Wildlife | 41 | 2022-05-01 | 59204 | keep | 0 | May | 2022 | 0.040324 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-05-01 02:40 | 2022-05-01 03:21 | 3630 | 000:41 | T | ANIMAL U OBJETO EXTRAÃ‘O | POSTES PRIMARIOS PARTIDOS LLEVA LA CARGA DEL 6014-01, SE SECCIONALIZO AVERIA Y SE CERRO EL INTERRUPTOR | M22050100014 | New_Event |  |  | Include | Wildlife | 41 | 2022-05-01 | 148830 | keep | 0 | May | 2022 | 0.10137 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-05-01 03:21 | 2022-05-01 22:34 | 3630 | 019:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTES PRIMARIOS PARTIDOS SE CERRO MACHETES | M22050100012 | Partial_restoration |  |  | Include | Wildlife | 1153 | 2022-05-01 | 4185390 | keep | 0 | May | 2022 | 2.8507 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-01 03:35 | 2022-05-01 08:56 | 1681 | 005:21 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-01 QUE A SU VEZ LLEVA LA CARGA DEL 1346-06. SE ABRIO EN CAMINO LUIS VIGOREAUX Y SE CERRO INTERRUPTOR | S22050100050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-05-01 | 539601 | keep | 0 | May | 2022 | 0.36752 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-01 03:35 | 2022-05-01 08:56 | 1598 | 005:21 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-01 QUE A SU VEZ LLEVA LA CRAG DEL 1346-06. SE ABRIO EN CAMINO LUIS VIGOREAUX Y SE CERRO INTERRUPTOR | S22050100050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-05-01 | 512958 | keep | 0 | May | 2022 | 0.34937 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
GUAYAMA | 2022-05-01 03:43 | 2022-05-01 03:44 | 1173 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 1173 | keep | 0 | May | 2022 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
MAYAGÃœEZ | 2022-05-01 04:20 | 2022-05-01 05:54 | 30 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050100016 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2022-05-01 | 2820 | keep | 0 | May | 2022 | 0.0019207 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-05-01 04:21 | 2022-05-01 09:35 | 90 | 005:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22050100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2022-05-01 | 28260 | keep | 0 | May | 2022 | 0.019248 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-05-01 05:02 | 2022-05-01 05:03 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 1 | keep | 0 | May | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-01 05:28 | 2022-05-01 05:29 | 2770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 2770 | keep | 0 | May | 2022 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
SAN JUAN | 2022-05-01 05:43 | 2022-05-01 17:25 | 117 | 011:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | S22050100033 | New_Event | Cutout Failure | Include | Include | Equipment | 702 | 2022-05-01 | 82134 | keep | 0 | May | 2022 | 0.055941 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
BAYAMON | 2022-05-01 06:03 | 2022-05-01 12:56 | 19 | 006:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE Y 1 X 65 EN C/L | S22050100035 | New_Event | Wire Down | Include | Include | Equipment | 413 | 2022-05-01 | 7847 | keep | 0 | May | 2022 | 0.0053446 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2022-05-01 06:12 | 2022-05-01 12:55 | 35 | 006:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R22050100012 | New_Event | Bad Weather | Include | Include | Weather | 403 | 2022-05-01 | 14105 | keep | 0 | May | 2022 | 0.0096069 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2022-05-01 06:26 | 2022-05-01 08:45 | 120 | 002:19 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22050100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-05-01 | 16680 | keep | 0 | May | 2022 | 0.011361 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-05-01 06:30 | 2022-05-01 06:32 | 598 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-01 | 1196 | keep | 0 | May | 2022 | 0.00081459 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
CAGUAS | 2022-05-01 06:30 | 2022-05-01 06:32 | 2486 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-01 | 4972 | keep | 0 | May | 2022 | 0.0033864 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
CAGUAS | 2022-05-01 06:30 | 2022-05-01 06:32 | 1403 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-01 | 2806 | keep | 0 | May | 2022 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
CAGUAS | 2022-05-01 06:30 | 2022-05-01 06:32 | 1001 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-01 | 2002 | keep | 0 | May | 2022 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
CAGUAS | 2022-05-01 06:32 | 2022-05-01 10:40 | 30 | 004:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C22043000264 | Partial_restoration | Bad Weather | Include | Include | Weather | 248 | 2022-05-01 | 7440 | keep | 0 | May | 2022 | 0.0050674 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-05-01 06:44 | 2022-05-01 08:49 | 60 | 002:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | P22050100011 | New_Event | Bad Weather | Include | Include | Weather | 125 | 2022-05-01 | 7500 | keep | 0 | May | 2022 | 0.0051082 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-01 06:55 | 2022-05-01 06:56 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 1565 | keep | 0 | May | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-05-01 06:55 | 2022-05-01 06:56 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 976 | keep | 0 | May | 2022 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-05-01 06:55 | 2022-05-01 06:56 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 548 | keep | 0 | May | 2022 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-05-01 06:55 | 2022-05-01 06:56 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 315 | keep | 0 | May | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-05-01 06:55 | 2022-05-01 06:56 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-05-01 06:55 | 2022-05-01 06:56 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 2906 | keep | 0 | May | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-05-01 06:55 | 2022-05-01 06:56 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 2343 | keep | 0 | May | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
HUMACAO | 2022-05-01 06:56 | 2022-05-01 12:20 | 40 | 005:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22050100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 324 | 2022-05-01 | 12960 | keep | 0 | May | 2022 | 0.008827 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-01 06:59 | 2022-05-01 07:00 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 95% DE LA CARGA DEL 1717-02 | B22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 5961 | keep | 0 | May | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-05-01 06:59 | 2022-05-01 07:00 | 865 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 95% DE LA CARGA POR EL 1713-05 | B22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 865 | keep | 0 | May | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
PONCE | 2022-05-01 07:22 | 2022-05-01 07:23 | 948 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1800 | P220501000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 948 | keep | 0 | May | 2022 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
PONCE | 2022-05-01 07:22 | 2022-05-01 07:23 | 7 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1800 | P220501000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 7 | keep | 0 | May | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-05-01 07:22 | 2022-05-01 07:23 | 114 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1800 | P220501000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 114 | keep | 0 | May | 2022 | 7.7645e-05 | 7.7645e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 114
YAUCO | 2022-05-01 07:22 | 2022-05-01 13:57 | 40 | 006:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L SE FIJO ALABRE SAFADO SOBRE CRUZETA | P22050100015 | New_Event | Wire Down | Include | Include | Equipment | 395 | 2022-05-01 | 15800 | keep | 0 | May | 2022 | 0.010761 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-01 07:24 | 2022-05-01 11:02 | 150 | 003:38 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050100025 | New_Event | Bad Weather | Include | Include | Weather | 218 | 2022-05-01 | 32700 | keep | 0 | May | 2022 | 0.022272 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-05-01 07:28 | 2022-05-01 18:12 | 18 | 010:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L SE REMPLAZO CAJA AISLADOR Y SE SUBIO LINEA | R22050100018 | New_Event | Cutout Failure | Include | Include | Equipment | 644 | 2022-05-01 | 11592 | keep | 0 | May | 2022 | 0.0078953 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-05-01 07:32 | 2022-05-01 13:58 | 85 | 006:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 50 C/L AVE | S22050100057 | New_Event |  |  | Include | Wildlife | 386 | 2022-05-01 | 32810 | keep | 0 | May | 2022 | 0.022347 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2022-05-01 07:34 | 2022-05-01 07:35 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22050100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-05-01 07:35 | 2022-05-01 14:15 | 30 | 006:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22050100022 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 400 | 2022-05-01 | 12000 | keep | 0 | May | 2022 | 0.0081731 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-05-01 07:39 | 2022-05-01 12:53 | 7 | 005:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22050100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 314 | 2022-05-01 | 2198 | keep | 0 | May | 2022 | 0.001497 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-05-01 07:56 | 2022-05-01 13:27 | 1 | 005:31 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | C22050100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-05-01 | 331 | keep | 0 | May | 2022 | 0.00022544 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-05-01 08:06 | 2022-05-01 11:18 | 60 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R22050100029 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2022-05-01 | 11520 | keep | 0 | May | 2022 | 0.0078462 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-05-01 08:12 | 2022-05-01 08:13 | 562 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22050100023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 562 | keep | 0 | May | 2022 | 0.00038278 | 0.00038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 562
PONCE | 2022-05-01 08:12 | 2022-05-01 08:13 | 688 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22050100023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 688 | keep | 0 | May | 2022 | 0.00046859 | 0.00046859 | Momentary | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2022-05-01 08:12 | 2022-05-01 08:13 | 658 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22050100023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 658 | keep | 0 | May | 2022 | 0.00044816 | 0.00044816 | Momentary | FALSE | FALSE | Not_TMED_Event | 658
PONCE | 2022-05-01 08:12 | 2022-05-01 08:13 | 4009 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22050100026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 4009 | keep | 0 | May | 2022 | 0.0027305 | 0.0027305 | Momentary | FALSE | FALSE | Not_TMED_Event | 4009
BAYAMON | 2022-05-01 08:18 | 2022-05-01 08:19 | 320 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 320 | keep | 0 | May | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
CANOVANAS | 2022-05-01 08:19 | 2022-05-01 08:50 | 40 | 000:31 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R22050100033 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 31 | 2022-05-01 | 1240 | keep | 0 | May | 2022 | 0.00084456 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-01 08:19 | 2022-05-01 11:35 | 50 | 003:16 | P | NO SE REPORTO CAUSA | 2 X 40 EN C/L | B22050100012 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 196 | 2022-05-01 | 9800 | keep | 0 | May | 2022 | 0.0066747 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-05-01 08:22 | 2022-05-01 10:20 | 40 | 001:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22050100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-05-01 | 4720 | keep | 0 | May | 2022 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-05-01 08:32 | 2022-05-01 10:50 | 40 | 002:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE CAMBIO AISLADOR Y CAJA PRIMARIIA | C22050100020 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 138 | 2022-05-01 | 5520 | keep | 0 | May | 2022 | 0.0037596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-05-01 08:36 | 2022-05-01 10:35 | 400 | 001:59 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTES HACIA RESIDENCIAL DR PILA POSTE PRIMARIO PARTIDO | P22050100033 | New_Event | Defective Pole | Include | Include | Equipment | 119 | 2022-05-01 | 47600 | keep | 0 | May | 2022 | 0.03242 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CAGUAS | 2022-05-01 08:40 | 2022-05-01 19:19 | 203 | 010:39 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPLAZO SU-3 Y SU-4 | C22053000010 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 639 | 2022-05-01 | 129717 | keep | 0 | May | 2022 | 0.08835 | 0.00013826 | Sustained | FALSE | FALSE | Not_TMED_Event | 203
CAGUAS | 2022-05-01 08:42 | 2022-05-01 10:58 | 1 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN BANCO DE XMR CRUCE POR AVE | C22050100023 | New_Event |  |  | Include | Wildlife | 136 | 2022-05-01 | 136 | keep | 0 | May | 2022 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-05-01 08:53 | 2022-05-01 09:21 | 50 | 000:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR AVE | C22050100024 | New_Event |  |  | Include | Wildlife | 28 | 2022-05-01 | 1400 | keep | 0 | May | 2022 | 0.00095353 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-01 08:56 | 2022-05-01 09:25 | 80 | 000:29 | P | DESGANCHE | SE ABRIO MACHETES EN CAMINO LUIS VIGOREAUX Y SE REALIZO DESGANCHE | S2205010000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 29 | 2022-05-01 | 2320 | keep | 0 | May | 2022 | 0.0015801 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-01 08:58 | 2022-05-01 14:50 | 35 | 005:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR Y 1 X 50 EN C/L AVE | S22050100091 | New_Event |  |  | Include | Wildlife | 352 | 2022-05-01 | 12320 | keep | 0 | May | 2022 | 0.0083911 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-05-01 09:01 | 2022-05-01 14:59 | 60 | 005:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y 1 X 80 EN C/L SE QUEDO FUERA 4 XMR (25 CLIENTES FUERA) POR CAJA PRIMARIA QUEMADA EL FOREMAN INDICA QUE ESTA SOLO QUE TRABAJARA LA CONDICION MAS TARDE CUANDO CONSIGA PERSONAL | C22050100025 | New_Event | Cutout Failure | Include | Include | Equipment | 358 | 2022-05-01 | 21480 | keep | 0 | May | 2022 | 0.01463 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-05-01 09:02 | 2022-05-01 15:50 | 23 | 006:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22050100036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2022-05-01 | 9384 | keep | 0 | May | 2022 | 0.0063914 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2022-05-01 09:18 | 2022-05-01 09:19 | 1483 | 000:01 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ LLEVA LA CARGA TOTAL DEL 1336-09 Y UN 30% DEL 1204-04 | S22050100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-01 | 1483 | keep | 0 | May | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-01 09:18 | 2022-05-01 09:19 | 5290 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ LLEVA LA CARGA TOTAL DEL 1336-09 Y UN 30% DEL 1204-04 | S22050100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-01 | 5290 | keep | 0 | May | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-05-01 09:18 | 2022-05-01 09:19 | 207 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ LLEVA LA CARGA TOTAL DEL 1336-09 Y UN 30% DEL 1204-04 | S22050100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-01 | 207 | keep | 0 | May | 2022 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
AGUADILLA | 2022-05-01 09:18 | 2022-05-01 09:19 | 1827 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | M22050100000 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-01 | 1827 | keep | 0 | May | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2022-05-01 09:19 | 2022-05-01 15:39 | 122 | 006:20 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN C/L SE REALIZO DESGANCHE | S22050100146 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 380 | 2022-05-01 | 46360 | keep | 0 | May | 2022 | 0.031576 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
SAN JUAN | 2022-05-01 09:19 | 2022-05-01 12:23 | 50 | 003:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22050100100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2022-05-01 | 9200 | keep | 0 | May | 2022 | 0.0062661 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-05-01 09:19 | 2022-05-01 14:36 | 80 | 005:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22050100063 | 1st_after_momentary |  |  | Include | Wildlife | 317 | 2022-05-01 | 25360 | keep | 0 | May | 2022 | 0.017273 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-01 09:24 | 2022-05-01 09:25 | 1210 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 1210 | keep | 0 | May | 2022 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
SAN JUAN | 2022-05-01 09:27 | 2022-05-01 13:22 | 1 | 003:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR Y SE RETIRO LAGARTIJO DE CONTADOR | S22050100102 | New_Event |  |  | Include | Wildlife | 235 | 2022-05-01 | 235 | keep | 0 | May | 2022 | 0.00016006 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-01 09:31 | 2022-05-01 10:47 | 1 | 001:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050100064 | New_Event | Bad Weather | Include | Include | Weather | 76 | 2022-05-01 | 76 | keep | 0 | May | 2022 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-05-01 09:34 | 2022-05-01 09:35 | 4882 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22050100000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-01 | 4882 | keep | 0 | May | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
PONCE | 2022-05-01 09:35 | 2022-05-01 09:36 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050100042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 3744 | keep | 0 | May | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
AGUADILLA | 2022-05-01 09:35 | 2022-05-01 13:31 | 50 | 003:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR LLUVIA | M22050100075 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 236 | 2022-05-01 | 11800 | keep | 0 | May | 2022 | 0.0080369 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-01 09:39 | 2022-05-01 14:32 | 79 | 004:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE DESCRUZARON LINEAS Y SE DESGANCHO | S22050100107 | New_Event | Wire Down | Include | Include | Equipment | 293 | 2022-05-01 | 23147 | keep | 0 | May | 2022 | 0.015765 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
CAGUAS | 2022-05-01 09:44 | 2022-05-01 11:10 | 2178 | 001:26 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO | C22050100000 | New_Event |  |  | Include | Wildlife | 86 | 2022-05-01 | 187308 | keep | 0 | May | 2022 | 0.12757 | 0.0014834 | Sustained | FALSE | FALSE | Not_TMED_Event | 2178
HUMACAO | 2022-05-01 09:49 | 2022-05-01 15:29 | 13 | 005:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22050100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 340 | 2022-05-01 | 4420 | keep | 0 | May | 2022 | 0.0030104 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
GUAYAMA | 2022-05-01 09:54 | 2022-05-01 11:07 | 50 | 001:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L AVE CRUZO LINEAS | P22050100051 | New_Event |  |  | Include | Wildlife | 73 | 2022-05-01 | 3650 | keep | 0 | May | 2022 | 0.002486 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-01 10:00 | 2022-05-01 11:45 | 8 | 001:45 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C22043000077 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 105 | 2022-05-01 | 840 | keep | 0 | May | 2022 | 0.00057212 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-05-01 10:01 | 2022-05-01 15:03 | 150 | 005:02 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | R22050100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2022-05-01 | 45300 | keep | 0 | May | 2022 | 0.030854 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-05-01 10:05 | 2022-05-01 12:37 | 100 | 002:32 | P | DESGANCHE | 2 X 40 Y 2 X 50 EN DIFERENTES C/LS DESGANCHE | P22050100028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-05-01 | 15200 | keep | 0 | May | 2022 | 0.010353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-01 10:08 | 2022-05-01 13:20 | 10 | 003:12 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22050100116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2022-05-01 | 1920 | keep | 0 | May | 2022 | 0.0013077 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-05-01 10:08 | 2022-05-01 19:08 | 10 | 009:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO AVERIA DE ALAMBRE EN EL PISO CONTINUA TRABAJANDO EN EL CASO CON EVENTO P220503000108 | P22050100055 | New_Event | Wire Down | Include | Include | Equipment | 540 | 2022-05-01 | 5400 | keep | 0 | May | 2022 | 0.0036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-01 10:16 | 2022-05-01 16:55 | 50 | 006:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M22050100081 | New_Event |  |  | Include | Wildlife | 399 | 2022-05-01 | 19950 | keep | 0 | May | 2022 | 0.013588 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-01 10:31 | 2022-05-01 14:40 | 20 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 25 RBA EN SU | S22050100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2022-05-01 | 4980 | keep | 0 | May | 2022 | 0.0033919 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-05-01 10:35 | 2022-05-01 17:15 | 66 | 006:40 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTE PRIMARIO | P22050100072 | New_Event | Defective Pole | Include | Include | Equipment | 400 | 2022-05-01 | 26400 | keep | 0 | May | 2022 | 0.017981 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2022-05-01 10:52 | 2022-05-01 15:04 | 7 | 004:12 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S22050100126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2022-05-01 | 1764 | keep | 0 | May | 2022 | 0.0012015 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-05-01 10:53 | 2022-05-01 11:40 | 1 | 000:47 | P | DESGANCHE | 1 X 40 C/L SE DESGANCHO | B22050100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-05-01 | 47 | keep | 0 | May | 2022 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-01 10:55 | 2022-05-01 15:25 | 50 | 004:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050100009 | New_Event | Bad Weather | Include | Include | Weather | 270 | 2022-05-01 | 13500 | keep | 0 | May | 2022 | 0.0091948 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-01 10:58 | 2022-05-01 16:20 | 40 | 005:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | C22050100065 | New_Event | Bad Weather | Include | Include | Weather | 322 | 2022-05-01 | 12880 | keep | 0 | May | 2022 | 0.0087725 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-01 11:10 | 2022-05-01 12:04 | 1306 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REALIZARON OPERACIONES 60% EN SERVICIO | C22050100000 | New_Event |  |  | Include | Wildlife | 54 | 2022-05-01 | 70524 | keep | 0 | May | 2022 | 0.048034 | 0.00088951 | Sustained | FALSE | FALSE | Not_TMED_Event | 1306
SAN JUAN | 2022-05-01 11:14 | 2022-05-01 11:53 | 4 | 000:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE RETIRO PENCA DE PALMA | S22050100112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2022-05-01 | 156 | keep | 0 | May | 2022 | 0.00010625 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-05-01 11:15 | 2022-05-01 20:07 | 2 | 008:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22050100094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 532 | 2022-05-01 | 1064 | keep | 0 | May | 2022 | 0.00072469 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-05-01 11:22 | 2022-05-01 11:23 | 3012 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF PERMANENTE | R22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 3012 | keep | 0 | May | 2022 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2022-05-01 11:23 | 2022-05-01 14:30 | 150 | 003:07 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | R22050100073 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 187 | 2022-05-01 | 28050 | keep | 0 | May | 2022 | 0.019105 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-05-01 11:29 | 2022-05-01 11:30 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF PERMANENTE | R22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 2106 | keep | 0 | May | 2022 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2022-05-01 11:43 | 2022-05-01 16:36 | 4 | 004:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22050100074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 293 | 2022-05-01 | 1172 | keep | 0 | May | 2022 | 0.00079824 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-01 11:48 | 2022-05-01 11:49 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050100076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 3046 | keep | 0 | May | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-05-01 11:54 | 2022-05-01 11:55 | 5 | 000:01 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR Y SE REALIZO DESGANCHE PRIMARIO | S22050100121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-01 | 5 | keep | 0 | May | 2022 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-05-01 12:03 | 2022-05-01 18:39 | 2 | 006:36 | P | DESGANCHE | 1 X 80 C/L 2 X 25 EN RISER DE PIZZA HUT | S22050100139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 396 | 2022-05-01 | 792 | keep | 0 | May | 2022 | 0.00053943 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-05-01 12:03 | 2022-05-01 17:16 | 6 | 005:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22050100080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2022-05-01 | 1878 | keep | 0 | May | 2022 | 0.0012791 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-05-01 12:04 | 2022-05-01 12:45 | 870 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REALIZO DESGANCHE, SE RETIRO GATO MUERTO EN SU-2 Y SE NORMALIZO 100% EN SERVICIO | C22050100000 | Partial_restoration |  |  | Include | Wildlife | 41 | 2022-05-01 | 35670 | keep | 0 | May | 2022 | 0.024295 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-01 12:15 | 2022-05-01 16:16 | 1 | 004:01 | P | NO SE REPORTO CAUSA | 2 X 20 EN XMR 1 X 25 EN RISER | C22050100081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2022-05-01 | 241 | keep | 0 | May | 2022 | 0.00016414 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-05-01 12:18 | 2022-05-01 12:19 | 676 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR QUEDO EN SERVICIO | S22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 676 | keep | 0 | May | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
FAJARDO | 2022-05-01 12:19 | 2022-05-01 19:07 | 100 | 006:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22050100078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 408 | 2022-05-01 | 40800 | keep | 0 | May | 2022 | 0.027789 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-05-01 12:19 | 2022-05-01 14:36 | 10 | 002:17 | P | NO SE REPORTO CAUSA | 2 X 10 EN BANCO DE XMR | C22043000249 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-05-01 | 1370 | keep | 0 | May | 2022 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-01 12:22 | 2022-05-01 14:40 | 25 | 002:18 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22050100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-05-01 | 3450 | keep | 0 | May | 2022 | 0.0023498 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-05-01 12:50 | 2022-05-01 17:35 | 10 | 004:45 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | R22050100081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2022-05-01 | 2850 | keep | 0 | May | 2022 | 0.0019411 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-05-01 13:00 | 2022-05-01 15:44 | 8 | 002:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO | R22050100083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 164 | 2022-05-01 | 1312 | keep | 0 | May | 2022 | 0.0008936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-01 13:03 | 2022-05-01 18:17 | 80 | 005:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M22050100117 | New_Event | Cutout Failure | Include | Include | Equipment | 314 | 2022-05-01 | 25120 | keep | 0 | May | 2022 | 0.017109 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-01 13:11 | 2022-05-01 16:00 | 30 | 002:49 | P | DESGANCHE | 1 X 30 Y DESGANCHE | B22050100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-05-01 | 5070 | keep | 0 | May | 2022 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-01 13:28 | 2022-05-01 15:10 | 20 | 001:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22050100128 | New_Event | Bad Weather | Include | Include | Weather | 102 | 2022-05-01 | 2040 | keep | 0 | May | 2022 | 0.0013894 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-01 13:30 | 2022-05-01 17:30 | 10 | 004:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EM PM T-4 Y CERRO PUENTE DE LINEA A CAJA | S22050100153 | New_Event | Wire Down | Include | Include | Equipment | 240 | 2022-05-01 | 2400 | keep | 0 | May | 2022 | 0.0016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-05-01 13:42 | 2022-05-01 14:43 | 159 | 001:01 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO | R22050100089 | New_Event | Switch Failure | Include | Include | Equipment | 61 | 2022-05-01 | 9699 | keep | 0 | May | 2022 | 0.0066059 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
HUMACAO | 2022-05-01 13:47 | 2022-05-01 17:47 | 30 | 004:00 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | C22050100093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-05-01 | 7200 | keep | 0 | May | 2022 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-01 14:07 | 2022-05-01 15:35 | 60 | 001:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN C/L MAL TIEMPO | C22050100094 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2022-05-01 | 5280 | keep | 0 | May | 2022 | 0.0035962 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-01 14:11 | 2022-05-01 14:12 | 1227 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A22050100012 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-01 | 1227 | keep | 0 | May | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-05-01 14:11 | 2022-05-01 14:12 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22050100013 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-01 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2022-05-01 14:15 | 2022-05-01 14:16 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22005010000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
MAYAGÃœEZ | 2022-05-01 14:15 | 2022-05-01 15:30 | 21 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M22050100136 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2022-05-01 | 1575 | keep | 0 | May | 2022 | 0.0010727 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CAGUAS | 2022-05-01 14:16 | 2022-05-01 15:34 | 30 | 001:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22050100022 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-05-01 | 2340 | keep | 0 | May | 2022 | 0.0015938 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-05-01 14:23 | 2022-05-01 18:25 | 30 | 004:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN C/L MAL TIEMPO | R22050100093 | New_Event | Bad Weather | Include | Include | Weather | 242 | 2022-05-01 | 7260 | keep | 0 | May | 2022 | 0.0049448 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-01 14:23 | 2022-05-01 17:18 | 100 | 002:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050100014 | New_Event | Bad Weather | Include | Include | Weather | 175 | 2022-05-01 | 17500 | keep | 0 | May | 2022 | 0.011919 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-01 14:33 | 2022-05-01 14:34 | 1227 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A22050100018 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-05-01 | 1227 | keep | 0 | May | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-05-01 14:33 | 2022-05-01 14:34 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22050100019 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-01 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-05-01 14:36 | 2022-05-01 14:37 | 1227 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A22050100020 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-05-01 | 1227 | keep | 0 | May | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-05-01 14:36 | 2022-05-01 14:37 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22050100021 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-01 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-05-01 14:38 | 2022-05-01 14:39 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22050100022 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-01 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
MAYAGÃœEZ | 2022-05-01 14:40 | 2022-05-01 19:20 | 20 | 004:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22050100142 | New_Event | Bad Weather | Include | Include | Weather | 280 | 2022-05-01 | 5600 | keep | 0 | May | 2022 | 0.0038141 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-01 14:43 | 2022-05-01 17:45 | 40 | 003:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETIRO GROUND DE POSTE QUE ESTABA SUELTO CRUZANDO CON EL CONDUCTOR | A22050100025 | New_Event | Wire Down | Include | Include | Equipment | 182 | 2022-05-01 | 7280 | keep | 0 | May | 2022 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-01 14:45 | 2022-05-01 14:46 | 1345 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A22050100028 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-01 | 1345 | keep | 0 | May | 2022 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2022-05-01 14:46 | 2022-05-01 14:47 | 1916 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22050100030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 1916 | keep | 0 | May | 2022 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2022-05-01 14:53 | 2022-05-01 16:10 | 300 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050100024 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2022-05-01 | 23100 | keep | 0 | May | 2022 | 0.015733 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2022-05-01 14:55 | 2022-05-01 14:56 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22050100035 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-01 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2022-05-01 14:56 | 2022-05-01 16:38 | 10 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR AVE | C22050100103 | New_Event |  |  | Include | Wildlife | 102 | 2022-05-01 | 1020 | keep | 0 | May | 2022 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-01 14:56 | 2022-05-01 15:59 | 5042 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-05-01 | 317646 | keep | 0 | May | 2022 | 0.21635 | 0.0034341 | Sustained | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2022-05-01 14:56 | 2022-05-01 15:59 | 2720 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-05-01 | 171360 | keep | 0 | May | 2022 | 0.11671 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2022-05-01 14:56 | 2022-05-01 15:59 | 1883 | 001:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-05-01 | 118629 | keep | 0 | May | 2022 | 0.080798 | 0.0012825 | Sustained | FALSE | FALSE | Not_TMED_Event | 1883
ARECIBO | 2022-05-01 14:56 | 2022-05-01 14:57 | 1227 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A22050100037 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-05-01 | 1227 | keep | 0 | May | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-05-01 14:57 | 2022-05-01 21:00 | 12 | 006:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A22050100210 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 363 | 2022-05-01 | 4356 | keep | 0 | May | 2022 | 0.0029669 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-01 14:58 | 2022-05-01 14:59 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22050100039 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-01 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2022-05-01 14:59 | 2022-05-02 13:05 | 25 | 022:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA QUEMADA | C22050100025 | New_Event | Cutout Failure | Include | Include | Equipment | 1326 | 2022-05-01 | 33150 | keep | 0 | May | 2022 | 0.022578 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-05-01 14:59 | 2022-05-01 15:00 | 2694 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A22050100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-01 | 2694 | keep | 0 | May | 2022 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2022-05-01 14:59 | 2022-05-01 22:33 | 200 | 007:34 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050100031 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 454 | 2022-05-01 | 90800 | keep | 0 | May | 2022 | 0.061843 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-01 15:11 | 2022-05-01 19:15 | 61 | 004:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L AVE | B22050100028 | New_Event |  |  | Include | Wildlife | 244 | 2022-05-01 | 14884 | keep | 0 | May | 2022 | 0.010137 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2022-05-01 15:11 | 2022-05-01 16:30 | 20 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22050100099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-05-01 | 1580 | keep | 0 | May | 2022 | 0.0010761 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-01 15:11 | 2022-05-01 17:07 | 40 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22050100120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-05-01 | 4640 | keep | 0 | May | 2022 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-01 15:13 | 2022-05-01 15:14 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22050100079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 2201 | keep | 0 | May | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
BAYAMON | 2022-05-01 15:19 | 2022-05-01 20:17 | 35 | 004:58 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22050100160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2022-05-01 | 10430 | keep | 0 | May | 2022 | 0.0071038 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-05-01 15:21 | 2022-05-01 16:22 | 1345 | 001:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL INTERRUPTOR POR SEGURIDAD POR LINEA PRIMARIA ROTA Y VIVA EN EL PISO INFORMADO POR EL ING LUIS FENEQUE SE SECCIONALIZO Y SE CERRO EL INTERRUPTOR | A22050100093 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 61 | 2022-05-01 | 82045 | keep | 0 | May | 2022 | 0.05588 | 0.00091607 | Sustained | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2022-05-01 15:22 | 2022-05-01 15:23 | 316 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22050100097 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-01 | 316 | keep | 0 | May | 2022 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2022-05-01 15:26 | 2022-05-01 16:58 | 2694 | 001:32 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA Y SE CERRO EL INTERRUPTOR | A22050100104 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 92 | 2022-05-01 | 247848 | keep | 0 | May | 2022 | 0.16881 | 0.0018349 | Sustained | FALSE | FALSE | Not_TMED_Event | 2694
AGUADILLA | 2022-05-01 15:27 | 2022-05-01 15:28 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22050100162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 3041 | keep | 0 | May | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
MAYAGÃœEZ | 2022-05-01 15:34 | 2022-05-01 15:35 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22050100163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 1192 | keep | 0 | May | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
VEGA BAJA | 2022-05-01 15:37 | 2022-05-01 19:24 | 20 | 003:47 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22050100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-05-01 | 4540 | keep | 0 | May | 2022 | 0.0030922 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-01 16:00 | 2022-05-01 18:03 | 10 | 002:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C22050100131 | New_Event | Bad Weather | Include | Include | Weather | 123 | 2022-05-01 | 1230 | keep | 0 | May | 2022 | 0.00083775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-01 16:13 | 2022-05-01 16:14 | 320 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 320 | keep | 0 | May | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
CANOVANAS | 2022-05-01 16:17 | 2022-05-01 17:21 | 52 | 001:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR | R22050100106 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 64 | 2022-05-01 | 3328 | keep | 0 | May | 2022 | 0.0022667 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2022-05-01 16:19 | 2022-05-01 16:21 | 1825 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1118-09 Y SE CERRO POR SCADA LLEVA 1118-08 | S22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-01 | 3650 | keep | 0 | May | 2022 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-05-01 16:19 | 2022-05-01 16:21 | 4398 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1118-09 Y SE CERRO POR SCADA LLEVA 1118-08 | S22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-01 | 8796 | keep | 0 | May | 2022 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
ARECIBO | 2022-05-01 16:22 | 2022-05-01 18:30 | 15 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO PUENTE | A22050100093 | Partial_restoration | Wire Down | Include | Include | Equipment | 128 | 2022-05-01 | 1920 | keep | 0 | May | 2022 | 0.0013077 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-01 16:30 | 2022-05-01 17:56 | 40 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M22050100173 | New_Event |  |  | Include | Wildlife | 86 | 2022-05-01 | 3440 | keep | 0 | May | 2022 | 0.002343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-01 16:36 | 2022-05-02 09:52 | 6 | 017:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR RAYOS | A22050100161 | New_Event | Bad Weather | Include | Include | Weather | 1036 | 2022-05-01 | 6216 | keep | 0 | May | 2022 | 0.0042337 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-05-01 16:52 | 2022-05-01 16:53 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 2203 | keep | 0 | May | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
HUMACAO | 2022-05-01 16:55 | 2022-05-01 17:13 | 50 | 000:18 | P | NO SE REPORTO CAUSA | 1 X 20 EMU EN SU | C22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2022-05-01 | 900 | keep | 0 | May | 2022 | 0.00061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-05-01 16:57 | 2022-05-01 18:03 | 20 | 001:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REMPLAZO CAJA PRIMARIA | R22050100110 | New_Event | Cutout Failure | Include | Include | Equipment | 66 | 2022-05-01 | 1320 | keep | 0 | May | 2022 | 0.00089905 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-01 16:58 | 2022-05-01 18:20 | 75 | 001:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REALIZO DESGANCHE SE REMPLAZO AISLADOR ROTO Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR AVERIA Y CERRAR EL INTERRUPTOR | A22050100104 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 82 | 2022-05-01 | 6150 | keep | 0 | May | 2022 | 0.0041887 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-01 16:59 | 2022-05-02 02:55 | 1 | 009:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER AVE CRUZO LINEAS | M22050200012 | New_Event |  |  | Include | Wildlife | 596 | 2022-05-01 | 596 | keep | 0 | May | 2022 | 0.00040593 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-05-01 17:00 | 2022-05-01 18:06 | 15 | 001:06 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | C22050100142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-05-01 | 990 | keep | 0 | May | 2022 | 0.00067428 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-01 17:02 | 2022-05-01 18:26 | 158 | 001:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L AVE | B22050100043 | New_Event |  |  | Include | Wildlife | 84 | 2022-05-01 | 13272 | keep | 0 | May | 2022 | 0.0090395 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
ARECIBO | 2022-05-01 17:04 | 2022-05-01 18:20 | 9 | 001:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR SE RETIRO NIDO DE AVE DE LA CAJA DEL TRANSFORMADOR | A22050100173 | New_Event |  |  | Include | Wildlife | 76 | 2022-05-01 | 684 | keep | 0 | May | 2022 | 0.00046587 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-05-01 17:45 | 2022-05-03 14:00 | 50 | 044:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 Y 2 X 40 EN CORTES DE LINEAS SE REPARO LINEAS PRIMARIAS CRUZADAS | M22050300138 | New_Event | Wire Down | Include | Include | Equipment | 2655 | 2022-05-01 | 132750 | keep | 0 | May | 2022 | 0.090415 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-05-01 17:55 | 2022-05-01 17:56 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22050100145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 5630 | keep | 0 | May | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
ARECIBO | 2022-05-01 18:02 | 2022-05-01 20:16 | 1548 | 002:14 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REPARO LINEA PRIMARIA ZAFADA DE AISLADOR Y SE REMPLAZO AISLADOR ROTO EN EL TRONCAL DEL ALIMENTADOR | A22050100187 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 134 | 2022-05-01 | 207432 | keep | 0 | May | 2022 | 0.14128 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
CAGUAS | 2022-05-01 18:11 | 2022-05-01 18:12 | 718 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | C22050100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-01 | 718 | keep | 0 | May | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
CAGUAS | 2022-05-01 18:12 | 2022-05-01 18:58 | 239 | 000:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO BKR A PETICION DE JOSE FUENTES PARA SECCIONALIZAR Y TRABAJAR CONDICION DE ALAMBRE EN EL PISO EN LA SALIDA DEL ALIMENTADOR | C22050100161 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 46 | 2022-05-01 | 10994 | keep | 0 | May | 2022 | 0.007488 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
ARECIBO | 2022-05-01 18:27 | 2022-05-02 23:18 | 213 | 028:51 | P | ESTRUCTURA AVERIADA | SE REMPLAZO DOS POSTES PARTIDOS Y SE REPARO LINEAS PRIMARIAS | A22050100201 | New_Event | Defective Pole | Include | Include | Equipment | 1731 | 2022-05-01 | 368703 | keep | 0 | May | 2022 | 0.25112 | 0.00014507 | Sustained | FALSE | FALSE | Not_TMED_Event | 213
ARECIBO | 2022-05-01 18:41 | 2022-05-02 09:44 | 40 | 015:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050100206 | New_Event | Bad Weather | Include | Include | Weather | 903 | 2022-05-01 | 36120 | keep | 0 | May | 2022 | 0.024601 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-01 18:49 | 2022-05-01 21:55 | 32 | 003:06 | P | ESTRUCTURA AVERIADA | 1 X 20 EN PROVISIONAL AVERIA NUEVA DEL T-19 @ T-20 SE QUEDO FUERA EL T-20 16 CLIENTES FUERA | R22050100114 | New_Event | Defective Pole | Include | Include | Equipment | 186 | 2022-05-01 | 5952 | keep | 0 | May | 2022 | 0.0040539 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2022-05-01 18:58 | 2022-05-01 21:27 | 718 | 002:29 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO BKR A PETICION DE JOSE FUENTES PARA SECCIONALIZAR Y TRABAJAR CONDICION DE ALAMBRE EN EL PISO EN LA SALIDA DEL ALIMENTADOR | C22050100161 | Additional_clients | Wire Down | Include | Include | Equipment | 149 | 2022-05-01 | 106982 | keep | 0 | May | 2022 | 0.072865 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-01 19:19 | 2022-05-01 20:15 | 35 | 000:56 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REPARO BARRA EN SU Y SE ENERGIZO | C22050100010 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 56 | 2022-05-01 | 1960 | keep | 0 | May | 2022 | 0.0013349 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-05-01 19:21 | 2022-05-01 19:22 | 3871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 3871 | keep | 0 | May | 2022 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
BAYAMON | 2022-05-01 19:25 | 2022-05-01 21:00 | 1 | 001:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22050100174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2022-05-01 | 95 | keep | 0 | May | 2022 | 6.4704e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-05-01 20:05 | 2022-05-02 03:18 | 100 | 007:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050100201 | New_Event | Bad Weather | Include | Include | Weather | 433 | 2022-05-01 | 43300 | keep | 0 | May | 2022 | 0.029491 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-01 20:13 | 2022-05-01 20:14 | 1106 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1529-15 Y SE CERRO POR SCADA LLEVA 60% DEL 1346-02 | S22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 1106 | keep | 0 | May | 2022 | 0.00075329 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
BAYAMON | 2022-05-01 20:13 | 2022-05-01 20:14 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1529-15 Y SE CERRO POR SCADA LLEVA 60% DEL 1346-02 | S22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 1802 | keep | 0 | May | 2022 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
UTUADO | 2022-05-01 20:14 | 2022-05-02 09:55 | 40 | 013:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RELOCALIZO LINEA SECUNDARIA CHOCANDO CON LINEA PRIMARIA | A22050100237 | New_Event | Wire Down | Include | Include | Equipment | 821 | 2022-05-01 | 32840 | keep | 0 | May | 2022 | 0.022367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 1339 | keep | 0 | May | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 470 | keep | 0 | May | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 2483 | keep | 0 | May | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 2190 | keep | 0 | May | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 3006 | keep | 0 | May | 2022 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 179 | keep | 0 | May | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 107 | keep | 0 | May | 2022 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 1666 | keep | 0 | May | 2022 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 4387 | keep | 0 | May | 2022 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 3147 | keep | 0 | May | 2022 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-05-01 20:15 | 2022-05-01 20:16 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 13400 | M22050100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-01 | 4304 | keep | 0 | May | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
SAN JUAN | 2022-05-01 20:30 | 2022-05-01 21:49 | 50 | 001:19 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22050100178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-05-01 | 3950 | keep | 0 | May | 2022 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-01 20:37 | 2022-05-01 21:42 | 225 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22050100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-05-01 | 14625 | keep | 0 | May | 2022 | 0.009961 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-01 21:05 | 2022-05-02 11:40 | 25 | 014:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S22050100184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 875 | 2022-05-01 | 21875 | keep | 0 | May | 2022 | 0.014899 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-01 21:13 | 2022-05-01 23:04 | 15 | 001:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE ZAFADO A CAJA | B22050100063 | New_Event | Wire Down | Include | Include | Equipment | 111 | 2022-05-01 | 1665 | keep | 0 | May | 2022 | 0.001134 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-01 21:13 | 2022-05-02 01:42 | 1584 | 004:29 | T | NO SE REPORTO CAUSA | SE ABRIO EL AMARRE CON EL 6801-01 Y SE CERRO EL INTERRUPTOR | M22050100210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2022-05-01 | 426096 | keep | 0 | May | 2022 | 0.29021 | 0.0010789 | Sustained | FALSE | FALSE | Not_TMED_Event | 1584
FAJARDO | 2022-05-01 21:33 | 2022-05-01 21:34 | 693 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR QUEDO EN SERVICIO | R22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 693 | keep | 0 | May | 2022 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
BAYAMON | 2022-05-01 21:46 | 2022-05-02 01:35 | 8 | 003:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO BAJANTE PRIMARIO A C/L | S22050100187 | New_Event | Wire Down | Include | Include | Equipment | 229 | 2022-05-01 | 1832 | keep | 0 | May | 2022 | 0.0012478 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-05-01 21:50 | 2022-05-02 09:25 | 30 | 011:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTO | A22050100271 | New_Event | Bad Weather | Include | Include | Weather | 695 | 2022-05-01 | 20850 | keep | 0 | May | 2022 | 0.014201 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-01 21:52 | 2022-05-02 14:30 | 150 | 016:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A22050100274 | New_Event | Wire Down | Include | Include | Equipment | 998 | 2022-05-01 | 149700 | keep | 0 | May | 2022 | 0.10196 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-05-01 21:53 | 2022-05-02 14:30 | 100 | 016:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA | S22050100189 | New_Event | Cutout Failure | Include | Include | Equipment | 997 | 2022-05-01 | 99700 | keep | 0 | May | 2022 | 0.067905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-01 22:00 | 2022-05-02 10:45 | 78 | 012:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA PRINCIPAL Y 1 X 65 EN CORTE DE LINEA RAMAL DESGANCHE DE BAMBUAS Y SE LEVANTO LINEA PRIMARIA. | S22050200193 | New_Event | Wire Down | Include | Include | Equipment | 765 | 2022-05-01 | 59670 | keep | 0 | May | 2022 | 0.040641 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
ARECIBO | 2022-05-01 22:08 | 2022-05-01 22:09 | 316 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR | A22050100284 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-01 | 316 | keep | 0 | May | 2022 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
CANOVANAS | 2022-05-01 22:09 | 2022-05-02 13:10 | 36 | 015:01 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22050100124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 901 | 2022-05-01 | 32436 | keep | 0 | May | 2022 | 0.022092 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2022-05-01 22:09 | 2022-05-01 23:18 | 100 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050100245 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 69 | 2022-05-01 | 6900 | keep | 0 | May | 2022 | 0.0046996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-01 22:25 | 2022-05-01 22:26 | 3871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22050100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 3871 | keep | 0 | May | 2022 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
MAYAGÃœEZ | 2022-05-01 22:34 | 2022-05-03 07:37 | 1 | 033:03 | P | ERROR HUMANO | SE CERRO MONTURA DE TRANSFORMADORES QUE SE HABIA DEJADO ABIERTA DESDE EL 05/01/2022 CUANDO HUBO AVERIA DE POSTES PARTIDOS | M22050100012 | New_Event | Human Error | Include | Include | Other | 1983 | 2022-05-01 | 1983 | keep | 0 | May | 2022 | 0.0013506 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-01 22:36 | 2022-05-02 12:07 | 65 | 013:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA Y SE FIJO PUENTE SAFADO | S22050100202 | New_Event | Wire Down | Include | Include | Equipment | 811 | 2022-05-01 | 52715 | keep | 0 | May | 2022 | 0.035904 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BARRANQUITAS | 2022-05-01 22:39 | 2022-05-02 10:21 | 40 | 011:42 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22050100189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 702 | 2022-05-01 | 28080 | keep | 0 | May | 2022 | 0.019125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-01 22:49 | 2022-05-02 14:30 | 100 | 015:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A22050100308 | New_Event | Wire Down | Include | Include | Equipment | 941 | 2022-05-01 | 94100 | keep | 0 | May | 2022 | 0.064091 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-01 22:58 | 2022-05-01 22:59 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 2147 | keep | 0 | May | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-05-01 23:00 | 2022-05-02 19:57 | 9 | 020:57 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE | S22050100213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1257 | 2022-05-01 | 11313 | keep | 0 | May | 2022 | 0.0077052 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2022-05-01 23:06 | 2022-05-02 09:29 | 90 | 010:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | R22050100126 | New_Event | Bad Weather | Include | Include | Weather | 623 | 2022-05-01 | 56070 | keep | 0 | May | 2022 | 0.038189 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2022-05-01 23:25 | 2022-05-02 07:45 | 100 | 008:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22050200192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 500 | 2022-05-01 | 50000 | keep | 0 | May | 2022 | 0.034055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-01 23:32 | 2022-05-03 09:39 | 1 | 034:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA UNIDAD MARITIMA POLICIA | A22050100317 | New_Event | Cutout Failure | Include | Include | Equipment | 2047 | 2022-05-01 | 2047 | keep | 0 | May | 2022 | 0.0013942 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-05-01 23:43 | 2022-05-01 23:44 | 2722 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050100127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-01 | 2722 | keep | 0 | May | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
AGUADILLA | 2022-05-01 23:58 | 2022-05-02 02:03 | 300 | 002:05 | P | ESTRUCTURA AVERIADA | ABRIR CORTE DE LINEA PARA RELOCALIZAR LINEAS EN POSTE PARTIDO | M22050100184 | New_Event | Defective Pole | Include | Include | Equipment | 125 | 2022-05-01 | 37500 | keep | 0 | May | 2022 | 0.025541 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-05-02 00:18 | 2022-05-02 05:16 | 18 | 004:58 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B22050200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2022-05-02 | 5364 | keep | 0 | May | 2022 | 0.0036534 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2022-05-02 00:52 | 2022-05-02 00:53 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | A22050200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 2697 | keep | 0 | May | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
SAN JUAN | 2022-05-02 01:26 | 2022-05-03 09:29 | 103 | 032:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22050200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1923 | 2022-05-02 | 198069 | keep | 0 | May | 2022 | 0.1349 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
MAYAGÃœEZ | 2022-05-02 01:42 | 2022-05-02 10:54 | 1185 | 009:12 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON MACHETES DE BARRA | M22050200008 | New_Event | Switch Failure | Include | Include | Equipment | 552 | 2022-05-02 | 654120 | keep | 0 | May | 2022 | 0.44552 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
UTUADO | 2022-05-02 02:10 | 2022-05-02 12:54 | 50 | 010:44 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A22050200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 644 | 2022-05-02 | 32200 | keep | 0 | May | 2022 | 0.021931 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-05-02 02:58 | 2022-05-02 02:59 | 1827 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22050200013 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-02 | 1827 | keep | 0 | May | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-05-02 02:59 | 2022-05-02 05:06 | 100 | 002:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200014 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 127 | 2022-05-02 | 12700 | keep | 0 | May | 2022 | 0.0086499 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-02 03:16 | 2022-05-02 16:33 | 16 | 013:17 | P | ESTRUCTURA AVERIADA | 1 X 15 EN C/L SE REMPLAZO POSTE | R22050200002 | New_Event | Defective Pole | Include | Include | Equipment | 797 | 2022-05-02 | 12752 | keep | 0 | May | 2022 | 0.0086853 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2022-05-02 03:16 | 2022-05-02 03:17 | 676 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 676 | keep | 0 | May | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
CAGUAS | 2022-05-02 04:18 | 2022-05-02 04:19 | 2178 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22050200000 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-02 | 2178 | keep | 0 | May | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CAGUAS | 2022-05-02 04:19 | 2022-05-02 11:05 | 70 | 006:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN SU-C CRUCE POR GATO | C22050200017 | 1st_after_momentary |  |  | Include | Wildlife | 406 | 2022-05-02 | 28420 | keep | 0 | May | 2022 | 0.019357 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-05-02 04:58 | 2022-05-02 09:09 | 2435 | 004:11 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR CARGA POR EL 1909-08 BY-220502-01 | S22050200006 | New_Event | UG Cable Fault | Include | Include | Equipment | 251 | 2022-05-02 | 611185 | keep | 0 | May | 2022 | 0.41628 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-05-02 04:58 | 2022-05-02 15:13 | 2956 | 010:15 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR ENTRO EN SERVICIO 50% | S22050200000 | New_Event | UG Cable Fault | Include | Include | Equipment | 615 | 2022-05-02 | 1817940 | keep | 0 | May | 2022 | 1.2382 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-05-02 05:10 | 2022-05-02 11:09 | 11 | 005:59 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B2205020004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2022-05-02 | 3949 | keep | 0 | May | 2022 | 0.0026896 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2022-05-02 05:38 | 2022-05-02 05:39 | 603 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9206-08 LLEVA 9206-09 | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 603 | keep | 0 | May | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-05-02 05:38 | 2022-05-02 05:39 | 6 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9206-08 LLEVA 9206-09 | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 6 | keep | 0 | May | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-02 05:50 | 2022-05-02 09:02 | 8 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A22050200016 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2022-05-02 | 1536 | keep | 0 | May | 2022 | 0.0010462 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-05-02 06:30 | 2022-05-02 06:31 | 1984 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-12 QUE A SU VEZ LLEVA LA CARGA DEL 1911-07 | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 1984 | keep | 0 | May | 2022 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-05-02 06:30 | 2022-05-02 06:31 | 577 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-12 QUE A SU VEZ LLEVA LA CARGA DEL 1911-07 | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 577 | keep | 0 | May | 2022 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
GUAYAMA | 2022-05-02 06:30 | 2022-05-02 14:03 | 60 | 007:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR AVERIADO | P22050200002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 453 | 2022-05-02 | 27180 | keep | 0 | May | 2022 | 0.018512 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-05-02 06:33 | 2022-05-02 08:00 | 80 | 001:27 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22050200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-05-02 | 6960 | keep | 0 | May | 2022 | 0.0047404 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-05-02 06:34 | 2022-05-02 08:50 | 30 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | P22050200004 | New_Event |  |  | Include | Wildlife | 136 | 2022-05-02 | 4080 | keep | 0 | May | 2022 | 0.0027789 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-05-02 06:35 | 2022-05-02 19:10 | 20 | 012:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22050200015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 755 | 2022-05-02 | 15100 | keep | 0 | May | 2022 | 0.010285 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-02 06:35 | 2022-05-02 18:00 | 50 | 011:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN RISER SE RETIRO AVE | B22050200010 | New_Event |  |  | Include | Wildlife | 685 | 2022-05-02 | 34250 | keep | 0 | May | 2022 | 0.023328 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-02 06:36 | 2022-05-02 06:37 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
ARECIBO | 2022-05-02 06:38 | 2022-05-02 11:28 | 60 | 004:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 Y 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTO | A22050200023 | New_Event | Bad Weather | Include | Include | Weather | 290 | 2022-05-02 | 17400 | keep | 0 | May | 2022 | 0.011851 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-02 06:43 | 2022-05-02 06:44 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE | R22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 2000 | keep | 0 | May | 2022 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2022-05-02 06:43 | 2022-05-02 06:44 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | R22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 5062 | keep | 0 | May | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
AGUADILLA | 2022-05-02 06:50 | 2022-05-02 10:00 | 50 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200021 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2022-05-02 | 9500 | keep | 0 | May | 2022 | 0.0064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-02 07:00 | 2022-05-02 10:04 | 1 | 003:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN RAICER NO CAUSAS | P22050200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2022-05-02 | 184 | keep | 0 | May | 2022 | 0.00012532 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-02 07:06 | 2022-05-02 08:59 | 10 | 001:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22050200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-05-02 | 1130 | keep | 0 | May | 2022 | 0.00076964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-02 07:19 | 2022-05-02 10:14 | 60 | 002:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE DE LINEA A CAJA PRIMARIA. NO FUNDIO FUSIBLE | R22050200041 | New_Event | Wire Down | Include | Include | Equipment | 175 | 2022-05-02 | 10500 | keep | 0 | May | 2022 | 0.0071515 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-05-02 07:22 | 2022-05-02 11:20 | 70 | 003:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | R22050200022 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 238 | 2022-05-02 | 16660 | keep | 0 | May | 2022 | 0.011347 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-05-02 07:32 | 2022-05-02 07:33 | 3332 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B22050200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-02 | 3332 | keep | 0 | May | 2022 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2022-05-02 07:33 | 2022-05-02 18:16 | 30 | 010:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22050200020 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 643 | 2022-05-02 | 19290 | keep | 0 | May | 2022 | 0.013138 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-02 07:39 | 2022-05-02 13:02 | 75 | 005:23 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 80 EN CORTE DE LINEA TORNADO | A22050200046 | New_Event | Bad Weather | Include | Include | Weather | 323 | 2022-05-02 | 24225 | keep | 0 | May | 2022 | 0.0165 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-05-02 07:41 | 2022-05-02 14:23 | 30 | 006:42 | P | NO SE REPORTO CAUSA | 1 X 40 SMU-20 EN SU-2B8C Y OTRO IGUAL EN SU-3MC NO CAUSA | C22050200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 402 | 2022-05-02 | 12060 | keep | 0 | May | 2022 | 0.008214 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-02 07:48 | 2022-05-02 11:00 | 25 | 003:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22050200039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2022-05-02 | 4800 | keep | 0 | May | 2022 | 0.0032693 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-05-02 07:48 | 2022-05-02 12:14 | 80 | 004:26 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE DESGANCHO PALMA | A22050200051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2022-05-02 | 21280 | keep | 0 | May | 2022 | 0.014494 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-05-02 08:02 | 2022-05-02 11:23 | 4 | 003:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REEMPLAZO PORTAFUSIBLE | R22050200046 | New_Event | Cutout Failure | Include | Include | Equipment | 201 | 2022-05-02 | 804 | keep | 0 | May | 2022 | 0.0005476 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-05-02 08:02 | 2022-05-02 18:30 | 100 | 010:28 | P | DESGANCHE | 3 X 50 Y 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M22050200040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 628 | 2022-05-02 | 62800 | keep | 0 | May | 2022 | 0.042773 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-02 08:02 | 2022-05-02 09:46 | 2735 | 001:44 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO BKR A PETICION JESUS GRACIAS ACCIDENTE CONTACTO ELECTRICO. CONDUCTOR ESTABA VIVO EN EL SUELO Y PEATON TUVO CONTACTO CON EL EN COROZAL CARRETERA 568 INT 805 BY-220502-02 ENTRO 50% EN SERVICIO | B22050200027 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2022-05-02 | 284440 | keep | 0 | May | 2022 | 0.19373 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
ARECIBO | 2022-05-02 08:07 | 2022-05-02 09:59 | 274 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEAS PARTIDAS EN TRONCAL | A22050200060 | New_Event | Wire Down | Include | Include | Equipment | 112 | 2022-05-02 | 30688 | keep | 0 | May | 2022 | 0.020901 | 0.00018662 | Sustained | FALSE | FALSE | Not_TMED_Event | 274
ARECIBO | 2022-05-02 08:09 | 2022-05-02 09:51 | 100 | 001:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTES VIENTO | A22050200063 | New_Event | Bad Weather | Include | Include | Weather | 102 | 2022-05-02 | 10200 | keep | 0 | May | 2022 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-02 08:19 | 2022-05-02 12:25 | 1 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22050200053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2022-05-02 | 246 | keep | 0 | May | 2022 | 0.00016755 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-02 08:20 | 2022-05-02 18:00 | 16 | 009:40 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | S22050200041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 580 | 2022-05-02 | 9280 | keep | 0 | May | 2022 | 0.0063206 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-05-02 08:25 | 2022-05-02 08:26 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 312 | keep | 0 | May | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-05-02 08:25 | 2022-05-02 08:26 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 4641 | keep | 0 | May | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
ARECIBO | 2022-05-02 08:27 | 2022-05-02 11:30 | 60 | 003:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | A22050200072 | New_Event | Bad Weather | Include | Include | Weather | 183 | 2022-05-02 | 10980 | keep | 0 | May | 2022 | 0.0074784 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-02 08:28 | 2022-05-02 09:31 | 3 | 001:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R22050200057 | New_Event |  |  | Include | Wildlife | 63 | 2022-05-02 | 189 | keep | 0 | May | 2022 | 0.00012873 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-05-02 08:33 | 2022-05-02 10:29 | 12 | 001:56 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR PALMA CRUZO SECUNDARIA | C22050200021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 116 | 2022-05-02 | 1392 | keep | 0 | May | 2022 | 0.00094808 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-02 08:37 | 2022-05-02 17:45 | 2 | 009:08 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | P22050200051 | New_Event | Defective Pole | Include | Include | Equipment | 548 | 2022-05-02 | 1096 | keep | 0 | May | 2022 | 0.00074648 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-05-02 08:45 | 2022-05-02 19:50 | 60 | 011:05 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22050200040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 665 | 2022-05-02 | 39900 | keep | 0 | May | 2022 | 0.027176 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-02 08:48 | 2022-05-02 11:48 | 281 | 003:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-05-02 | 50580 | keep | 0 | May | 2022 | 0.03445 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-05-02 08:48 | 2022-05-02 11:48 | 1252 | 003:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-05-02 | 225360 | keep | 0 | May | 2022 | 0.15349 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-05-02 08:48 | 2022-05-02 11:48 | 595 | 003:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-05-02 | 107100 | keep | 0 | May | 2022 | 0.072945 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-05-02 08:48 | 2022-05-02 11:48 | 51 | 003:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-05-02 | 9180 | keep | 0 | May | 2022 | 0.0062525 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-05-02 08:48 | 2022-05-02 11:48 | 721 | 003:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-05-02 | 129780 | keep | 0 | May | 2022 | 0.088393 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-05-02 08:48 | 2022-05-02 11:48 | 1382 | 003:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-05-02 | 248760 | keep | 0 | May | 2022 | 0.16943 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-05-02 08:48 | 2022-05-02 11:48 | 654 | 003:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-05-02 | 117720 | keep | 0 | May | 2022 | 0.080179 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
BAYAMON | 2022-05-02 08:58 | 2022-05-02 20:10 | 10 | 011:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22050200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 672 | 2022-05-02 | 6720 | keep | 0 | May | 2022 | 0.004577 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-02 08:59 | 2022-05-02 09:00 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 1253 | keep | 0 | May | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-02 08:59 | 2022-05-02 09:00 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 1266 | keep | 0 | May | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-02 08:59 | 2022-05-02 09:00 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 411 | keep | 0 | May | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-02 08:59 | 2022-05-02 09:00 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 863 | keep | 0 | May | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-02 08:59 | 2022-05-02 09:00 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 309 | keep | 0 | May | 2022 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-02 08:59 | 2022-05-02 09:00 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 176 | keep | 0 | May | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-02 08:59 | 2022-05-02 09:00 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 974 | keep | 0 | May | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
MAYAGÃœEZ | 2022-05-02 09:00 | 2022-05-03 13:32 | 40 | 028:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M22050300062 | New_Event | Bad Weather | Include | Include | Weather | 1712 | 2022-05-02 | 68480 | keep | 0 | May | 2022 | 0.046641 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-05-02 09:00 | 2022-05-02 15:25 | 25 | 006:25 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200556 | New_Event | Bad Weather | Include | Include | Weather | 385 | 2022-05-02 | 9625 | keep | 0 | May | 2022 | 0.0065555 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-02 09:02 | 2022-05-02 09:03 | 2076 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 40% DE LA CARGA POR EL 1718-03 | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 2076 | keep | 0 | May | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-05-02 09:02 | 2022-05-02 09:03 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 40% DEL 1710-05 | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 2605 | keep | 0 | May | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
SAN JUAN | 2022-05-02 09:09 | 2022-05-02 09:11 | 256 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 QUE A SU VEZ LLEVA EL 20% DEL 1111-01 | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-02 | 512 | keep | 0 | May | 2022 | 0.00034872 | 0.00017436 | Momentary | FALSE | FALSE | Not_TMED_Event | 256
SAN JUAN | 2022-05-02 09:09 | 2022-05-02 09:11 | 2782 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 QUE A SU VEZ LLEVA EL 20% DEL 1111-01 | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-02 | 5564 | keep | 0 | May | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
MAYAGÃœEZ | 2022-05-02 09:10 | 2022-05-02 16:05 | 1 | 006:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA EL JOURNEYMAN NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | M22050200084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 415 | 2022-05-02 | 415 | keep | 0 | May | 2022 | 0.00028265 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-02 09:12 | 2022-05-04 17:12 | 11 | 055:60 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE LEVANTO CONDUCTOR Y SE REALIZO DESGANCHE | B22050200049 | New_Event | Defective Pole | Include | Include | Equipment | 3360 | 2022-05-02 | 36960 | keep | 0 | May | 2022 | 0.025173 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2022-05-02 09:15 | 2022-05-02 11:09 | 100 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | A22050200115 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2022-05-02 | 11400 | keep | 0 | May | 2022 | 0.0077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-02 09:19 | 2022-05-02 11:24 | 1241 | 002:05 | T | DESGANCHE | SE ABRIO CORTE DE LINEA Y SE CERRO INTERRUPTOR | A22050200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-05-02 | 155125 | keep | 0 | May | 2022 | 0.10565 | 0.00084524 | Sustained | FALSE | FALSE | Not_TMED_Event | 1241
CAGUAS | 2022-05-02 09:24 | 2022-05-02 09:25 | 1709 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C22050200049 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-05-02 | 1709 | keep | 0 | May | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2022-05-02 09:25 | 2022-05-02 11:09 | 120 | 001:44 | P | CABLE SOTERRADO AVERIADO | 1 X 140 DE RISER @ SU-20 SE REPARO AVERIA SOTERRADA | C22050200052 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 104 | 2022-05-02 | 12480 | keep | 0 | May | 2022 | 0.0085001 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-05-02 09:30 | 2022-05-03 14:00 | 50 | 028:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES SIN SERVCIO DEL DIA 5/02/2022 | M22050300016 | New_Event | Bad Weather | Include | Include | Weather | 1710 | 2022-05-02 | 85500 | keep | 0 | May | 2022 | 0.058234 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-05-02 09:32 | 2022-05-02 11:20 | 150 | 001:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22050200054 | New_Event |  |  | Include | Wildlife | 108 | 2022-05-02 | 16200 | keep | 0 | May | 2022 | 0.011034 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-05-02 09:33 | 2022-05-02 14:21 | 80 | 004:48 | P | DESGANCHE | 2 X 80 EN C/L SE RETIRARON BAMBUAS | C22050200055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-05-02 | 23040 | keep | 0 | May | 2022 | 0.015692 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-02 09:33 | 2022-05-02 17:00 | 80 | 007:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200126 | New_Event | Bad Weather | Include | Include | Weather | 447 | 2022-05-02 | 35760 | keep | 0 | May | 2022 | 0.024356 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-02 09:37 | 2022-05-02 17:00 | 50 | 007:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22050200140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 443 | 2022-05-02 | 22150 | keep | 0 | May | 2022 | 0.015086 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-05-02 09:39 | 2022-05-02 09:40 | 4132 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE LA CARGA POR EL 4006-05 | P22050200023 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-02 | 4132 | keep | 0 | May | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-05-02 09:39 | 2022-05-02 09:40 | 4279 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR CARGA POR 4006-05 | P22050200023 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-02 | 4279 | keep | 0 | May | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-05-02 09:39 | 2022-05-02 09:40 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE LLEVA LA CARGA DEL 4003-01 | P22050200023 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-02 | 464 | keep | 0 | May | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-05-02 09:40 | 2022-05-02 12:03 | 30 | 002:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L AVE CRUZO LINEAS | P22050200047 | 1st_after_momentary |  |  | Include | Wildlife | 143 | 2022-05-02 | 4290 | keep | 0 | May | 2022 | 0.0029219 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-02 09:40 | 2022-05-03 10:15 | 50 | 024:35 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22050300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1475 | 2022-05-02 | 73750 | keep | 0 | May | 2022 | 0.050231 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-02 09:43 | 2022-05-02 13:39 | 55 | 003:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO PUENTE ABIERTO Y REEMPLAZO CAJA PRIMARIA QUEMADA NO FUNDIO FUSIBLE. | C22050200060 | New_Event | Wire Down | Include | Include | Equipment | 236 | 2022-05-02 | 12980 | keep | 0 | May | 2022 | 0.0088406 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 1339 | keep | 0 | May | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 470 | keep | 0 | May | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 2483 | keep | 0 | May | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 2190 | keep | 0 | May | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 3006 | keep | 0 | May | 2022 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 179 | keep | 0 | May | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 107 | keep | 0 | May | 2022 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 1666 | keep | 0 | May | 2022 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 4387 | keep | 0 | May | 2022 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 3147 | keep | 0 | May | 2022 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-05-02 09:45 | 2022-05-02 09:46 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050200184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-02 | 4304 | keep | 0 | May | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2022-05-02 09:46 | 2022-05-02 12:27 | 1367 | 002:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO EN EL SUELO | B22050200027 | Partial_restoration | Wire Down | Include | Include | Equipment | 161 | 2022-05-02 | 220087 | keep | 0 | May | 2022 | 0.1499 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-02 09:49 | 2022-05-02 13:14 | 1253 | 003:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2022-05-02 | 256865 | keep | 0 | May | 2022 | 0.17495 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-02 09:49 | 2022-05-02 13:14 | 1266 | 003:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2022-05-02 | 259530 | keep | 0 | May | 2022 | 0.17676 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-02 09:49 | 2022-05-02 13:14 | 411 | 003:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2022-05-02 | 84255 | keep | 0 | May | 2022 | 0.057386 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-02 09:49 | 2022-05-02 13:14 | 863 | 003:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2022-05-02 | 176915 | keep | 0 | May | 2022 | 0.1205 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-02 09:49 | 2022-05-02 13:14 | 309 | 003:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2022-05-02 | 63345 | keep | 0 | May | 2022 | 0.043144 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-02 09:49 | 2022-05-02 13:14 | 176 | 003:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2022-05-02 | 36080 | keep | 0 | May | 2022 | 0.024574 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-02 09:49 | 2022-05-02 13:14 | 974 | 003:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22050200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2022-05-02 | 199670 | keep | 0 | May | 2022 | 0.13599 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
UTUADO | 2022-05-02 09:54 | 2022-05-02 10:29 | 1527 | 000:35 | T | DESGANCHE | SE PATRULLO SE CERRO INTERRUPTOR BAMBUS SOBRE LAS LINEAS | A22050200171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2022-05-02 | 53445 | keep | 0 | May | 2022 | 0.036401 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
PONCE | 2022-05-02 09:59 | 2022-05-02 18:43 | 30 | 008:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22050200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 524 | 2022-05-02 | 15720 | keep | 0 | May | 2022 | 0.010707 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-02 09:59 | 2022-05-02 11:31 | 274 | 001:32 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR LINEAS PARTIDAS EN TRONCAL | A22050200060 | Partial_restoration | Wire Down | Include | Include | Equipment | 92 | 2022-05-02 | 25208 | keep | 0 | May | 2022 | 0.017169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-02 09:59 | 2022-05-02 11:31 | 185 | 001:32 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SU CARGA POR EL 8001-02 SE ABRIO INTERRUPTOR 8001-02 POR LINEAS PARTIDAS EN TRONCAL | A22050200060 | New_Event | Wire Down | Include | Include | Equipment | 92 | 2022-05-02 | 17020 | keep | 0 | May | 2022 | 0.011592 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
MAYAGÃœEZ | 2022-05-02 10:01 | 2022-05-02 16:40 | 200 | 006:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 140 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | M22050200192 | New_Event | Wire Down | Include | Include | Equipment | 399 | 2022-05-02 | 79800 | keep | 0 | May | 2022 | 0.054351 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-02 10:02 | 2022-05-02 21:25 | 100 | 011:23 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22050200141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 683 | 2022-05-02 | 68300 | keep | 0 | May | 2022 | 0.046519 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:21 | 1339 | 001:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 71 | 2022-05-02 | 95069 | keep | 0 | May | 2022 | 0.064751 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:21 | 470 | 001:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 71 | 2022-05-02 | 33370 | keep | 0 | May | 2022 | 0.022728 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:21 | 2483 | 001:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 71 | 2022-05-02 | 176293 | keep | 0 | May | 2022 | 0.12007 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:21 | 2190 | 001:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 71 | 2022-05-02 | 155490 | keep | 0 | May | 2022 | 0.1059 | 0.0014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:21 | 3006 | 001:11 | S | LINEA DE TRANSMISION 38KV | CERRADA LINEA PARCIAL (13450) | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 71 | 2022-05-02 | 213426 | keep | 0 | May | 2022 | 0.14536 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:21 | 179 | 001:11 | S | LINEA DE TRANSMISION 38KV | CERRADA LINEA PARCIAL (13450) | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 71 | 2022-05-02 | 12709 | keep | 0 | May | 2022 | 0.008656 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:31 | 107 | 001:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 81 | 2022-05-02 | 8667 | keep | 0 | May | 2022 | 0.0059031 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:31 | 1666 | 001:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 81 | 2022-05-02 | 134946 | keep | 0 | May | 2022 | 0.091911 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:31 | 4387 | 001:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 81 | 2022-05-02 | 355347 | keep | 0 | May | 2022 | 0.24203 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:31 | 3147 | 001:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 81 | 2022-05-02 | 254907 | keep | 0 | May | 2022 | 0.17362 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-05-02 10:10 | 2022-05-02 11:31 | 4304 | 001:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 81 | 2022-05-02 | 348624 | keep | 0 | May | 2022 | 0.23745 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
VEGA BAJA | 2022-05-02 10:13 | 2022-05-02 17:10 | 100 | 006:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 SE REMPLAZO DOS CAJA PRIMARIAS | B22050200076 | New_Event | Cutout Failure | Include | Include | Equipment | 417 | 2022-05-02 | 41700 | keep | 0 | May | 2022 | 0.028402 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-02 10:16 | 2022-05-02 15:04 | 75 | 004:48 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200214 | New_Event | Bad Weather | Include | Include | Weather | 288 | 2022-05-02 | 21600 | keep | 0 | May | 2022 | 0.014712 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-05-02 10:20 | 2022-05-02 13:35 | 200 | 003:15 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA 1 X 100 EN CORTE DE LINEA | M22050200226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-05-02 | 39000 | keep | 0 | May | 2022 | 0.026563 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-05-02 10:29 | 2022-05-02 20:58 | 200 | 010:29 | P | DESGANCHE | 1 X 200 Y 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22050200345 | New_Event | Vegetation Contact | Include | Include | Vegetation | 629 | 2022-05-02 | 125800 | keep | 0 | May | 2022 | 0.085682 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-05-02 10:29 | 2022-05-02 14:17 | 30 | 003:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200217 | New_Event | Bad Weather | Include | Include | Weather | 228 | 2022-05-02 | 6840 | keep | 0 | May | 2022 | 0.0046587 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-05-02 10:29 | 2022-05-02 10:30 | 2362 | 000:01 | T | DESGANCHE | RECIERRE | C22050200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-02 | 2362 | keep | 0 | May | 2022 | 0.0016087 | 0.0016087 | Momentary | FALSE | FALSE | Not_TMED_Event | 2362
BARRANQUITAS | 2022-05-02 10:30 | 2022-05-02 13:14 | 300 | 002:44 | P | DESGANCHE | 3 X 140 EN CORTE DE LINEA RETIRO ARBOL SOBRE LINEA | C22050200089 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-05-02 | 49200 | keep | 0 | May | 2022 | 0.03351 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2022-05-02 10:30 | 2022-05-02 12:12 | 12 | 001:42 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR PALMA CRUZO SECUNDARIA | C22050200021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 102 | 2022-05-02 | 1224 | keep | 0 | May | 2022 | 0.00083366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-05-02 10:32 | 2022-05-02 20:25 | 120 | 009:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 Y 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22050200222 | New_Event | Wire Down | Include | Include | Equipment | 593 | 2022-05-02 | 71160 | keep | 0 | May | 2022 | 0.048467 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-05-02 10:38 | 2022-05-02 10:39 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 90% DEL 1705-03 | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 478 | keep | 0 | May | 2022 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-05-02 10:38 | 2022-05-02 10:39 | 854 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 90% DE LA CARGA POR EL 1705-03 | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 854 | keep | 0 | May | 2022 | 0.00058166 | 0.00058166 | Momentary | FALSE | FALSE | Not_TMED_Event | 854
BAYAMON | 2022-05-02 10:39 | 2022-05-02 10:41 | 723 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1711-05 | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-02 | 1446 | keep | 0 | May | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-05-02 10:39 | 2022-05-02 10:41 | 1976 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1711-02 | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-02 | 3952 | keep | 0 | May | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-05-02 10:39 | 2022-05-02 10:41 | 293 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 38KV | S22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-02 | 586 | keep | 0 | May | 2022 | 0.00039912 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2022-05-02 10:39 | 2022-05-02 10:41 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 38KV | S22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-02 | 630 | keep | 0 | May | 2022 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2022-05-02 10:39 | 2022-05-02 10:41 | 216 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 38KV | S22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-02 | 432 | keep | 0 | May | 2022 | 0.00029423 | 0.00014712 | Momentary | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2022-05-02 10:39 | 2022-05-02 10:41 | 1310 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 38KV | S22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-02 | 2620 | keep | 0 | May | 2022 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CAGUAS | 2022-05-02 10:42 | 2022-05-02 16:08 | 14 | 005:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22050200094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 326 | 2022-05-02 | 4564 | keep | 0 | May | 2022 | 0.0031085 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-05-02 10:45 | 2022-05-02 14:50 | 6 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200231 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2022-05-02 | 1470 | keep | 0 | May | 2022 | 0.0010012 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-02 10:54 | 2022-05-02 12:12 | 400 | 001:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO | M22050200008 | New_Event | Wire Down | Include | Include | Equipment | 78 | 2022-05-02 | 31200 | keep | 0 | May | 2022 | 0.02125 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
YAUCO | 2022-05-02 10:58 | 2022-05-02 14:08 | 150 | 003:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22050200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-05-02 | 28500 | keep | 0 | May | 2022 | 0.019411 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-05-02 11:01 | 2022-05-02 17:40 | 100 | 006:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200249 | New_Event | Bad Weather | Include | Include | Weather | 399 | 2022-05-02 | 39900 | keep | 0 | May | 2022 | 0.027176 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-02 11:03 | 2022-05-02 17:45 | 150 | 006:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA VIENTOS FUERTES | A22050200251 | New_Event | Bad Weather | Include | Include | Weather | 402 | 2022-05-02 | 60300 | keep | 0 | May | 2022 | 0.04107 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-05-02 11:08 | 2022-05-02 15:36 | 132 | 004:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 65 EN C/L SE SUBIERON Y REPARARON LAS LINEAS A CRUCETA PROVISIONAL. IMPACTO POR CAMION | S22050200199 | New_Event |  |  | Include | Wildlife | 268 | 2022-05-02 | 35376 | keep | 0 | May | 2022 | 0.024094 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
CAGUAS | 2022-05-02 11:09 | 2022-05-02 11:10 | 1709 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C22050200115 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-05-02 | 1709 | keep | 0 | May | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2022-05-02 11:10 | 2022-05-02 17:42 | 120 | 006:32 | P | CABLE SOTERRADO AVERIADO | 1 X 140 DE RISER @ SU-20 SE REPARO AVERIA SOTERRADA | C22050200052 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 392 | 2022-05-02 | 47040 | keep | 0 | May | 2022 | 0.032039 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-05-02 11:19 | 2022-05-02 15:15 | 580 | 003:56 | P | DESGANCHE | 1 X 200 Y 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22050200103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-05-02 | 136880 | keep | 0 | May | 2022 | 0.093228 | 0.00039504 | Sustained | FALSE | FALSE | Not_TMED_Event | 580
SAN JUAN | 2022-05-02 11:21 | 2022-05-02 13:25 | 1066 | 002:04 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE REALIZO DESGANCHE | S22050200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-05-02 | 132184 | keep | 0 | May | 2022 | 0.09003 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
BARRANQUITAS | 2022-05-02 11:22 | 2022-05-02 20:00 | 50 | 008:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22050200122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 518 | 2022-05-02 | 25900 | keep | 0 | May | 2022 | 0.01764 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-02 11:24 | 2022-05-02 12:25 | 300 | 001:01 | P | DESGANCHE | 1 X 100 Y 3 X 50 EN CORTE DE LINEA SE RETIRO BAMBUAS | A22050200177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-05-02 | 18300 | keep | 0 | May | 2022 | 0.012464 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2022-05-02 11:24 | 2022-05-02 12:13 | 150 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | C22050200124 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2022-05-02 | 7350 | keep | 0 | May | 2022 | 0.0050061 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-02 11:28 | 2022-05-02 19:00 | 50 | 007:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA | B22050200106 | New_Event | Wire Down | Include | Include | Equipment | 452 | 2022-05-02 | 22600 | keep | 0 | May | 2022 | 0.015393 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-02 11:48 | 2022-05-02 12:04 | 75 | 000:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200295 | New_Event | Bad Weather | Include | Include | Weather | 16 | 2022-05-02 | 1200 | keep | 0 | May | 2022 | 0.00081731 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
FAJARDO | 2022-05-02 11:58 | 2022-05-02 12:57 | 1 | 000:59 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | R22050200111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-05-02 | 59 | keep | 0 | May | 2022 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-02 11:58 | 2022-05-03 10:58 | 100 | 023:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE RETIAR BAMBUS SOBRE LA LINEA | M22050300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1380 | 2022-05-02 | 138000 | keep | 0 | May | 2022 | 0.093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-02 12:04 | 2022-05-02 12:14 | 281 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-02 | 2810 | keep | 0 | May | 2022 | 0.0019139 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-05-02 12:04 | 2022-05-02 12:14 | 1252 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-02 | 12520 | keep | 0 | May | 2022 | 0.0085273 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-05-02 12:04 | 2022-05-02 12:14 | 595 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-02 | 5950 | keep | 0 | May | 2022 | 0.0040525 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-05-02 12:04 | 2022-05-02 12:14 | 51 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-02 | 510 | keep | 0 | May | 2022 | 0.00034736 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-05-02 12:04 | 2022-05-02 12:14 | 721 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-02 | 7210 | keep | 0 | May | 2022 | 0.0049107 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-05-02 12:04 | 2022-05-02 12:14 | 1382 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-02 | 13820 | keep | 0 | May | 2022 | 0.0094127 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-05-02 12:04 | 2022-05-02 12:14 | 654 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22050200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-02 | 6540 | keep | 0 | May | 2022 | 0.0044544 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
MAYAGÃœEZ | 2022-05-02 12:10 | 2022-05-02 18:30 | 12 | 006:20 | P | LINEA DE TRANSMISION 38KV | 1 X 15 EN TRANSFORMADOR INFORMO EL JORNEYMAN QUE HOY HUBO UNA AVERIA EN LA LINEA 1200 QUE CAYO SOBRE EL ALIMENTADOR Y CAUSO AVERIAS EN EL AREA | M22050200552 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 380 | 2022-05-02 | 4560 | keep | 0 | May | 2022 | 0.0031058 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-02 12:11 | 2022-05-02 13:23 | 2689 | 001:12 | T | BREAKER DEFECTUOSO O NO OPERA | INTERUPTOR PROBO MALO ESTA QUEMADO SE TRANSFIRIO CARGA AL 5002-01 | P22020200065 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 72 | 2022-05-02 | 193608 | keep | 0 | May | 2022 | 0.13187 | 0.0018315 | Sustained | FALSE | FALSE | Not_TMED_Event | 2689
MAYAGÃœEZ | 2022-05-02 12:12 | 2022-05-02 12:18 | 1185 | 000:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR A PETICION DE PERSONAL DE CAMPO PARA REPARAR PUENTE PRIMARIO | M22050200008 | Additional_clients | Wire Down | Include | Include | Equipment | 6 | 2022-05-02 | 7110 | keep | 0 | May | 2022 | 0.0048426 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-02 12:12 | 2022-05-02 12:48 | 60 | 000:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22050200167 | New_Event | Bad Weather | Include | Include | Weather | 36 | 2022-05-02 | 2160 | keep | 0 | May | 2022 | 0.0014712 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-02 12:14 | 2022-05-02 12:15 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 3718 | keep | 0 | May | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
UTUADO | 2022-05-02 12:14 | 2022-05-02 17:45 | 75 | 005:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200295 | Partial_restoration | Bad Weather | Include | Include | Weather | 331 | 2022-05-02 | 24825 | keep | 0 | May | 2022 | 0.016908 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-02 12:23 | 2022-05-02 16:06 | 38 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN C/L MAL TIEMPO | C22050200018 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2022-05-02 | 8474 | keep | 0 | May | 2022 | 0.0057716 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2022-05-02 12:26 | 2022-05-03 10:26 | 146 | 022:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA Y SE DEJO SECCIONALIZO CONDUCTOR EN EL SUELO. SE REFIRE POR SER TRAS PATIO Y POSTE EN MAL ESTADO | S22050300450 | New_Event | Wire Down | Include | Include | Equipment | 1320 | 2022-05-02 | 192720 | keep | 0 | May | 2022 | 0.13126 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
PONCE | 2022-05-02 12:26 | 2022-05-02 12:27 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 2039 | keep | 0 | May | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2022-05-02 12:27 | 2022-05-02 22:42 | 39 | 010:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN RISER SE DESENRREDO LINEA PRIMARIA | P22050200166 | New_Event | Wire Down | Include | Include | Equipment | 615 | 2022-05-02 | 23985 | keep | 0 | May | 2022 | 0.016336 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2022-05-02 12:30 | 2022-05-02 14:30 | 100 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN C/L MAL TIEMPO | C22050200188 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2022-05-02 | 12000 | keep | 0 | May | 2022 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-02 12:30 | 2022-05-03 15:30 | 50 | 027:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050200581 | New_Event | Bad Weather | Include | Include | Weather | 1620 | 2022-05-02 | 81000 | keep | 0 | May | 2022 | 0.055169 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-02 12:33 | 2022-05-02 14:30 | 50 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200587 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2022-05-02 | 5850 | keep | 0 | May | 2022 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-02 12:34 | 2022-05-02 16:42 | 16 | 004:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22050200190 | New_Event | Secondary Wire Down | Include | Include | Equipment | 248 | 2022-05-02 | 3968 | keep | 0 | May | 2022 | 0.0027026 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-05-02 12:45 | 2022-05-02 23:40 | 60 | 010:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 1 X 80 C/L SE SUBIO LINEA PRIMARIA | B22050200136 | New_Event | Wire Down | Include | Include | Equipment | 655 | 2022-05-02 | 39300 | keep | 0 | May | 2022 | 0.026767 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-02 12:46 | 2022-05-02 18:21 | 922 | 005:35 | T | CABLE SOTERRADO AVERIADO | DISPARO 1401-08 SE ABRIO DE MH-4 @ CAJAS SECAS VIEJAS QUEMADAS SIN CLIENTES CONECTADOS 100% EN SERVICIO | S22050200342 | New_Event | UG Cable Fault | Include | Include | Equipment | 335 | 2022-05-02 | 308870 | keep | 0 | May | 2022 | 0.21037 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-05-02 12:46 | 2022-05-02 17:35 | 135 | 004:49 | T | CABLE SOTERRADO AVERIADO | EL INTERRUPTOR DISPARO EN EL CAMPO Y NO SE VIO REFLEJADO EL CAMBIO DE ESTATUS EN SCADA Y TAMPOCO PERMITE OPERARLO POR SCADA. SE SECCIONALIZO Y SE CERRO EN EL CAMPO 20% EN SERVICIO 1401-08 LLEVA EL 1346-05 | S22050200342 | New_Event | UG Cable Fault | Include | Include | Equipment | 289 | 2022-05-02 | 39015 | keep | 0 | May | 2022 | 0.026573 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
HUMACAO | 2022-05-02 12:52 | 2022-05-02 14:54 | 1 | 002:02 | P | NO SE REPORTO CAUSA | 3 X 20 EN BANCO Y CAJAS PRIMARIAS | C22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-05-02 | 122 | keep | 0 | May | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-02 12:57 | 2022-05-03 12:58 | 100 | 024:01 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22050200572 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1441 | 2022-05-02 | 144100 | keep | 0 | May | 2022 | 0.098146 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-02 13:03 | 2022-05-02 15:14 | 10 | 002:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN XMR AVE | C22050200220 | New_Event |  |  | Include | Wildlife | 131 | 2022-05-02 | 1310 | keep | 0 | May | 2022 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-02 13:08 | 2022-05-02 13:44 | 3431 | 000:36 | T | NO SE REPORTO CAUSA | SE VERIFICO PERSONAL FUERA DE AREA Y SE CERRO INTERRUPTOR | A22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2022-05-02 | 123516 | keep | 0 | May | 2022 | 0.084126 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2022-05-02 13:10 | 2022-05-02 15:28 | 60 | 002:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L IGUANA | C22050200228 | New_Event |  |  | Include | Wildlife | 138 | 2022-05-02 | 8280 | keep | 0 | May | 2022 | 0.0056395 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-02 13:13 | 2022-05-02 15:09 | 65 | 001:56 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | S22050200344 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-05-02 | 7540 | keep | 0 | May | 2022 | 0.0051355 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-05-02 13:14 | 2022-05-02 14:14 | 411 | 001:00 | T | DESGANCHE | DISPARO DE INTERRUPTOR EL JORNEYMAN BRIAN JONES PATRULLO Y SOLICITO QUE SE CERRARA EL INTERRUPTOR INFORMO QUE TIENE AREAS QUE REQUIERE DESGANCHE | M22050200102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-05-02 | 24660 | keep | 0 | May | 2022 | 0.016796 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
YAUCO | 2022-05-02 13:15 | 2022-05-02 15:40 | 40 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | P22050200095 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2022-05-02 | 5800 | keep | 0 | May | 2022 | 0.0039504 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-02 13:19 | 2022-05-02 18:15 | 80 | 004:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22050200214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-05-02 | 23680 | keep | 0 | May | 2022 | 0.016128 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-05-02 13:20 | 2022-05-02 17:11 | 47 | 003:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA | C22050200232 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2022-05-02 | 10857 | keep | 0 | May | 2022 | 0.0073947 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2022-05-02 13:22 | 2022-05-02 18:58 | 20 | 005:36 | P | DESGANCHE | 1 X 30 C/ DESGANCHE | C22050200235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2022-05-02 | 6720 | keep | 0 | May | 2022 | 0.004577 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-05-02 13:24 | 2022-05-02 13:25 | 551 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C22050200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-02 | 551 | keep | 0 | May | 2022 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2022-05-02 13:25 | 2022-05-02 18:59 | 50 | 005:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 C/L CAJA PRIMARIA | C22050200321 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 334 | 2022-05-02 | 16700 | keep | 0 | May | 2022 | 0.011374 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-02 13:35 | 2022-05-02 22:48 | 25 | 009:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050200451 | New_Event | Bad Weather | Include | Include | Weather | 553 | 2022-05-02 | 13825 | keep | 0 | May | 2022 | 0.0094161 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-02 13:42 | 2022-05-02 16:38 | 122 | 002:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | SECCIONALIZAR POSTE PARTIDO DE ALUMBRADO QUE LLEVA LINEA DE PROVISIONAL IMPACTADO POR VEHCIULO. | S22050200371 | New_Event |  |  | Include | Wildlife | 176 | 2022-05-02 | 21472 | keep | 0 | May | 2022 | 0.014624 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
BAYAMON | 2022-05-02 13:44 | 2022-05-02 15:00 | 40 | 001:16 | P | DESGANCHE | 1 X 50 EN C/L 1 X 40 EN MONTURA SE REALIZO DESGANCHE | B22050200154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-05-02 | 3040 | keep | 0 | May | 2022 | 0.0020705 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-02 13:55 | 2022-05-02 14:02 | 2435 | 000:07 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO CABLE SOTERRADO AVERIADO | S22050200000 | New_Event | UG Cable Fault | Include | Include | Equipment | 7 | 2022-05-02 | 17045 | keep | 0 | May | 2022 | 0.011609 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
MAYAGÃœEZ | 2022-05-02 13:58 | 2022-05-02 23:05 | 30 | 009:07 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200711 | New_Event | Bad Weather | Include | Include | Weather | 547 | 2022-05-02 | 16410 | keep | 0 | May | 2022 | 0.011177 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-02 13:58 | 2022-05-04 14:28 | 20 | 048:30 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22050200711 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2910 | 2022-05-02 | 58200 | keep | 0 | May | 2022 | 0.03964 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-02 13:59 | 2022-05-02 18:15 | 50 | 004:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE LEVANTO CONDUCTOR | S22050200410 | New_Event | Wire Down | Include | Include | Equipment | 256 | 2022-05-02 | 12800 | keep | 0 | May | 2022 | 0.008718 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-02 14:08 | 2022-05-02 14:09 | 1078 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P22050200118 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-02 | 1078 | keep | 0 | May | 2022 | 0.00073422 | 0.00073422 | Momentary | FALSE | FALSE | Not_TMED_Event | 1078
PONCE | 2022-05-02 14:08 | 2022-05-02 14:09 | 2689 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO CARGA POR 5002-01 | P22050200118 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-02 | 2689 | keep | 0 | May | 2022 | 0.0018315 | 0.0018315 | Momentary | FALSE | FALSE | Not_TMED_Event | 2689
BAYAMON | 2022-05-02 14:09 | 2022-05-02 20:30 | 90 | 006:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B22050200173 | New_Event | Wire Down | Include | Include | Equipment | 381 | 2022-05-02 | 34290 | keep | 0 | May | 2022 | 0.023355 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2022-05-02 14:12 | 2022-05-02 14:13 | 1078 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22050200122 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-05-02 | 1078 | keep | 0 | May | 2022 | 0.00073422 | 0.00073422 | Momentary | FALSE | FALSE | Not_TMED_Event | 1078
PONCE | 2022-05-02 14:12 | 2022-05-02 14:13 | 2689 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO CARGA POR 5002-01 | P22050200122 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-05-02 | 2689 | keep | 0 | May | 2022 | 0.0018315 | 0.0018315 | Momentary | FALSE | FALSE | Not_TMED_Event | 2689
MAYAGÃœEZ | 2022-05-02 14:12 | 2022-05-02 14:48 | 100 | 000:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22050200733 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2022-05-02 | 3600 | keep | 0 | May | 2022 | 0.0024519 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-02 14:14 | 2022-05-02 14:18 | 30 | 000:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22050200008 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-05-02 | 120 | keep | 0 | May | 2022 | 8.1731e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-02 14:18 | 2022-05-02 20:22 | 60 | 006:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES LAJAS PERTENCE A YAUCO REGION DE PONCE EVENTOS SON P | P22050200121 | New_Event | Bad Weather | Include | Include | Weather | 364 | 2022-05-02 | 21840 | keep | 0 | May | 2022 | 0.014875 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-05-02 14:18 | 2022-05-02 17:03 | 12 | 002:45 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22050200271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-05-02 | 1980 | keep | 0 | May | 2022 | 0.0013486 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-05-02 14:19 | 2022-05-02 22:00 | 50 | 007:41 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22050200175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 461 | 2022-05-02 | 23050 | keep | 0 | May | 2022 | 0.015699 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-02 14:22 | 2022-05-02 16:08 | 200 | 001:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22050200508 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2022-05-02 | 21200 | keep | 0 | May | 2022 | 0.014439 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-05-02 14:27 | 2022-05-02 20:22 | 10 | 005:55 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | R22050200133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2022-05-02 | 3550 | keep | 0 | May | 2022 | 0.0024179 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-05-02 14:33 | 2022-05-03 09:01 | 1 | 018:28 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22050200279 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1108 | 2022-05-02 | 1108 | keep | 0 | May | 2022 | 0.00075465 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-02 14:33 | 2022-05-02 20:20 | 125 | 005:47 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA INDICA REQUIERE DESGANCHE | A22050200518 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2022-05-02 | 43375 | keep | 0 | May | 2022 | 0.029543 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
PONCE | 2022-05-02 14:37 | 2022-05-02 14:38 | 1078 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22050200132 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-05-02 | 1078 | keep | 0 | May | 2022 | 0.00073422 | 0.00073422 | Momentary | FALSE | FALSE | Not_TMED_Event | 1078
PONCE | 2022-05-02 14:37 | 2022-05-02 14:38 | 2689 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO CARGA POR 5002-01 | P22050200132 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-05-02 | 2689 | keep | 0 | May | 2022 | 0.0018315 | 0.0018315 | Momentary | FALSE | FALSE | Not_TMED_Event | 2689
MAYAGÃœEZ | 2022-05-02 14:47 | 2022-05-02 17:55 | 150 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200770 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2022-05-02 | 28200 | keep | 0 | May | 2022 | 0.019207 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-02 14:49 | 2022-05-02 21:30 | 100 | 006:41 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 80 Y 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200771 | New_Event | Bad Weather | Include | Include | Weather | 401 | 2022-05-02 | 40100 | keep | 0 | May | 2022 | 0.027312 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-02 14:58 | 2022-05-02 15:11 | 60 | 000:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200546 | New_Event | Bad Weather | Include | Include | Weather | 13 | 2022-05-02 | 780 | keep | 0 | May | 2022 | 0.00053125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-05-02 15:01 | 2022-05-02 16:58 | 1078 | 001:57 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE INTERRUPTOR DEBIDO A OPERACIONES DE RECIERRE SE REMOVIO IGUANA CRUZANDO CAJA PRIMARIA | P22050200140 | 1st_after_momentary |  |  | Include | Wildlife | 117 | 2022-05-02 | 126126 | keep | 0 | May | 2022 | 0.085904 | 0.00073422 | Sustained | FALSE | FALSE | Not_TMED_Event | 1078
PONCE | 2022-05-02 15:01 | 2022-05-02 16:58 | 2689 | 001:57 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE INTERRUPTOR DEBIDO A OPERACIONES DE RECIERRE CON CARGA DEL 5002-03 | P22050200140 | 1st_after_momentary |  |  | Include | Wildlife | 117 | 2022-05-02 | 314613 | keep | 0 | May | 2022 | 0.21428 | 0.0018315 | Sustained | FALSE | FALSE | Not_TMED_Event | 2689
MAYAGÃœEZ | 2022-05-02 15:06 | 2022-05-03 01:54 | 15 | 010:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 Y 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200088 | New_Event | Bad Weather | Include | Include | Weather | 648 | 2022-05-02 | 9720 | keep | 0 | May | 2022 | 0.0066202 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-05-02 15:06 | 2022-05-02 16:30 | 100 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200562 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2022-05-02 | 8400 | keep | 0 | May | 2022 | 0.0057212 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-05-02 15:08 | 2022-05-02 21:55 | 100 | 006:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRAR PUENTE ABIERTO | C22050200300 | New_Event | Wire Down | Include | Include | Equipment | 407 | 2022-05-02 | 40700 | keep | 0 | May | 2022 | 0.027721 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-02 15:10 | 2022-05-03 06:32 | 15 | 015:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22050200304 | New_Event | Secondary Wire Down | Include | Include | Equipment | 922 | 2022-05-02 | 13830 | keep | 0 | May | 2022 | 0.0094196 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-02 15:13 | 2022-05-02 17:00 | 1626 | 001:47 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR 45% EN SERVICIO ADICIONAL | S22050200000 | New_Event | UG Cable Fault | Include | Include | Equipment | 107 | 2022-05-02 | 173982 | keep | 0 | May | 2022 | 0.1185 | 0.0011075 | Sustained | FALSE | FALSE | Not_TMED_Event | 1626
UTUADO | 2022-05-02 15:18 | 2022-05-02 19:10 | 30 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200576 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2022-05-02 | 6960 | keep | 0 | May | 2022 | 0.0047404 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-05-02 15:30 | 2022-05-02 16:39 | 1 | 001:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJAS EN MONTURA PARA FIJAR BAJANTE PRIMARIO EN MONTURA TRIFASICA | P22050200156 | New_Event | Wire Down | Include | Include | Equipment | 69 | 2022-05-02 | 69 | keep | 0 | May | 2022 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-02 15:35 | 2022-05-02 22:25 | 110 | 006:50 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTES DE LINEA | C22050200316 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 410 | 2022-05-02 | 45100 | keep | 0 | May | 2022 | 0.030717 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
SAN JUAN | 2022-05-02 15:39 | 2022-05-03 15:24 | 30 | 023:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA Y 1 X 65 EN RISER SE REMPLAZO PORTAFUSIBLE | S22050200514 | New_Event | Cutout Failure | Include | Include | Equipment | 1425 | 2022-05-02 | 42750 | keep | 0 | May | 2022 | 0.029117 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-02 15:56 | 2022-05-03 09:00 | 150 | 017:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22050200870 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1024 | 2022-05-02 | 153600 | keep | 0 | May | 2022 | 0.10462 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-05-02 16:14 | 2022-05-02 20:20 | 25 | 004:06 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22050200141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2022-05-02 | 6150 | keep | 0 | May | 2022 | 0.0041887 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-05-02 16:18 | 2022-05-02 17:19 | 35 | 001:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22050200191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-05-02 | 2135 | keep | 0 | May | 2022 | 0.0014541 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-05-02 16:29 | 2022-05-02 16:58 | 4 | 000:29 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22050200143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 29 | 2022-05-02 | 116 | keep | 0 | May | 2022 | 7.9007e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-02 16:33 | 2022-05-02 16:34 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 390 | keep | 0 | May | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
MAYAGÃœEZ | 2022-05-02 16:35 | 2022-05-02 19:40 | 65 | 003:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22050200927 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-05-02 | 12025 | keep | 0 | May | 2022 | 0.0081902 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-05-02 16:36 | 2022-05-02 18:49 | 10 | 002:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 XMR PORTAFUSIBLES | R22050200144 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2022-05-02 | 1330 | keep | 0 | May | 2022 | 0.00090586 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-02 16:38 | 2022-05-02 19:00 | 60 | 002:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | SECCIONALIZAR POSTE PARTIDO DE ALUMBRADO QUE LLEVA LINEA DE PROVISIONAL IMPACTADO POR VEHCIULO. | S22050200371 | Partial_restoration |  |  | Include | Wildlife | 142 | 2022-05-02 | 8520 | keep | 0 | May | 2022 | 0.0058029 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-02 16:44 | 2022-05-02 16:45 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
BAYAMON | 2022-05-02 17:00 | 2022-05-02 19:15 | 148 | 002:15 | P | CABLE SOTERRADO AVERIADO | EN VS DE MH-3 SE SECCIONALIZO TRAMO DEL VS @ RISER Y SE CERRO MACHETES 100% EN SERVICIO | S22050200000 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 135 | 2022-05-02 | 19980 | keep | 0 | May | 2022 | 0.013608 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-02 17:00 | 2022-05-03 18:23 | 100 | 025:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN RISER SE REPARO LINEAS PRIMARIAS CRUZADAS CLIENTE SIN SERVICIO Y EVENTO DEL DIA 2 DE MAYO DE 2022 | M22050300259 | New_Event | Wire Down | Include | Include | Equipment | 1523 | 2022-05-02 | 152300 | keep | 0 | May | 2022 | 0.10373 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-02 17:03 | 2022-05-03 11:30 | 30 | 018:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M22050200958 | New_Event | Bad Weather | Include | Include | Weather | 1107 | 2022-05-02 | 33210 | keep | 0 | May | 2022 | 0.022619 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-02 17:05 | 2022-05-03 14:58 | 20 | 021:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050200961 | New_Event | Bad Weather | Include | Include | Weather | 1313 | 2022-05-02 | 26260 | keep | 0 | May | 2022 | 0.017886 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-02 17:07 | 2022-05-03 04:30 | 60 | 011:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050200966 | New_Event | Vegetation Contact | Include | Include | Vegetation | 683 | 2022-05-02 | 40980 | keep | 0 | May | 2022 | 0.027911 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-02 17:08 | 2022-05-02 21:30 | 150 | 004:22 | P | DESGANCHE | 2 X 65 2 X 40 Y 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22050200969 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-05-02 | 39300 | keep | 0 | May | 2022 | 0.026767 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-05-02 17:08 | 2022-05-02 20:20 | 2 | 003:12 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | A22050200688 | New_Event | Switch Failure | Include | Include | Equipment | 192 | 2022-05-02 | 384 | keep | 0 | May | 2022 | 0.00026154 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-05-02 17:10 | 2022-05-02 21:10 | 32 | 004:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R22050200146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2022-05-02 | 7680 | keep | 0 | May | 2022 | 0.0052308 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
ARECIBO | 2022-05-02 17:11 | 2022-05-02 17:12 | 1066 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 1066 | keep | 0 | May | 2022 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
UTUADO | 2022-05-02 17:25 | 2022-05-02 18:30 | 40 | 001:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200728 | New_Event | Bad Weather | Include | Include | Weather | 65 | 2022-05-02 | 2600 | keep | 0 | May | 2022 | 0.0017708 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-02 17:29 | 2022-05-03 08:20 | 8 | 014:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO BARRAS EN PEDESTAL | C22050200353 | New_Event | Secondary Wire Down | Include | Include | Equipment | 891 | 2022-05-02 | 7128 | keep | 0 | May | 2022 | 0.0048548 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-02 17:35 | 2022-05-02 18:21 | 108 | 000:46 | P | CABLE SOTERRADO AVERIADO | SE ABRIO DE MH-4 @ CAJAS SECAS VIEJAS QUEMADAS SIN CLIENTES CONECTADOS 100% EN SERVICIO | S22050200342 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 46 | 2022-05-02 | 4968 | keep | 0 | May | 2022 | 0.0033837 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-02 17:35 | 2022-05-03 03:43 | 30 | 010:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050200997 | New_Event | Bad Weather | Include | Include | Weather | 608 | 2022-05-02 | 18240 | keep | 0 | May | 2022 | 0.012423 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-02 17:41 | 2022-05-03 13:07 | 30 | 019:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050200718 | New_Event | Bad Weather | Include | Include | Weather | 1166 | 2022-05-02 | 34980 | keep | 0 | May | 2022 | 0.023825 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-02 17:45 | 2022-05-02 19:15 | 10 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR SE REPARO SECUNDARIA | C22050200174 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-05-02 | 900 | keep | 0 | May | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-02 17:57 | 2022-05-03 16:41 | 7 | 022:44 | P | SECUNDARIA/DESGANCHE | SE ABRE MONTURA PARA REPARAR BAJANTE Y DESGANCHE SECUNDARIO | S22050200597 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1364 | 2022-05-02 | 9548 | keep | 0 | May | 2022 | 0.0065031 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-05-02 18:31 | 2022-05-02 22:15 | 40 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 20 EN TRANSFORMADOR SE DESENRREDO SECUNDARIA | P22050200254 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2022-05-02 | 8960 | keep | 0 | May | 2022 | 0.0061026 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-02 18:31 | 2022-05-02 20:20 | 50 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200581 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2022-05-02 | 5450 | keep | 0 | May | 2022 | 0.003712 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-02 18:31 | 2022-05-02 20:00 | 30 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200748 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2022-05-02 | 2670 | keep | 0 | May | 2022 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-05-02 18:32 | 2022-05-03 14:40 | 60 | 020:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200749 | New_Event | Bad Weather | Include | Include | Weather | 1208 | 2022-05-02 | 72480 | keep | 0 | May | 2022 | 0.049366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-02 18:37 | 2022-05-02 19:52 | 50 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050200752 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2022-05-02 | 3750 | keep | 0 | May | 2022 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-02 18:45 | 2022-05-03 11:35 | 60 | 016:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M22050201056 | New_Event | Bad Weather | Include | Include | Weather | 1010 | 2022-05-02 | 60600 | keep | 0 | May | 2022 | 0.041274 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-05-02 18:57 | 2022-05-03 10:22 | 257 | 015:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DELINEA Y SE REPARO NETRAL DE LINEA PRIMARIA | B22050200286 | New_Event | Wire Down | Include | Include | Equipment | 925 | 2022-05-02 | 237725 | keep | 0 | May | 2022 | 0.16191 | 0.00017504 | Sustained | FALSE | FALSE | Not_TMED_Event | 257
SAN JUAN | 2022-05-02 19:00 | 2022-05-02 19:26 | 122 | 000:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | SECCIONALIZAR POSTE PARTIDO DE ALUMBRADO QUE LLEVA LINEA DE PROVISIONAL IMPACTADO POR VEHCIULO. | S22050200371 | Additional_clients |  |  | Include | Wildlife | 26 | 2022-05-02 | 3172 | keep | 0 | May | 2022 | 0.0021604 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-02 19:03 | 2022-05-02 20:58 | 10 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE POR AVE | S22050200622 | New_Event |  |  | Include | Wildlife | 115 | 2022-05-02 | 1150 | keep | 0 | May | 2022 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-02 19:10 | 2022-05-02 22:56 | 300 | 003:46 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO Y CAJA QUEMADA | C22050200362 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 226 | 2022-05-02 | 67800 | keep | 0 | May | 2022 | 0.046178 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2022-05-02 19:12 | 2022-05-02 20:25 | 150 | 001:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050200768 | New_Event | Bad Weather | Include | Include | Weather | 73 | 2022-05-02 | 10950 | keep | 0 | May | 2022 | 0.007458 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-05-02 19:23 | 2022-05-03 15:30 | 30 | 020:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIAS ROTAS ESTE EVENTO NO TENGO EN BITOCORA A JOSE VELEZ CON ORDENES | A22050200774 | New_Event | Wire Down | Include | Include | Equipment | 1207 | 2022-05-02 | 36210 | keep | 0 | May | 2022 | 0.024662 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-05-02 19:23 | 2022-05-03 20:34 | 30 | 025:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | A22050200774 | New_Event | Wire Down | Include | Include | Equipment | 1511 | 2022-05-02 | 45330 | keep | 0 | May | 2022 | 0.030874 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-02 19:31 | 2022-05-03 12:34 | 70 | 017:03 | P | NO SE REPORTO CAUSA | 2 X 80 Y 1 X 65 EN DIFERENTES CORTES DE LINEA | M22050201090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1023 | 2022-05-02 | 71610 | keep | 0 | May | 2022 | 0.048773 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2022-05-02 19:38 | 2022-05-03 07:20 | 6 | 011:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA AVERIADA Y PARARRAYO | C22050200369 | New_Event | Cutout Failure | Include | Include | Equipment | 702 | 2022-05-02 | 4212 | keep | 0 | May | 2022 | 0.0028688 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-05-02 19:43 | 2022-05-02 22:00 | 20 | 002:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22050200787 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-05-02 | 2740 | keep | 0 | May | 2022 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-02 19:57 | 2022-05-03 06:56 | 30 | 010:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | C22050200376 | New_Event | Cutout Failure | Include | Include | Equipment | 659 | 2022-05-02 | 19770 | keep | 0 | May | 2022 | 0.013465 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-05-02 20:04 | 2022-05-03 11:10 | 40 | 015:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 65 EN CORTES DE LINEAS MAL TIEMPO VIENTOS FUERTES | A22050200801 | New_Event | Bad Weather | Include | Include | Weather | 906 | 2022-05-02 | 36240 | keep | 0 | May | 2022 | 0.024683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-05-02 20:09 | 2022-05-02 22:00 | 60 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050200802 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2022-05-02 | 6660 | keep | 0 | May | 2022 | 0.0045361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-05-02 20:21 | 2022-05-03 08:48 | 15 | 012:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050200809 | New_Event | Bad Weather | Include | Include | Weather | 747 | 2022-05-02 | 11205 | keep | 0 | May | 2022 | 0.0076317 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-05-02 20:38 | 2022-05-02 20:39 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22050200299 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 2113 | keep | 0 | May | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
MAYAGÃœEZ | 2022-05-02 20:38 | 2022-05-03 00:54 | 60 | 004:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050201157 | New_Event | Bad Weather | Include | Include | Weather | 256 | 2022-05-02 | 15360 | keep | 0 | May | 2022 | 0.010462 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-02 20:43 | 2022-05-03 17:20 | 10 | 020:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050201162 | New_Event | Bad Weather | Include | Include | Weather | 1237 | 2022-05-02 | 12370 | keep | 0 | May | 2022 | 0.0084252 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-02 20:57 | 2022-05-03 16:42 | 6 | 019:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO SECUNDARIA | C22050200384 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1185 | 2022-05-02 | 7110 | keep | 0 | May | 2022 | 0.0048426 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-02 21:02 | 2022-05-02 22:14 | 31 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | CAMION SE LLEVO SECUNDARIA SE REPARO SECUNDARIA | S22050200633 | New_Event |  |  | Include | Wildlife | 72 | 2022-05-02 | 2232 | keep | 0 | May | 2022 | 0.0015202 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2022-05-02 21:12 | 2022-05-03 00:30 | 10 | 003:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE ABRIO PUENTES PARA SECCIONALIZAR CONDUCTOR Y POSTE EN EL SUELO QUEDARON 2 CLIENTES SIN SERVICIO | B22050200049 | New_Event | Wire Down | Include | Include | Equipment | 198 | 2022-05-02 | 1980 | keep | 0 | May | 2022 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-02 21:25 | 2022-05-03 05:40 | 51 | 008:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050201187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 495 | 2022-05-02 | 25245 | keep | 0 | May | 2022 | 0.017194 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
ARECIBO | 2022-05-02 21:27 | 2022-05-03 08:37 | 8 | 011:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22050200820 | New_Event | Bad Weather | Include | Include | Weather | 670 | 2022-05-02 | 5360 | keep | 0 | May | 2022 | 0.0036507 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-05-02 21:39 | 2022-05-02 22:42 | 130 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P22050200326 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-05-02 | 8190 | keep | 0 | May | 2022 | 0.0055782 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
UTUADO | 2022-05-02 21:51 | 2022-05-02 22:17 | 15 | 000:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22050200825 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2022-05-02 | 390 | keep | 0 | May | 2022 | 0.00026563 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-05-02 22:02 | 2022-05-02 22:03 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 4702 | keep | 0 | May | 2022 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
CANOVANAS | 2022-05-02 22:04 | 2022-05-02 22:05 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 4188 | keep | 0 | May | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
MAYAGÃœEZ | 2022-05-02 22:06 | 2022-05-03 07:37 | 30 | 009:31 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050201209 | New_Event | Bad Weather | Include | Include | Weather | 571 | 2022-05-02 | 17130 | keep | 0 | May | 2022 | 0.011667 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-05-02 22:16 | 2022-05-02 22:17 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22050200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 4702 | keep | 0 | May | 2022 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
SAN JUAN | 2022-05-02 22:20 | 2022-05-03 15:04 | 1 | 016:44 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R22050200171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1004 | 2022-05-02 | 1004 | keep | 0 | May | 2022 | 0.00068382 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-02 22:23 | 2022-05-02 23:10 | 1483 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1336-08 PROBO MALO SE ESPERO Y SE VOLVIO A CERRAR Y SE QUEDO EN SERVICIO LLEVA 30% DEL 1204-04 | S22050200643 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2022-05-02 | 69701 | keep | 0 | May | 2022 | 0.047473 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-02 22:23 | 2022-05-02 23:10 | 1000 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1336-08 PROBO MALO SE ESPERO Y SE VOLVIO A CERRAR Y SE QUEDO EN SERVICIO LLEVA PARTE DEL 1204-05 | S22050200643 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2022-05-02 | 47000 | keep | 0 | May | 2022 | 0.032011 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-05-02 22:23 | 2022-05-02 23:10 | 4900 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO PROBO MALO SE ESPERO Y SE VOLVIO A CERRAR Y SE QUEDO EN SERVICIO. PARTE DEL 1336-08 POR 1424-08 Y LLEVA 1336-09, PARTE DEL 1204-05 Y 30% DEL 1204-04 | S22050200643 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2022-05-02 | 230300 | keep | 0 | May | 2022 | 0.15686 | 0.0033374 | Sustained | FALSE | FALSE | Not_TMED_Event | 4900
SAN JUAN | 2022-05-02 22:23 | 2022-05-02 23:10 | 207 | 000:47 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1336-08 PROBO MALO SE ESPERO Y SE VOLVIO A CERRAR Y SE QUEDO EN SERVICIO LLEVA 1336-09 | S22050200643 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2022-05-02 | 9729 | keep | 0 | May | 2022 | 0.0066264 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
CANOVANAS | 2022-05-02 22:28 | 2022-05-02 22:29 | 424 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 424 | keep | 0 | May | 2022 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
VEGA BAJA | 2022-05-02 22:29 | 2022-05-03 16:31 | 34 | 018:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L AVE CRUZO LINEAS | B22050200342 | New_Event |  |  | Include | Wildlife | 1082 | 2022-05-02 | 36788 | keep | 0 | May | 2022 | 0.025056 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
VEGA BAJA | 2022-05-02 22:34 | 2022-05-02 22:35 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 1310 | keep | 0 | May | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-05-02 22:41 | 2022-05-03 17:56 | 75 | 019:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22050200345 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1155 | 2022-05-02 | 86625 | keep | 0 | May | 2022 | 0.059 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-05-02 22:42 | 2022-05-02 22:43 | 1000 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1206-03 LLEVA PARTE DEL 1204-05 | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 1000 | keep | 0 | May | 2022 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-05-02 22:42 | 2022-05-02 22:43 | 3900 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE PARTE POR 1620-05 PERO LLEVA PARTE DEL 1204-05 | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 3900 | keep | 0 | May | 2022 | 0.0026563 | 0.0026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 3900
CANOVANAS | 2022-05-02 23:04 | 2022-05-03 15:52 | 50 | 016:48 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | R22050200185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1008 | 2022-05-02 | 50400 | keep | 0 | May | 2022 | 0.034327 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-02 23:15 | 2022-05-02 23:16 | 500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA 1620-05 QUE LLEVA PARTE DEL 1206-03 | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 500 | keep | 0 | May | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-05-02 23:15 | 2022-05-02 23:16 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA 1620-05 QUE LLEVA PARTE DEL 1206-03 | S22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 1615 | keep | 0 | May | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
UTUADO | 2022-05-02 23:16 | 2022-05-03 19:28 | 25 | 020:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A22050200833 | New_Event | Wire Down | Include | Include | Equipment | 1212 | 2022-05-02 | 30300 | keep | 0 | May | 2022 | 0.020637 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-02 23:32 | 2022-05-03 14:00 | 10 | 014:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA ARBOL SOBRE LINEA Y SE FIJO FASE | S22050200763 | New_Event | Vegetation Contact | Include | Include | Vegetation | 868 | 2022-05-02 | 8680 | keep | 0 | May | 2022 | 0.0059119 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-02 23:32 | 2022-05-03 12:15 | 50 | 012:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE DE RAMAS | R22050200190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 763 | 2022-05-02 | 38150 | keep | 0 | May | 2022 | 0.025984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-02 23:34 | 2022-05-02 23:35 | 1210 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-02 | 1210 | keep | 0 | May | 2022 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
BAYAMON | 2022-05-02 23:37 | 2022-05-03 03:10 | 10 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22050200351 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2022-05-02 | 2130 | keep | 0 | May | 2022 | 0.0014507 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-02 23:40 | 2022-05-02 23:41 | 2735 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLUVIA Y VIENTO FUERTE | B22050200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-02 | 2735 | keep | 0 | May | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
MAYAGÃœEZ | 2022-05-02 23:47 | 2022-05-03 01:23 | 30 | 001:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050201230 | New_Event | Bad Weather | Include | Include | Weather | 96 | 2022-05-02 | 2880 | keep | 0 | May | 2022 | 0.0019616 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-03 00:05 | 2022-05-03 00:07 | 3115 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE 1710-05, 40% DE ESTE ESTA POR EL 1718-03 | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 6230 | keep | 0 | May | 2022 | 0.0042432 | 0.0021216 | Momentary | FALSE | FALSE | Not_TMED_Event | 3115
BAYAMON | 2022-05-03 00:05 | 2022-05-03 00:06 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 3511 | keep | 0 | May | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2022-05-03 00:08 | 2022-05-03 14:34 | 71 | 014:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22050300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 866 | 2022-05-03 | 61486 | keep | 0 | May | 2022 | 0.041878 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
BAYAMON | 2022-05-03 00:11 | 2022-05-03 04:00 | 5961 | 003:49 | T | MAL TIEMPO/RAYOS/WET ASH | SE SECCIONALIZO Y SE CERRO POR SCADA ENTRO 30% DEL 1713-05 Y ENTRO LA CARGA DEL 1717-02 (95%) | B22050300005 | New_Event | Bad Weather | Include | Include | Weather | 229 | 2022-05-03 | 1365069 | keep | 0 | May | 2022 | 0.92974 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-05-03 00:11 | 2022-05-03 04:00 | 865 | 003:49 | P | MAL TIEMPO/RAYOS/WET ASH | SE SECCIONALIZO 1713-05 Y SE CERRO POR SCADA ENTRO 30% DEL 1713-05 Y ENTRO LA CARGA DEL 1717-02 (95%) | B22050300005 | New_Event | Bad Weather | Include | Include | Weather | 229 | 2022-05-03 | 198085 | keep | 0 | May | 2022 | 0.13491 | 0.00058915 | Sustained | FALSE | FALSE | Not_TMED_Event | 865
VEGA BAJA | 2022-05-03 00:11 | 2022-05-03 03:05 | 215 | 002:54 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL LLUVIA Y VIENTO FUERTE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2022-05-03 | 37410 | keep | 0 | May | 2022 | 0.02548 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2022-05-03 00:15 | 2022-05-03 00:16 | 259 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 259 | keep | 0 | May | 2022 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2022-05-03 00:20 | 2022-05-03 00:24 | 738 | 000:04 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1346-02 Y SE CERRO POR SCADA 60% DE ESTE POR 1529-15 PERO LLEVA 30 % DEL 1346-03 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2022-05-03 | 2952 | keep | 0 | May | 2022 | 0.0020106 | 0.00050265 | Momentary | FALSE | FALSE | Not_TMED_Event | 738
SAN JUAN | 2022-05-03 00:20 | 2022-05-03 00:24 | 727 | 000:04 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1346-02 Y SE CERRO POR SCADA 60% DE ESTE POR 1529-15 PERO LLEVA 30 % DEL 1346-03 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2022-05-03 | 2908 | keep | 0 | May | 2022 | 0.0019806 | 0.00049516 | Momentary | FALSE | FALSE | Not_TMED_Event | 727
CANOVANAS | 2022-05-03 00:31 | 2022-05-03 10:58 | 366 | 010:27 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO DE BAMBUAS | R22050300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 627 | 2022-05-03 | 229482 | keep | 0 | May | 2022 | 0.1563 | 0.00024928 | Sustained | FALSE | FALSE | Not_TMED_Event | 366
ARECIBO | 2022-05-03 00:40 | 2022-05-03 12:28 | 10 | 011:48 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZAR TRANSFORMADOR DE 25KVA POR UNO DE 25KVA | A22050300003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 708 | 2022-05-03 | 7080 | keep | 0 | May | 2022 | 0.0048222 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-05-03 00:42 | 2022-05-03 00:43 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE MAL TIEMPO | C22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 181 | keep | 0 | May | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
BAYAMON | 2022-05-03 00:52 | 2022-05-03 00:54 | 222 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO Y QUEDO FUERA 1907-03. SE CERRO POR SCADA LLEVA 1909-09 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 444 | keep | 0 | May | 2022 | 0.00030241 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-05-03 00:52 | 2022-05-03 00:54 | 4456 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO Y QUEDO FUERA 1907-03. SE CERRO POR SCADA LLEVA 1909-09 | S22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-03 | 8912 | keep | 0 | May | 2022 | 0.0060699 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
VEGA BAJA | 2022-05-03 00:57 | 2022-05-03 18:17 | 10 | 017:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE POR AVE | B22050300077 | New_Event |  |  | Include | Wildlife | 1040 | 2022-05-03 | 10400 | keep | 0 | May | 2022 | 0.0070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-03 01:00 | 2022-05-03 01:01 | 316 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22050300004 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-03 | 316 | keep | 0 | May | 2022 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2022-05-03 01:01 | 2022-05-03 13:22 | 150 | 012:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22050300005 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 741 | 2022-05-03 | 111150 | keep | 0 | May | 2022 | 0.075704 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-03 01:05 | 2022-05-03 01:06 | 679 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 679 | keep | 0 | May | 2022 | 0.00046246 | 0.00046246 | Momentary | FALSE | FALSE | Not_TMED_Event | 679
BAYAMON | 2022-05-03 01:05 | 2022-05-03 01:06 | 541 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 541 | keep | 0 | May | 2022 | 0.00036847 | 0.00036847 | Momentary | FALSE | FALSE | Not_TMED_Event | 541
MAYAGÃœEZ | 2022-05-03 01:07 | 2022-05-03 02:04 | 28 | 000:57 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA EMPLEADO DE CAMPO NO ENCONTRO CAUSA | M22050300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-05-03 | 1596 | keep | 0 | May | 2022 | 0.001087 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2022-05-03 01:12 | 2022-05-03 02:27 | 20 | 001:15 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LNEA SE REMPLAZO 2 PARARRAYOS | S22050300034 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 75 | 2022-05-03 | 1500 | keep | 0 | May | 2022 | 0.0010216 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-03 01:34 | 2022-05-03 01:38 | 89 | 000:04 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1011-05 Y SE CERRO POR SCADA LLEVA 75% DEL 1011-02 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2022-05-03 | 356 | keep | 0 | May | 2022 | 0.00024247 | 6.0617e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 89
BAYAMON | 2022-05-03 01:34 | 2022-05-03 01:38 | 719 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1011-05 Y SE CERRO POR SCADA LLEVA 75% DEL 1011-02 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2022-05-03 | 2876 | keep | 0 | May | 2022 | 0.0019588 | 0.00048971 | Momentary | FALSE | FALSE | Not_TMED_Event | 719
BAYAMON | 2022-05-03 01:34 | 2022-05-03 01:35 | 2076 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 SE CERRO POR SCADA | B22050300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-03 | 2076 | keep | 0 | May | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-05-03 01:34 | 2022-05-03 01:35 | 2605 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 2605 | keep | 0 | May | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-05-03 01:48 | 2022-05-03 01:50 | 2234 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL LLUVIA Y VIENTO FUERTE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 4468 | keep | 0 | May | 2022 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BARRANQUITAS | 2022-05-03 01:50 | 2022-05-03 11:06 | 54 | 009:16 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHO Y ELIMINO PARARRAYO | C22050300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 556 | 2022-05-03 | 30024 | keep | 0 | May | 2022 | 0.020449 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BAYAMON | 2022-05-03 02:01 | 2022-05-03 02:02 | 878 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLUVIA Y VIENTO FUERTE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 878 | keep | 0 | May | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2022-05-03 02:04 | 2022-05-03 02:05 | 679 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | B22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 679 | keep | 0 | May | 2022 | 0.00046246 | 0.00046246 | Momentary | FALSE | FALSE | Not_TMED_Event | 679
BAYAMON | 2022-05-03 02:04 | 2022-05-03 02:05 | 622 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 622 | keep | 0 | May | 2022 | 0.00042364 | 0.00042364 | Momentary | FALSE | FALSE | Not_TMED_Event | 622
SAN JUAN | 2022-05-03 02:05 | 2022-05-03 02:07 | 929 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1414-04 Y SE CERRO POR SCADA LLEVA 1421-03 Y 1421-04 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 1858 | keep | 0 | May | 2022 | 0.0012655 | 0.00063274 | Momentary | FALSE | FALSE | Not_TMED_Event | 929
SAN JUAN | 2022-05-03 02:05 | 2022-05-03 02:07 | 533 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1414-04 Y SE CERRO POR SCADA LLEVA 1421-03 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 1066 | keep | 0 | May | 2022 | 0.00072605 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
SAN JUAN | 2022-05-03 02:05 | 2022-05-03 02:07 | 451 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1414-04 Y SE CERRO POR SCADA LLEVA 1421-04 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 902 | keep | 0 | May | 2022 | 0.00061435 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
HUMACAO | 2022-05-03 02:07 | 2022-05-03 02:08 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE MAL TIEMPO | C22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 2450 | keep | 0 | May | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
SAN JUAN | 2022-05-03 02:09 | 2022-05-03 02:10 | 2203 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 2203 | keep | 0 | May | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-05-03 02:09 | 2022-05-03 02:10 | 3957 | 000:01 | T | DESGANCHE | DISPARO SE CERRO POR CONTROL | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-03 | 3957 | keep | 0 | May | 2022 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2022-05-03 02:10 | 2022-05-03 02:12 | 1983 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 3966 | keep | 0 | May | 2022 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-05-03 02:10 | 2022-05-03 02:12 | 500 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL LLUVIA Y VIENTO FUERTE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 1000 | keep | 0 | May | 2022 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-05-03 02:10 | 2022-05-03 02:12 | 186 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL LLUVIA Y VIENTO FUERTE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 372 | keep | 0 | May | 2022 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
ARECIBO | 2022-05-03 02:10 | 2022-05-03 10:37 | 60 | 008:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300011 | New_Event | Bad Weather | Include | Include | Weather | 507 | 2022-05-03 | 30420 | keep | 0 | May | 2022 | 0.020719 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-05-03 02:11 | 2022-05-03 02:12 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22050300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 3041 | keep | 0 | May | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BAYAMON | 2022-05-03 02:16 | 2022-05-03 02:17 | 878 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLUVIA Y VIENTO FUERTE | B2205030000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 878 | keep | 0 | May | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2022-05-03 02:19 | 2022-05-03 02:34 | 1501 | 000:15 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA MAL TIEMPO | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 15 | 2022-05-03 | 22515 | keep | 0 | May | 2022 | 0.015335 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-05-03 02:20 | 2022-05-03 02:34 | 1501 | 000:14 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 14 | 2022-05-03 | 21014 | keep | 0 | May | 2022 | 0.014313 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-05-03 02:20 | 2022-05-03 02:21 | 686 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 686 | keep | 0 | May | 2022 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
BAYAMON | 2022-05-03 02:23 | 2022-05-03 02:29 | 199 | 000:06 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 6 | 2022-05-03 | 1194 | keep | 0 | May | 2022 | 0.00081323 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2022-05-03 02:24 | 2022-05-03 02:30 | 295 | 000:06 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 6 | 2022-05-03 | 1770 | keep | 0 | May | 2022 | 0.0012055 | 0.00020092 | Sustained | FALSE | FALSE | Not_TMED_Event | 295
BAYAMON | 2022-05-03 02:24 | 2022-05-03 02:25 | 6136 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | B22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 6136 | keep | 0 | May | 2022 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
SAN JUAN | 2022-05-03 02:27 | 2022-05-03 02:30 | 858 | 000:03 | P | DESGANCHE | DISPARO 1303-02 SE CERRO POR CONTROL LLEVA 20% DEL 1204-02 | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-05-03 | 2574 | keep | 0 | May | 2022 | 0.0017531 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-03 02:27 | 2022-05-03 02:30 | 600 | 000:03 | P | DESGANCHE | DISPARO 1303-02 SE CERRO POR CONTROL LLEVA 60AMP DEL 1206-04 | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-05-03 | 1800 | keep | 0 | May | 2022 | 0.001226 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-05-03 02:27 | 2022-05-03 02:31 | 1681 | 000:04 | T | DESGANCHE | DISPARO 1303-04 SE CERRO POR CONTROL LLEVA 1303-01 | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-05-03 | 6724 | keep | 0 | May | 2022 | 0.0045797 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-03 02:27 | 2022-05-03 02:30 | 1948 | 000:03 | P | DESGANCHE | DISPARO SE CERRO POR CONTROL LLEVA 60A POR 1206-04 Y LLEVA 20% DEL 1204-02 | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-05-03 | 5844 | keep | 0 | May | 2022 | 0.0039803 | 0.0013268 | Momentary | FALSE | FALSE | Not_TMED_Event | 1948
SAN JUAN | 2022-05-03 02:27 | 2022-05-03 02:31 | 1598 | 000:04 | T | DESGANCHE | DISPARO 1303-04 SE CERRO POR CONTROL LLEVA 1346-06 | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-05-03 | 6392 | keep | 0 | May | 2022 | 0.0043536 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2022-05-03 02:29 | 2022-05-03 13:12 | 3 | 010:43 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 25 EN SUB ARBYS 3 X 40 EN RISER PARTY CITY 3 X 30 EN RISER Y 3 X 25 EN SUB Y 4 X 5 EN MEDICION REST BUDA INUNDACION | S22050300536 | Partial_restoration | Bad Weather | Include | Include | Weather | 643 | 2022-05-03 | 1929 | keep | 0 | May | 2022 | 0.0013138 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 02:30 | 2022-05-03 02:37 | 20 | 000:07 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LNEA SE REMPLAZO 2 PARARRAYOS | S22050300034 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 7 | 2022-05-03 | 140 | keep | 0 | May | 2022 | 9.5353e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 02:34 | 2022-05-03 02:35 | 5668 | 000:01 | T | DESGANCHE | RECIERRE | R22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-03 | 5668 | keep | 0 | May | 2022 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2022-05-03 02:35 | 2022-05-03 14:05 | 225 | 011:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA, 2 RBA DE 50 AMP. EN SU-3A, 1 X 50 EN RISER Y 1 X 50 EN OTRO RISER SE REALIZO DESGANCHE | R22050300066 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 690 | 2022-05-03 | 155250 | keep | 0 | May | 2022 | 0.10574 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-03 02:37 | 2022-05-03 02:41 | 858 | 000:04 | P | DESGANCHE | DISPARO 1303-02 SE CERRO POR CONTROL LLEVA 20% DEL 1204-02 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-05-03 | 3432 | keep | 0 | May | 2022 | 0.0023375 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-03 02:37 | 2022-05-03 02:41 | 600 | 000:04 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1303-02 SE CERRO POR CONTROL LLEVA 60AMP DEL 1206-04 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2022-05-03 | 2400 | keep | 0 | May | 2022 | 0.0016346 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-05-03 02:37 | 2022-05-03 02:41 | 1681 | 000:04 | T | DESGANCHE | DISPARO 1303-04 SE CERRO POR CONTROL LLEVA 1303-01 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-05-03 | 6724 | keep | 0 | May | 2022 | 0.0045797 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-03 02:37 | 2022-05-03 02:41 | 1948 | 000:04 | P | DESGANCHE | DISPARO SE CERRO POR CONTROL LLEVA 60AMP DEL 1206-04 Y LLEVA 20% DEL 1204-02 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-05-03 | 7792 | keep | 0 | May | 2022 | 0.0053071 | 0.0013268 | Momentary | FALSE | FALSE | Not_TMED_Event | 1948
SAN JUAN | 2022-05-03 02:37 | 2022-05-03 02:41 | 1598 | 000:04 | T | DESGANCHE | DISPARO 1303-04 SE CERRO POR CONTROL LLEVA 1346-06 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-05-03 | 6392 | keep | 0 | May | 2022 | 0.0043536 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-05-03 02:41 | 2022-05-03 02:56 | 20 | 000:15 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LNEA SE REMPLAZO 2 PARARRAYOS | S22050300034 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 15 | 2022-05-03 | 300 | keep | 0 | May | 2022 | 0.00020433 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 02:41 | 2022-05-03 02:42 | 872 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 872 | keep | 0 | May | 2022 | 0.00059392 | 0.00059392 | Momentary | FALSE | FALSE | Not_TMED_Event | 872
SAN JUAN | 2022-05-03 02:41 | 2022-05-03 02:42 | 2966 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 2966 | keep | 0 | May | 2022 | 0.0020201 | 0.0020201 | Momentary | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2022-05-03 02:41 | 2022-05-03 02:42 | 1799 | 000:01 | T | DESGANCHE | RECIERRE | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-03 | 1799 | keep | 0 | May | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-03 02:41 | 2022-05-03 02:42 | 487 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL 1206-04 QUE LLEVA 20% DEL 1303-02 | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 487 | keep | 0 | May | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-05-03 02:44 | 2022-05-03 02:45 | 872 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 872 | keep | 0 | May | 2022 | 0.00059392 | 0.00059392 | Momentary | FALSE | FALSE | Not_TMED_Event | 872
SAN JUAN | 2022-05-03 02:44 | 2022-05-03 02:45 | 2966 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 2966 | keep | 0 | May | 2022 | 0.0020201 | 0.0020201 | Momentary | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2022-05-03 02:44 | 2022-05-03 02:45 | 1799 | 000:01 | T | DESGANCHE | RECIERRE | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-03 | 1799 | keep | 0 | May | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-03 02:44 | 2022-05-03 02:45 | 487 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL 1206-04 QUE LLEVA 20% DEL 1303-02 | S22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 487 | keep | 0 | May | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-05-03 02:51 | 2022-05-03 02:52 | 1452 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 1452 | keep | 0 | May | 2022 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
BAYAMON | 2022-05-03 02:51 | 2022-05-03 02:52 | 2435 | 000:01 | T | DESGANCHE | RECIERRE | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-03 | 2435 | keep | 0 | May | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-05-03 02:51 | 2022-05-03 02:52 | 2956 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 2956 | keep | 0 | May | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-05-03 02:52 | 2022-05-03 17:49 | 70 | 014:57 | P | DESGANCHE | DESGANCHE Y 2 X100 EN C/L | S22050300658 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 897 | 2022-05-03 | 62790 | keep | 0 | May | 2022 | 0.042766 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-05-03 02:56 | 2022-05-03 02:58 | 858 | 000:02 | P | DESGANCHE | DISPARO 1303-02 SE CERRO POR CONTROL LLEVA 20% DEL 1204-02 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-03 | 1716 | keep | 0 | May | 2022 | 0.0011688 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-03 02:56 | 2022-05-03 02:58 | 600 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1303-02 SE CERRO POR CONTROL LLEVA 60AMP DEL 1206-04 | S22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 1200 | keep | 0 | May | 2022 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-05-03 02:56 | 2022-05-03 02:58 | 1681 | 000:02 | T | DESGANCHE | DISPARO 1303-04 SE CERRO POR CONTROL LLEVA 1303-01 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-03 | 3362 | keep | 0 | May | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-03 02:56 | 2022-05-03 02:58 | 1948 | 000:02 | P | DESGANCHE | DISPARO SE CERRO POR CONTROL LLEVA 60AMP DEL 1206-04 Y LLEVA 20% DEL 1204-02 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-03 | 3896 | keep | 0 | May | 2022 | 0.0026535 | 0.0013268 | Momentary | FALSE | FALSE | Not_TMED_Event | 1948
SAN JUAN | 2022-05-03 02:56 | 2022-05-03 02:58 | 487 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL 1206-04 QUE LLEVA 20% DEL 1303-02 | S22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 974 | keep | 0 | May | 2022 | 0.00066339 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-05-03 02:56 | 2022-05-03 02:58 | 1598 | 000:02 | T | DESGANCHE | DISPARO 1303-04 SE CERRO POR CONTROL LLEVA 1346-06 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-03 | 3196 | keep | 0 | May | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
AGUADILLA | 2022-05-03 02:56 | 2022-05-03 02:57 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22050300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 1047 | keep | 0 | May | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
SAN JUAN | 2022-05-03 02:58 | 2022-05-03 03:24 | 20 | 000:26 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LNEA SE REMPLAZO 2 PARARRAYOS | S22050300034 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 26 | 2022-05-03 | 520 | keep | 0 | May | 2022 | 0.00035417 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 03:00 | 2022-05-03 03:01 | 872 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 872 | keep | 0 | May | 2022 | 0.00059392 | 0.00059392 | Momentary | FALSE | FALSE | Not_TMED_Event | 872
SAN JUAN | 2022-05-03 03:00 | 2022-05-03 03:01 | 2966 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | S22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 2966 | keep | 0 | May | 2022 | 0.0020201 | 0.0020201 | Momentary | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2022-05-03 03:00 | 2022-05-03 03:01 | 1799 | 000:01 | T | DESGANCHE | RECIERRE | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-03 | 1799 | keep | 0 | May | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-03 03:00 | 2022-05-03 03:01 | 487 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL 1206-04 QUE LLEVA 20% DEL 1303-02 | S22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 487 | keep | 0 | May | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
BARRANQUITAS | 2022-05-03 03:00 | 2022-05-03 12:21 | 55 | 009:21 | P | DESGANCHE | 1 X 40 EN C/L | C22050300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 561 | 2022-05-03 | 30855 | keep | 0 | May | 2022 | 0.021015 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2022-05-03 03:02 | 2022-05-03 03:04 | 262 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 524 | keep | 0 | May | 2022 | 0.00035689 | 0.00017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 262
SAN JUAN | 2022-05-03 03:04 | 2022-05-03 08:48 | 52 | 005:44 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | R22050300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2022-05-03 | 17888 | keep | 0 | May | 2022 | 0.012183 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2022-05-03 03:04 | 2022-05-03 12:33 | 271 | 009:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X65 EN C/L | B22050300133 | New_Event | Cutout Failure | Include | Include | Equipment | 569 | 2022-05-03 | 154199 | keep | 0 | May | 2022 | 0.10502 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2022-05-03 03:05 | 2022-05-03 03:08 | 87 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-03 | 261 | keep | 0 | May | 2022 | 0.00017777 | 5.9255e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 87
SAN JUAN | 2022-05-03 03:05 | 2022-05-03 03:08 | 1 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE CERRO POR CONTROL | R22050300000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-05-03 | 3 | keep | 0 | May | 2022 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-03 03:06 | 2022-05-03 03:07 | 2859 | 000:01 | T | DESGANCHE | RECIERRE | C22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-03 | 2859 | keep | 0 | May | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
BAYAMON | 2022-05-03 03:07 | 2022-05-03 14:55 | 36 | 011:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU | B22050300134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 708 | 2022-05-03 | 25488 | keep | 0 | May | 2022 | 0.01736 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-05-03 03:07 | 2022-05-03 14:16 | 1 | 011:09 | P | DESGANCHE | 2 X 25 EN C/L | C22050300091 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 669 | 2022-05-03 | 669 | keep | 0 | May | 2022 | 0.00045565 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-03 03:08 | 2022-05-03 09:18 | 125 | 006:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | R22050300038 | New_Event | Bad Weather | Include | Include | Weather | 370 | 2022-05-03 | 46250 | keep | 0 | May | 2022 | 0.031501 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-05-03 03:09 | 2022-05-03 03:13 | 2076 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 SE CERRO POR SCADA | B22050300000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 4 | 2022-05-03 | 8304 | keep | 0 | May | 2022 | 0.0056558 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-05-03 03:09 | 2022-05-03 03:13 | 2605 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE CERRO POR CONTROL | B22050300000 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2022-05-03 | 10420 | keep | 0 | May | 2022 | 0.007097 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-05-03 03:13 | 2022-05-03 05:09 | 2076 | 001:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO AREA PARA CERRAR PUENTE ABIERTO 40% DE 1710-05 CARGA POR EL 1718-03 | B22050300578 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 116 | 2022-05-03 | 240816 | keep | 0 | May | 2022 | 0.16402 | 0.001414 | Sustained | FALSE | FALSE | Not_TMED_Event | 2076
SAN JUAN | 2022-05-03 03:24 | 2022-05-03 03:31 | 858 | 000:07 | P | DESGANCHE | DISPARO 1303-02 SE CERRO POR CONTROL LLEVA 20% DEL 1204-02 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-05-03 | 6006 | keep | 0 | May | 2022 | 0.0040907 | 0.00058438 | Sustained | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-03 03:24 | 2022-05-03 03:31 | 600 | 000:07 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO 1303-02 SE CERRO POR CONTROL LLEVA 60AMP DEL 1206-04 | S22050300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 7 | 2022-05-03 | 4200 | keep | 0 | May | 2022 | 0.0028606 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-05-03 03:24 | 2022-05-03 03:31 | 1681 | 000:07 | T | DESGANCHE | DISPARO 1303-04 SE CERRO POR CONTROL LLEVA 1303-01 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-05-03 | 11767 | keep | 0 | May | 2022 | 0.0080145 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-03 03:24 | 2022-05-03 03:31 | 1948 | 000:07 | P | DESGANCHE | DISPARO SE CERRO POR CONTROL LLEVA 60A POR 1206-04 Y LLEVA 20% DEL 1204-02 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-05-03 | 13636 | keep | 0 | May | 2022 | 0.0092874 | 0.0013268 | Sustained | FALSE | FALSE | Not_TMED_Event | 1948
SAN JUAN | 2022-05-03 03:24 | 2022-05-03 03:31 | 1598 | 000:07 | T | DESGANCHE | DISPARO 1303-04 SE CERRO POR CONTROL LLEVA 1346-06 | S22050300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-05-03 | 11186 | keep | 0 | May | 2022 | 0.0076187 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2022-05-03 03:28 | 2022-05-03 10:00 | 70 | 006:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300016 | New_Event | Bad Weather | Include | Include | Weather | 392 | 2022-05-03 | 27440 | keep | 0 | May | 2022 | 0.018689 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-05-03 03:31 | 2022-05-03 03:36 | 20 | 000:05 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LNEA SE REMPLAZO 2 PARARRAYOS | S22050300034 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 5 | 2022-05-03 | 100 | keep | 0 | May | 2022 | 6.811e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 03:36 | 2022-05-03 05:44 | 858 | 002:08 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1303-02 QUE A SU LLEVA LA CARGA DEL 1204-02 UN 20%. SE RETIRO BAMBUAS SOBRE LA LINEA Y SE CERRO INTERRUPTOR | S22050300000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-05-03 | 109824 | keep | 0 | May | 2022 | 0.074801 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 03:36 | 2022-05-03 05:44 | 1681 | 002:08 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-01 QUE A SU LLEVA LA CARGA DEL 1346-06 . SE RETIRO BAMBUAS SOBRE LA LINEA Y SE CERRO INTERRUPTOR | S22050300000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-05-03 | 215168 | keep | 0 | May | 2022 | 0.14655 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 03:36 | 2022-05-03 05:44 | 2435 | 002:08 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-02 QUE A SU LLEVA LA CARGA DEL 1204-02 UN 20%. SE RETIRO BAMBUAS SOBRE LA LINEA Y SE CERRO INTERRUPTOR | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-05-03 | 311680 | keep | 0 | May | 2022 | 0.21228 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2022-05-03 03:36 | 2022-05-03 05:44 | 1598 | 002:08 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-01 QUE A SU LLEVA LA CARGA DEL 1346-06 . SE RETIRO BAMBUAS SOBRE LA LINEA Y SE CERRO INTERRUPTOR | S22050300000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-05-03 | 204544 | keep | 0 | May | 2022 | 0.13931 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 03:50 | 2022-05-03 03:51 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 3046 | keep | 0 | May | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
BAYAMON | 2022-05-03 04:00 | 2022-05-03 05:25 | 4173 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | SE SECCIONALIZO 1713-05 Y SE CERRO MACHETES Y ENTRO UN 90% EN SERVICIO | B22050300005 | Partial_restoration | Bad Weather | Include | Include | Weather | 85 | 2022-05-03 | 354705 | keep | 0 | May | 2022 | 0.24159 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 04:20 | 2022-05-03 13:55 | 51 | 009:35 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22050300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 575 | 2022-05-03 | 29325 | keep | 0 | May | 2022 | 0.019973 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
SAN JUAN | 2022-05-03 04:29 | 2022-05-03 11:00 | 88 | 006:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN AEREO PROVISIONAL HACIA T-4 QUE SE INUNDO POR EL MAL TIEMPO | R22050300024 | New_Event | Bad Weather | Include | Include | Weather | 391 | 2022-05-03 | 34408 | keep | 0 | May | 2022 | 0.023435 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
SAN JUAN | 2022-05-03 04:37 | 2022-05-03 12:33 | 39 | 007:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE DE RAMA | R22050300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 476 | 2022-05-03 | 18564 | keep | 0 | May | 2022 | 0.012644 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2022-05-03 04:51 | 2022-05-03 14:52 | 30 | 010:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L LLUVIA Y VIENTO FUERTE | B22050300167 | New_Event | Bad Weather | Include | Include | Weather | 601 | 2022-05-03 | 18030 | keep | 0 | May | 2022 | 0.01228 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-05-03 04:56 | 2022-05-03 08:43 | 46 | 003:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22050300014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-05-03 | 10442 | keep | 0 | May | 2022 | 0.007112 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
BAYAMON | 2022-05-03 05:09 | 2022-05-03 09:54 | 2076 | 004:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETE PARA CERRAR PUENTE ABIERTO 40% DE LA CARGA POR EL 1718-03 | B22050300578 | Partial_restoration | Wire Down | Include | Include | Equipment | 285 | 2022-05-03 | 591660 | keep | 0 | May | 2022 | 0.40298 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-03 05:09 | 2022-05-03 09:54 | 2605 | 004:45 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO AREA PARA CERRAR PUENTE ABIERTO LLEVA 40% DE LA CARGA DEL 1710-05 | B22050300578 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 285 | 2022-05-03 | 742425 | keep | 0 | May | 2022 | 0.50566 | 0.0017743 | Sustained | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-05-03 05:19 | 2022-05-03 05:21 | 946 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 1892 | keep | 0 | May | 2022 | 0.0012886 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
BAYAMON | 2022-05-03 05:19 | 2022-05-03 05:21 | 937 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | S22050300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-05-03 | 1874 | keep | 0 | May | 2022 | 0.0012764 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
BAYAMON | 2022-05-03 05:25 | 2022-05-03 07:33 | 596 | 002:08 | P | MAL TIEMPO/RAYOS/WET ASH | SE SECCIONALIZO 1713-05 PARA REALIZAR DESGANCHE Y SE CERRO MACHETES | B22050300005 | Partial_restoration | Bad Weather | Include | Include | Weather | 128 | 2022-05-03 | 76288 | keep | 0 | May | 2022 | 0.051959 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-03 05:32 | 2022-05-03 05:33 | 989 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE CERRO POR CONTROL | C22050300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-03 | 989 | keep | 0 | May | 2022 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2022-05-03 05:33 | 2022-05-03 10:19 | 100 | 004:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN RISER CRUCE X AV | C22050300018 | 1st_after_momentary |  |  | Include | Wildlife | 286 | 2022-05-03 | 28600 | keep | 0 | May | 2022 | 0.019479 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-03 05:37 | 2022-05-03 16:12 | 80 | 010:35 | P | NO SE REPORTO CAUSA | 1 X 80, 2 X 65 Y 1 X 50 EN CORTES DE LINEAS | B22050300200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 635 | 2022-05-03 | 50800 | keep | 0 | May | 2022 | 0.0346 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-03 05:44 | 2022-05-03 14:00 | 20 | 008:16 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LNEA SE REMPLAZO 2 PARARRAYOS | S22050300034 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 496 | 2022-05-03 | 9920 | keep | 0 | May | 2022 | 0.0067565 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-05-03 05:51 | 2022-05-03 09:12 | 100 | 003:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | P22050300043 | New_Event | Cutout Failure | Include | Include | Equipment | 201 | 2022-05-03 | 20100 | keep | 0 | May | 2022 | 0.01369 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-03 05:57 | 2022-05-03 11:25 | 90 | 005:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | B22050300215 | New_Event | Cutout Failure | Include | Include | Equipment | 328 | 2022-05-03 | 29520 | keep | 0 | May | 2022 | 0.020106 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-05-03 06:12 | 2022-05-03 12:45 | 7 | 006:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-1 | S22050300306 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 393 | 2022-05-03 | 2751 | keep | 0 | May | 2022 | 0.0018737 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-05-03 06:16 | 2022-05-03 13:37 | 50 | 007:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L LEVANTO NEUTRAL PRIMARIO | C22050300023 | New_Event | Wire Down | Include | Include | Equipment | 441 | 2022-05-03 | 22050 | keep | 0 | May | 2022 | 0.015018 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-03 06:24 | 2022-05-03 06:25 | 2608 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22050300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-03 | 2608 | keep | 0 | May | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2022-05-03 06:25 | 2022-05-03 09:45 | 1 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER CRUCE X AVE | C22050300054 | 1st_after_momentary |  |  | Include | Wildlife | 200 | 2022-05-03 | 200 | keep | 0 | May | 2022 | 0.00013622 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-03 06:32 | 2022-05-03 06:33 | 598 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-03 | 598 | keep | 0 | May | 2022 | 0.0004073 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
CAGUAS | 2022-05-03 06:32 | 2022-05-03 06:33 | 2486 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-03 | 2486 | keep | 0 | May | 2022 | 0.0016932 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
CAGUAS | 2022-05-03 06:32 | 2022-05-03 06:33 | 1403 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-03 | 1403 | keep | 0 | May | 2022 | 0.00095558 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
CAGUAS | 2022-05-03 06:32 | 2022-05-03 06:33 | 1001 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-03 | 1001 | keep | 0 | May | 2022 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
CAGUAS | 2022-05-03 06:33 | 2022-05-03 10:28 | 15 | 003:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22050200304 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 235 | 2022-05-03 | 3525 | keep | 0 | May | 2022 | 0.0024009 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-03 06:35 | 2022-05-03 20:23 | 20 | 013:48 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 Y 1 X 50 EN CORTES DE LINEAS MAL TIEMPO VIENTOS FUERTES | A22050300029 | New_Event | Bad Weather | Include | Include | Weather | 828 | 2022-05-03 | 16560 | keep | 0 | May | 2022 | 0.011279 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-03 06:41 | 2022-05-03 13:15 | 65 | 006:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DE LINEA PRINCIPAL Y 1 X 50 EN CORTE DE LINEA RAMAL | S22050300326 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2022-05-03 | 25610 | keep | 0 | May | 2022 | 0.017443 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-05-03 06:57 | 2022-05-03 08:20 | 3 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22050300033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2022-05-03 | 249 | keep | 0 | May | 2022 | 0.00016959 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-05-03 07:00 | 2022-05-03 10:22 | 100 | 003:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300035 | New_Event | Bad Weather | Include | Include | Weather | 202 | 2022-05-03 | 20200 | keep | 0 | May | 2022 | 0.013758 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-03 07:00 | 2022-05-03 10:15 | 22 | 003:15 | P | DESGANCHE | 2 X 50 EN C/L SE RETIRO RAMA | B22050300265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-05-03 | 4290 | keep | 0 | May | 2022 | 0.0029219 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2022-05-03 07:02 | 2022-05-03 10:17 | 2366 | 003:15 | T | BREAKER DEFECTUOSO O NO OPERA | BOBINA DE CIERRE QUEMADA CERRADO MANUAL MECANICO | M22050300028 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 195 | 2022-05-03 | 461370 | keep | 0 | May | 2022 | 0.31424 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
YAUCO | 2022-05-03 07:20 | 2022-05-03 11:22 | 25 | 004:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22050300062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-05-03 | 6050 | keep | 0 | May | 2022 | 0.0041206 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-05-03 07:21 | 2022-05-03 12:16 | 150 | 004:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | P22050300063 | New_Event | Cutout Failure | Include | Include | Equipment | 295 | 2022-05-03 | 44250 | keep | 0 | May | 2022 | 0.030138 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-05-03 07:27 | 2022-05-03 10:23 | 90 | 002:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22050300066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-05-03 | 15840 | keep | 0 | May | 2022 | 0.010789 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-05-03 07:33 | 2022-05-03 08:44 | 5961 | 001:11 | T | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYYO Y SE DESGANCHO BY-22050300005 INTERRUPTOR 1713-05 LLEVA 95% 1717-02 | B22050300005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 71 | 2022-05-03 | 423231 | keep | 0 | May | 2022 | 0.28826 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-05-03 07:33 | 2022-05-03 08:44 | 865 | 001:11 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYYO Y SE DESGANCHO BY-22050300005 INTERRUPTOR 1713-05 LLEVA 95% 1717-02 | B22050300005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 71 | 2022-05-03 | 61415 | keep | 0 | May | 2022 | 0.041829 | 0.00058915 | Sustained | FALSE | FALSE | Not_TMED_Event | 865
BAYAMON | 2022-05-03 07:34 | 2022-05-03 07:36 | 1984 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-12 QUE A SU VEZ LLEVA LA CARGA DEL 1911-07 | S22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-03 | 3968 | keep | 0 | May | 2022 | 0.0027026 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-05-03 07:34 | 2022-05-03 07:35 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1711-05 | B22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 723 | keep | 0 | May | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-05-03 07:34 | 2022-05-03 07:35 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1711-02 | B22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 1976 | keep | 0 | May | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-05-03 07:34 | 2022-05-03 07:36 | 577 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-12 QUE A SU VEZ LLEVA LA CARGA DEL 1911-07 | S22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-03 | 1154 | keep | 0 | May | 2022 | 0.00078598 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
VEGA BAJA | 2022-05-03 07:34 | 2022-05-03 13:10 | 4 | 005:36 | P | NO SE REPORTO CAUSA | 1 X 15 XMR | B22050300296 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 336 | 2022-05-03 | 1344 | keep | 0 | May | 2022 | 0.00091539 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-05-03 07:35 | 2022-05-03 13:04 | 100 | 005:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300043 | New_Event | Bad Weather | Include | Include | Weather | 329 | 2022-05-03 | 32900 | keep | 0 | May | 2022 | 0.022408 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-03 07:36 | 2022-05-03 12:00 | 40 | 004:24 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22050300370 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2022-05-03 | 10560 | keep | 0 | May | 2022 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-03 07:36 | 2022-05-03 11:17 | 165 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22050300298 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-05-03 | 36465 | keep | 0 | May | 2022 | 0.024836 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
BAYAMON | 2022-05-03 07:37 | 2022-05-03 17:26 | 9 | 009:49 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR SE RETIRO BEJUCO DE TRANSFORMADOR | S22050300373 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 589 | 2022-05-03 | 5301 | keep | 0 | May | 2022 | 0.0036105 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-05-03 07:37 | 2022-05-03 07:38 | 1444 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | CARGA POR 6014-02 | M22050300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 1444 | keep | 0 | May | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-05-03 07:37 | 2022-05-03 07:38 | 3630 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR NO RECERRO CERRADO POR SCADA | M22050300000 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2022-05-03 | 3630 | keep | 0 | May | 2022 | 0.0024724 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-03 07:38 | 2022-05-03 08:46 | 3 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETIRO ALAMBRE PRIMARIO CRUZADO FUERA DE SERVICIO | P22050300072 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-05-03 | 204 | keep | 0 | May | 2022 | 0.00013894 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-05-03 07:38 | 2022-05-04 17:00 | 1 | 033:22 | P | ERROR HUMANO | SE CERRO MONTURA DE TRANSFORMADORES QUE SE HABIA DEJADO ABIERTA DESDE EL 05/01/2022 CUANDO HUBO AVERIA DE POSTES PARTIDOS | M22050400161 | Partial_restoration | Human Error | Include | Include | Other | 2002 | 2022-05-03 | 2002 | keep | 0 | May | 2022 | 0.0013636 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-03 07:38 | 2022-05-03 19:57 | 30 | 012:19 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050201209 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 739 | 2022-05-03 | 22170 | keep | 0 | May | 2022 | 0.0151 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-03 07:42 | 2022-05-03 22:54 | 7 | 015:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22050300307 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 912 | 2022-05-03 | 6384 | keep | 0 | May | 2022 | 0.0043481 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-05-03 07:44 | 2022-05-03 07:45 | 143 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-06 Y A SU VEZ LLEVA LA CARGA PARCIAL DEL 1404-07 UN 80% | S22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 143 | keep | 0 | May | 2022 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-05-03 07:44 | 2022-05-03 07:45 | 1086 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-06 Y A SU VEZ LLEVA LA CARGA PARCIAL DEL 1404-07 UN 80% | S22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 1086 | keep | 0 | May | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
PONCE | 2022-05-03 07:45 | 2022-05-03 11:14 | 2 | 003:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22050300074 | New_Event |  |  | Include | Wildlife | 209 | 2022-05-03 | 418 | keep | 0 | May | 2022 | 0.0002847 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-05-03 07:46 | 2022-05-03 19:10 | 3 | 011:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22050300312 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 684 | 2022-05-03 | 2052 | keep | 0 | May | 2022 | 0.0013976 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-05-03 07:46 | 2022-05-03 09:58 | 15 | 002:12 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22050300047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-05-03 | 1980 | keep | 0 | May | 2022 | 0.0013486 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-05-03 07:52 | 2022-05-03 17:31 | 4 | 009:39 | P | SECUNDARIA/DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22050300051 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 579 | 2022-05-03 | 2316 | keep | 0 | May | 2022 | 0.0015774 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-05-03 07:57 | 2022-05-03 12:46 | 50 | 004:49 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22050300539 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-05-03 | 14450 | keep | 0 | May | 2022 | 0.0098418 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-05-03 08:07 | 2022-05-03 10:20 | 60 | 002:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22050300080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-05-03 | 7980 | keep | 0 | May | 2022 | 0.0054351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-05-03 08:10 | 2022-05-03 13:15 | 8 | 005:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22050300082 | New_Event |  |  | Include | Wildlife | 305 | 2022-05-03 | 2440 | keep | 0 | May | 2022 | 0.0016619 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-05-03 08:13 | 2022-05-03 08:15 | 1565 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 3130 | keep | 0 | May | 2022 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-05-03 08:13 | 2022-05-03 08:15 | 976 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 1952 | keep | 0 | May | 2022 | 0.0013295 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-05-03 08:13 | 2022-05-03 08:15 | 548 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 1096 | keep | 0 | May | 2022 | 0.00074648 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-05-03 08:13 | 2022-05-03 08:15 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 630 | keep | 0 | May | 2022 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-05-03 08:13 | 2022-05-03 08:15 | 870 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 1740 | keep | 0 | May | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-05-03 08:13 | 2022-05-03 08:15 | 2906 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 5812 | keep | 0 | May | 2022 | 0.0039585 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-05-03 08:13 | 2022-05-03 08:15 | 2343 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 4686 | keep | 0 | May | 2022 | 0.0031916 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
ARECIBO | 2022-05-03 08:20 | 2022-05-03 14:55 | 30 | 006:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050300064 | New_Event | Bad Weather | Include | Include | Weather | 395 | 2022-05-03 | 11850 | keep | 0 | May | 2022 | 0.008071 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-03 08:24 | 2022-05-03 13:53 | 5 | 005:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R22050300058 | New_Event |  |  | Include | Wildlife | 329 | 2022-05-03 | 1645 | keep | 0 | May | 2022 | 0.0011204 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-03 08:32 | 2022-05-03 15:44 | 12 | 007:12 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | S22050300433 | New_Event | Vegetation Contact | Include | Include | Vegetation | 432 | 2022-05-03 | 5184 | keep | 0 | May | 2022 | 0.0035308 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-03 08:34 | 2022-05-03 08:36 | 1712 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO OPERO SE LE DIO PRUEBA Y QUEDA EN SERVICIO | P22050300098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-03 | 3424 | keep | 0 | May | 2022 | 0.0023321 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
ARECIBO | 2022-05-03 08:37 | 2022-05-03 18:30 | 50 | 009:53 | P | DESGANCHE | 3 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22050300079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 593 | 2022-05-03 | 29650 | keep | 0 | May | 2022 | 0.020194 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-05-03 08:40 | 2022-05-03 09:30 | 1 | 000:50 | P | OTRAS CAUSAS | 1 X 10 EN BANCO DE TRANSFORMADORES APARENTA TENER ESA FASE MAS CARGADA SE ORIENTO AL CLIENTE | R22050300062 | New_Event | Other Causes | Include | Include | Other | 50 | 2022-05-03 | 50 | keep | 0 | May | 2022 | 3.4055e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-03 08:40 | 2022-05-03 11:16 | 8 | 002:36 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22050300061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2022-05-03 | 1248 | keep | 0 | May | 2022 | 0.00085001 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-05-03 08:44 | 2022-05-03 15:37 | 596 | 006:53 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE MASIVO CON GOI BY-220503-06A | B22050300560 | New_Event | Vegetation Contact | Include | Include | Vegetation | 413 | 2022-05-03 | 246148 | keep | 0 | May | 2022 | 0.16765 | 0.00040593 | Sustained | FALSE | FALSE | Not_TMED_Event | 596
MAYAGÃœEZ | 2022-05-03 08:44 | 2022-05-03 14:47 | 20 | 006:03 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22050300029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2022-05-03 | 7260 | keep | 0 | May | 2022 | 0.0049448 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-03 08:50 | 2022-05-03 16:48 | 10 | 007:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22050300088 | New_Event | Bad Weather | Include | Include | Weather | 478 | 2022-05-03 | 4780 | keep | 0 | May | 2022 | 0.0032556 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-03 08:52 | 2022-05-03 14:23 | 40 | 005:31 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | R22050300092 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-05-03 | 13240 | keep | 0 | May | 2022 | 0.0090177 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 08:52 | 2022-05-03 12:58 | 202 | 004:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER Y 1 RBA DE 50 AMP. EN SU-1 MAL TIEMPO | R22050300068 | New_Event | Bad Weather | Include | Include | Weather | 246 | 2022-05-03 | 49692 | keep | 0 | May | 2022 | 0.033845 | 0.00013758 | Sustained | FALSE | FALSE | Not_TMED_Event | 202
ARECIBO | 2022-05-03 08:52 | 2022-05-04 13:49 | 70 | 028:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22050300407 | New_Event | Cutout Failure | Include | Include | Equipment | 1737 | 2022-05-03 | 121590 | keep | 0 | May | 2022 | 0.082814 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-05-03 08:52 | 2022-05-03 16:58 | 50 | 008:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300094 | New_Event | Bad Weather | Include | Include | Weather | 486 | 2022-05-03 | 24300 | keep | 0 | May | 2022 | 0.016551 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-03 08:54 | 2022-05-03 08:55 | 3309 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR POR PUENTE PRIMARIO ABIERTO | A22050300097 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-03 | 3309 | keep | 0 | May | 2022 | 0.0022537 | 0.0022537 | Momentary | FALSE | FALSE | Not_TMED_Event | 3309
SAN JUAN | 2022-05-03 08:55 | 2022-05-03 15:11 | 50 | 006:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL | S22050300455 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 376 | 2022-05-03 | 18800 | keep | 0 | May | 2022 | 0.012805 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-03 08:55 | 2022-05-03 20:10 | 100 | 011:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO EN SALIDA DEL INTERRUPTOR 7502-02 | A22050300338 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 675 | 2022-05-03 | 67500 | keep | 0 | May | 2022 | 0.045974 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-03 09:00 | 2022-05-03 09:01 | 2107 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR SE REPARO PUENTES PRIMARIOS | A22050300107 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-03 | 2107 | keep | 0 | May | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2022-05-03 09:01 | 2022-05-03 16:00 | 300 | 006:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A22050300150 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 419 | 2022-05-03 | 125700 | keep | 0 | May | 2022 | 0.085614 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-05-03 09:19 | 2022-05-03 14:01 | 45 | 004:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050300120 | New_Event | Bad Weather | Include | Include | Weather | 282 | 2022-05-03 | 12690 | keep | 0 | May | 2022 | 0.0086431 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-05-03 09:23 | 2022-05-03 11:25 | 150 | 002:02 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22050300124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-05-03 | 18300 | keep | 0 | May | 2022 | 0.012464 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-05-03 09:25 | 2022-05-03 11:02 | 30 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22050300118 | New_Event |  |  | Include | Wildlife | 97 | 2022-05-03 | 2910 | keep | 0 | May | 2022 | 0.001982 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-05-03 09:27 | 2022-05-03 20:34 | 25 | 011:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22050300431 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 667 | 2022-05-03 | 16675 | keep | 0 | May | 2022 | 0.011357 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-03 09:45 | 2022-05-03 10:02 | 69 | 000:17 | P | NO SE REPORTO CAUSA | 1 X 100 C/L | S22050300517 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2022-05-03 | 1173 | keep | 0 | May | 2022 | 0.00079892 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2022-05-03 09:47 | 2022-05-03 15:00 | 48 | 005:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S22050300521 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2022-05-03 | 15024 | keep | 0 | May | 2022 | 0.010233 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
SAN JUAN | 2022-05-03 09:51 | 2022-05-03 10:20 | 5 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDADARIA | R22050300015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2022-05-03 | 145 | keep | 0 | May | 2022 | 9.8759e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-05-03 09:51 | 2022-05-03 19:30 | 25 | 009:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300167 | New_Event | Bad Weather | Include | Include | Weather | 579 | 2022-05-03 | 14475 | keep | 0 | May | 2022 | 0.0098589 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-03 09:52 | 2022-05-03 14:23 | 40 | 004:31 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R22050300092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-05-03 | 10840 | keep | 0 | May | 2022 | 0.0073831 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-03 09:53 | 2022-05-03 15:55 | 20 | 006:02 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050300155 | New_Event | Bad Weather | Include | Include | Weather | 362 | 2022-05-03 | 7240 | keep | 0 | May | 2022 | 0.0049311 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-03 09:54 | 2022-05-03 10:39 | 390 | 000:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETE PARA CERRAR PUENTE ABIERTO | B22050300578 | Partial_restoration | Wire Down | Include | Include | Equipment | 45 | 2022-05-03 | 17550 | keep | 0 | May | 2022 | 0.011953 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-03 10:02 | 2022-05-03 10:03 | 1370 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S22050300532 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 1370 | keep | 0 | May | 2022 | 0.0009331 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2022-05-03 10:03 | 2022-05-04 00:46 | 69 | 014:43 | P | NO SE REPORTO CAUSA | 1 X 100 C/L | S22050300517 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 883 | 2022-05-03 | 60927 | keep | 0 | May | 2022 | 0.041497 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
UTUADO | 2022-05-03 10:03 | 2022-05-03 13:44 | 40 | 003:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CONVERTIDOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050300180 | New_Event | Bad Weather | Include | Include | Weather | 221 | 2022-05-03 | 8840 | keep | 0 | May | 2022 | 0.0060209 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-03 10:06 | 2022-05-03 19:50 | 60 | 009:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22050300163 | New_Event | Wire Down | Include | Include | Equipment | 584 | 2022-05-03 | 35040 | keep | 0 | May | 2022 | 0.023866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-05-03 10:16 | 2022-05-03 12:55 | 2 | 002:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | C22050300080 | New_Event |  |  | Include | Wildlife | 159 | 2022-05-03 | 318 | keep | 0 | May | 2022 | 0.00021659 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-05-03 10:19 | 2022-05-04 16:40 | 3 | 030:21 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22050300199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1821 | 2022-05-03 | 5463 | keep | 0 | May | 2022 | 0.0037208 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-05-03 10:26 | 2022-05-03 11:47 | 50 | 001:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA Y SE LEVANTO LINEA PRIMARIA | S22050300552 | Partial_restoration | Wire Down | Include | Include | Equipment | 81 | 2022-05-03 | 4050 | keep | 0 | May | 2022 | 0.0027584 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-05-03 10:26 | 2022-05-03 14:30 | 379 | 004:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE REMPLAZO PERNO DE CRUCETA | B22050300485 | New_Event | Wire Down | Include | Include | Equipment | 244 | 2022-05-03 | 92476 | keep | 0 | May | 2022 | 0.062985 | 0.00025814 | Sustained | FALSE | FALSE | Not_TMED_Event | 379
BAYAMON | 2022-05-03 10:43 | 2022-05-03 10:44 | 1085 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 1085 | keep | 0 | May | 2022 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2022-05-03 10:44 | 2022-05-03 22:45 | 41 | 012:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN C/L SE RETIRO CHIRINGA | B22050300493 | New_Event |  |  | Include | Wildlife | 721 | 2022-05-03 | 29561 | keep | 0 | May | 2022 | 0.020134 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2022-05-03 10:46 | 2022-05-03 11:39 | 2402 | 000:53 | T | DESGANCHE | SE ABRIO MACHETE PARA REALIZAR DESGANCHE PRIMARIO | S22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2022-05-03 | 127306 | keep | 0 | May | 2022 | 0.086708 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
AGUADILLA | 2022-05-03 10:53 | 2022-05-03 16:05 | 1 | 005:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AVE CRUZO LINEAS | M22050300223 | New_Event |  |  | Include | Wildlife | 312 | 2022-05-03 | 312 | keep | 0 | May | 2022 | 0.0002125 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-03 10:55 | 2022-05-03 12:00 | 50 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE SECCIONALIZO AVERIA DE LINEAS PRIMARIAS PARTIDAS | A22050200240 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2022-05-03 | 3250 | keep | 0 | May | 2022 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-03 10:57 | 2022-05-03 11:37 | 80 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22050300222 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2022-05-03 | 3200 | keep | 0 | May | 2022 | 0.0021795 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-05-03 11:07 | 2022-05-03 16:44 | 68 | 005:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR CHANGO | R22050300107 | New_Event |  |  | Include | Wildlife | 337 | 2022-05-03 | 22916 | keep | 0 | May | 2022 | 0.015608 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
PONCE | 2022-05-03 11:11 | 2022-05-03 11:20 | 1 | 000:09 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE ABRIO CAJA EN TRANSFORMADOR PARA RETIRAR ENREDADERA | P22050300148 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 9 | 2022-05-03 | 9 | keep | 0 | May | 2022 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-03 11:12 | 2022-05-03 20:31 | 150 | 009:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO PUENTES | M22050300237 | New_Event | Wire Down | Include | Include | Equipment | 559 | 2022-05-03 | 83850 | keep | 0 | May | 2022 | 0.05711 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-05-03 11:13 | 2022-05-03 20:51 | 25 | 009:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300231 | New_Event | Bad Weather | Include | Include | Weather | 578 | 2022-05-03 | 14450 | keep | 0 | May | 2022 | 0.0098418 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-05-03 11:15 | 2022-05-03 13:07 | 7 | 001:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22050300150 | New_Event | Secondary Wire Down | Include | Include | Equipment | 112 | 2022-05-03 | 784 | keep | 0 | May | 2022 | 0.00053398 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-05-03 11:15 | 2022-05-03 14:30 | 150 | 003:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40, 2 X 30 Y 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22050200262 | New_Event | Wire Down | Include | Include | Equipment | 195 | 2022-05-03 | 29250 | keep | 0 | May | 2022 | 0.019922 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-05-03 11:24 | 2022-05-03 14:25 | 15 | 003:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22050300251 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 181 | 2022-05-03 | 2715 | keep | 0 | May | 2022 | 0.0018492 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-03 11:32 | 2022-05-03 11:33 | 1501 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22050300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-03 | 1501 | keep | 0 | May | 2022 | 0.0010223 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-05-03 11:33 | 2022-05-03 16:30 | 60 | 004:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO LINEA A CAJA EN C/L | B22050300566 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 297 | 2022-05-03 | 17820 | keep | 0 | May | 2022 | 0.012137 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-03 11:38 | 2022-05-05 11:00 | 200 | 047:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEAS PRIMARIAS CRUZADAS | M22050300255 | New_Event | Wire Down | Include | Include | Equipment | 2842 | 2022-05-03 | 568400 | keep | 0 | May | 2022 | 0.38713 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-03 11:39 | 2022-05-03 13:06 | 360 | 001:27 | P | DESGANCHE | SE ABRIO MACHETE PARA REALIZAR DESGANCHE PRIMARIO | S22050300000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-05-03 | 31320 | keep | 0 | May | 2022 | 0.021332 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-03 11:51 | 2022-05-03 11:52 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 438 | keep | 0 | May | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2022-05-03 11:58 | 2022-05-03 14:49 | 114 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 80 EN C/L | B22050300548 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-05-03 | 19494 | keep | 0 | May | 2022 | 0.013277 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
ARECIBO | 2022-05-03 12:01 | 2022-05-03 15:33 | 80 | 003:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22050300260 | New_Event | Wire Down | Include | Include | Equipment | 212 | 2022-05-03 | 16960 | keep | 0 | May | 2022 | 0.011551 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-05-03 12:02 | 2022-05-04 13:04 | 20 | 025:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22050300261 | New_Event | Cutout Failure | Include | Include | Equipment | 1502 | 2022-05-03 | 30040 | keep | 0 | May | 2022 | 0.02046 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-05-03 12:06 | 2022-05-03 14:41 | 100 | 002:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | P22050300167 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2022-05-03 | 15500 | keep | 0 | May | 2022 | 0.010557 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-05-03 12:07 | 2022-05-03 12:08 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22050300169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 1478 | keep | 0 | May | 2022 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
VEGA BAJA | 2022-05-03 12:10 | 2022-05-03 18:23 | 10 | 006:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22050300559 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 373 | 2022-05-03 | 3730 | keep | 0 | May | 2022 | 0.0025405 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-03 12:15 | 2022-05-03 13:34 | 329 | 001:19 | T | DESGANCHE | SE SECCIONALIZO ARBOL SOBRE LAS LINEAS | C22050300107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-05-03 | 25991 | keep | 0 | May | 2022 | 0.017702 | 0.00022408 | Sustained | FALSE | FALSE | Not_TMED_Event | 329
BAYAMON | 2022-05-03 12:24 | 2022-05-03 19:10 | 150 | 006:46 | P | DESGANCHE | DESGANCHE Y 2 X 100 EN CONVERTIDOR | B22050300655 | New_Event | Vegetation Contact | Include | Include | Vegetation | 406 | 2022-05-03 | 60900 | keep | 0 | May | 2022 | 0.041479 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-05-03 12:26 | 2022-05-03 16:55 | 1 | 004:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R22050300118 | New_Event |  |  | Include | Wildlife | 269 | 2022-05-03 | 269 | keep | 0 | May | 2022 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-03 12:27 | 2022-05-03 18:18 | 7 | 005:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 25 EN CORTES DE LINEAS MAL TIEMPO DESCARGAS ELECTRICAS | A22050300272 | New_Event | Bad Weather | Include | Include | Weather | 351 | 2022-05-03 | 2457 | keep | 0 | May | 2022 | 0.0016735 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-05-03 12:37 | 2022-05-03 17:47 | 6 | 005:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050300285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-05-03 | 1860 | keep | 0 | May | 2022 | 0.0012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-03 12:37 | 2022-05-03 18:03 | 10 | 005:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300276 | New_Event | Bad Weather | Include | Include | Weather | 326 | 2022-05-03 | 3260 | keep | 0 | May | 2022 | 0.0022204 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-03 12:39 | 2022-05-03 17:32 | 30 | 004:53 | P | ESTRUCTURA AVERIADA | 2 X 40 EN CORTE DE LINEA SE ELIMINO CRUCETA PARTIDA Y POSTE QUEMADO | S22050300662 | New_Event | Defective Pole | Include | Include | Equipment | 293 | 2022-05-03 | 8790 | keep | 0 | May | 2022 | 0.0059868 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-03 12:52 | 2022-05-03 19:30 | 40 | 006:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R22050300120 | New_Event |  |  | Include | Wildlife | 398 | 2022-05-03 | 15920 | keep | 0 | May | 2022 | 0.010843 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-03 12:53 | 2022-05-03 12:54 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-03 12:53 | 2022-05-03 12:54 | 871 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6012-05 | M22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
PONCE | 2022-05-03 13:00 | 2022-05-03 14:38 | 3 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR IGUANA | P22050300213 | New_Event |  |  | Include | Wildlife | 98 | 2022-05-03 | 294 | keep | 0 | May | 2022 | 0.00020024 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-05-03 13:00 | 2022-05-03 15:10 | 30 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050300409 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2022-05-03 | 3900 | keep | 0 | May | 2022 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-05-03 13:05 | 2022-05-03 15:20 | 7 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300260 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2022-05-03 | 945 | keep | 0 | May | 2022 | 0.00064364 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-05-03 13:07 | 2022-05-03 18:57 | 20 | 005:50 | P | DESGANCHE | 1 X 30 EN C/L SE RETIRO RAMA DE LINEA | B22050300594 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2022-05-03 | 7000 | keep | 0 | May | 2022 | 0.0047677 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-05-03 13:10 | 2022-05-03 13:35 | 3 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BARRAS EN PEDESTAL SECUNDARIO | P22050300186 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2022-05-03 | 75 | keep | 0 | May | 2022 | 5.1082e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-05-03 13:14 | 2022-05-03 13:55 | 1 | 000:41 | P | NO SE REPORTO CAUSA | 3 X 80 EN C/L | B22050300598 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2022-05-03 | 41 | keep | 0 | May | 2022 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-03 13:17 | 2022-05-03 13:19 | 1337 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 2 OPERACIONES DE RECIERRE SE CERRO POR CONTROL SCADA | M22050300305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-03 | 2674 | keep | 0 | May | 2022 | 0.0018212 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2022-05-03 13:21 | 2022-05-03 13:22 | 1352 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M22050300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-03 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-03 13:21 | 2022-05-03 13:22 | 871 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA POR 6012-05 | M22050300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-03 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-03 13:25 | 2022-05-03 16:30 | 1352 | 003:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ALIMENTADOR SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 6014-03 NEUTRAL TOCANDO CON LINEA PRIMARIA | M22050300312 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 185 | 2022-05-03 | 250120 | keep | 0 | May | 2022 | 0.17036 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-03 13:25 | 2022-05-03 16:30 | 871 | 003:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA POR 6012-05 NEUTRAL TOCANDO CON LINEA PRIMARIA EN ALIMENTADOR 6012-05 | M22050300312 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 185 | 2022-05-03 | 161135 | keep | 0 | May | 2022 | 0.10975 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
CAGUAS | 2022-05-03 13:34 | 2022-05-03 15:17 | 63 | 001:43 | P | DESGANCHE | SE RETIRO ARBOL DE LAS LINEAS | C22050300107 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-05-03 | 6489 | keep | 0 | May | 2022 | 0.0044196 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-03 13:39 | 2022-05-03 20:01 | 20 | 006:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22050300300 | New_Event | Bad Weather | Include | Include | Weather | 382 | 2022-05-03 | 7640 | keep | 0 | May | 2022 | 0.0052036 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-05-03 13:40 | 2022-05-03 16:14 | 6 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | P22050300193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-05-03 | 924 | keep | 0 | May | 2022 | 0.00062933 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-03 13:45 | 2022-05-03 15:23 | 10 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S22050300686 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2022-05-03 | 980 | keep | 0 | May | 2022 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-03 13:48 | 2022-05-03 15:45 | 5 | 001:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22050300335 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-05-03 | 585 | keep | 0 | May | 2022 | 0.00039844 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-03 13:58 | 2022-05-03 16:26 | 100 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050300349 | New_Event | Bad Weather | Include | Include | Weather | 148 | 2022-05-03 | 14800 | keep | 0 | May | 2022 | 0.01008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-05-03 14:04 | 2022-05-03 16:15 | 5 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | R22050300131 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2022-05-03 | 655 | keep | 0 | May | 2022 | 0.00044612 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-03 14:09 | 2022-05-03 18:00 | 3 | 003:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22050300133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2022-05-03 | 693 | keep | 0 | May | 2022 | 0.000472 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-05-03 14:09 | 2022-05-03 16:45 | 150 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050300363 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2022-05-03 | 23400 | keep | 0 | May | 2022 | 0.015938 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-03 14:12 | 2022-05-04 05:20 | 100 | 015:08 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050300367 | New_Event | Bad Weather | Include | Include | Weather | 908 | 2022-05-03 | 90800 | keep | 0 | May | 2022 | 0.061843 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-05-03 14:12 | 2022-05-03 14:13 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRA DE INTERRUPTOR | B22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 1859 | keep | 0 | May | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
SAN JUAN | 2022-05-03 14:17 | 2022-05-03 14:43 | 12 | 000:26 | P | CABLE SOTERRADO AVERIADO | SE MOVIO DE FASE EL T-267 Y SE DEJO LA CARGA TRIFASICA (COLEGIO PREBISTERIANO) FUERA QUE SE ALIMENTAN DEL SU-2A | R22050300135 | New_Event | UG Cable Fault | Include | Include | Equipment | 26 | 2022-05-03 | 312 | keep | 0 | May | 2022 | 0.0002125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-05-03 14:27 | 2022-05-03 19:38 | 13 | 005:11 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22050300630 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 311 | 2022-05-03 | 4043 | keep | 0 | May | 2022 | 0.0027537 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2022-05-03 14:43 | 2022-05-03 14:44 | 3046 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR EN SERVICIO | R22050300140 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-03 | 3046 | keep | 0 | May | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-05-03 14:44 | 2022-05-03 15:40 | 12 | 000:56 | P | CABLE SOTERRADO AVERIADO | SE MOVIO DE FASE EL T-267 Y SE DEJO LA CARGA TRIFASICA (COLEGIO PREBISTERIANO) FUERA QUE SE ALIMENTAN DEL SU-2A | R22050300135 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 56 | 2022-05-03 | 672 | keep | 0 | May | 2022 | 0.0004577 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 14:44 | 2022-05-03 15:40 | 40 | 000:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y REPARO BAJANTE DE LINEA A CAJA | R22050300142 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 56 | 2022-05-03 | 2240 | keep | 0 | May | 2022 | 0.0015257 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-03 14:47 | 2022-05-03 15:55 | 1617 | 001:08 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-05-03 | 109956 | keep | 0 | May | 2022 | 0.074891 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-05-03 14:47 | 2022-05-03 15:55 | 1017 | 001:08 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-05-03 | 69156 | keep | 0 | May | 2022 | 0.047102 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-03 14:47 | 2022-05-03 15:55 | 828 | 001:08 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-05-03 | 56304 | keep | 0 | May | 2022 | 0.038348 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
BAYAMON | 2022-05-03 15:00 | 2022-05-03 22:22 | 60 | 007:22 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22050300649 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 442 | 2022-05-03 | 26520 | keep | 0 | May | 2022 | 0.018063 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-03 15:05 | 2022-05-03 16:33 | 100 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22050300652 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2022-05-03 | 8800 | keep | 0 | May | 2022 | 0.0059936 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-03 15:05 | 2022-05-03 16:46 | 65 | 001:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S22050300302 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2022-05-03 | 6565 | keep | 0 | May | 2022 | 0.0044714 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
AGUADILLA | 2022-05-03 15:09 | 2022-05-03 21:52 | 30 | 006:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050300421 | New_Event | Vegetation Contact | Include | Include | Vegetation | 403 | 2022-05-03 | 12090 | keep | 0 | May | 2022 | 0.0082344 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-03 15:26 | 2022-05-03 16:38 | 10 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR 1 X 40 EN CORTE DE LINEA | S22050300722 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2022-05-03 | 720 | keep | 0 | May | 2022 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-03 15:31 | 2022-05-03 20:10 | 50 | 004:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | B22050300662 | New_Event |  |  | Include | Wildlife | 279 | 2022-05-03 | 13950 | keep | 0 | May | 2022 | 0.0095013 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-03 15:31 | 2022-05-03 17:59 | 120 | 002:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO Y SE LEVANTO LINEA PRIMARIA PARTIDA | P22050300229 | New_Event | Wire Down | Include | Include | Equipment | 148 | 2022-05-03 | 17760 | keep | 0 | May | 2022 | 0.012096 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-05-03 15:32 | 2022-05-03 19:50 | 8 | 004:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22050300335 | New_Event | Bad Weather | Include | Include | Weather | 258 | 2022-05-03 | 2064 | keep | 0 | May | 2022 | 0.0014058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-05-03 15:37 | 2022-05-03 15:40 | 5961 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1713-05 LLEVANDO 95% 1717-02 SE CERRO POR SCADA | B22050300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-05-03 | 17883 | keep | 0 | May | 2022 | 0.01218 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-05-03 15:37 | 2022-05-03 15:40 | 865 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1713-05 LLEVANDO 95% 1717-02 SE CERRO POR SCADA | B22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-03 | 2595 | keep | 0 | May | 2022 | 0.0017674 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
UTUADO | 2022-05-03 15:39 | 2022-05-03 21:00 | 100 | 005:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300337 | New_Event | Bad Weather | Include | Include | Weather | 321 | 2022-05-03 | 32100 | keep | 0 | May | 2022 | 0.021863 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-03 15:40 | 2022-05-03 15:41 | 3046 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR EN SERVICIO | R22050300142 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-03 | 3046 | keep | 0 | May | 2022 | 0.0020746 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-03 15:40 | 2022-05-03 18:05 | 596 | 002:25 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE MASIVO CON GOI BY-220503-06A | B22050300560 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-05-03 | 86420 | keep | 0 | May | 2022 | 0.05886 | 0.00040593 | Sustained | FALSE | FALSE | Not_TMED_Event | 596
SAN JUAN | 2022-05-03 15:41 | 2022-05-03 18:08 | 12 | 002:27 | P | CABLE SOTERRADO AVERIADO | SE MOVIO DE FASE DEL T-267 Y SE DEJO LA CARGA TRIFASICA (COLEGIO PREBISTERIANO) FUERA QUE SE ALIMENTAN DEL SU-2A | R22050300135 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 147 | 2022-05-03 | 1764 | keep | 0 | May | 2022 | 0.0012015 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-03 15:41 | 2022-05-03 16:15 | 40 | 000:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y REPARO BAJANTE DE LINEA A CAJA | R22050300142 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 34 | 2022-05-03 | 1360 | keep | 0 | May | 2022 | 0.00092629 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-03 15:42 | 2022-05-04 14:12 | 9 | 022:30 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PODRIDA | B22050300669 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1350 | 2022-05-03 | 12150 | keep | 0 | May | 2022 | 0.0082753 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-05-03 15:42 | 2022-05-04 11:17 | 9 | 019:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | B22050300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1175 | 2022-05-03 | 10575 | keep | 0 | May | 2022 | 0.0072026 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2022-05-03 15:43 | 2022-05-03 18:45 | 6 | 003:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A22050300339 | New_Event | Secondary Wire Down | Include | Include | Equipment | 182 | 2022-05-03 | 1092 | keep | 0 | May | 2022 | 0.00074376 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-03 15:47 | 2022-05-04 04:18 | 50 | 012:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050300540 | New_Event | Vegetation Contact | Include | Include | Vegetation | 751 | 2022-05-03 | 37550 | keep | 0 | May | 2022 | 0.025575 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-03 15:55 | 2022-05-04 17:40 | 20 | 025:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | M22050300029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1545 | 2022-05-03 | 30900 | keep | 0 | May | 2022 | 0.021046 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-03 15:59 | 2022-05-03 18:32 | 2859 | 002:33 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL BKR PARA LEVANTAR NEUTRAL PRIMARIO ROTO | C22050300135 | New_Event | Wire Down | Include | Include | Equipment | 153 | 2022-05-03 | 437427 | keep | 0 | May | 2022 | 0.29793 | 0.0019473 | Sustained | FALSE | FALSE | Not_TMED_Event | 2859
SAN JUAN | 2022-05-03 16:00 | 2022-05-03 18:29 | 15 | 002:29 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | S22050300737 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-05-03 | 2235 | keep | 0 | May | 2022 | 0.0015222 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-03 16:07 | 2022-05-03 19:30 | 120 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU 1 | B22050300679 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2022-05-03 | 24360 | keep | 0 | May | 2022 | 0.016591 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-05-03 16:13 | 2022-05-03 19:00 | 300 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050300518 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2022-05-03 | 50100 | keep | 0 | May | 2022 | 0.034123 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-05-03 16:13 | 2022-05-03 19:26 | 2 | 003:13 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS Y BAMBUS SOBRE LAS LINEAS | M22050300519 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-05-03 | 386 | keep | 0 | May | 2022 | 0.0002629 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2022-05-03 16:17 | 2022-05-03 16:18 | 7 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | P22050300108 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-03 | 7 | keep | 0 | May | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-05-03 16:27 | 2022-05-03 20:55 | 10 | 004:28 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S22050300749 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-05-03 | 2680 | keep | 0 | May | 2022 | 0.0018253 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-05-03 16:27 | 2022-05-03 22:08 | 70 | 005:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO TRAMO AVERIADO PARA CONTINUAR TRABAJOS MAÃ‘ANA | A22050300356 | New_Event | Wire Down | Include | Include | Equipment | 341 | 2022-05-03 | 23870 | keep | 0 | May | 2022 | 0.016258 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-05-03 16:30 | 2022-05-03 17:40 | 430 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO Y SE RETIRO NEUTRAL TOCANDO CON LINEA PRIMARIA SE CERRO MACHETES | M22050300533 | Partial_restoration | Wire Down | Include | Include | Equipment | 70 | 2022-05-03 | 30100 | keep | 0 | May | 2022 | 0.020501 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-03 16:38 | 2022-05-03 21:35 | 300 | 004:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M22050300535 | New_Event | Cutout Failure | Include | Include | Equipment | 297 | 2022-05-03 | 89100 | keep | 0 | May | 2022 | 0.060686 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2022-05-03 16:42 | 2022-05-03 16:43 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050300141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 2450 | keep | 0 | May | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
VEGA BAJA | 2022-05-03 16:52 | 2022-05-03 17:07 | 1 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA XMR | B22050300700 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-05-03 | 15 | keep | 0 | May | 2022 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-03 16:57 | 2022-05-04 17:32 | 6 | 024:35 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | B22050300702 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1475 | 2022-05-03 | 8850 | keep | 0 | May | 2022 | 0.0060277 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-05-03 17:03 | 2022-05-03 20:21 | 1 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR NO CAUSA | C22050300146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2022-05-03 | 198 | keep | 0 | May | 2022 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-03 17:14 | 2022-05-04 05:17 | 19 | 012:03 | P | OTRAS CAUSAS | 3 X 100 SE DEJO RISER @CLIENTE FUERA | B22050300708 | New_Event | Other Causes | Include | Include | Other | 723 | 2022-05-03 | 13737 | keep | 0 | May | 2022 | 0.0093562 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
UTUADO | 2022-05-03 17:19 | 2022-05-04 10:35 | 6 | 017:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050300362 | New_Event | Bad Weather | Include | Include | Weather | 1036 | 2022-05-03 | 6216 | keep | 0 | May | 2022 | 0.0042337 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-05-03 17:21 | 2022-05-03 21:53 | 6 | 004:32 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22050300151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2022-05-03 | 1632 | keep | 0 | May | 2022 | 0.0011115 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-05-03 17:22 | 2022-05-03 18:35 | 7 | 001:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN XMR REPARO NEUTRAL SECUNDARIO | C22050300149 | New_Event | Secondary Wire Down | Include | Include | Equipment | 73 | 2022-05-03 | 511 | keep | 0 | May | 2022 | 0.00034804 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-03 17:25 | 2022-05-03 19:03 | 15 | 001:38 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | S22050300776 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-05-03 | 1470 | keep | 0 | May | 2022 | 0.0010012 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-05-03 17:28 | 2022-05-03 19:26 | 93 | 001:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE INSTALO RIGIDO | R22050300153 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 118 | 2022-05-03 | 10974 | keep | 0 | May | 2022 | 0.0074743 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2022-05-03 17:34 | 2022-05-03 21:20 | 50 | 003:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 Y 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22050300565 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2022-05-03 | 11300 | keep | 0 | May | 2022 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-05-03 17:36 | 2022-05-03 17:38 | 989 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22050300153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-03 | 1978 | keep | 0 | May | 2022 | 0.0013472 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
BAYAMON | 2022-05-03 17:38 | 2022-05-03 19:46 | 8 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO CAJA PRIMARIA Y PARARRAYO | B22050300719 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2022-05-03 | 1024 | keep | 0 | May | 2022 | 0.00069744 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-03 17:40 | 2022-05-03 17:42 | 761 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1421-01 | S22050300787 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-03 | 1522 | keep | 0 | May | 2022 | 0.0010366 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2022-05-03 17:40 | 2022-05-03 17:42 | 1498 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1310-04 | S22050300787 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-03 | 2996 | keep | 0 | May | 2022 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
FAJARDO | 2022-05-03 17:40 | 2022-05-03 18:45 | 8 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO DEL TRANSFORMADOR Y SE REEMPLAZO CONECTOR EN BAJANTE SECUNDARIO. Y SE DIO CONECTOR EN TOMA | R22050300155 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2022-05-03 | 520 | keep | 0 | May | 2022 | 0.00035417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-05-03 17:40 | 2022-05-03 18:55 | 8 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y VARIOS TRAMOS DE LA SECUNDARIA | R22050300156 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2022-05-03 | 600 | keep | 0 | May | 2022 | 0.00040866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-05-03 17:40 | 2022-05-03 18:30 | 50 | 000:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR AVE | P22050300258 | New_Event |  |  | Include | Wildlife | 50 | 2022-05-03 | 2500 | keep | 0 | May | 2022 | 0.0017027 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-03 17:40 | 2022-05-03 18:04 | 1 | 000:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN RISER SE REPARO NEUTRAL TOCANDO CON LINEA PRIMARIA | M22050300580 | Partial_restoration | Wire Down | Include | Include | Equipment | 24 | 2022-05-03 | 24 | keep | 0 | May | 2022 | 1.6346e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-03 17:51 | 2022-05-03 19:40 | 100 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22050300582 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2022-05-03 | 10900 | keep | 0 | May | 2022 | 0.0074239 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-05-03 17:55 | 2022-05-03 21:33 | 1 | 003:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22050300724 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2022-05-03 | 218 | keep | 0 | May | 2022 | 0.00014848 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-03 17:56 | 2022-05-03 20:15 | 80 | 002:19 | P | DESGANCHE | 1 X 100 Y 2 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22050300583 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-05-03 | 11120 | keep | 0 | May | 2022 | 0.0075738 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-03 18:00 | 2022-05-04 10:32 | 1 | 016:32 | P | NO SE REPORTO CAUSA | 3 X 20 EN RISER | S22050300804 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 992 | 2022-05-03 | 992 | keep | 0 | May | 2022 | 0.00067565 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-03 18:02 | 2022-05-04 01:05 | 68 | 007:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22050300726 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 423 | 2022-05-03 | 28764 | keep | 0 | May | 2022 | 0.019591 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
HUMACAO | 2022-05-03 18:16 | 2022-05-03 18:42 | 1 | 000:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 CRUCE X AVE | C22050300161 | New_Event |  |  | Include | Wildlife | 26 | 2022-05-03 | 26 | keep | 0 | May | 2022 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-03 18:30 | 2022-05-03 19:34 | 1 | 001:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | P22050300264 | New_Event | Cutout Failure | Include | Include | Equipment | 64 | 2022-05-03 | 64 | keep | 0 | May | 2022 | 4.359e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-03 18:47 | 2022-05-04 11:43 | 34 | 016:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22050300165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1016 | 2022-05-03 | 34544 | keep | 0 | May | 2022 | 0.023528 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2022-05-03 18:57 | 2022-05-03 20:18 | 18 | 001:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN BOVEDA AREA INUNDADA POR LLUVIA | B22050300739 | New_Event | Bad Weather | Include | Include | Weather | 81 | 2022-05-03 | 1458 | keep | 0 | May | 2022 | 0.00099304 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-05-03 19:03 | 2022-05-03 19:04 | 766 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 LLEVANDO CARGA 1709-05 Y 50% DE SU CARGA POR 1909-07 | B22050300740 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 766 | keep | 0 | May | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-05-03 19:03 | 2022-05-03 19:04 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 LLEVANDO CARGA 1709-05 Y 50% DE SU CARGA POR 1909-07 | B22050300740 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 2364 | keep | 0 | May | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2022-05-03 19:04 | 2022-05-03 21:58 | 1 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B22050300824 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-05-03 | 174 | keep | 0 | May | 2022 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-03 19:06 | 2022-05-04 01:30 | 6 | 006:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN BANCO NIDO | B22050300742 | New_Event |  |  | Include | Wildlife | 384 | 2022-05-03 | 2304 | keep | 0 | May | 2022 | 0.0015692 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-03 19:10 | 2022-05-03 19:11 | 6136 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B22050300000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-03 | 6136 | keep | 0 | May | 2022 | 0.0041792 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-03 19:11 | 2022-05-03 21:16 | 150 | 002:05 | P | DESGANCHE | DESGANCHE Y 2 X 100 EN CONVERTIDOR | B22050300655 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-05-03 | 18750 | keep | 0 | May | 2022 | 0.012771 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-03 19:11 | 2022-05-03 22:07 | 3 | 002:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22050300312 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2022-05-03 | 528 | keep | 0 | May | 2022 | 0.00035962 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-05-03 19:13 | 2022-05-03 20:21 | 75 | 001:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA QUEMADA | P22050300271 | New_Event | Cutout Failure | Include | Include | Equipment | 68 | 2022-05-03 | 5100 | keep | 0 | May | 2022 | 0.0034736 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-05-03 19:16 | 2022-05-03 20:38 | 817 | 001:22 | T | NO SE REPORTO CAUSA | CERRO BKR ELECTRICAMENTE BANDERA 3 FASES INSTANTANEA | C22050300171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-05-03 | 66994 | keep | 0 | May | 2022 | 0.045629 | 0.00055645 | Sustained | FALSE | FALSE | Not_TMED_Event | 817
CANOVANAS | 2022-05-03 19:17 | 2022-05-03 20:08 | 6 | 000:51 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22050300160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-05-03 | 306 | keep | 0 | May | 2022 | 0.00020842 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-05-03 19:18 | 2022-05-03 19:50 | 1 | 000:32 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22050300384 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2022-05-03 | 32 | keep | 0 | May | 2022 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-03 19:27 | 2022-05-03 20:26 | 30 | 000:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22050300746 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2022-05-03 | 1770 | keep | 0 | May | 2022 | 0.0012055 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-05-03 19:32 | 2022-05-03 20:50 | 75 | 001:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22050300747 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-05-03 | 5850 | keep | 0 | May | 2022 | 0.0039844 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-05-03 19:48 | 2022-05-04 11:45 | 50 | 015:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22050300615 | New_Event | Wire Down | Include | Include | Equipment | 957 | 2022-05-03 | 47850 | keep | 0 | May | 2022 | 0.03259 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-03 20:25 | 2022-05-03 21:34 | 3 | 001:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA ZAFADA DE AISLADOR | A22050300391 | New_Event | Wire Down | Include | Include | Equipment | 69 | 2022-05-03 | 207 | keep | 0 | May | 2022 | 0.00014099 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-05-03 20:36 | 2022-05-04 01:12 | 50 | 004:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22050300636 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2022-05-03 | 13800 | keep | 0 | May | 2022 | 0.0093991 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-03 20:38 | 2022-05-03 22:25 | 70 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22050300204 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 107 | 2022-05-03 | 7490 | keep | 0 | May | 2022 | 0.0051014 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-03 20:44 | 2022-05-03 22:15 | 100 | 001:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | A22050300392 | New_Event | Wire Down | Include | Include | Equipment | 91 | 2022-05-03 | 9100 | keep | 0 | May | 2022 | 0.006198 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-03 20:46 | 2022-05-04 02:19 | 65 | 005:33 | P | DESGANCHE | 1 X 100 C/L DESGANCHE | S22050300822 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2022-05-03 | 21645 | keep | 0 | May | 2022 | 0.014742 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-05-03 21:21 | 2022-05-04 07:15 | 5 | 009:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050300650 | New_Event | Bad Weather | Include | Include | Weather | 594 | 2022-05-03 | 2970 | keep | 0 | May | 2022 | 0.0020229 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-05-03 21:25 | 2022-05-04 09:52 | 30 | 012:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22050300397 | New_Event | Bad Weather | Include | Include | Weather | 747 | 2022-05-03 | 22410 | keep | 0 | May | 2022 | 0.015263 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-05-03 21:38 | 2022-05-03 21:39 | 1979 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050300287 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 1979 | keep | 0 | May | 2022 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
HUMACAO | 2022-05-03 21:51 | 2022-05-04 07:58 | 1 | 010:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22050300215 | New_Event |  |  | Include | Wildlife | 607 | 2022-05-03 | 607 | keep | 0 | May | 2022 | 0.00041342 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-03 22:03 | 2022-05-04 00:20 | 150 | 002:17 | P | DESGANCHE | 1 X 80 Y 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22050300623 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-05-03 | 20550 | keep | 0 | May | 2022 | 0.013997 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-03 22:05 | 2022-05-04 13:40 | 12 | 015:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA SUBIR 2 TRAMOS CABLE SECUNDARIO Y SE REALIZO DESGANCHE | B22050300623 | New_Event | Secondary Wire Down | Include | Include | Equipment | 935 | 2022-05-03 | 11220 | keep | 0 | May | 2022 | 0.0076419 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-05-03 22:05 | 2022-05-04 09:50 | 70 | 011:45 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22050300640 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 705 | 2022-05-03 | 49350 | keep | 0 | May | 2022 | 0.033612 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-05-03 22:08 | 2022-05-04 12:30 | 100 | 014:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA SE CERRO PUENTES PRIMARIOS | A22050400008 | Additional_clients | Wire Down | Include | Include | Equipment | 862 | 2022-05-03 | 86200 | keep | 0 | May | 2022 | 0.05871 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-03 22:11 | 2022-05-04 00:09 | 100 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO SE REPORTO LA CAUSA | P22050300298 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2022-05-03 | 11800 | keep | 0 | May | 2022 | 0.0080369 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-03 22:29 | 2022-05-04 10:10 | 10 | 011:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE Y SECUNDARIA | B22050300769 | New_Event | Secondary Wire Down | Include | Include | Equipment | 701 | 2022-05-03 | 7010 | keep | 0 | May | 2022 | 0.0047745 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-03 22:30 | 2022-05-04 02:15 | 345 | 003:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050300404 | New_Event | Bad Weather | Include | Include | Weather | 225 | 2022-05-03 | 77625 | keep | 0 | May | 2022 | 0.05287 | 0.00023498 | Sustained | FALSE | FALSE | Not_TMED_Event | 345
HUMACAO | 2022-05-03 22:46 | 2022-05-03 22:47 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 2126 | keep | 0 | May | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
PONCE | 2022-05-03 22:46 | 2022-05-04 16:30 | 25 | 017:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANFORMADOR 50KVA A 7.620KV AVERIADO | P22050300302 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1064 | 2022-05-03 | 26600 | keep | 0 | May | 2022 | 0.018117 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-05-03 22:56 | 2022-05-03 22:57 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050300305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-03 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CAGUAS | 2022-05-03 23:01 | 2022-05-04 08:37 | 20 | 009:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA PRIMARIA DEL TRANSFORMADOR | C22050300222 | New_Event | Wire Down | Include | Include | Equipment | 576 | 2022-05-03 | 11520 | keep | 0 | May | 2022 | 0.0078462 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-05-03 23:20 | 2022-05-04 11:10 | 93 | 011:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA AVERIADA | C22050300224 | New_Event | Cutout Failure | Include | Include | Equipment | 710 | 2022-05-03 | 66030 | keep | 0 | May | 2022 | 0.044973 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
FAJARDO | 2022-05-03 23:29 | 2022-05-03 23:31 | 1902 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 3804 | keep | 0 | May | 2022 | 0.0025909 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2022-05-03 23:29 | 2022-05-03 23:31 | 970 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 1940 | keep | 0 | May | 2022 | 0.0013213 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2022-05-03 23:29 | 2022-05-03 23:31 | 3003 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 6006 | keep | 0 | May | 2022 | 0.0040907 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2022-05-03 23:29 | 2022-05-03 23:31 | 2343 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 4686 | keep | 0 | May | 2022 | 0.0031916 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2022-05-03 23:29 | 2022-05-03 23:31 | 1830 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 3660 | keep | 0 | May | 2022 | 0.0024928 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2022-05-03 23:29 | 2022-05-03 23:31 | 710 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 1420 | keep | 0 | May | 2022 | 0.00096716 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2022-05-03 23:29 | 2022-05-03 23:31 | 1197 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | C22050300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-03 | 2394 | keep | 0 | May | 2022 | 0.0016305 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
FAJARDO | 2022-05-04 01:00 | 2022-05-04 09:22 | 10 | 008:22 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | R22050400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 502 | 2022-05-04 | 5020 | keep | 0 | May | 2022 | 0.0034191 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-04 01:51 | 2022-05-04 07:53 | 386 | 006:02 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTES DE LINEA | B22050400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 362 | 2022-05-04 | 139732 | keep | 0 | May | 2022 | 0.095171 | 0.0002629 | Sustained | FALSE | FALSE | Not_TMED_Event | 386
BAYAMON | 2022-05-04 01:59 | 2022-05-04 15:32 | 10 | 013:33 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y SE RETIRO ENREDADERA | B22050400002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 813 | 2022-05-04 | 8130 | keep | 0 | May | 2022 | 0.0055373 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-04 02:07 | 2022-05-04 02:08 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22050400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 990 | keep | 0 | May | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
FAJARDO | 2022-05-04 02:52 | 2022-05-04 09:27 | 30 | 006:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L REMPLAZO PORTAFUSIBLE | R22050400001 | New_Event | Cutout Failure | Include | Include | Equipment | 395 | 2022-05-04 | 11850 | keep | 0 | May | 2022 | 0.008071 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-05-04 02:56 | 2022-05-04 10:35 | 75 | 007:39 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 SMU-20 SE CORRIGIO TERMINACION SOTERRADA | P22050400001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 459 | 2022-05-04 | 34425 | keep | 0 | May | 2022 | 0.023447 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-05-04 03:36 | 2022-05-04 19:35 | 40 | 015:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050400003 | New_Event | Bad Weather | Include | Include | Weather | 959 | 2022-05-04 | 38360 | keep | 0 | May | 2022 | 0.026127 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-04 03:39 | 2022-05-04 07:45 | 80 | 004:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | A22050400003 | New_Event | Bad Weather | Include | Include | Weather | 246 | 2022-05-04 | 19680 | keep | 0 | May | 2022 | 0.013404 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-05-04 03:53 | 2022-05-04 09:57 | 10 | 006:04 | P | OTRAS CAUSAS | 1 X 10 EN XMR FUSIBLE PODRIDO | R22050400002 | New_Event | Other Causes | Include | Include | Other | 364 | 2022-05-04 | 3640 | keep | 0 | May | 2022 | 0.0024792 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-05-04 04:21 | 2022-05-04 04:22 | 31 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 31 | keep | 0 | May | 2022 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
HUMACAO | 2022-05-04 04:28 | 2022-05-04 09:24 | 12 | 004:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 80 EN TRANSFORMADOR SE REPARO SECUNDARIA Y SE REEMPLAZO 40 PIES DE TOMA 3/4 | C22050400022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 296 | 2022-05-04 | 3552 | keep | 0 | May | 2022 | 0.0024193 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-05-04 04:48 | 2022-05-04 06:29 | 2064 | 001:41 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR. SE ABRIO MACHETES AL 50% DE SU CORRIDA Y SE CERRO POR SCADA | S22050400004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 101 | 2022-05-04 | 208464 | keep | 0 | May | 2022 | 0.14198 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2022-05-04 05:32 | 2022-05-04 13:37 | 33 | 008:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO PUENTE Y AISLADOR | S22050400009 | New_Event | Wire Down | Include | Include | Equipment | 485 | 2022-05-04 | 16005 | keep | 0 | May | 2022 | 0.010901 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BARRANQUITAS | 2022-05-04 06:00 | 2022-05-04 11:40 | 139 | 005:40 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22050400007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2022-05-04 | 47260 | keep | 0 | May | 2022 | 0.032189 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
SAN JUAN | 2022-05-04 06:29 | 2022-05-04 06:50 | 1032 | 000:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO POSTE AISLADOR PARTIDO Y SE RESTABLECIO EL RESTANTE 50% DE LA CARGA. 100% EN SERVICIO | S22050400004 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 21 | 2022-05-04 | 21672 | keep | 0 | May | 2022 | 0.014761 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-04 06:34 | 2022-05-04 12:07 | 40 | 005:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2022-05-04 | 13320 | keep | 0 | May | 2022 | 0.0090722 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-04 06:37 | 2022-05-04 15:27 | 15 | 008:50 | P | DESGANCHE | 1 X 25 EN C/L SE REALIZO DESGANCHE | C22050400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 530 | 2022-05-04 | 7950 | keep | 0 | May | 2022 | 0.0054147 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-05-04 06:44 | 2022-05-04 08:10 | 5 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22050400015 | New_Event |  |  | Include | Wildlife | 86 | 2022-05-04 | 430 | keep | 0 | May | 2022 | 0.00029287 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-05-04 06:49 | 2022-05-04 14:19 | 1 | 007:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIAS Y EL TRI-WIRE | P22050400005 | New_Event | Cutout Failure | Include | Include | Equipment | 450 | 2022-05-04 | 450 | keep | 0 | May | 2022 | 0.00030649 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-04 06:50 | 2022-05-04 06:51 | 2064 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR EN OPERACIONES DE RESTABLECIMIENTO | S22050400004 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-04 | 2064 | keep | 0 | May | 2022 | 0.0014058 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-04 06:51 | 2022-05-04 08:28 | 454 | 001:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO POSTE AISLADOR PARTIDO Y SE RESTABLECIO SERVICIO | S22050400004 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 97 | 2022-05-04 | 44038 | keep | 0 | May | 2022 | 0.029994 | 0.00030922 | Sustained | FALSE | FALSE | Not_TMED_Event | 454
ARECIBO | 2022-05-04 06:59 | 2022-05-04 10:17 | 1 | 003:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO PORTAFUSIBLE AVERIADO | A22050400006 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2022-05-04 | 198 | keep | 0 | May | 2022 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-04 07:06 | 2022-05-04 09:40 | 80 | 002:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22050400008 | New_Event |  |  | Include | Wildlife | 154 | 2022-05-04 | 12320 | keep | 0 | May | 2022 | 0.0083911 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-04 07:09 | 2022-05-04 07:10 | 602 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR | S22050400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-04 | 602 | keep | 0 | May | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-05-04 07:10 | 2022-05-04 13:35 | 55 | 006:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA Y SE REEMPLAZO CAJA | S22050400023 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 385 | 2022-05-04 | 21175 | keep | 0 | May | 2022 | 0.014422 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2022-05-04 07:26 | 2022-05-04 07:27 | 453 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 10% DE SU CARGA POR EL 1806-02 | B22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 453 | keep | 0 | May | 2022 | 0.00030854 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2022-05-04 07:26 | 2022-05-04 07:27 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 10% DEL 1717-01 | B22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 4622 | keep | 0 | May | 2022 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2022-05-04 07:29 | 2022-05-04 19:54 | 12 | 012:25 | P | NO SE REPORTO CAUSA | 1 X 12 NX EN T13 HACIA T12 | B22050400027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 745 | 2022-05-04 | 8940 | keep | 0 | May | 2022 | 0.006089 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-04 07:41 | 2022-05-04 08:42 | 65 | 001:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 40 EN CORTES DE LINEA CRUCE POR AVE | C22050400027 | New_Event |  |  | Include | Wildlife | 61 | 2022-05-04 | 3965 | keep | 0 | May | 2022 | 0.0027005 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-05-04 07:53 | 2022-05-04 17:47 | 150 | 009:54 | P | NO SE REPORTO CAUSA | INDICA FOREMAN DAN JESTER QUE ENERGIZO Y NO ENCONTRO AVERIA | B22050400001 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 594 | 2022-05-04 | 89100 | keep | 0 | May | 2022 | 0.060686 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 873 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 873 | keep | 0 | May | 2022 | 0.0005946 | 0.0005946 | Momentary | FALSE | FALSE | Not_TMED_Event | 873
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 1261 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 1261 | keep | 0 | May | 2022 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 2713 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 2713 | keep | 0 | May | 2022 | 0.0018478 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 51 | keep | 0 | May | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 285 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 285 | keep | 0 | May | 2022 | 0.00019411 | 0.00019411 | Momentary | FALSE | FALSE | Not_TMED_Event | 285
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 1253 | keep | 0 | May | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 1266 | keep | 0 | May | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 411 | keep | 0 | May | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 863 | keep | 0 | May | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 309 | keep | 0 | May | 2022 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 176 | keep | 0 | May | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-04 07:56 | 2022-05-04 07:57 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 974 | keep | 0 | May | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
HUMACAO | 2022-05-04 07:58 | 2022-05-04 07:59 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22050400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 2450 | keep | 0 | May | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-05-04 07:59 | 2022-05-04 13:47 | 1 | 005:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22050300215 | Partial_restoration |  |  | Include | Wildlife | 348 | 2022-05-04 | 348 | keep | 0 | May | 2022 | 0.00023702 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-04 07:59 | 2022-05-04 16:45 | 50 | 008:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M22050400014 | New_Event |  |  | Include | Wildlife | 526 | 2022-05-04 | 26300 | keep | 0 | May | 2022 | 0.017913 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-04 08:01 | 2022-05-04 10:36 | 6 | 002:35 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | S22050400039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-05-04 | 930 | keep | 0 | May | 2022 | 0.00063342 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-05-04 08:07 | 2022-05-04 14:39 | 48 | 006:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L SE LEVANTARON 3 TRAMOS CONDUCTOR PRIMARIO | B22050400036 | New_Event | Wire Down | Include | Include | Equipment | 392 | 2022-05-04 | 18816 | keep | 0 | May | 2022 | 0.012815 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
CANOVANAS | 2022-05-04 08:13 | 2022-05-04 12:19 | 1 | 004:06 | P | DESGANCHE | 1 X 20 EN C/L | R22050400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2022-05-04 | 246 | keep | 0 | May | 2022 | 0.00016755 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-05-04 08:19 | 2022-05-04 08:20 | 4882 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 4882 | keep | 0 | May | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
CANOVANAS | 2022-05-04 08:23 | 2022-05-04 09:46 | 30 | 001:23 | P | DESGANCHE | 1 X 30 EN C/L | R22050400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-05-04 | 2490 | keep | 0 | May | 2022 | 0.0016959 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-04 08:34 | 2022-05-04 13:33 | 20 | 004:59 | P | DESGANCHE | 1 X 25 EN C/L | R22050400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 299 | 2022-05-04 | 5980 | keep | 0 | May | 2022 | 0.004073 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-05-04 08:39 | 2022-05-04 13:25 | 188 | 004:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C22050400041 | New_Event |  |  | Include | Wildlife | 286 | 2022-05-04 | 53768 | keep | 0 | May | 2022 | 0.036621 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
CANOVANAS | 2022-05-04 08:40 | 2022-05-04 14:30 | 13 | 005:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN C/L CRUCE X AVE REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | R22050400014 | New_Event |  |  | Include | Wildlife | 350 | 2022-05-04 | 4550 | keep | 0 | May | 2022 | 0.003099 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-05-04 09:01 | 2022-05-04 19:46 | 63 | 010:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE REMPLAZO CONECTOR PRIMARIO QUEMADO | B22050400053 | New_Event | Wire Down | Include | Include | Equipment | 645 | 2022-05-04 | 40635 | keep | 0 | May | 2022 | 0.027676 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
GUAYAMA | 2022-05-04 09:01 | 2022-05-04 17:23 | 6 | 008:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZARON BAJANTES SECUNDARIOS DE TRANSFORMADOR AVERIADOS POR CAMION | P22050400078 | New_Event |  |  | Include | Wildlife | 502 | 2022-05-04 | 3012 | keep | 0 | May | 2022 | 0.0020515 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-05-04 09:21 | 2022-05-04 12:10 | 4 | 002:49 | P | HERRAJE ROTO O PODRIDO | REMPLAZO DE CRUCETA INSTALO CAJA Y PARARRAYO | R22050400017 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 169 | 2022-05-04 | 676 | keep | 0 | May | 2022 | 0.00046042 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-05-04 09:30 | 2022-05-04 12:26 | 20 | 002:56 | P | DESGANCHE | SE RETIRO BAMBUAS Y SE CERRO CAJAS EN TRANSFORMADOR | P22050400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-05-04 | 3520 | keep | 0 | May | 2022 | 0.0023975 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-04 09:31 | 2022-05-05 11:37 | 12 | 026:06 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR AVERIADO DE 50KVA | S22050400248 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1566 | 2022-05-04 | 18792 | keep | 0 | May | 2022 | 0.012799 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-04 09:41 | 2022-05-04 09:42 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P22050400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 2113 | keep | 0 | May | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
UTUADO | 2022-05-04 09:46 | 2022-05-05 14:08 | 55 | 028:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PARTIDA | A22050400027 | New_Event | Wire Down | Include | Include | Equipment | 1702 | 2022-05-04 | 93610 | keep | 0 | May | 2022 | 0.063757 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
VEGA BAJA | 2022-05-04 09:48 | 2022-05-04 13:29 | 6 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22050400067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-05-04 | 1326 | keep | 0 | May | 2022 | 0.00090313 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-04 10:05 | 2022-05-04 12:33 | 1 | 002:28 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22050400074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2022-05-04 | 148 | keep | 0 | May | 2022 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-04 10:07 | 2022-05-04 11:49 | 163 | 001:42 | P | DESGANCHE | 1 X 100 EN C/L | R22050400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-05-04 | 16626 | keep | 0 | May | 2022 | 0.011324 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
CAGUAS | 2022-05-04 10:11 | 2022-05-04 16:02 | 14 | 005:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA QUE ESTABA FUERA DESDE MARIA Y SE DIVIDIO LA CARGA | C22050400058 | New_Event | Service Transformer Failure | Include | Include | Equipment | 351 | 2022-05-04 | 4914 | keep | 0 | May | 2022 | 0.0033469 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
UTUADO | 2022-05-04 10:16 | 2022-05-04 12:50 | 50 | 002:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22050400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-05-04 | 7700 | keep | 0 | May | 2022 | 0.0052444 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-04 10:19 | 2022-05-04 11:20 | 1952 | 001:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR VEHICULO IMPACTA TENSOR PRIMARIO Y CRUZA FASE PRIMARIA | P22050400026 | New_Event |  |  | Include | Wildlife | 61 | 2022-05-04 | 119072 | keep | 0 | May | 2022 | 0.081099 | 0.0013295 | Sustained | FALSE | FALSE | Not_TMED_Event | 1952
MAYAGÃœEZ | 2022-05-04 10:26 | 2022-05-04 10:30 | 1337 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-05-04 | 5348 | keep | 0 | May | 2022 | 0.0036425 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
SAN JUAN | 2022-05-04 10:27 | 2022-05-04 14:00 | 5 | 003:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S22050400069 | New_Event | Cutout Failure | Include | Include | Equipment | 213 | 2022-05-04 | 1065 | keep | 0 | May | 2022 | 0.00072537 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-05-04 10:30 | 2022-05-04 12:30 | 30 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | R22050400025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-05-04 | 3600 | keep | 0 | May | 2022 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-04 10:35 | 2022-05-05 11:51 | 40 | 025:16 | P | CABLE SOTERRADO AVERIADO | SE ABRIO DEL SU-4 AL SU-22 PARA PODER HACER PRUEBA CON MAQUINA. PROBO MALO Y ESTA TRASPATIO | R22050400037 | New_Event | UG Cable Fault | Include | Include | Equipment | 1516 | 2022-05-04 | 60640 | keep | 0 | May | 2022 | 0.041302 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-04 10:35 | 2022-05-04 15:00 | 5 | 004:25 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO | M22050400153 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 265 | 2022-05-04 | 1325 | keep | 0 | May | 2022 | 0.00090245 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-04 10:46 | 2022-05-04 18:30 | 350 | 007:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CONVERTIDOR MAL TIEMPO VIENTOS FUERTES | M22050400062 | New_Event | Bad Weather | Include | Include | Weather | 464 | 2022-05-04 | 162400 | keep | 0 | May | 2022 | 0.11061 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
PONCE | 2022-05-04 10:57 | 2022-05-04 12:54 | 50 | 001:57 | P | NO SE REPORTO CAUSA | NO SE ENCONTRO CAUSA | P22050400035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2022-05-04 | 5850 | keep | 0 | May | 2022 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-04 11:04 | 2022-05-04 18:16 | 7 | 007:12 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO DE 37. KVA SE PASO CARGA A XMR ADYACENTE DE 50 KVA | B22050400080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 432 | 2022-05-04 | 3024 | keep | 0 | May | 2022 | 0.0020596 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-05-04 11:08 | 2022-05-04 12:40 | 309 | 001:32 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA PODER RETIRAR BAMBUAS SOBRE LAS LINEA 2000 DE 38KV. LINEA DISTRIBUCION DEBAJO | M22050400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 92 | 2022-05-04 | 28428 | keep | 0 | May | 2022 | 0.019362 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
SAN JUAN | 2022-05-04 11:30 | 2022-05-04 15:09 | 106 | 003:39 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S22050400080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-05-04 | 23214 | keep | 0 | May | 2022 | 0.015811 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
AGUADILLA | 2022-05-04 11:38 | 2022-05-04 17:08 | 10 | 005:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050400082 | New_Event | Bad Weather | Include | Include | Weather | 330 | 2022-05-04 | 3300 | keep | 0 | May | 2022 | 0.0022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-05-04 11:47 | 2022-05-04 12:20 | 5 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA Y SE REEMPLAZO 20 PIES DE TOMA | C22050400049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2022-05-04 | 165 | keep | 0 | May | 2022 | 0.00011238 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-05-04 12:01 | 2022-05-04 13:08 | 3 | 001:07 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22050400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-05-04 | 201 | keep | 0 | May | 2022 | 0.0001369 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-05-04 12:10 | 2022-05-04 14:36 | 3 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO TRES TOMAS | C22050400061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2022-05-04 | 438 | keep | 0 | May | 2022 | 0.00029832 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-05-04 12:10 | 2022-05-04 14:30 | 54 | 002:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C22050400077 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2022-05-04 | 7560 | keep | 0 | May | 2022 | 0.0051491 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2022-05-04 12:16 | 2022-05-06 16:00 | 24 | 051:44 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVICIONAL DE PROVICIONAL EXISTENTE A T-36 | R22050400037 | New_Event | UG Cable Fault | Include | Include | Equipment | 3104 | 2022-05-04 | 74496 | keep | 0 | May | 2022 | 0.050739 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2022-05-04 12:16 | 2022-05-05 10:35 | 40 | 022:19 | P | CABLE SOTERRADO AVERIADO | SE ABRIO DEL SU-4 AL SU-22 PARA PODER HACER PRUEBA CON MAQUINA. PROBO MALO Y ESTA TRASPATIO | R22050400037 | New_Event | UG Cable Fault | Include | Include | Equipment | 1339 | 2022-05-04 | 53560 | keep | 0 | May | 2022 | 0.036479 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-05-04 12:33 | 2022-05-04 16:27 | 1 | 003:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO BAJANTE SECUNDARIO DE MONTURA TRIFASICA | P22050400050 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2022-05-04 | 234 | keep | 0 | May | 2022 | 0.00015938 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-04 12:39 | 2022-05-04 17:39 | 100 | 005:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA INFORMA REQUIERE DESGANCHE | A22050400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-05-04 | 30000 | keep | 0 | May | 2022 | 0.020433 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-05-04 12:44 | 2022-05-04 14:38 | 65 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | C22050400085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-05-04 | 7410 | keep | 0 | May | 2022 | 0.0050469 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-05-04 12:50 | 2022-05-04 23:37 | 6 | 010:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22050400102 | New_Event | Wire Down | Include | Include | Equipment | 647 | 2022-05-04 | 3882 | keep | 0 | May | 2022 | 0.002644 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-05-04 12:52 | 2022-05-04 14:10 | 1 | 001:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE POR BAMBUA | C22050400087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-05-04 | 78 | keep | 0 | May | 2022 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-04 12:53 | 2022-05-04 15:07 | 21 | 002:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA POR UNO DE 100KVA A 7620 | P22050400027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 134 | 2022-05-04 | 2814 | keep | 0 | May | 2022 | 0.0019166 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2022-05-04 12:54 | 2022-05-04 16:13 | 19 | 003:19 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA | S22050400093 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 199 | 2022-05-04 | 3781 | keep | 0 | May | 2022 | 0.0025752 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-05-04 13:02 | 2022-05-04 17:52 | 12 | 004:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN XMR SE REMPLAZO SECUNDARIA ABIERTA | B22050400102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 290 | 2022-05-04 | 3480 | keep | 0 | May | 2022 | 0.0023702 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-04 13:09 | 2022-05-05 01:20 | 10 | 012:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22050400112 | New_Event | Bad Weather | Include | Include | Weather | 731 | 2022-05-04 | 7310 | keep | 0 | May | 2022 | 0.0049788 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-04 13:16 | 2022-05-04 15:52 | 60 | 002:36 | P | SECUNDARIA/DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LAS LINEAS | M22050400113 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 156 | 2022-05-04 | 9360 | keep | 0 | May | 2022 | 0.0063751 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-04 13:29 | 2022-05-04 15:25 | 70 | 001:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22050400058 | New_Event | Wire Down | Include | Include | Equipment | 116 | 2022-05-04 | 8120 | keep | 0 | May | 2022 | 0.0055305 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-05-04 13:30 | 2022-05-04 13:48 | 12 | 000:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S22050400099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 18 | 2022-05-04 | 216 | keep | 0 | May | 2022 | 0.00014712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-05-04 13:32 | 2022-05-04 17:47 | 15 | 004:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 25KVA @ 4.16KV | P22050400052 | New_Event | Service Transformer Failure | Include | Include | Equipment | 255 | 2022-05-04 | 3825 | keep | 0 | May | 2022 | 0.0026052 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-04 13:48 | 2022-05-04 13:49 | 108 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22050400215 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 108 | keep | 0 | May | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2022-05-04 13:48 | 2022-05-04 13:49 | 1368 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22050400215 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 1368 | keep | 0 | May | 2022 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2022-05-04 13:48 | 2022-05-04 13:49 | 2064 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22050400215 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 2064 | keep | 0 | May | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2022-05-04 13:48 | 2022-05-04 13:49 | 1681 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22050400215 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 1681 | keep | 0 | May | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-04 13:48 | 2022-05-04 13:49 | 2435 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22050400215 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 2435 | keep | 0 | May | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2022-05-04 13:48 | 2022-05-04 13:49 | 726 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22050400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 726 | keep | 0 | May | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-05-04 13:48 | 2022-05-04 13:49 | 225 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22050400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 225 | keep | 0 | May | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-04 13:48 | 2022-05-04 13:49 | 870 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22050400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-05-04 13:48 | 2022-05-04 13:49 | 1598 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22050400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-04 | 1598 | keep | 0 | May | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
UTUADO | 2022-05-04 13:48 | 2022-05-04 16:00 | 10 | 002:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22050400062 | New_Event | Bad Weather | Include | Include | Weather | 132 | 2022-05-04 | 1320 | keep | 0 | May | 2022 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-04 13:50 | 2022-05-04 13:53 | 12 | 000:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S22050400099 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 3 | 2022-05-04 | 36 | keep | 0 | May | 2022 | 2.4519e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-04 13:53 | 2022-05-04 14:00 | 108 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S22050400215 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-04 | 756 | keep | 0 | May | 2022 | 0.00051491 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2022-05-04 13:53 | 2022-05-04 14:00 | 1368 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S22050400215 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-04 | 9576 | keep | 0 | May | 2022 | 0.0065222 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2022-05-04 13:53 | 2022-05-04 14:00 | 2064 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S22050400215 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-04 | 14448 | keep | 0 | May | 2022 | 0.0098405 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2022-05-04 13:53 | 2022-05-04 14:00 | 1681 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 SU CARGA POR 1303-4 | S22050400215 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-04 | 11767 | keep | 0 | May | 2022 | 0.0080145 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-04 13:53 | 2022-05-04 14:00 | 2435 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S22050400215 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-04 | 17045 | keep | 0 | May | 2022 | 0.011609 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2022-05-04 13:53 | 2022-05-04 14:00 | 726 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S22050400215 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-04 | 5082 | keep | 0 | May | 2022 | 0.0034613 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-05-04 13:53 | 2022-05-04 14:00 | 225 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 SU CARGA POR 1303-5 | S22050400215 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-04 | 1575 | keep | 0 | May | 2022 | 0.0010727 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-04 13:53 | 2022-05-04 14:00 | 870 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S22050400215 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-04 | 6090 | keep | 0 | May | 2022 | 0.0041479 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2022-05-04 13:54 | 2022-05-04 15:34 | 50 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050400124 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2022-05-04 | 5000 | keep | 0 | May | 2022 | 0.0034055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-04 13:58 | 2022-05-04 14:00 | 858 | 000:02 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 20% POR 1303-02 | S22050400215 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-04 | 1716 | keep | 0 | May | 2022 | 0.0011688 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-04 13:58 | 2022-05-04 14:00 | 3932 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 SU CARGA POR 1303-03 | S22050400215 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-04 | 7864 | keep | 0 | May | 2022 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2022-05-04 13:58 | 2022-05-04 14:00 | 1598 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 3200 SU CARGA POR 1303-04 | S22050400215 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-04 | 3196 | keep | 0 | May | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-05-04 13:58 | 2022-05-04 14:00 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO | S22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-04 | 3230 | keep | 0 | May | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2022-05-04 14:00 | 2022-05-04 14:33 | 12 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S22050400099 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 33 | 2022-05-04 | 396 | keep | 0 | May | 2022 | 0.00026971 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-05-04 14:00 | 2022-05-05 14:08 | 7 | 024:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR Y SE REMPLAZO CAJA Y BAJANTE SECUNDARIO | S22050400226 | New_Event | Cutout Failure | Include | Include | Equipment | 1448 | 2022-05-04 | 10136 | keep | 0 | May | 2022 | 0.0069036 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-04 14:04 | 2022-05-04 16:43 | 12 | 002:39 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22050400105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-05-04 | 1908 | keep | 0 | May | 2022 | 0.0012995 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-05-04 14:07 | 2022-05-04 16:35 | 40 | 002:28 | P | DESGANCHE | 1 X 40 EN AEREO PROVISIONAL SE REALIZO DESGANCHE | S22040500167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-05-04 | 5920 | keep | 0 | May | 2022 | 0.0040321 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-04 14:09 | 2022-05-04 16:07 | 80 | 001:58 | P | DESGANCHE | 1 X 65 EN C/L | R22050400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-05-04 | 9440 | keep | 0 | May | 2022 | 0.0064295 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-05-04 14:31 | 2022-05-04 17:07 | 10 | 002:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE LINEA A CAJA EN XMR | B22050400112 | New_Event | Wire Down | Include | Include | Equipment | 156 | 2022-05-04 | 1560 | keep | 0 | May | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-04 14:33 | 2022-05-04 14:49 | 108 | 000:16 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA SE ABRIO 36204 Y 36265 Y SE CERRO DE JUNCOS A QUEBRADA NEGRITO | S22050400197 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 16 | 2022-05-04 | 1728 | keep | 0 | May | 2022 | 0.0011769 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-04 14:33 | 2022-05-04 14:49 | 1368 | 000:16 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA SE ABRIO 36204 Y 36265 Y SE CERRO DE JUNCOS A QUEBRADA NEGRITO | S22050400197 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 16 | 2022-05-04 | 21888 | keep | 0 | May | 2022 | 0.014908 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-04 14:33 | 2022-05-04 14:49 | 2064 | 000:16 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA SE ABRIO 36204 Y 36265 Y SE CERRO DE JUNCOS A QUEBRADA NEGRITO | S22050400197 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 16 | 2022-05-04 | 33024 | keep | 0 | May | 2022 | 0.022492 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-04 14:49 | 2022-05-04 15:34 | 12 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S22050400099 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-05-04 | 540 | keep | 0 | May | 2022 | 0.00036779 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-04 14:49 | 2022-05-04 17:08 | 65 | 002:19 | P | DESGANCHE | 1 X 80 EN C/L | R22050400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-05-04 | 9035 | keep | 0 | May | 2022 | 0.0061537 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-05-04 14:49 | 2022-05-04 18:44 | 40 | 003:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | P22050400073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 235 | 2022-05-04 | 9400 | keep | 0 | May | 2022 | 0.0064023 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-04 15:00 | 2022-05-04 17:32 | 4 | 002:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22050400145 | New_Event | Secondary Wire Down | Include | Include | Equipment | 152 | 2022-05-04 | 608 | keep | 0 | May | 2022 | 0.00041411 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-04 15:02 | 2022-05-04 18:05 | 30 | 003:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | S22050400212 | New_Event |  |  | Include | Wildlife | 183 | 2022-05-04 | 5490 | keep | 0 | May | 2022 | 0.0037392 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-04 15:02 | 2022-05-04 15:03 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 308 | keep | 0 | May | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CAGUAS | 2022-05-04 15:03 | 2022-05-05 10:05 | 1 | 019:02 | P | NO SE REPORTO CAUSA | 2 X 40 EN C/L NO CAUSA | C22050400111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1142 | 2022-05-04 | 1142 | keep | 0 | May | 2022 | 0.00077781 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-04 15:16 | 2022-05-04 19:12 | 22 | 003:56 | P | HERRAJE ROTO O PODRIDO | 1 X 65 EN CORTE DE LINEA SE ABRIO PUENTE PARA SECCIONLIZAR CRUCETA PARTIDA | S22050400217 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 236 | 2022-05-04 | 5192 | keep | 0 | May | 2022 | 0.0035362 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CANOVANAS | 2022-05-04 15:17 | 2022-05-04 16:42 | 150 | 001:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 Y 1 X 65 EN C/L'S DIGGER TUMBO ARBOL SOBRE LAS LINEAS | R22050400062 | New_Event |  |  | Include | Wildlife | 85 | 2022-05-04 | 12750 | keep | 0 | May | 2022 | 0.008684 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-05-04 15:28 | 2022-05-06 10:10 | 4 | 042:42 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA QUEMADO | C22050400113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2562 | 2022-05-04 | 10248 | keep | 0 | May | 2022 | 0.0069799 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-04 15:46 | 2022-05-04 15:48 | 1500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE POR 1620-05 | S22050400222 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-04 | 3000 | keep | 0 | May | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-05-04 15:46 | 2022-05-04 15:48 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA PARTE 1206-3 | S22050400222 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-04 | 3230 | keep | 0 | May | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
PONCE | 2022-05-04 15:48 | 2022-05-04 18:13 | 20 | 002:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR NEUTRAL PRIMARIO | P22050400096 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2022-05-04 | 2900 | keep | 0 | May | 2022 | 0.0019752 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-04 15:51 | 2022-05-04 16:45 | 5 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA DESGANCHAR Y LAVANTAR SECUNDARIA DEL SUELO | C22050400116 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-05-04 | 270 | keep | 0 | May | 2022 | 0.0001839 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-04 15:52 | 2022-05-04 18:52 | 80 | 003:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22050400223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2022-05-04 | 14400 | keep | 0 | May | 2022 | 0.0098078 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-04 15:52 | 2022-05-04 15:53 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22050400154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 6285 | keep | 0 | May | 2022 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
ARECIBO | 2022-05-04 15:52 | 2022-05-04 17:40 | 6 | 001:48 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO BAMBUS SOBRE LAS LINEAS | A22050400078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-05-04 | 648 | keep | 0 | May | 2022 | 0.00044135 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-05-04 15:54 | 2022-05-04 17:40 | 11 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | C22050400117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-05-04 | 1166 | keep | 0 | May | 2022 | 0.00079416 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-05-04 16:00 | 2022-05-05 14:00 | 12 | 022:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO | S22050400229 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1320 | 2022-05-04 | 15840 | keep | 0 | May | 2022 | 0.010789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-05-04 16:01 | 2022-05-04 17:30 | 50 | 001:29 | P | DESGANCHE | 1 X 50 EN C/L | R22050400066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-05-04 | 4450 | keep | 0 | May | 2022 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-04 16:22 | 2022-05-04 19:25 | 15 | 003:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA Y SE REPARO BAJANTE SECUNDARIO | S22050400230 | New_Event | Secondary Wire Down | Include | Include | Equipment | 183 | 2022-05-04 | 2745 | keep | 0 | May | 2022 | 0.0018696 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-04 16:22 | 2022-05-04 18:02 | 7 | 001:40 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REPARO NEUTRAL ABIERTO EN SECUNDARIA Y SE REALIZO DESGANCHE | B22050400127 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 100 | 2022-05-04 | 700 | keep | 0 | May | 2022 | 0.00047677 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-04 16:26 | 2022-05-04 17:28 | 4 | 001:02 | P | NO SE REPORTO CAUSA | 2 X 50 EN AEREO PROVISIONAL | B22050400129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-05-04 | 248 | keep | 0 | May | 2022 | 0.00016891 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-05-04 16:33 | 2022-05-04 19:22 | 1 | 002:49 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22050400081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-05-04 | 169 | keep | 0 | May | 2022 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-04 16:40 | 2022-05-05 08:25 | 1 | 015:45 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR. SE REALIZO PODA DE BAMBUAS | S22050400232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 945 | 2022-05-04 | 945 | keep | 0 | May | 2022 | 0.00064364 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-04 16:45 | 2022-05-04 17:07 | 10 | 000:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA DAR CONECTOR EN BAJANTE SECUNDARIO | C22050400084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 22 | 2022-05-04 | 220 | keep | 0 | May | 2022 | 0.00014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-05-04 16:48 | 2022-05-04 18:28 | 25 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22050400082 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2022-05-04 | 2500 | keep | 0 | May | 2022 | 0.0017027 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-05-04 16:53 | 2022-05-04 18:22 | 1 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A22050400083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2022-05-04 | 89 | keep | 0 | May | 2022 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-04 17:16 | 2022-05-04 18:57 | 4 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | R22050400072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2022-05-04 | 404 | keep | 0 | May | 2022 | 0.00027516 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-04 17:16 | 2022-05-04 18:23 | 1 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y SECUNDARIA | B22050400064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2022-05-04 | 67 | keep | 0 | May | 2022 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-04 17:26 | 2022-05-04 17:27 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 222 | keep | 0 | May | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-05-04 17:26 | 2022-05-04 17:27 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 4456 | keep | 0 | May | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
CAGUAS | 2022-05-04 17:28 | 2022-05-05 08:48 | 1 | 015:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN XMR CRUCE X AVE | C22050400125 | New_Event |  |  | Include | Wildlife | 920 | 2022-05-04 | 920 | keep | 0 | May | 2022 | 0.00062661 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-04 17:57 | 2022-05-05 03:55 | 200 | 009:58 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050400205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 598 | 2022-05-04 | 119600 | keep | 0 | May | 2022 | 0.081459 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-05-04 18:02 | 2022-05-04 18:35 | 10 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22050400104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2022-05-04 | 330 | keep | 0 | May | 2022 | 0.00022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-05-04 18:10 | 2022-05-04 19:28 | 6 | 001:18 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING PRIMARIO TRANSFORMADOR | P22050400105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 78 | 2022-05-04 | 468 | keep | 0 | May | 2022 | 0.00031875 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-04 18:12 | 2022-05-04 21:15 | 100 | 003:03 | P | DESGANCHE | 2 X 100 Y 1 X 80 EN CORTES DE LINEAS SE RETIRO ARBOL SOBRE LAS LINEAS | M22050400213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-05-04 | 18300 | keep | 0 | May | 2022 | 0.012464 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-04 18:16 | 2022-05-04 18:55 | 16 | 000:39 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR DE 50 KVA PARA PASAR CARGA DE XMR 37.5 KVA AVERIADO A ESTE | B22050400080 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 39 | 2022-05-04 | 624 | keep | 0 | May | 2022 | 0.000425 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-04 18:34 | 2022-05-04 22:52 | 15 | 004:18 | P | SECUNDARIA/DESGANCHE | ABRIR XMR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR SEC | B22050300736 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 258 | 2022-05-04 | 3870 | keep | 0 | May | 2022 | 0.0026358 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-04 18:43 | 2022-05-05 03:25 | 5 | 008:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22050400222 | New_Event | Bad Weather | Include | Include | Weather | 522 | 2022-05-04 | 2610 | keep | 0 | May | 2022 | 0.0017777 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-05-04 19:02 | 2022-05-05 15:06 | 4 | 020:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZARON 450 PIES DE CONDUCTOR PRIMARIO SE CERRO CORTE DE LINEA | R22050400077 | New_Event | Wire Down | Include | Include | Equipment | 1204 | 2022-05-04 | 4816 | keep | 0 | May | 2022 | 0.0032802 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-05-04 19:03 | 2022-05-05 00:25 | 20 | 005:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR HAY QUE REMAPLAZAR 100 PIES DE LINEA SECUNDARIA EVENTO SE QUEDA ABIERTO CON 6 CLIENTES SIN SERVICIO | M22050400227 | New_Event | Cutout Failure | Include | Include | Equipment | 322 | 2022-05-04 | 6440 | keep | 0 | May | 2022 | 0.0043863 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-04 19:12 | 2022-05-05 21:16 | 9 | 026:04 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA TRAS PATIO Y SE CERRO PUENTE | S22050400217 | Partial_restoration | Broken / Rusty Hardware | Include | Include | Equipment | 1564 | 2022-05-04 | 14076 | keep | 0 | May | 2022 | 0.0095871 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-05-04 19:29 | 2022-05-04 22:38 | 30 | 003:09 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050400235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2022-05-04 | 5670 | keep | 0 | May | 2022 | 0.0038618 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-04 19:30 | 2022-05-05 14:00 | 12 | 018:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA EN VARIOS PUNTOS | S22050400226 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1110 | 2022-05-04 | 13320 | keep | 0 | May | 2022 | 0.0090722 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-05-04 19:53 | 2022-05-04 23:04 | 50 | 003:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22050400098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-05-04 | 9550 | keep | 0 | May | 2022 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-04 21:16 | 2022-05-05 12:25 | 25 | 015:09 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S22050400266 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 909 | 2022-05-04 | 22725 | keep | 0 | May | 2022 | 0.015478 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-04 21:35 | 2022-05-04 22:09 | 9 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR SEC | B22050400047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2022-05-04 | 306 | keep | 0 | May | 2022 | 0.00020842 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-05-04 21:49 | 2022-05-04 21:50 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22050400250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 3458 | keep | 0 | May | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
ARECIBO | 2022-05-04 21:50 | 2022-05-04 22:38 | 14 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | A22050400048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2022-05-04 | 672 | keep | 0 | May | 2022 | 0.0004577 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-05-04 22:05 | 2022-05-05 11:40 | 50 | 013:35 | P | DESGANCHE | SE REPARO BAJANTE PRIMARIO Y DESGANCHE | S22050400640 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2022-05-04 | 40750 | keep | 0 | May | 2022 | 0.027755 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-05-04 22:14 | 2022-05-05 01:10 | 540 | 002:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P22050400113 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2022-05-04 | 95040 | keep | 0 | May | 2022 | 0.064731 | 0.00036779 | Sustained | FALSE | FALSE | Not_TMED_Event | 540
SAN JUAN | 2022-05-04 22:30 | 2022-05-04 22:31 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 2203 | keep | 0 | May | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
MAYAGÃœEZ | 2022-05-04 23:13 | 2022-05-05 12:37 | 100 | 013:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050400253 | New_Event | Bad Weather | Include | Include | Weather | 804 | 2022-05-04 | 80400 | keep | 0 | May | 2022 | 0.05476 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-04 23:43 | 2022-05-04 23:44 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-04 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
MAYAGÃœEZ | 2022-05-05 | 2022-05-05 00:01 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22050500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 1097 | keep | 0 | May | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
BAYAMON | 2022-05-05 00:08 | 2022-05-05 01:51 | 74 | 001:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA | B22050500001 | New_Event | Cutout Failure | Include | Include | Equipment | 103 | 2022-05-05 | 7622 | keep | 0 | May | 2022 | 0.0051913 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
CAGUAS | 2022-05-05 00:24 | 2022-05-05 07:36 | 14 | 007:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22050500001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 432 | 2022-05-05 | 6048 | keep | 0 | May | 2022 | 0.0041193 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-05-05 00:25 | 2022-05-05 10:56 | 5 | 010:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS PARTIDAS | M22050400227 | New_Event | Secondary Wire Down | Include | Include | Equipment | 631 | 2022-05-05 | 3155 | keep | 0 | May | 2022 | 0.0021489 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-05 01:54 | 2022-05-05 10:00 | 152 | 008:06 | P | HERRAJE ROTO O PODRIDO | CRUCETA PARTIDA Y HERRAJE ROTO, SE ABRIO TOTAL PARA PODER REPARAR | R22050500003 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 486 | 2022-05-05 | 73872 | keep | 0 | May | 2022 | 0.050314 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
PONCE | 2022-05-05 02:19 | 2022-05-05 02:20 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 1478 | keep | 0 | May | 2022 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
MAYAGÃœEZ | 2022-05-05 02:32 | 2022-05-05 04:56 | 10 | 002:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22050500004 | New_Event | Bad Weather | Include | Include | Weather | 144 | 2022-05-05 | 1440 | keep | 0 | May | 2022 | 0.00098078 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-05 05:57 | 2022-05-05 12:30 | 1 | 006:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER ROEDOR CRUZO LINEAS | M22050500005 | New_Event |  |  | Include | Wildlife | 393 | 2022-05-05 | 393 | keep | 0 | May | 2022 | 0.00026767 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-05 06:35 | 2022-05-05 06:40 | 763 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE SABANA LLANA TC | R22050500010 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-05-05 | 3815 | keep | 0 | May | 2022 | 0.0025984 | 0.00051968 | Momentary | FALSE | FALSE | Not_TMED_Event | 763
SAN JUAN | 2022-05-05 06:35 | 2022-05-05 06:40 | 27 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE SABANA LLANA TC | R22050500010 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-05-05 | 135 | keep | 0 | May | 2022 | 9.1948e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2022-05-05 06:35 | 2022-05-05 06:40 | 1259 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE SABANA LLANA TC | R22050500010 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-05-05 | 6295 | keep | 0 | May | 2022 | 0.0042875 | 0.0008575 | Momentary | FALSE | FALSE | Not_TMED_Event | 1259
SAN JUAN | 2022-05-05 06:35 | 2022-05-05 06:40 | 1051 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE SABANA LLANA TC | R22050500010 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-05-05 | 5255 | keep | 0 | May | 2022 | 0.0035792 | 0.00071583 | Momentary | FALSE | FALSE | Not_TMED_Event | 1051
SAN JUAN | 2022-05-05 06:35 | 2022-05-05 06:40 | 188 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE SABANA LLANA TC | R22050500010 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-05-05 | 940 | keep | 0 | May | 2022 | 0.00064023 | 0.00012805 | Momentary | FALSE | FALSE | Not_TMED_Event | 188
SAN JUAN | 2022-05-05 06:35 | 2022-05-05 06:38 | 614 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE SABANA LLANA TC | S22050500006 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-05-05 | 1842 | keep | 0 | May | 2022 | 0.0012546 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-05-05 06:35 | 2022-05-05 06:38 | 770 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE SABANA LLANA TC | S22050500006 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-05-05 | 2310 | keep | 0 | May | 2022 | 0.0015733 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-05-05 06:35 | 2022-05-05 06:38 | 1271 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE SABANA LLANA TC | S22050500006 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-05-05 | 3813 | keep | 0 | May | 2022 | 0.002597 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2022-05-05 06:35 | 2022-05-05 06:38 | 247 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE SABANA LLANA TC | S22050500006 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-05-05 | 741 | keep | 0 | May | 2022 | 0.00050469 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
VEGA BAJA | 2022-05-05 06:46 | 2022-05-05 07:52 | 40 | 001:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22050500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-05-05 | 2640 | keep | 0 | May | 2022 | 0.0017981 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-05-05 06:51 | 2022-05-05 09:20 | 10 | 002:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR CHANGO | R22050500011 | New_Event |  |  | Include | Wildlife | 149 | 2022-05-05 | 1490 | keep | 0 | May | 2022 | 0.0010148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-05 06:54 | 2022-05-05 08:38 | 20 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN RISER Y 1 X 50 CORTE DE LINEA POR PAJARO | A22050500004 | New_Event |  |  | Include | Wildlife | 104 | 2022-05-05 | 2080 | keep | 0 | May | 2022 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-05-05 07:02 | 2022-05-05 07:03 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 2725 | keep | 0 | May | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-05-05 07:02 | 2022-05-05 07:03 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 1834 | keep | 0 | May | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-05-05 07:02 | 2022-05-05 07:03 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 1437 | keep | 0 | May | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-05-05 07:02 | 2022-05-05 07:03 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 2565 | keep | 0 | May | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-05-05 07:02 | 2022-05-05 07:03 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 3565 | keep | 0 | May | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-05-05 07:02 | 2022-05-05 07:03 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22050500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 2751 | keep | 0 | May | 2022 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-05-05 07:02 | 2022-05-05 07:03 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22050500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 576 | keep | 0 | May | 2022 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-05-05 07:02 | 2022-05-05 07:03 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22050500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 2584 | keep | 0 | May | 2022 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-05-05 07:02 | 2022-05-05 07:03 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22050500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 1606 | keep | 0 | May | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-05-05 07:02 | 2022-05-05 07:03 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22050500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 29 | keep | 0 | May | 2022 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2022-05-05 07:02 | 2022-05-05 07:03 | 4035 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22050500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 4035 | keep | 0 | May | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-05-05 07:02 | 2022-05-05 07:03 | 3718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22050500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 3718 | keep | 0 | May | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BARRANQUITAS | 2022-05-05 07:03 | 2022-05-05 07:04 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 2725 | keep | 0 | May | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-05-05 07:03 | 2022-05-05 07:04 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 1834 | keep | 0 | May | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-05-05 07:03 | 2022-05-05 07:04 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 1437 | keep | 0 | May | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-05-05 07:03 | 2022-05-05 07:04 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 2565 | keep | 0 | May | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-05-05 07:03 | 2022-05-05 07:04 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C22050500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-05 | 3565 | keep | 0 | May | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
BAYAMON | 2022-05-05 07:27 | 2022-05-05 13:23 | 80 | 005:56 | P | NO SE REPORTO CAUSA | 1 X 140 Y 1 X 100 EN CORTES DE LINEA | S22050500011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 356 | 2022-05-05 | 28480 | keep | 0 | May | 2022 | 0.019398 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-05-05 07:38 | 2022-05-05 15:21 | 9 | 007:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN XMR CRUCE X AVE | C22050500004 | New_Event |  |  | Include | Wildlife | 463 | 2022-05-05 | 4167 | keep | 0 | May | 2022 | 0.0028381 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-05-05 07:52 | 2022-05-05 09:55 | 1 | 002:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A22050500009 | New_Event | Bad Weather | Include | Include | Weather | 123 | 2022-05-05 | 123 | keep | 0 | May | 2022 | 8.3775e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-05 07:54 | 2022-05-05 16:06 | 20 | 008:12 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S22050500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 492 | 2022-05-05 | 9840 | keep | 0 | May | 2022 | 0.006702 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-05 08:08 | 2022-05-05 12:33 | 8 | 004:25 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO SECUNDARIA | C22050500008 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 265 | 2022-05-05 | 2120 | keep | 0 | May | 2022 | 0.0014439 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-05-05 08:14 | 2022-05-05 12:51 | 150 | 004:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22050500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2022-05-05 | 41550 | keep | 0 | May | 2022 | 0.0283 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-05-05 08:15 | 2022-05-05 16:17 | 1 | 008:02 | P | TRANSFORMADOR AVERIADO | ABRIO XMR PARA REMPLAZAR 2 BUSHING SECUNDARIOS | C22050500011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 482 | 2022-05-05 | 482 | keep | 0 | May | 2022 | 0.00032829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-05 08:19 | 2022-05-05 10:53 | 148 | 002:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 65 EN C/L'S CRUCE X AVE | C22050500012 | New_Event |  |  | Include | Wildlife | 154 | 2022-05-05 | 22792 | keep | 0 | May | 2022 | 0.015524 | 0.0001008 | Sustained | FALSE | FALSE | Not_TMED_Event | 148
SAN JUAN | 2022-05-05 08:25 | 2022-05-05 08:26 | 858 | 000:01 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1303-02 QUE ADEMAS LLEVA EL 20% DEL 1204-02 | S22050500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-05 | 858 | keep | 0 | May | 2022 | 0.00058438 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-05 08:25 | 2022-05-05 08:26 | 2435 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-02 QUE ADEMAS LLEVA EL 20% DEL 1204-02 | S22050500000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-05 | 2435 | keep | 0 | May | 2022 | 0.0016585 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-05 08:26 | 2022-05-05 13:50 | 1 | 005:24 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR. SE REALIZO PODA DE BAMBUAS | S22050400232 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 324 | 2022-05-05 | 324 | keep | 0 | May | 2022 | 0.00022067 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-05 08:31 | 2022-05-05 15:17 | 1 | 006:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y SE REPARO PUENTE PRIMARIO EN RISER | S22050500022 | New_Event | Cutout Failure | Include | Include | Equipment | 406 | 2022-05-05 | 406 | keep | 0 | May | 2022 | 0.00027652 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-05 08:36 | 2022-05-05 13:21 | 1 | 004:45 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR HACIA BOMBAS AAA | S22050500025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2022-05-05 | 285 | keep | 0 | May | 2022 | 0.00019411 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-05 08:50 | 2022-05-05 14:10 | 50 | 005:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO A CAUSA DE BAMBUAS SOBRE LINEAS SE RETIRO BAMBUAS SOBRE LAS LINEAS | M22050500017 | New_Event | Wire Down | Include | Include | Equipment | 320 | 2022-05-05 | 16000 | keep | 0 | May | 2022 | 0.010898 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-05 08:51 | 2022-05-05 09:27 | 16 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE RETEZO LINEA SECUNDARIA | A22050400063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-05-05 | 576 | keep | 0 | May | 2022 | 0.00039231 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-05-05 08:57 | 2022-05-05 12:24 | 60 | 003:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PUENTE PRIMARIO CRUZADO CON TENSOR | M22050500020 | New_Event |  |  | Include | Wildlife | 207 | 2022-05-05 | 12420 | keep | 0 | May | 2022 | 0.0084592 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-05 09:01 | 2022-05-05 12:41 | 10 | 003:40 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | C22050500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2022-05-05 | 2200 | keep | 0 | May | 2022 | 0.0014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-05-05 09:02 | 2022-05-05 10:47 | 10 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L PERSONAS DESGANCHANDO | C22050500017 | New_Event |  |  | Include | Wildlife | 105 | 2022-05-05 | 1050 | keep | 0 | May | 2022 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-05 09:06 | 2022-05-05 11:00 | 40 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22050500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-05-05 | 4560 | keep | 0 | May | 2022 | 0.0031058 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-05 09:13 | 2022-05-05 12:32 | 12 | 003:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR Y SE REPORTA CONTAMINACION POR SALITRE | S22050500022 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2022-05-05 | 2388 | keep | 0 | May | 2022 | 0.0016265 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-05 09:19 | 2022-05-05 11:42 | 509 | 002:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A22050500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 143 | 2022-05-05 | 72787 | keep | 0 | May | 2022 | 0.049575 | 0.00034668 | Sustained | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2022-05-05 09:19 | 2022-05-05 11:42 | 2620 | 002:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A22050500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 143 | 2022-05-05 | 374660 | keep | 0 | May | 2022 | 0.25518 | 0.0017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2022-05-05 09:19 | 2022-05-05 11:42 | 1916 | 002:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A22050500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 143 | 2022-05-05 | 273988 | keep | 0 | May | 2022 | 0.18661 | 0.001305 | Sustained | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2022-05-05 09:19 | 2022-05-05 11:42 | 5042 | 002:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 OVERHEAD SOBRE LINEA | A22050500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 143 | 2022-05-05 | 721006 | keep | 0 | May | 2022 | 0.49107 | 0.0034341 | Sustained | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2022-05-05 09:19 | 2022-05-05 11:42 | 2720 | 002:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A22050500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 143 | 2022-05-05 | 388960 | keep | 0 | May | 2022 | 0.26492 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2022-05-05 09:19 | 2022-05-05 11:42 | 1883 | 002:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A22050500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 143 | 2022-05-05 | 269269 | keep | 0 | May | 2022 | 0.1834 | 0.0012825 | Sustained | FALSE | FALSE | Not_TMED_Event | 1883
MAYAGÃœEZ | 2022-05-05 09:21 | 2022-05-05 12:07 | 7 | 002:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M22050500023 | New_Event |  |  | Include | Wildlife | 166 | 2022-05-05 | 1162 | keep | 0 | May | 2022 | 0.00079143 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-05-05 09:50 | 2022-05-05 09:51 | 2280 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9902-03 LLEVA LA CARGA DEL 9902-02 | C22050500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 2280 | keep | 0 | May | 2022 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-05-05 09:50 | 2022-05-05 09:51 | 1617 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 9902-02 | C22050500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 1617 | keep | 0 | May | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
SAN JUAN | 2022-05-05 10:00 | 2022-05-05 12:55 | 456 | 002:55 | P | HERRAJE ROTO O PODRIDO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO JUEGO DE DISCO, CAJA PRIMARIA, SE ELIMINO CRUCETA E INSTALO DOS RIGIDOS Y SE REEMPLAZO BAJANTES | R22050500003 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 175 | 2022-05-05 | 79800 | keep | 0 | May | 2022 | 0.054351 | 0.00031058 | Sustained | FALSE | FALSE | Not_TMED_Event | 456
VEGA BAJA | 2022-05-05 10:04 | 2022-05-05 10:05 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22050500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 1310 | keep | 0 | May | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CANOVANAS | 2022-05-05 10:08 | 2022-05-05 10:09 | 3766 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22050500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 3766 | keep | 0 | May | 2022 | 0.002565 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
SAN JUAN | 2022-05-05 10:29 | 2022-05-05 13:03 | 30 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN PROVISIONAL | S22050500050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-05-05 | 4620 | keep | 0 | May | 2022 | 0.0031467 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-05-05 10:33 | 2022-05-05 11:30 | 100 | 000:57 | P | ERROR HUMANO | 2 X 100 EN C/L PERSONAL CONTRATISTA DESGANCHANDO | C22050500031 | New_Event | Human Error | Include | Include | Other | 57 | 2022-05-05 | 5700 | keep | 0 | May | 2022 | 0.0038822 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-05 10:35 | 2022-05-05 10:55 | 20 | 000:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22050400252 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-05-05 | 400 | keep | 0 | May | 2022 | 0.00027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-05 10:58 | 2022-05-05 16:19 | 50 | 005:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | S22050500056 | New_Event |  |  | Include | Wildlife | 321 | 2022-05-05 | 16050 | keep | 0 | May | 2022 | 0.010932 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-05-05 11:01 | 2022-05-05 18:11 | 6 | 007:10 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C22050500035 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 430 | 2022-05-05 | 2580 | keep | 0 | May | 2022 | 0.0017572 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-05 11:04 | 2022-05-05 20:51 | 4 | 009:47 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA ROTA A CAUSA DE RAMAS SOBRE LINEAS SE RETIRO RAMAS SOBRE LAS LINEAS | M22050500051 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 587 | 2022-05-05 | 2348 | keep | 0 | May | 2022 | 0.0015992 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-05-05 11:10 | 2022-05-05 11:46 | 3 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR Y SE REPARAN CONEXIONES EN SALIDA | A22050500105 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-05-05 | 108 | keep | 0 | May | 2022 | 7.3558e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-05-05 11:20 | 2022-05-05 14:53 | 6 | 003:33 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR SE REALIZO DESGANCHE SECUNDARIO | B22050500031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 213 | 2022-05-05 | 1278 | keep | 0 | May | 2022 | 0.00087044 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-05 11:30 | 2022-05-05 20:52 | 67 | 009:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO PORTAFUSIBLE | S22050500067 | New_Event | Cutout Failure | Include | Include | Equipment | 562 | 2022-05-05 | 37654 | keep | 0 | May | 2022 | 0.025646 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2022-05-05 11:38 | 2022-05-05 19:12 | 10 | 007:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 8 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22050500056 | New_Event | Wire Down | Include | Include | Equipment | 454 | 2022-05-05 | 4540 | keep | 0 | May | 2022 | 0.0030922 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-05 11:42 | 2022-05-05 11:51 | 40 | 000:09 | P | LINEA DE TRANSMISION 38KV | 1 X 50 EN CORTE DE LINEA OVER HEAD DE LINEA 2100 SOBRE ALIMENTADOR 7702-02 | A22050500142 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-05-05 | 360 | keep | 0 | May | 2022 | 0.00024519 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-05-05 11:43 | 2022-05-05 14:25 | 1 | 002:42 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA PARQUE PELOTA JAYUYA REQUIERE DESGANCHE DE BAMBUAS | A22050500162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-05-05 | 162 | keep | 0 | May | 2022 | 0.00011034 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-05 12:25 | 2022-05-05 18:01 | 63 | 005:36 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22050500077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 336 | 2022-05-05 | 21168 | keep | 0 | May | 2022 | 0.014417 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
SAN JUAN | 2022-05-05 12:29 | 2022-05-05 12:30 | 1 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA Y SE REEPLAZO CAJA | S22050500014 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-05 | 1 | keep | 0 | May | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-05 12:33 | 2022-05-05 14:27 | 11 | 001:54 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR T - 4 PARA REMPLAZAR PEDESTAL Y BARRAS | C22050500030 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 114 | 2022-05-05 | 1254 | keep | 0 | May | 2022 | 0.00085409 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2022-05-05 12:58 | 2022-05-05 17:54 | 70 | 004:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22050500079 | New_Event | Cutout Failure | Include | Include | Equipment | 296 | 2022-05-05 | 20720 | keep | 0 | May | 2022 | 0.014112 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-05-05 13:10 | 2022-05-05 13:49 | 50 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A22050500176 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2022-05-05 | 1950 | keep | 0 | May | 2022 | 0.0013281 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-05-05 13:20 | 2022-05-05 13:58 | 8 | 000:38 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR 37.54 A 2.4KV SE RETIRA UNO DE 50KVA AVERIADO | P22050500036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 38 | 2022-05-05 | 304 | keep | 0 | May | 2022 | 0.00020705 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-05-05 13:23 | 2022-05-05 13:24 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22050500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 6136 | keep | 0 | May | 2022 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2022-05-05 13:24 | 2022-05-05 17:07 | 80 | 003:43 | P | NO SE REPORTO CAUSA | 1 X 140 Y 1 X 100 EN CORTES DE LINEA | S22050500011 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-05-05 | 17840 | keep | 0 | May | 2022 | 0.012151 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-05-05 13:26 | 2022-05-05 14:25 | 50 | 000:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE CORTE DE LINEA Y BAJANTE PRIMARIO EN VIVO | P22050500037 | New_Event | Cutout Failure | Include | Include | Equipment | 59 | 2022-05-05 | 2950 | keep | 0 | May | 2022 | 0.0020092 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-05-05 13:42 | 2022-05-05 13:43 | 1310 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | B22050500000 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-05 | 1310 | keep | 0 | May | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-05-05 13:43 | 2022-05-05 16:50 | 80 | 003:07 | P | CABLE SOTERRADO AVERIADO | 1 SMU 20 DE 100 AMP. EN SU-28, 1 X 65 EN AEREO PROVISIONAL AVERIA NUEVA DEL T-37 AL T-36, AVERIA VIEJA DE T-36 A T-35 | R22050500056 | New_Event | UG Cable Fault | Include | Include | Equipment | 187 | 2022-05-05 | 14960 | keep | 0 | May | 2022 | 0.010189 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-05-05 13:43 | 2022-05-05 17:39 | 68 | 003:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L AVE CRUZO LINEAS | B22050500043 | 1st_after_momentary |  |  | Include | Wildlife | 236 | 2022-05-05 | 16048 | keep | 0 | May | 2022 | 0.01093 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
UTUADO | 2022-05-05 13:47 | 2022-05-05 17:21 | 932 | 003:34 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE REPARO LINEA PARTIDA EN TRONCAL DE ALIMENTADOR | A22050500180 | New_Event | Wire Down | Include | Include | Equipment | 214 | 2022-05-05 | 199448 | keep | 0 | May | 2022 | 0.13584 | 0.00063478 | Sustained | FALSE | FALSE | Not_TMED_Event | 932
BAYAMON | 2022-05-05 13:48 | 2022-05-05 16:56 | 67 | 003:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO Y SE REALIZO DESGANCHE | B22050400106 | New_Event | Wire Down | Include | Include | Equipment | 188 | 2022-05-05 | 12596 | keep | 0 | May | 2022 | 0.0085791 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-05-05 13:54 | 2022-05-05 16:42 | 80 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22050500046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-05-05 | 13440 | keep | 0 | May | 2022 | 0.0091539 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-05 14:00 | 2022-05-05 14:01 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22050500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 390 | keep | 0 | May | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2022-05-05 14:05 | 2022-05-05 17:20 | 16 | 003:15 | P | ESTRUCTURA AVERIADA | SE ABRIO C/L PARA REALIZAR CAMBIO POSTE Y TRANSFORMADOR | B22050500020 | New_Event | Defective Pole | Include | Include | Equipment | 195 | 2022-05-05 | 3120 | keep | 0 | May | 2022 | 0.002125 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-05-05 14:29 | 2022-05-06 06:34 | 6 | 016:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22050500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 965 | 2022-05-05 | 5790 | keep | 0 | May | 2022 | 0.0039435 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-05-05 14:30 | 2022-05-05 19:07 | 25 | 004:37 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN RISER SE REPARO PISTOLA | S22050500101 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 277 | 2022-05-05 | 6925 | keep | 0 | May | 2022 | 0.0047166 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-05 15:02 | 2022-05-05 18:11 | 87 | 003:09 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22050500061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2022-05-05 | 16443 | keep | 0 | May | 2022 | 0.011199 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
PONCE | 2022-05-05 15:10 | 2022-05-05 18:34 | 24 | 003:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 CAJAS PRIMARIAS DE RISER QUEMADAS, DESGACHE Y SE REPARO BAJANTE DE RISER PRIMARIO | P22050500044 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2022-05-05 | 4896 | keep | 0 | May | 2022 | 0.0033346 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2022-05-05 15:17 | 2022-05-05 15:19 | 57 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE INTERRUPTOR PARA RETIRAR PUENTE PRIMARIO ENCIMA DE CRUCETA REFERENTE A EVENTO S22050500022 | S22050500000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-05-05 | 114 | keep | 0 | May | 2022 | 7.7645e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2022-05-05 15:29 | 2022-05-05 18:48 | 11 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22050500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-05-05 | 2189 | keep | 0 | May | 2022 | 0.0014909 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2022-05-05 15:30 | 2022-05-05 17:00 | 7 | 001:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R22050500069 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2022-05-05 | 630 | keep | 0 | May | 2022 | 0.00042909 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-05-05 15:32 | 2022-05-05 18:50 | 18 | 003:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE DE ARBOL | R22050500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2022-05-05 | 3564 | keep | 0 | May | 2022 | 0.0024274 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-05-05 15:33 | 2022-05-05 15:34 | 2276 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 2276 | keep | 0 | May | 2022 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
MAYAGÃœEZ | 2022-05-05 15:33 | 2022-05-05 17:13 | 8 | 001:40 | P | SECUNDARIA/DESGANCHE | SE REPARO LINEA SECUNDARIA ROTA A CAUSA DE RAMAS DE ARBOL CAIDAS ENCIMA DE LINEA | M22050500094 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 100 | 2022-05-05 | 800 | keep | 0 | May | 2022 | 0.00054488 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-05 15:36 | 2022-05-05 18:14 | 78 | 002:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE Y SE DESENREDO LINEA | S22050500120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-05-05 | 12324 | keep | 0 | May | 2022 | 0.0083938 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
CAGUAS | 2022-05-05 15:38 | 2022-05-05 15:39 | 3005 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050500049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 3005 | keep | 0 | May | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2022-05-05 15:53 | 2022-05-05 18:29 | 80 | 002:36 | P | DESGANCHE | 1 X 40 EN C/L | C22050500050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-05-05 | 12480 | keep | 0 | May | 2022 | 0.0085001 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-05 16:16 | 2022-05-05 18:00 | 80 | 001:44 | P | CABLE SOTERRADO AVERIADO | SE ABRIO VS A MH 3 PARA CONECTAR CABLE SOTERRADO NUEVO DE TOMA EAT MOTOR SPORT A CAJAS SECAS | S22050500006 | New_Event | UG Cable Fault | Include | Include | Equipment | 104 | 2022-05-05 | 8320 | keep | 0 | May | 2022 | 0.0056667 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-05-05 16:23 | 2022-05-05 18:11 | 25 | 001:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR CONTACTO DE ANIMAL | P22050500049 | New_Event |  |  | Include | Wildlife | 108 | 2022-05-05 | 2700 | keep | 0 | May | 2022 | 0.001839 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-05-05 16:35 | 2022-05-05 16:36 | 1843 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050500055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-05 | 1843 | keep | 0 | May | 2022 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
MAYAGÃœEZ | 2022-05-05 17:12 | 2022-05-05 20:00 | 4 | 002:48 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050500092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-05-05 | 672 | keep | 0 | May | 2022 | 0.0004577 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2022-05-05 17:22 | 2022-05-05 19:15 | 35 | 001:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA Y 1 X 20 EN RISER SE REEMPLAZO CAJA PRIMARIA | R22050500075 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2022-05-05 | 3955 | keep | 0 | May | 2022 | 0.0026937 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-05-05 17:44 | 2022-05-05 18:46 | 1 | 001:02 | P | NO SE REPORTO CAUSA | 3 X 20 EN RISER | B22050500095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-05-05 | 62 | keep | 0 | May | 2022 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-05 18:06 | 2022-05-05 22:45 | 161 | 004:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | S22050500143 | New_Event | Wire Down | Include | Include | Equipment | 279 | 2022-05-05 | 44919 | keep | 0 | May | 2022 | 0.030594 | 0.00010966 | Sustained | FALSE | FALSE | Not_TMED_Event | 161
BAYAMON | 2022-05-05 18:06 | 2022-05-06 00:39 | 40 | 006:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22050500139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 393 | 2022-05-05 | 15720 | keep | 0 | May | 2022 | 0.010707 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-05 18:23 | 2022-05-06 06:34 | 48 | 012:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C22050500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 731 | 2022-05-05 | 35088 | keep | 0 | May | 2022 | 0.023898 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
SAN JUAN | 2022-05-05 18:26 | 2022-05-05 21:20 | 1300 | 002:54 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE CARR.181 INT. VILLA ANDALUCIA | S22050500344 | New_Event | Switch Failure | Include | Include | Equipment | 174 | 2022-05-05 | 226200 | keep | 0 | May | 2022 | 0.15406 | 0.00088542 | Sustained | FALSE | FALSE | Not_TMED_Event | 1300
SAN JUAN | 2022-05-05 18:26 | 2022-05-05 21:20 | 1500 | 002:54 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE | S22050500344 | New_Event | Switch Failure | Include | Include | Equipment | 174 | 2022-05-05 | 261000 | keep | 0 | May | 2022 | 0.17777 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
MAYAGÃœEZ | 2022-05-05 18:58 | 2022-05-06 18:25 | 10 | 023:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 3 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | M22050500114 | New_Event |  |  | Include | Wildlife | 1407 | 2022-05-05 | 14070 | keep | 0 | May | 2022 | 0.009583 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-05-05 19:14 | 2022-05-05 21:43 | 75 | 002:29 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050500115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-05-05 | 11175 | keep | 0 | May | 2022 | 0.0076112 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-05-05 19:16 | 2022-05-05 21:30 | 40 | 002:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22050500061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-05-05 | 5360 | keep | 0 | May | 2022 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-05 19:45 | 2022-05-05 20:36 | 9 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE Y CONECTORES SECUNDARIOS | A22050500169 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2022-05-05 | 459 | keep | 0 | May | 2022 | 0.00031262 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-05-05 20:10 | 2022-05-06 02:39 | 10 | 006:29 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR SE DESGANCHO SECUNDARIO | S22050500135 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 389 | 2022-05-05 | 3890 | keep | 0 | May | 2022 | 0.0026495 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-05 20:10 | 2022-05-05 22:50 | 2 | 002:40 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22050500102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2022-05-05 | 320 | keep | 0 | May | 2022 | 0.00021795 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-05-05 20:17 | 2022-05-06 07:16 | 8 | 010:59 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C22050500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 659 | 2022-05-05 | 5272 | keep | 0 | May | 2022 | 0.0035907 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-05-05 20:19 | 2022-05-05 23:10 | 30 | 002:51 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE INSTALO TIGUERO A LINEA PRIMARIA QUE ESTABA CRUZANDO CON LINEA SECUNDARIA EN LO QUE SE REPARA POSTE PRIMARIO INCLINADO | A22050500209 | New_Event | Defective Pole | Include | Include | Equipment | 171 | 2022-05-05 | 5130 | keep | 0 | May | 2022 | 0.003494 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-05-05 20:25 | 2022-05-05 22:38 | 162 | 002:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | P22050500079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-05-05 | 21546 | keep | 0 | May | 2022 | 0.014675 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
BAYAMON | 2022-05-05 21:03 | 2022-05-06 10:41 | 20 | 013:38 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22050500397 | New_Event | Vegetation Contact | Include | Include | Vegetation | 818 | 2022-05-05 | 16360 | keep | 0 | May | 2022 | 0.011143 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-05 21:11 | 2022-05-05 22:04 | 200 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22050500105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2022-05-05 | 10600 | keep | 0 | May | 2022 | 0.0072196 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-05-05 21:22 | 2022-05-06 16:25 | 5 | 019:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZA TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5KVA X 37.5KVA | A22050500214 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1143 | 2022-05-05 | 5715 | keep | 0 | May | 2022 | 0.0038925 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-05 21:46 | 2022-05-06 14:00 | 50 | 016:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO Y SE REPARO NEUTRAL PRIMARIO ROTO | M22050500139 | New_Event | Wire Down | Include | Include | Equipment | 974 | 2022-05-05 | 48700 | keep | 0 | May | 2022 | 0.033169 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-05 21:55 | 2022-05-06 05:09 | 990 | 007:14 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL SOTERRADO DE LA ZONA URBANA DE CABO ROJO Y SE CERRO EL INTERRUPTOR | M22050500142 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 434 | 2022-05-05 | 429660 | keep | 0 | May | 2022 | 0.29264 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
SAN JUAN | 2022-05-05 22:03 | 2022-05-06 20:53 | 100 | 022:50 | P | CABLE SOTERRADO AVERIADO | SE HIZO GOI HACER PRUEBA AVERIA SU-2 A T-15 NUEVA AVERIA VIEJA T-16 A T-15 SE REMPLAZO 1 FASE DEL SU-2 A T-15 | S22050600151 | New_Event | UG Cable Fault | Include | Include | Equipment | 1370 | 2022-05-05 | 137000 | keep | 0 | May | 2022 | 0.09331 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-05 22:47 | 2022-05-06 14:25 | 12 | 015:38 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE | C22050500074 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 938 | 2022-05-05 | 11256 | keep | 0 | May | 2022 | 0.0076664 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-05 22:55 | 2022-05-06 19:20 | 20 | 020:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22050500181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1225 | 2022-05-05 | 24500 | keep | 0 | May | 2022 | 0.016687 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-06 01:05 | 2022-05-06 04:30 | 528 | 003:25 | T | LINEA DE TRANSMISION 38KV | DISPARO DE INTERRUPTOR 6012-02 SE RETIRO OVERHEAD CAIDO DE LA LINEA 5600 SOBRE EL ALIMENTADOR Y SE CERRO EL INTERRUPTOR ESTE ESTA LLEVANDO LA CARGA DEL 6012-01. | M22050600006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2022-05-06 | 108240 | keep | 0 | May | 2022 | 0.073722 | 0.00035962 | Sustained | FALSE | FALSE | Not_TMED_Event | 528
MAYAGÃœEZ | 2022-05-06 01:05 | 2022-05-06 04:30 | 4664 | 003:25 | T | LINEA DE TRANSMISION 38KV | DISPARO DE INTERRUPTOR SE RETIRO OVERHEAD CAIDO DE LA LINEA 5600 SOBRE EL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M22050600006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2022-05-06 | 956120 | keep | 0 | May | 2022 | 0.65121 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
PONCE | 2022-05-06 01:20 | 2022-05-06 01:21 | 562 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 562 | keep | 0 | May | 2022 | 0.00038278 | 0.00038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 562
PONCE | 2022-05-06 01:20 | 2022-05-06 01:21 | 688 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 688 | keep | 0 | May | 2022 | 0.00046859 | 0.00046859 | Momentary | FALSE | FALSE | Not_TMED_Event | 688
ARECIBO | 2022-05-06 02:07 | 2022-05-06 04:10 | 6 | 002:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES AVERIADO | A22050600003 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2022-05-06 | 738 | keep | 0 | May | 2022 | 0.00050265 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-05-06 03:20 | 2022-05-06 11:52 | 50 | 008:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REEMPLAZO CAJA PRIMARIA | C22050600002 | New_Event | Cutout Failure | Include | Include | Equipment | 512 | 2022-05-06 | 25600 | keep | 0 | May | 2022 | 0.017436 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-06 04:40 | 2022-05-06 10:45 | 87 | 006:05 | P | DESGANCHE | SE RETIRO ARBOL Y SE REPUSO 2 X 100 EN C/L SE TRABAJO CON GOI BY-220506-02A RELACIONADO A EVENTO P22050600008 | B22050600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2022-05-06 | 31755 | keep | 0 | May | 2022 | 0.021628 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
BAYAMON | 2022-05-06 04:44 | 2022-05-06 07:39 | 75 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L 1 X 65 EN RISER Y 1 X 40 EN SU-2 | S22050600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2022-05-06 | 13125 | keep | 0 | May | 2022 | 0.0089394 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-05-06 05:09 | 2022-05-06 12:18 | 80 | 007:09 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO CAJAS SECAS AVERIADAS EN MH-2A | M22050600037 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 429 | 2022-05-06 | 34320 | keep | 0 | May | 2022 | 0.023375 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-05-06 05:46 | 2022-05-06 07:42 | 15 | 001:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR POR PAJARO | A22050600004 | New_Event |  |  | Include | Wildlife | 116 | 2022-05-06 | 1740 | keep | 0 | May | 2022 | 0.0011851 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-06 06:14 | 2022-05-06 17:12 | 50 | 010:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M22050600039 | New_Event | Cutout Failure | Include | Include | Equipment | 658 | 2022-05-06 | 32900 | keep | 0 | May | 2022 | 0.022408 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-06 06:31 | 2022-05-06 08:36 | 184 | 002:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA | S22050600004 | New_Event | Wire Down | Include | Include | Equipment | 125 | 2022-05-06 | 23000 | keep | 0 | May | 2022 | 0.015665 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
CAGUAS | 2022-05-06 07:06 | 2022-05-06 07:07 | 125 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22050600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 125 | keep | 0 | May | 2022 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-05-06 07:13 | 2022-05-06 16:42 | 12 | 009:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y 1 X 40 EN SU-2 SE REMPLAZO PORTAFUSIBLE | S22050600007 | New_Event | Cutout Failure | Include | Include | Equipment | 569 | 2022-05-06 | 6828 | keep | 0 | May | 2022 | 0.0046505 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-06 07:14 | 2022-05-06 08:50 | 5 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22050600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-05-06 | 480 | keep | 0 | May | 2022 | 0.00032693 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-05-06 07:36 | 2022-05-06 10:18 | 830 | 002:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 200 EN CORTE DE LINEA CRUCE POR PALOMA | C22050600010 | New_Event |  |  | Include | Wildlife | 162 | 2022-05-06 | 134460 | keep | 0 | May | 2022 | 0.09158 | 0.00056531 | Sustained | FALSE | FALSE | Not_TMED_Event | 830
BAYAMON | 2022-05-06 07:39 | 2022-05-06 10:30 | 75 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L Y 1 X 65 EN RISER Y 1 X 40 EN SU-2 AVERIA NUEVA T-3 @ T-4 VIEJA VIEJA SU-2 @ T-4 SE QUEDO FUERA EL T-4 | S22050600003 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-05-06 | 12825 | keep | 0 | May | 2022 | 0.008735 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-06 07:40 | 2022-05-06 15:45 | 1 | 008:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA SE SE ENCONTRO CAUSA | M22050600048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 485 | 2022-05-06 | 485 | keep | 0 | May | 2022 | 0.00033033 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-06 07:50 | 2022-05-06 10:10 | 500 | 002:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22050600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-05-06 | 70000 | keep | 0 | May | 2022 | 0.047677 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
HUMACAO | 2022-05-06 08:16 | 2022-05-06 08:17 | 989 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22050600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 989 | keep | 0 | May | 2022 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
MAYAGÃœEZ | 2022-05-06 08:18 | 2022-05-06 10:47 | 1 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO INFORMARON CAUSA | M22050600052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-05-06 | 149 | keep | 0 | May | 2022 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-06 08:30 | 2022-05-06 14:20 | 50 | 005:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA POR CAJA PRIMARIA QUEMADA | P22050600014 | New_Event | Cutout Failure | Include | Include | Equipment | 350 | 2022-05-06 | 17500 | keep | 0 | May | 2022 | 0.011919 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-06 08:31 | 2022-05-06 19:00 | 35 | 010:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22050600014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 629 | 2022-05-06 | 22015 | keep | 0 | May | 2022 | 0.014994 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-05-06 08:32 | 2022-05-06 11:19 | 350 | 002:47 | P | DESGANCHE | 1 X 80, 1 X 65 Y 1 X 50 EN CORTES DE LINEA SE RETIRO PARARRAYO Y DESGANCHE | R22050600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-05-06 | 58450 | keep | 0 | May | 2022 | 0.03981 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
MAYAGÃœEZ | 2022-05-06 08:33 | 2022-05-06 12:50 | 70 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M22050600055 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2022-05-06 | 17990 | keep | 0 | May | 2022 | 0.012253 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-05-06 08:36 | 2022-05-06 08:37 | 6136 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | B22050600000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-05-06 | 6136 | keep | 0 | May | 2022 | 0.0041792 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-06 08:37 | 2022-05-06 17:15 | 184 | 008:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA | S22050600004 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 518 | 2022-05-06 | 95312 | keep | 0 | May | 2022 | 0.064917 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
CAGUAS | 2022-05-06 08:37 | 2022-05-06 11:59 | 10 | 003:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 Y 2 X 50 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22050600039 | New_Event | Cutout Failure | Include | Include | Equipment | 202 | 2022-05-06 | 2020 | keep | 0 | May | 2022 | 0.0013758 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-06 08:40 | 2022-05-06 15:00 | 15 | 006:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZA TRANSFORMADOR DE 50KVA X 50KVA | A22050600013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 380 | 2022-05-06 | 5700 | keep | 0 | May | 2022 | 0.0038822 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-05-06 08:45 | 2022-05-06 11:18 | 1 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 8 EN BANCO DE TRANSFORMADORES | C22050600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2022-05-06 | 153 | keep | 0 | May | 2022 | 0.00010421 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-06 08:50 | 2022-05-06 11:59 | 1 | 003:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR AVE | S22050600020 | New_Event |  |  | Include | Wildlife | 189 | 2022-05-06 | 189 | keep | 0 | May | 2022 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-06 08:54 | 2022-05-06 14:08 | 68 | 005:14 | P | DESGANCHE | 2 X 40 EN C/L | R22050600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2022-05-06 | 21352 | keep | 0 | May | 2022 | 0.014543 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2022-05-06 09:08 | 2022-05-06 09:57 | 8 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22050500100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2022-05-06 | 392 | keep | 0 | May | 2022 | 0.00026699 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-05-06 09:16 | 2022-05-06 12:30 | 12 | 003:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR NEUTRAL SECUNDARIO | S22050600024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 194 | 2022-05-06 | 2328 | keep | 0 | May | 2022 | 0.0015856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-05-06 09:24 | 2022-05-06 09:26 | 1483 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INERRUPTOR SE CERRO POR CONTROL 30% DE LA CARGA POR 1336-08 | S22050600000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-05-06 | 2966 | keep | 0 | May | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-06 09:24 | 2022-05-06 09:26 | 1500 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INERRUPTOR SE CERRO POR CONTROL PARTE DE LA CARGA POR 1336-08 | S22050600000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-05-06 | 3000 | keep | 0 | May | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-05-06 09:24 | 2022-05-06 09:26 | 5290 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INERRUPTOR SE CERRO POR CONTROL LLEVA 1336-09, 30% 1204-04, PARTE 1204-05 | S22050600000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-05-06 | 10580 | keep | 0 | May | 2022 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-05-06 09:24 | 2022-05-06 09:26 | 207 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INERRUPTOR SE CERRO POR CONTROL CARGA POR 1336-08 | S22050600000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-05-06 | 414 | keep | 0 | May | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-05-06 09:26 | 2022-05-06 17:55 | 50 | 008:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE CORTE DE LINEA | S22050600085 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 509 | 2022-05-06 | 25450 | keep | 0 | May | 2022 | 0.017334 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-05-06 09:41 | 2022-05-06 13:59 | 2 | 004:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | P22050600023 | New_Event | Bad Weather | Include | Include | Weather | 258 | 2022-05-06 | 516 | keep | 0 | May | 2022 | 0.00035145 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-05-06 09:44 | 2022-05-06 09:45 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22050600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 3699 | keep | 0 | May | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
FAJARDO | 2022-05-06 10:03 | 2022-05-06 13:14 | 8 | 003:11 | P | TRANSFORMADOR AVERIADO | 2 X 10 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 50 KVA X 50 KVA | R22050600016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 191 | 2022-05-06 | 1528 | keep | 0 | May | 2022 | 0.0010407 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-06 10:20 | 2022-05-06 10:21 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22050600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 3458 | keep | 0 | May | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2022-05-06 10:21 | 2022-05-06 17:15 | 80 | 006:54 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO ENCONTRARON CAUSA | M22050600091 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 414 | 2022-05-06 | 33120 | keep | 0 | May | 2022 | 0.022558 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-05-06 10:24 | 2022-05-06 12:03 | 10 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BARRA EN PEDESTAL SECUNDARIO | P22050600027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2022-05-06 | 990 | keep | 0 | May | 2022 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-06 10:27 | 2022-05-07 09:43 | 20 | 023:16 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050600074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1396 | 2022-05-06 | 27920 | keep | 0 | May | 2022 | 0.019016 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-06 10:30 | 2022-05-06 13:57 | 6 | 003:27 | P | NO SE REPORTO CAUSA | SE ESTABLECIO GOI PARA HACER PRUEBA DE CABLE SOTERRADODE SU1 A T4 | S22050600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 207 | 2022-05-06 | 1242 | keep | 0 | May | 2022 | 0.00084592 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-05-06 10:30 | 2022-05-06 12:24 | 124 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22050600055 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2022-05-06 | 14136 | keep | 0 | May | 2022 | 0.009628 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
BARRANQUITAS | 2022-05-06 10:32 | 2022-05-06 14:00 | 5 | 003:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22050600056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-05-06 | 1040 | keep | 0 | May | 2022 | 0.00070834 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-05-06 10:33 | 2022-05-07 11:45 | 8 | 025:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE DE LINEA A CAJA | S22050600060 | New_Event | Wire Down | Include | Include | Equipment | 1512 | 2022-05-06 | 12096 | keep | 0 | May | 2022 | 0.0082385 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-06 10:34 | 2022-05-06 14:30 | 10 | 003:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR LINEAS SECUNDARIAS Y TRANSFORMADOR A POSTE NUEVO | M22050600075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 236 | 2022-05-06 | 2360 | keep | 0 | May | 2022 | 0.0016074 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-06 10:49 | 2022-05-06 15:10 | 100 | 004:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22050600082 | New_Event | Wire Down | Include | Include | Equipment | 261 | 2022-05-06 | 26100 | keep | 0 | May | 2022 | 0.017777 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-06 10:55 | 2022-05-06 12:25 | 8 | 001:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE | S22050600053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2022-05-06 | 720 | keep | 0 | May | 2022 | 0.00049039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-05-06 11:16 | 2022-05-06 14:45 | 200 | 003:29 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE SECUNDARIO SOBRE LINEA PRIMARIA | C22050600063 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 209 | 2022-05-06 | 41800 | keep | 0 | May | 2022 | 0.02847 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-05-06 11:47 | 2022-05-06 17:26 | 20 | 005:39 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA REEMPLAZO DE POSTE PARTIDO | A22050600046 | New_Event | Defective Pole | Include | Include | Equipment | 339 | 2022-05-06 | 6780 | keep | 0 | May | 2022 | 0.0046178 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-06 11:50 | 2022-05-06 12:35 | 12 | 000:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 FUSIBLE RBA DE 15AMP. MAL TIEMPO | B22050600028 | New_Event | Bad Weather | Include | Include | Weather | 45 | 2022-05-06 | 540 | keep | 0 | May | 2022 | 0.00036779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-06 12:18 | 2022-05-06 12:20 | 990 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR | M22050600105 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2022-05-06 | 1980 | keep | 0 | May | 2022 | 0.0013486 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BAYAMON | 2022-05-06 12:18 | 2022-05-06 14:28 | 36 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 30 EN CORTES DE LINEA | B22050600031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-05-06 | 4680 | keep | 0 | May | 2022 | 0.0031875 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2022-05-06 12:20 | 2022-05-06 13:55 | 80 | 001:35 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO CAJAS SECAS AVERIADAS EN MH-2A | M22050600037 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 95 | 2022-05-06 | 7600 | keep | 0 | May | 2022 | 0.0051763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-06 12:44 | 2022-05-06 12:45 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERE DE INTERRUPTOR | M22050600118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-06 12:44 | 2022-05-06 12:45 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERE DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M22050600118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-06 13:00 | 2022-05-07 03:10 | 1 | 014:10 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22050600125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 850 | 2022-05-06 | 850 | keep | 0 | May | 2022 | 0.00057893 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-06 13:02 | 2022-05-06 13:03 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22050600127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-06 13:02 | 2022-05-06 13:03 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M22050600127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
CANOVANAS | 2022-05-06 13:10 | 2022-05-06 13:11 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
AGUADILLA | 2022-05-06 13:10 | 2022-05-07 05:25 | 15 | 016:15 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA / NO SE ENCONTRO CAUSA | M22050600130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 975 | 2022-05-06 | 14625 | keep | 0 | May | 2022 | 0.009961 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-05-06 13:18 | 2022-05-06 14:15 | 15 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | C22050600005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-05-06 | 855 | keep | 0 | May | 2022 | 0.00058234 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-05-06 13:34 | 2022-05-07 13:00 | 1 | 023:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA POR UNO DE 25KVA | A22050600058 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1406 | 2022-05-06 | 1406 | keep | 0 | May | 2022 | 0.00095762 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-06 13:55 | 2022-05-07 09:22 | 80 | 019:27 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO CAJAS SECAS AVERIADAS EN MH-2A | M22050600037 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 1167 | 2022-05-06 | 93360 | keep | 0 | May | 2022 | 0.063587 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-06 13:57 | 2022-05-06 14:45 | 75 | 000:48 | P | NO SE REPORTO CAUSA | SE ABRIO RISER A SU 1 A PETICION PERSONAL SOTERRADO PARA HACER PRUEBA DE CABLE | S22050600003 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 48 | 2022-05-06 | 3600 | keep | 0 | May | 2022 | 0.0024519 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-06 14:04 | 2022-05-06 21:01 | 3 | 006:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN C/L REMPLAZO AISLADOR QUEMADO | R22050600028 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 417 | 2022-05-06 | 1251 | keep | 0 | May | 2022 | 0.00085205 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-05-06 14:09 | 2022-05-06 15:50 | 25 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22050600081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-05-06 | 2525 | keep | 0 | May | 2022 | 0.0017198 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-06 14:10 | 2022-05-06 17:06 | 50 | 002:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22050600147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-05-06 | 8800 | keep | 0 | May | 2022 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-06 14:32 | 2022-05-06 15:26 | 10 | 000:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22050600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2022-05-06 | 540 | keep | 0 | May | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-05-06 14:35 | 2022-05-06 18:20 | 40 | 003:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22050600155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-05-06 | 9000 | keep | 0 | May | 2022 | 0.0061299 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-06 14:41 | 2022-05-06 16:30 | 150 | 001:49 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA | B22050600046 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 109 | 2022-05-06 | 16350 | keep | 0 | May | 2022 | 0.011136 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-06 14:45 | 2022-05-06 14:52 | 6 | 000:07 | P | NO SE REPORTO CAUSA | SE REALIZO PRUEBA DE CABLE Y NO SE ENCONTRO AVERIA. SE CERRO DE SU1 A T4 Y SE DEJO EN PARKING BUSHING AVERIA VIEJA DE T3 2 T4 | S22050600003 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-05-06 | 42 | keep | 0 | May | 2022 | 2.8606e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-06 14:49 | 2022-05-06 18:27 | 15 | 003:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | MAQUINA LIMPIANDO TERRENO SACUDIO POSTE PRIMARIO | C22050600086 | New_Event |  |  | Include | Wildlife | 218 | 2022-05-06 | 3270 | keep | 0 | May | 2022 | 0.0022272 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-05-06 14:53 | 2022-05-06 16:45 | 300 | 001:52 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22050600087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-05-06 | 33600 | keep | 0 | May | 2022 | 0.022885 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2022-05-06 15:01 | 2022-05-06 16:30 | 100 | 001:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P22050600047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-05-06 | 8900 | keep | 0 | May | 2022 | 0.0060617 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-05-06 15:19 | 2022-05-07 00:20 | 60 | 009:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 Y 2 X 40 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | B22050600050 | New_Event | Wire Down | Include | Include | Equipment | 541 | 2022-05-06 | 32460 | keep | 0 | May | 2022 | 0.022108 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-05-06 15:22 | 2022-05-06 15:23 | 932 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22050600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 932 | keep | 0 | May | 2022 | 0.00063478 | 0.00063478 | Momentary | FALSE | FALSE | Not_TMED_Event | 932
MAYAGÃœEZ | 2022-05-06 15:32 | 2022-05-06 18:50 | 25 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22050600169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2022-05-06 | 4950 | keep | 0 | May | 2022 | 0.0033714 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-06 15:51 | 2022-05-06 17:45 | 41 | 001:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | R22050600033 | New_Event |  |  | Include | Wildlife | 114 | 2022-05-06 | 4674 | keep | 0 | May | 2022 | 0.0031834 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
MAYAGÃœEZ | 2022-05-06 15:52 | 2022-05-07 09:00 | 15 | 017:08 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050600175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1028 | 2022-05-06 | 15420 | keep | 0 | May | 2022 | 0.010502 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-05-06 15:54 | 2022-05-06 15:55 | 932 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22050600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 932 | keep | 0 | May | 2022 | 0.00063478 | 0.00063478 | Momentary | FALSE | FALSE | Not_TMED_Event | 932
BARRANQUITAS | 2022-05-06 16:03 | 2022-05-06 16:50 | 10 | 000:47 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22050600093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2022-05-06 | 470 | keep | 0 | May | 2022 | 0.00032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-05-06 16:08 | 2022-05-06 17:29 | 35 | 001:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS | A22050600076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-05-06 | 2835 | keep | 0 | May | 2022 | 0.0019309 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-05-06 16:14 | 2022-05-06 16:15 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050600060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
AGUADILLA | 2022-05-06 16:24 | 2022-05-06 23:02 | 3 | 006:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR VEHICULO IMPACTO RISER SECUNDARIO | M22050600182 | New_Event |  |  | Include | Wildlife | 398 | 2022-05-06 | 1194 | keep | 0 | May | 2022 | 0.00081323 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-05-06 16:29 | 2022-05-06 17:13 | 10 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22050600055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2022-05-06 | 440 | keep | 0 | May | 2022 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-06 16:31 | 2022-05-06 18:17 | 5 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | B22050600061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2022-05-06 | 530 | keep | 0 | May | 2022 | 0.00036098 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-05-06 16:33 | 2022-05-06 16:51 | 50 | 000:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P22050600051 | New_Event |  |  | Include | Wildlife | 18 | 2022-05-06 | 900 | keep | 0 | May | 2022 | 0.00061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-06 16:35 | 2022-05-06 17:52 | 3 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO | S22050600128 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2022-05-06 | 231 | keep | 0 | May | 2022 | 0.00015733 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-05-06 16:35 | 2022-05-07 12:28 | 35 | 019:53 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | S22050600129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1193 | 2022-05-06 | 41755 | keep | 0 | May | 2022 | 0.028439 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-05-06 16:41 | 2022-05-06 19:55 | 50 | 003:14 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22050600187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-05-06 | 9700 | keep | 0 | May | 2022 | 0.0066066 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-06 17:23 | 2022-05-07 08:52 | 25 | 015:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO DE CAJA A LINEA | S22050600143 | New_Event | Wire Down | Include | Include | Equipment | 929 | 2022-05-06 | 23225 | keep | 0 | May | 2022 | 0.015818 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-06 17:31 | 2022-05-06 20:51 | 43 | 003:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22050600146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2022-05-06 | 8600 | keep | 0 | May | 2022 | 0.0058574 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BAYAMON | 2022-05-06 18:22 | 2022-05-07 09:59 | 50 | 015:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S22050700164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 937 | 2022-05-06 | 46850 | keep | 0 | May | 2022 | 0.031909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-06 18:25 | 2022-05-07 09:01 | 70 | 014:36 | P | NO SE REPORTO CAUSA | 1 X 65 EN AEREO PROVISIONAL | S22050700167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 876 | 2022-05-06 | 61320 | keep | 0 | May | 2022 | 0.041765 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-05-06 18:33 | 2022-05-06 20:12 | 135 | 001:39 | P | DESGANCHE | 1 X 140 EN C/L | R22050600057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-05-06 | 13365 | keep | 0 | May | 2022 | 0.0091028 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
UTUADO | 2022-05-06 18:38 | 2022-05-06 19:03 | 932 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA RETIRAR HOT CLAMP PEGANDO A ESTRUCTURA | A22050600086 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2022-05-06 | 23300 | keep | 0 | May | 2022 | 0.01587 | 0.00063478 | Sustained | FALSE | FALSE | Not_TMED_Event | 932
HUMACAO | 2022-05-06 18:47 | 2022-05-06 18:48 | 824 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 65% DE SU CARGA POR 2604-03 | C22050600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-06 | 824 | keep | 0 | May | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
AGUADILLA | 2022-05-06 18:52 | 2022-05-06 22:10 | 150 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22050600212 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2022-05-06 | 29700 | keep | 0 | May | 2022 | 0.020229 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-05-06 18:53 | 2022-05-06 20:09 | 10 | 001:16 | P | CABLE SOTERRADO AVERIADO | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES EN LA BARRA DE PEDESTAL | A22050600087 | New_Event | UG Cable Fault | Include | Include | Equipment | 76 | 2022-05-06 | 760 | keep | 0 | May | 2022 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-06 19:23 | 2022-05-06 21:43 | 8 | 002:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22050600035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 140 | 2022-05-06 | 1120 | keep | 0 | May | 2022 | 0.00076283 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-06 19:25 | 2022-05-07 02:20 | 100 | 006:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA VEHICULO IMPACTO POSTE PRIMARIO | M22050600231 | New_Event |  |  | Include | Wildlife | 415 | 2022-05-06 | 41500 | keep | 0 | May | 2022 | 0.028265 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-06 20:38 | 2022-05-07 01:25 | 30 | 004:47 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22050600084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2022-05-06 | 8610 | keep | 0 | May | 2022 | 0.0058642 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-06 21:01 | 2022-05-07 08:53 | 60 | 011:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22050600191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 712 | 2022-05-06 | 42720 | keep | 0 | May | 2022 | 0.029096 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-05-06 21:36 | 2022-05-07 11:50 | 161 | 014:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE INSTALO RIGIDO | R22050600073 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 854 | 2022-05-06 | 137494 | keep | 0 | May | 2022 | 0.093647 | 0.00010966 | Sustained | FALSE | FALSE | Not_TMED_Event | 161
AGUADILLA | 2022-05-06 22:24 | 2022-05-07 04:10 | 200 | 005:46 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA TENIA FUSIBLE DE 80 AMP Y LLEVA DE 100 AMP | M22050600274 | New_Event | Trip Due To Overload | Include | Include | Other | 346 | 2022-05-06 | 69200 | keep | 0 | May | 2022 | 0.047132 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-06 22:33 | 2022-05-07 08:54 | 200 | 010:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22050600278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 621 | 2022-05-06 | 124200 | keep | 0 | May | 2022 | 0.084592 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-05-06 22:36 | 2022-05-07 01:17 | 30 | 002:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A22050600099 | New_Event | Bad Weather | Include | Include | Weather | 161 | 2022-05-06 | 4830 | keep | 0 | May | 2022 | 0.0032897 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-05-07 02:17 | 2022-05-07 03:33 | 1173 | 001:16 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE DISPARO INTERRUPTOR DEBIDO AISLADOR ROTO SECIONALIZO LINEA | P22050700004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 76 | 2022-05-07 | 89148 | keep | 0 | May | 2022 | 0.060718 | 0.00079892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1173
MAYAGÃœEZ | 2022-05-07 02:20 | 2022-05-07 14:05 | 200 | 011:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE PARTIDO A CAUSA DE ACCIDENTE VEHICULAR | M22050700081 | Additional_clients |  |  | Include | Wildlife | 705 | 2022-05-07 | 141000 | keep | 0 | May | 2022 | 0.096034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-07 02:30 | 2022-05-07 03:00 | 15 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22050700002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-05-07 | 450 | keep | 0 | May | 2022 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-07 03:04 | 2022-05-07 05:46 | 60 | 002:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22050700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2022-05-07 | 9720 | keep | 0 | May | 2022 | 0.0066202 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-07 03:08 | 2022-05-07 09:38 | 160 | 006:30 | P | CABLE SOTERRADO AVERIADO | 1 SMU 20 DE 40 AMP. EN SU-8 AVERIA NUEVA DEL T-235 AL T-234, AVERIA VIEJA DEL SU-7 AL T-233 | R22050700001 | New_Event | UG Cable Fault | Include | Include | Equipment | 390 | 2022-05-07 | 62400 | keep | 0 | May | 2022 | 0.0425 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
ARECIBO | 2022-05-07 03:16 | 2022-05-07 09:00 | 80 | 005:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22050700002 | New_Event | Wire Down | Include | Include | Equipment | 344 | 2022-05-07 | 27520 | keep | 0 | May | 2022 | 0.018744 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-05-07 03:33 | 2022-05-07 04:35 | 525 | 001:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | MACHETES ABIERTOS AISLADOR ROTO SE ELIMINO AISLADOR Y SE CERRO MACHETES | P22050700008 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 62 | 2022-05-07 | 32550 | keep | 0 | May | 2022 | 0.02217 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-07 05:12 | 2022-05-07 09:42 | 50 | 004:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050700003 | New_Event | Bad Weather | Include | Include | Weather | 270 | 2022-05-07 | 13500 | keep | 0 | May | 2022 | 0.0091948 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-05-07 06:09 | 2022-05-07 08:46 | 25 | 002:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22050700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-05-07 | 3925 | keep | 0 | May | 2022 | 0.0026733 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-05-07 06:12 | 2022-05-07 06:13 | 4085 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 2404-06 EN SERVICIO | R22050700003 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-07 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-05-07 06:12 | 2022-05-07 06:13 | 7621 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR CARGA POR EL 2402-03 EN SERVICIO | R22050700003 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-07 | 7621 | keep | 0 | May | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
ARECIBO | 2022-05-07 06:22 | 2022-05-07 10:41 | 80 | 004:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA PERSONAL INFORMO NECESIDAD DE DESGANCHE | M22050700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-05-07 | 20720 | keep | 0 | May | 2022 | 0.014112 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-05-07 06:44 | 2022-05-07 11:27 | 14 | 004:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER 1 X 20 EN C/L Y 1 X 10 EN XMR CRUCE X AVE | C22050700003 | New_Event |  |  | Include | Wildlife | 283 | 2022-05-07 | 3962 | keep | 0 | May | 2022 | 0.0026985 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-05-07 06:45 | 2022-05-07 09:36 | 3006 | 002:51 | S | DISPARO DE BARRA DE TRANSMISION | SE DISPARO DE BARRA 38KV SE INSPECCIONO SUBESTACION Y SE ENCONTRO OBJETO DE PLASTICO ENTRE LAS FASES | M22050700060 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 171 | 2022-05-07 | 514026 | keep | 0 | May | 2022 | 0.3501 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-05-07 06:45 | 2022-05-07 09:36 | 179 | 002:51 | S | DISPARO DE BARRA DE TRANSMISION | SE DISPARO DE BARRA 38KV SE INSPECCIONO SUBESTACION Y SE ENCONTRO OBJETO DE PLASTICO ENTRE LAS FASES | M22050700060 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 171 | 2022-05-07 | 30609 | keep | 0 | May | 2022 | 0.020848 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
BAYAMON | 2022-05-07 06:51 | 2022-05-07 08:48 | 130 | 001:57 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L Y 1 X 10 EN XMR | B22050700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2022-05-07 | 15210 | keep | 0 | May | 2022 | 0.010359 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
FAJARDO | 2022-05-07 06:56 | 2022-05-07 07:20 | 81 | 000:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R22050700005 | New_Event |  |  | Include | Wildlife | 24 | 2022-05-07 | 1944 | keep | 0 | May | 2022 | 0.001324 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
FAJARDO | 2022-05-07 07:23 | 2022-05-07 08:45 | 122 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 25 EN CORTES DE LINEA CRUCE POR AVE | R22050700006 | New_Event |  |  | Include | Wildlife | 82 | 2022-05-07 | 10004 | keep | 0 | May | 2022 | 0.0068137 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
CANOVANAS | 2022-05-07 07:23 | 2022-05-07 07:24 | 4085 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 2404-06 | R22050700007 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-05-07 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-05-07 07:23 | 2022-05-07 07:24 | 7621 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR CARGA POR EL 2402-03 | R22050700007 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-05-07 | 7621 | keep | 0 | May | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
SAN JUAN | 2022-05-07 07:24 | 2022-05-07 13:00 | 6 | 005:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA SE RETIRO GLOBO DE LA LINEA | R22050700009 | 1st_after_momentary |  |  | Include | Wildlife | 336 | 2022-05-07 | 2016 | keep | 0 | May | 2022 | 0.0013731 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-07 07:29 | 2022-05-07 08:08 | 2228 | 000:39 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 8007-4 EL CUAL ESTA LLEVANDO LA CARGA DEL 8007-03 | A22050700005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-05-07 | 86892 | keep | 0 | May | 2022 | 0.059182 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-05-07 07:29 | 2022-05-07 08:08 | 438 | 000:39 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A22050700005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-05-07 | 17082 | keep | 0 | May | 2022 | 0.011634 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
BARRANQUITAS | 2022-05-07 07:31 | 2022-05-07 16:42 | 20 | 009:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22050700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 551 | 2022-05-07 | 11020 | keep | 0 | May | 2022 | 0.0075057 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-05-07 07:47 | 2022-05-07 07:48 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR QUEDO EN SERVICIO | B22050700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-07 | 1310 | keep | 0 | May | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BARRANQUITAS | 2022-05-07 07:48 | 2022-05-07 07:49 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22050700010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 2725 | keep | 0 | May | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-05-07 07:48 | 2022-05-07 07:49 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22050700010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 1834 | keep | 0 | May | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-05-07 07:48 | 2022-05-07 07:49 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22050700010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 1437 | keep | 0 | May | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-05-07 07:48 | 2022-05-07 07:49 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22050700011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 2565 | keep | 0 | May | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-05-07 07:48 | 2022-05-07 07:49 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22050700011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 3565 | keep | 0 | May | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-05-07 07:48 | 2022-05-07 07:49 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DESGANCHE | P22050700020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 2751 | keep | 0 | May | 2022 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-05-07 07:48 | 2022-05-07 07:49 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DESGANCHE | P22050700020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 576 | keep | 0 | May | 2022 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-05-07 07:48 | 2022-05-07 07:49 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DESGANCHE | P22050700020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 2584 | keep | 0 | May | 2022 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-05-07 07:48 | 2022-05-07 07:49 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DESGANCHE | P22050700020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 1606 | keep | 0 | May | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-05-07 07:48 | 2022-05-07 07:49 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DESGANCHE | P22050700020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 29 | keep | 0 | May | 2022 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2022-05-07 07:48 | 2022-05-07 07:49 | 4035 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DESGANCHE | P22050700020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 4035 | keep | 0 | May | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-05-07 07:48 | 2022-05-07 07:49 | 3718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DESGANCHE | P22050700020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-07 | 3718 | keep | 0 | May | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2022-05-07 08:13 | 2022-05-07 14:06 | 40 | 005:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO CAJA | S22050700020 | New_Event | Cutout Failure | Include | Include | Equipment | 353 | 2022-05-07 | 14120 | keep | 0 | May | 2022 | 0.0096171 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-05-07 08:15 | 2022-05-07 14:36 | 5 | 006:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA ROTA | M22050700035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 381 | 2022-05-07 | 1905 | keep | 0 | May | 2022 | 0.0012975 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-05-07 08:17 | 2022-05-07 19:15 | 8 | 010:58 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN C/L ELIMINO PARARRAYO | C22050700014 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 658 | 2022-05-07 | 5264 | keep | 0 | May | 2022 | 0.0035853 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-07 08:20 | 2022-05-07 09:56 | 50 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 30 Y 1 X 50 EN CORTE DE LINEA | S22050700023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-05-07 | 4800 | keep | 0 | May | 2022 | 0.0032693 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-07 08:25 | 2022-05-07 11:56 | 15 | 003:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 1 X 80 EN CORTE DE LINEA MAQUINA DE ASFALTO CRUZO FASE | S22050700025 | New_Event |  |  | Include | Wildlife | 211 | 2022-05-07 | 3165 | keep | 0 | May | 2022 | 0.0021557 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-05-07 08:43 | 2022-05-07 13:53 | 189 | 005:10 | P | DESGANCHE | 1 X 100 EN C/L | C22050700018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-05-07 | 58590 | keep | 0 | May | 2022 | 0.039905 | 0.00012873 | Sustained | FALSE | FALSE | Not_TMED_Event | 189
MAYAGÃœEZ | 2022-05-07 08:50 | 2022-05-07 10:04 | 15 | 001:14 | P | SOBRECARGA | 1 X 15 EN TRANSFORMADOR FUSIBLE FUNDIDO POR SOBRECARGA | M22050700053 | New_Event | Trip Due To Overload | Include | Include | Other | 74 | 2022-05-07 | 1110 | keep | 0 | May | 2022 | 0.00075602 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-07 09:17 | 2022-05-07 09:18 | 3070 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B22050700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-07 | 3070 | keep | 0 | May | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-05-07 09:18 | 2022-05-07 11:57 | 80 | 002:39 | P | DESGANCHE | 2 X 100 EN C/L SE DESGANCHO | B22050700014 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-05-07 | 12720 | keep | 0 | May | 2022 | 0.0086635 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-07 09:22 | 2022-05-07 09:23 | 990 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE DEL INTERRUPTOR | M22050700068 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-05-07 | 990 | keep | 0 | May | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2022-05-07 09:23 | 2022-05-07 17:23 | 15 | 008:00 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CAMBIARON TRES CAJAS SECAS Y TRES TERMINACIONES | M22050600196 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 480 | 2022-05-07 | 7200 | keep | 0 | May | 2022 | 0.0049039 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-07 09:38 | 2022-05-07 16:33 | 40 | 006:55 | P | CABLE SOTERRADO AVERIADO | CONSTRUYO AEREO PROVICIONAL DEL SU - 7 @ T - 233 INSTALO C/L 1 X 25 EN C/L NUEVO | R22050700017 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 415 | 2022-05-07 | 16600 | keep | 0 | May | 2022 | 0.011306 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-07 09:50 | 2022-05-07 10:40 | 12 | 000:50 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE SECCIONALIZO PEDESTAL PARA REPARAR SECUNDARIA | R22050700016 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 50 | 2022-05-07 | 600 | keep | 0 | May | 2022 | 0.00040866 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-05-07 10:28 | 2022-05-07 10:29 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | B22050700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-07 | 2435 | keep | 0 | May | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-05-07 10:28 | 2022-05-07 10:29 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | B22050700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-07 | 2956 | keep | 0 | May | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-05-07 10:29 | 2022-05-07 15:00 | 11 | 004:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | S22050700044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 271 | 2022-05-07 | 2981 | keep | 0 | May | 2022 | 0.0020303 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-05-07 10:30 | 2022-05-07 15:30 | 1 | 005:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22050700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 300 | 2022-05-07 | 300 | keep | 0 | May | 2022 | 0.00020433 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-07 10:47 | 2022-05-07 13:05 | 40 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22050700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2022-05-07 | 5520 | keep | 0 | May | 2022 | 0.0037596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-07 11:02 | 2022-05-07 11:03 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22050700013 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-05-07 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-05-07 11:03 | 2022-05-07 13:00 | 80 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050700015 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 117 | 2022-05-07 | 9360 | keep | 0 | May | 2022 | 0.0063751 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-05-07 11:14 | 2022-05-07 15:17 | 44 | 004:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA POR PAJARO | A22050700014 | New_Event |  |  | Include | Wildlife | 243 | 2022-05-07 | 10692 | keep | 0 | May | 2022 | 0.0072823 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
VEGA BAJA | 2022-05-07 11:50 | 2022-05-07 17:10 | 40 | 005:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L 1 X 15 EN XMR SE RETIRO IGUANA | B22050700025 | New_Event |  |  | Include | Wildlife | 320 | 2022-05-07 | 12800 | keep | 0 | May | 2022 | 0.008718 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-07 11:55 | 2022-05-07 15:55 | 30 | 004:00 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S22050700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2022-05-07 | 7200 | keep | 0 | May | 2022 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-07 11:57 | 2022-05-07 19:40 | 75 | 007:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS SE REFIERE PARA TRABAJAR DESGANCHE MASIVO | M22050700095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 463 | 2022-05-07 | 34725 | keep | 0 | May | 2022 | 0.023651 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-05-07 12:15 | 2022-05-07 13:02 | 19 | 000:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE TRANSFORMADOR PARA LEVANTAR LINEA SECUNDARIA DEL PISO AVERIADA POR CAMION | P22050700030 | New_Event |  |  | Include | Wildlife | 47 | 2022-05-07 | 893 | keep | 0 | May | 2022 | 0.00060822 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-05-07 12:30 | 2022-05-07 14:40 | 50 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22050700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-05-07 | 6500 | keep | 0 | May | 2022 | 0.0044271 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-07 13:11 | 2022-05-07 14:35 | 5 | 001:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | S22050700060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-05-07 | 420 | keep | 0 | May | 2022 | 0.00028606 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-05-07 13:15 | 2022-05-07 13:32 | 13 | 000:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA AJUSTAR BANDERA | C22050700044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 17 | 2022-05-07 | 221 | keep | 0 | May | 2022 | 0.00015052 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-05-07 13:30 | 2022-05-07 16:15 | 6 | 002:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22050500455 | New_Event | Secondary Wire Down | Include | Include | Equipment | 165 | 2022-05-07 | 990 | keep | 0 | May | 2022 | 0.00067428 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-07 13:44 | 2022-05-07 13:50 | 80 | 000:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22050700049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-05-07 | 480 | keep | 0 | May | 2022 | 0.00032693 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-07 13:48 | 2022-05-07 16:27 | 150 | 002:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L 1 X 65 EN C/L Y 1 X 85 SU-1 | B22050700035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2022-05-07 | 23850 | keep | 0 | May | 2022 | 0.016244 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-07 13:59 | 2022-05-07 14:48 | 10 | 000:49 | P | SOBRECARGA | 1 X 10 EN TRANSFORMADOR SE FUNDIO FUSIBLE POR SOBRECARGA | M22050700119 | New_Event | Trip Due To Overload | Include | Include | Other | 49 | 2022-05-07 | 490 | keep | 0 | May | 2022 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-05-07 14:08 | 2022-05-08 09:05 | 35 | 018:57 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22050700047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1137 | 2022-05-07 | 39795 | keep | 0 | May | 2022 | 0.027104 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-05-07 14:15 | 2022-05-07 18:00 | 511 | 003:45 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN C/L CONTAMINACION EN SU - 4A | R22050700029 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 225 | 2022-05-07 | 114975 | keep | 0 | May | 2022 | 0.078309 | 0.00034804 | Sustained | FALSE | FALSE | Not_TMED_Event | 511
PONCE | 2022-05-07 14:15 | 2022-05-07 14:16 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050700051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-07 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2022-05-07 14:21 | 2022-05-07 17:13 | 1 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER EMPLEADO NO ENCONTRO CAUSA | M22050700133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2022-05-07 | 172 | keep | 0 | May | 2022 | 0.00011715 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-07 14:25 | 2022-05-07 16:54 | 1 | 002:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | A22050700011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 149 | 2022-05-07 | 149 | keep | 0 | May | 2022 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-07 14:27 | 2022-05-10 12:02 | 2 | 069:35 | P | ERROR HUMANO | CERRAR MANIJA DEL MH#3 @ MH#2. EL PERSONAL DEL CAMPO (AXEL RODRIGUEZ) OLVIDO CERRAR DE MH-3 @ MH-2 REFERENTE A VIA LIBRE D2022-00757 | S22051000027 | New_Event | Human Error | Include | Include | Other | 4175 | 2022-05-07 | 8350 | keep | 0 | May | 2022 | 0.0056871 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-05-07 14:45 | 2022-05-07 15:15 | 1 | 000:30 | P | DESGANCHE | 1 X 25 EN C/L | R22050700052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-05-07 | 30 | keep | 0 | May | 2022 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-07 15:00 | 2022-05-07 15:01 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050700056 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-07 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
AGUADILLA | 2022-05-07 15:13 | 2022-05-07 19:35 | 60 | 004:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22050700075 | New_Event | Wire Down | Include | Include | Equipment | 262 | 2022-05-07 | 15720 | keep | 0 | May | 2022 | 0.010707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-07 15:19 | 2022-05-07 17:15 | 75 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22050700049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-05-07 | 8700 | keep | 0 | May | 2022 | 0.0059255 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-05-07 15:21 | 2022-05-07 16:22 | 15 | 001:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22050700050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2022-05-07 | 915 | keep | 0 | May | 2022 | 0.0006232 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-05-07 15:39 | 2022-05-07 15:40 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22050700123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-07 | 1827 | keep | 0 | May | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2022-05-07 15:53 | 2022-05-07 21:14 | 40 | 005:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REMPLAZO CAJA QUEMADA | S22050700070 | New_Event | Cutout Failure | Include | Include | Equipment | 321 | 2022-05-07 | 12840 | keep | 0 | May | 2022 | 0.0087453 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-07 15:56 | 2022-05-07 23:59 | 125 | 008:03 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | S22050700071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 483 | 2022-05-07 | 60375 | keep | 0 | May | 2022 | 0.041121 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
PONCE | 2022-05-07 16:01 | 2022-05-07 16:02 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22050700061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-07 | 3114 | keep | 0 | May | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
SAN JUAN | 2022-05-07 16:06 | 2022-05-07 18:26 | 194 | 002:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA RAMA SOBRE LINEA | S22050700072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-05-07 | 27160 | keep | 0 | May | 2022 | 0.018499 | 0.00013213 | Sustained | FALSE | FALSE | Not_TMED_Event | 194
CAGUAS | 2022-05-07 16:08 | 2022-05-07 16:09 | 1342 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22050700048 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-07 | 1342 | keep | 0 | May | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2022-05-07 16:09 | 2022-05-07 18:08 | 184 | 001:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C22050700050 | 1st_after_momentary |  |  | Include | Wildlife | 119 | 2022-05-07 | 21896 | keep | 0 | May | 2022 | 0.014913 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
AGUADILLA | 2022-05-07 16:31 | 2022-05-08 00:55 | 60 | 008:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22050700130 | New_Event |  |  | Include | Wildlife | 504 | 2022-05-07 | 30240 | keep | 0 | May | 2022 | 0.020596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-05-07 17:21 | 2022-05-07 18:47 | 7 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR DIGGER SACUDIO POSTE | C22050700059 | New_Event |  |  | Include | Wildlife | 86 | 2022-05-07 | 602 | keep | 0 | May | 2022 | 0.00041002 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-07 17:35 | 2022-05-07 19:00 | 50 | 001:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA | B22050700070 | New_Event | Cutout Failure | Include | Include | Equipment | 85 | 2022-05-07 | 4250 | keep | 0 | May | 2022 | 0.0028947 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-05-07 17:38 | 2022-05-07 19:43 | 15 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA SOTERRADA | C22050700061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2022-05-07 | 1875 | keep | 0 | May | 2022 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-05-07 17:46 | 2022-05-07 20:00 | 60 | 002:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22050700072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-05-07 | 8040 | keep | 0 | May | 2022 | 0.005476 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-07 18:04 | 2022-05-07 22:00 | 4 | 003:56 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22050700056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-05-07 | 944 | keep | 0 | May | 2022 | 0.00064295 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-05-07 18:52 | 2022-05-08 09:35 | 10 | 014:43 | P | ERROR HUMANO | SE CERRO OPERADOR EN EL VACUUM SWITCH (MANHOLE 2A) QUE HABIAN DEJADO ABIERTO CUANDO REMPLAZARON CAJAS SECAS | M22050700141 | New_Event | Human Error | Include | Include | Other | 883 | 2022-05-07 | 8830 | keep | 0 | May | 2022 | 0.0060141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-07 19:10 | 2022-05-07 19:11 | 271 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22050700093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-07 | 271 | keep | 0 | May | 2022 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2022-05-07 20:19 | 2022-05-07 23:10 | 60 | 002:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22050700075 | New_Event | Wire Down | Include | Include | Equipment | 171 | 2022-05-07 | 10260 | keep | 0 | May | 2022 | 0.006988 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-05-07 20:59 | 2022-05-08 17:16 | 45 | 020:17 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B22050700080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1217 | 2022-05-07 | 54765 | keep | 0 | May | 2022 | 0.0373 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-05-07 20:59 | 2022-05-08 07:40 | 45 | 010:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22050700080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 641 | 2022-05-07 | 28845 | keep | 0 | May | 2022 | 0.019646 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-05-07 21:09 | 2022-05-08 00:50 | 200 | 003:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN ENTRADA DE CONVERTIDOR Y 1 X 200 EN SALIDA DE CONVERTIDOR SE REMPLAZO 1 PORTAFUSIBLES QUEMADO | M22050700170 | New_Event | Cutout Failure | Include | Include | Equipment | 221 | 2022-05-07 | 44200 | keep | 0 | May | 2022 | 0.030104 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-07 21:35 | 2022-05-08 16:10 | 3 | 018:35 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR NO TAPEA MAS - HAY QUE REMPLAZARLO - ES DE 10KVA @ 8KV - LO REFIRIERON POR E-MAIL @ GABRIEL MACHADO | B22050700091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1115 | 2022-05-07 | 3345 | keep | 0 | May | 2022 | 0.0022783 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-05-07 21:57 | 2022-05-08 03:40 | 10 | 005:43 | P | TRANSFORMADOR AVERIADO | SE VERIFICO TRANSFORMADOR AVERIADO SE PASO LA CARGA DE ESTE TRANSFORMADOR A OTRO TRANSFORMADOR QUE HABIA EN EL AREA | M22050700182 | New_Event | Service Transformer Failure | Include | Include | Equipment | 343 | 2022-05-07 | 3430 | keep | 0 | May | 2022 | 0.0023362 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-07 22:44 | 2022-05-08 06:33 | 141 | 007:49 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 100 EN C/L | C22050700072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 469 | 2022-05-07 | 66129 | keep | 0 | May | 2022 | 0.04504 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
SAN JUAN | 2022-05-07 22:51 | 2022-05-08 08:04 | 117 | 009:13 | P | DESGANCHE | 1 X 65 EN C/L | R22050700089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 553 | 2022-05-07 | 64701 | keep | 0 | May | 2022 | 0.044068 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
BAYAMON | 2022-05-07 22:58 | 2022-05-07 23:56 | 60 | 000:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22050700094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-05-07 | 3480 | keep | 0 | May | 2022 | 0.0023702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-07 23:33 | 2022-05-07 23:34 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22050700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-07 | 5252 | keep | 0 | May | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
CAGUAS | 2022-05-07 23:35 | 2022-05-08 07:52 | 50 | 008:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22050700074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 497 | 2022-05-07 | 24850 | keep | 0 | May | 2022 | 0.016925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-07 23:49 | 2022-05-08 08:27 | 18 | 008:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22050700097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 518 | 2022-05-07 | 9324 | keep | 0 | May | 2022 | 0.0063505 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-05-08 00:15 | 2022-05-08 02:30 | 80 | 002:15 | P | ESTRUCTURA AVERIADA | 1 X 100 EN CORTE DE LINEA POSTE PARTIDO POR ACCIDENTE DE AUTO | B22050800001 | New_Event | Defective Pole | Include | Include | Equipment | 135 | 2022-05-08 | 10800 | keep | 0 | May | 2022 | 0.0073558 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-05-08 00:16 | 2022-05-08 12:15 | 5 | 011:59 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R22050800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 719 | 2022-05-08 | 3595 | keep | 0 | May | 2022 | 0.0024485 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-08 01:04 | 2022-05-08 06:45 | 50 | 005:41 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22050800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 341 | 2022-05-08 | 17050 | keep | 0 | May | 2022 | 0.011613 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-08 01:38 | 2022-05-08 09:00 | 12 | 007:22 | P | NO SE REPORTO CAUSA | 1 X 100 SMU-20 EN SU-5B | R22050800006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 442 | 2022-05-08 | 5304 | keep | 0 | May | 2022 | 0.0036125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-05-08 02:36 | 2022-05-08 02:37 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 824 | keep | 0 | May | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
MAYAGÃœEZ | 2022-05-08 02:49 | 2022-05-08 06:17 | 80 | 003:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-05-08 | 16640 | keep | 0 | May | 2022 | 0.011333 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-05-08 03:47 | 2022-05-08 09:35 | 75 | 005:48 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTE DE LINEA INDICO NO IDENTIFICO CAUSA | A22050800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 348 | 2022-05-08 | 26100 | keep | 0 | May | 2022 | 0.017777 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-05-08 03:51 | 2022-05-08 03:52 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | A22050800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 1494 | keep | 0 | May | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2022-05-08 03:52 | 2022-05-08 09:30 | 250 | 005:38 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA INDICO NO IDENTIFICO CAUSA | A22050800005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 338 | 2022-05-08 | 84500 | keep | 0 | May | 2022 | 0.057553 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2022-05-08 05:44 | 2022-05-08 05:46 | 2888 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR BAJANTE DE MACHETE ZAFADO | A22050800010 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-05-08 | 5776 | keep | 0 | May | 2022 | 0.003934 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
HUMACAO | 2022-05-08 05:46 | 2022-05-08 09:12 | 30 | 003:26 | P | DESGANCHE | 1 X 40 EN C/L SE RETIRO RAMA DE LINEA | C22050800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2022-05-08 | 6180 | keep | 0 | May | 2022 | 0.0042092 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-08 05:46 | 2022-05-08 11:00 | 300 | 005:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO DE LINEA A MACHETE | A22050800021 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 314 | 2022-05-08 | 94200 | keep | 0 | May | 2022 | 0.064159 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-05-08 05:48 | 2022-05-08 05:49 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 1711-05 | B22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 723 | keep | 0 | May | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-05-08 05:48 | 2022-05-08 05:49 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1711-02 | B22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 1976 | keep | 0 | May | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
CAGUAS | 2022-05-08 06:04 | 2022-05-08 06:05 | 718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 718 | keep | 0 | May | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
CAGUAS | 2022-05-08 06:05 | 2022-05-08 07:12 | 318 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22050800004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-05-08 | 21306 | keep | 0 | May | 2022 | 0.014511 | 0.00021659 | Sustained | FALSE | FALSE | Not_TMED_Event | 318
SAN JUAN | 2022-05-08 06:37 | 2022-05-08 09:54 | 19 | 003:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 65 CRUCE POR ANIMAL | R22050800012 | New_Event |  |  | Include | Wildlife | 197 | 2022-05-08 | 3743 | keep | 0 | May | 2022 | 0.0025493 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2022-05-08 06:38 | 2022-05-08 06:39 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 2179 | keep | 0 | May | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
MAYAGÃœEZ | 2022-05-08 06:45 | 2022-05-08 06:46 | 2999 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22050800008 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-08 | 2999 | keep | 0 | May | 2022 | 0.0020426 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-08 06:46 | 2022-05-08 11:47 | 50 | 005:01 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22050800003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 301 | 2022-05-08 | 15050 | keep | 0 | May | 2022 | 0.01025 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-05-08 06:59 | 2022-05-08 07:00 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 5630 | keep | 0 | May | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
SAN JUAN | 2022-05-08 07:05 | 2022-05-08 07:06 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SPARE 1619-02 LLEVANDO 30% DEL 1336-06 | R22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 2000 | keep | 0 | May | 2022 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2022-05-08 07:24 | 2022-05-08 13:37 | 30 | 006:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO ALAMBRE EN EL SUELO TRAMO RADIAL | S22050800006 | New_Event | Wire Down | Include | Include | Equipment | 373 | 2022-05-08 | 11190 | keep | 0 | May | 2022 | 0.0076215 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-08 07:40 | 2022-05-08 10:41 | 68 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22050800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-05-08 | 12308 | keep | 0 | May | 2022 | 0.0083829 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2022-05-08 08:04 | 2022-05-08 10:40 | 200 | 002:36 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA INDICO NO IDENTIFICO CAUSA | A22050800027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2022-05-08 | 31200 | keep | 0 | May | 2022 | 0.02125 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-08 08:08 | 2022-05-08 08:09 | 57 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1912-07 | S22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 57 | keep | 0 | May | 2022 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
CAGUAS | 2022-05-08 08:09 | 2022-05-08 11:46 | 4 | 003:37 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22050800011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2022-05-08 | 868 | keep | 0 | May | 2022 | 0.00059119 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-05-08 08:10 | 2022-05-08 14:13 | 50 | 006:03 | T | NO SE REPORTO CAUSA | 1X40 EN C/L | B22050800061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 363 | 2022-05-08 | 18150 | keep | 0 | May | 2022 | 0.012362 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-08 08:51 | 2022-05-08 08:52 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 6136 | keep | 0 | May | 2022 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
HUMACAO | 2022-05-08 09:01 | 2022-05-08 09:39 | 3896 | 000:38 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE DISPARO ALIMENTADOR A PETICION DE CARLOS MIRANDA POR HOMBRE TREPADO EN POSTE PRIMARIO (INTENTO DE SUICIDIO) ERICK OLMEDA PATRULLO ALIMENTADOR CONFIRMO QUE NO ESTA LA PERSONA EN EL POSTE Y SE PROCEDIO A CERRAR ALIMENTADOR POR SCADA | C22050800015 | New_Event |  |  | Include | Wildlife | 38 | 2022-05-08 | 148048 | keep | 0 | May | 2022 | 0.10083 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
VEGA BAJA | 2022-05-08 09:06 | 2022-05-08 12:56 | 30 | 003:50 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22050800065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2022-05-08 | 6900 | keep | 0 | May | 2022 | 0.0046996 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-08 09:12 | 2022-05-08 09:13 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 Y LLEVA 1711-04 | B22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 1983 | keep | 0 | May | 2022 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-05-08 09:12 | 2022-05-08 09:13 | 500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1801-02 LLEVA PARTE DEL 1717-01 | B22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 500 | keep | 0 | May | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-05-08 09:12 | 2022-05-08 09:13 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 LLEVA PARTE DEL 1717-01 Y LLEVA 1711-04 | B22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 186 | keep | 0 | May | 2022 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2022-05-08 09:13 | 2022-05-08 09:47 | 6 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22050700015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2022-05-08 | 204 | keep | 0 | May | 2022 | 0.00013894 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-08 09:55 | 2022-05-08 11:20 | 8 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22050800053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2022-05-08 | 680 | keep | 0 | May | 2022 | 0.00046314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-05-08 10:10 | 2022-05-08 10:11 | 424 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 424 | keep | 0 | May | 2022 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2022-05-08 10:17 | 2022-05-08 13:47 | 1380 | 003:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO Y SE REPARO AISLADOR | R22050800000 | New_Event | Wire Down | Include | Include | Equipment | 210 | 2022-05-08 | 289800 | keep | 0 | May | 2022 | 0.19738 | 0.00093991 | Sustained | FALSE | FALSE | Not_TMED_Event | 1380
CANOVANAS | 2022-05-08 10:30 | 2022-05-08 10:31 | 424 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22050800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 424 | keep | 0 | May | 2022 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
CAGUAS | 2022-05-08 11:04 | 2022-05-08 11:32 | 7 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIA | C22050800038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-05-08 | 196 | keep | 0 | May | 2022 | 0.00013349 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 1339 | keep | 0 | May | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 470 | keep | 0 | May | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 2483 | keep | 0 | May | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 2190 | keep | 0 | May | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 3006 | keep | 0 | May | 2022 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 179 | keep | 0 | May | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 107 | keep | 0 | May | 2022 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 1666 | keep | 0 | May | 2022 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 4387 | keep | 0 | May | 2022 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 3147 | keep | 0 | May | 2022 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-05-08 11:21 | 2022-05-08 11:22 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-08 | 4304 | keep | 0 | May | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
CAGUAS | 2022-05-08 11:34 | 2022-05-08 11:35 | 3131 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 3131 | keep | 0 | May | 2022 | 0.0021325 | 0.0021325 | Momentary | FALSE | FALSE | Not_TMED_Event | 3131
SAN JUAN | 2022-05-08 12:05 | 2022-05-08 13:05 | 1 | 001:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO PORTA FUSIBLE Y BAJANTE | S22050800022 | New_Event | Cutout Failure | Include | Include | Equipment | 60 | 2022-05-08 | 60 | keep | 0 | May | 2022 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-08 12:44 | 2022-05-08 12:45 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 2203 | keep | 0 | May | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
ARECIBO | 2022-05-08 12:49 | 2022-05-08 18:30 | 5 | 005:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN TRANSFORMADOR POR AVE | A22050800065 | New_Event |  |  | Include | Wildlife | 341 | 2022-05-08 | 1705 | keep | 0 | May | 2022 | 0.0011613 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-05-08 12:52 | 2022-05-08 13:43 | 15 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZO SECUNDARIA NO SE LOGRO REPARAR SECUNDARIA SOTERRADA SE CERRO TRANSFORMADOR PARA TRABAJARLO MAÃ‘ANA | C22050700061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2022-05-08 | 765 | keep | 0 | May | 2022 | 0.00052104 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-08 13:17 | 2022-05-08 13:18 | 4641 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22050800028 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-08 | 4641 | keep | 0 | May | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-05-08 13:18 | 2022-05-08 18:30 | 80 | 005:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 100 EN CORTES DE LINEA SE RETIRO GLOBO DE LAS LINEAS | M22050800034 | 1st_after_momentary |  |  | Include | Wildlife | 312 | 2022-05-08 | 24960 | keep | 0 | May | 2022 | 0.017 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-05-08 13:35 | 2022-05-08 13:37 | 2178 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPCION SE CERRO POR SCADA | C22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-08 | 4356 | keep | 0 | May | 2022 | 0.0029669 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2022-05-08 13:38 | 2022-05-08 14:49 | 253 | 001:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X65 EN C/L & 1X50 EN PROVISIONAL AEREO & SE RETIRO GLOBO DE HULE DEL 13KV | B22050800077 | New_Event |  |  | Include | Wildlife | 71 | 2022-05-08 | 17963 | keep | 0 | May | 2022 | 0.012235 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
CAGUAS | 2022-05-08 13:43 | 2022-05-09 19:56 | 100 | 030:13 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN SU15 SE REPARO AVERIA SOTERRADA DEL T29 AL T30 | C22050800051 | New_Event | UG Cable Fault | Include | Include | Equipment | 1813 | 2022-05-08 | 181300 | keep | 0 | May | 2022 | 0.12348 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-08 13:52 | 2022-05-08 17:35 | 128 | 003:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X80 EN C/L (POR AVE EN LA LINEA) | B22050800079 | New_Event |  |  | Include | Wildlife | 223 | 2022-05-08 | 28544 | keep | 0 | May | 2022 | 0.019441 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
SAN JUAN | 2022-05-08 14:16 | 2022-05-08 14:19 | 1825 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-08 | 5475 | keep | 0 | May | 2022 | 0.003729 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-05-08 14:16 | 2022-05-08 14:19 | 47 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-08 | 141 | keep | 0 | May | 2022 | 9.6034e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-05-08 14:16 | 2022-05-08 14:19 | 315 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-08 | 945 | keep | 0 | May | 2022 | 0.00064364 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-05-08 14:16 | 2022-05-08 14:19 | 2 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-08 | 6 | keep | 0 | May | 2022 | 4.0866e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-05-08 14:16 | 2022-05-08 14:19 | 2391 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-08 | 7173 | keep | 0 | May | 2022 | 0.0048855 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2022-05-08 14:16 | 2022-05-08 14:19 | 2276 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-08 | 6828 | keep | 0 | May | 2022 | 0.0046505 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-05-08 14:16 | 2022-05-08 14:19 | 777 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-08 | 2331 | keep | 0 | May | 2022 | 0.0015876 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-05-08 14:16 | 2022-05-08 14:19 | 12 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-08 | 36 | keep | 0 | May | 2022 | 2.4519e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-08 14:16 | 2022-05-08 14:19 | 1290 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22050800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-08 | 3870 | keep | 0 | May | 2022 | 0.0026358 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2022-05-08 14:28 | 2022-05-08 17:10 | 80 | 002:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22050800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2022-05-08 | 12960 | keep | 0 | May | 2022 | 0.008827 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-08 14:39 | 2022-05-08 14:40 | 33 | 000:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22050800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-08 | 33 | keep | 0 | May | 2022 | 2.2476e-05 | 2.2476e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2022-05-08 14:49 | 2022-05-08 14:51 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22050800083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-08 | 4468 | keep | 0 | May | 2022 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
CANOVANAS | 2022-05-08 14:50 | 2022-05-08 14:51 | 4085 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE INTERRUPTOR 2402-03 LLEVANDO CARGA DEL 2404-06 | R22050800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-08 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-05-08 14:50 | 2022-05-08 14:51 | 7621 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE INTERRUPTOR 2402-03 LLEVANDO CARGA DEL 2404-06 | R22050800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-08 | 7621 | keep | 0 | May | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CAGUAS | 2022-05-08 14:50 | 2022-05-08 14:51 | 540 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 540 | keep | 0 | May | 2022 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CANOVANAS | 2022-05-08 14:51 | 2022-05-08 17:20 | 80 | 002:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REPARO DISCO ZAFADO | R22050800103 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 149 | 2022-05-08 | 11920 | keep | 0 | May | 2022 | 0.0081187 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-05-08 14:58 | 2022-05-08 17:20 | 3 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22050800070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-05-08 | 426 | keep | 0 | May | 2022 | 0.00029015 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-05-08 15:02 | 2022-05-08 16:11 | 7 | 001:09 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22050800057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-05-08 | 483 | keep | 0 | May | 2022 | 0.00032897 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-05-08 15:15 | 2022-05-08 18:22 | 76 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | R22050800102 | New_Event | Bad Weather | Include | Include | Weather | 187 | 2022-05-08 | 14212 | keep | 0 | May | 2022 | 0.0096797 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
MAYAGÃœEZ | 2022-05-08 15:26 | 2022-05-08 17:56 | 5 | 002:30 | P | NO SE REPORTO CAUSA | 2 X 30 EN RISER NO SE REPORTO CAUSA | M22050800037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2022-05-08 | 750 | keep | 0 | May | 2022 | 0.00051082 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-05-08 15:49 | 2022-05-08 15:50 | 1902 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 1902 | keep | 0 | May | 2022 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
CANOVANAS | 2022-05-08 15:49 | 2022-05-08 17:56 | 96 | 002:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22050800080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-05-08 | 12192 | keep | 0 | May | 2022 | 0.0083039 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
SAN JUAN | 2022-05-08 15:57 | 2022-05-08 20:28 | 300 | 004:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO CAJA PRIMARIA, SE CERRO PUENTE PRIMARIO (NO FUNDIO) | S22050800036 | New_Event | Wire Down | Include | Include | Equipment | 271 | 2022-05-08 | 81300 | keep | 0 | May | 2022 | 0.055373 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-05-08 15:59 | 2022-05-08 20:05 | 100 | 004:06 | P | DESGANCHE | 2 X 50 Y 2 X 40 EN CORTES DE LINEA | R22050800106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2022-05-08 | 24600 | keep | 0 | May | 2022 | 0.016755 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-08 17:00 | 2022-05-08 17:01 | 4188 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22050800000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-08 | 4188 | keep | 0 | May | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-05-08 17:10 | 2022-05-08 17:11 | 4188 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22050800000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-08 | 4188 | keep | 0 | May | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-05-08 17:11 | 2022-05-08 22:40 | 110 | 005:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER REEMPLAZO CAJA DE RISER QUEMADA | R22050800125 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 329 | 2022-05-08 | 36190 | keep | 0 | May | 2022 | 0.024649 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2022-05-08 17:56 | 2022-05-08 17:57 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22050800043 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 990 | keep | 0 | May | 2022 | 0.00067428 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-08 17:57 | 2022-05-08 20:30 | 5 | 002:33 | P | NO SE REPORTO CAUSA | 2 X 30 EN RISER NO SE REPORTO CAUSA | M22050800037 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 153 | 2022-05-08 | 765 | keep | 0 | May | 2022 | 0.00052104 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-05-08 18:14 | 2022-05-09 10:35 | 90 | 016:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22050800073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 981 | 2022-05-08 | 88290 | keep | 0 | May | 2022 | 0.060134 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2022-05-08 18:16 | 2022-05-09 09:17 | 70 | 015:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22050800074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 901 | 2022-05-08 | 63070 | keep | 0 | May | 2022 | 0.042957 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-05-08 18:18 | 2022-05-08 18:19 | 64 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22050800044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 64 | keep | 0 | May | 2022 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
BAYAMON | 2022-05-08 18:41 | 2022-05-08 18:42 | 1370 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S22050800058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-08 | 1370 | keep | 0 | May | 2022 | 0.0009331 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2022-05-08 18:42 | 2022-05-08 19:36 | 60 | 000:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22050800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2022-05-08 | 3240 | keep | 0 | May | 2022 | 0.0022067 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-08 18:59 | 2022-05-08 19:53 | 3433 | 000:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1204-02 EL 80% DE SU CARGA ATRAVEZ DE LA PORTATIL 22. SE SECCIONALIZO LINEA PRIMARIA EN EL SUELO Y SE CERRO INTEARRUPTOR | S22050800000 | New_Event | Wire Down | Include | Include | Equipment | 54 | 2022-05-08 | 185382 | keep | 0 | May | 2022 | 0.12626 | 0.0023382 | Sustained | FALSE | FALSE | Not_TMED_Event | 3433
BAYAMON | 2022-05-08 19:01 | 2022-05-08 21:15 | 100 | 002:14 | P | NO SE REPORTO CAUSA | 2X65 EN C/L | B22050800095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2022-05-08 | 13400 | keep | 0 | May | 2022 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-08 19:23 | 2022-05-08 21:52 | 75 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22050800075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-05-08 | 11175 | keep | 0 | May | 2022 | 0.0076112 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-05-08 19:26 | 2022-05-08 20:14 | 99 | 000:48 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22050800104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2022-05-08 | 4752 | keep | 0 | May | 2022 | 0.0032366 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
SAN JUAN | 2022-05-08 19:53 | 2022-05-08 21:07 | 2403 | 001:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA Y SE CERRO MACHETE POR TRAMO ENTRA UN 30% | S22050800000 | Partial_restoration | Wire Down | Include | Include | Equipment | 74 | 2022-05-08 | 177822 | keep | 0 | May | 2022 | 0.12111 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-08 20:48 | 2022-05-08 23:40 | 15 | 002:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | A22050800079 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2022-05-08 | 2580 | keep | 0 | May | 2022 | 0.0017572 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-08 21:07 | 2022-05-08 21:17 | 1545 | 000:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA Y SE CERRO MACHETE POR TRAMO ENTRA UN 100% | S22050800000 | Partial_restoration | Wire Down | Include | Include | Equipment | 10 | 2022-05-08 | 15450 | keep | 0 | May | 2022 | 0.010523 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-08 21:13 | 2022-05-08 22:35 | 130 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22050800107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-05-08 | 10660 | keep | 0 | May | 2022 | 0.0072605 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
PONCE | 2022-05-08 21:14 | 2022-05-09 06:54 | 65 | 009:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22050800121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 580 | 2022-05-08 | 37700 | keep | 0 | May | 2022 | 0.025677 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2022-05-08 21:18 | 2022-05-08 23:46 | 200 | 002:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L & SE REMPLAZO CAJA PRIMARIA | B22050800130 | New_Event | Cutout Failure | Include | Include | Equipment | 148 | 2022-05-08 | 29600 | keep | 0 | May | 2022 | 0.02016 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-05-08 23:18 | 2022-05-09 02:53 | 200 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO ENCONTRO CAUSA | A22050800082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2022-05-08 | 43000 | keep | 0 | May | 2022 | 0.029287 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-05-08 23:26 | 2022-05-09 00:42 | 100 | 001:16 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22050800084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2022-05-08 | 7600 | keep | 0 | May | 2022 | 0.0051763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-05-09 00:10 | 2022-05-09 04:18 | 275 | 004:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L & SE REMPLAZO EL PORTAFUSIBLE | B22050900001 | New_Event | Cutout Failure | Include | Include | Equipment | 248 | 2022-05-09 | 68200 | keep | 0 | May | 2022 | 0.046451 | 0.0001873 | Sustained | FALSE | FALSE | Not_TMED_Event | 275
VEGA BAJA | 2022-05-09 00:10 | 2022-05-09 04:18 | 275 | 004:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L & SE REMPLAZO EL PORTAFUSIBLE | B22050900001 | New_Event | Cutout Failure | Include | Include | Equipment | 248 | 2022-05-09 | 68200 | keep | 0 | May | 2022 | 0.046451 | 0.0001873 | Sustained | FALSE | FALSE | Not_TMED_Event | 275
SAN JUAN | 2022-05-09 00:27 | 2022-05-09 00:28 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22050900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 2203 | keep | 0 | May | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2022-05-09 00:37 | 2022-05-09 06:03 | 99 | 005:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22050900002 | New_Event | Cutout Failure | Include | Include | Equipment | 326 | 2022-05-09 | 32274 | keep | 0 | May | 2022 | 0.021982 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
ARECIBO | 2022-05-09 00:59 | 2022-05-09 09:40 | 18 | 008:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN RISER LINEAS CRUZADAS | A22050900002 | New_Event | Wire Down | Include | Include | Equipment | 521 | 2022-05-09 | 9378 | keep | 0 | May | 2022 | 0.0063873 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-05-09 03:07 | 2022-05-09 08:05 | 60 | 004:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C22050900001 | New_Event |  |  | Include | Wildlife | 298 | 2022-05-09 | 17880 | keep | 0 | May | 2022 | 0.012178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-09 03:17 | 2022-05-09 03:18 | 1923 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | A22050900004 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-09 | 1923 | keep | 0 | May | 2022 | 0.0013097 | 0.0013097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1923
ARECIBO | 2022-05-09 03:18 | 2022-05-09 04:50 | 200 | 001:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A22050900007 | 1st_after_momentary |  |  | Include | Wildlife | 92 | 2022-05-09 | 18400 | keep | 0 | May | 2022 | 0.012532 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-05-09 04:00 | 2022-05-09 10:16 | 122 | 006:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZARON CAJAS QUEMADAS | R22050900002 | New_Event | Cutout Failure | Include | Include | Equipment | 376 | 2022-05-09 | 45872 | keep | 0 | May | 2022 | 0.031243 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
CAGUAS | 2022-05-09 04:20 | 2022-05-09 04:21 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CANOVANAS | 2022-05-09 04:22 | 2022-05-09 04:23 | 500 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22050900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 500 | keep | 0 | May | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2022-05-09 04:22 | 2022-05-09 04:23 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050900003 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-05-09 04:28 | 2022-05-09 04:29 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22050900004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
ARECIBO | 2022-05-09 05:07 | 2022-05-09 08:50 | 25 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050900011 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2022-05-09 | 5575 | keep | 0 | May | 2022 | 0.0037971 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-09 05:30 | 2022-05-09 05:31 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 1617 | keep | 0 | May | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-05-09 05:30 | 2022-05-09 05:31 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 1017 | keep | 0 | May | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-09 05:30 | 2022-05-09 05:31 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 828 | keep | 0 | May | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
ARECIBO | 2022-05-09 05:44 | 2022-05-09 05:45 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22050900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 2697 | keep | 0 | May | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2022-05-09 05:45 | 2022-05-09 07:53 | 150 | 002:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22050900020 | New_Event | Bad Weather | Include | Include | Weather | 128 | 2022-05-09 | 19200 | keep | 0 | May | 2022 | 0.013077 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-09 06:04 | 2022-05-09 07:41 | 8 | 001:37 | P | SECUNDARIA/DESGANCHE | 1 X 15 XMR DESGANCHE | B22050900007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 97 | 2022-05-09 | 776 | keep | 0 | May | 2022 | 0.00052853 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-05-09 06:36 | 2022-05-09 09:11 | 60 | 002:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L AVE | B22050900014 | New_Event |  |  | Include | Wildlife | 155 | 2022-05-09 | 9300 | keep | 0 | May | 2022 | 0.0063342 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-09 06:42 | 2022-05-09 11:02 | 7 | 004:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22050900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2022-05-09 | 1820 | keep | 0 | May | 2022 | 0.0012396 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-05-09 06:53 | 2022-05-09 12:00 | 50 | 005:07 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22050900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2022-05-09 | 15350 | keep | 0 | May | 2022 | 0.010455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-09 06:55 | 2022-05-09 10:23 | 25 | 003:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22050900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-05-09 | 5200 | keep | 0 | May | 2022 | 0.0035417 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-09 07:19 | 2022-05-09 07:20 | 5809 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1710-02 SPARE QUE LLEVA 1710-01 Y SE CERRO POR SCADA | B22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 5809 | keep | 0 | May | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-05-09 07:20 | 2022-05-09 10:50 | 50 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22050900021 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 210 | 2022-05-09 | 10500 | keep | 0 | May | 2022 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-09 07:27 | 2022-05-09 07:31 | 1105 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS NO SE ENCONTRO CAUSA | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 4420 | keep | 0 | May | 2022 | 0.0030104 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 1405 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 5620 | keep | 0 | May | 2022 | 0.0038278 | 0.00095694 | Momentary | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 669 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 2676 | keep | 0 | May | 2022 | 0.0018226 | 0.00045565 | Momentary | FALSE | FALSE | Not_TMED_Event | 669
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 1527 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 6108 | keep | 0 | May | 2022 | 0.0041601 | 0.00104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 1054 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 4216 | keep | 0 | May | 2022 | 0.0028715 | 0.00071787 | Momentary | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 932 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 3728 | keep | 0 | May | 2022 | 0.0025391 | 0.00063478 | Momentary | FALSE | FALSE | Not_TMED_Event | 932
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 1633 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 6532 | keep | 0 | May | 2022 | 0.0044489 | 0.0011122 | Momentary | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 1624 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 6496 | keep | 0 | May | 2022 | 0.0044244 | 0.0011061 | Momentary | FALSE | FALSE | Not_TMED_Event | 1624
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 705 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 2820 | keep | 0 | May | 2022 | 0.0019207 | 0.00048017 | Momentary | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 1521 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 6084 | keep | 0 | May | 2022 | 0.0041438 | 0.0010359 | Momentary | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2022-05-09 07:27 | 2022-05-09 07:31 | 882 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV DOS BOCAS | A22050900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-05-09 | 3528 | keep | 0 | May | 2022 | 0.0024029 | 0.00060073 | Momentary | FALSE | FALSE | Not_TMED_Event | 882
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 873 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 90792 | keep | 0 | May | 2022 | 0.061838 | 0.0005946 | Sustained | FALSE | FALSE | Not_TMED_Event | 873
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 1261 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 131144 | keep | 0 | May | 2022 | 0.089322 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 2713 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 282152 | keep | 0 | May | 2022 | 0.19217 | 0.0018478 | Sustained | FALSE | FALSE | Not_TMED_Event | 2713
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 51 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 LLEVA CARGA DE 6001-05 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 5304 | keep | 0 | May | 2022 | 0.0036125 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 285 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 CARGA POR 6001-04 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 29640 | keep | 0 | May | 2022 | 0.020188 | 0.00019411 | Sustained | FALSE | FALSE | Not_TMED_Event | 285
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 1253 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 LLEVA CARGA DE 6010-02 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 130312 | keep | 0 | May | 2022 | 0.088755 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 1266 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 CARGA POR 6010-01 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 131664 | keep | 0 | May | 2022 | 0.089676 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 411 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 42744 | keep | 0 | May | 2022 | 0.029113 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 1444 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 CARGA POR 6014-02 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 150176 | keep | 0 | May | 2022 | 0.10228 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 3630 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 LLEVA CARGA DE 6014-01 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 377520 | keep | 0 | May | 2022 | 0.25713 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 871 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 CARGA POR 6012-05 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 90584 | keep | 0 | May | 2022 | 0.061696 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 863 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 89752 | keep | 0 | May | 2022 | 0.06113 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 309 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 32136 | keep | 0 | May | 2022 | 0.021888 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 176 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 18304 | keep | 0 | May | 2022 | 0.012467 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 108 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 11232 | keep | 0 | May | 2022 | 0.0076501 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2022-05-09 07:30 | 2022-05-09 09:14 | 974 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22050900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-05-09 | 101296 | keep | 0 | May | 2022 | 0.068992 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
CAGUAS | 2022-05-09 07:41 | 2022-05-09 10:51 | 30 | 003:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C22050900014 | New_Event |  |  | Include | Wildlife | 190 | 2022-05-09 | 5700 | keep | 0 | May | 2022 | 0.0038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-05-09 08:00 | 2022-05-09 19:23 | 8 | 011:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22050900200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 683 | 2022-05-09 | 5464 | keep | 0 | May | 2022 | 0.0037215 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-09 08:10 | 2022-05-09 13:38 | 65 | 005:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050900120 | New_Event | Bad Weather | Include | Include | Weather | 328 | 2022-05-09 | 21320 | keep | 0 | May | 2022 | 0.014521 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-05-09 08:15 | 2022-05-09 08:16 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050900068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 1565 | keep | 0 | May | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-05-09 08:15 | 2022-05-09 08:16 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050900068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 976 | keep | 0 | May | 2022 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-05-09 08:15 | 2022-05-09 08:16 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050900068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 548 | keep | 0 | May | 2022 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-05-09 08:15 | 2022-05-09 08:16 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050900069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 315 | keep | 0 | May | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-05-09 08:15 | 2022-05-09 08:16 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050900069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-05-09 08:15 | 2022-05-09 08:16 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050900070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 2906 | keep | 0 | May | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-05-09 08:15 | 2022-05-09 08:16 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22050900070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-09 | 2343 | keep | 0 | May | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
BAYAMON | 2022-05-09 08:18 | 2022-05-09 08:19 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 73 | keep | 0 | May | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
FAJARDO | 2022-05-09 08:32 | 2022-05-09 12:24 | 74 | 003:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22050900029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2022-05-09 | 17168 | keep | 0 | May | 2022 | 0.011693 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
PONCE | 2022-05-09 08:47 | 2022-05-09 09:30 | 1746 | 000:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE ABRE RISER DE SALIDA PARA SECCIONALIZAR AVERIA | P22050900020 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2022-05-09 | 75078 | keep | 0 | May | 2022 | 0.051135 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
CANOVANAS | 2022-05-09 08:49 | 2022-05-09 11:01 | 1 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | R22050900031 | New_Event |  |  | Include | Wildlife | 132 | 2022-05-09 | 132 | keep | 0 | May | 2022 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-09 08:50 | 2022-05-09 11:14 | 16 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONECTORES SULFATADOS EN TRONCAL DE SECUNDARIA | C22050900034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2022-05-09 | 2304 | keep | 0 | May | 2022 | 0.0015692 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-05-09 09:00 | 2022-05-10 15:00 | 1 | 030:00 | P | NO SE REPORTO CAUSA | 1 X 20 EN BANCO DE TRANSFORMADOR | S22050900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1800 | 2022-05-09 | 1800 | keep | 0 | May | 2022 | 0.001226 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-05-09 09:03 | 2022-05-09 14:03 | 100 | 005:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22050900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-05-09 | 30000 | keep | 0 | May | 2022 | 0.020433 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-05-09 09:14 | 2022-05-09 12:45 | 10 | 003:31 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR CRUCE DE FASES POR RAMA | P22050900034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 211 | 2022-05-09 | 2110 | keep | 0 | May | 2022 | 0.0014371 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-09 09:17 | 2022-05-09 09:22 | 2000 | 000:05 | P | NO SE REPORTO CAUSA | DISPARO DEL 1619-02 LLEVANDO 30% DEL 1336-06 SE CERRO POR CONTROL | R22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-05-09 | 10000 | keep | 0 | May | 2022 | 0.006811 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
BARRANQUITAS | 2022-05-09 09:24 | 2022-05-09 13:24 | 14 | 004:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONECTORES SULFATADOS | C22050900043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 240 | 2022-05-09 | 3360 | keep | 0 | May | 2022 | 0.0022885 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2022-05-09 09:30 | 2022-05-09 12:44 | 428 | 003:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO RISER DE SALIDA DE SOTERRADO | P22050900047 | Partial_restoration | Wire Down | Include | Include | Equipment | 194 | 2022-05-09 | 83032 | keep | 0 | May | 2022 | 0.056553 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-09 09:43 | 2022-05-09 15:42 | 30 | 005:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22050900054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2022-05-09 | 10770 | keep | 0 | May | 2022 | 0.0073354 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-09 09:49 | 2022-05-09 14:12 | 1420 | 004:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA DEL 1530-07 Y SE CERRO MACHETES DE AMARRE CONTRA 1526-02 Y 1530-06 | S22050900064 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2022-05-09 | 373460 | keep | 0 | May | 2022 | 0.25436 | 0.00096716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-05-09 09:49 | 2022-05-09 14:12 | 437 | 004:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA DEL 1530-07 Y SE CERRO MACHETES DE AMARRE CONTRA 1526-02 Y 1530-06 | S22050900064 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2022-05-09 | 114931 | keep | 0 | May | 2022 | 0.078279 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-05-09 09:49 | 2022-05-09 09:53 | 643 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO ALIMENTADOR A PETICION DE FRANKI RAMOS POR CONDUCTOR VIVO EN EL SUELO | S22050900064 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2022-05-09 | 2572 | keep | 0 | May | 2022 | 0.0017518 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
BAYAMON | 2022-05-09 09:53 | 2022-05-09 14:12 | 450 | 004:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA DEL 1530-07 Y SE COMPLETARON TRABAJOS DE TRANSFERENCIAS | S22050900064 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 259 | 2022-05-09 | 116550 | keep | 0 | May | 2022 | 0.079382 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
BAYAMON | 2022-05-09 09:58 | 2022-05-09 11:58 | 6 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S22050900063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-05-09 | 720 | keep | 0 | May | 2022 | 0.00049039 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-05-09 09:59 | 2022-05-09 16:45 | 100 | 006:46 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO SU-2A PARA REMPLAZO DE MACHETE MEDIANTE SWITCH FORM SJ-220509-50 | R22050900000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 406 | 2022-05-09 | 40600 | keep | 0 | May | 2022 | 0.027652 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-05-09 10:06 | 2022-05-09 11:03 | 6 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON BAJANTES QUEMADOS | C22050900034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-05-09 | 342 | keep | 0 | May | 2022 | 0.00023293 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-05-09 10:07 | 2022-05-09 11:59 | 350 | 001:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REEMPLAZARON CAJAS QUEMADAS | R22050900004 | New_Event | Cutout Failure | Include | Include | Equipment | 112 | 2022-05-09 | 39200 | keep | 0 | May | 2022 | 0.026699 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
MAYAGÃœEZ | 2022-05-09 10:14 | 2022-05-09 16:53 | 50 | 006:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M22050900261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 399 | 2022-05-09 | 19950 | keep | 0 | May | 2022 | 0.013588 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-05-09 10:20 | 2022-05-09 19:24 | 16 | 009:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C22050900057 | New_Event |  |  | Include | Wildlife | 544 | 2022-05-09 | 8704 | keep | 0 | May | 2022 | 0.0059283 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-05-09 10:20 | 2022-05-09 14:45 | 1 | 004:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22050900263 | New_Event | Cutout Failure | Include | Include | Equipment | 265 | 2022-05-09 | 265 | keep | 0 | May | 2022 | 0.00018049 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-09 10:21 | 2022-05-09 12:43 | 100 | 002:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN RISER Y 1 X 40 EN SU-3 CRUCE DE FASE PRIMARIA POR IGUANA | P22050900060 | New_Event |  |  | Include | Wildlife | 142 | 2022-05-09 | 14200 | keep | 0 | May | 2022 | 0.0096716 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-09 10:28 | 2022-05-09 16:10 | 8 | 005:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A22050900053 | New_Event | Wire Down | Include | Include | Equipment | 342 | 2022-05-09 | 2736 | keep | 0 | May | 2022 | 0.0018635 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-05-09 10:32 | 2022-05-10 09:29 | 9 | 022:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN XMR CRUCE X AVE | C22050900060 | New_Event |  |  | Include | Wildlife | 1377 | 2022-05-09 | 12393 | keep | 0 | May | 2022 | 0.0084408 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-05-09 10:36 | 2022-05-09 14:02 | 516 | 003:26 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE AVERIADO | S22050900083 | New_Event | Defective Pole | Include | Include | Equipment | 206 | 2022-05-09 | 106296 | keep | 0 | May | 2022 | 0.072398 | 0.00035145 | Sustained | FALSE | FALSE | Not_TMED_Event | 516
PONCE | 2022-05-09 10:38 | 2022-05-09 16:06 | 1 | 005:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22050900065 | New_Event |  |  | Include | Wildlife | 328 | 2022-05-09 | 328 | keep | 0 | May | 2022 | 0.0002234 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-09 10:40 | 2022-05-09 16:00 | 7 | 005:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA ZAFADA | M22050900267 | New_Event | Secondary Wire Down | Include | Include | Equipment | 320 | 2022-05-09 | 2240 | keep | 0 | May | 2022 | 0.0015257 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-09 10:42 | 2022-05-09 14:26 | 6 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR BAJANTE SECUNDARIO | B22050900045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2022-05-09 | 1344 | keep | 0 | May | 2022 | 0.00091539 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-05-09 10:49 | 2022-05-09 12:55 | 19 | 002:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO BAJANTE CRUZADO Y SE ENDEREZO POSTE VIRADO | R22050900074 | New_Event | Wire Down | Include | Include | Equipment | 126 | 2022-05-09 | 2394 | keep | 0 | May | 2022 | 0.0016305 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2022-05-09 10:49 | 2022-05-09 14:00 | 100 | 003:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22050900074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-05-09 | 19100 | keep | 0 | May | 2022 | 0.013009 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-05-09 11:00 | 2022-05-09 18:01 | 34 | 007:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA ABIERTA Y SAFADO DEL TRANSFORMADOR | C22050900024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 421 | 2022-05-09 | 14314 | keep | 0 | May | 2022 | 0.0097492 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
UTUADO | 2022-05-09 11:06 | 2022-05-09 13:45 | 1 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22050900058 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2022-05-09 | 159 | keep | 0 | May | 2022 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-09 11:16 | 2022-05-09 13:41 | 40 | 002:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C22050900066 | New_Event |  |  | Include | Wildlife | 145 | 2022-05-09 | 5800 | keep | 0 | May | 2022 | 0.0039504 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-05-09 11:20 | 2022-05-09 14:20 | 30 | 003:00 | P | NO SE REPORTO CAUSA | 1 X 30 EN PROVISIONAL AEREO | R22050900087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2022-05-09 | 5400 | keep | 0 | May | 2022 | 0.0036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-09 11:22 | 2022-05-09 17:00 | 1 | 005:38 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER | R22050900089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 338 | 2022-05-09 | 338 | keep | 0 | May | 2022 | 0.00023021 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-09 11:24 | 2022-05-09 13:35 | 20 | 002:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22050900061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-05-09 | 2620 | keep | 0 | May | 2022 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-05-09 11:38 | 2022-05-09 11:39 | 1833 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERREPTOR | P22050900076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1833 | keep | 0 | May | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
SAN JUAN | 2022-05-09 11:43 | 2022-05-09 13:00 | 457 | 001:17 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE DESGANCHO BAMBUA CON BARETA Y SE CERRO POR CONTROL LLEVA PARTE DEL 1206-01 | S22050900114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-05-09 | 35189 | keep | 0 | May | 2022 | 0.023967 | 0.00031126 | Sustained | FALSE | FALSE | Not_TMED_Event | 457
SAN JUAN | 2022-05-09 11:43 | 2022-05-09 13:00 | 304 | 001:17 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE DESGANCHO BAMBUA CON BARRETA Y SE CERRO POR CONTROL PARTE DE LA CARGA POR EL 1201-02 | S22050900114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-05-09 | 23408 | keep | 0 | May | 2022 | 0.015943 | 0.00020705 | Sustained | FALSE | FALSE | Not_TMED_Event | 304
BAYAMON | 2022-05-09 12:10 | 2022-05-09 15:00 | 1 | 002:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA Y SE REEMPLAZARON DOS CAJAS Y PUENTES | S22050900127 | New_Event | Cutout Failure | Include | Include | Equipment | 170 | 2022-05-09 | 170 | keep | 0 | May | 2022 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-09 12:24 | 2022-05-09 23:12 | 80 | 010:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | R22050900093 | New_Event | Wire Down | Include | Include | Equipment | 648 | 2022-05-09 | 51840 | keep | 0 | May | 2022 | 0.035308 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-05-09 12:24 | 2022-05-09 14:49 | 30 | 002:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEAS CRUZADAS | R22050900000 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2022-05-09 | 4350 | keep | 0 | May | 2022 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-05-09 12:30 | 2022-05-09 14:10 | 50 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 100 Y 2 X 80 EN C/L | R22050900094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-05-09 | 5000 | keep | 0 | May | 2022 | 0.0034055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-09 12:30 | 2022-05-09 14:56 | 90 | 002:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C22050900094 | New_Event |  |  | Include | Wildlife | 146 | 2022-05-09 | 13140 | keep | 0 | May | 2022 | 0.0089496 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-05-09 12:39 | 2022-05-09 12:40 | 296 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 1416-05 | S22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 296 | keep | 0 | May | 2022 | 0.0002016 | 0.0002016 | Momentary | FALSE | FALSE | Not_TMED_Event | 296
SAN JUAN | 2022-05-09 12:39 | 2022-05-09 12:40 | 79 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 1416-05 | S22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 79 | keep | 0 | May | 2022 | 5.3807e-05 | 5.3807e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2022-05-09 12:39 | 2022-05-09 12:40 | 1573 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1416-03 Y 1416-02 | S22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1573 | keep | 0 | May | 2022 | 0.0010714 | 0.0010714 | Momentary | FALSE | FALSE | Not_TMED_Event | 1573
MAYAGÃœEZ | 2022-05-09 12:41 | 2022-05-09 16:48 | 16 | 004:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050900285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2022-05-09 | 3952 | keep | 0 | May | 2022 | 0.0026917 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-05-09 12:49 | 2022-05-09 12:53 | 2402 | 000:04 | T | SECUNDARIA/DESGANCHE | DISPARO BKR 1709-02 QUE LLEVA 1720-08 Y SE CERRO POR SCADA | S22050900055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 4 | 2022-05-09 | 9608 | keep | 0 | May | 2022 | 0.006544 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-05-09 12:49 | 2022-05-09 12:53 | 1 | 000:04 | T | SECUNDARIA/DESGANCHE | DISPARO BKR 1709-02 QUE LLEVA 1720-08 Y SE CERRO POR SCADA | B22050900055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 4 | 2022-05-09 | 4 | keep | 0 | May | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-09 12:53 | 2022-05-09 16:16 | 21 | 003:23 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN XMR | S22050900183 | 1st_after_momentary | Secondary Vegetation | Include | Include | Vegetation | 203 | 2022-05-09 | 4263 | keep | 0 | May | 2022 | 0.0029035 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
PONCE | 2022-05-09 12:57 | 2022-05-09 17:17 | 60 | 004:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA EVENTO ENTRO CON CODIGO DE CAGUAS | C22050900100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2022-05-09 | 15600 | keep | 0 | May | 2022 | 0.010625 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-09 12:59 | 2022-05-09 16:02 | 552 | 003:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1204-03 40% DE SU CARGA TRANSFERIDA. SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA | S22050900165 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 183 | 2022-05-09 | 101016 | keep | 0 | May | 2022 | 0.068802 | 0.00037596 | Sustained | FALSE | FALSE | Not_TMED_Event | 552
BAYAMON | 2022-05-09 13:00 | 2022-05-09 16:09 | 4 | 003:09 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 10KVA X 15KVA Y 2 CAJAS PRIMARIAS | B22050700091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 189 | 2022-05-09 | 756 | keep | 0 | May | 2022 | 0.00051491 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-09 13:02 | 2022-05-09 13:26 | 457 | 000:24 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE SECCIONALIZO PARA PROBAR TRAMO. SE DEJO FUERA LA CARGA PARCIAL DEL 1206-01 | S22050900114 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 24 | 2022-05-09 | 10968 | keep | 0 | May | 2022 | 0.0074703 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-09 13:02 | 2022-05-09 14:35 | 304 | 001:33 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | S22050900114 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-05-09 | 28272 | keep | 0 | May | 2022 | 0.019256 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-09 13:05 | 2022-05-09 15:26 | 50 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22050900290 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2022-05-09 | 7050 | keep | 0 | May | 2022 | 0.0048017 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-09 13:15 | 2022-05-09 18:52 | 14 | 005:37 | P | NO SE REPORTO CAUSA | 1 X 25 Y 1X 15 EN XMR | B22050900057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2022-05-09 | 4718 | keep | 0 | May | 2022 | 0.0032134 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-05-09 13:26 | 2022-05-09 13:27 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22050900294 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-09 13:26 | 2022-05-09 13:27 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M22050900294 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
VEGA BAJA | 2022-05-09 13:28 | 2022-05-09 16:46 | 1 | 003:18 | P | NO SE REPORTO CAUSA | 3 X 10 EN MONTURA DE XMR | B22050900062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2022-05-09 | 198 | keep | 0 | May | 2022 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-09 13:34 | 2022-05-09 15:00 | 1 | 001:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | R22050900106 | New_Event | Wire Down | Include | Include | Equipment | 86 | 2022-05-09 | 86 | keep | 0 | May | 2022 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-09 13:40 | 2022-05-10 12:52 | 15 | 023:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTES SECUNDARIOS | B22050900064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1392 | 2022-05-09 | 20880 | keep | 0 | May | 2022 | 0.014221 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-05-09 13:43 | 2022-05-09 14:50 | 15 | 001:07 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR SE REALIZO DESGANCHE | R22050900108 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 67 | 2022-05-09 | 1005 | keep | 0 | May | 2022 | 0.0006845 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-09 13:47 | 2022-05-09 18:18 | 40 | 004:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22050900065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2022-05-09 | 10840 | keep | 0 | May | 2022 | 0.0073831 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-05-09 13:51 | 2022-05-09 15:33 | 27 | 001:42 | S | LINEA DE TRANSMISION 38KV | ABRIR LINEA BKR DE ALTA 0040 PARA CDS LLENAR DE SF6 INTERRUPTOR | B22050900060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2022-05-09 | 2754 | keep | 0 | May | 2022 | 0.0018757 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2022-05-09 13:51 | 2022-05-09 15:33 | 603 | 001:42 | S | LINEA DE TRANSMISION 38KV | ABRIR LINEA BKR DE ALTA 0040 PARA CDS LLENAR DE SF6 INTERRUPTOR | B22050900060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2022-05-09 | 61506 | keep | 0 | May | 2022 | 0.041891 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-05-09 13:51 | 2022-05-09 15:33 | 325 | 001:42 | S | LINEA DE TRANSMISION 38KV | ABRIR LINEA BKR DE ALTA 0040 PARA CDS LLENAR DE SF6 INTERRUPTOR | B22050900060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2022-05-09 | 33150 | keep | 0 | May | 2022 | 0.022578 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2022-05-09 13:51 | 2022-05-09 15:33 | 172 | 001:42 | S | LINEA DE TRANSMISION 38KV | ABRIR LINEA BKR DE ALTA 0040 PARA CDS LLENAR DE SF6 INTERRUPTOR | B22050900060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2022-05-09 | 17544 | keep | 0 | May | 2022 | 0.011949 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
VEGA BAJA | 2022-05-09 13:57 | 2022-05-09 17:21 | 300 | 003:24 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO | B22050900030 | New_Event | Defective Pole | Include | Include | Equipment | 204 | 2022-05-09 | 61200 | keep | 0 | May | 2022 | 0.041683 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2022-05-09 13:57 | 2022-05-10 08:32 | 40 | 018:35 | P | DESGANCHE | 1 X 50 EN C/L | C22050900116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1115 | 2022-05-09 | 44600 | keep | 0 | May | 2022 | 0.030377 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-05-09 13:58 | 2022-05-09 15:37 | 10 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22050900068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-05-09 | 990 | keep | 0 | May | 2022 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-09 14:00 | 2022-05-09 14:01 | 3838 | 000:01 | T | DESGANCHE | RECERRO | R22050900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-09 | 3838 | keep | 0 | May | 2022 | 0.002614 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
MAYAGÃœEZ | 2022-05-09 14:00 | 2022-05-09 19:00 | 35 | 005:00 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050900296 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-05-09 | 10500 | keep | 0 | May | 2022 | 0.0071515 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-05-09 14:01 | 2022-05-09 18:15 | 30 | 004:14 | P | DESGANCHE | 1 X 30 C/L Y 1 X 10 EN XMR | R22050900121 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-05-09 | 7620 | keep | 0 | May | 2022 | 0.0051899 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-09 14:07 | 2022-05-09 14:09 | 2000 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL FEEDER 1619-02 LLEVA 2000 CLIENTES DEL 1336-06 | R22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-09 | 4000 | keep | 0 | May | 2022 | 0.0027244 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
AGUADILLA | 2022-05-09 14:12 | 2022-05-09 16:02 | 20 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | M22050900300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2022-05-09 | 2200 | keep | 0 | May | 2022 | 0.0014984 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-05-09 14:16 | 2022-05-09 18:30 | 5 | 004:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22050900095 | New_Event |  |  | Include | Wildlife | 254 | 2022-05-09 | 1270 | keep | 0 | May | 2022 | 0.00086499 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-09 14:20 | 2022-05-09 20:44 | 50 | 006:24 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050900303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 384 | 2022-05-09 | 19200 | keep | 0 | May | 2022 | 0.013077 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-09 14:22 | 2022-05-09 14:23 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22050900097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2022-05-09 14:22 | 2022-05-09 14:23 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22050900305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1192 | keep | 0 | May | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BAYAMON | 2022-05-09 14:29 | 2022-05-09 18:15 | 50 | 003:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22050900212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2022-05-09 | 11300 | keep | 0 | May | 2022 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-09 14:31 | 2022-05-09 22:28 | 200 | 007:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR VIENTO FUERTE | M22050900307 | New_Event | Bad Weather | Include | Include | Weather | 477 | 2022-05-09 | 95400 | keep | 0 | May | 2022 | 0.064977 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-05-09 14:42 | 2022-05-09 17:36 | 3 | 002:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON BAJANTES DE ALUMINIO SULFATADOS POR COBRE | C22050900125 | New_Event | Secondary Wire Down | Include | Include | Equipment | 174 | 2022-05-09 | 522 | keep | 0 | May | 2022 | 0.00035553 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-05-09 14:45 | 2022-05-09 16:00 | 35 | 001:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y DESGANCHE | S22050900220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-05-09 | 2625 | keep | 0 | May | 2022 | 0.0017879 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-05-09 14:45 | 2022-05-09 19:20 | 75 | 004:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22050900082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2022-05-09 | 20625 | keep | 0 | May | 2022 | 0.014048 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-05-09 14:48 | 2022-05-09 19:11 | 4 | 004:23 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE SECUNDARIO | S22050900221 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 263 | 2022-05-09 | 1052 | keep | 0 | May | 2022 | 0.00071651 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-09 14:49 | 2022-05-09 14:50 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 2234 | keep | 0 | May | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-05-09 14:52 | 2022-05-09 22:24 | 12 | 007:32 | P | DESGANCHE | 2X15 EN TRANSFORMADOR | B22050900089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 452 | 2022-05-09 | 5424 | keep | 0 | May | 2022 | 0.0036943 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-05-09 14:52 | 2022-05-09 17:24 | 1 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X100 EN C/L | B22050900088 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2022-05-09 | 152 | keep | 0 | May | 2022 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-09 14:59 | 2022-05-09 16:42 | 2106 | 001:43 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR ENTRO 10% | R22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-05-09 | 216918 | keep | 0 | May | 2022 | 0.14774 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
CAGUAS | 2022-05-09 15:00 | 2022-05-09 16:59 | 90 | 001:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE X AVE | C22050900129 | New_Event |  |  | Include | Wildlife | 119 | 2022-05-09 | 10710 | keep | 0 | May | 2022 | 0.0072945 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2022-05-09 15:04 | 2022-05-09 17:00 | 50 | 001:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A22050900085 | New_Event |  |  | Include | Wildlife | 116 | 2022-05-09 | 5800 | keep | 0 | May | 2022 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-09 15:08 | 2022-05-09 16:57 | 200 | 001:49 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22050900133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-05-09 | 21800 | keep | 0 | May | 2022 | 0.014848 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-09 15:09 | 2022-05-09 16:41 | 225 | 001:32 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO INTERRUPTOR LOCAL | S22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2022-05-09 | 20700 | keep | 0 | May | 2022 | 0.014099 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-09 15:09 | 2022-05-09 16:41 | 870 | 001:32 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO INTERRUPTOR LOCAL | S22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2022-05-09 | 80040 | keep | 0 | May | 2022 | 0.054515 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-05-09 15:10 | 2022-05-09 18:58 | 100 | 003:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22050900134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2022-05-09 | 22800 | keep | 0 | May | 2022 | 0.015529 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-09 15:16 | 2022-05-09 18:02 | 100 | 002:46 | P | DESGANCHE | SE REALIZO DESGANCHE CRITICO 1 X 40 EN SMU20 | B22050900096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-05-09 | 16600 | keep | 0 | May | 2022 | 0.011306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-09 15:26 | 2022-05-09 19:28 | 1 | 004:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M22050900369 | New_Event | Wire Down | Include | Include | Equipment | 242 | 2022-05-09 | 242 | keep | 0 | May | 2022 | 0.00016483 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-09 15:30 | 2022-05-09 15:31 | 5809 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1710-02 | B22050900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-09 | 5809 | keep | 0 | May | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
SAN JUAN | 2022-05-09 15:31 | 2022-05-09 20:58 | 75 | 005:27 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22050900266 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 327 | 2022-05-09 | 24525 | keep | 0 | May | 2022 | 0.016704 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-05-09 15:31 | 2022-05-10 02:40 | 445 | 011:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE TRANSFIRIO LA MITAD DE LA CARGA DEL ALIMENTADOR AL 1716-03 Y LA OTRA MITAD SE TRANSFIRIO AL 1710-04 MEDIANTE G.O.I. BY-220509-03 (TODO QUEDO EN SERVICIO) | B22050900107 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 669 | 2022-05-09 | 297705 | keep | 0 | May | 2022 | 0.20277 | 0.00030309 | Sustained | FALSE | FALSE | Not_TMED_Event | 445
FAJARDO | 2022-05-09 15:31 | 2022-05-09 17:00 | 60 | 001:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | R22050900152 | New_Event | Cutout Failure | Include | Include | Equipment | 89 | 2022-05-09 | 5340 | keep | 0 | May | 2022 | 0.003637 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-05-09 15:32 | 2022-05-09 17:40 | 25 | 002:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA BAMBUS HACIENDO CONTACTO CON LINEA PRIMARIA REQUIERE DESGANCHE | A22050900104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-05-09 | 3200 | keep | 0 | May | 2022 | 0.0021795 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-09 15:34 | 2022-05-09 16:30 | 30 | 000:56 | P | DESGANCHE | 2 X 30 Y SE REALIZO DESGANCHE | S22050900270 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-05-09 | 1680 | keep | 0 | May | 2022 | 0.0011442 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-05-09 15:41 | 2022-05-09 17:54 | 1 | 002:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22050900318 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2022-05-09 | 133 | keep | 0 | May | 2022 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-09 15:51 | 2022-05-10 09:45 | 20 | 017:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22050900322 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1074 | 2022-05-09 | 21480 | keep | 0 | May | 2022 | 0.01463 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-09 15:56 | 2022-05-09 20:00 | 1 | 004:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | P22050900323 | New_Event |  |  | Include | Wildlife | 244 | 2022-05-09 | 244 | keep | 0 | May | 2022 | 0.00016619 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-09 16:01 | 2022-05-09 17:04 | 4 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO IDENTIFICO CAUSA | A22050900099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-05-09 | 252 | keep | 0 | May | 2022 | 0.00017164 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-09 16:02 | 2022-05-09 18:14 | 138 | 002:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR PARTIDO Y SE CERRO RESTABLECIO SERVICIO | S22050900165 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 132 | 2022-05-09 | 18216 | keep | 0 | May | 2022 | 0.012407 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-09 16:02 | 2022-05-10 15:28 | 1 | 023:26 | P | DESGANCHE | 1 X 15 EN BANCO DE TRANSFORMADORES | R22050900171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1406 | 2022-05-09 | 1406 | keep | 0 | May | 2022 | 0.00095762 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-09 16:04 | 2022-05-09 18:55 | 30 | 002:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22050900100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-05-09 | 5130 | keep | 0 | May | 2022 | 0.003494 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-09 16:06 | 2022-05-09 19:01 | 35 | 002:55 | P | DESGANCHE | SE DESGANCHO 1 X 40 EN C/L | S22050900304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-05-09 | 6125 | keep | 0 | May | 2022 | 0.0041717 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-05-09 16:29 | 2022-05-10 01:25 | 60 | 008:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22050900332 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 536 | 2022-05-09 | 32160 | keep | 0 | May | 2022 | 0.021904 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-09 16:35 | 2022-05-09 19:49 | 200 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M22050900338 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-05-09 | 38800 | keep | 0 | May | 2022 | 0.026427 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-05-09 16:42 | 2022-05-09 16:48 | 1474 | 000:06 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES Y ENTRO 30% DE LOS CLIENTES | R22050900000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-05-09 | 8844 | keep | 0 | May | 2022 | 0.0060236 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-09 16:48 | 2022-05-09 16:59 | 1053 | 000:11 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES Y ENTRO 50% DE LOS CLIENTES | R22050900000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-05-09 | 11583 | keep | 0 | May | 2022 | 0.0078891 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-09 16:53 | 2022-05-10 04:26 | 10 | 011:33 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO ENCONTRARON CAUSA | M22050900348 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 693 | 2022-05-09 | 6930 | keep | 0 | May | 2022 | 0.00472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-09 16:55 | 2022-05-10 11:39 | 1 | 018:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C22050900179 | New_Event |  |  | Include | Wildlife | 1124 | 2022-05-09 | 1124 | keep | 0 | May | 2022 | 0.00076555 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-09 16:59 | 2022-05-09 17:30 | 1053 | 000:31 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES Y ENTRO 100% DE LOS CLIENTES | R22050900000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 31 | 2022-05-09 | 32643 | keep | 0 | May | 2022 | 0.022233 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-09 17:02 | 2022-05-10 12:20 | 35 | 019:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22050900343 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1158 | 2022-05-09 | 40530 | keep | 0 | May | 2022 | 0.027605 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-05-09 17:06 | 2022-05-09 19:41 | 35 | 002:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22050900345 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-05-09 | 5425 | keep | 0 | May | 2022 | 0.0036949 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-05-09 17:23 | 2022-05-09 20:00 | 80 | 002:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22050900193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-05-09 | 12560 | keep | 0 | May | 2022 | 0.0085546 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-05-09 17:26 | 2022-05-09 17:27 | 906 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 906 | keep | 0 | May | 2022 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
UTUADO | 2022-05-09 17:37 | 2022-05-09 17:39 | 934 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR RECIERRE ON NO RECERRO SE CERRO POR CONTROL SCADA | A22050900110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-09 | 1868 | keep | 0 | May | 2022 | 0.0012723 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
BAYAMON | 2022-05-09 17:49 | 2022-05-09 19:25 | 1 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO LINEA SAFADA A SU SITIO | S22050900362 | New_Event | Wire Down | Include | Include | Equipment | 96 | 2022-05-09 | 96 | keep | 0 | May | 2022 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-09 17:49 | 2022-05-10 17:09 | 5 | 023:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR IGUANA | B22050900273 | New_Event |  |  | Include | Wildlife | 1400 | 2022-05-09 | 7000 | keep | 0 | May | 2022 | 0.0047677 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-05-09 18:22 | 2022-05-09 20:30 | 300 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO CON SWITCHING FORM CG-220509-01 | C22050900146 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2022-05-09 | 38400 | keep | 0 | May | 2022 | 0.026154 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-05-09 18:23 | 2022-05-09 21:46 | 300 | 003:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C22050900249 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2022-05-09 | 60900 | keep | 0 | May | 2022 | 0.041479 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-05-09 18:28 | 2022-05-10 00:54 | 40 | 006:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | R22050900119 | New_Event | Wire Down | Include | Include | Equipment | 386 | 2022-05-09 | 15440 | keep | 0 | May | 2022 | 0.010516 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-09 18:28 | 2022-05-10 17:51 | 148 | 023:23 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPLAZO EL SU - 10 | C22050900249 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1403 | 2022-05-09 | 207644 | keep | 0 | May | 2022 | 0.14143 | 0.0001008 | Sustained | FALSE | FALSE | Not_TMED_Event | 148
HUMACAO | 2022-05-09 18:45 | 2022-05-09 18:46 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22050900146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 824 | keep | 0 | May | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
SAN JUAN | 2022-05-09 19:00 | 2022-05-10 16:57 | 100 | 021:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S22050900381 | New_Event | Wire Down | Include | Include | Equipment | 1317 | 2022-05-09 | 131700 | keep | 0 | May | 2022 | 0.0897 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-09 19:01 | 2022-05-09 19:02 | 2096 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | B22050900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-09 | 2096 | keep | 0 | May | 2022 | 0.0014276 | 0.0014276 | Momentary | FALSE | FALSE | Not_TMED_Event | 2096
BAYAMON | 2022-05-09 19:02 | 2022-05-09 23:43 | 436 | 004:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO EN TRONCAL MEDIANTE G.O.I. BY-220509-05 | B22050900354 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 281 | 2022-05-09 | 122516 | keep | 0 | May | 2022 | 0.083445 | 0.00029696 | Sustained | FALSE | FALSE | Not_TMED_Event | 436
PONCE | 2022-05-09 19:24 | 2022-05-09 19:25 | 1339 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR CARGA POR 4501-05 | P22050900157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1339 | keep | 0 | May | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
PONCE | 2022-05-09 19:24 | 2022-05-09 19:25 | 1295 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22050900157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1295 | keep | 0 | May | 2022 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
BARRANQUITAS | 2022-05-09 19:25 | 2022-05-09 23:31 | 100 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22050900284 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2022-05-09 | 24600 | keep | 0 | May | 2022 | 0.016755 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-09 19:33 | 2022-05-10 10:23 | 33 | 014:50 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22050900205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 890 | 2022-05-09 | 29370 | keep | 0 | May | 2022 | 0.020004 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
PONCE | 2022-05-09 19:38 | 2022-05-09 19:39 | 1339 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR CARGA POR 4501-05 | P22050900166 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1339 | keep | 0 | May | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
PONCE | 2022-05-09 19:38 | 2022-05-09 19:39 | 1295 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22050900166 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1295 | keep | 0 | May | 2022 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
MAYAGÃœEZ | 2022-05-09 19:51 | 2022-05-10 03:30 | 100 | 007:39 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO ENCONTRARON CAUSA | M22050900393 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 459 | 2022-05-09 | 45900 | keep | 0 | May | 2022 | 0.031262 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-05-09 19:52 | 2022-05-09 19:53 | 1339 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR CARGA POR 4501-05 | P22050900173 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1339 | keep | 0 | May | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
PONCE | 2022-05-09 19:52 | 2022-05-09 19:53 | 1295 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22050900173 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1295 | keep | 0 | May | 2022 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
BAYAMON | 2022-05-09 20:00 | 2022-05-09 22:05 | 85 | 002:05 | P | DESGANCHE | 1X30 EN C/L | B22050900421 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-05-09 | 10625 | keep | 0 | May | 2022 | 0.0072366 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
ARECIBO | 2022-05-09 20:10 | 2022-05-10 08:07 | 10 | 011:57 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A22050900117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 717 | 2022-05-09 | 7170 | keep | 0 | May | 2022 | 0.0048835 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-09 20:20 | 2022-05-10 02:30 | 300 | 006:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22050900400 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2022-05-09 | 111000 | keep | 0 | May | 2022 | 0.075602 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-05-09 20:36 | 2022-05-10 04:39 | 9 | 008:03 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 100 KVA X 100 KVA | R22050900219 | New_Event | Service Transformer Failure | Include | Include | Equipment | 483 | 2022-05-09 | 4347 | keep | 0 | May | 2022 | 0.0029607 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-05-09 20:40 | 2022-05-09 20:41 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22050900404 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 4304 | keep | 0 | May | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
HUMACAO | 2022-05-09 20:50 | 2022-05-10 10:37 | 40 | 013:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L REEMPLAZO AISLADOR ROTO E INSTALO CAJA | C22050900333 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 827 | 2022-05-09 | 33080 | keep | 0 | May | 2022 | 0.022531 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-05-09 20:50 | 2022-05-10 00:25 | 12 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22050900335 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2022-05-09 | 2580 | keep | 0 | May | 2022 | 0.0017572 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-05-09 21:10 | 2022-05-10 11:43 | 41 | 014:33 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S22050900410 | New_Event | Vegetation Contact | Include | Include | Vegetation | 873 | 2022-05-09 | 35793 | keep | 0 | May | 2022 | 0.024378 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2022-05-09 21:58 | 2022-05-10 12:09 | 30 | 014:11 | P | DESGANCHE | 2 X 30 EN C/L RAMA | B22050900538 | New_Event | Vegetation Contact | Include | Include | Vegetation | 851 | 2022-05-09 | 25530 | keep | 0 | May | 2022 | 0.017388 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-09 22:04 | 2022-05-10 11:48 | 72 | 013:44 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S22050900422 | New_Event | Vegetation Contact | Include | Include | Vegetation | 824 | 2022-05-09 | 59328 | keep | 0 | May | 2022 | 0.040408 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
CANOVANAS | 2022-05-09 22:09 | 2022-05-10 10:05 | 8 | 011:56 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22050900224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 716 | 2022-05-09 | 5728 | keep | 0 | May | 2022 | 0.0039013 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-09 22:14 | 2022-05-10 13:56 | 101 | 015:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S22050900425 | New_Event | Wire Down | Include | Include | Equipment | 942 | 2022-05-09 | 95142 | keep | 0 | May | 2022 | 0.064801 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
BAYAMON | 2022-05-09 22:23 | 2022-05-10 02:48 | 222 | 004:25 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1909-09 SE REMPLAZO MACHETE PRIMARIO MEDIANTE G.O.I. BY-220509-04 | B22050900000 | New_Event | Switch Failure | Include | Include | Equipment | 265 | 2022-05-09 | 58830 | keep | 0 | May | 2022 | 0.040069 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-05-09 22:23 | 2022-05-10 02:48 | 4456 | 004:25 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1907-03 LLEVA LA CARGA DEL 1909-09 SE REMPLAZO MACHETE PRIMARIO MEDIANTE G.O.I. BY-220509-04 | B22050900000 | New_Event | Switch Failure | Include | Include | Equipment | 265 | 2022-05-09 | 1180840 | keep | 0 | May | 2022 | 0.80426 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
MAYAGÃœEZ | 2022-05-09 22:45 | 2022-05-10 10:18 | 30 | 011:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22050900431 | New_Event | Vegetation Contact | Include | Include | Vegetation | 693 | 2022-05-09 | 20790 | keep | 0 | May | 2022 | 0.01416 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-09 23:43 | 2022-05-10 09:41 | 128 | 009:58 | P | DESGANCHE | 1 X 100 EN C/L | C22050900380 | New_Event | Vegetation Contact | Include | Include | Vegetation | 598 | 2022-05-09 | 76544 | keep | 0 | May | 2022 | 0.052134 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
BAYAMON | 2022-05-09 23:43 | 2022-05-10 03:19 | 2096 | 003:36 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO EN TRONCAL MEDIANTE G.O.I. BY-220509-05 | B22050900354 | Additional_clients | Wire Down | Include | Include | Equipment | 216 | 2022-05-09 | 452736 | keep | 0 | May | 2022 | 0.30836 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-09 23:48 | 2022-05-09 23:49 | 1647 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-09 | 1647 | keep | 0 | May | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
CANOVANAS | 2022-05-09 23:50 | 2022-05-10 11:57 | 80 | 012:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJAS QUEMADAS | R22050900237 | New_Event | Cutout Failure | Include | Include | Equipment | 727 | 2022-05-09 | 58160 | keep | 0 | May | 2022 | 0.039613 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-05-10 01:38 | 2022-05-10 12:45 | 100 | 011:07 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 50 EN RISERS | B22051000015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 667 | 2022-05-10 | 66700 | keep | 0 | May | 2022 | 0.045429 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-10 01:54 | 2022-05-10 04:39 | 80 | 002:45 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO Y CAJA QUEMADOS | R22051000002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 165 | 2022-05-10 | 13200 | keep | 0 | May | 2022 | 0.0089905 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-05-10 02:39 | 2022-05-10 09:46 | 50 | 007:07 | P | DESGANCHE | 1 X 65 EN C/L | C22051000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 427 | 2022-05-10 | 21350 | keep | 0 | May | 2022 | 0.014541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-05-10 04:39 | 2022-05-10 04:40 | 4085 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 2402-03 LLEVANDO CARGA DEL 2404-06 | R22051000003 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-05-10 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-05-10 04:39 | 2022-05-10 04:40 | 7621 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 2402-03 LLEVANDO CARGA DEL 2404-06 | R22051000003 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-05-10 | 7621 | keep | 0 | May | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
SAN JUAN | 2022-05-10 04:40 | 2022-05-10 15:22 | 133 | 010:42 | P | DESCONECTIVO DEFECTUOSO | 2 JUEGOS DE MACHETES AEREOS Y SMU QUEMADOS EN SU5 | R22051000010 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 642 | 2022-05-10 | 85386 | keep | 0 | May | 2022 | 0.058156 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
SAN JUAN | 2022-05-10 04:40 | 2022-05-10 14:33 | 80 | 009:53 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO Y CAJA QUEMADOS | R22051000002 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 593 | 2022-05-10 | 47440 | keep | 0 | May | 2022 | 0.032311 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-10 04:40 | 2022-05-10 12:20 | 9 | 007:40 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 100 KVA X 100 KVA | R22050900219 | New_Event | Service Transformer Failure | Include | Include | Equipment | 460 | 2022-05-10 | 4140 | keep | 0 | May | 2022 | 0.0028197 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2022-05-10 06:16 | 2022-05-10 08:48 | 19 | 002:32 | P | DESGANCHE | 1 X 50 EN C/L | R22051000012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-05-10 | 2888 | keep | 0 | May | 2022 | 0.001967 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-05-10 06:32 | 2022-05-10 06:33 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | SS2205100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 6136 | keep | 0 | May | 2022 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2022-05-10 06:51 | 2022-05-10 06:52 | 2466 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22051000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 2466 | keep | 0 | May | 2022 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
GUAYAMA | 2022-05-10 07:04 | 2022-05-10 07:05 | 4132 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE CARGA TRANSFERIDA AL 4006-05 | P22051000007 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-10 | 4132 | keep | 0 | May | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-05-10 07:04 | 2022-05-10 07:05 | 4279 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE CARGA TRANSFERIDA AL 4006-05 | P22051000007 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-10 | 4279 | keep | 0 | May | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-05-10 07:04 | 2022-05-10 07:05 | 464 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE LLEVA LA CARGA DEL 4003-01 Y DEL 4003-02 | P22051000007 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-10 | 464 | keep | 0 | May | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-05-10 07:05 | 2022-05-10 10:49 | 10 | 003:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | P22051000003 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 224 | 2022-05-10 | 2240 | keep | 0 | May | 2022 | 0.0015257 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-05-10 07:11 | 2022-05-10 20:19 | 33 | 013:08 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B22051000032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 788 | 2022-05-10 | 26004 | keep | 0 | May | 2022 | 0.017711 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
SAN JUAN | 2022-05-10 07:17 | 2022-05-10 11:59 | 150 | 004:42 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE MASIVO | S22051000063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-05-10 | 42300 | keep | 0 | May | 2022 | 0.02881 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-10 07:47 | 2022-05-10 16:18 | 15 | 008:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER AVE CRUZO RISER | M22051000014 | New_Event |  |  | Include | Wildlife | 511 | 2022-05-10 | 7665 | keep | 0 | May | 2022 | 0.0052206 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-10 07:47 | 2022-05-10 17:46 | 30 | 009:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M22051000011 | New_Event | Wire Down | Include | Include | Equipment | 599 | 2022-05-10 | 17970 | keep | 0 | May | 2022 | 0.012239 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-05-10 07:57 | 2022-05-10 14:59 | 3 | 007:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22051000007 | New_Event | Wire Down | Include | Include | Equipment | 422 | 2022-05-10 | 1266 | keep | 0 | May | 2022 | 0.00086227 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-05-10 08:21 | 2022-05-10 11:06 | 8 | 002:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L SE REEMPLAZO PORTAFUSIBLE | S22050900041 | New_Event | Cutout Failure | Include | Include | Equipment | 165 | 2022-05-10 | 1320 | keep | 0 | May | 2022 | 0.00089905 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-05-10 08:21 | 2022-05-11 08:22 | 4 | 024:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A22051000146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1441 | 2022-05-10 | 5764 | keep | 0 | May | 2022 | 0.0039258 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-10 08:29 | 2022-05-10 15:20 | 65 | 006:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22051000099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2022-05-10 | 26715 | keep | 0 | May | 2022 | 0.018195 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-05-10 08:39 | 2022-05-10 12:04 | 1 | 003:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA DE RISER | M22051000020 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2022-05-10 | 205 | keep | 0 | May | 2022 | 0.00013962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-10 08:42 | 2022-05-10 16:22 | 80 | 007:40 | P | DESGANCHE | 1 X 80 EN C/L | C22051000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 460 | 2022-05-10 | 36800 | keep | 0 | May | 2022 | 0.025064 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-10 08:43 | 2022-05-10 11:58 | 45 | 003:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-05-10 | 8775 | keep | 0 | May | 2022 | 0.0059766 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-05-10 08:45 | 2022-05-10 08:46 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22051000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 73 | keep | 0 | May | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
BARRANQUITAS | 2022-05-10 08:48 | 2022-05-10 10:25 | 20 | 001:37 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN C/L REEMPLAZO PARARRAYO | C22051000072 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 97 | 2022-05-10 | 1940 | keep | 0 | May | 2022 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-10 09:00 | 2022-05-10 14:19 | 158 | 005:19 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO Y FIJO CONDUCTOR | C22051000080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2022-05-10 | 50402 | keep | 0 | May | 2022 | 0.034329 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
VEGA BAJA | 2022-05-10 09:24 | 2022-05-10 09:25 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22051000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 3332 | keep | 0 | May | 2022 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
CAGUAS | 2022-05-10 09:28 | 2022-05-10 09:29 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22051000104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 1879 | keep | 0 | May | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
ARECIBO | 2022-05-10 09:32 | 2022-05-10 11:43 | 1 | 002:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA EN BOMBAS DE AAA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-05-10 | 131 | keep | 0 | May | 2022 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-10 09:51 | 2022-05-10 14:00 | 50 | 004:09 | P | DESGANCHE | 1 X 50 EN C/L | C22051000119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-05-10 | 12450 | keep | 0 | May | 2022 | 0.0084796 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-10 10:05 | 2022-05-10 12:25 | 30 | 002:20 | P | DESGANCHE | 1 X 30 EN C/L | R22051000047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-05-10 | 4200 | keep | 0 | May | 2022 | 0.0028606 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-10 10:15 | 2022-05-10 10:52 | 2888 | 000:37 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE CERRO POR SCADA Y QUEDO FUERA DE SERVICIO DESPACHO DISTRIBUCION MONACILLOS TENIA ORDEN DE VIA LIBRE Y SE ABRIO EL AMARRE Y SE CERRARON AMBOS INTERRUPTORES YA QUE SE CANCELO LA VIA LIBRE | A22051000020 | New_Event | Wire Down | Include | Include | Equipment | 37 | 2022-05-10 | 106856 | keep | 0 | May | 2022 | 0.072779 | 0.001967 | Sustained | FALSE | FALSE | Not_TMED_Event | 2888
VEGA BAJA | 2022-05-10 10:15 | 2022-05-10 10:57 | 3387 | 000:42 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | D2022-00776 EN AMARRE DE VIA LIBRE SE PARTIO CONDUCTOR DEL 9004-08 QUE SE HABIA TRANSFERIDO AL 8404-04 PARA LIBERAR XMR 9004-00 SE SECCIONALIZO, SE CANCELO VIA LIBRE Y SE CERRO 8404-04 Y 9004-08 QUE LLEVABA 9004-11 POR VIA LIBRE | B22051000051 | New_Event | Wire Down | Include | Include | Equipment | 42 | 2022-05-10 | 142254 | keep | 0 | May | 2022 | 0.096889 | 0.0023069 | Sustained | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2022-05-10 10:15 | 2022-05-10 10:57 | 377 | 000:42 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | D2022-00776 EN AMARRE DE VIA LIBRE SE PARTIO CONDUCTOR DEL 9004-08 QUE SE HABIA TRANSFERIDO AL 8404-04 PARA LIBERAR XMR 9004-00 SE SECCIONALIZO, SE CANCELO VIA LIBRE Y SE CERRO 8404-04 Y 9004-08 QUE LLEVABA 9004-11 POR VIA LIBRE | B22051000051 | New_Event | Wire Down | Include | Include | Equipment | 42 | 2022-05-10 | 15834 | keep | 0 | May | 2022 | 0.010784 | 0.00025677 | Sustained | FALSE | FALSE | Not_TMED_Event | 377
ARECIBO | 2022-05-10 10:17 | 2022-05-10 10:18 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA PARTE DE LA CARGA DEL 7403-02 OMS DICE QUE HAY 1106 CLIENTES | A22051000021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 1 | keep | 0 | May | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-10 10:20 | 2022-05-10 12:57 | 4 | 002:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIR XMR PARA REPARAR SECUNDARIA AVERIADA POR EXCAVACION DE CONTRATISTA | C22051000149 | New_Event |  |  | Include | Wildlife | 157 | 2022-05-10 | 628 | keep | 0 | May | 2022 | 0.00042773 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-05-10 10:27 | 2022-05-10 12:11 | 1000 | 001:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO INTERRUPTOR SE INTENTO CERRAR POR SCADA Y QUEDO FUERA DE SERVICIO POR LINEA PRIMARIA ROTA. HAY MAS CLEINTES SE A PEDIDO EL ING DE DISTRITO LA INFORMACION Y ESTAMOS EN ESPERA. PARTE DE LA CARGA POR EL 7403-01 | A22051000020 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2022-05-10 | 104000 | keep | 0 | May | 2022 | 0.070834 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
BAYAMON | 2022-05-10 10:42 | 2022-05-10 10:44 | 1370 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22051000147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-10 | 2740 | keep | 0 | May | 2022 | 0.0018662 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
CAGUAS | 2022-05-10 10:48 | 2022-05-10 12:06 | 1 | 001:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REEMPLAZO PORTAFUSIBLE | C22051000157 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2022-05-10 | 78 | keep | 0 | May | 2022 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-10 10:52 | 2022-05-10 13:21 | 25 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051000030 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2022-05-10 | 3725 | keep | 0 | May | 2022 | 0.0025371 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-05-10 10:55 | 2022-05-10 15:26 | 1 | 004:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN MONTURA TRIFASICA CRUCE DE FASE POR AVE | P22051000038 | New_Event |  |  | Include | Wildlife | 271 | 2022-05-10 | 271 | keep | 0 | May | 2022 | 0.00018458 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-10 10:57 | 2022-05-10 13:15 | 377 | 002:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | D2022-00776 EN AMARRE DE VIA LIBRE SE PARTIO CONDUCTOR DEL 9004-08 QUE SE HABIA TRANSFERIDO AL 8404-04 PARA LIBERAR XMR 9004-00 SE SECCIONALIZO, SE CANCELO VIA LIBRE Y SE CERRO 8404-04 Y 9004-08 QUE LLEVABA 9004-11 POR VIA LIBRE | B22051000051 | Partial_restoration | Wire Down | Include | Include | Equipment | 138 | 2022-05-10 | 52026 | keep | 0 | May | 2022 | 0.035435 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-10 11:05 | 2022-05-10 16:15 | 35 | 005:10 | P | DESGANCHE | 1 X 50 EN C/L | C22051000165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-05-10 | 10850 | keep | 0 | May | 2022 | 0.0073899 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-05-10 11:05 | 2022-05-11 12:10 | 70 | 025:05 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051000041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1505 | 2022-05-10 | 105350 | keep | 0 | May | 2022 | 0.071753 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-05-10 11:10 | 2022-05-10 13:28 | 100 | 002:18 | P | DESGANCHE | 1 X 100 EN C/L | C22051000168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-05-10 | 13800 | keep | 0 | May | 2022 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-10 11:12 | 2022-05-10 13:18 | 1 | 002:06 | P | NO SE REPORTO CAUSA | 2 X 30 EN CORTE DE LINEA | A22051000033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-05-10 | 126 | keep | 0 | May | 2022 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-10 11:28 | 2022-05-10 11:32 | 860 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN ON PERO NO RECERRO SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P22051000050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-05-10 | 3440 | keep | 0 | May | 2022 | 0.002343 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
BAYAMON | 2022-05-10 11:29 | 2022-05-10 17:32 | 1 | 006:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 2 X 100 EN C/L | S22051000166 | New_Event | Cutout Failure | Include | Include | Equipment | 363 | 2022-05-10 | 363 | keep | 0 | May | 2022 | 0.00024724 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-10 11:31 | 2022-05-10 11:32 | 1979 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P22051000051 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-10 | 1979 | keep | 0 | May | 2022 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2022-05-10 11:32 | 2022-05-10 13:53 | 660 | 002:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA EN SALIDA DE ALIMENTADOR SE ABRIO INTERRUPTOR PARA REPARAR | P22051000117 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 141 | 2022-05-10 | 93060 | keep | 0 | May | 2022 | 0.063383 | 0.00044952 | Sustained | FALSE | FALSE | Not_TMED_Event | 660
VEGA BAJA | 2022-05-10 11:39 | 2022-05-10 17:48 | 80 | 006:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22051000086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 369 | 2022-05-10 | 29520 | keep | 0 | May | 2022 | 0.020106 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-05-10 11:40 | 2022-05-10 12:39 | 75 | 000:59 | T | DESGANCHE | DISPARO DE INTERRUPTOR ARBOL CAYO SOBRE LA LINEA EN EL TRONCAL SE ABREN MACHETES PARA SECCIONALIZAR ALIMENTADOR LA CARGA DE ESTE INTERRUPTOR ESTA TRANSFERIDA AL 4402-02 | P22051000056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-05-10 | 4425 | keep | 0 | May | 2022 | 0.0030138 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-05-10 11:40 | 2022-05-10 12:39 | 449 | 000:59 | T | DESGANCHE | DISPARO DE INTERRUPTOR ARBOL CAYO SOBRE LA LINEA EN EL TRONCAL SE ABREN MACHETES PARA SECCIONALIZAR ALIMENTADOR ESTE INTERRUPTOR LLEVA LA CARGA DEL 4402-01 | P22051000056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-05-10 | 26491 | keep | 0 | May | 2022 | 0.018043 | 0.00030581 | Sustained | FALSE | FALSE | Not_TMED_Event | 449
MAYAGÃœEZ | 2022-05-10 11:50 | 2022-05-10 13:38 | 240 | 001:48 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEAS Y RETEZAR LINEAS PRIMARIAS | M22051000050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-05-10 | 25920 | keep | 0 | May | 2022 | 0.017654 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
ARECIBO | 2022-05-10 12:11 | 2022-05-10 14:15 | 1 | 002:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRARRON MACHETES SOLIDOS LLEVA PARTE DE LA CARGA DEL 7403-02 | A22051000020 | New_Event | Wire Down | Include | Include | Equipment | 124 | 2022-05-10 | 124 | keep | 0 | May | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-05-10 12:16 | 2022-05-10 16:00 | 100 | 003:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INDICA REQUIERE DESGANCHE | M22051000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-05-10 | 22400 | keep | 0 | May | 2022 | 0.015257 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-10 12:28 | 2022-05-10 17:36 | 10 | 005:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA Y SE REALIZO DESGANCHE | S22051000177 | New_Event | Secondary Wire Down | Include | Include | Equipment | 308 | 2022-05-10 | 3080 | keep | 0 | May | 2022 | 0.0020978 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-05-10 12:32 | 2022-05-10 15:38 | 562 | 003:06 | S | PROTECCION DEFECTUOSA | 1 X 125 STANDARD SPEED FASE A SE VERIFICARAN VALORES DE PROTECCION EN INTERRUPTORES | P22051000103 | New_Event | Protection Miscoordination | Include | Include | Other | 186 | 2022-05-10 | 104532 | keep | 0 | May | 2022 | 0.071196 | 0.00038278 | Sustained | FALSE | FALSE | Not_TMED_Event | 562
PONCE | 2022-05-10 12:32 | 2022-05-10 15:38 | 688 | 003:06 | S | PROTECCION DEFECTUOSA | 1 X 125 STANDARD SPEED FASE A SE VERIFICARAN VALORES DE PROTECCION EN INTERRUPTORES | P22051000103 | New_Event | Protection Miscoordination | Include | Include | Other | 186 | 2022-05-10 | 127968 | keep | 0 | May | 2022 | 0.087158 | 0.00046859 | Sustained | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2022-05-10 12:32 | 2022-05-10 15:38 | 658 | 003:06 | S | PROTECCION DEFECTUOSA | 1 X 125 STANDARD SPEED FASE A SE VERIFICARAN VALORES DE PROTECCION EN INTERRUPTORES | P22051000103 | New_Event | Protection Miscoordination | Include | Include | Other | 186 | 2022-05-10 | 122388 | keep | 0 | May | 2022 | 0.083358 | 0.00044816 | Sustained | FALSE | FALSE | Not_TMED_Event | 658
BAYAMON | 2022-05-10 12:35 | 2022-05-10 16:20 | 50 | 003:45 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | B22051000100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2022-05-10 | 11250 | keep | 0 | May | 2022 | 0.0076623 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-10 12:39 | 2022-05-10 13:22 | 262 | 000:43 | P | DESGANCHE | SE RETIRO ARBOL DE LA LINEA Y SE CERRARON MACHETES | P22051000086 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-05-10 | 11266 | keep | 0 | May | 2022 | 0.0076732 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-10 12:40 | 2022-05-10 12:43 | 1370 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22051000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-10 | 4110 | keep | 0 | May | 2022 | 0.0027993 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
CAGUAS | 2022-05-10 12:50 | 2022-05-10 16:09 | 117 | 003:19 | P | DESGANCHE | 2 X 65 EN C/L | C22051000212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-05-10 | 23283 | keep | 0 | May | 2022 | 0.015858 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
MAYAGÃœEZ | 2022-05-10 13:20 | 2022-05-10 14:00 | 8 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22051000034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-05-10 | 320 | keep | 0 | May | 2022 | 0.00021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-05-10 13:22 | 2022-05-10 16:36 | 50 | 003:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051000048 | New_Event | Bad Weather | Include | Include | Weather | 194 | 2022-05-10 | 9700 | keep | 0 | May | 2022 | 0.0066066 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-05-10 13:23 | 2022-05-10 17:16 | 30 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN C/L FUERTES LLUVIAS | C22051000233 | New_Event | Bad Weather | Include | Include | Weather | 233 | 2022-05-10 | 6990 | keep | 0 | May | 2022 | 0.0047609 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-10 13:23 | 2022-05-10 13:24 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051000085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-10 13:23 | 2022-05-10 13:24 | 871 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6012-05 | M22051000085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-10 13:33 | 2022-05-10 19:35 | 25 | 006:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051000094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-05-10 | 9050 | keep | 0 | May | 2022 | 0.0061639 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-05-10 13:53 | 2022-05-10 14:31 | 1979 | 000:38 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO INTERRUPTOR | P22051000117 | Additional_clients | Wire Down | Include | Include | Equipment | 38 | 2022-05-10 | 75202 | keep | 0 | May | 2022 | 0.05122 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-10 14:00 | 2022-05-10 19:09 | 30 | 005:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051000055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2022-05-10 | 9270 | keep | 0 | May | 2022 | 0.0063138 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-10 14:05 | 2022-05-10 18:45 | 7 | 004:40 | P | SOBRECARGA | 1 X 10 EN TRANSFORMADOR SOBRE CARGA | M22051000120 | New_Event | Trip Due To Overload | Include | Include | Other | 280 | 2022-05-10 | 1960 | keep | 0 | May | 2022 | 0.0013349 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-05-10 14:30 | 2022-05-10 16:52 | 35 | 002:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22051000204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-05-10 | 4970 | keep | 0 | May | 2022 | 0.003385 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-05-10 14:30 | 2022-05-10 14:31 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051000268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-05-10 14:32 | 2022-05-10 14:33 | 191 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C22051000206 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-10 | 191 | keep | 0 | May | 2022 | 0.00013009 | 0.00013009 | Momentary | FALSE | FALSE | Not_TMED_Event | 191
BAYAMON | 2022-05-10 14:39 | 2022-05-10 16:01 | 2402 | 001:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO LLEVA LA CARGA DEL 1720-08 QUE ENTRO UN 95% | S22051000218 | New_Event | Wire Down | Include | Include | Equipment | 82 | 2022-05-10 | 196964 | keep | 0 | May | 2022 | 0.13415 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-05-10 14:39 | 2022-05-10 16:01 | 1 | 001:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO DEL 1709-02 LLEVA LA CARGA DEL 1720-08. | S22051000218 | New_Event | Wire Down | Include | Include | Equipment | 82 | 2022-05-10 | 82 | keep | 0 | May | 2022 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-10 14:45 | 2022-05-10 21:40 | 100 | 006:55 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051000125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2022-05-10 | 41500 | keep | 0 | May | 2022 | 0.028265 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-05-10 14:46 | 2022-05-10 19:00 | 24 | 004:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L AVE CRUZO LINEAS | B22051000121 | New_Event |  |  | Include | Wildlife | 254 | 2022-05-10 | 6096 | keep | 0 | May | 2022 | 0.004152 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CANOVANAS | 2022-05-10 14:47 | 2022-05-10 15:38 | 18 | 000:51 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R22051000078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2022-05-10 | 918 | keep | 0 | May | 2022 | 0.00062525 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-05-10 14:48 | 2022-05-10 15:37 | 1 | 000:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE CORTE DE LINEA PARA REMPLAZAR AISLADOR | P22051000132 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 49 | 2022-05-10 | 49 | keep | 0 | May | 2022 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-10 14:56 | 2022-05-10 16:46 | 1 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN MONTURA TRIFASICA CRUCE DE FASE POR AVE | P22051000133 | New_Event |  |  | Include | Wildlife | 110 | 2022-05-10 | 110 | keep | 0 | May | 2022 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-10 15:01 | 2022-05-10 19:37 | 1587 | 004:36 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO BY-220510-02 | S22051000221 | New_Event | Wire Down | Include | Include | Equipment | 276 | 2022-05-10 | 438012 | keep | 0 | May | 2022 | 0.29833 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
SAN JUAN | 2022-05-10 15:04 | 2022-05-10 15:05 | 3046 | 000:01 | T | DESGANCHE | RECIERRE | R22051000080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-10 | 3046 | keep | 0 | May | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-05-10 15:05 | 2022-05-10 17:12 | 90 | 002:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22051000082 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-05-10 | 11430 | keep | 0 | May | 2022 | 0.0077849 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2022-05-10 15:11 | 2022-05-10 21:15 | 100 | 006:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | A22051000068 | New_Event | Wire Down | Include | Include | Equipment | 364 | 2022-05-10 | 36400 | keep | 0 | May | 2022 | 0.024792 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-10 15:18 | 2022-05-10 18:03 | 30 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051000070 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2022-05-10 | 4950 | keep | 0 | May | 2022 | 0.0033714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-05-10 15:21 | 2022-05-10 18:55 | 40 | 003:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051000072 | New_Event | Bad Weather | Include | Include | Weather | 214 | 2022-05-10 | 8560 | keep | 0 | May | 2022 | 0.0058302 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-10 15:22 | 2022-05-10 18:39 | 596 | 003:17 | P | DESCONECTIVO DEFECTUOSO | 2 JUEGOS DE MACHETES AEREOS Y SMU QUEMADOS EN SU5 | R22051000010 | New_Event | Switch Failure | Include | Include | Equipment | 197 | 2022-05-10 | 117412 | keep | 0 | May | 2022 | 0.079969 | 0.00040593 | Sustained | FALSE | FALSE | Not_TMED_Event | 596
SAN JUAN | 2022-05-10 15:24 | 2022-05-10 16:14 | 761 | 000:50 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1310-04 QUE A SU VEZ LLEVA LA CARGA DEL 1421-01 | S22051000306 | New_Event | Switch Failure | Include | Include | Equipment | 50 | 2022-05-10 | 38050 | keep | 0 | May | 2022 | 0.025916 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2022-05-10 15:24 | 2022-05-10 16:14 | 1498 | 000:50 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1310-04 QUE A SU VEZ LLEVA LA CARGA DEL 1421-01 | S22051000306 | New_Event | Switch Failure | Include | Include | Equipment | 50 | 2022-05-10 | 74900 | keep | 0 | May | 2022 | 0.051014 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2022-05-10 15:36 | 2022-05-10 21:20 | 30 | 005:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22051000262 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 344 | 2022-05-10 | 10320 | keep | 0 | May | 2022 | 0.0070289 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-10 15:40 | 2022-05-10 15:41 | 3500 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR PARTE POR 1620-05 | S22051000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-10 | 3500 | keep | 0 | May | 2022 | 0.0023838 | 0.0023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 3500
SAN JUAN | 2022-05-10 15:41 | 2022-05-10 15:44 | 1337 | 000:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA TRONCAL EN MACHETE | S22051000292 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 3 | 2022-05-10 | 4011 | keep | 0 | May | 2022 | 0.0027319 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
SAN JUAN | 2022-05-10 15:44 | 2022-05-10 15:45 | 3500 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR PARTE POR 1620-05 | S22051000000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-05-10 | 3500 | keep | 0 | May | 2022 | 0.0023838 | 0.0023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 3500
SAN JUAN | 2022-05-10 15:45 | 2022-05-10 20:17 | 1337 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA TRONCAL EN MACHETE | S22051000292 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 272 | 2022-05-10 | 363664 | keep | 0 | May | 2022 | 0.24769 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2022-05-10 16:00 | 2022-05-10 18:10 | 55 | 002:10 | P | SOBRECARGA | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SOBRECARGA | M22051000177 | New_Event | Trip Due To Overload | Include | Include | Other | 130 | 2022-05-10 | 7150 | keep | 0 | May | 2022 | 0.0048698 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2022-05-10 16:01 | 2022-05-10 17:46 | 100 | 001:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | S22051000218 | Partial_restoration | Wire Down | Include | Include | Equipment | 105 | 2022-05-10 | 10500 | keep | 0 | May | 2022 | 0.0071515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-10 16:09 | 2022-05-10 18:15 | 30 | 002:06 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051000151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-05-10 | 3780 | keep | 0 | May | 2022 | 0.0025745 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-10 16:12 | 2022-05-10 20:37 | 100 | 004:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REEMPLAZO DISCO QUEMADO | R22051000088 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 265 | 2022-05-10 | 26500 | keep | 0 | May | 2022 | 0.018049 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-10 16:14 | 2022-05-10 21:00 | 253 | 004:46 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE AVERIADO | S22051000331 | Partial_restoration | Switch Failure | Include | Include | Equipment | 286 | 2022-05-10 | 72358 | keep | 0 | May | 2022 | 0.049283 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-10 16:22 | 2022-05-11 07:39 | 10 | 015:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22051000337 | New_Event | Secondary Wire Down | Include | Include | Equipment | 917 | 2022-05-10 | 9170 | keep | 0 | May | 2022 | 0.0062456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-10 16:25 | 2022-05-10 19:10 | 24 | 002:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C22051000339 | New_Event |  |  | Include | Wildlife | 165 | 2022-05-10 | 3960 | keep | 0 | May | 2022 | 0.0026971 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CAGUAS | 2022-05-10 16:26 | 2022-05-10 18:53 | 68 | 002:27 | P | DESGANCHE | 1 X 80 EN C/L | C22051000341 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-05-10 | 9996 | keep | 0 | May | 2022 | 0.0068082 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
CANOVANAS | 2022-05-10 16:30 | 2022-05-10 18:47 | 80 | 002:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO GLOBO SOBRE PARARRAYO Y SE REEMPLAZO PARARRAYO QUEMADO | R22051000102 | New_Event |  |  | Include | Wildlife | 137 | 2022-05-10 | 10960 | keep | 0 | May | 2022 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-10 16:41 | 2022-05-10 19:38 | 4 | 002:57 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22051000141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2022-05-10 | 708 | keep | 0 | May | 2022 | 0.00048222 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-05-10 16:53 | 2022-05-10 23:12 | 50 | 006:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | A22051000088 | New_Event | Wire Down | Include | Include | Equipment | 379 | 2022-05-10 | 18950 | keep | 0 | May | 2022 | 0.012907 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-10 16:55 | 2022-05-10 16:56 | 2658 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CON RECIERRE EN ON SE CERRO POR CONTROL SCADA | M22051000164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 2658 | keep | 0 | May | 2022 | 0.0018104 | 0.0018104 | Momentary | FALSE | FALSE | Not_TMED_Event | 2658
BARRANQUITAS | 2022-05-10 17:05 | 2022-05-10 17:10 | 2725 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C22051000358 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 13625 | keep | 0 | May | 2022 | 0.0092799 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-05-10 17:05 | 2022-05-10 17:10 | 1834 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C22051000358 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 9170 | keep | 0 | May | 2022 | 0.0062456 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-05-10 17:05 | 2022-05-10 17:10 | 1437 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C22051000358 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 7185 | keep | 0 | May | 2022 | 0.0048937 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-05-10 17:05 | 2022-05-10 17:10 | 2565 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C22051000361 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 12825 | keep | 0 | May | 2022 | 0.008735 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-05-10 17:05 | 2022-05-10 17:10 | 3565 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C22051000361 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 17825 | keep | 0 | May | 2022 | 0.012141 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-05-10 17:05 | 2022-05-10 17:10 | 2751 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 NO SE ENCONTRO CAUSA | P22051000158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 13755 | keep | 0 | May | 2022 | 0.0093685 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-05-10 17:05 | 2022-05-10 17:10 | 576 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 NO SE ENCONTRO CAUSA | P22051000158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 2880 | keep | 0 | May | 2022 | 0.0019616 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-05-10 17:05 | 2022-05-10 17:10 | 2584 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 NO SE ENCONTRO CAUSA | P22051000158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 12920 | keep | 0 | May | 2022 | 0.0087998 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-05-10 17:05 | 2022-05-10 17:10 | 1606 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 NO SE ENCONTRO CAUSA | P22051000158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 8030 | keep | 0 | May | 2022 | 0.0054692 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-05-10 17:05 | 2022-05-10 17:10 | 29 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 NO SE ENCONTRO CAUSA | P22051000158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 145 | keep | 0 | May | 2022 | 9.8759e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2022-05-10 17:05 | 2022-05-10 17:10 | 4035 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 NO SE ENCONTRO CAUSA | P22051000158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 20175 | keep | 0 | May | 2022 | 0.013741 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-05-10 17:05 | 2022-05-10 17:10 | 3718 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 NO SE ENCONTRO CAUSA | P22051000158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-10 | 18590 | keep | 0 | May | 2022 | 0.012662 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
ARECIBO | 2022-05-10 17:20 | 2022-05-10 19:18 | 150 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA DE 200 AMP | A22051000100 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2022-05-10 | 17700 | keep | 0 | May | 2022 | 0.012055 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-10 17:23 | 2022-05-10 18:41 | 4 | 001:18 | P | NO SE REPORTO CAUSA | 3 X 125 EN SU-1 | S22051000172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-05-10 | 312 | keep | 0 | May | 2022 | 0.0002125 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-05-10 17:31 | 2022-05-10 19:54 | 12 | 002:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EVENTO DICE 4502-02 PERO DESPUES MARIA FUE TRANSFERIDO AL SEGUN EL SUP JOSE T MORALES, CORRIGIO NUM CLIENTES DE 100 A 12 | P22051000173 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-05-10 | 1716 | keep | 0 | May | 2022 | 0.0011688 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-10 17:34 | 2022-05-10 17:35 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22051000107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 2697 | keep | 0 | May | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2022-05-10 17:35 | 2022-05-10 19:24 | 60 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A22051000109 | New_Event |  |  | Include | Wildlife | 109 | 2022-05-10 | 6540 | keep | 0 | May | 2022 | 0.0044544 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-05-10 17:50 | 2022-05-10 20:10 | 6 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051000118 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2022-05-10 | 840 | keep | 0 | May | 2022 | 0.00057212 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-05-10 18:05 | 2022-05-11 05:56 | 16 | 011:51 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTA CAUSA | P22051000175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 711 | 2022-05-10 | 11376 | keep | 0 | May | 2022 | 0.0077481 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-05-10 18:07 | 2022-05-10 18:54 | 75 | 000:47 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051000181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-05-10 | 3525 | keep | 0 | May | 2022 | 0.0024009 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-05-10 18:22 | 2022-05-11 08:56 | 12 | 014:34 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | S22051000438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 874 | 2022-05-10 | 10488 | keep | 0 | May | 2022 | 0.0071433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-05-10 18:32 | 2022-05-10 21:34 | 10 | 003:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CAJA PRIMARIA ZAFADO | R22051000129 | New_Event | Wire Down | Include | Include | Equipment | 182 | 2022-05-10 | 1820 | keep | 0 | May | 2022 | 0.0012396 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-10 18:39 | 2022-05-10 18:44 | 4085 | 000:05 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA CERRAR MACHETE AEREO RECIO Y NORMALIZAR LINEA AEREA DEL 2404-06 | R22051000010 | New_Event | Switch Failure | Include | Include | Equipment | 5 | 2022-05-10 | 20425 | keep | 0 | May | 2022 | 0.013911 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2022-05-10 18:39 | 2022-05-10 18:44 | 7621 | 000:05 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA CERRAR MACHETE AEREO RECIO Y NORMALIZAR LINEA AEREA | R22051000010 | Additional_clients | Switch Failure | Include | Include | Equipment | 5 | 2022-05-10 | 38105 | keep | 0 | May | 2022 | 0.025953 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-10 18:44 | 2022-05-10 20:59 | 141 | 002:15 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA CERRAR MACHETE AEREO RECIO Y NORMALIZAR LINEA AEREA DEL 2404-06 | R22051000010 | Partial_restoration | Switch Failure | Include | Include | Equipment | 135 | 2022-05-10 | 19035 | keep | 0 | May | 2022 | 0.012965 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-10 18:48 | 2022-05-10 18:50 | 2904 | 000:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 50% DE LA CARGA DEL 1710-01. PUENTE ABIERTO EN MACHETES PERTENECIENTES AL 1716-03 | B22051000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-05-10 | 5808 | keep | 0 | May | 2022 | 0.0039558 | 0.0019779 | Momentary | FALSE | FALSE | Not_TMED_Event | 2904
BAYAMON | 2022-05-10 18:48 | 2022-05-10 18:49 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA EL 1711-05 SE CERRO POR SCADA | B22051000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 723 | keep | 0 | May | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-05-10 18:48 | 2022-05-10 18:49 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1711-02 SE CERRO POR SCADA | B22051000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 1976 | keep | 0 | May | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-05-10 18:48 | 2022-05-10 18:50 | 1812 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR LLEVA UN 50% DEL 1710-01 SE CERRO POR SCADA | B22051000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-05-10 | 3624 | keep | 0 | May | 2022 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2022-05-10 18:50 | 2022-05-10 18:58 | 500 | 000:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | PUENTE PRIMARIO ABIERTO EN MACHETE PUENTE CARRETERA 177 | B22051000198 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 8 | 2022-05-10 | 4000 | keep | 0 | May | 2022 | 0.0027244 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2022-05-10 18:51 | 2022-05-10 18:52 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22051000133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-05-10 18:52 | 2022-05-10 19:59 | 100 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | A22051000135 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-05-10 | 6700 | keep | 0 | May | 2022 | 0.0045633 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-10 18:57 | 2022-05-11 10:44 | 45 | 015:47 | P | DESGANCHE | 1 X 65 EN C/L | C22051000404 | New_Event | Vegetation Contact | Include | Include | Vegetation | 947 | 2022-05-10 | 42615 | keep | 0 | May | 2022 | 0.029025 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-05-10 18:58 | 2022-05-10 19:00 | 2904 | 000:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 50% DE LA CARGA 1710-01 SE CERRO POR SCADA. PUENTE ABIERTO EN MACHETES PERTENECIENTES AL 1716-03 | B22051000000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-05-10 | 5808 | keep | 0 | May | 2022 | 0.0039558 | 0.0019779 | Momentary | FALSE | FALSE | Not_TMED_Event | 2904
BAYAMON | 2022-05-10 18:58 | 2022-05-10 19:00 | 1812 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR LLEVA 50% DEL 1710-01 SE CERRO POR SCADA | B22051000000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-05-10 | 3624 | keep | 0 | May | 2022 | 0.0024683 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-10 19:00 | 2022-05-10 19:08 | 500 | 000:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | PUENTE PRIMARIO ABIERTO EN MACHETE PUENTE CARRETERA 177 | B22051000198 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 8 | 2022-05-10 | 4000 | keep | 0 | May | 2022 | 0.0027244 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-05-10 19:08 | 2022-05-10 20:57 | 2904 | 001:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO PUENTE ABIERTO EN MACHETES Y SE CERRO POR SCADA 50% DE SU CARGA POR EL 1716-03 | B22051000000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 109 | 2022-05-10 | 316536 | keep | 0 | May | 2022 | 0.21559 | 0.0019779 | Sustained | FALSE | FALSE | Not_TMED_Event | 2904
BAYAMON | 2022-05-10 19:08 | 2022-05-10 20:57 | 1812 | 001:49 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO PUENTE PRIMARIO ABIERTO EN MACHETES Y SE CERRO POR SCADA LLEVA 50% DEL 1710-01 | B22051000000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 109 | 2022-05-10 | 197508 | keep | 0 | May | 2022 | 0.13452 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-10 19:30 | 2022-05-11 16:11 | 1 | 020:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 3 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22051000140 | New_Event | Cutout Failure | Include | Include | Equipment | 1241 | 2022-05-10 | 1241 | keep | 0 | May | 2022 | 0.00084524 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-10 19:51 | 2022-05-10 21:12 | 69 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22051000241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-05-10 | 5589 | keep | 0 | May | 2022 | 0.0038066 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
HUMACAO | 2022-05-10 20:24 | 2022-05-11 09:46 | 4 | 013:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO NO FUNDIO | C22051000409 | New_Event | Secondary Wire Down | Include | Include | Equipment | 802 | 2022-05-10 | 3208 | keep | 0 | May | 2022 | 0.002185 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-05-10 20:52 | 2022-05-11 07:30 | 60 | 010:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051000150 | New_Event | Bad Weather | Include | Include | Weather | 638 | 2022-05-10 | 38280 | keep | 0 | May | 2022 | 0.026072 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-10 20:57 | 2022-05-10 21:01 | 500 | 000:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | PUENTE PRIMARIO ABIERTO EN MACHETE PUENTE CARRETERA 177 | B22051000198 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2022-05-10 | 2000 | keep | 0 | May | 2022 | 0.0013622 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-10 20:59 | 2022-05-10 22:30 | 8 | 001:31 | P | SECUNDARIA/DESGANCHE | SE LEVANTO ALAMBRE SECUNDARIO Y SE REALIZO DESGANCHE | S22051000538 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 91 | 2022-05-10 | 728 | keep | 0 | May | 2022 | 0.00049584 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-10 20:59 | 2022-05-10 21:29 | 16 | 000:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R22051000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-05-10 | 480 | keep | 0 | May | 2022 | 0.00032693 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-05-10 21:01 | 2022-05-10 23:13 | 2904 | 002:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRO N/O CONTRA 1716-03 SE REMPLAZO AISLADOR ROTO CON GOI BY-220510-03A. ENTRO 50% DE LA CARGA TRANSFERIDA AL 1716-03 | B22051000198 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 132 | 2022-05-10 | 383328 | keep | 0 | May | 2022 | 0.26108 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-10 21:01 | 2022-05-10 22:13 | 1812 | 001:12 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO PUENTE PRIMARIO ABIERTO EN MACHETES Y SE CERRO POR SCADA ABRIENDO N/O CONTRA 1710-01 | B22051000198 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 72 | 2022-05-10 | 130464 | keep | 0 | May | 2022 | 0.088858 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
FAJARDO | 2022-05-10 21:03 | 2022-05-11 10:35 | 40 | 013:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L REPARO BAJANTE PRIMARIO | R22051000150 | New_Event | Wire Down | Include | Include | Equipment | 812 | 2022-05-10 | 32480 | keep | 0 | May | 2022 | 0.022122 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-05-10 21:10 | 2022-05-11 14:17 | 1 | 017:07 | P | DESGANCHE | 1 X 40 EN C/L | R22051000151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1027 | 2022-05-10 | 1027 | keep | 0 | May | 2022 | 0.00069949 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-10 21:17 | 2022-05-11 12:25 | 9 | 015:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA | A22051000151 | New_Event | Cutout Failure | Include | Include | Equipment | 908 | 2022-05-10 | 8172 | keep | 0 | May | 2022 | 0.0055659 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-05-10 21:18 | 2022-05-10 21:19 | 164 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1531-02 QUE A SU VEZ LLEVA LA CARGA DEL 1421-02 | S22051000547 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-05-10 | 164 | keep | 0 | May | 2022 | 0.0001117 | 0.0001117 | Momentary | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2022-05-10 21:18 | 2022-05-10 21:19 | 716 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1531-02 QUE A SU VEZ LLEVA LA CARGA DEL 1421-02 | S22051000547 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-05-10 | 716 | keep | 0 | May | 2022 | 0.00048766 | 0.00048766 | Momentary | FALSE | FALSE | Not_TMED_Event | 716
BAYAMON | 2022-05-10 21:19 | 2022-05-11 12:38 | 550 | 015:19 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | S22051000576 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 919 | 2022-05-10 | 505450 | keep | 0 | May | 2022 | 0.34426 | 0.0003746 | Sustained | FALSE | FALSE | Not_TMED_Event | 550
SAN JUAN | 2022-05-10 21:30 | 2022-05-11 15:45 | 10 | 018:15 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S22051000055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1095 | 2022-05-10 | 10950 | keep | 0 | May | 2022 | 0.007458 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-05-10 21:34 | 2022-05-11 00:09 | 9 | 002:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA AVERIADA POR CAMION | P22051000183 | New_Event |  |  | Include | Wildlife | 155 | 2022-05-10 | 1395 | keep | 0 | May | 2022 | 0.00095013 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-05-10 22:01 | 2022-05-11 08:18 | 20 | 010:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051000154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 617 | 2022-05-10 | 12340 | keep | 0 | May | 2022 | 0.0084047 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-10 22:12 | 2022-05-10 23:25 | 400 | 001:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES AVERIADO | M22051000198 | New_Event | Cutout Failure | Include | Include | Equipment | 73 | 2022-05-10 | 29200 | keep | 0 | May | 2022 | 0.019888 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CAGUAS | 2022-05-10 22:17 | 2022-05-11 02:08 | 20 | 003:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | C22051000416 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2022-05-10 | 4620 | keep | 0 | May | 2022 | 0.0031467 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-10 23:01 | 2022-05-11 13:30 | 80 | 014:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22051000571 | New_Event | Vegetation Contact | Include | Include | Vegetation | 869 | 2022-05-10 | 69520 | keep | 0 | May | 2022 | 0.04735 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-10 23:01 | 2022-05-11 14:18 | 40 | 015:17 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22051100251 | New_Event | Vegetation Contact | Include | Include | Vegetation | 917 | 2022-05-10 | 36680 | keep | 0 | May | 2022 | 0.024983 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-10 23:13 | 2022-05-10 23:20 | 1452 | 000:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRO MACHETES QUE SE ABRIERON PARA ESTABLECER GOI PARA REMPLAZO DE AISLADOR | B22051000198 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 7 | 2022-05-10 | 10164 | keep | 0 | May | 2022 | 0.0069227 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-10 23:38 | 2022-05-10 23:39 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051000185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 752 | keep | 0 | May | 2022 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2022-05-10 23:38 | 2022-05-10 23:39 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051000185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-10 | 2696 | keep | 0 | May | 2022 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
SAN JUAN | 2022-05-11 00:01 | 2022-05-11 09:49 | 30 | 009:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22051100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 588 | 2022-05-11 | 17640 | keep | 0 | May | 2022 | 0.012015 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-11 00:06 | 2022-05-11 12:05 | 78 | 011:59 | P | DESGANCHE | 2 X 30 EN C/L | C22051100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 719 | 2022-05-11 | 56082 | keep | 0 | May | 2022 | 0.038197 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
BAYAMON | 2022-05-11 00:45 | 2022-05-11 00:46 | 318 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1711-03 LLEVANDO 20% 1711-01 | B22051100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 318 | keep | 0 | May | 2022 | 0.00021659 | 0.00021659 | Momentary | FALSE | FALSE | Not_TMED_Event | 318
BAYAMON | 2022-05-11 00:45 | 2022-05-11 00:46 | 13 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1711-03 LLEVANDO 20% 1711-01 | B22051100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 13 | keep | 0 | May | 2022 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-05-11 01:23 | 2022-05-11 01:24 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 3941 | keep | 0 | May | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
MAYAGÃœEZ | 2022-05-11 01:45 | 2022-05-11 07:00 | 150 | 005:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA QUEMADA EN SALIDA DEL CONVERTIDOR | M22051100006 | New_Event | Cutout Failure | Include | Include | Equipment | 315 | 2022-05-11 | 47250 | keep | 0 | May | 2022 | 0.032182 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-05-11 02:14 | 2022-05-11 08:29 | 60 | 006:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN C/L CRUCE X AVE | R22051100009 | New_Event |  |  | Include | Wildlife | 375 | 2022-05-11 | 22500 | keep | 0 | May | 2022 | 0.015325 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-11 02:29 | 2022-05-11 02:30 | 4634 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22051100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-11 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-05-11 02:38 | 2022-05-11 02:39 | 4634 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22051100010 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-11 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
BAYAMON | 2022-05-11 03:38 | 2022-05-11 03:39 | 2076 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 AISLADOR ROTO EN 1718-03 | B22051100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 2076 | keep | 0 | May | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-05-11 03:38 | 2022-05-11 03:39 | 2605 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 | B22051100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 2605 | keep | 0 | May | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-05-11 03:39 | 2022-05-11 10:45 | 72 | 007:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 SE REMPLAZO AISLADOR | B22051100011 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 426 | 2022-05-11 | 30672 | keep | 0 | May | 2022 | 0.020891 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2022-05-11 03:56 | 2022-05-11 10:07 | 25 | 006:11 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22051100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 371 | 2022-05-11 | 9275 | keep | 0 | May | 2022 | 0.0063172 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-11 04:03 | 2022-05-11 18:30 | 90 | 014:27 | P | CABLE SOTERRADO AVERIADO | 1 X 100 PRINCIPAL Y 1 X 80 RAMAL. SE DEJO FUERA T-20 FID-30072727 AVERIA VIEJA DEL T-21 AL T-20 Y DEL T-20 AL T-19, SE DEJO FUERA PROVISIONAL AEREO QUE IGUAL PROBO AVERIADO CONTRA TRANSFORMADOR T-20 | S22051100015 | New_Event | UG Cable Fault | Include | Include | Equipment | 867 | 2022-05-11 | 78030 | keep | 0 | May | 2022 | 0.053146 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-05-11 04:05 | 2022-05-11 04:06 | 4634 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22051100012 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-11 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-05-11 04:10 | 2022-05-11 04:11 | 4634 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22051100013 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-11 | 4634 | keep | 0 | May | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
SAN JUAN | 2022-05-11 04:39 | 2022-05-11 09:25 | 150 | 004:46 | P | DESGANCHE | 2 X 80 EN C/L | R22051100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2022-05-11 | 42900 | keep | 0 | May | 2022 | 0.029219 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-05-11 04:43 | 2022-05-11 10:28 | 69 | 005:45 | P | DESGANCHE | 1 X 100 EN C/L Y 1 X 8 EN XMR | R22051100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2022-05-11 | 23805 | keep | 0 | May | 2022 | 0.016213 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
CAGUAS | 2022-05-11 04:43 | 2022-05-11 07:44 | 4634 | 003:01 | T | DESGANCHE | DISPARO CERRADO X CONTROL SE RETIRO RAMA DE LAS LINEAS | C22051100016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-05-11 | 838754 | keep | 0 | May | 2022 | 0.57127 | 0.0031562 | Sustained | FALSE | FALSE | Not_TMED_Event | 4634
FAJARDO | 2022-05-11 04:49 | 2022-05-11 09:36 | 55 | 004:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | R22051100039 | New_Event | Bad Weather | Include | Include | Weather | 287 | 2022-05-11 | 15785 | keep | 0 | May | 2022 | 0.010751 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
FAJARDO | 2022-05-11 04:56 | 2022-05-11 10:00 | 200 | 005:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L REEMPLAZO DE CAJA QUEMADA | R22051100040 | New_Event | Cutout Failure | Include | Include | Equipment | 304 | 2022-05-11 | 60800 | keep | 0 | May | 2022 | 0.041411 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-11 05:29 | 2022-05-11 12:47 | 35 | 007:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S22051100018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 438 | 2022-05-11 | 15330 | keep | 0 | May | 2022 | 0.010441 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2022-05-11 05:29 | 2022-05-11 10:08 | 68 | 004:39 | P | DESGANCHE | 1 X 80 EN C/L | R22051100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-05-11 | 18972 | keep | 0 | May | 2022 | 0.012922 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
HUMACAO | 2022-05-11 05:33 | 2022-05-11 07:58 | 1 | 002:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE X AVE | C22051100020 | New_Event |  |  | Include | Wildlife | 145 | 2022-05-11 | 145 | keep | 0 | May | 2022 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-11 06:10 | 2022-05-11 06:11 | 638 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22051100023 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-11 | 638 | keep | 0 | May | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2022-05-11 06:11 | 2022-05-11 13:30 | 40 | 007:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22051100025 | 1st_after_momentary |  |  | Include | Wildlife | 439 | 2022-05-11 | 17560 | keep | 0 | May | 2022 | 0.01196 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-11 06:22 | 2022-05-11 06:24 | 1681 | 000:02 | T | DESGANCHE | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-04 | S22051100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-11 | 3362 | keep | 0 | May | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-11 06:22 | 2022-05-11 06:24 | 1598 | 000:02 | T | DESGANCHE | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-04 | S22051100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-11 | 3196 | keep | 0 | May | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-05-11 06:24 | 2022-05-11 17:24 | 10 | 011:00 | P | DESGANCHE | SE RETIRO ENREDADERA DE LA PRIMARIA Y 1 X 15 EN TRANSFORMADOR | S22051100425 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 660 | 2022-05-11 | 6600 | keep | 0 | May | 2022 | 0.0044952 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-11 06:38 | 2022-05-11 09:17 | 49 | 002:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L CONDUCTOR CRUZADO | R22051100055 | New_Event | Wire Down | Include | Include | Equipment | 159 | 2022-05-11 | 7791 | keep | 0 | May | 2022 | 0.0053064 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
MAYAGÃœEZ | 2022-05-11 07:00 | 2022-05-11 08:05 | 1073 | 001:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CAJAS DEL CONVERTIDOR PARA REMPLAZAR CAJA QUEMADA EN LA SALIDA | M22051100006 | Additional_clients | Cutout Failure | Include | Include | Equipment | 65 | 2022-05-11 | 69745 | keep | 0 | May | 2022 | 0.047503 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-11 07:02 | 2022-05-11 10:25 | 20 | 003:23 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-05-11 | 4060 | keep | 0 | May | 2022 | 0.0027652 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-11 07:08 | 2022-05-11 10:24 | 75 | 003:16 | P | DESGANCHE | 1 X 80 EN C/L | C22051100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-05-11 | 14700 | keep | 0 | May | 2022 | 0.010012 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-05-11 07:11 | 2022-05-11 15:24 | 4 | 008:13 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN C/L 1 X 15 EN XMR REEMPLAZO XMR QUEMADO DE 37.5 KVA X 37.5 KVA | C22051100032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 493 | 2022-05-11 | 1972 | keep | 0 | May | 2022 | 0.0013431 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-11 07:17 | 2022-05-11 07:18 | 766 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 1709-03, 50% POR 1909-07 Y LLEVA 1709-05 | B22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 766 | keep | 0 | May | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-05-11 07:17 | 2022-05-11 07:18 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1709-03, 50% POR 1909-07 Y LLEVA 1709-05 | B22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 2364 | keep | 0 | May | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2022-05-11 07:18 | 2022-05-11 10:37 | 105 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22051100045 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-05-11 | 20895 | keep | 0 | May | 2022 | 0.014231 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
GUAYAMA | 2022-05-11 07:35 | 2022-05-11 09:29 | 15 | 001:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE | P22051100002 | New_Event |  |  | Include | Wildlife | 114 | 2022-05-11 | 1710 | keep | 0 | May | 2022 | 0.0011647 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-05-11 07:39 | 2022-05-11 08:52 | 4027 | 001:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE AMARRO EL 90% ATRAVES DEL 9103-02 | B22051100013 | New_Event | Wire Down | Include | Include | Equipment | 73 | 2022-05-11 | 293971 | keep | 0 | May | 2022 | 0.20022 | 0.0027428 | Sustained | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2022-05-11 07:39 | 2022-05-11 14:16 | 1310 | 006:37 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | B22051100013 | New_Event | Wire Down | Include | Include | Equipment | 397 | 2022-05-11 | 520070 | keep | 0 | May | 2022 | 0.35422 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
HUMACAO | 2022-05-11 07:48 | 2022-05-11 14:20 | 2 | 006:32 | P | NO SE REPORTO CAUSA | 2 X 80 Y 2 X 65 EN C/L'S NO CAUSA | C22051100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 392 | 2022-05-11 | 784 | keep | 0 | May | 2022 | 0.00053398 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-05-11 07:59 | 2022-05-11 14:42 | 40 | 006:43 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | B22051100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 403 | 2022-05-11 | 16120 | keep | 0 | May | 2022 | 0.010979 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-11 08:00 | 2022-05-11 11:20 | 150 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051100013 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2022-05-11 | 30000 | keep | 0 | May | 2022 | 0.020433 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-05-11 08:06 | 2022-05-11 08:07 | 1500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO PARTE POR 1620-05 | S22051100046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 1500 | keep | 0 | May | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-05-11 08:06 | 2022-05-11 08:07 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-05 LLEVA PARTE 1206-3 | S22051100046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 1615 | keep | 0 | May | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
BAYAMON | 2022-05-11 08:07 | 2022-05-11 08:48 | 100 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 65 EN C/L SE REPORTO CRUCE POR AVE | B22051100036 | New_Event |  |  | Include | Wildlife | 41 | 2022-05-11 | 4100 | keep | 0 | May | 2022 | 0.0027925 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-11 08:09 | 2022-05-11 09:48 | 79 | 001:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 65 EN C/L PALOMA | B22051100042 | New_Event |  |  | Include | Wildlife | 99 | 2022-05-11 | 7821 | keep | 0 | May | 2022 | 0.0053268 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
CAGUAS | 2022-05-11 08:25 | 2022-05-11 09:40 | 60 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | C22051100042 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2022-05-11 | 4500 | keep | 0 | May | 2022 | 0.0030649 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-11 08:26 | 2022-05-11 17:47 | 110 | 009:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO C/L Y FIJO CONDUCTOR AL AISLADOR , PONCHO SOLIDO Y ELIMINO C/L | C22051100043 | New_Event | Wire Down | Include | Include | Equipment | 561 | 2022-05-11 | 61710 | keep | 0 | May | 2022 | 0.04203 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2022-05-11 08:26 | 2022-05-11 08:27 | 4664 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22051100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 4664 | keep | 0 | May | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2022-05-11 08:26 | 2022-05-11 15:01 | 50 | 006:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 395 | 2022-05-11 | 19750 | keep | 0 | May | 2022 | 0.013452 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-05-11 08:29 | 2022-05-11 08:30 | 4188 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22051100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-11 | 4188 | keep | 0 | May | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-05-11 08:29 | 2022-05-11 08:30 | 1386 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR 40% DE LA CARGA POR EL 2402-02 | R22051100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-11 | 1386 | keep | 0 | May | 2022 | 0.000944 | 0.000944 | Momentary | FALSE | FALSE | Not_TMED_Event | 1386
CANOVANAS | 2022-05-11 08:29 | 2022-05-11 08:30 | 2675 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR CARGA POR EL 2402-02 | R22051100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-11 | 2675 | keep | 0 | May | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2022-05-11 08:30 | 2022-05-11 11:44 | 1 | 003:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 SMU 20 DE 10 AMP Y 1 X 20 EN SU - 1BELTZ CONDUCTOR CRUZADO | R22051100113 | New_Event | Wire Down | Include | Include | Equipment | 194 | 2022-05-11 | 194 | keep | 0 | May | 2022 | 0.00013213 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-11 08:30 | 2022-05-11 09:56 | 165 | 001:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L DESGANCHO Y REMPLAZO CAJA QUEMADA | R22051100100 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 86 | 2022-05-11 | 14190 | keep | 0 | May | 2022 | 0.0096647 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
HUMACAO | 2022-05-11 08:33 | 2022-05-11 08:34 | 640 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 640 | keep | 0 | May | 2022 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
BARRANQUITAS | 2022-05-11 08:38 | 2022-05-11 10:18 | 60 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22051100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-05-11 | 6000 | keep | 0 | May | 2022 | 0.0040866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-05-11 08:52 | 2022-05-11 14:15 | 403 | 005:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | B22051100013 | Partial_restoration | Wire Down | Include | Include | Equipment | 323 | 2022-05-11 | 130169 | keep | 0 | May | 2022 | 0.088658 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-11 08:53 | 2022-05-11 12:04 | 85 | 003:11 | P | DESGANCHE | 1 X 80 EN C/L | C22051100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-05-11 | 16235 | keep | 0 | May | 2022 | 0.011058 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2022-05-11 08:54 | 2022-05-11 12:08 | 8 | 003:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR SE RETIRO NIDO | B22051100078 | New_Event |  |  | Include | Wildlife | 194 | 2022-05-11 | 1552 | keep | 0 | May | 2022 | 0.0010571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-05-11 09:12 | 2022-05-11 14:27 | 6 | 005:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO NEUTRAL Y SE SUBIO TAP 3 AL 4 QUEDO 121/242V | C22051100084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 315 | 2022-05-11 | 1890 | keep | 0 | May | 2022 | 0.0012873 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-05-11 09:14 | 2022-05-11 11:38 | 100 | 002:24 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-05-11 | 14400 | keep | 0 | May | 2022 | 0.0098078 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-11 09:15 | 2022-05-11 15:11 | 1 | 005:56 | P | NO SE REPORTO CAUSA | 2 X 20 EN BANCO DE XMR | B22051100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 356 | 2022-05-11 | 356 | keep | 0 | May | 2022 | 0.00024247 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-11 09:21 | 2022-05-11 09:24 | 2905 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO DE 1716-03 LLEVA 50% DEL 1710-01 | B22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-11 | 8715 | keep | 0 | May | 2022 | 0.0059357 | 0.0019786 | Momentary | FALSE | FALSE | Not_TMED_Event | 2905
BAYAMON | 2022-05-11 09:21 | 2022-05-11 09:24 | 1812 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE 1716-03 LLEVA 50% DEL 1710-01 | B22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-11 | 5436 | keep | 0 | May | 2022 | 0.0037024 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2022-05-11 09:23 | 2022-05-11 15:37 | 69 | 006:14 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | B22051100092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2022-05-11 | 25806 | keep | 0 | May | 2022 | 0.017576 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
UTUADO | 2022-05-11 09:26 | 2022-05-11 12:30 | 1 | 003:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051100010 | New_Event | Bad Weather | Include | Include | Weather | 184 | 2022-05-11 | 184 | keep | 0 | May | 2022 | 0.00012532 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-11 09:30 | 2022-05-11 13:08 | 1 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN MONTURA TRIFASICA SE REEMPLAZO CAJA PRIMARIA QUEMADA EN MONTURA | P22051100007 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2022-05-11 | 218 | keep | 0 | May | 2022 | 0.00014848 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-11 09:33 | 2022-05-11 10:32 | 6136 | 000:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO POR SCADA 40% EN SERVICIO | B22051100000 | New_Event | Wire Down | Include | Include | Equipment | 59 | 2022-05-11 | 362024 | keep | 0 | May | 2022 | 0.24657 | 0.0041792 | Sustained | FALSE | FALSE | Not_TMED_Event | 6136
MAYAGÃœEZ | 2022-05-11 09:44 | 2022-05-11 13:08 | 1 | 003:24 | P | OTRAS CAUSAS | ABRIR CAJAS DE TRANSFORMADOR PARA RELOCALIZAR TRANSFORMADOR EN EL MISMO POSTE. CAMBIO DE POSICION DEL TRANSFORMADOR SOLICITADA POR DIVISION DE INGENIERIA. | M22051100046 | New_Event | Other Causes | Include | Include | Other | 204 | 2022-05-11 | 204 | keep | 0 | May | 2022 | 0.00013894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-05-11 09:50 | 2022-05-11 12:00 | 50 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22051100009 | New_Event |  |  | Include | Wildlife | 130 | 2022-05-11 | 6500 | keep | 0 | May | 2022 | 0.0044271 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-11 09:54 | 2022-05-11 11:22 | 70 | 001:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22051100010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-05-11 | 6160 | keep | 0 | May | 2022 | 0.0041955 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-05-11 09:56 | 2022-05-11 09:57 | 4188 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22051100000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-11 | 4188 | keep | 0 | May | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-05-11 09:56 | 2022-05-11 09:57 | 1386 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 40% DE LA CARGA POR EL 2402-02 | R22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 1386 | keep | 0 | May | 2022 | 0.000944 | 0.000944 | Momentary | FALSE | FALSE | Not_TMED_Event | 1386
CANOVANAS | 2022-05-11 09:56 | 2022-05-11 09:57 | 2675 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR 100% DE LA CARGA POR EL 2402-02 | R22051100000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-11 | 2675 | keep | 0 | May | 2022 | 0.0018219 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-11 09:57 | 2022-05-11 10:15 | 165 | 000:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L DESGANCHO Y REMPLAZO CAJA QUEMADA | R22051100100 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 18 | 2022-05-11 | 2970 | keep | 0 | May | 2022 | 0.0020229 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
SAN JUAN | 2022-05-11 10:03 | 2022-05-11 10:17 | 1 | 000:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | S2205100128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-05-11 | 14 | keep | 0 | May | 2022 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-11 10:06 | 2022-05-11 11:00 | 25 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CAMION DE ASFALTO ROZO LINEA | B22051100146 | New_Event |  |  | Include | Wildlife | 54 | 2022-05-11 | 1350 | keep | 0 | May | 2022 | 0.00091948 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-05-11 10:11 | 2022-05-11 16:17 | 25 | 006:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051100018 | New_Event | Bad Weather | Include | Include | Weather | 366 | 2022-05-11 | 9150 | keep | 0 | May | 2022 | 0.006232 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-11 10:12 | 2022-05-11 17:22 | 15 | 007:10 | P | DESGANCHE | 1 X 30 EN TRANSFORMADOR. SE RETIRO RAMA EN LA PRIMARIA | S22051100157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 430 | 2022-05-11 | 6450 | keep | 0 | May | 2022 | 0.0043931 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-05-11 10:13 | 2022-05-11 10:15 | 640 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-11 | 1280 | keep | 0 | May | 2022 | 0.0008718 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
CANOVANAS | 2022-05-11 10:15 | 2022-05-11 10:16 | 4188 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22051100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-11 | 4188 | keep | 0 | May | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-05-11 10:15 | 2022-05-11 10:16 | 1386 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR 40% DE LA CARGA POR EL 2402-02 | R22051100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-11 | 1386 | keep | 0 | May | 2022 | 0.000944 | 0.000944 | Momentary | FALSE | FALSE | Not_TMED_Event | 1386
CANOVANAS | 2022-05-11 10:15 | 2022-05-11 10:16 | 2675 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR 100% DE LA CARGA POR EL 2402-02 | R22051100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-11 | 2675 | keep | 0 | May | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2022-05-11 10:16 | 2022-05-11 11:22 | 165 | 001:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L DESGANCHO Y REMPLAZO CAJA QUEMADA | R22051100100 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 66 | 2022-05-11 | 10890 | keep | 0 | May | 2022 | 0.0074171 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
SAN JUAN | 2022-05-11 10:17 | 2022-05-11 13:10 | 4 | 002:53 | P | ESTRUCTURA AVERIADA | SE INSTALO POSTE PARA MEJORAR PROVISIONAL EN MAL ESTADO | S22051100168 | New_Event | Defective Pole | Include | Include | Equipment | 173 | 2022-05-11 | 692 | keep | 0 | May | 2022 | 0.00047132 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-11 10:17 | 2022-05-11 13:44 | 4 | 003:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S22011050015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 207 | 2022-05-11 | 828 | keep | 0 | May | 2022 | 0.00056395 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-11 10:32 | 2022-05-11 12:38 | 3682 | 002:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE NORMALIZO CARGAS | B22051100115 | New_Event | Wire Down | Include | Include | Equipment | 126 | 2022-05-11 | 463932 | keep | 0 | May | 2022 | 0.31598 | 0.0025078 | Sustained | FALSE | FALSE | Not_TMED_Event | 3682
SAN JUAN | 2022-05-11 10:34 | 2022-05-11 12:45 | 922 | 002:11 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR 1401-08 QUE LLEVA A SU VEZ LA CARGA DEL 1346-05. SE ABRIO EN MH-4 Y SE CERRO INTERRUPTOR. | S22051100214 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 131 | 2022-05-11 | 120782 | keep | 0 | May | 2022 | 0.082264 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-05-11 10:34 | 2022-05-11 12:45 | 135 | 002:11 | T | PARARRAYOS DEFECTUOSO | SE ABRIO MH-4 Y SE CERRO INTERRUPTOR 100% EN SERVICIO 1401-8 ADEMAS LLEVA LA CARGA DEL 1346-05 SE RETIRARON 2 PARARRAYOS | S22051100214 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 131 | 2022-05-11 | 17685 | keep | 0 | May | 2022 | 0.012045 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
HUMACAO | 2022-05-11 10:37 | 2022-05-11 14:57 | 30 | 004:20 | P | DESGANCHE | 1 X 50 EN C/L | C22051100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2022-05-11 | 7800 | keep | 0 | May | 2022 | 0.0053125 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-05-11 10:37 | 2022-05-11 11:42 | 1 | 001:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN RISER REMPLAZO PORTAFUSIBLE QUEMADO | C22051100080 | New_Event | Cutout Failure | Include | Include | Equipment | 65 | 2022-05-11 | 65 | keep | 0 | May | 2022 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-05-11 10:40 | 2022-05-11 18:00 | 40 | 007:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | C22051100083 | New_Event |  |  | Include | Wildlife | 440 | 2022-05-11 | 17600 | keep | 0 | May | 2022 | 0.011987 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-11 10:42 | 2022-05-11 17:31 | 150 | 006:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22051100178 | New_Event | Wire Down | Include | Include | Equipment | 409 | 2022-05-11 | 61350 | keep | 0 | May | 2022 | 0.041785 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-11 10:42 | 2022-05-11 16:59 | 102 | 006:17 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22051100178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2022-05-11 | 38454 | keep | 0 | May | 2022 | 0.026191 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
MAYAGÃœEZ | 2022-05-11 10:43 | 2022-05-11 10:44 | 411 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22051100068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 411 | keep | 0 | May | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-11 10:43 | 2022-05-11 10:44 | 4381 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22051100057 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-05-11 | 4381 | keep | 0 | May | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2022-05-11 10:44 | 2022-05-11 17:53 | 40 | 007:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22051100038 | New_Event | Cutout Failure | Include | Include | Equipment | 429 | 2022-05-11 | 17160 | keep | 0 | May | 2022 | 0.011688 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-05-11 10:44 | 2022-05-11 12:22 | 50 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L AVE | B22051100180 | New_Event |  |  | Include | Wildlife | 98 | 2022-05-11 | 4900 | keep | 0 | May | 2022 | 0.0033374 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-11 10:45 | 2022-05-11 10:46 | 2076 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 1718-03 LLEVA 40% DEL 1710-05 AISLADOR ROTO EN 1718-03 | B22051100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 2076 | keep | 0 | May | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-05-11 10:45 | 2022-05-11 10:46 | 2605 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 1718-03 LLEVA 40% DEL 1710-05 | B22051100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 2605 | keep | 0 | May | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-05-11 10:46 | 2022-05-11 12:10 | 72 | 001:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 SE REMPLAZO AISLADOR | B22051100011 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 84 | 2022-05-11 | 6048 | keep | 0 | May | 2022 | 0.0041193 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
UTUADO | 2022-05-11 10:46 | 2022-05-11 16:25 | 104 | 005:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A22051100022 | New_Event | Primary Wire Break | Include | Include | Equipment | 339 | 2022-05-11 | 35256 | keep | 0 | May | 2022 | 0.024013 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
MAYAGÃœEZ | 2022-05-11 10:58 | 2022-05-11 15:30 | 1 | 004:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REQUIERE DESGANCHE | M22051100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2022-05-11 | 272 | keep | 0 | May | 2022 | 0.00018526 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-11 11:01 | 2022-05-11 11:02 | 1352 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051100073 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-11 11:01 | 2022-05-11 11:02 | 871 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | CARGA POR 6012-05 | M22051100073 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2022-05-11 11:04 | 2022-05-11 11:09 | 614 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22051100244 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-11 | 3070 | keep | 0 | May | 2022 | 0.002091 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-05-11 11:04 | 2022-05-11 11:09 | 770 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22051100244 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-11 | 3850 | keep | 0 | May | 2022 | 0.0026222 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-05-11 11:04 | 2022-05-11 11:09 | 1271 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22051100244 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-11 | 6355 | keep | 0 | May | 2022 | 0.0043284 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2022-05-11 11:04 | 2022-05-11 11:09 | 247 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22051100244 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-11 | 1235 | keep | 0 | May | 2022 | 0.00084115 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
MAYAGÃœEZ | 2022-05-11 11:09 | 2022-05-11 13:37 | 100 | 002:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051100083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-05-11 | 14800 | keep | 0 | May | 2022 | 0.01008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-11 11:13 | 2022-05-11 11:14 | 1352 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051100000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-11 11:13 | 2022-05-11 11:14 | 871 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | CARGA POR 6012-05 | M22051100000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-11 11:13 | 2022-05-11 15:32 | 40 | 004:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051100086 | New_Event | Bad Weather | Include | Include | Weather | 259 | 2022-05-11 | 10360 | keep | 0 | May | 2022 | 0.0070561 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-05-11 11:14 | 2022-05-11 12:38 | 50 | 001:24 | P | DESGANCHE | 1 X 50 EN C/L | C22051100094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-05-11 | 4200 | keep | 0 | May | 2022 | 0.0028606 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-11 11:18 | 2022-05-11 14:36 | 25 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L AVE | B22051100201 | New_Event |  |  | Include | Wildlife | 198 | 2022-05-11 | 4950 | keep | 0 | May | 2022 | 0.0033714 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-11 11:18 | 2022-05-11 11:19 | 1352 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051100094 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-11 11:18 | 2022-05-11 11:19 | 871 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | CARGA POR 6012-05 | M22051100094 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2022-05-11 11:21 | 2022-05-12 15:30 | 10 | 028:09 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR Y SE REPORTO DESGANCHE | S22051100260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1689 | 2022-05-11 | 16890 | keep | 0 | May | 2022 | 0.011504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-05-11 11:24 | 2022-05-11 14:19 | 100 | 002:55 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051100024 | New_Event | Bad Weather | Include | Include | Weather | 175 | 2022-05-11 | 17500 | keep | 0 | May | 2022 | 0.011919 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-11 11:24 | 2022-05-11 17:11 | 30 | 005:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2022-05-11 | 10410 | keep | 0 | May | 2022 | 0.0070902 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-05-11 11:25 | 2022-05-11 17:00 | 100 | 005:35 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | B22051100211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2022-05-11 | 33500 | keep | 0 | May | 2022 | 0.022817 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-11 11:30 | 2022-05-11 12:51 | 20 | 001:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO | S22051000576 | New_Event | Secondary Wire Down | Include | Include | Equipment | 81 | 2022-05-11 | 1620 | keep | 0 | May | 2022 | 0.0011034 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-11 11:33 | 2022-05-11 14:30 | 200 | 002:57 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22051100103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-05-11 | 35400 | keep | 0 | May | 2022 | 0.024111 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-11 11:39 | 2022-05-11 11:40 | 1352 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051100111 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-11 11:39 | 2022-05-11 11:40 | 871 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | CARGA POR 6012-05 | M22051100111 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-11 11:44 | 2022-05-11 11:45 | 1352 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051100115 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-11 11:44 | 2022-05-11 11:45 | 871 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | CARGA POR 6012-05 | M22051100115 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-11 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
CAGUAS | 2022-05-11 11:55 | 2022-05-11 11:56 | 2276 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 2276 | keep | 0 | May | 2022 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
BAYAMON | 2022-05-11 12:05 | 2022-05-11 12:30 | 61 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR AVERIA DEL 1720-07 SACO LINEA DEL 1705-05 DE AISLADOR, SE LLEVO A SU SITIO Y SE CERRO POR SCADA BY-220511-02. LLEVA 1707-03 | B22051100000 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2022-05-11 | 1525 | keep | 0 | May | 2022 | 0.0010387 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-05-11 12:05 | 2022-05-11 12:30 | 546 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR AVERIA DEL 1720-07 SACO LINEA DEL 1705-05 DE AISLADOR, SE LLEVO A SU SITIO Y SE CERRO POR SCADA BY-220511-02. LLEVA 1707-03 | B22051100000 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2022-05-11 | 13650 | keep | 0 | May | 2022 | 0.009297 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
CAGUAS | 2022-05-11 12:11 | 2022-05-11 14:14 | 45 | 002:03 | P | DESGANCHE | 1 X 80 EN C/L | C22051100106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-05-11 | 5535 | keep | 0 | May | 2022 | 0.0037699 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2022-05-11 12:21 | 2022-05-11 14:25 | 120 | 002:04 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051100050 | New_Event | Bad Weather | Include | Include | Weather | 124 | 2022-05-11 | 14880 | keep | 0 | May | 2022 | 0.010135 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-05-11 12:26 | 2022-05-11 14:32 | 20 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A22051100054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-05-11 | 2520 | keep | 0 | May | 2022 | 0.0017164 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-11 12:30 | 2022-05-11 12:31 | 3433 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLVEA 80% DE SU CARGA | S22051100304 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-11 | 3433 | keep | 0 | May | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
HUMACAO | 2022-05-11 12:32 | 2022-05-11 12:54 | 7 | 000:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA CONECTAR TOMA | C22051100121 | New_Event | Secondary Wire Down | Include | Include | Equipment | 22 | 2022-05-11 | 154 | keep | 0 | May | 2022 | 0.00010489 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-11 12:33 | 2022-05-11 12:35 | 723 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 Y SE CERRO POR SCADA LLEVA 1711-05 | B22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-11 | 1446 | keep | 0 | May | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-05-11 12:33 | 2022-05-11 12:35 | 1976 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 Y SE CERRO POR SCADA LLEVA 1711-05 | B22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-11 | 3952 | keep | 0 | May | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
SAN JUAN | 2022-05-11 12:35 | 2022-05-11 12:36 | 3433 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLVEA 80% DE SU CARGA | S22051100309 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-05-11 | 3433 | keep | 0 | May | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
AGUADILLA | 2022-05-11 12:35 | 2022-05-11 18:10 | 60 | 005:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22051100146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2022-05-11 | 20100 | keep | 0 | May | 2022 | 0.01369 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-11 12:45 | 2022-05-11 12:46 | 3433 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLEVA 80% DE SU CARGA | S22051100331 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-05-11 | 3433 | keep | 0 | May | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
SAN JUAN | 2022-05-11 12:45 | 2022-05-11 13:50 | 830 | 001:05 | P | PARARRAYOS DEFECTUOSO | SE RETIRO PARARRAYO AVERIADO Y SE CERRO PARTE DE LA CARGA EN MH4 DEJANDO FUERA 92 CLIENTES POR OTRO PARARRAYO AVERIADO | S22051100214 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 65 | 2022-05-11 | 53950 | keep | 0 | May | 2022 | 0.036745 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-11 12:46 | 2022-05-11 12:47 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22051100153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 108 | keep | 0 | May | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
UTUADO | 2022-05-11 12:48 | 2022-05-11 16:14 | 15 | 003:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO INFORME QUE REQUIERE DESGANCHE | A22051100065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2022-05-11 | 3090 | keep | 0 | May | 2022 | 0.0021046 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-11 12:59 | 2022-05-11 18:45 | 1352 | 005:46 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REMPLAZO AISLADORES ROTOS | M22051100161 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 346 | 2022-05-11 | 467792 | keep | 0 | May | 2022 | 0.31861 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-11 12:59 | 2022-05-11 18:45 | 871 | 005:46 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 SE REMPLAZO AISLADORES ROTOS | M22051100262 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 346 | 2022-05-11 | 301366 | keep | 0 | May | 2022 | 0.20526 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-11 12:59 | 2022-05-11 16:25 | 150 | 003:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051100160 | New_Event | Bad Weather | Include | Include | Weather | 206 | 2022-05-11 | 30900 | keep | 0 | May | 2022 | 0.021046 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-05-11 13:04 | 2022-05-11 18:50 | 25 | 005:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L Y SE REMPLAZO CAJA PRIMARIA | S22051100332 | New_Event | Cutout Failure | Include | Include | Equipment | 346 | 2022-05-11 | 8650 | keep | 0 | May | 2022 | 0.0058915 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-11 13:06 | 2022-05-11 13:07 | 3433 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLEVA 80% DE SU CARGA | S22051100335 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-05-11 | 3433 | keep | 0 | May | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
BAYAMON | 2022-05-11 13:12 | 2022-05-11 17:49 | 1 | 004:37 | P | NO SE REPORTO CAUSA | 2 X 40 EN C/L | B22051100288 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2022-05-11 | 277 | keep | 0 | May | 2022 | 0.00018866 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-11 13:13 | 2022-05-11 16:51 | 36 | 003:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZARON 2 POSTES Y TRANSFORMADOR AVERIADO POR IMPACTO DE VEHICULO DE 25 X 37.5KVA | R22051100151 | New_Event |  |  | Include | Wildlife | 218 | 2022-05-11 | 7848 | keep | 0 | May | 2022 | 0.0053452 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-05-11 13:14 | 2022-05-11 18:06 | 160 | 004:52 | P | NO SE REPORTO CAUSA | 1 X 140 EN LA SALIDA DEL CONVERTIDO | C22051100226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 292 | 2022-05-11 | 46720 | keep | 0 | May | 2022 | 0.031821 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
CAGUAS | 2022-05-11 13:14 | 2022-05-11 18:03 | 40 | 004:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PUENTE ABIERTO Y SE TRANSFIRIO PARTE DE LA CARGA AL 3006-05 | C22051100144 | New_Event | Wire Down | Include | Include | Equipment | 289 | 2022-05-11 | 11560 | keep | 0 | May | 2022 | 0.0078735 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-11 13:15 | 2022-05-11 13:16 | 3433 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLEVA 80% DE SU CARGA | S22051100345 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-05-11 | 3433 | keep | 0 | May | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
SAN JUAN | 2022-05-11 13:19 | 2022-05-11 14:03 | 3433 | 000:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR. SE REALIZARON OPERACIONES DE CAMPO Y SE CERRO POR SCADA | S22051100000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 44 | 2022-05-11 | 151052 | keep | 0 | May | 2022 | 0.10288 | 0.0023382 | Sustained | FALSE | FALSE | Not_TMED_Event | 3433
CAGUAS | 2022-05-11 13:22 | 2022-05-11 19:50 | 50 | 006:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L FIJO CONDUCTOR PRIMARIO | C22051100151 | New_Event | Wire Down | Include | Include | Equipment | 388 | 2022-05-11 | 19400 | keep | 0 | May | 2022 | 0.013213 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-11 13:27 | 2022-05-11 17:57 | 80 | 004:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051100184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-05-11 | 21600 | keep | 0 | May | 2022 | 0.014712 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-05-11 13:31 | 2022-05-11 21:00 | 47 | 007:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L Y 1 X 15 EN XMR MAL TIEMPO | C22051100155 | New_Event | Bad Weather | Include | Include | Weather | 449 | 2022-05-11 | 21103 | keep | 0 | May | 2022 | 0.014373 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
CANOVANAS | 2022-05-11 13:39 | 2022-05-11 15:38 | 120 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R22051100155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2022-05-11 | 14280 | keep | 0 | May | 2022 | 0.009726 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-05-11 13:50 | 2022-05-11 14:30 | 92 | 000:40 | P | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR 1401-08 QUE LLEVA A SU VEZ LA CARGA DEL 1346-05. SE REALIZARON MANIOBRAS DE CAMPO Y SE CERRO EN MH-4. SE REPORTA SE ELIMINO PARARRAYO AVERIADO | S22051100214 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 40 | 2022-05-11 | 3680 | keep | 0 | May | 2022 | 0.0025064 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-11 13:57 | 2022-05-11 13:58 | 2410 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 2410 | keep | 0 | May | 2022 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
SAN JUAN | 2022-05-11 14:03 | 2022-05-11 14:28 | 1716 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR. SE DESPEGO PUENTE RECOSTADO EN CRUCETA Y SE RESTABLECIO SERVICO | S22051100000 | Partial_restoration | Wire Down | Include | Include | Equipment | 25 | 2022-05-11 | 42900 | keep | 0 | May | 2022 | 0.029219 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-11 14:06 | 2022-05-11 20:20 | 21 | 006:14 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051100107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2022-05-11 | 7854 | keep | 0 | May | 2022 | 0.0053493 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-05-11 14:20 | 2022-05-11 22:41 | 10 | 008:21 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO BAJANTE SECUNDARIO SE REPARO TOMA Y SE REGULO VOLTAJE B @ D QUEDO 121 VOLTIOS | S22051100509 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 501 | 2022-05-11 | 5010 | keep | 0 | May | 2022 | 0.0034123 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-11 14:21 | 2022-05-11 16:00 | 50 | 001:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE CERRO PUENTE PRIMARIO | A22051100097 | New_Event | Wire Down | Include | Include | Equipment | 99 | 2022-05-11 | 4950 | keep | 0 | May | 2022 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-11 14:32 | 2022-05-11 21:19 | 50 | 006:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M22051100243 | New_Event | Wire Down | Include | Include | Equipment | 407 | 2022-05-11 | 20350 | keep | 0 | May | 2022 | 0.01386 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-11 14:32 | 2022-05-11 17:55 | 45 | 003:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA SE ENCONTRO GLOBO PEGADO EN LA LINEA | A22051100120 | New_Event |  |  | Include | Wildlife | 203 | 2022-05-11 | 9135 | keep | 0 | May | 2022 | 0.0062218 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-05-11 14:33 | 2022-05-11 16:02 | 30 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C22051100170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2022-05-11 | 2670 | keep | 0 | May | 2022 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-11 14:34 | 2022-05-11 19:20 | 100 | 004:46 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN CORTES DE LINEAS SE RETIRO RAMAS SOBRE LAS LINEAS | M22051100245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2022-05-11 | 28600 | keep | 0 | May | 2022 | 0.019479 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-11 14:46 | 2022-05-11 16:00 | 100 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051100256 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2022-05-11 | 7400 | keep | 0 | May | 2022 | 0.0050401 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-05-11 14:46 | 2022-05-11 19:28 | 100 | 004:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 50 EN C/L CLIENTES DESGANCHANDO | C22051100176 | New_Event |  |  | Include | Wildlife | 282 | 2022-05-11 | 28200 | keep | 0 | May | 2022 | 0.019207 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-11 14:47 | 2022-05-11 16:40 | 200 | 001:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | M22051100257 | New_Event | Wire Down | Include | Include | Equipment | 113 | 2022-05-11 | 22600 | keep | 0 | May | 2022 | 0.015393 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-05-11 14:53 | 2022-05-11 19:47 | 15 | 004:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | A22051100134 | New_Event | Secondary Wire Down | Include | Include | Equipment | 294 | 2022-05-11 | 4410 | keep | 0 | May | 2022 | 0.0030036 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-11 14:54 | 2022-05-11 19:01 | 33 | 004:07 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22051100328 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2022-05-11 | 8151 | keep | 0 | May | 2022 | 0.0055516 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2022-05-11 14:56 | 2022-05-11 18:01 | 30 | 003:05 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22051100330 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-05-11 | 5550 | keep | 0 | May | 2022 | 0.0037801 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-05-11 15:06 | 2022-05-11 19:05 | 40 | 003:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051100139 | New_Event | Bad Weather | Include | Include | Weather | 239 | 2022-05-11 | 9560 | keep | 0 | May | 2022 | 0.0065113 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-11 15:07 | 2022-05-11 19:00 | 100 | 003:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA TRONCAL | S22051100418 | New_Event | Wire Down | Include | Include | Equipment | 233 | 2022-05-11 | 23300 | keep | 0 | May | 2022 | 0.01587 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-11 15:12 | 2022-05-11 17:52 | 50 | 002:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22051100144 | New_Event | Cutout Failure | Include | Include | Equipment | 160 | 2022-05-11 | 8000 | keep | 0 | May | 2022 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-11 15:13 | 2022-05-11 16:00 | 4 | 000:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | M22051100137 | New_Event | Wire Down | Include | Include | Equipment | 47 | 2022-05-11 | 188 | keep | 0 | May | 2022 | 0.00012805 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-11 15:15 | 2022-05-12 13:06 | 1 | 021:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER REMPLAZO CAJA QUEMADA Y REPARO BAJANTE | R22051100165 | New_Event | Cutout Failure | Include | Include | Equipment | 1311 | 2022-05-11 | 1311 | keep | 0 | May | 2022 | 0.00089292 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-05-11 15:15 | 2022-05-11 21:01 | 30 | 005:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051100280 | New_Event | Bad Weather | Include | Include | Weather | 346 | 2022-05-11 | 10380 | keep | 0 | May | 2022 | 0.0070698 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-11 15:19 | 2022-05-11 19:06 | 11 | 003:47 | P | DESGANCHE | 1 X 65 EN C/L Y SE REALIZO DESGANCHE | S22051100423 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-05-11 | 2497 | keep | 0 | May | 2022 | 0.0017007 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2022-05-11 15:22 | 2022-05-11 18:08 | 50 | 002:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051100147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-05-11 | 8300 | keep | 0 | May | 2022 | 0.0056531 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-11 15:32 | 2022-05-11 16:37 | 70 | 001:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CONVERTIDOR MAL TIEMPO VIENTOS FUERTES | A22051100153 | New_Event | Bad Weather | Include | Include | Weather | 65 | 2022-05-11 | 4550 | keep | 0 | May | 2022 | 0.003099 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-05-11 15:35 | 2022-05-11 17:49 | 65 | 002:14 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B22051100339 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-05-11 | 8710 | keep | 0 | May | 2022 | 0.0059323 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-05-11 15:38 | 2022-05-11 15:39 | 3699 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE CARGA POR EL 2402-04 | R22051100000 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-11 | 3699 | keep | 0 | May | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
YAUCO | 2022-05-11 15:38 | 2022-05-11 18:29 | 2 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO SE REPORTO CAUSA | P22051100047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-05-11 | 342 | keep | 0 | May | 2022 | 0.00023293 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-05-11 15:39 | 2022-05-11 16:33 | 100 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | R22051100162 | 1st_after_momentary |  |  | Include | Wildlife | 54 | 2022-05-11 | 5400 | keep | 0 | May | 2022 | 0.0036779 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-11 15:39 | 2022-05-11 15:52 | 120 | 000:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R22051100155 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-05-11 | 1560 | keep | 0 | May | 2022 | 0.0010625 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-11 15:39 | 2022-05-11 19:51 | 47 | 004:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L FIJO CONDUCTOR AL PIN | C22051100197 | New_Event | Wire Down | Include | Include | Equipment | 252 | 2022-05-11 | 11844 | keep | 0 | May | 2022 | 0.0080669 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2022-05-11 15:42 | 2022-05-11 18:02 | 18 | 002:20 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO Y REPARO LINEA PRIMARIA | C22051100198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-05-11 | 2520 | keep | 0 | May | 2022 | 0.0017164 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-05-11 15:48 | 2022-05-11 19:00 | 39 | 003:12 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR NO HAY RTU. SE CERRO MANUALMENTE. MAL TIEMPO VIENTOS FUERTES | M22051100314 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2022-05-11 | 7488 | keep | 0 | May | 2022 | 0.0051 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CANOVANAS | 2022-05-11 15:52 | 2022-05-11 16:05 | 9 | 000:13 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22051100168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-05-11 | 117 | keep | 0 | May | 2022 | 7.9688e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2022-05-11 15:59 | 2022-05-12 10:49 | 5 | 018:50 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | C22051100204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1130 | 2022-05-11 | 5650 | keep | 0 | May | 2022 | 0.0038482 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-11 16:00 | 2022-05-12 11:00 | 100 | 019:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051100325 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1140 | 2022-05-11 | 114000 | keep | 0 | May | 2022 | 0.077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-11 16:07 | 2022-05-11 21:56 | 100 | 005:49 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO AEREO PROVISIONAL LA TERMINACION , SE REEMPLAZO SMU 20 DE 80 EN SU 4 HACIA LOS AEREOS PROVIONALES Y LA BASE DEL SMU 20 ESTA QUEMADA SE CAMBIO BASE A LA DEL AL LADO | S22051100430 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 349 | 2022-05-11 | 34900 | keep | 0 | May | 2022 | 0.02377 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-11 16:09 | 2022-05-11 19:07 | 100 | 002:58 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S22051100431 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-05-11 | 17800 | keep | 0 | May | 2022 | 0.012123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-11 16:11 | 2022-05-12 12:09 | 40 | 019:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051100336 | New_Event | Bad Weather | Include | Include | Weather | 1198 | 2022-05-11 | 47920 | keep | 0 | May | 2022 | 0.032638 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-05-11 16:14 | 2022-05-11 19:00 | 1 | 002:46 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 25 AMP | C22051100211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-05-11 | 166 | keep | 0 | May | 2022 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-11 16:14 | 2022-05-11 18:45 | 228 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22051100350 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2022-05-11 | 34428 | keep | 0 | May | 2022 | 0.023449 | 0.00015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 228
UTUADO | 2022-05-11 16:16 | 2022-05-11 18:30 | 100 | 002:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE ENCONTRO CONDUCTORES CRUZADOS | A22051100171 | New_Event | Wire Down | Include | Include | Equipment | 134 | 2022-05-11 | 13400 | keep | 0 | May | 2022 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-11 16:23 | 2022-05-11 19:30 | 10 | 003:07 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR Y SE REALIZO DESGACHE SECUNDARIO | S22051100434 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 187 | 2022-05-11 | 1870 | keep | 0 | May | 2022 | 0.0012736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-11 16:23 | 2022-05-11 20:00 | 40 | 003:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE INFORMO QUE REQUIERE DESGANCHE | A22051100173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-05-11 | 8680 | keep | 0 | May | 2022 | 0.0059119 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-05-11 16:24 | 2022-05-11 19:57 | 70 | 003:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051100343 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-05-11 | 14910 | keep | 0 | May | 2022 | 0.010155 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-05-11 16:31 | 2022-05-11 16:32 | 1222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | A22051100175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 1222 | keep | 0 | May | 2022 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
UTUADO | 2022-05-11 16:33 | 2022-05-12 14:28 | 10 | 021:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA | A22051200063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1315 | 2022-05-11 | 13150 | keep | 0 | May | 2022 | 0.0089564 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-11 16:35 | 2022-05-11 21:26 | 6 | 004:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051100349 | New_Event | Bad Weather | Include | Include | Weather | 291 | 2022-05-11 | 1746 | keep | 0 | May | 2022 | 0.0011892 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-05-11 16:37 | 2022-05-11 16:38 | 1527 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | A22051100178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 1527 | keep | 0 | May | 2022 | 0.00104 | 0.00104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1527
CANOVANAS | 2022-05-11 16:38 | 2022-05-11 19:00 | 133 | 002:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R22051100170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-05-11 | 18886 | keep | 0 | May | 2022 | 0.012863 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
UTUADO | 2022-05-11 16:38 | 2022-05-11 17:32 | 45 | 000:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | A22051100181 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 54 | 2022-05-11 | 2430 | keep | 0 | May | 2022 | 0.0016551 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-05-11 16:39 | 2022-05-11 17:18 | 12 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22051100104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-05-11 | 468 | keep | 0 | May | 2022 | 0.00031875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-11 16:47 | 2022-05-11 19:08 | 80 | 002:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EM C/L SE REMPLAZO CAJA QUEMADA EN C/L | P22051100061 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2022-05-11 | 11280 | keep | 0 | May | 2022 | 0.0076828 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-05-11 16:49 | 2022-05-11 19:55 | 40 | 003:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L LEVANTO CONDUCTOR PRIMARIO | C22051100224 | New_Event | Wire Down | Include | Include | Equipment | 186 | 2022-05-11 | 7440 | keep | 0 | May | 2022 | 0.0050674 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-11 16:50 | 2022-05-12 10:56 | 100 | 018:06 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REFIRIO PARA REALIZAR DESGANCHE EN VARIOS PUNTOS | M22051100364 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1086 | 2022-05-11 | 108600 | keep | 0 | May | 2022 | 0.073967 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-11 17:11 | 2022-05-12 14:41 | 7 | 021:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REPARO SECUNDARIA | C22051100228 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1290 | 2022-05-11 | 9030 | keep | 0 | May | 2022 | 0.0061503 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2022-05-11 17:11 | 2022-05-11 21:14 | 25 | 004:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN C/L MAL TIEMPO | P22051100063 | New_Event | Bad Weather | Include | Include | Weather | 243 | 2022-05-11 | 6075 | keep | 0 | May | 2022 | 0.0041377 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-05-11 17:16 | 2022-05-12 16:20 | 4 | 023:04 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C22051100229 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1384 | 2022-05-11 | 5536 | keep | 0 | May | 2022 | 0.0037705 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2022-05-11 17:26 | 2022-05-11 18:21 | 38 | 000:55 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R22051100173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-05-11 | 2090 | keep | 0 | May | 2022 | 0.0014235 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
MAYAGÃœEZ | 2022-05-11 17:39 | 2022-05-11 23:15 | 30 | 005:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22051100413 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2022-05-11 | 10080 | keep | 0 | May | 2022 | 0.0068654 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-05-11 17:46 | 2022-05-11 17:47 | 4132 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE SE FIJO BAJANTE EN C/L LA CARGA POR EL 4006-05 | P22051100065 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-11 | 4132 | keep | 0 | May | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-05-11 17:46 | 2022-05-11 17:47 | 4279 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE SE FIJO BAJANTE EN C/L LA CARGA POR EL 4006-05 | P22051100065 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-11 | 4279 | keep | 0 | May | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-05-11 17:46 | 2022-05-11 17:47 | 464 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE SE FIJO BAJANTE EN C/L LLEVA LA CARGA DEL 7003-01 Y 4003-02 | P22051100065 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-11 | 464 | keep | 0 | May | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
BAYAMON | 2022-05-11 17:46 | 2022-05-11 19:06 | 6 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE | B22051100371 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2022-05-11 | 480 | keep | 0 | May | 2022 | 0.00032693 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-05-11 17:47 | 2022-05-11 18:40 | 25 | 000:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE FIJO BAJANTE SAFADO EN C/L | P22051100068 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 53 | 2022-05-11 | 1325 | keep | 0 | May | 2022 | 0.00090245 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-05-11 17:50 | 2022-05-11 17:56 | 75 | 000:06 | P | DESGANCHE | 1 X 80 EN C/L | C22051100237 | New_Event | Vegetation Contact | Include | Include | Vegetation | 6 | 2022-05-11 | 450 | keep | 0 | May | 2022 | 0.00030649 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-05-11 17:51 | 2022-05-12 12:00 | 17 | 018:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REFIRIO PARA REALIZAR DESGANCHE PREVENTIVO EN EL AREA | M22051100423 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1089 | 2022-05-11 | 18513 | keep | 0 | May | 2022 | 0.012609 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2022-05-11 18:00 | 2022-05-11 18:01 | 100 | 000:01 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22051100267 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-11 | 100 | keep | 0 | May | 2022 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-05-11 18:13 | 2022-05-11 19:34 | 8 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ENDEREZO POSTE SECUNDARIO Y SE LEVANTO LINEA SECUNDARIA DEL SUELO DERRIBADA POR CAMION PRIVADO | R22051100176 | New_Event |  |  | Include | Wildlife | 81 | 2022-05-11 | 648 | keep | 0 | May | 2022 | 0.00044135 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-05-11 18:14 | 2022-05-11 18:15 | 2888 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | A22051100199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 2888 | keep | 0 | May | 2022 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
ARECIBO | 2022-05-11 18:15 | 2022-05-12 07:50 | 20 | 013:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051100197 | New_Event | Bad Weather | Include | Include | Weather | 815 | 2022-05-11 | 16300 | keep | 0 | May | 2022 | 0.011102 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-11 18:20 | 2022-05-12 11:58 | 60 | 017:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS VERIFICADO EN OMS EVENTO ES CORRECTO PERTENCE A ISABELA | A22051100201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1058 | 2022-05-11 | 63480 | keep | 0 | May | 2022 | 0.043236 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-05-11 18:31 | 2022-05-11 20:35 | 38 | 002:04 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN CORTE DE LINEA SE REEMPLAZARON PARARRAYOS QUEMADOS | R22051100179 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 124 | 2022-05-11 | 4712 | keep | 0 | May | 2022 | 0.0032093 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CAGUAS | 2022-05-11 18:44 | 2022-05-12 09:15 | 59 | 014:31 | P | DESGANCHE | 1 X 40 EN C/L | C22051100248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 871 | 2022-05-11 | 51389 | keep | 0 | May | 2022 | 0.035001 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
CAGUAS | 2022-05-11 18:44 | 2022-05-11 21:39 | 50 | 002:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C22051100248 | New_Event | Bad Weather | Include | Include | Weather | 175 | 2022-05-11 | 8750 | keep | 0 | May | 2022 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-11 18:45 | 2022-05-11 22:24 | 60 | 003:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051100447 | New_Event | Bad Weather | Include | Include | Weather | 219 | 2022-05-11 | 13140 | keep | 0 | May | 2022 | 0.0089496 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-11 19:00 | 2022-05-11 20:46 | 30 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN C/L Y SE CERRO PUENTE | B22051100353 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2022-05-11 | 3180 | keep | 0 | May | 2022 | 0.0021659 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-11 19:02 | 2022-05-12 02:05 | 40 | 007:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22051100458 | New_Event | Vegetation Contact | Include | Include | Vegetation | 423 | 2022-05-11 | 16920 | keep | 0 | May | 2022 | 0.011524 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-11 19:08 | 2022-05-11 20:05 | 50 | 000:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO PORTAFUSIBLE | S22051100491 | New_Event | Cutout Failure | Include | Include | Equipment | 57 | 2022-05-11 | 2850 | keep | 0 | May | 2022 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-11 19:20 | 2022-05-12 16:30 | 10 | 021:10 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR Y SE REALIZO DESGANCHE PRIMARIO | S22051100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1270 | 2022-05-11 | 12700 | keep | 0 | May | 2022 | 0.0086499 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-11 19:24 | 2022-05-11 22:52 | 8 | 003:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | R22051100184 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2022-05-11 | 1664 | keep | 0 | May | 2022 | 0.0011333 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-05-11 19:24 | 2022-05-11 21:03 | 6 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22051100183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-05-11 | 594 | keep | 0 | May | 2022 | 0.00040457 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-11 19:25 | 2022-05-12 11:56 | 90 | 016:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051100467 | New_Event | Bad Weather | Include | Include | Weather | 991 | 2022-05-11 | 89190 | keep | 0 | May | 2022 | 0.060747 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-05-11 19:28 | 2022-05-12 10:41 | 483 | 015:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L REEMPLAZO CAJA QUEMADA EN LA SALIDA DEL CONVERTIDOR | C22051100257 | New_Event | Cutout Failure | Include | Include | Equipment | 913 | 2022-05-11 | 440979 | keep | 0 | May | 2022 | 0.30035 | 0.00032897 | Sustained | FALSE | FALSE | Not_TMED_Event | 483
GUAYAMA | 2022-05-11 19:37 | 2022-05-12 09:35 | 50 | 013:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEA ARRIADA | P22051100079 | New_Event | Wire Down | Include | Include | Equipment | 838 | 2022-05-11 | 41900 | keep | 0 | May | 2022 | 0.028538 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-11 19:53 | 2022-05-11 22:58 | 150 | 003:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22051100214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-05-11 | 27750 | keep | 0 | May | 2022 | 0.0189 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-05-11 20:02 | 2022-05-12 09:56 | 55 | 013:54 | P | DESGANCHE | 1 X 50 EN C/L | C22051100263 | New_Event | Vegetation Contact | Include | Include | Vegetation | 834 | 2022-05-11 | 45870 | keep | 0 | May | 2022 | 0.031242 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2022-05-11 20:02 | 2022-05-12 09:06 | 30 | 013:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051100215 | New_Event | Bad Weather | Include | Include | Weather | 784 | 2022-05-11 | 23520 | keep | 0 | May | 2022 | 0.016019 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-11 20:04 | 2022-05-11 20:05 | 638 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051100272 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 638 | keep | 0 | May | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2022-05-11 20:04 | 2022-05-11 20:07 | 4634 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22051100265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-11 | 13902 | keep | 0 | May | 2022 | 0.0094686 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-05-11 20:18 | 2022-05-12 10:03 | 65 | 013:45 | P | NO SE REPORTO CAUSA | 1 X 80 C/L NO CAUSA | C22051100275 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 825 | 2022-05-11 | 53625 | keep | 0 | May | 2022 | 0.036524 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-05-11 20:25 | 2022-05-12 03:09 | 20 | 006:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22051100482 | New_Event | Vegetation Contact | Include | Include | Vegetation | 404 | 2022-05-11 | 8080 | keep | 0 | May | 2022 | 0.0055033 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-05-11 20:34 | 2022-05-11 23:44 | 337 | 003:10 | P | DESGANCHE | 1 X 200 EN C/L DESGANCHE | P22051100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-05-11 | 64030 | keep | 0 | May | 2022 | 0.043611 | 0.00022953 | Sustained | FALSE | FALSE | Not_TMED_Event | 337
ARECIBO | 2022-05-11 20:53 | 2022-05-11 20:55 | 3654 | 000:02 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | A22051100221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-11 | 7308 | keep | 0 | May | 2022 | 0.0049774 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
ARECIBO | 2022-05-11 20:55 | 2022-05-11 23:43 | 200 | 002:48 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22051100224 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-05-11 | 33600 | keep | 0 | May | 2022 | 0.022885 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-11 21:03 | 2022-05-12 05:24 | 50 | 008:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22051100492 | New_Event | Vegetation Contact | Include | Include | Vegetation | 501 | 2022-05-11 | 25050 | keep | 0 | May | 2022 | 0.017061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-11 21:06 | 2022-05-12 11:00 | 23 | 013:54 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO TERMINACION Y CABLE SE ENERGIZO PROVISIONAL A T-20 | S22051100528 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 834 | 2022-05-11 | 19182 | keep | 0 | May | 2022 | 0.013065 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BARRANQUITAS | 2022-05-11 21:26 | 2022-05-12 09:16 | 105 | 011:50 | P | DESGANCHE | 2 X 50 EN C/L | C22051100302 | New_Event | Vegetation Contact | Include | Include | Vegetation | 710 | 2022-05-11 | 74550 | keep | 0 | May | 2022 | 0.050776 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
VEGA BAJA | 2022-05-11 21:27 | 2022-05-12 07:16 | 79 | 009:49 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 30 EN C/L | B22051100387 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 589 | 2022-05-11 | 46531 | keep | 0 | May | 2022 | 0.031692 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
PONCE | 2022-05-11 21:33 | 2022-05-12 06:50 | 50 | 009:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 1 X 40 EN CORTE DE LINEA PAJARO CRUZO FASE | P22051100099 | New_Event |  |  | Include | Wildlife | 557 | 2022-05-11 | 27850 | keep | 0 | May | 2022 | 0.018969 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-11 21:45 | 2022-05-12 11:10 | 30 | 013:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | A22051100235 | New_Event | Cutout Failure | Include | Include | Equipment | 805 | 2022-05-11 | 24150 | keep | 0 | May | 2022 | 0.016448 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-05-11 22:14 | 2022-05-11 22:15 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE NO CAUSA | P220511000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-11 | 215 | keep | 0 | May | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
HUMACAO | 2022-05-11 22:16 | 2022-05-12 13:38 | 7 | 015:22 | P | DESGANCHE | 2 X 65 Y 2 X 80 EN C/L | C22051100200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 922 | 2022-05-11 | 6454 | keep | 0 | May | 2022 | 0.0043958 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-05-11 22:19 | 2022-05-11 23:50 | 14 | 001:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR CONTAMINACION EN CAJA PRIMARIA | R22051100201 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2022-05-11 | 1274 | keep | 0 | May | 2022 | 0.00086772 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-05-11 22:41 | 2022-05-12 01:39 | 1420 | 002:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR EN EL SUELO PERTENECIENTE A 1530-07 Y SE CERRO MACHETES. CARGA DE 1526-02 POR 1530-07 | S22051100537 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2022-05-11 | 252760 | keep | 0 | May | 2022 | 0.17215 | 0.00096716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-05-11 22:41 | 2022-05-12 01:39 | 437 | 002:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR EN EL SUELO PERTENECIENTE A 1530-07 Y SE CERRO MACHETES CARGA DE 1530-06 POR 1530-07 | S22051100537 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2022-05-11 | 77786 | keep | 0 | May | 2022 | 0.05298 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-05-11 22:41 | 2022-05-12 00:05 | 643 | 001:24 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1530-07 LLEVANDO CARGA 1526-02 Y 1530-06. SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO POR CONTROL. SOLO ENTRO 10% DE 1530-07 | S22051100537 | New_Event | Wire Down | Include | Include | Equipment | 84 | 2022-05-11 | 54012 | keep | 0 | May | 2022 | 0.036787 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
SAN JUAN | 2022-05-11 23:10 | 2022-05-12 13:42 | 50 | 014:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESPEJO SU-10 Y 1 X 80 SMU-20 | S22051100575 | New_Event | Vegetation Contact | Include | Include | Vegetation | 872 | 2022-05-11 | 43600 | keep | 0 | May | 2022 | 0.029696 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-11 23:58 | 2022-05-12 13:40 | 40 | 013:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S22051100597 | New_Event | Cutout Failure | Include | Include | Equipment | 822 | 2022-05-11 | 32880 | keep | 0 | May | 2022 | 0.022394 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-12 00:02 | 2022-05-12 00:03 | 2859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22051200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 2859 | keep | 0 | May | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
BAYAMON | 2022-05-12 00:05 | 2022-05-12 01:39 | 579 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRO MACHETES | S22051100537 | Partial_restoration | Wire Down | Include | Include | Equipment | 94 | 2022-05-12 | 54426 | keep | 0 | May | 2022 | 0.037069 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-12 01:37 | 2022-05-12 10:58 | 12 | 009:21 | P | TERMINACION SOTERRADA AVERIADA | 2 X 50 EN RISER TERMINACION EN SU-7 | B22051200002 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 561 | 2022-05-12 | 6732 | keep | 0 | May | 2022 | 0.0045851 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-05-12 01:39 | 2022-05-13 16:48 | 10 | 039:09 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO BAJANTE SECUNDARIO SE REPARO TOMA Y SE REGULO VOLTAJE B @ D QUEDO 121 VOLTIOS | S22051100509 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2349 | 2022-05-12 | 23490 | keep | 0 | May | 2022 | 0.015999 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-05-12 02:04 | 2022-05-12 02:05 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 2696 | keep | 0 | May | 2022 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
BAYAMON | 2022-05-12 02:14 | 2022-05-12 09:15 | 40 | 007:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22051200013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 421 | 2022-05-12 | 16840 | keep | 0 | May | 2022 | 0.01147 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-05-12 02:32 | 2022-05-12 02:35 | 4702 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B22051200003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-12 | 14106 | keep | 0 | May | 2022 | 0.0096075 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2022-05-12 02:39 | 2022-05-12 11:15 | 85 | 008:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN CONVERTIDOR 1 X 10 EN XMR Y 1 X 80 RISER | B22051200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 516 | 2022-05-12 | 43860 | keep | 0 | May | 2022 | 0.029873 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CANOVANAS | 2022-05-12 02:52 | 2022-05-12 12:36 | 15 | 009:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REEMPLAZO CAJA PRIMARIA DE XMR | R22051200002 | New_Event | Cutout Failure | Include | Include | Equipment | 584 | 2022-05-12 | 8760 | keep | 0 | May | 2022 | 0.0059664 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-05-12 03:01 | 2022-05-12 10:37 | 65 | 007:36 | P | DESGANCHE | 1 X 100 EN C/L | R22051200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 456 | 2022-05-12 | 29640 | keep | 0 | May | 2022 | 0.020188 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-05-12 03:02 | 2022-05-12 14:29 | 60 | 011:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051200005 | New_Event | Bad Weather | Include | Include | Weather | 687 | 2022-05-12 | 41220 | keep | 0 | May | 2022 | 0.028075 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-05-12 03:22 | 2022-05-12 08:43 | 118 | 005:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C22051200003 | New_Event |  |  | Include | Wildlife | 321 | 2022-05-12 | 37878 | keep | 0 | May | 2022 | 0.025799 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
VEGA BAJA | 2022-05-12 03:27 | 2022-05-12 13:21 | 2468 | 009:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRO C/L | B22051200057 | New_Event | Wire Down | Include | Include | Equipment | 594 | 2022-05-12 | 1465992 | keep | 0 | May | 2022 | 0.99848 | 0.0016809 | Sustained | FALSE | FALSE | Not_TMED_Event | 2468
ARECIBO | 2022-05-12 04:05 | 2022-05-12 09:45 | 30 | 005:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051200003 | New_Event | Bad Weather | Include | Include | Weather | 340 | 2022-05-12 | 10200 | keep | 0 | May | 2022 | 0.0069472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-05-12 04:39 | 2022-05-12 04:40 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 3973 | keep | 0 | May | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
FAJARDO | 2022-05-12 05:10 | 2022-05-12 09:45 | 50 | 004:35 | P | DESGANCHE | 1 X 50 C/L | R22051200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2022-05-12 | 13750 | keep | 0 | May | 2022 | 0.0093651 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-05-12 05:16 | 2022-05-12 14:34 | 130 | 009:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR SE REEMPLAZARON CAJAS QUEMADAS | R22051200013 | New_Event | Cutout Failure | Include | Include | Equipment | 558 | 2022-05-12 | 72540 | keep | 0 | May | 2022 | 0.049407 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
AGUADILLA | 2022-05-12 05:37 | 2022-05-12 09:33 | 80 | 003:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-05-12 | 18880 | keep | 0 | May | 2022 | 0.012859 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-12 05:51 | 2022-05-12 05:52 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 312 | keep | 0 | May | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
HUMACAO | 2022-05-12 05:52 | 2022-05-12 05:53 | 1530 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR 65% DE SU CARGA POR 2604-03 | C22051200000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-05-12 | 1530 | keep | 0 | May | 2022 | 0.0010421 | 0.0010421 | Momentary | FALSE | FALSE | Not_TMED_Event | 1530
HUMACAO | 2022-05-12 05:52 | 2022-05-12 05:53 | 1593 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR EN SERVICIO | C22051200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-12 | 1593 | keep | 0 | May | 2022 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2022-05-12 05:53 | 2022-05-12 10:17 | 88 | 004:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L LEVANTO NEUTRAL PRIMARIO | C22051200012 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 264 | 2022-05-12 | 23232 | keep | 0 | May | 2022 | 0.015823 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
VEGA BAJA | 2022-05-12 05:57 | 2022-05-12 05:58 | 603 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9206-08 LLEVA 9206-09 | B22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 603 | keep | 0 | May | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-05-12 05:57 | 2022-05-12 05:58 | 6 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9206-08 LLEVA 9206-09 | B22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 6 | keep | 0 | May | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-12 06:24 | 2022-05-12 09:21 | 100 | 002:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REFIRIO PARA REALIZAR DESGANCHE EN VARIOS PUNTOS | M22051200020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-05-12 | 17700 | keep | 0 | May | 2022 | 0.012055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-05-12 06:48 | 2022-05-12 07:35 | 60 | 000:47 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | B22051200022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2022-05-12 | 2820 | keep | 0 | May | 2022 | 0.0019207 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-05-12 06:50 | 2022-05-12 07:17 | 55 | 000:27 | P | DESGANCHE | 1 X 50 EN C/L | C22051200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2022-05-12 | 1485 | keep | 0 | May | 2022 | 0.0010114 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
PONCE | 2022-05-12 07:01 | 2022-05-12 10:36 | 43 | 003:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE VERIFICADO EN BITACORA Y OMS EL EVENTO | P22051200010 | New_Event |  |  | Include | Wildlife | 215 | 2022-05-12 | 9245 | keep | 0 | May | 2022 | 0.0062967 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-05-12 07:02 | 2022-05-12 07:04 | 17 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-12 | 34 | keep | 0 | May | 2022 | 2.3157e-05 | 1.1579e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2022-05-12 07:06 | 2022-05-12 07:07 | 5630 | 000:01 | T | ANIMAL | RECIERRE | C22051200022 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-12 | 5630 | keep | 0 | May | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-05-12 07:07 | 2022-05-12 11:08 | 71 | 004:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN C/L CRUCE X AVE | C22051200050 | New_Event |  |  | Include | Wildlife | 241 | 2022-05-12 | 17111 | keep | 0 | May | 2022 | 0.011654 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
HUMACAO | 2022-05-12 07:17 | 2022-05-12 07:19 | 1089 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-12 | 2178 | keep | 0 | May | 2022 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-05-12 07:17 | 2022-05-12 07:19 | 3896 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-12 | 7792 | keep | 0 | May | 2022 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-05-12 07:17 | 2022-05-12 07:19 | 1467 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-12 | 2934 | keep | 0 | May | 2022 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
PONCE | 2022-05-12 07:17 | 2022-05-12 20:05 | 12 | 012:48 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO BARRA SECA PRIMARIA Y PISTOLA 200 AMPERES | P22051200012 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 768 | 2022-05-12 | 9216 | keep | 0 | May | 2022 | 0.006277 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-05-12 07:19 | 2022-05-12 09:47 | 55 | 002:28 | P | DESGANCHE | 1 X 50 EN C/L | C22051200018 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-05-12 | 8140 | keep | 0 | May | 2022 | 0.0055441 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-12 07:26 | 2022-05-12 13:38 | 5 | 006:12 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051200036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2022-05-12 | 1860 | keep | 0 | May | 2022 | 0.0012668 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-12 07:35 | 2022-05-12 11:47 | 40 | 004:12 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2022-05-12 | 10080 | keep | 0 | May | 2022 | 0.0068654 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-12 07:38 | 2022-05-12 09:19 | 50 | 001:41 | P | CABLE SOTERRADO AVERIADO | DISPARO DEL 1117-07 SE ABRIO DE V.S.2 Y SE CERRO 1117-7 | S22051200040 | New_Event | UG Cable Fault | Include | Include | Equipment | 101 | 2022-05-12 | 5050 | keep | 0 | May | 2022 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-12 07:44 | 2022-05-12 07:45 | 513 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 20% POR 1118-10 SE PROBO QUEDO EN SERVICIO | S22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 513 | keep | 0 | May | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-05-12 07:44 | 2022-05-12 07:45 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 20% DEL 1111-1 SE PROBO QUEDO EN SERVICIO | S22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 2782 | keep | 0 | May | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
YAUCO | 2022-05-12 07:44 | 2022-05-13 14:30 | 131 | 030:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA SE ESPARO POR PROBLEMAS DE ABEJAS EN EL AREA Y PERSONAL DE DESGANCHE | P22051200017 | New_Event | Primary Wire Break | Include | Include | Equipment | 1846 | 2022-05-12 | 241826 | keep | 0 | May | 2022 | 0.16471 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2022-05-12 07:51 | 2022-05-12 11:15 | 18 | 003:24 | P | DESGANCHE | 1 X 30 EN C/L | C22051200040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-05-12 | 3672 | keep | 0 | May | 2022 | 0.002501 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-05-12 07:55 | 2022-05-12 09:50 | 5 | 001:55 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE | C22051200044 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 115 | 2022-05-12 | 575 | keep | 0 | May | 2022 | 0.00039163 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-05-12 08:03 | 2022-05-12 11:04 | 1 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | R22051200033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-05-12 | 181 | keep | 0 | May | 2022 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-05-12 08:14 | 2022-05-12 16:09 | 1 | 007:55 | P | DESGANCHE | 1 X 40 EN C/L | C22051200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2022-05-12 | 475 | keep | 0 | May | 2022 | 0.00032352 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-12 08:37 | 2022-05-12 12:07 | 6 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22051200058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2022-05-12 | 1260 | keep | 0 | May | 2022 | 0.00085818 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-05-12 08:41 | 2022-05-12 10:46 | 10 | 002:05 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR PARA CONECTAR SECUNDARIA NUEVA PARA SERVICIO NUEVO | A22051200011 | New_Event | Other Causes | Include | Include | Other | 125 | 2022-05-12 | 1250 | keep | 0 | May | 2022 | 0.00085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-12 08:47 | 2022-05-12 13:29 | 177 | 004:42 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | S22051200059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 282 | 2022-05-12 | 49914 | keep | 0 | May | 2022 | 0.033996 | 0.00012055 | Sustained | FALSE | FALSE | Not_TMED_Event | 177
BAYAMON | 2022-05-12 08:50 | 2022-05-12 08:51 | 4431 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | B22051200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-12 | 4431 | keep | 0 | May | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2022-05-12 08:51 | 2022-05-12 15:23 | 80 | 006:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22051200039 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 392 | 2022-05-12 | 31360 | keep | 0 | May | 2022 | 0.021359 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-05-12 09:04 | 2022-05-12 16:02 | 4 | 006:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON BARRAS EN PEDESTAL | R22051200042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 418 | 2022-05-12 | 1672 | keep | 0 | May | 2022 | 0.0011388 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-05-12 09:07 | 2022-05-12 12:30 | 200 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051200080 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2022-05-12 | 40600 | keep | 0 | May | 2022 | 0.027652 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-05-12 09:07 | 2022-05-12 11:20 | 30 | 002:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE ASEGURO BAJANTE ZAFADO DE LINEA A CAJA DE TRANSFORMADOR SE REPARA POR OTRO GRUPO | A22051200024 | New_Event | Wire Down | Include | Include | Equipment | 133 | 2022-05-12 | 3990 | keep | 0 | May | 2022 | 0.0027176 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-05-12 09:12 | 2022-05-12 13:13 | 50 | 004:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22051200042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2022-05-12 | 12050 | keep | 0 | May | 2022 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-12 09:19 | 2022-05-12 09:39 | 50 | 000:20 | P | CABLE SOTERRADO AVERIADO | AL CERRAR DE V.S.2 A V.S.4 DISPARO ALIMENTADOR SE DEJO FUERA TRAMO | S22051200040 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 20 | 2022-05-12 | 1000 | keep | 0 | May | 2022 | 0.0006811 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-05-12 09:19 | 2022-05-12 16:05 | 100 | 006:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22051200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 406 | 2022-05-12 | 40600 | keep | 0 | May | 2022 | 0.027652 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-05-12 09:29 | 2022-05-12 13:08 | 7 | 003:39 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C22051200080 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 219 | 2022-05-12 | 1533 | keep | 0 | May | 2022 | 0.0010441 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-05-12 09:30 | 2022-05-12 13:09 | 12 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A22051200025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-05-12 | 2628 | keep | 0 | May | 2022 | 0.0017899 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-12 09:36 | 2022-05-12 10:41 | 6 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 C/L CRUCE POR AVE | C22051200083 | New_Event |  |  | Include | Wildlife | 65 | 2022-05-12 | 390 | keep | 0 | May | 2022 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-12 09:38 | 2022-05-12 14:30 | 50 | 004:52 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L Y SE RETIRO PARARRAYO Y SE RETEZO LINEA | B22051200054 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 292 | 2022-05-12 | 14600 | keep | 0 | May | 2022 | 0.009944 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-12 09:39 | 2022-05-12 09:40 | 50 | 000:01 | P | CABLE SOTERRADO AVERIADO | AL CERRAR DE V.S.2 A V.S.4 DISPARO ALIMENTADOR SE DEJO FUERA TRAMO | S22051200040 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1 | 2022-05-12 | 50 | keep | 0 | May | 2022 | 3.4055e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-05-12 09:39 | 2022-05-12 12:18 | 1 | 002:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN RISER CULEBRA CRUZO FASE | P22051200028 | New_Event |  |  | Include | Wildlife | 159 | 2022-05-12 | 159 | keep | 0 | May | 2022 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-12 09:40 | 2022-05-12 18:34 | 20 | 008:54 | P | CABLE SOTERRADO AVERIADO | SE REALIZO BY-PASS DEL VS-3 Y SE RESTABLECIÃ“ SERVICIO | S22051200040 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 534 | 2022-05-12 | 10680 | keep | 0 | May | 2022 | 0.0072741 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-12 09:56 | 2022-05-12 11:41 | 1 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22051200086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-05-12 | 105 | keep | 0 | May | 2022 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-12 10:06 | 2022-05-12 10:21 | 50 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22051200104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-05-12 | 750 | keep | 0 | May | 2022 | 0.00051082 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-12 10:18 | 2022-05-12 10:19 | 2067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22051200111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 2067 | keep | 0 | May | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
CAGUAS | 2022-05-12 10:27 | 2022-05-12 12:16 | 1 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22051200098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-05-12 | 109 | keep | 0 | May | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-12 10:35 | 2022-05-12 14:00 | 30 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | A22051200034 | New_Event | Bad Weather | Include | Include | Weather | 205 | 2022-05-12 | 6150 | keep | 0 | May | 2022 | 0.0041887 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-12 10:44 | 2022-05-13 00:23 | 11 | 013:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE LEVANTO SECUNDARIA Y SE DESGANCHO | S22051200263 | New_Event | Secondary Wire Down | Include | Include | Equipment | 819 | 2022-05-12 | 9009 | keep | 0 | May | 2022 | 0.006136 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2022-05-12 10:49 | 2022-05-12 15:29 | 11 | 004:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22051200040 | New_Event | Cutout Failure | Include | Include | Equipment | 280 | 2022-05-12 | 3080 | keep | 0 | May | 2022 | 0.0020978 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-05-12 11:02 | 2022-05-12 15:13 | 2 | 004:11 | P | SECUNDARIA/DESGANCHE | 2 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22051200132 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 251 | 2022-05-12 | 502 | keep | 0 | May | 2022 | 0.00034191 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-05-12 11:03 | 2022-05-12 12:52 | 1 | 001:49 | P | OTRAS CAUSAS | 1 X 15 EN RISER REPLAZO PORTAFUSIBLE QUEMADO PROBLEMA DEL CLIENTE | R22051200061 | New_Event | Other Causes | Include | Include | Other | 109 | 2022-05-12 | 109 | keep | 0 | May | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-12 11:09 | 2022-05-12 16:11 | 21 | 005:02 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFOPRMADOR PARA DESPEJAR LINEA SECUNDARIA | S22051200073 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 302 | 2022-05-12 | 6342 | keep | 0 | May | 2022 | 0.0043195 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2022-05-12 11:11 | 2022-05-12 15:02 | 80 | 003:51 | P | CABLE SOTERRADO AVERIADO | SE REALIZO JUMPER EN SU-5 Y SE REFIRIO PARA REPARAR CABLE SOTERRADO AVERIADO | S22051200121 | New_Event | UG Cable Fault | Include | Include | Equipment | 231 | 2022-05-12 | 18480 | keep | 0 | May | 2022 | 0.012587 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-05-12 11:14 | 2022-05-12 12:45 | 50 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051200048 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2022-05-12 | 4550 | keep | 0 | May | 2022 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-12 11:23 | 2022-05-12 16:20 | 8 | 004:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051200142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-05-12 | 2376 | keep | 0 | May | 2022 | 0.0016183 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-05-12 12:15 | 2022-05-12 13:44 | 20 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X REPTIL | C22051200115 | New_Event |  |  | Include | Wildlife | 89 | 2022-05-12 | 1780 | keep | 0 | May | 2022 | 0.0012123 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-12 12:23 | 2022-05-12 13:17 | 20 | 000:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051200085 | New_Event | Bad Weather | Include | Include | Weather | 54 | 2022-05-12 | 1080 | keep | 0 | May | 2022 | 0.00073558 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-12 12:25 | 2022-05-12 19:18 | 20 | 006:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 413 | 2022-05-12 | 8260 | keep | 0 | May | 2022 | 0.0056258 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-05-12 12:34 | 2022-05-12 15:24 | 30 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | A22051200060 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2022-05-12 | 5100 | keep | 0 | May | 2022 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-12 12:42 | 2022-05-12 16:34 | 50 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C22051200121 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2022-05-12 | 11600 | keep | 0 | May | 2022 | 0.0079007 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-12 12:44 | 2022-05-12 12:45 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 QUE LLEVA 1909-09 | S22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 222 | keep | 0 | May | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-05-12 12:44 | 2022-05-12 12:45 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 QUE LLEVA 1909-09 | S22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 4456 | keep | 0 | May | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
HUMACAO | 2022-05-12 12:44 | 2022-05-12 15:23 | 13 | 002:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C22051200122 | New_Event |  |  | Include | Wildlife | 159 | 2022-05-12 | 2067 | keep | 0 | May | 2022 | 0.0014078 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-05-12 12:45 | 2022-05-12 16:45 | 17 | 004:00 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR RAMAS SOBRE LAS LINEAS PRIMARIAS | M22051200161 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-05-12 | 4080 | keep | 0 | May | 2022 | 0.0027789 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-12 12:48 | 2022-05-12 17:00 | 20 | 004:12 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO | M22051200138 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 252 | 2022-05-12 | 5040 | keep | 0 | May | 2022 | 0.0034327 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-12 12:52 | 2022-05-12 18:37 | 12 | 005:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22051200158 | New_Event | Secondary Wire Down | Include | Include | Equipment | 345 | 2022-05-12 | 4140 | keep | 0 | May | 2022 | 0.0028197 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-12 12:52 | 2022-05-12 13:48 | 100 | 000:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | M22051200167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 56 | 2022-05-12 | 5600 | keep | 0 | May | 2022 | 0.0038141 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-12 12:59 | 2022-05-12 18:27 | 50 | 005:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22051200089 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 328 | 2022-05-12 | 16400 | keep | 0 | May | 2022 | 0.01117 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-12 13:04 | 2022-05-13 09:05 | 1 | 020:01 | P | DESGANCHE | X40 EN C/L & SE RETIRO BAMBUA DE LA LINEA - UN (1) SOLO CLIENTE AFECTADO | S22051200161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1201 | 2022-05-12 | 1201 | keep | 0 | May | 2022 | 0.000818 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-12 13:13 | 2022-05-12 16:55 | 3 | 003:42 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22051200066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2022-05-12 | 666 | keep | 0 | May | 2022 | 0.00045361 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-05-12 13:16 | 2022-05-12 18:50 | 80 | 005:34 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA Y REALIZO DESGANCHE | S22051200165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2022-05-12 | 26720 | keep | 0 | May | 2022 | 0.018199 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-05-12 13:24 | 2022-05-12 14:48 | 80 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R22051200068 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2022-05-12 | 6720 | keep | 0 | May | 2022 | 0.004577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-05-12 13:28 | 2022-05-12 16:14 | 10 | 002:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO NEUTRAL SECUNDARIO Y BAJO TAP 5 AL 2 QUEDO 125/250V REEMPLAZO HERRAJE DE LA CAJA PRIMARIA | C22051200132 | New_Event | Secondary Wire Down | Include | Include | Equipment | 166 | 2022-05-12 | 1660 | keep | 0 | May | 2022 | 0.0011306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-12 13:32 | 2022-05-12 15:10 | 12 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR AVE | B22051200094 | New_Event |  |  | Include | Wildlife | 98 | 2022-05-12 | 1176 | keep | 0 | May | 2022 | 0.00080097 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-05-12 13:38 | 2022-05-12 13:40 | 87 | 000:02 | P | CONDUCTOR ROTO O ABIERTO | CARGAS X 1658-14 | R22051200078 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-05-12 | 174 | keep | 0 | May | 2022 | 0.00011851 | 5.9255e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 87
SAN JUAN | 2022-05-12 13:38 | 2022-05-12 13:40 | 1 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CERRADO X CONTROL | R22051200078 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-05-12 | 2 | keep | 0 | May | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-12 13:44 | 2022-05-12 15:09 | 5252 | 001:25 | T | OTRAS CAUSAS | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE RETIRO TENSOR EN LOS PREDIOS DEL VERTEDERO CARR 866 | B22051200101 | New_Event | Other Causes | Include | Include | Other | 85 | 2022-05-12 | 446420 | keep | 0 | May | 2022 | 0.30405 | 0.0035771 | Sustained | FALSE | FALSE | Not_TMED_Event | 5252
PONCE | 2022-05-12 13:45 | 2022-05-12 19:18 | 15 | 005:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE LINEA PRIMARIA POR RAMA | P22051200057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2022-05-12 | 4995 | keep | 0 | May | 2022 | 0.0034021 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-12 13:49 | 2022-05-12 13:50 | 331 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-12 | 331 | keep | 0 | May | 2022 | 0.00022544 | 0.00022544 | Momentary | FALSE | FALSE | Not_TMED_Event | 331
SAN JUAN | 2022-05-12 13:49 | 2022-05-12 13:50 | 1132 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-12 | 1132 | keep | 0 | May | 2022 | 0.000771 | 0.000771 | Momentary | FALSE | FALSE | Not_TMED_Event | 1132
SAN JUAN | 2022-05-12 13:49 | 2022-05-12 13:50 | 234 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-12 | 234 | keep | 0 | May | 2022 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
SAN JUAN | 2022-05-12 13:49 | 2022-05-12 13:50 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-12 | 2179 | keep | 0 | May | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2022-05-12 13:49 | 2022-05-12 13:50 | 5062 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-12 | 5062 | keep | 0 | May | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2022-05-12 13:49 | 2022-05-12 13:50 | 58 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | S22051200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-12 | 58 | keep | 0 | May | 2022 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2022-05-12 13:50 | 2022-05-12 16:13 | 4 | 002:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L Y CAJA PRIMARIA | S22051200195 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 143 | 2022-05-12 | 572 | keep | 0 | May | 2022 | 0.00038959 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-12 13:52 | 2022-05-12 14:56 | 6 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR DESGANCHAR Y REPARAR SECUNDARIA | B22051200088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2022-05-12 | 384 | keep | 0 | May | 2022 | 0.00026154 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-05-12 14:05 | 2022-05-12 18:59 | 13 | 004:54 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR | R22051200076 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 294 | 2022-05-12 | 3822 | keep | 0 | May | 2022 | 0.0026031 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-05-12 14:05 | 2022-05-12 16:00 | 25 | 001:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051200205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-05-12 | 2875 | keep | 0 | May | 2022 | 0.0019581 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-05-12 14:09 | 2022-05-12 14:10 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22051200061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 3744 | keep | 0 | May | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
SAN JUAN | 2022-05-12 14:17 | 2022-05-12 14:20 | 87 | 000:03 | P | CONDUCTOR ROTO O ABIERTO | CARGAS X 1658-14 | R22051200000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 3 | 2022-05-12 | 261 | keep | 0 | May | 2022 | 0.00017777 | 5.9255e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 87
SAN JUAN | 2022-05-12 14:17 | 2022-05-12 14:20 | 1 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE CERRO POR CONTROL LLEVA LA CARGA DEL 1657-02 | R22051200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 3 | 2022-05-12 | 3 | keep | 0 | May | 2022 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-12 14:20 | 2022-05-12 20:11 | 1 | 005:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON BAJANTES ZAFADOS HACIA BANCO DE TRANSFORMADORES | R22051200082 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 351 | 2022-05-12 | 351 | keep | 0 | May | 2022 | 0.00023906 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-12 14:29 | 2022-05-12 17:37 | 100 | 003:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 Y 1 X 40 EN C/L Y SE REEMPLAZO DISCO | B22051200115 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 188 | 2022-05-12 | 18800 | keep | 0 | May | 2022 | 0.012805 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-12 14:36 | 2022-05-12 18:30 | 30 | 003:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22051200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-05-12 | 7020 | keep | 0 | May | 2022 | 0.0047813 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-12 14:37 | 2022-05-12 17:40 | 100 | 003:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051200033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-05-12 | 18300 | keep | 0 | May | 2022 | 0.012464 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-12 14:43 | 2022-05-12 19:31 | 20 | 004:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051200078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-05-12 | 5760 | keep | 0 | May | 2022 | 0.0039231 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-05-12 14:45 | 2022-05-12 16:56 | 70 | 002:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE LINEA PRIMARIA POR RAMA | P22051200063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-05-12 | 9170 | keep | 0 | May | 2022 | 0.0062456 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2022-05-12 14:46 | 2022-05-12 19:04 | 6 | 004:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22051200141 | New_Event | Secondary Wire Down | Include | Include | Equipment | 258 | 2022-05-12 | 1548 | keep | 0 | May | 2022 | 0.0010543 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-05-12 14:54 | 2022-05-12 14:55 | 638 | 000:01 | T | DESGANCHE | RECIERRE | C22051200146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-12 | 638 | keep | 0 | May | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2022-05-12 14:55 | 2022-05-12 18:56 | 40 | 004:01 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHO Y CERRO PUENTE | C22051200148 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-05-12 | 9640 | keep | 0 | May | 2022 | 0.0065658 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-12 14:57 | 2022-05-12 14:58 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 3941 | keep | 0 | May | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BARRANQUITAS | 2022-05-12 15:01 | 2022-05-12 17:49 | 15 | 002:48 | P | DESGANCHE | 2 X 30 EN C/L | C22051200144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-05-12 | 2520 | keep | 0 | May | 2022 | 0.0017164 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-12 15:04 | 2022-05-12 21:38 | 12 | 006:34 | P | SECUNDARIA/DESGANCHE | SE REPARO BAJANTE SECUNDARIO Y SE DESGANCHO | S22051200194 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 394 | 2022-05-12 | 4728 | keep | 0 | May | 2022 | 0.0032202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-12 15:06 | 2022-05-12 15:07 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22051200068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 2379 | keep | 0 | May | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2022-05-12 15:10 | 2022-05-12 15:11 | 3295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 3295 | keep | 0 | May | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
HUMACAO | 2022-05-12 15:11 | 2022-05-12 17:20 | 17 | 002:09 | P | DESGANCHE | 2 X 80 EN C/L | C22051200152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-05-12 | 2193 | keep | 0 | May | 2022 | 0.0014936 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-05-12 15:11 | 2022-05-12 18:01 | 12 | 002:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR AVE | B22051200094 | Partial_restoration |  |  | Include | Wildlife | 170 | 2022-05-12 | 2040 | keep | 0 | May | 2022 | 0.0013894 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-12 15:13 | 2022-05-12 20:52 | 1 | 005:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22051200082 | New_Event | Bad Weather | Include | Include | Weather | 339 | 2022-05-12 | 339 | keep | 0 | May | 2022 | 0.00023089 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-12 15:17 | 2022-05-12 16:37 | 3 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR SECUNDARIA | B22051200081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2022-05-12 | 240 | keep | 0 | May | 2022 | 0.00016346 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-05-12 15:30 | 2022-05-12 15:31 | 948 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 948 | keep | 0 | May | 2022 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
MAYAGÃœEZ | 2022-05-12 15:38 | 2022-05-12 21:09 | 200 | 005:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051200240 | New_Event | Bad Weather | Include | Include | Weather | 331 | 2022-05-12 | 66200 | keep | 0 | May | 2022 | 0.045089 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-05-12 15:50 | 2022-05-12 18:03 | 1 | 002:13 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B22051200142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-05-12 | 133 | keep | 0 | May | 2022 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-12 15:58 | 2022-05-12 17:31 | 30 | 001:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22051200084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-05-12 | 2790 | keep | 0 | May | 2022 | 0.0019003 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-12 16:06 | 2022-05-12 18:03 | 30 | 001:57 | P | DESGANCHE | 1 X 50 EN C/L | C22051200159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-05-12 | 3510 | keep | 0 | May | 2022 | 0.0023906 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-12 16:07 | 2022-05-13 04:15 | 50 | 012:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051200261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 728 | 2022-05-12 | 36400 | keep | 0 | May | 2022 | 0.024792 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-05-12 16:08 | 2022-05-12 17:45 | 1 | 001:37 | P | SECUNDARIA/DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE LINEA PRIMARIA POR RAMA | P22051200074 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 97 | 2022-05-12 | 97 | keep | 0 | May | 2022 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-05-12 16:20 | 2022-05-12 16:21 | 4132 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO CARGA POR 4006-05 | P22051200103 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-12 | 4132 | keep | 0 | May | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-05-12 16:20 | 2022-05-12 16:21 | 4279 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO CARGA POR 4006-05 | P22051200103 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-12 | 4279 | keep | 0 | May | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-05-12 16:20 | 2022-05-12 16:21 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22051200103 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-12 | 464 | keep | 0 | May | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-05-12 16:21 | 2022-05-12 17:06 | 20 | 000:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE LINEA PRIMARIA POR AVE | P22051200077 | 1st_after_momentary |  |  | Include | Wildlife | 45 | 2022-05-12 | 900 | keep | 0 | May | 2022 | 0.00061299 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-12 16:22 | 2022-05-12 17:45 | 40 | 001:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | A22051200087 | New_Event | Bad Weather | Include | Include | Weather | 83 | 2022-05-12 | 3320 | keep | 0 | May | 2022 | 0.0022612 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-05-12 16:35 | 2022-05-12 17:57 | 10 | 001:22 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R22051200084 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 82 | 2022-05-12 | 820 | keep | 0 | May | 2022 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-12 16:37 | 2022-05-12 19:11 | 300 | 002:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR Y 1 X 50 EN C/L GLOBO | B22051200152 | New_Event |  |  | Include | Wildlife | 154 | 2022-05-12 | 46200 | keep | 0 | May | 2022 | 0.031467 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-05-12 16:42 | 2022-05-12 18:15 | 13 | 001:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIERON 2 XMR , SE LEVANTO LINEA SECUNDARIA DEL PISO , SE REPARARON LAS TOMAS Y EN UNO DE LOS XMR SE DEJO LA CARGA EN EL XMR MAS CERCANO | S22051200193 | New_Event | Secondary Wire Down | Include | Include | Equipment | 93 | 2022-05-12 | 1209 | keep | 0 | May | 2022 | 0.00082344 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-05-12 16:50 | 2022-05-12 20:38 | 1 | 003:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN MONTURA DE XMR AVE | B22051200155 | New_Event |  |  | Include | Wildlife | 228 | 2022-05-12 | 228 | keep | 0 | May | 2022 | 0.00015529 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-12 17:05 | 2022-05-12 20:45 | 1 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051200091 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2022-05-12 | 220 | keep | 0 | May | 2022 | 0.00014984 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-12 17:15 | 2022-05-12 17:17 | 1712 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE COLOCA RR EN OFF Y SE REALIZA PRUEBA QUEDANDO EN SERVICIO | P22051200087 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-05-12 | 3424 | keep | 0 | May | 2022 | 0.0023321 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2022-05-12 17:15 | 2022-05-12 17:17 | 7 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE COLOCA RR EN OFF Y SE REALIZA PRUEBA QUEDANDO EN SERVICIO CARGA POR 5005-03 | P22051200087 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-05-12 | 14 | keep | 0 | May | 2022 | 9.5353e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-05-12 17:17 | 2022-05-12 22:17 | 200 | 005:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ELIMINO ALAMBRE QUE NO DA SERVICIO A NADIE 2 X 100 EN CORTE DE LINEA DESGANCHE | P22051200095 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 300 | 2022-05-12 | 60000 | keep | 0 | May | 2022 | 0.040866 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-05-12 18:17 | 2022-05-12 18:50 | 1 | 000:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22051200096 | New_Event | Wire Down | Include | Include | Equipment | 33 | 2022-05-12 | 33 | keep | 0 | May | 2022 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-12 18:23 | 2022-05-12 19:44 | 30 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M22051200141 | New_Event |  |  | Include | Wildlife | 81 | 2022-05-12 | 2430 | keep | 0 | May | 2022 | 0.0016551 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-12 18:26 | 2022-05-12 18:41 | 250 | 000:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051200312 | New_Event | Vegetation Contact | Include | Include | Vegetation | 15 | 2022-05-12 | 3750 | keep | 0 | May | 2022 | 0.0025541 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2022-05-12 18:50 | 2022-05-13 11:11 | 7 | 016:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22051200178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 981 | 2022-05-12 | 6867 | keep | 0 | May | 2022 | 0.0046771 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-05-12 19:20 | 2022-05-12 22:26 | 102 | 003:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO SE REALIZO DESGANCHE ES TRASPATIO | S22051200231 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2022-05-12 | 18972 | keep | 0 | May | 2022 | 0.012922 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
BAYAMON | 2022-05-12 19:27 | 2022-05-12 22:29 | 151 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22051200175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2022-05-12 | 27482 | keep | 0 | May | 2022 | 0.018718 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
BAYAMON | 2022-05-12 19:37 | 2022-05-12 21:54 | 50 | 002:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO AISLADOR | S22051200237 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 137 | 2022-05-12 | 6850 | keep | 0 | May | 2022 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-12 19:45 | 2022-05-12 19:46 | 1 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22051200150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-12 | 1 | keep | 0 | May | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-12 20:29 | 2022-05-12 22:10 | 300 | 001:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA LINEAS CRUZADAS POR GLOBO | M22051200348 | New_Event | Wire Down | Include | Include | Equipment | 101 | 2022-05-12 | 30300 | keep | 0 | May | 2022 | 0.020637 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-05-12 20:36 | 2022-05-13 12:39 | 25 | 016:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22051200347 | New_Event | Vegetation Contact | Include | Include | Vegetation | 963 | 2022-05-12 | 24075 | keep | 0 | May | 2022 | 0.016397 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-12 20:42 | 2022-05-12 21:25 | 12 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNADARIO | B22051200178 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2022-05-12 | 516 | keep | 0 | May | 2022 | 0.00035145 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-05-12 21:01 | 2022-05-12 22:06 | 91 | 001:05 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 25 AMP. | R22051200095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-05-12 | 5915 | keep | 0 | May | 2022 | 0.0040287 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
AGUADILLA | 2022-05-12 21:50 | 2022-05-13 09:15 | 2 | 011:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE ABRIO TOMA CRUZADA DE CASA QUE SE QUEMO | M22051200369 | New_Event | Secondary Wire Down | Include | Include | Equipment | 685 | 2022-05-12 | 1370 | keep | 0 | May | 2022 | 0.0009331 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-05-12 23:34 | 2022-05-13 06:59 | 7 | 007:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE X CULEBRA | C22051200183 | New_Event |  |  | Include | Wildlife | 445 | 2022-05-12 | 3115 | keep | 0 | May | 2022 | 0.0021216 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-05-13 00:09 | 2022-05-13 00:10 | 552 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INETRRUPTOR 1204-01 QUE LLEVA 40% 1204-03 | S22051300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 552 | keep | 0 | May | 2022 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2022-05-13 00:10 | 2022-05-13 02:16 | 25 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22051300001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-05-13 | 3150 | keep | 0 | May | 2022 | 0.0021455 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-05-13 00:52 | 2022-05-13 06:49 | 65 | 005:57 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22051300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 357 | 2022-05-13 | 23205 | keep | 0 | May | 2022 | 0.015805 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-05-13 02:06 | 2022-05-13 02:07 | 320 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-01 LLLEVANDO 1206-02 Y PARTE DE SU CARGA POR 1201-02 | S22051300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 320 | keep | 0 | May | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2022-05-13 02:06 | 2022-05-13 02:07 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-01 LLLEVANDO 1206-02 Y PARTE DE SU CARGA POR 1201-02 | S22051300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 733 | keep | 0 | May | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2022-05-13 02:09 | 2022-05-13 11:00 | 80 | 008:51 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN RISER SE REPARO TERMINACION EN SU-3 | B22051300001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 531 | 2022-05-13 | 42480 | keep | 0 | May | 2022 | 0.028933 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-13 02:16 | 2022-05-13 02:17 | 829 | 000:01 | P | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 LLEVA 20% 1303-02 40% 1204-04 Y 50% 1204-03 | S22051300004 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 829 | keep | 0 | May | 2022 | 0.00056463 | 0.00056463 | Momentary | FALSE | FALSE | Not_TMED_Event | 829
SAN JUAN | 2022-05-13 02:16 | 2022-05-13 02:17 | 1977 | 000:01 | P | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 LLEVA 20% 1303-02 40% 1204-04 Y 50% 1204-03 | S22051300004 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 1977 | keep | 0 | May | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-05-13 02:16 | 2022-05-13 02:17 | 5000 | 000:01 | P | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 PARTE DE SU CARGA POR 1620-05 Y LLEVA PARTE 1204-05 | S22051300004 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 5000 | keep | 0 | May | 2022 | 0.0034055 | 0.0034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 5000
SAN JUAN | 2022-05-13 02:16 | 2022-05-13 02:17 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S22051300004 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 320 | keep | 0 | May | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2022-05-13 02:16 | 2022-05-13 02:17 | 733 | 000:01 | S | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 | S22051300004 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 733 | keep | 0 | May | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-05-13 02:16 | 2022-05-13 02:17 | 2500 | 000:01 | S | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 PARTE DE SU CARGA POR 1620-05 Y LLEVA PARTE 1204-05 | S22051300004 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 2500 | keep | 0 | May | 2022 | 0.0017027 | 0.0017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 2500
SAN JUAN | 2022-05-13 02:16 | 2022-05-13 02:17 | 1799 | 000:01 | S | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 LLEVA 20% 1303-02 40% 1204-04 Y 60% 1204-03 | S22051300004 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 1799 | keep | 0 | May | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-13 02:16 | 2022-05-13 02:17 | 359 | 000:01 | P | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 LLEVA 20% 1303-02 40% 1204-04 Y 50% 1204-03 | S22051300004 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 359 | keep | 0 | May | 2022 | 0.00024451 | 0.00024451 | Momentary | FALSE | FALSE | Not_TMED_Event | 359
SAN JUAN | 2022-05-13 02:18 | 2022-05-13 02:19 | 829 | 000:01 | P | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 LLEVA 20% 1303-02 40% 1204-04 Y 50% 1204-03 | S22051300004 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 829 | keep | 0 | May | 2022 | 0.00056463 | 0.00056463 | Momentary | FALSE | FALSE | Not_TMED_Event | 829
SAN JUAN | 2022-05-13 02:18 | 2022-05-13 02:19 | 1977 | 000:01 | P | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 LLEVA 20% 1303-02 40% 1204-04 Y 50% 1204-03 | S22051300004 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 1977 | keep | 0 | May | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-05-13 02:18 | 2022-05-13 02:19 | 5000 | 000:01 | P | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 PARTE DE SU CARGA POR 1620-05 Y LLEVA PARTE 1204-05 | S22051300004 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 5000 | keep | 0 | May | 2022 | 0.0034055 | 0.0034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 5000
SAN JUAN | 2022-05-13 02:18 | 2022-05-13 02:19 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S22051300004 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 320 | keep | 0 | May | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2022-05-13 02:18 | 2022-05-13 02:19 | 733 | 000:01 | S | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 | S22051300004 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 733 | keep | 0 | May | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-05-13 02:18 | 2022-05-13 02:19 | 2500 | 000:01 | S | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 PARTE DE SU CARGA POR 1620-05 Y LLEVA PARTE DE 1204-05 | S22051300004 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 2500 | keep | 0 | May | 2022 | 0.0017027 | 0.0017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 2500
SAN JUAN | 2022-05-13 02:18 | 2022-05-13 02:19 | 1799 | 000:01 | S | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 LLEVANDO 20% 1303-02 40% 1204-04 Y 60% 1204-03 | S22051300004 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 1799 | keep | 0 | May | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-13 02:18 | 2022-05-13 02:19 | 359 | 000:01 | P | LINEA DE TRANSMISION 115KV | OPERACION DE LINEA 37900 AL OPERAR INTERRUPTOR 1206-01 LLEVA 20% 1303-02 40% 1204-04 Y 50% 1204-03 | S22051300004 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 359 | keep | 0 | May | 2022 | 0.00024451 | 0.00024451 | Momentary | FALSE | FALSE | Not_TMED_Event | 359
SAN JUAN | 2022-05-13 02:19 | 2022-05-13 10:25 | 25 | 008:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22051300001 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 486 | 2022-05-13 | 12150 | keep | 0 | May | 2022 | 0.0082753 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-13 02:21 | 2022-05-13 04:37 | 320 | 002:16 | P | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR 1206-01 ABRIENDO AMARRE CONTRA 1206-02. PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S22051300011 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-05-13 | 43520 | keep | 0 | May | 2022 | 0.029641 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2022-05-13 02:21 | 2022-05-13 05:57 | 733 | 003:36 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETE Y SE CERRO N/O POR 1206-1 5% EN SERVICIO | S22051300011 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 216 | 2022-05-13 | 158328 | keep | 0 | May | 2022 | 0.10784 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
ARECIBO | 2022-05-13 02:40 | 2022-05-13 09:33 | 40 | 006:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22051300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 413 | 2022-05-13 | 16520 | keep | 0 | May | 2022 | 0.011252 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-05-13 03:55 | 2022-05-13 10:06 | 15 | 006:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A22051300002 | New_Event | Bad Weather | Include | Include | Weather | 371 | 2022-05-13 | 5565 | keep | 0 | May | 2022 | 0.0037903 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-13 04:09 | 2022-05-13 09:38 | 11 | 005:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA (NO FUNDIO) | B22051300002 | New_Event | Cutout Failure | Include | Include | Equipment | 329 | 2022-05-13 | 3619 | keep | 0 | May | 2022 | 0.0024649 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-05-13 04:22 | 2022-05-13 07:55 | 40 | 003:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22051300004 | New_Event |  |  | Include | Wildlife | 213 | 2022-05-13 | 8520 | keep | 0 | May | 2022 | 0.0058029 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-13 04:33 | 2022-05-13 04:35 | 1984 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-12 LLEVANDO CARGA 1911-07 SE CERRO POR SCADA | S22051300029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-13 | 3968 | keep | 0 | May | 2022 | 0.0027026 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-05-13 04:33 | 2022-05-13 04:35 | 577 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-12 LLEVANDO CARGA 1911-07 SE CERRO POR SCADA | S22051300029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-13 | 1154 | keep | 0 | May | 2022 | 0.00078598 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
CANOVANAS | 2022-05-13 04:42 | 2022-05-13 04:43 | 424 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR EN SERVICIO | R22051300002 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-13 | 424 | keep | 0 | May | 2022 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2022-05-13 04:43 | 2022-05-13 07:16 | 297 | 002:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE TRANSFIRIO CARGA 30% DEL ALIMENTADOR | R22051300004 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 153 | 2022-05-13 | 45441 | keep | 0 | May | 2022 | 0.03095 | 0.00020229 | Sustained | FALSE | FALSE | Not_TMED_Event | 297
SAN JUAN | 2022-05-13 05:31 | 2022-05-13 08:14 | 2203 | 002:43 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO MACHETE PARA SECCIONALIZAR TERMINACION AVERIADA EN V.S.4 A SU-5 | S22051300037 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 163 | 2022-05-13 | 359089 | keep | 0 | May | 2022 | 0.24457 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-05-13 05:57 | 2022-05-13 06:11 | 618 | 000:14 | P | NO SE REPORTO CAUSA | SE ABRIO MACHETE VIA DEL LAGO Y SE CERRO MACHETE VIA VENTURA 80% EN SERVICIO | S22051300011 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 14 | 2022-05-13 | 8652 | keep | 0 | May | 2022 | 0.0058928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-13 06:11 | 2022-05-13 06:22 | 155 | 000:11 | P | NO SE REPORTO CAUSA | SE CERRO MACHETE VIA DEL LAGO 100% EN SERVICIO SU CARGA POR 1206-01 | S22051300011 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-05-13 | 1705 | keep | 0 | May | 2022 | 0.0011613 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-13 07:11 | 2022-05-13 10:09 | 30 | 002:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA | A22051300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-05-13 | 5340 | keep | 0 | May | 2022 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-13 07:16 | 2022-05-13 07:52 | 128 | 000:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO Y SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO 70% | R22051300004 | Partial_restoration | Wire Down | Include | Include | Equipment | 36 | 2022-05-13 | 4608 | keep | 0 | May | 2022 | 0.0031385 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-13 07:28 | 2022-05-13 15:00 | 30 | 007:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | C22051300012 | New_Event |  |  | Include | Wildlife | 452 | 2022-05-13 | 13560 | keep | 0 | May | 2022 | 0.0092357 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-05-13 07:29 | 2022-05-13 07:30 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 1192 | keep | 0 | May | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BAYAMON | 2022-05-13 07:33 | 2022-05-13 09:10 | 12 | 001:37 | P | NO SE REPORTO CAUSA | 1X15 EN XMER | B22051300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-05-13 | 1164 | keep | 0 | May | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-13 07:48 | 2022-05-13 16:28 | 30 | 008:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22051300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 520 | 2022-05-13 | 15600 | keep | 0 | May | 2022 | 0.010625 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-13 07:52 | 2022-05-13 10:39 | 35 | 002:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ABIRENDO PUENTES PARA LEVANTAR CONDUCTOR PRIMARIO DEL SUELO Y SE INSTALO CORTE DE LINEA 10% AFECTADO | R22051300004 | Partial_restoration | Wire Down | Include | Include | Equipment | 167 | 2022-05-13 | 5845 | keep | 0 | May | 2022 | 0.003981 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-13 08:10 | 2022-05-13 10:05 | 120 | 001:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE RETEZO LINEA | A22051300011 | New_Event | Wire Down | Include | Include | Equipment | 115 | 2022-05-13 | 13800 | keep | 0 | May | 2022 | 0.0093991 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-05-13 08:14 | 2022-05-13 08:25 | 830 | 000:11 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | AL CERRAR MACHETE CALLE MAYAGÃœEZ DISPARO INTERRUPTOR | S22051300037 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 11 | 2022-05-13 | 9130 | keep | 0 | May | 2022 | 0.0062184 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-13 08:19 | 2022-05-13 12:16 | 1106 | 003:57 | P | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA DE EMERGENCIA BSUHING AVERIADO DE ALTA LLEVA 60% POR 1529-15 | S22051300090 | New_Event | Power Transformer Failure | Include | Include | Equipment | 237 | 2022-05-13 | 262122 | keep | 0 | May | 2022 | 0.17853 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
BAYAMON | 2022-05-13 08:19 | 2022-05-13 11:28 | 577 | 003:09 | T | POWER TRANSFORMER AVERIADO | SE RETIRO CARGA PARA REMPLAZO BUSHING DE ALTA, SE TRANSFIRIO AL 1711-2 | S22051300090 | New_Event | Power Transformer Failure | Include | Include | Equipment | 189 | 2022-05-13 | 109053 | keep | 0 | May | 2022 | 0.074276 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2022-05-13 08:21 | 2022-05-13 12:16 | 1370 | 003:55 | S | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA DE EMERGENCIA BUSHING AVERIADO DE ALTA | S22051300090 | New_Event | Power Transformer Failure | Include | Include | Equipment | 235 | 2022-05-13 | 321950 | keep | 0 | May | 2022 | 0.21928 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2022-05-13 08:21 | 2022-05-13 12:16 | 1984 | 003:55 | S | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA DE EMERGENCIA BUSHING AVERIADO DE ALTA | S22051300091 | New_Event | Power Transformer Failure | Include | Include | Equipment | 235 | 2022-05-13 | 466240 | keep | 0 | May | 2022 | 0.31755 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-05-13 08:21 | 2022-05-13 12:16 | 199 | 003:55 | S | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA DE EMERGENCIA BUSHING AVERIADO DE ALTA | S22051300092 | New_Event | Power Transformer Failure | Include | Include | Equipment | 235 | 2022-05-13 | 46765 | keep | 0 | May | 2022 | 0.031851 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2022-05-13 08:21 | 2022-05-13 12:16 | 1802 | 003:55 | S | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA DE EMERGENCIA BUSHING AVERIADO DE ALTA LLEVA 60% DEL 1346-02 | S22051300090 | New_Event | Power Transformer Failure | Include | Include | Equipment | 235 | 2022-05-13 | 423470 | keep | 0 | May | 2022 | 0.28842 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-05-13 08:25 | 2022-05-13 08:26 | 2203 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | AL CERRAR MACHETE CALLE MAYAGÃœEZ DISPARO INTERRUPTOR | S22051300037 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-05-13 | 2203 | keep | 0 | May | 2022 | 0.0015005 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-13 08:26 | 2022-05-13 12:08 | 1463 | 003:42 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | AL CERRAR MACHETE CALLE MAYAGÃœEZ DISPARO INTERRUPTOR | S22051300037 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 222 | 2022-05-13 | 324786 | keep | 0 | May | 2022 | 0.22121 | 0.00099644 | Sustained | FALSE | FALSE | Not_TMED_Event | 1463
CANOVANAS | 2022-05-13 08:36 | 2022-05-13 20:49 | 20 | 012:13 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | R22051300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 733 | 2022-05-13 | 14660 | keep | 0 | May | 2022 | 0.0099849 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-05-13 08:37 | 2022-05-13 14:00 | 1 | 005:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2022-05-13 | 323 | keep | 0 | May | 2022 | 0.00021999 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-05-13 08:44 | 2022-05-13 15:30 | 15 | 006:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | C22051300020 | New_Event |  |  | Include | Wildlife | 406 | 2022-05-13 | 6090 | keep | 0 | May | 2022 | 0.0041479 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-13 09:05 | 2022-05-13 13:07 | 50 | 004:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22051300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-05-13 | 12100 | keep | 0 | May | 2022 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-13 09:18 | 2022-05-13 10:30 | 23 | 001:12 | P | DESGANCHE | SE HIZO DESGANCHE Y SE REPUSO FUSIBLE DE 50 EN CORTE DE LINEA | P22051300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-05-13 | 1656 | keep | 0 | May | 2022 | 0.0011279 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
FAJARDO | 2022-05-13 09:20 | 2022-05-13 14:20 | 50 | 005:00 | P | DESGANCHE | SE DESGANCHO Y SE CERRO CORTE DE LINEA | R22051300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-05-13 | 15000 | keep | 0 | May | 2022 | 0.010216 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-13 09:34 | 2022-05-13 10:04 | 5 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22051200172 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-05-13 | 150 | keep | 0 | May | 2022 | 0.00010216 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-05-13 09:39 | 2022-05-13 14:39 | 60 | 005:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN SU-8. SE REPARO AEREO PROVISIONAL | B22051300011 | New_Event | Wire Down | Include | Include | Equipment | 300 | 2022-05-13 | 18000 | keep | 0 | May | 2022 | 0.01226 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-13 09:48 | 2022-05-13 14:22 | 1 | 004:34 | P | NO SE REPORTO CAUSA | 2 X 30 EN C/L | R22051300034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2022-05-13 | 274 | keep | 0 | May | 2022 | 0.00018662 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-13 09:50 | 2022-05-13 15:40 | 200 | 005:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M22051300017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2022-05-13 | 70000 | keep | 0 | May | 2022 | 0.047677 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-13 09:51 | 2022-05-13 11:54 | 80 | 002:03 | P | DESGANCHE | 1 RBA DE 80 EN SU-3A DESGANCHE | R22051300036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-05-13 | 9840 | keep | 0 | May | 2022 | 0.006702 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-13 09:55 | 2022-05-13 12:17 | 10 | 002:22 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | S22051300188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-05-13 | 1420 | keep | 0 | May | 2022 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-05-13 09:59 | 2022-05-13 11:06 | 40 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN C/L CRUCE POR AVE | R22051300039 | New_Event |  |  | Include | Wildlife | 67 | 2022-05-13 | 2680 | keep | 0 | May | 2022 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-13 10:01 | 2022-05-13 10:02 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 NO SE REPORTO CAUSA | M22051300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 1253 | keep | 0 | May | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-13 10:01 | 2022-05-13 10:02 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 NO SE REPORTO CAUSA | M22051300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 1266 | keep | 0 | May | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-13 10:01 | 2022-05-13 10:02 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 NO SE REPORTO CAUSA | M22051300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 411 | keep | 0 | May | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-13 10:01 | 2022-05-13 10:02 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 NO SE REPORTO CAUSA | M22051300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 863 | keep | 0 | May | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-13 10:01 | 2022-05-13 10:02 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 NO SE REPORTO CAUSA | M22051300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 309 | keep | 0 | May | 2022 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-13 10:01 | 2022-05-13 10:02 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 NO SE REPORTO CAUSA | M22051300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 176 | keep | 0 | May | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-13 10:01 | 2022-05-13 10:02 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 NO SE REPORTO CAUSA | M22051300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 974 | keep | 0 | May | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
FAJARDO | 2022-05-13 10:02 | 2022-05-13 10:43 | 80 | 000:41 | P | DESGANCHE | 2 X 80 EN C/L | R22051300043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2022-05-13 | 3280 | keep | 0 | May | 2022 | 0.002234 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-13 10:02 | 2022-05-13 14:32 | 8 | 004:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA | M22051300108 | New_Event | Service Transformer Failure | Include | Include | Equipment | 270 | 2022-05-13 | 2160 | keep | 0 | May | 2022 | 0.0014712 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-05-13 10:05 | 2022-05-13 10:58 | 12 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BAJANTES SECUNDARIOS DE TRANSFORMADOR | P22051300012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2022-05-13 | 636 | keep | 0 | May | 2022 | 0.00043318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-05-13 10:08 | 2022-05-13 11:25 | 5 | 001:17 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22051300018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2022-05-13 | 385 | keep | 0 | May | 2022 | 0.00026222 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-05-13 10:15 | 2022-05-13 12:45 | 2 | 002:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A22051300029 | New_Event | Bad Weather | Include | Include | Weather | 150 | 2022-05-13 | 300 | keep | 0 | May | 2022 | 0.00020433 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-05-13 10:19 | 2022-05-13 13:13 | 60 | 002:54 | P | DESGANCHE | 1 X 100 EN C/L | C22051300029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-05-13 | 10440 | keep | 0 | May | 2022 | 0.0071106 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-05-13 10:19 | 2022-05-13 17:55 | 1717 | 007:36 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR PRIMARIO PARTIDO NO OPERO RELES POR BANCO DE BATERIAS Y CARGADOR DEFECTUOSO FUNDE DOS FUSIBLES 38KV SE REPARO LINEA PRIMARIA Y SE REMPLAZO BANCO DE BATERIAS Y CARGADOR | P22051300014 | New_Event | Wire Down | Include | Include | Equipment | 456 | 2022-05-13 | 782952 | keep | 0 | May | 2022 | 0.53327 | 0.0011694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1717
PONCE | 2022-05-13 10:19 | 2022-05-13 14:29 | 974 | 004:10 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | NO OPERO EN AVERIA DE CONDUCTOR PRIMARIO PARTIDO Y INTERRUPTOR 5802-01 NO OPERO RELES POR BANCO DE BATERIAS Y CARGADOR DEFECTUOSO FUNDE DOS FUSIBLES 38KV SE CERRO AMARRE CON 5802-04 SE REPARO LINEA PRIMARIA Y SE REMPLAZO BANCO DE BATERIAS Y CARGADOR | P22051300014 | New_Event | Wire Down | Include | Include | Equipment | 250 | 2022-05-13 | 243500 | keep | 0 | May | 2022 | 0.16585 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
PONCE | 2022-05-13 10:19 | 2022-05-13 14:19 | 1905 | 004:00 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | INTERRUPTOR 5802-01 CONDUCTOR PRIMARIO PARTIDO NO OPERO RELES POR BANCO DE BATERIAS Y CARGADOR DEFECTUOSO FUNDE DOS FUSIBLES 38KV SE REPARO LINEA PRIMARIA Y SE REMPLAZO BANCO DE BATERIAS Y CARGADOR | P22051300014 | New_Event | Wire Down | Include | Include | Equipment | 240 | 2022-05-13 | 457200 | keep | 0 | May | 2022 | 0.3114 | 0.0012975 | Sustained | FALSE | FALSE | Not_TMED_Event | 1905
PONCE | 2022-05-13 10:19 | 2022-05-13 14:19 | 1262 | 004:00 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | INTERRUPTOR 5802-01 CONDUCTOR PRIMARIO PARTIDO NO OPERO RELES POR BANCO DE BATERIAS Y CARGADOR DEFECTUOSO FUNDE DOS FUSIBLES 38KV SE REPARO LINEA PRIMARIA Y SE REMPLAZO BANCO DE BATERIAS Y CARGADOR | P22051300014 | New_Event | Wire Down | Include | Include | Equipment | 240 | 2022-05-13 | 302880 | keep | 0 | May | 2022 | 0.20629 | 0.00085954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1262
PONCE | 2022-05-13 10:19 | 2022-05-13 14:03 | 200 | 003:44 | S | PROTECCION DEFECTUOSA | INTERRUPTOR 5802-01 CONDUCTOR PRIMARIO PARTIDO NO OPERO RELES POR BANCO DE BATERIAS Y CARGADOR DEFECTUOSO FUNDE DOS FUSIBLES 38KV SE REPARO LINEA PRIMARIA Y SE REMPLAZO BANCO DE BATERIAS Y CARGADOR | P22051300014 | New_Event | Protection Miscoordination | Include | Include | Other | 224 | 2022-05-13 | 44800 | keep | 0 | May | 2022 | 0.030513 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-05-13 10:24 | 2022-05-13 10:26 | 1565 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22051300031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-13 | 3130 | keep | 0 | May | 2022 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BAYAMON | 2022-05-13 10:34 | 2022-05-13 10:36 | 1983 | 000:02 | T | OTRAS CAUSAS | CARGA TRANSFERIDA AL 1801-02 INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B22051300000 | New_Event | Other Causes | Include | Include | Other | 2 | 2022-05-13 | 3966 | keep | 0 | May | 2022 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-05-13 10:34 | 2022-05-13 10:36 | 186 | 000:02 | T | OTRAS CAUSAS | DISPARO Y SE CERRO POR CONTROL LLEVA 1711-04 | B22051300000 | New_Event | Other Causes | Include | Include | Other | 2 | 2022-05-13 | 372 | keep | 0 | May | 2022 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2022-05-13 10:34 | 2022-05-14 11:45 | 40 | 025:11 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B22051300032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1511 | 2022-05-13 | 60440 | keep | 0 | May | 2022 | 0.041165 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-13 10:36 | 2022-05-13 13:35 | 16 | 002:59 | P | OTRAS CAUSAS | 2X100 EN C/L POR PROBLEMA INTERIOR EN TRANSPORTE SONELL | B22051300056 | 1st_after_momentary | Other Causes | Include | Include | Other | 179 | 2022-05-13 | 2864 | keep | 0 | May | 2022 | 0.0019507 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2022-05-13 10:39 | 2022-05-13 12:14 | 12 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | R22051300004 | New_Event | Wire Down | Include | Include | Equipment | 95 | 2022-05-13 | 1140 | keep | 0 | May | 2022 | 0.00077645 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-13 10:41 | 2022-05-13 12:46 | 8 | 002:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CAMION IMPACTO POSTE | P22051300034 | New_Event |  |  | Include | Wildlife | 125 | 2022-05-13 | 1000 | keep | 0 | May | 2022 | 0.0006811 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-05-13 10:45 | 2022-05-13 13:15 | 35 | 002:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22051300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-05-13 | 5250 | keep | 0 | May | 2022 | 0.0035758 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-05-13 10:46 | 2022-05-13 13:18 | 200 | 002:32 | P | NO SE REPORTO CAUSA | 1X100 EN C/L & 1X80 EN OTRO C/L | B22051300038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-05-13 | 30400 | keep | 0 | May | 2022 | 0.020705 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-13 10:57 | 2022-05-13 13:57 | 80 | 003:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA PRIMARIA. NO FUNDIO FUSIBLE. | B22051300049 | New_Event | Wire Down | Include | Include | Equipment | 180 | 2022-05-13 | 14400 | keep | 0 | May | 2022 | 0.0098078 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-05-13 11:04 | 2022-05-13 15:00 | 7 | 003:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | A22051300036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 236 | 2022-05-13 | 1652 | keep | 0 | May | 2022 | 0.0011252 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-05-13 11:05 | 2022-05-13 13:35 | 150 | 002:30 | P | DESGANCHE | 1 X 80 EN C/L | R22051300059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-05-13 | 22500 | keep | 0 | May | 2022 | 0.015325 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-05-13 11:16 | 2022-05-13 15:15 | 10 | 003:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22051300238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-05-13 | 2390 | keep | 0 | May | 2022 | 0.0016278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-05-13 11:16 | 2022-05-13 11:18 | 327 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE TRANSMISION 115KV | C22051300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-05-13 | 654 | keep | 0 | May | 2022 | 0.00044544 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2022-05-13 11:16 | 2022-05-13 11:18 | 5630 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE TRANSMISION 115KV | C22051300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-05-13 | 11260 | keep | 0 | May | 2022 | 0.0076691 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-05-13 11:16 | 2022-05-13 11:18 | 2126 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE TRANSMISION 115KV | C22051300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-05-13 | 4252 | keep | 0 | May | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-05-13 11:16 | 2022-05-13 11:18 | 551 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE TRANSMISION 115KV | C22051300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-05-13 | 1102 | keep | 0 | May | 2022 | 0.00075057 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
CANOVANAS | 2022-05-13 11:17 | 2022-05-13 14:15 | 12 | 002:58 | P | DESGANCHE | 1 X 15 EN C/L | R22051300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-05-13 | 2136 | keep | 0 | May | 2022 | 0.0014548 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-13 11:20 | 2022-05-13 17:00 | 3 | 005:40 | P | MAL TIEMPO/RAYOS/WET ASH | MAL TIEMPO VIENTOS FUERTES | M22051300075 | New_Event | Bad Weather | Include | Include | Weather | 340 | 2022-05-13 | 1020 | keep | 0 | May | 2022 | 0.00069472 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-05-13 11:35 | 2022-05-13 15:05 | 25 | 003:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y BAJANTE PRIMARIO | R22051300065 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2022-05-13 | 5250 | keep | 0 | May | 2022 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-13 11:43 | 2022-05-13 15:24 | 60 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22051300058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-05-13 | 13260 | keep | 0 | May | 2022 | 0.0090313 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-13 11:56 | 2022-05-13 14:35 | 100 | 002:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA. REEMPLAZO CAJA PRIMARIA | B22051300060 | New_Event | Cutout Failure | Include | Include | Equipment | 159 | 2022-05-13 | 15900 | keep | 0 | May | 2022 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-13 11:56 | 2022-05-13 11:57 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22051300058 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 1565 | keep | 0 | May | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-05-13 11:56 | 2022-05-13 11:57 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22051300058 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 976 | keep | 0 | May | 2022 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-05-13 11:56 | 2022-05-13 11:57 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22051300058 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 548 | keep | 0 | May | 2022 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-05-13 11:56 | 2022-05-13 11:57 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22051300059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 315 | keep | 0 | May | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-05-13 11:56 | 2022-05-13 11:57 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22051300059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-05-13 11:56 | 2022-05-13 11:57 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22051300060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 2906 | keep | 0 | May | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-05-13 11:56 | 2022-05-13 11:57 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C22051300060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-13 | 2343 | keep | 0 | May | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
BAYAMON | 2022-05-13 12:00 | 2022-05-14 00:20 | 32 | 012:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER Y SE REMPLAZO CAJA PRIMARIA | S22051300252 | New_Event | Cutout Failure | Include | Include | Equipment | 740 | 2022-05-13 | 23680 | keep | 0 | May | 2022 | 0.016128 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2022-05-13 12:05 | 2022-05-13 12:06 | 2907 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051300063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 2907 | keep | 0 | May | 2022 | 0.0019799 | 0.0019799 | Momentary | FALSE | FALSE | Not_TMED_Event | 2907
SAN JUAN | 2022-05-13 12:08 | 2022-05-13 12:11 | 2203 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION EN V.S.4 A SU-5 | S22051300037 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2022-05-13 | 6609 | keep | 0 | May | 2022 | 0.0045014 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-05-13 12:11 | 2022-05-13 14:00 | 74 | 001:49 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION EN V.S.4 A SU-5 | S22051300037 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 109 | 2022-05-13 | 8066 | keep | 0 | May | 2022 | 0.0054937 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
ARECIBO | 2022-05-13 12:13 | 2022-05-13 12:14 | 2697 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A22051300047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-13 | 2697 | keep | 0 | May | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2022-05-13 12:14 | 2022-05-13 14:45 | 150 | 002:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051300048 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-05-13 | 22650 | keep | 0 | May | 2022 | 0.015427 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-05-13 12:15 | 2022-05-13 12:16 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051300062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 3114 | keep | 0 | May | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2022-05-13 12:18 | 2022-05-13 15:48 | 300 | 003:30 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051300100 | New_Event | Bad Weather | Include | Include | Weather | 210 | 2022-05-13 | 63000 | keep | 0 | May | 2022 | 0.042909 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-05-13 12:19 | 2022-05-13 21:00 | 100 | 008:41 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22051300102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2022-05-13 | 52100 | keep | 0 | May | 2022 | 0.035485 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-05-13 12:27 | 2022-05-13 13:55 | 2 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | R22051300066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2022-05-13 | 176 | keep | 0 | May | 2022 | 0.00011987 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-05-13 12:34 | 2022-05-14 13:29 | 84 | 024:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2X50 EN RISER 1X40 EN SU-1 & SE RETIRO UN GATO DEL SU-1 | S22051300286 | New_Event |  |  | Include | Wildlife | 1495 | 2022-05-13 | 125580 | keep | 0 | May | 2022 | 0.085532 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
UTUADO | 2022-05-13 12:38 | 2022-05-13 17:50 | 120 | 005:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051300057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2022-05-13 | 37440 | keep | 0 | May | 2022 | 0.0255 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-05-13 12:45 | 2022-05-13 21:05 | 110 | 008:20 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | B22051300069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 500 | 2022-05-13 | 55000 | keep | 0 | May | 2022 | 0.03746 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CANOVANAS | 2022-05-13 12:47 | 2022-05-13 19:21 | 40 | 006:34 | P | DESGANCHE | 1 X 40 EN C/L 1 X 10 EN XMR | R22051300070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2022-05-13 | 15760 | keep | 0 | May | 2022 | 0.010734 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-13 13:08 | 2022-05-14 08:54 | 40 | 019:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | M22051300125 | New_Event | Bad Weather | Include | Include | Weather | 1186 | 2022-05-13 | 47440 | keep | 0 | May | 2022 | 0.032311 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-13 13:10 | 2022-05-13 13:46 | 109 | 000:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO FUERTES LLUVIA | C22051300080 | New_Event | Bad Weather | Include | Include | Weather | 36 | 2022-05-13 | 3924 | keep | 0 | May | 2022 | 0.0026726 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
UTUADO | 2022-05-13 13:18 | 2022-05-13 19:30 | 50 | 006:12 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051300065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2022-05-13 | 18600 | keep | 0 | May | 2022 | 0.012668 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-13 13:19 | 2022-05-13 14:20 | 79 | 001:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C22051300079 | New_Event | Wire Down | Include | Include | Equipment | 61 | 2022-05-13 | 4819 | keep | 0 | May | 2022 | 0.0032822 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
PONCE | 2022-05-13 13:20 | 2022-05-14 10:23 | 50 | 021:03 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P22051300074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1263 | 2022-05-13 | 63150 | keep | 0 | May | 2022 | 0.043011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-13 13:20 | 2022-05-13 15:13 | 15 | 001:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-05-13 | 1695 | keep | 0 | May | 2022 | 0.0011545 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-13 13:21 | 2022-05-13 13:22 | 528 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-02 QUE ESTA LLEVANDO LA CARGA DEL 6012-01 | M22051300130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 528 | keep | 0 | May | 2022 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
MAYAGÃœEZ | 2022-05-13 13:21 | 2022-05-13 13:22 | 4664 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051300130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 4664 | keep | 0 | May | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
HUMACAO | 2022-05-13 13:22 | 2022-05-13 16:50 | 100 | 003:28 | P | DESGANCHE | 1 X 65 EN C/L | C22051300081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-05-13 | 20800 | keep | 0 | May | 2022 | 0.014167 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-13 13:25 | 2022-05-13 16:53 | 10 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22051300078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-05-13 | 2080 | keep | 0 | May | 2022 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-13 13:31 | 2022-05-13 13:32 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051300137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-13 13:31 | 2022-05-13 13:32 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M22051300137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2022-05-13 13:44 | 2022-05-13 17:15 | 28 | 003:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22051300300 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-05-13 | 5908 | keep | 0 | May | 2022 | 0.0040239 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2022-05-13 14:00 | 2022-05-13 14:59 | 74 | 000:59 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO MACHETE QUEMADO CALLE MARCIAL Y AL CERRAR DISPARO INTERRUPTOR | S22051300037 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 59 | 2022-05-13 | 4366 | keep | 0 | May | 2022 | 0.0029737 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-13 14:00 | 2022-05-13 14:10 | 1 | 000:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER MAL TIEMPO | C22051300095 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2022-05-13 | 10 | keep | 0 | May | 2022 | 6.811e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-13 14:03 | 2022-05-13 20:20 | 300 | 006:17 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN CORTES DE LINEA SE NECESITA REALIZAR DESGANCHE | M22051300159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2022-05-13 | 113100 | keep | 0 | May | 2022 | 0.077032 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-05-13 14:04 | 2022-05-13 14:05 | 637 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 637 | keep | 0 | May | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
AGUADILLA | 2022-05-13 14:06 | 2022-05-13 18:39 | 15 | 004:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22051300164 | New_Event | Secondary Wire Break | Include | Include | Equipment | 273 | 2022-05-13 | 4095 | keep | 0 | May | 2022 | 0.0027891 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-05-13 14:06 | 2022-05-13 16:45 | 100 | 002:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | B22051300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-05-13 | 15900 | keep | 0 | May | 2022 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-05-13 14:10 | 2022-05-13 15:35 | 4132 | 001:25 | T | NO SE REPORTO CAUSA | SE CERRO MACHETES DE AMARRE CON 4006-05 Y QUEDO EN SERVICIO NO SE ENCONTRO CAUSA | P22051300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-05-13 | 351220 | keep | 0 | May | 2022 | 0.23921 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-05-13 14:10 | 2022-05-13 14:33 | 4279 | 000:23 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE ABREN MACHETES DE AMARRE CON 4003-01 Y SE COLOCA EN SERVICIO CARGA POR 4006-05 | P22051300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-05-13 | 98417 | keep | 0 | May | 2022 | 0.067031 | 0.0029144 | Sustained | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-05-13 14:10 | 2022-05-13 14:33 | 464 | 000:23 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE ABREN MACHETES DE AMARRE CON 4003-01 Y SE COLOCA EN SERVICIO | P22051300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-05-13 | 10672 | keep | 0 | May | 2022 | 0.0072687 | 0.00031603 | Sustained | FALSE | FALSE | Not_TMED_Event | 464
CAGUAS | 2022-05-13 14:12 | 2022-05-13 16:13 | 117 | 002:01 | P | DESGANCHE | 2 X 100 EN C/L | C22051300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-05-13 | 14157 | keep | 0 | May | 2022 | 0.0096423 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
MAYAGÃœEZ | 2022-05-13 14:14 | 2022-05-14 10:09 | 100 | 019:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZA DESGANCHE | M22051300166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1195 | 2022-05-13 | 119500 | keep | 0 | May | 2022 | 0.081391 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-13 14:22 | 2022-05-13 16:05 | 7 | 001:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | A22051300082 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-05-13 | 721 | keep | 0 | May | 2022 | 0.00049107 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-13 14:24 | 2022-05-13 18:08 | 155 | 003:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN PARALELA | S22051300309 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2022-05-13 | 34720 | keep | 0 | May | 2022 | 0.023648 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
ARECIBO | 2022-05-13 14:27 | 2022-05-13 18:00 | 150 | 003:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22051300083 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 213 | 2022-05-13 | 31950 | keep | 0 | May | 2022 | 0.021761 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-05-13 14:28 | 2022-05-13 15:16 | 4 | 000:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER Y REEMPLAZO DE PORTAFUSIBLE | R22051300088 | New_Event | Cutout Failure | Include | Include | Equipment | 48 | 2022-05-13 | 192 | keep | 0 | May | 2022 | 0.00013077 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-05-13 14:29 | 2022-05-13 20:30 | 75 | 006:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LINEA PRIMARIAS | P22051300101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2022-05-13 | 27075 | keep | 0 | May | 2022 | 0.018441 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-05-13 14:33 | 2022-05-13 15:09 | 70 | 000:36 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22051300103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2022-05-13 | 2520 | keep | 0 | May | 2022 | 0.0017164 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-05-13 14:38 | 2022-05-13 14:39 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22051300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 3511 | keep | 0 | May | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
GUAYAMA | 2022-05-13 14:44 | 2022-05-13 17:45 | 3 | 003:01 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO 37.5 KVA A 4.16 KV SE TRANSFIRIO CARGA A TRANSFOMADOR ALEDAÃ‘O | P22051300114 | New_Event | Service Transformer Failure | Include | Include | Equipment | 181 | 2022-05-13 | 543 | keep | 0 | May | 2022 | 0.00036983 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-05-13 14:47 | 2022-05-13 18:13 | 180 | 003:26 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B22051300106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2022-05-13 | 37080 | keep | 0 | May | 2022 | 0.025255 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BAYAMON | 2022-05-13 14:49 | 2022-05-13 16:38 | 1221 | 001:49 | T | DESGANCHE | SE RETIRO RAMA CRUZANDO LINEAS EN CALLE 17 MAGNOLIA, BAYAMON | B22051300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-05-13 | 133089 | keep | 0 | May | 2022 | 0.090646 | 0.00083162 | Sustained | FALSE | FALSE | Not_TMED_Event | 1221
MAYAGÃœEZ | 2022-05-13 14:54 | 2022-05-13 14:55 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051300184 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-13 14:54 | 2022-05-13 14:55 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M22051300184 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-13 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2022-05-13 14:59 | 2022-05-13 15:02 | 2203 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO MACHETE QUEMADO CALLE MARCIAL Y AL CERRAR DISPARO INTERRUPTOR | S22051300037 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2022-05-13 | 6609 | keep | 0 | May | 2022 | 0.0045014 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-13 15:02 | 2022-05-13 15:36 | 30 | 000:34 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO SU-1 CALLE AÃ‘ASCO Y SE CERRO N/O CONTRA 1401-10 EN CALLE MUÃ‘OS RIVERA | S22051300037 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 34 | 2022-05-13 | 1020 | keep | 0 | May | 2022 | 0.00069472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-13 15:04 | 2022-05-13 15:05 | 4641 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M22051300000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-13 | 4641 | keep | 0 | May | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-05-13 15:07 | 2022-05-14 13:30 | 10 | 022:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M22051300018 | New_Event | Wire Down | Include | Include | Equipment | 1343 | 2022-05-13 | 13430 | keep | 0 | May | 2022 | 0.0091471 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-13 15:09 | 2022-05-13 15:10 | 1984 | 000:01 | T | POWER TRANSFORMER AVERIADO | SE ABRIO INTERRUPTOR PARA PODER ABRIR N/O CARR.2 CONTRA 1911-7 Y 1529-12 (N/O HAY QUE REMPLAZAR MACHETE ESTAN INOPERANTES) | S22051300090 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1 | 2022-05-13 | 1984 | keep | 0 | May | 2022 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-05-13 15:09 | 2022-05-13 15:10 | 723 | 000:01 | T | POWER TRANSFORMER AVERIADO | SE ABRIO INTERRUPTOR PARA PODER ABRIR N/O CARR.2 CONTRA 1911-7 Y 1529-12 (N/O HAY QUE REMPLAZAR MACHETE ESTAN INOPERANTES) | S22051300090 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1 | 2022-05-13 | 723 | keep | 0 | May | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-05-13 15:09 | 2022-05-13 15:10 | 1976 | 000:01 | T | POWER TRANSFORMER AVERIADO | SE ABRIO INTERRUPTOR PARA PODER ABRIR N/O CARR.2 CONTRA 1911-7 Y 1529-12 (N/O HAY QUE REMPLAZAR MACHETE ESTAN INOPERANTES) | S22051300090 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1 | 2022-05-13 | 1976 | keep | 0 | May | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-05-13 15:09 | 2022-05-13 15:10 | 577 | 000:01 | T | POWER TRANSFORMER AVERIADO | SE ABRIO INTERRUPTOR PARA PODER ABRIR N/O CARR.2 CONTRA 1911-7 Y 1529-12 (N/O HAY QUE REMPLAZAR MACHETE ESTAN INOPERANTES) | S22051300090 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1 | 2022-05-13 | 577 | keep | 0 | May | 2022 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
ARECIBO | 2022-05-13 15:11 | 2022-05-13 17:50 | 50 | 002:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051300091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-05-13 | 7950 | keep | 0 | May | 2022 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-13 15:21 | 2022-05-13 15:24 | 1106 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO 60% POR 1529-12 | S22051300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-13 | 3318 | keep | 0 | May | 2022 | 0.0022599 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
BAYAMON | 2022-05-13 15:21 | 2022-05-13 15:24 | 1802 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 60% 1346-2 | S22051300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-13 | 5406 | keep | 0 | May | 2022 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
ARECIBO | 2022-05-13 15:22 | 2022-05-13 16:34 | 30 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051300094 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2022-05-13 | 2160 | keep | 0 | May | 2022 | 0.0014712 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-13 15:28 | 2022-05-13 21:08 | 70 | 005:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | M22051300200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2022-05-13 | 23800 | keep | 0 | May | 2022 | 0.01621 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-05-13 15:42 | 2022-05-13 18:35 | 100 | 002:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 65 EN CORTES DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051300212 | New_Event | Bad Weather | Include | Include | Weather | 173 | 2022-05-13 | 17300 | keep | 0 | May | 2022 | 0.011783 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-13 15:46 | 2022-05-13 17:19 | 12 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN C/L | R22051300094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-05-13 | 1116 | keep | 0 | May | 2022 | 0.0007601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-05-13 15:50 | 2022-05-14 10:23 | 1 | 018:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIEMPO | C22051300097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1113 | 2022-05-13 | 1113 | keep | 0 | May | 2022 | 0.00075806 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-13 15:54 | 2022-05-13 17:39 | 752 | 001:45 | T | TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO MH-92A CON AVERIA EN TERMINACION SOTERRADA Y SE COLOCO INTERRUPTOR EN SERVICIO CARGA POR 5018-04 | P22051300137 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 105 | 2022-05-13 | 78960 | keep | 0 | May | 2022 | 0.053779 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2022-05-13 15:54 | 2022-05-13 17:39 | 2696 | 001:45 | T | TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO MH-92A CON AVERIA EN TERMINACION SOTERRADA Y SE COLOCO INTERRUPTOR EN SERVICIO LLEVA LA CARGA EL 5011-04 | P22051300137 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 105 | 2022-05-13 | 283080 | keep | 0 | May | 2022 | 0.1928 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
AGUADILLA | 2022-05-13 15:54 | 2022-05-13 20:52 | 10 | 004:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA AVE CRUZO LINEAS | M22051300218 | New_Event |  |  | Include | Wildlife | 298 | 2022-05-13 | 2980 | keep | 0 | May | 2022 | 0.0020297 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-13 15:55 | 2022-05-13 18:48 | 40 | 002:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C22051300123 | New_Event | Wire Down | Include | Include | Equipment | 173 | 2022-05-13 | 6920 | keep | 0 | May | 2022 | 0.0047132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-05-13 15:58 | 2022-05-14 12:57 | 4 | 020:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | P22051300138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1259 | 2022-05-13 | 5036 | keep | 0 | May | 2022 | 0.00343 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-05-13 16:01 | 2022-05-14 12:41 | 100 | 020:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | M22051300228 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1240 | 2022-05-13 | 124000 | keep | 0 | May | 2022 | 0.084456 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-13 16:07 | 2022-05-15 15:59 | 10 | 047:52 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO PUENTES. INTERRUPCION DESDE 05/13/2022 CON EVENTO M22051300236 DE SITUACION PELIGROSA | M22051500030 | New_Event | Primary Wire Break | Include | Include | Equipment | 2872 | 2022-05-13 | 28720 | keep | 0 | May | 2022 | 0.019561 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-13 16:10 | 2022-05-13 17:36 | 8 | 001:26 | P | DESGANCHE | 2 X 40 EN C/L | R22051300100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-05-13 | 688 | keep | 0 | May | 2022 | 0.00046859 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-05-13 16:14 | 2022-05-13 17:45 | 10 | 001:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA. CRUCE DE FASE PRIMARIA POR RAMA | P22051300146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-05-13 | 910 | keep | 0 | May | 2022 | 0.0006198 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-13 16:16 | 2022-05-13 19:52 | 50 | 003:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051300245 | New_Event | Bad Weather | Include | Include | Weather | 216 | 2022-05-13 | 10800 | keep | 0 | May | 2022 | 0.0073558 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-13 16:17 | 2022-05-13 16:18 | 3295 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO NO RECIERRA | B22051300000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-13 | 3295 | keep | 0 | May | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-05-13 16:18 | 2022-05-13 19:29 | 3295 | 003:11 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR AVERIADO EN CARR 164 INT 803 Y RETIRO DOS PARARRAYOS EN CARR 164 KM 14. | B22051300215 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 191 | 2022-05-13 | 629345 | keep | 0 | May | 2022 | 0.42864 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
UTUADO | 2022-05-13 16:19 | 2022-05-13 19:51 | 50 | 003:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-05-13 | 10600 | keep | 0 | May | 2022 | 0.0072196 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-13 16:54 | 2022-05-13 20:00 | 50 | 003:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22051300159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-05-13 | 9300 | keep | 0 | May | 2022 | 0.0063342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-05-13 17:06 | 2022-05-13 17:07 | 2484 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22051300164 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-05-13 | 2484 | keep | 0 | May | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
YAUCO | 2022-05-13 17:07 | 2022-05-13 17:29 | 200 | 000:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR PRIMARIO PARTIDO SE ABRIO INTERRUPTOR | P22051300180 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 22 | 2022-05-13 | 4400 | keep | 0 | May | 2022 | 0.0029968 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-13 17:13 | 2022-05-13 21:34 | 300 | 004:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051300273 | New_Event | Bad Weather | Include | Include | Weather | 261 | 2022-05-13 | 78300 | keep | 0 | May | 2022 | 0.05333 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-05-13 17:19 | 2022-05-13 18:42 | 30 | 001:23 | P | DESGANCHE | 1 X 100 EN C/L | R22051300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-05-13 | 2490 | keep | 0 | May | 2022 | 0.0016959 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-13 17:19 | 2022-05-13 17:20 | 4641 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M22051300000 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-13 | 4641 | keep | 0 | May | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
YAUCO | 2022-05-13 17:20 | 2022-05-13 23:07 | 1924 | 005:47 | S | ANIMAL U OBJETO EXTRAÃ‘O | AVE CRUZO 2 FASES Y FUNDIO 2 FUSIBLES DE ALTA | P22051300168 | New_Event |  |  | Include | Wildlife | 347 | 2022-05-13 | 667628 | keep | 0 | May | 2022 | 0.45472 | 0.0013104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2022-05-13 17:20 | 2022-05-13 23:07 | 968 | 005:47 | S | ANIMAL U OBJETO EXTRAÃ‘O | AVE CRUZO 2 FASES Y FUNDIO 2 FUSIBLES DE ALTA | P22051300168 | New_Event |  |  | Include | Wildlife | 347 | 2022-05-13 | 335896 | keep | 0 | May | 2022 | 0.22878 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-05-13 17:20 | 2022-05-13 23:07 | 680 | 005:47 | S | ANIMAL | AVE CRUZO 2 FASES Y FUNDIO 2 FUSIBLES DE ALTA | P22051300168 | New_Event | Animals | Include | Include | Wildlife | 347 | 2022-05-13 | 235960 | keep | 0 | May | 2022 | 0.16071 | 0.00046314 | Sustained | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2022-05-13 17:20 | 2022-05-13 23:07 | 2246 | 005:47 | S | ANIMAL U OBJETO EXTRAÃ‘O | AVE CRUZO 2 FASES Y FUNDIO 2 FUSIBLES DE ALTA | P22051300168 | New_Event |  |  | Include | Wildlife | 347 | 2022-05-13 | 779362 | keep | 0 | May | 2022 | 0.53082 | 0.0015297 | Sustained | FALSE | FALSE | Not_TMED_Event | 2246
MAYAGÃœEZ | 2022-05-13 17:20 | 2022-05-13 18:00 | 60 | 000:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051300191 | New_Event | Bad Weather | Include | Include | Weather | 40 | 2022-05-13 | 2400 | keep | 0 | May | 2022 | 0.0016346 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-05-13 17:29 | 2022-05-13 18:49 | 2484 | 001:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERREPTOR POR CONDUCTOR PRIMARIO EN EL SUELO SE ABRIO MACHETES EN CARR 324 BO ENSENA Y SE COLOCA INTERRUPTOR EN SERVICIO | P22051300180 | Additional_clients | Wire Down | Include | Include | Equipment | 80 | 2022-05-13 | 198720 | keep | 0 | May | 2022 | 0.13535 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-13 17:39 | 2022-05-13 19:51 | 8 | 002:12 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO BARRA SECA PRIMARIA Y SE CERRO DEL MH-92A AL MH-93 | P22051300206 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 132 | 2022-05-13 | 1056 | keep | 0 | May | 2022 | 0.00071924 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-05-13 17:53 | 2022-05-13 22:36 | 113 | 004:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22051300204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2022-05-13 | 31979 | keep | 0 | May | 2022 | 0.021781 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
CANOVANAS | 2022-05-13 17:57 | 2022-05-13 21:32 | 7 | 003:35 | P | OTRAS CAUSAS | 1 X 10 EN XMR CAUSA FUE CONTADOR DE FABRICA 120V/240V ESTABA CRUZADO SE DEJO FUERA EL CLIENTE | R22051300105 | New_Event | Other Causes | Include | Include | Other | 215 | 2022-05-13 | 1505 | keep | 0 | May | 2022 | 0.001025 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-13 19:07 | 2022-05-14 09:56 | 3 | 014:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2X100 EN C/L & SE REMPLAZARON TRES (3) CAJAS PRIMARIAS | S22051300344 | New_Event | Cutout Failure | Include | Include | Equipment | 889 | 2022-05-13 | 2667 | keep | 0 | May | 2022 | 0.0018165 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-05-13 19:08 | 2022-05-14 11:20 | 40 | 016:12 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B22051300022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 972 | 2022-05-13 | 38880 | keep | 0 | May | 2022 | 0.026481 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-05-13 19:09 | 2022-05-13 20:13 | 18 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN C/L MAL TIEMPO | C22051300154 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2022-05-13 | 1152 | keep | 0 | May | 2022 | 0.00078462 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2022-05-13 19:10 | 2022-05-13 21:58 | 100 | 002:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22051300212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-05-13 | 16800 | keep | 0 | May | 2022 | 0.011442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-13 19:24 | 2022-05-14 11:05 | 120 | 015:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L & SE REMPLAZO EL PORTAFUSIBLE | S22051300346 | New_Event | Cutout Failure | Include | Include | Equipment | 941 | 2022-05-13 | 112920 | keep | 0 | May | 2022 | 0.076909 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-05-13 19:35 | 2022-05-14 11:10 | 80 | 015:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22051300331 | New_Event | Cutout Failure | Include | Include | Equipment | 935 | 2022-05-13 | 74800 | keep | 0 | May | 2022 | 0.050946 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-13 19:42 | 2022-05-14 11:57 | 25 | 016:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22051300351 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 975 | 2022-05-13 | 24375 | keep | 0 | May | 2022 | 0.016602 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-13 19:54 | 2022-05-13 22:30 | 200 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051300341 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2022-05-13 | 31200 | keep | 0 | May | 2022 | 0.02125 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-05-13 20:05 | 2022-05-13 20:36 | 60 | 000:31 | P | DESGANCHE | ABRIO C/L PARA RETIRAR BAMBUA CRUZANDO LAS LINEAS | C22051300145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2022-05-13 | 1860 | keep | 0 | May | 2022 | 0.0012668 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-05-13 20:10 | 2022-05-14 09:00 | 60 | 012:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22051300225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 770 | 2022-05-13 | 46200 | keep | 0 | May | 2022 | 0.031467 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-13 20:11 | 2022-05-13 22:20 | 8 | 002:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE | A22051300116 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2022-05-13 | 1032 | keep | 0 | May | 2022 | 0.00070289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-05-13 20:24 | 2022-05-14 02:50 | 125 | 006:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22051300356 | New_Event | Cutout Failure | Include | Include | Equipment | 386 | 2022-05-13 | 48250 | keep | 0 | May | 2022 | 0.032863 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-05-13 20:55 | 2022-05-13 21:49 | 4 | 000:54 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA Y TOMA | S22051300291 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 54 | 2022-05-13 | 216 | keep | 0 | May | 2022 | 0.00014712 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-13 20:55 | 2022-05-14 15:30 | 5 | 018:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA ABIERTA. | B22051300233 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1115 | 2022-05-13 | 5575 | keep | 0 | May | 2022 | 0.0037971 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-13 21:13 | 2022-05-14 09:59 | 15 | 012:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR POR LLUVIAS | M22051300386 | New_Event | Bad Weather | Include | Include | Weather | 766 | 2022-05-13 | 11490 | keep | 0 | May | 2022 | 0.0078258 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-05-13 21:32 | 2022-05-14 08:30 | 40 | 010:58 | P | DESGANCHE | 1X40 EN C/L & SE RETIRO UN ARBOL ENTERO DE LA LINEA | B22051300237 | New_Event | Vegetation Contact | Include | Include | Vegetation | 658 | 2022-05-13 | 26320 | keep | 0 | May | 2022 | 0.017926 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-13 21:39 | 2022-05-13 21:40 | 1307 | 000:01 | T | DESGANCHE | RECIERRE | C22051300161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-13 | 1307 | keep | 0 | May | 2022 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2022-05-13 21:40 | 2022-05-14 06:22 | 150 | 008:42 | P | DESGANCHE | 2 X 65 EN C/L | C22051300163 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 522 | 2022-05-13 | 78300 | keep | 0 | May | 2022 | 0.05333 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-05-13 22:09 | 2022-05-14 10:18 | 152 | 012:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 100 EN C/L'S MAL TIEMPO | C22051300170 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 729 | 2022-05-13 | 110808 | keep | 0 | May | 2022 | 0.075471 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
PONCE | 2022-05-13 22:57 | 2022-05-14 11:20 | 75 | 012:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22051300245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 743 | 2022-05-13 | 55725 | keep | 0 | May | 2022 | 0.037954 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-05-13 23:57 | 2022-05-14 18:16 | 20 | 018:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO LINEA SECUNDARIA CRUZADA SE REALIZO DESGANCHE Y SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | A22051300120 | New_Event | Cutout Failure | Include | Include | Equipment | 1099 | 2022-05-13 | 21980 | keep | 0 | May | 2022 | 0.01497 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-14 01:13 | 2022-05-14 09:46 | 6 | 008:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO ENCONTRARON CAUSA | A22051400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 513 | 2022-05-14 | 3078 | keep | 0 | May | 2022 | 0.0020964 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-05-14 01:20 | 2022-05-14 08:06 | 50 | 006:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C22051400004 | New_Event | Bad Weather | Include | Include | Weather | 406 | 2022-05-14 | 20300 | keep | 0 | May | 2022 | 0.013826 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-14 01:23 | 2022-05-14 17:50 | 25 | 016:27 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22051400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 987 | 2022-05-14 | 24675 | keep | 0 | May | 2022 | 0.016806 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-14 01:42 | 2022-05-14 12:53 | 80 | 011:11 | P | DESGANCHE | 1 X 65 Y 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22051400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 671 | 2022-05-14 | 53680 | keep | 0 | May | 2022 | 0.036561 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-05-14 02:11 | 2022-05-14 02:12 | 2133 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-05 LLEVANDO PARTE 1206-03 SE CERRO POR SCADA | S22051400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 2133 | keep | 0 | May | 2022 | 0.0014528 | 0.0014528 | Momentary | FALSE | FALSE | Not_TMED_Event | 2133
SAN JUAN | 2022-05-14 02:11 | 2022-05-14 02:12 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-05 LLEVANDO PARTE 1206-03 SE CERRO POR SCADA | S22051400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1615 | keep | 0 | May | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2022-05-14 03:02 | 2022-05-14 03:03 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 2404-06 EN SERVICIO | R22051400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-05-14 03:02 | 2022-05-14 03:03 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 2402-03 EN SERVICIO | R22051400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 7621 | keep | 0 | May | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
MAYAGÃœEZ | 2022-05-14 03:17 | 2022-05-14 15:04 | 70 | 011:47 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051400013 | New_Event | Bad Weather | Include | Include | Weather | 707 | 2022-05-14 | 49490 | keep | 0 | May | 2022 | 0.033707 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-05-14 03:39 | 2022-05-14 09:24 | 30 | 005:45 | P | DESGANCHE | 1 X 30 EN C/L | C22051400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2022-05-14 | 10350 | keep | 0 | May | 2022 | 0.0070493 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-05-14 03:54 | 2022-05-14 13:00 | 50 | 009:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L SE REEMPLAZO PUENTE PRIMARIO, SE ELIMINO PARARRAYO Y DESGANCHE | R22051400024 | New_Event | Wire Down | Include | Include | Equipment | 546 | 2022-05-14 | 27300 | keep | 0 | May | 2022 | 0.018594 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-14 04:05 | 2022-05-14 10:36 | 40 | 006:31 | P | DESGANCHE | 1 X 80 EN C/L | C22051400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 391 | 2022-05-14 | 15640 | keep | 0 | May | 2022 | 0.010652 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-05-14 05:13 | 2022-05-14 08:59 | 20 | 003:46 | P | DESGANCHE | 1 X 50 EN C/L Y 1 X 30 EN C/L SE RETIRO BEJUCO Y SE ENDEREZO PUENTE | R22051400027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-05-14 | 4520 | keep | 0 | May | 2022 | 0.0030786 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-14 05:51 | 2022-05-14 05:53 | 1 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1001-03 LLEVANDO 1002-02 Y 1001-01 | S22051400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-14 | 2 | keep | 0 | May | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-14 05:51 | 2022-05-14 05:53 | 245 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1001-03 LLEVANDO 1002-02 Y 1001-01 | S22051400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-14 | 490 | keep | 0 | May | 2022 | 0.00033374 | 0.00016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 245
BAYAMON | 2022-05-14 05:51 | 2022-05-14 05:53 | 126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1001-03 LLEVANDO 1002-02 Y 1001-01 | S22051400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-14 | 252 | keep | 0 | May | 2022 | 0.00017164 | 8.5818e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 126
CANOVANAS | 2022-05-14 05:51 | 2022-05-14 05:52 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 2404-06 | R22051400028 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-05-14 05:51 | 2022-05-14 05:52 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 2402-03 | R22051400028 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 7621 | keep | 0 | May | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
MAYAGÃœEZ | 2022-05-14 05:51 | 2022-05-14 12:47 | 100 | 006:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR VIENTOS | M22051400017 | New_Event | Bad Weather | Include | Include | Weather | 416 | 2022-05-14 | 41600 | keep | 0 | May | 2022 | 0.028334 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-05-14 05:59 | 2022-05-14 12:18 | 50 | 006:19 | P | SOBRECARGA | 1 X 65 EN C/L SOBRE CARGA | C22051400016 | New_Event | Trip Due To Overload | Include | Include | Other | 379 | 2022-05-14 | 18950 | keep | 0 | May | 2022 | 0.012907 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-05-14 06:08 | 2022-05-14 12:59 | 50 | 006:51 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22051400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2022-05-14 | 20550 | keep | 0 | May | 2022 | 0.013997 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-14 06:18 | 2022-05-14 17:29 | 89 | 011:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22051400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 671 | 2022-05-14 | 59719 | keep | 0 | May | 2022 | 0.040674 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
MAYAGÃœEZ | 2022-05-14 06:18 | 2022-05-14 12:45 | 15 | 006:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE CAMBIO AISLADOR PARTIDO | M22051400024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 387 | 2022-05-14 | 5805 | keep | 0 | May | 2022 | 0.0039538 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-05-14 06:22 | 2022-05-14 06:23 | 1307 | 000:01 | T | DESGANCHE | RECIERRE | C22051400022 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-14 | 1307 | keep | 0 | May | 2022 | 0.00089019 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-14 06:23 | 2022-05-14 06:42 | 150 | 000:19 | P | DESGANCHE | 2 X 65 EN C/L | C22051300163 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 19 | 2022-05-14 | 2850 | keep | 0 | May | 2022 | 0.0019411 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-05-14 06:26 | 2022-05-14 10:24 | 6 | 003:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR POR IGUANA | M22051400027 | New_Event |  |  | Include | Wildlife | 238 | 2022-05-14 | 1428 | keep | 0 | May | 2022 | 0.0009726 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-14 06:45 | 2022-05-14 08:40 | 100 | 001:55 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22051400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-05-14 | 11500 | keep | 0 | May | 2022 | 0.0078326 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-14 06:50 | 2022-05-14 06:51 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22051400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 3438 | keep | 0 | May | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
MAYAGÃœEZ | 2022-05-14 06:58 | 2022-05-14 06:59 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-14 06:58 | 2022-05-14 06:59 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 LLEVA LA CARGA DEL 6012-03 | M22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-14 07:02 | 2022-05-14 10:13 | 300 | 003:11 | P | DESGANCHE | 3 X 200 EN CORTE DE LINEA RAMA CRUZO LINEA | M22051400031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-05-14 | 57300 | keep | 0 | May | 2022 | 0.039027 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-05-14 07:13 | 2022-05-14 07:14 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1401-05 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 922 | keep | 0 | May | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-05-14 07:13 | 2022-05-14 07:14 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1346-05 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 135 | keep | 0 | May | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CAGUAS | 2022-05-14 07:22 | 2022-05-14 07:23 | 1702 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | C22051400053 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-14 | 1702 | keep | 0 | May | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-05-14 07:23 | 2022-05-14 12:40 | 286 | 005:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 200 EN C/L REMPLAZO 2 AISLADORES | C22051400057 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 317 | 2022-05-14 | 90662 | keep | 0 | May | 2022 | 0.061749 | 0.00019479 | Sustained | FALSE | FALSE | Not_TMED_Event | 286
GUAYAMA | 2022-05-14 07:27 | 2022-05-14 08:50 | 35 | 001:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22051400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-05-14 | 2905 | keep | 0 | May | 2022 | 0.0019786 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-05-14 07:38 | 2022-05-14 14:18 | 13 | 006:40 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22051400032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2022-05-14 | 5200 | keep | 0 | May | 2022 | 0.0035417 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2022-05-14 07:42 | 2022-05-14 12:06 | 122 | 004:24 | P | DESGANCHE | 2 X 50 EN C/L Y 1 X 40 C/L DESGANCHE | R22051400033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2022-05-14 | 32208 | keep | 0 | May | 2022 | 0.021937 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
GUAYAMA | 2022-05-14 07:42 | 2022-05-14 11:23 | 60 | 003:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE SE LEVANTO LINEA PRIMARIA DEL PISO | P22051400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-05-14 | 13260 | keep | 0 | May | 2022 | 0.0090313 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-05-14 07:43 | 2022-05-14 13:09 | 20 | 005:26 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22051400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 326 | 2022-05-14 | 6520 | keep | 0 | May | 2022 | 0.0044407 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-05-14 07:50 | 2022-05-14 17:00 | 40 | 009:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTE VIENTO | A22051400008 | New_Event | Bad Weather | Include | Include | Weather | 550 | 2022-05-14 | 22000 | keep | 0 | May | 2022 | 0.014984 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-14 07:58 | 2022-05-14 13:02 | 18 | 005:04 | P | DESGANCHE | 1 X 30 EN C/L | C22051400043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2022-05-14 | 5472 | keep | 0 | May | 2022 | 0.003727 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-05-14 08:04 | 2022-05-14 13:48 | 122 | 005:44 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR 1 X 50 EN CORTE DE LINEA SE HIZO DESGANCHE Y SE REMPLAZO PARARRAYOS | S22051400036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2022-05-14 | 41968 | keep | 0 | May | 2022 | 0.028584 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
CAGUAS | 2022-05-14 08:12 | 2022-05-14 14:46 | 150 | 006:34 | P | DESGANCHE | 1 X 50 Y 2 X 65 EN C/L'S | C22051400048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2022-05-14 | 59100 | keep | 0 | May | 2022 | 0.040253 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-05-14 08:13 | 2022-05-14 13:23 | 50 | 005:10 | P | DESGANCHE | 1 X 50 EN C/L | C22051400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-05-14 | 15500 | keep | 0 | May | 2022 | 0.010557 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-14 08:14 | 2022-05-15 11:59 | 56 | 027:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22051400052 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1665 | 2022-05-14 | 93240 | keep | 0 | May | 2022 | 0.063505 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
MAYAGÃœEZ | 2022-05-14 08:21 | 2022-05-14 14:23 | 40 | 006:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22051400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-05-14 | 14480 | keep | 0 | May | 2022 | 0.0098623 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-05-14 08:21 | 2022-05-14 10:41 | 100 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR VIENTO | A22051400013 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2022-05-14 | 14000 | keep | 0 | May | 2022 | 0.0095353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-14 08:22 | 2022-05-14 08:55 | 150 | 000:33 | P | DESGANCHE | 1 X 50 Y 2 X 65 EN CORTES DE LINEA SE REALIZO DESGANCHE DE BAMBUAS | A22051400015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2022-05-14 | 4950 | keep | 0 | May | 2022 | 0.0033714 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-05-14 08:24 | 2022-05-14 11:12 | 43 | 002:48 | P | DESGANCHE | 1 X 80 EN C/L | C22051400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-05-14 | 7224 | keep | 0 | May | 2022 | 0.0049202 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
ARECIBO | 2022-05-14 08:25 | 2022-05-14 13:23 | 70 | 004:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO SAFADO EN CORTE DE LINEA | A22051400017 | New_Event | Wire Down | Include | Include | Equipment | 298 | 2022-05-14 | 20860 | keep | 0 | May | 2022 | 0.014208 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-05-14 08:27 | 2022-05-14 12:48 | 8 | 004:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE POR AVE | R22051400041 | New_Event |  |  | Include | Wildlife | 261 | 2022-05-14 | 2088 | keep | 0 | May | 2022 | 0.0014221 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-14 08:35 | 2022-05-14 10:25 | 2000 | 001:50 | P | DESCONECTIVO DEFECTUOSO | SE DISPARO INTERRUPTOR 1619-02 Y SE SECCIONALIZO PARA REEMPLAZO DE 2 MACHETES EN N/O 1619-03/1619-02 QUEMADOS EN AVENIDA PONTEZUEL CALLE CACERAS SABANA ABAJO CAROLINA 2000 CLIENTES POR 1619-02 | R22051400000 | New_Event | Switch Failure | Include | Include | Equipment | 110 | 2022-05-14 | 220000 | keep | 0 | May | 2022 | 0.14984 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2022-05-14 08:35 | 2022-05-14 11:23 | 5062 | 002:48 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1619-03 Y SE SECCIONALIZO PARA REEMPLAZAR 2 LOS MACHETES QUEMADOS EN C/ NORTE DETRAS DE RES. VISTAMAR PLAZA | R22051400000 | New_Event | Switch Failure | Include | Include | Equipment | 168 | 2022-05-14 | 850416 | keep | 0 | May | 2022 | 0.57921 | 0.0034477 | Sustained | FALSE | FALSE | Not_TMED_Event | 5062
MAYAGÃœEZ | 2022-05-14 08:37 | 2022-05-14 08:38 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051400072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 108 | keep | 0 | May | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
UTUADO | 2022-05-14 08:55 | 2022-05-14 08:56 | 1241 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR CON EL RECIERRE EN ON SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | A22051400023 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-14 | 1241 | keep | 0 | May | 2022 | 0.00084524 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-14 08:56 | 2022-05-14 21:11 | 150 | 012:15 | P | DESGANCHE | 1 X 50 Y 2 X 65 EN CORTES DE LINEA SE REALIZO DESGANCHE DE BAMBUAS | A22051400015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 735 | 2022-05-14 | 110250 | keep | 0 | May | 2022 | 0.075091 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-14 08:57 | 2022-05-14 11:17 | 200 | 002:20 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22051400077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-05-14 | 28000 | keep | 0 | May | 2022 | 0.019071 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-05-14 08:58 | 2022-05-14 08:59 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051400079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1827 | keep | 0 | May | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BAYAMON | 2022-05-14 09:05 | 2022-05-14 09:07 | 823 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO LLEVA 95% POR 1119-04 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-14 | 1646 | keep | 0 | May | 2022 | 0.0011211 | 0.00056054 | Momentary | FALSE | FALSE | Not_TMED_Event | 823
BAYAMON | 2022-05-14 09:05 | 2022-05-14 09:07 | 2720 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 95% DEL 1115-5 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-14 | 5440 | keep | 0 | May | 2022 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
FAJARDO | 2022-05-14 09:10 | 2022-05-14 10:22 | 50 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE POR AVE | R22051400091 | New_Event |  |  | Include | Wildlife | 72 | 2022-05-14 | 3600 | keep | 0 | May | 2022 | 0.0024519 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-14 09:19 | 2022-05-16 18:30 | 7 | 057:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | M22051400095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 3431 | 2022-05-14 | 24017 | keep | 0 | May | 2022 | 0.016358 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-05-14 09:25 | 2022-05-14 13:54 | 9 | 004:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22051400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2022-05-14 | 2421 | keep | 0 | May | 2022 | 0.0016489 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-05-14 09:43 | 2022-05-14 15:35 | 100 | 005:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L AVE CRUZO LINEAS | P22051400021 | New_Event |  |  | Include | Wildlife | 352 | 2022-05-14 | 35200 | keep | 0 | May | 2022 | 0.023975 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-14 09:45 | 2022-05-15 12:31 | 10 | 026:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA LINEA PRIMARIA PARTIDA | A22051400035 | New_Event | Primary Wire Break | Include | Include | Equipment | 1606 | 2022-05-14 | 16060 | keep | 0 | May | 2022 | 0.010938 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-14 09:58 | 2022-05-14 09:59 | 8711 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO PARTE POR 1206-03 | S22051400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 8711 | keep | 0 | May | 2022 | 0.005933 | 0.005933 | Momentary | FALSE | FALSE | Not_TMED_Event | 8711
SAN JUAN | 2022-05-14 09:58 | 2022-05-14 09:59 | 2633 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1206-03 PARTE POR 1620-05 Y LLEVA PARTE DEL 1204-05 | S22051400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 2633 | keep | 0 | May | 2022 | 0.0017933 | 0.0017933 | Momentary | FALSE | FALSE | Not_TMED_Event | 2633
MAYAGÃœEZ | 2022-05-14 09:59 | 2022-05-14 10:00 | 1017 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051400118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1017 | keep | 0 | May | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
CAGUAS | 2022-05-14 10:01 | 2022-05-14 12:58 | 150 | 002:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN C/L DESGANCHO Y FIJO CONDUCTOR | C22051400086 | New_Event | Wire Down | Include | Include | Equipment | 177 | 2022-05-14 | 26550 | keep | 0 | May | 2022 | 0.018083 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-05-14 10:03 | 2022-05-14 11:53 | 146 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1 X 80 C/L'S CRUCE X AVE | C22051400090 | New_Event |  |  | Include | Wildlife | 110 | 2022-05-14 | 16060 | keep | 0 | May | 2022 | 0.010938 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
CANOVANAS | 2022-05-14 10:05 | 2022-05-14 15:24 | 2 | 005:19 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | R22051400132 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 319 | 2022-05-14 | 638 | keep | 0 | May | 2022 | 0.00043454 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-05-14 10:09 | 2022-05-14 11:48 | 253 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 65 EN C/L'S MAL TIEMPO | C22051400095 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2022-05-14 | 25047 | keep | 0 | May | 2022 | 0.017059 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
MAYAGÃœEZ | 2022-05-14 10:09 | 2022-05-14 16:10 | 60 | 006:01 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LAS LINEAS | M22051400122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2022-05-14 | 21660 | keep | 0 | May | 2022 | 0.014753 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-14 10:17 | 2022-05-14 12:56 | 40 | 002:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR ENREDADERA CRUZANDO PARARRAYO | M22051400128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-05-14 | 6360 | keep | 0 | May | 2022 | 0.0043318 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-05-14 10:24 | 2022-05-14 16:58 | 25 | 006:34 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHO Y REMPLAZO DISCO PARTIDO | C22051400103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2022-05-14 | 9850 | keep | 0 | May | 2022 | 0.0067088 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-14 10:39 | 2022-05-14 10:40 | 552 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 40% POR 1204-1 | S22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 552 | keep | 0 | May | 2022 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
BAYAMON | 2022-05-14 10:42 | 2022-05-14 12:57 | 70 | 002:15 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22051400039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2022-05-14 | 9450 | keep | 0 | May | 2022 | 0.0064364 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-05-14 10:49 | 2022-05-15 10:28 | 25 | 023:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA QUE CAYO SOBRE LA LINEA | M22051400154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1419 | 2022-05-14 | 35475 | keep | 0 | May | 2022 | 0.024162 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-14 10:55 | 2022-05-14 10:56 | 1105 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO 60% POR 1529-15 | S22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1105 | keep | 0 | May | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2022-05-14 10:55 | 2022-05-14 10:56 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 60% 1346-2 | S22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1802 | keep | 0 | May | 2022 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
ARECIBO | 2022-05-14 10:56 | 2022-05-14 14:30 | 25 | 003:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTE VIENTO | A22051400053 | New_Event | Bad Weather | Include | Include | Weather | 214 | 2022-05-14 | 5350 | keep | 0 | May | 2022 | 0.0036439 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-05-14 10:58 | 2022-05-14 12:35 | 80 | 001:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22051400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-05-14 | 7760 | keep | 0 | May | 2022 | 0.0052853 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-14 11:16 | 2022-05-14 13:59 | 20 | 002:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA RETEZO LINEA PRIMARIA | S22051400061 | New_Event | Wire Down | Include | Include | Equipment | 163 | 2022-05-14 | 3260 | keep | 0 | May | 2022 | 0.0022204 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-05-14 11:20 | 2022-05-14 11:21 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051400024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 3114 | keep | 0 | May | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
ARECIBO | 2022-05-14 11:31 | 2022-05-14 13:25 | 40 | 001:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22051400079 | New_Event | Wire Down | Include | Include | Equipment | 114 | 2022-05-14 | 4560 | keep | 0 | May | 2022 | 0.0031058 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-14 11:35 | 2022-05-14 14:45 | 50 | 003:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA ARBOL CAYO Y CAUSO QUE LAS LINEAS SE CRUZARAN | A22051400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-05-14 | 9500 | keep | 0 | May | 2022 | 0.0064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-14 11:37 | 2022-05-14 23:40 | 50 | 012:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | A22051400060 | New_Event | Wire Down | Include | Include | Equipment | 723 | 2022-05-14 | 36150 | keep | 0 | May | 2022 | 0.024622 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-14 11:38 | 2022-05-14 15:50 | 60 | 004:12 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22051400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2022-05-14 | 15120 | keep | 0 | May | 2022 | 0.010298 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-14 11:39 | 2022-05-14 11:40 | 3046 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | R22051400141 | New_Event |  |  | Include | Wildlife | 1 | 2022-05-14 | 3046 | keep | 0 | May | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-05-14 11:40 | 2022-05-14 13:24 | 9 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE POR AVE | R22051400155 | 1st_after_momentary |  |  | Include | Wildlife | 104 | 2022-05-14 | 936 | keep | 0 | May | 2022 | 0.00063751 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-05-14 11:41 | 2022-05-14 11:42 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051400028 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 3114 | keep | 0 | May | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
YAUCO | 2022-05-14 11:43 | 2022-05-14 13:57 | 1 | 002:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO LLUVIA | P22051400027 | New_Event | Bad Weather | Include | Include | Weather | 134 | 2022-05-14 | 134 | keep | 0 | May | 2022 | 9.1267e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-14 11:45 | 2022-05-14 13:36 | 15 | 001:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA (NO FUNDIO) | B22051400043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 111 | 2022-05-14 | 1665 | keep | 0 | May | 2022 | 0.001134 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-14 11:45 | 2022-05-14 11:46 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051400170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 108 | keep | 0 | May | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
ARECIBO | 2022-05-14 11:46 | 2022-05-14 11:47 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO ESTA AMARRADO | A22051400170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1227 | keep | 0 | May | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-05-14 11:46 | 2022-05-14 11:47 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO ESTA AMARRADO | A22051400170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2022-05-14 11:49 | 2022-05-14 15:53 | 100 | 004:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN C/L MAL TIEMPO | C22051400126 | New_Event | Bad Weather | Include | Include | Weather | 244 | 2022-05-14 | 24400 | keep | 0 | May | 2022 | 0.016619 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-14 11:51 | 2022-05-14 11:52 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO | S22051400068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1310 | keep | 0 | May | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2022-05-14 11:58 | 2022-05-14 19:25 | 12 | 007:27 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR POR CORROSIÃ“N DEL FUSIBLE CAUSADA POR SALITRE EN AL AREA | A22051400070 | New_Event | Other Causes | Include | Include | Other | 447 | 2022-05-14 | 5364 | keep | 0 | May | 2022 | 0.0036534 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-14 12:12 | 2022-05-14 16:00 | 30 | 003:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA CAIDA SOBRE LAS LINEAS | A22051400075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2022-05-14 | 6840 | keep | 0 | May | 2022 | 0.0046587 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-14 12:17 | 2022-05-14 14:32 | 90 | 002:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22051400072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-05-14 | 12150 | keep | 0 | May | 2022 | 0.0082753 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-05-14 12:20 | 2022-05-14 19:00 | 30 | 006:40 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22051400046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 400 | 2022-05-14 | 12000 | keep | 0 | May | 2022 | 0.0081731 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-05-14 12:22 | 2022-05-14 16:48 | 70 | 004:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22051400047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2022-05-14 | 18620 | keep | 0 | May | 2022 | 0.012682 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-05-14 12:30 | 2022-05-14 15:01 | 65 | 002:31 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN C/L'S | C22051400143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-05-14 | 9815 | keep | 0 | May | 2022 | 0.006685 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-05-14 12:31 | 2022-05-14 16:40 | 20 | 004:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE LINEA A CAJA NO FUNDIO | C22051400144 | New_Event | Wire Down | Include | Include | Equipment | 249 | 2022-05-14 | 4980 | keep | 0 | May | 2022 | 0.0033919 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-14 12:48 | 2022-05-14 19:00 | 100 | 006:12 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051400195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2022-05-14 | 37200 | keep | 0 | May | 2022 | 0.025337 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-14 12:58 | 2022-05-14 12:59 | 1228 | 000:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C22051400242 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-05-14 | 1228 | keep | 0 | May | 2022 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2022-05-14 12:59 | 2022-05-14 16:36 | 150 | 003:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN C/L DESGANCHO Y FIJO CONDUCTOR | C22051400086 | Partial_restoration | Wire Down | Include | Include | Equipment | 217 | 2022-05-14 | 32550 | keep | 0 | May | 2022 | 0.02217 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-14 13:01 | 2022-05-14 13:46 | 828 | 000:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE PATRULLO SE ENCONTRO PERSONAL AJENO A LUMA TUMBO LINEA CRUZO FASE Y VERIFICO Y SE PROBO INTERRUPTOR SU CARGA POR 1206-04 | S22051400083 | New_Event |  |  | Include | Wildlife | 45 | 2022-05-14 | 37260 | keep | 0 | May | 2022 | 0.025378 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-05-14 13:01 | 2022-05-14 13:46 | 1977 | 000:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE PATRULLO SE ENCONTRO PERSONAL AJENO A LUMA TUMBO LINEA CRUZO FASE Y VERIFICO Y SE PROBO INTERRUPTOR SU CARGA POR 1206-04 | S22051400083 | New_Event |  |  | Include | Wildlife | 45 | 2022-05-14 | 88965 | keep | 0 | May | 2022 | 0.060594 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-05-14 13:01 | 2022-05-14 13:46 | 1799 | 000:45 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE PATRULLO SE ENCONTRO PERSONAL AJENO A LUMA TUMBO LINEA CRUZO FASE Y VERIFICO Y SE PROBO INTERRUPTOR QUEDO EN SERVICIO LLEVA 20% 1303-2, 40% 1204-4 Y 60% 1204-3 | S22051400083 | New_Event |  |  | Include | Wildlife | 45 | 2022-05-14 | 80955 | keep | 0 | May | 2022 | 0.055138 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-14 13:01 | 2022-05-14 13:46 | 487 | 000:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE PATRULLO SE ENCONTRO PERSONAL AJENO A LUMA TUMBO LINEA CRUZO FASE Y VERIFICO Y SE PROBO INTERRUPTOR SU CARGA POR 1206-04 | S22051400083 | New_Event |  |  | Include | Wildlife | 45 | 2022-05-14 | 21915 | keep | 0 | May | 2022 | 0.014926 | 0.00033169 | Sustained | FALSE | FALSE | Not_TMED_Event | 487
GUAYAMA | 2022-05-14 13:03 | 2022-05-14 13:04 | 1457 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051400039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1457 | keep | 0 | May | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
BAYAMON | 2022-05-14 13:09 | 2022-05-14 16:53 | 30 | 003:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | B22051400051 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 224 | 2022-05-14 | 6720 | keep | 0 | May | 2022 | 0.004577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-05-14 13:14 | 2022-05-14 18:08 | 30 | 004:54 | P | DESGANCHE | 1 X 50 EN C/L | C22051400166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2022-05-14 | 8820 | keep | 0 | May | 2022 | 0.0060073 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-14 13:31 | 2022-05-15 16:17 | 24 | 026:46 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | C22051400171 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1606 | 2022-05-14 | 38544 | keep | 0 | May | 2022 | 0.026252 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
PONCE | 2022-05-14 13:35 | 2022-05-14 17:48 | 1 | 004:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 30 EN RAISER AVE CRUZO LINEAS | P22050140005 | New_Event |  |  | Include | Wildlife | 253 | 2022-05-14 | 253 | keep | 0 | May | 2022 | 0.00017232 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-05-14 13:44 | 2022-05-14 16:12 | 20 | 002:28 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22051400170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-05-14 | 2960 | keep | 0 | May | 2022 | 0.002016 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-05-14 13:49 | 2022-05-14 15:18 | 8 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P22051400045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 89 | 2022-05-14 | 712 | keep | 0 | May | 2022 | 0.00048494 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-14 13:59 | 2022-05-14 15:04 | 621 | 001:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO EN SUBESTACION | S22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-05-14 | 40365 | keep | 0 | May | 2022 | 0.027492 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
MAYAGÃœEZ | 2022-05-14 14:06 | 2022-05-14 18:35 | 1 | 004:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22051400214 | New_Event | Secondary Wire Down | Include | Include | Equipment | 269 | 2022-05-14 | 269 | keep | 0 | May | 2022 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-14 14:09 | 2022-05-15 10:50 | 17 | 020:41 | P | TERMINACION SOTERRADA AVERIADA | TERMINACION EN RISER A SU2 QUEMADA | C22051400177 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1241 | 2022-05-14 | 21097 | keep | 0 | May | 2022 | 0.014369 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2022-05-14 14:15 | 2022-05-14 15:05 | 10 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | M22051400220 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-05-14 | 500 | keep | 0 | May | 2022 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-14 14:18 | 2022-05-14 15:10 | 10 | 000:52 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22051400177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2022-05-14 | 520 | keep | 0 | May | 2022 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-14 14:18 | 2022-05-14 16:39 | 100 | 002:21 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | B22051400057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2022-05-14 | 14100 | keep | 0 | May | 2022 | 0.0096034 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-14 14:21 | 2022-05-14 15:46 | 45 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22051400104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-05-14 | 3825 | keep | 0 | May | 2022 | 0.0026052 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-05-14 14:22 | 2022-05-14 14:23 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 312 | keep | 0 | May | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
PONCE | 2022-05-14 14:26 | 2022-05-14 14:27 | 2039 | 000:01 | T | DESGANCHE | RECIERRE | P22051400047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-14 | 2039 | keep | 0 | May | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2022-05-14 14:27 | 2022-05-14 16:35 | 90 | 002:08 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22051400049 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-05-14 | 11520 | keep | 0 | May | 2022 | 0.0078462 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2022-05-14 14:27 | 2022-05-14 18:55 | 47 | 004:28 | P | DESGANCHE | 1 X 65 EN C/L | C22051400180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-05-14 | 12596 | keep | 0 | May | 2022 | 0.0085791 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
FAJARDO | 2022-05-14 14:33 | 2022-05-14 20:17 | 99 | 005:44 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN C/L Y 1 X 40 EN RISER SE REMPLAZO XMR T- 11 DE 50 KVA X 50 KVA | R22051400182 | New_Event | Service Transformer Failure | Include | Include | Equipment | 344 | 2022-05-14 | 34056 | keep | 0 | May | 2022 | 0.023195 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
SAN JUAN | 2022-05-14 14:48 | 2022-05-14 16:37 | 19 | 001:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE REPARO PUENTE PRIMARIO | R22051400184 | New_Event | Wire Down | Include | Include | Equipment | 109 | 2022-05-14 | 2071 | keep | 0 | May | 2022 | 0.0014105 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-05-14 14:57 | 2022-05-14 17:25 | 30 | 002:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22051400061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2022-05-14 | 4440 | keep | 0 | May | 2022 | 0.0030241 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-14 14:57 | 2022-05-14 17:36 | 70 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051400230 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2022-05-14 | 11130 | keep | 0 | May | 2022 | 0.0075806 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-05-14 14:57 | 2022-05-14 20:46 | 10 | 005:49 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B22051400060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 349 | 2022-05-14 | 3490 | keep | 0 | May | 2022 | 0.002377 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-05-14 15:01 | 2022-05-14 15:50 | 10 | 000:49 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P22051400051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2022-05-14 | 490 | keep | 0 | May | 2022 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-05-14 15:02 | 2022-05-14 15:03 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051400052 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 3114 | keep | 0 | May | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
HUMACAO | 2022-05-14 15:07 | 2022-05-14 16:29 | 2126 | 001:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RETIRO BAJANTE PEGADO A CRUCETA | C22051400191 | New_Event | Wire Down | Include | Include | Equipment | 82 | 2022-05-14 | 174332 | keep | 0 | May | 2022 | 0.11874 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2022-05-14 15:08 | 2022-05-14 17:40 | 40 | 002:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LAS LINEAS | A22051400113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-05-14 | 6080 | keep | 0 | May | 2022 | 0.0041411 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-14 15:24 | 2022-05-14 17:18 | 50 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTE VIENTO | A22051400114 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2022-05-14 | 5700 | keep | 0 | May | 2022 | 0.0038822 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-14 15:29 | 2022-05-14 16:20 | 150 | 000:51 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22051400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2022-05-14 | 7650 | keep | 0 | May | 2022 | 0.0052104 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-05-14 15:41 | 2022-05-14 15:42 | 253 | 000:01 | T | NO SE REPORTO CAUSA | NO SE REPORTO CAUSA | P22051400055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 253 | keep | 0 | May | 2022 | 0.00017232 | 0.00017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 253
BAYAMON | 2022-05-14 15:55 | 2022-05-14 18:05 | 65 | 002:10 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA REEMPLAZO PARARRAYO 6KV | B22051400065 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 130 | 2022-05-14 | 8450 | keep | 0 | May | 2022 | 0.0057553 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2022-05-14 16:00 | 2022-05-14 17:55 | 70 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22051400068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-05-14 | 8050 | keep | 0 | May | 2022 | 0.0054828 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-05-14 16:24 | 2022-05-14 16:25 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22051400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 4431 | keep | 0 | May | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2022-05-14 16:30 | 2022-05-14 18:15 | 60 | 001:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ABIERTO DE LINEA A CAJA PRIMARIA. NO FUNDIO FUSIBLE | S22051400172 | New_Event | Wire Down | Include | Include | Equipment | 105 | 2022-05-14 | 6300 | keep | 0 | May | 2022 | 0.0042909 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-14 16:36 | 2022-05-14 18:15 | 30 | 001:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA ARREADA | A22051400120 | New_Event | Wire Down | Include | Include | Equipment | 99 | 2022-05-14 | 2970 | keep | 0 | May | 2022 | 0.0020229 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-14 16:56 | 2022-05-14 17:36 | 45 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | C22051400245 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2022-05-14 | 1800 | keep | 0 | May | 2022 | 0.001226 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-05-14 17:14 | 2022-05-14 17:15 | 527 | 000:01 | T | NO SE REPORTO CAUSA | NO SE REPORTO CAUSA | P220514000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
SAN JUAN | 2022-05-14 17:20 | 2022-05-14 19:11 | 100 | 001:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L SE REPARO BAJANTE DE LINEA A CAJA | R22051400198 | New_Event | Wire Down | Include | Include | Equipment | 111 | 2022-05-14 | 11100 | keep | 0 | May | 2022 | 0.0075602 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-14 17:27 | 2022-05-14 20:34 | 14 | 003:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE. NO FUNDIO | S22051400179 | New_Event | Wire Down | Include | Include | Equipment | 187 | 2022-05-14 | 2618 | keep | 0 | May | 2022 | 0.0017831 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-05-14 17:27 | 2022-05-14 18:29 | 150 | 001:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN C/L | S22051400175 | New_Event | Wire Down | Include | Include | Equipment | 62 | 2022-05-14 | 9300 | keep | 0 | May | 2022 | 0.0063342 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-05-14 17:54 | 2022-05-14 17:55 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051400256 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 1702 | keep | 0 | May | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
ARECIBO | 2022-05-14 18:44 | 2022-05-14 19:30 | 60 | 000:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22051400131 | New_Event | Wire Down | Include | Include | Equipment | 46 | 2022-05-14 | 2760 | keep | 0 | May | 2022 | 0.0018798 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-05-14 18:49 | 2022-05-15 09:50 | 20 | 015:01 | P | DESGANCHE | 1 X 40 EN CONVERTIDOR POR DESGANCHE | A22051400133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 901 | 2022-05-14 | 18020 | keep | 0 | May | 2022 | 0.012273 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-14 19:09 | 2022-05-14 19:10 | 718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051400260 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-14 | 718 | keep | 0 | May | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
CAGUAS | 2022-05-14 19:18 | 2022-05-15 07:37 | 100 | 012:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C22051400261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 739 | 2022-05-14 | 73900 | keep | 0 | May | 2022 | 0.050333 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-14 19:20 | 2022-05-15 06:49 | 80 | 011:29 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22051400262 | New_Event | Animals | Include | Include | Wildlife | 689 | 2022-05-14 | 55120 | keep | 0 | May | 2022 | 0.037542 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-05-14 20:47 | 2022-05-15 08:40 | 50 | 011:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22051400149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 713 | 2022-05-14 | 35650 | keep | 0 | May | 2022 | 0.024281 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-14 21:02 | 2022-05-15 02:00 | 50 | 004:58 | P | NO SE REPORTO CAUSA | SE CERRO FUSIBLE QUE ESTABA ABIERTO NO FUNDIDO | P22051400066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 298 | 2022-05-14 | 14900 | keep | 0 | May | 2022 | 0.010148 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-05-14 21:21 | 2022-05-15 11:54 | 47 | 014:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L Y X 50 EN C/L MAL TIEMPO | R22051400203 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 873 | 2022-05-14 | 41031 | keep | 0 | May | 2022 | 0.027946 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
HUMACAO | 2022-05-14 22:40 | 2022-05-15 09:28 | 10 | 010:48 | P | SECUNDARIA/DESGANCHE | SE REPARO BAJANTE Y DESGANCHE SECUNDARIO | C22051400279 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 648 | 2022-05-14 | 6480 | keep | 0 | May | 2022 | 0.0044135 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-05-15 | 2022-05-15 10:45 | 7 | 010:45 | P | ANIMAL | 1 X 8 EN XMR CRUCE POR AVE | C22051500001 | New_Event | Animals | Include | Include | Wildlife | 645 | 2022-05-15 | 4515 | keep | 0 | May | 2022 | 0.0030751 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-05-15 00:15 | 2022-05-15 00:30 | 12 | 000:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA SECCIONALIZAR LINEA SECUNDARIA AVERIADA | M22051400244 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2022-05-15 | 180 | keep | 0 | May | 2022 | 0.0001226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-15 01:12 | 2022-05-15 15:05 | 6 | 013:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A22051500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 833 | 2022-05-15 | 4998 | keep | 0 | May | 2022 | 0.0034041 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-15 01:59 | 2022-05-16 14:43 | 25 | 036:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2204 | 2022-05-15 | 55100 | keep | 0 | May | 2022 | 0.037528 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-05-15 02:51 | 2022-05-15 19:20 | 5 | 016:29 | P | CAUSAS EXTERNAS | 1 X 100 EN CORTE DE LINEA SE RETIRO CHIRINGA SOBRE LINEAS PRIMARIAS LINEAS PRIMARIAS | M22051500002 | New_Event | Damage From Public | Include | Include | Public | 989 | 2022-05-15 | 4945 | keep | 0 | May | 2022 | 0.003368 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-15 05:49 | 2022-05-15 12:15 | 874 | 006:26 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA ROTA EN TRONCAL, SE ABRIO EL INTERRUPTOR PARA RETIRAR PELIGRO SUBESTACION SIN RTU | M22051500004 | New_Event | Primary Wire Break | Include | Include | Equipment | 386 | 2022-05-15 | 337364 | keep | 0 | May | 2022 | 0.22978 | 0.00059528 | Sustained | FALSE | FALSE | Not_TMED_Event | 874
CAGUAS | 2022-05-15 05:54 | 2022-05-15 05:55 | 1922 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C22051500000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-05-15 | 1922 | keep | 0 | May | 2022 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CANOVANAS | 2022-05-15 06:22 | 2022-05-15 06:25 | 4085 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 2404-08 | R22051500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-15 | 12255 | keep | 0 | May | 2022 | 0.0083468 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-05-15 06:22 | 2022-05-15 06:25 | 2675 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 2402-03 | R22051500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-15 | 8025 | keep | 0 | May | 2022 | 0.0054658 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
BAYAMON | 2022-05-15 06:34 | 2022-05-15 06:35 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22051500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 2605 | keep | 0 | May | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-05-15 06:34 | 2022-05-15 06:35 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22051500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 73 | keep | 0 | May | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
CAGUAS | 2022-05-15 06:38 | 2022-05-15 12:56 | 40 | 006:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22051500012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 378 | 2022-05-15 | 15120 | keep | 0 | May | 2022 | 0.010298 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-05-15 06:47 | 2022-05-15 10:48 | 204 | 004:01 | P | NO SE REPORTO CAUSA | 1 X 65 Y X 40 EN C/L | R22051500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2022-05-15 | 49164 | keep | 0 | May | 2022 | 0.033485 | 0.00013894 | Sustained | FALSE | FALSE | Not_TMED_Event | 204
MAYAGÃœEZ | 2022-05-15 06:49 | 2022-05-15 11:25 | 350 | 004:36 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22051500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-05-15 | 96600 | keep | 0 | May | 2022 | 0.065794 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
MAYAGÃœEZ | 2022-05-15 07:11 | 2022-05-15 12:35 | 150 | 005:24 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22051500009 | New_Event | Animals | Include | Include | Wildlife | 324 | 2022-05-15 | 48600 | keep | 0 | May | 2022 | 0.033101 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-05-15 07:15 | 2022-05-15 18:41 | 30 | 011:26 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 686 | 2022-05-15 | 20580 | keep | 0 | May | 2022 | 0.014017 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-15 07:24 | 2022-05-15 15:20 | 1 | 007:56 | P | NO SE REPORTO CAUSA | 2 X 10 EN BANCO DE TRANSFORMADORES | C22051500029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 476 | 2022-05-15 | 476 | keep | 0 | May | 2022 | 0.0003242 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-05-15 07:26 | 2022-05-15 09:46 | 235 | 002:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R22051500017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2022-05-15 | 32900 | keep | 0 | May | 2022 | 0.022408 | 0.00016006 | Sustained | FALSE | FALSE | Not_TMED_Event | 235
BAYAMON | 2022-05-15 07:34 | 2022-05-15 14:18 | 100 | 006:44 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE PARA CERRAR PUENTE ABIERTO. SE TRABAJO CON SWITCH FORM BY-220515-01 | B22051500005 | New_Event | Primary Wire Break | Include | Include | Equipment | 404 | 2022-05-15 | 40400 | keep | 0 | May | 2022 | 0.027516 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-15 07:51 | 2022-05-15 13:02 | 120 | 005:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 40 EN C/L MAL TIEMPO | R22051500019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 311 | 2022-05-15 | 37320 | keep | 0 | May | 2022 | 0.025418 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-05-15 08:04 | 2022-05-15 09:36 | 79 | 001:32 | P | ANIMAL | 1X50 EN C/L (POR AVE EN EL 13KV) | B22051500010 | New_Event | Animals | Include | Include | Wildlife | 92 | 2022-05-15 | 7268 | keep | 0 | May | 2022 | 0.0049502 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
VEGA BAJA | 2022-05-15 08:05 | 2022-05-15 12:34 | 9 | 004:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR EN BAJANTE SECUNDARIO. | B22051400024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 269 | 2022-05-15 | 2421 | keep | 0 | May | 2022 | 0.0016489 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-05-15 08:15 | 2022-05-15 09:15 | 173 | 001:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE ARBOL SOBRE LINEA | P22051500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-05-15 | 10380 | keep | 0 | May | 2022 | 0.0070698 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
ARECIBO | 2022-05-15 08:25 | 2022-05-15 16:08 | 15 | 007:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | A22051500010 | New_Event | Cutout Failure | Include | Include | Equipment | 463 | 2022-05-15 | 6945 | keep | 0 | May | 2022 | 0.0047302 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-05-15 08:33 | 2022-05-15 13:12 | 40 | 004:39 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C22051500030 | New_Event | Animals | Include | Include | Wildlife | 279 | 2022-05-15 | 11160 | keep | 0 | May | 2022 | 0.007601 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-05-15 08:37 | 2022-05-15 09:45 | 35 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO CAUSA | P22051500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-05-15 | 2380 | keep | 0 | May | 2022 | 0.001621 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-05-15 08:38 | 2022-05-15 08:39 | 1922 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C22051500000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-05-15 | 1922 | keep | 0 | May | 2022 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2022-05-15 08:42 | 2022-05-15 09:45 | 1922 | 001:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO | R22051500000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 63 | 2022-05-15 | 121086 | keep | 0 | May | 2022 | 0.082471 | 0.0013091 | Sustained | FALSE | FALSE | Not_TMED_Event | 1922
CANOVANAS | 2022-05-15 08:47 | 2022-05-15 14:42 | 3 | 005:55 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R22051500025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2022-05-15 | 1065 | keep | 0 | May | 2022 | 0.00072537 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-05-15 09:01 | 2022-05-15 09:02 | 76 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22051500027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 76 | keep | 0 | May | 2022 | 5.1763e-05 | 5.1763e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 76
BAYAMON | 2022-05-15 09:03 | 2022-05-15 11:39 | 12 | 002:36 | P | NO SE REPORTO CAUSA | 1X15 EN XMER | B22051500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2022-05-15 | 1872 | keep | 0 | May | 2022 | 0.001275 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-15 09:07 | 2022-05-16 01:50 | 15 | 016:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | M22051500022 | New_Event | Cutout Failure | Include | Include | Equipment | 1003 | 2022-05-15 | 15045 | keep | 0 | May | 2022 | 0.010247 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-05-15 09:13 | 2022-05-16 08:46 | 1 | 023:33 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R22051500029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1413 | 2022-05-15 | 1413 | keep | 0 | May | 2022 | 0.00096239 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-15 09:19 | 2022-05-15 18:17 | 12 | 008:58 | P | ERROR HUMANO | SE REMPLAZO TRANSFORMADOR DE 50 KVA @ 2400 POR UNO DE 50 KVA @ 4,160 YA QUE SE HABIA INSTALADO INCORRECTAMENTE | M22051500023 | New_Event | Human Error | Include | Include | Other | 538 | 2022-05-15 | 6456 | keep | 0 | May | 2022 | 0.0043972 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-15 09:45 | 2022-05-15 11:38 | 1044 | 001:53 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES QUEMADOS | R22051500000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 113 | 2022-05-15 | 117972 | keep | 0 | May | 2022 | 0.08035 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-15 09:53 | 2022-05-15 09:54 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 2126 | keep | 0 | May | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
SAN JUAN | 2022-05-15 10:20 | 2022-05-15 21:08 | 12 | 010:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S22051500010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 648 | 2022-05-15 | 7776 | keep | 0 | May | 2022 | 0.0052962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-15 10:20 | 2022-05-15 13:00 | 47 | 002:40 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZARON CONEXIONES EN PARARRAYO Y | P22051500012 | New_Event | Primary Wire Break | Include | Include | Equipment | 160 | 2022-05-15 | 7520 | keep | 0 | May | 2022 | 0.0051218 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
CAGUAS | 2022-05-15 10:39 | 2022-05-15 14:01 | 60 | 003:22 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C22051500086 | New_Event | Animals | Include | Include | Wildlife | 202 | 2022-05-15 | 12120 | keep | 0 | May | 2022 | 0.0082549 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-15 10:45 | 2022-05-15 10:48 | 2000 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL 2000 CLIENTES POR 1619-02 | R22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-15 | 6000 | keep | 0 | May | 2022 | 0.0040866 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
CAGUAS | 2022-05-15 10:50 | 2022-05-15 14:59 | 52 | 004:09 | P | TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO TERMINACION QUEMADA EN RISER A SU2 | C22051400177 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 249 | 2022-05-15 | 12948 | keep | 0 | May | 2022 | 0.0088188 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-15 10:53 | 2022-05-15 10:54 | 4481 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 30% POR 1619-2 | S22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 4481 | keep | 0 | May | 2022 | 0.003052 | 0.003052 | Momentary | FALSE | FALSE | Not_TMED_Event | 4481
UTUADO | 2022-05-15 10:55 | 2022-05-15 14:13 | 30 | 003:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051500015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 198 | 2022-05-15 | 5940 | keep | 0 | May | 2022 | 0.0040457 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-15 11:01 | 2022-05-15 18:50 | 50 | 007:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M22051500032 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 469 | 2022-05-15 | 23450 | keep | 0 | May | 2022 | 0.015972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-05-15 11:21 | 2022-05-15 14:40 | 60 | 003:19 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22051500123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-05-15 | 11940 | keep | 0 | May | 2022 | 0.0081323 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-15 11:22 | 2022-05-15 11:24 | 1106 | 000:02 | P | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 60% POR 1529-15 | S22051500000 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-05-15 | 2212 | keep | 0 | May | 2022 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
BAYAMON | 2022-05-15 11:22 | 2022-05-15 11:24 | 1802 | 000:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 60% DEL 1346-2 | S22051500000 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-05-15 | 3604 | keep | 0 | May | 2022 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2022-05-15 11:24 | 2022-05-15 12:39 | 368 | 001:15 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PUENTE PRIMARIO ABIERTO | S22051500032 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 75 | 2022-05-15 | 27600 | keep | 0 | May | 2022 | 0.018798 | 0.00025064 | Sustained | FALSE | FALSE | Not_TMED_Event | 368
BAYAMON | 2022-05-15 11:24 | 2022-05-15 12:39 | 600 | 001:15 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PUENTE PRIMARIO ABIERTO | S22051500032 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 75 | 2022-05-15 | 45000 | keep | 0 | May | 2022 | 0.030649 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-05-15 11:29 | 2022-05-15 12:15 | 80 | 000:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22051500027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 46 | 2022-05-15 | 3680 | keep | 0 | May | 2022 | 0.0025064 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-15 11:49 | 2022-05-15 14:37 | 120 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22051500053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-05-15 | 20160 | keep | 0 | May | 2022 | 0.013731 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-05-15 11:53 | 2022-05-15 11:55 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22051500033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-15 | 4468 | keep | 0 | May | 2022 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2022-05-15 11:59 | 2022-05-15 12:00 | 2888 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22051500023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 2888 | keep | 0 | May | 2022 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
AGUADILLA | 2022-05-15 12:07 | 2022-05-15 12:09 | 4882 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN ON SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M22051500045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-15 | 9764 | keep | 0 | May | 2022 | 0.0066502 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
MAYAGÃœEZ | 2022-05-15 12:13 | 2022-05-15 12:14 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-15 12:13 | 2022-05-15 12:14 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22051500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-15 12:15 | 2022-05-15 14:23 | 974 | 002:08 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR Y SE ABRIO PUENTES PARA SECCIONALIZAR LINEA PRIMARIA ROTA Y POSTE EN TRONCAL, SE CERRO EL INTERRUPTOR SIN SERVICIO 174 CLIENTES | M22051500048 | New_Event | Primary Wire Break | Include | Include | Equipment | 128 | 2022-05-15 | 124672 | keep | 0 | May | 2022 | 0.084914 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
SAN JUAN | 2022-05-15 12:21 | 2022-05-15 19:08 | 15 | 006:47 | P | PROBLEMA DEL CLIENTE | 1 X 65 EN C/L SE DEJO FUERA CALVIN SCHOOL POR MANTENIENTO (DESGANCHE) | R22051500043 | New_Event | Customer-Related Interruption | Include | Include | Public | 407 | 2022-05-15 | 6105 | keep | 0 | May | 2022 | 0.0041581 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-15 12:39 | 2022-05-15 15:01 | 1106 | 002:22 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA REPARAR PUENTE PRIMARIO ABIERTO 60% POR 1529-15 | S22051500032 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 142 | 2022-05-15 | 157052 | keep | 0 | May | 2022 | 0.10697 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-15 12:39 | 2022-05-15 15:01 | 1802 | 002:22 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA REPARAR PUENTE PRIMARIO ABIERTO LLEVA 60% DEL 1346-2 | S22051500032 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 142 | 2022-05-15 | 255884 | keep | 0 | May | 2022 | 0.17428 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-15 12:47 | 2022-05-15 12:48 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051500054 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-15 12:47 | 2022-05-15 12:48 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051500054 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
BAYAMON | 2022-05-15 12:56 | 2022-05-15 12:57 | 1079 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 1079 | keep | 0 | May | 2022 | 0.0007349 | 0.0007349 | Momentary | FALSE | FALSE | Not_TMED_Event | 1079
MAYAGÃœEZ | 2022-05-15 12:57 | 2022-05-15 12:58 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051500059 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-15 12:57 | 2022-05-15 12:58 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M22051500059 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
BAYAMON | 2022-05-15 13:02 | 2022-05-15 16:05 | 90 | 003:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO AISLADOR | B22051500038 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 183 | 2022-05-15 | 16470 | keep | 0 | May | 2022 | 0.011218 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-05-15 13:07 | 2022-05-15 16:55 | 15 | 003:48 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S22051500095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2022-05-15 | 3420 | keep | 0 | May | 2022 | 0.0023293 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-15 13:13 | 2022-05-15 19:44 | 1 | 006:31 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | R22051500117 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 391 | 2022-05-15 | 391 | keep | 0 | May | 2022 | 0.00026631 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-15 13:16 | 2022-05-15 13:17 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051500071 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-15 13:16 | 2022-05-15 13:17 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M22051500071 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
CANOVANAS | 2022-05-15 13:19 | 2022-05-15 17:07 | 1 | 003:48 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN XMR CLIENTE TIENE QUE REEMPLAZAR CAJA PRIMARIA | S22051500047 | New_Event | Customer-Related Interruption | Include | Include | Public | 228 | 2022-05-15 | 228 | keep | 0 | May | 2022 | 0.00015529 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-15 13:26 | 2022-05-15 13:27 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051500082 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-15 13:26 | 2022-05-15 13:27 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M22051500082 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-15 13:37 | 2022-05-15 16:16 | 4664 | 002:39 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 6012-03 EL CUAL LLEVA LA CARGA DEL 6014-03 SE ABRIO EL AMARRE. SE CERRO EL INTERRUPTOR Y VOLVIO A DISPARARSE. | M22051500089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2022-05-15 | 741576 | keep | 0 | May | 2022 | 0.50508 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2022-05-15 13:37 | 2022-05-15 17:15 | 871 | 003:38 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR EL CUAL LLEVA LA CARGA DEL 6014-03 NO SE DETERMINO CAUSA | M22051500089 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 218 | 2022-05-15 | 189878 | keep | 0 | May | 2022 | 0.12933 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
FAJARDO | 2022-05-15 13:43 | 2022-05-15 20:31 | 200 | 006:48 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN CORTES DE LINEA | R22051500049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2022-05-15 | 81600 | keep | 0 | May | 2022 | 0.055577 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-15 13:44 | 2022-05-15 14:25 | 6 | 000:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR TOMA. | B22051500041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 41 | 2022-05-15 | 246 | keep | 0 | May | 2022 | 0.00016755 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-15 13:56 | 2022-05-16 01:40 | 90 | 011:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | M22051500105 | New_Event | Primary Wire Break | Include | Include | Equipment | 704 | 2022-05-15 | 63360 | keep | 0 | May | 2022 | 0.043154 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-05-15 13:56 | 2022-05-15 19:49 | 8 | 005:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | A22051500031 | New_Event | Cutout Failure | Include | Include | Equipment | 353 | 2022-05-15 | 2824 | keep | 0 | May | 2022 | 0.0019234 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-05-15 14:00 | 2022-05-16 10:55 | 60 | 020:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | A22051500032 | New_Event | Primary Wire Break | Include | Include | Equipment | 1255 | 2022-05-15 | 75300 | keep | 0 | May | 2022 | 0.051286 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-05-15 14:17 | 2022-05-15 14:18 | 1463 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 1463 | keep | 0 | May | 2022 | 0.00099644 | 0.00099644 | Momentary | FALSE | FALSE | Not_TMED_Event | 1463
FAJARDO | 2022-05-15 14:18 | 2022-05-15 16:12 | 292 | 001:54 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR EN EL SUELO | R22051500086 | New_Event | Primary Wire Break | Include | Include | Equipment | 114 | 2022-05-15 | 33288 | keep | 0 | May | 2022 | 0.022672 | 0.00019888 | Sustained | FALSE | FALSE | Not_TMED_Event | 292
MAYAGÃœEZ | 2022-05-15 14:23 | 2022-05-16 14:52 | 800 | 024:29 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PARTIDO | M22051500048 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1469 | 2022-05-15 | 1175200 | keep | 0 | May | 2022 | 0.80042 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
AGUADILLA | 2022-05-15 14:23 | 2022-05-15 20:15 | 10 | 005:52 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DEL TRANSFORMADOR | M22051500118 | New_Event | Primary Wire Break | Include | Include | Equipment | 352 | 2022-05-15 | 3520 | keep | 0 | May | 2022 | 0.0023975 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-15 14:28 | 2022-05-15 20:23 | 200 | 005:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L Y 1 X 80 EN C/L MAL TIEMPO | R22051500063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 355 | 2022-05-15 | 71000 | keep | 0 | May | 2022 | 0.048358 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-05-15 14:34 | 2022-05-15 16:06 | 1 | 001:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO TOMA | C22051500131 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2022-05-15 | 92 | keep | 0 | May | 2022 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-15 14:48 | 2022-05-16 12:15 | 15 | 021:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA QUEMADO | C22051500133 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1287 | 2022-05-15 | 19305 | keep | 0 | May | 2022 | 0.013149 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-05-15 15:14 | 2022-05-15 15:15 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051500021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
BAYAMON | 2022-05-15 15:34 | 2022-05-15 17:49 | 80 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | S22051500116 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2022-05-15 | 10800 | keep | 0 | May | 2022 | 0.0073558 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-05-15 15:35 | 2022-05-16 08:48 | 3 | 017:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA NEUTRAL | R22051500076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1033 | 2022-05-15 | 3099 | keep | 0 | May | 2022 | 0.0021107 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-05-15 15:41 | 2022-05-15 21:07 | 30 | 005:26 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA. 1 X 20 EN TRANSFORMADOR SE ELIMINO PARARRAYO | S22051500117 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 326 | 2022-05-15 | 9780 | keep | 0 | May | 2022 | 0.0066611 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-15 16:05 | 2022-05-15 16:06 | 130 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 1717-04 LLEVANDO 20% 1716-02 | B22051500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-15 | 130 | keep | 0 | May | 2022 | 8.8542e-05 | 8.8542e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2022-05-15 16:05 | 2022-05-15 16:06 | 1362 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 1717-04 LLEVANDO 20% 1716-02 | B22051500000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-15 | 1362 | keep | 0 | May | 2022 | 0.00092765 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-15 16:06 | 2022-05-15 16:09 | 90 | 000:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO AISLADOR | B22051500038 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2022-05-15 | 270 | keep | 0 | May | 2022 | 0.0001839 | 6.1299e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-05-15 16:09 | 2022-05-15 16:10 | 130 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 1717-04 LLEVANDO 20% 1716-02 | B22051500000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-15 | 130 | keep | 0 | May | 2022 | 8.8542e-05 | 8.8542e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2022-05-15 16:09 | 2022-05-15 16:10 | 1362 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 1717-04 LLEVANDO 20% 1716-02 | B22051500000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-15 | 1362 | keep | 0 | May | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2022-05-15 16:10 | 2022-05-15 16:48 | 90 | 000:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO AISLADOR | B22051500038 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 38 | 2022-05-15 | 3420 | keep | 0 | May | 2022 | 0.0023293 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2022-05-15 16:12 | 2022-05-15 18:44 | 1463 | 002:32 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO ALIMENTADOR A PETICION DE VICTOR CEPEDA POR ALAMBRE EN EL PISO FRENTE A LA SUBESTACION SE SECCIONALIZO 40% EN SERVICIO | R22051500086 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 152 | 2022-05-15 | 222376 | keep | 0 | May | 2022 | 0.15146 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-15 16:16 | 2022-05-16 09:20 | 25 | 017:04 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE DESGANCHO | C22051500141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1024 | 2022-05-15 | 25600 | keep | 0 | May | 2022 | 0.017436 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-15 16:18 | 2022-05-15 17:15 | 4664 | 000:57 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETES DEL 6012-02 (FID:23558574) SE CERRO EL AMARRE CON EL 6014-03 Y SE CERRO EL INTERRUPTOR | M22051500156 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-05-15 | 265848 | keep | 0 | May | 2022 | 0.18107 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-15 16:21 | 2022-05-15 18:00 | 19 | 001:39 | P | ANIMAL | 1X 50 EN CORTE DE LINEA GLOBO DE HELIO EN LINEA | P22051500024 | New_Event | Animals | Include | Include | Wildlife | 99 | 2022-05-15 | 1881 | keep | 0 | May | 2022 | 0.0012811 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-05-15 16:39 | 2022-05-15 21:55 | 70 | 005:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA PRIMARIA. NO FUNDIO FUSIBLE | B22051500045 | New_Event | Primary Wire Break | Include | Include | Equipment | 316 | 2022-05-15 | 22120 | keep | 0 | May | 2022 | 0.015066 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-05-15 16:43 | 2022-05-16 06:31 | 10 | 013:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR POR LLUVIAS | M22051500163 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 828 | 2022-05-15 | 8280 | keep | 0 | May | 2022 | 0.0056395 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-15 16:48 | 2022-05-15 16:49 | 130 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 1717-04 LLEVANDO 20% 1716-02 | B22051500000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-15 | 130 | keep | 0 | May | 2022 | 8.8542e-05 | 8.8542e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2022-05-15 16:48 | 2022-05-15 16:49 | 1362 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE 1717-04 LLEVANDO 20% 1716-02 | B22051500000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-15 | 1362 | keep | 0 | May | 2022 | 0.00092765 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-15 16:49 | 2022-05-15 17:41 | 90 | 000:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO AISLADOR | B22051500038 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 52 | 2022-05-15 | 4680 | keep | 0 | May | 2022 | 0.0031875 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-05-15 16:56 | 2022-05-15 18:38 | 10 | 001:42 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A22051500040 | New_Event | Animals | Include | Include | Wildlife | 102 | 2022-05-15 | 1020 | keep | 0 | May | 2022 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-05-15 17:09 | 2022-05-16 14:15 | 30 | 021:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051500042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1266 | 2022-05-15 | 37980 | keep | 0 | May | 2022 | 0.025868 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-15 17:15 | 2022-05-15 17:54 | 450 | 000:39 | T | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE ENCONTRO CAUSA SE CERRO MACHETES (FID:23558574) | M22051500156 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-05-15 | 17550 | keep | 0 | May | 2022 | 0.011953 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-15 17:24 | 2022-05-15 18:54 | 40 | 001:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051500176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-05-15 | 3600 | keep | 0 | May | 2022 | 0.0024519 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-15 17:34 | 2022-05-15 17:38 | 36 | 000:04 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN CORTES DE LINEA | C22051400240 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-05-15 | 144 | keep | 0 | May | 2022 | 9.8078e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-05-15 17:40 | 2022-05-15 18:26 | 10 | 000:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONECTOR SECUNDARIO | S22051500019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2022-05-15 | 460 | keep | 0 | May | 2022 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-05-15 17:57 | 2022-05-15 19:38 | 17 | 001:41 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO PUENTE SAFADO EN TRANSFORMADOR | P22051500026 | New_Event | Primary Wire Break | Include | Include | Equipment | 101 | 2022-05-15 | 1717 | keep | 0 | May | 2022 | 0.0011694 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2022-05-15 18:24 | 2022-05-16 11:30 | 60 | 017:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 40 EN C/L SE REMPLAZO AISLADOR | C22051500145 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1026 | 2022-05-15 | 61560 | keep | 0 | May | 2022 | 0.041928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-05-15 18:29 | 2022-05-15 18:30 | 3766 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 3766 | keep | 0 | May | 2022 | 0.002565 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
MAYAGÃœEZ | 2022-05-15 18:36 | 2022-05-15 19:44 | 10 | 001:08 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR SE DESGANCHO EN LINEAS SECUNDARIAS | M22051500204 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 68 | 2022-05-15 | 680 | keep | 0 | May | 2022 | 0.00046314 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-15 18:37 | 2022-05-15 18:38 | 8711 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO PARTE POR 1206-03 | S22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 8711 | keep | 0 | May | 2022 | 0.005933 | 0.005933 | Momentary | FALSE | FALSE | Not_TMED_Event | 8711
SAN JUAN | 2022-05-15 18:37 | 2022-05-15 18:38 | 2633 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO PARTE DEL 1206-3 ESTA POR 1620-5 | S22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 2633 | keep | 0 | May | 2022 | 0.0017933 | 0.0017933 | Momentary | FALSE | FALSE | Not_TMED_Event | 2633
FAJARDO | 2022-05-15 18:44 | 2022-05-15 18:59 | 878 | 000:15 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE EN EL SUELO Y SE NORMALIZO 100% EN SERVICIO | R22051500086 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 15 | 2022-05-15 | 13170 | keep | 0 | May | 2022 | 0.00897 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-15 19:05 | 2022-05-15 23:29 | 25 | 004:24 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA Y SE DESCRUZO LINEAS | B22051500048 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 264 | 2022-05-15 | 6600 | keep | 0 | May | 2022 | 0.0044952 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-05-15 19:07 | 2022-05-15 19:08 | 128 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 128 | keep | 0 | May | 2022 | 8.718e-05 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2022-05-15 19:07 | 2022-05-15 19:08 | 273 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 273 | keep | 0 | May | 2022 | 0.00018594 | 0.00018594 | Momentary | FALSE | FALSE | Not_TMED_Event | 273
CAGUAS | 2022-05-15 19:07 | 2022-05-15 19:08 | 1772 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 1772 | keep | 0 | May | 2022 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
CAGUAS | 2022-05-15 19:08 | 2022-05-15 20:48 | 200 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22051500148 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-05-15 | 20000 | keep | 0 | May | 2022 | 0.013622 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-15 19:23 | 2022-05-16 04:25 | 30 | 009:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051500218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 542 | 2022-05-15 | 16260 | keep | 0 | May | 2022 | 0.011075 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-15 19:28 | 2022-05-16 11:00 | 39 | 015:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22051500159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 932 | 2022-05-15 | 36348 | keep | 0 | May | 2022 | 0.024756 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BARRANQUITAS | 2022-05-15 20:27 | 2022-05-16 07:25 | 200 | 010:58 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22051500168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 658 | 2022-05-15 | 131600 | keep | 0 | May | 2022 | 0.089632 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-05-15 20:32 | 2022-05-15 20:33 | 3766 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22051500130 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-15 | 3766 | keep | 0 | May | 2022 | 0.002565 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
MAYAGÃœEZ | 2022-05-15 20:37 | 2022-05-16 03:00 | 100 | 006:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051500238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2022-05-15 | 38300 | keep | 0 | May | 2022 | 0.026086 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-15 21:19 | 2022-05-16 18:35 | 200 | 021:16 | P | DESGANCHE | SE REPARO LINEA PRIMARIA ROTA A CAUSA DE BAMBUAS ENCIMA DE LINEAS PRIMARIAS SE REALIZO DESGANCHE | M22051500252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1276 | 2022-05-15 | 255200 | keep | 0 | May | 2022 | 0.17382 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-15 21:58 | 2022-05-16 09:40 | 300 | 011:42 | P | NO SE REPORTO CAUSA | 1X140 EN CONVERTIDOR | S22051500140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 702 | 2022-05-15 | 210600 | keep | 0 | May | 2022 | 0.14344 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
FAJARDO | 2022-05-15 22:39 | 2022-05-16 10:28 | 80 | 011:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22051500138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 709 | 2022-05-15 | 56720 | keep | 0 | May | 2022 | 0.038632 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-05-15 23:00 | 2022-05-16 09:11 | 170 | 010:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 140 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | M22051500271 | New_Event | Cutout Failure | Include | Include | Equipment | 611 | 2022-05-15 | 103870 | keep | 0 | May | 2022 | 0.070745 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
BAYAMON | 2022-05-15 23:24 | 2022-05-16 08:57 | 10 | 009:33 | P | DESGANCHE | 1X30 EN C/L (SERA REFERIDO PARA DESGANCHE) | B22051500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 573 | 2022-05-15 | 5730 | keep | 0 | May | 2022 | 0.0039027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-05-15 23:56 | 2022-05-16 11:26 | 40 | 011:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P22051500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 690 | 2022-05-15 | 27600 | keep | 0 | May | 2022 | 0.018798 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-16 | 2022-05-16 06:10 | 15 | 006:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA DE TRANSFORMADOR AVERIADA SE ABRIO CORTE DE LINEA PARA REMPLAZARLA | A22051600275 | New_Event | Cutout Failure | Include | Include | Equipment | 370 | 2022-05-16 | 5550 | keep | 0 | May | 2022 | 0.0037801 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-16 00:05 | 2022-05-16 00:06 | 2324 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 2324 | keep | 0 | May | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
HUMACAO | 2022-05-16 00:24 | 2022-05-16 07:35 | 20 | 007:11 | P | DESGANCHE | 1 X 25 EN C/L SE REALIZO DESGANCHE | C22051600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 431 | 2022-05-16 | 8620 | keep | 0 | May | 2022 | 0.005871 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-05-16 02:45 | 2022-05-16 05:54 | 80 | 003:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22051600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2022-05-16 | 15120 | keep | 0 | May | 2022 | 0.010298 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-16 04:37 | 2022-05-16 10:57 | 150 | 006:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA CAMBIO DE AISLADOR | M22051600013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 380 | 2022-05-16 | 57000 | keep | 0 | May | 2022 | 0.038822 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-16 05:31 | 2022-05-17 05:40 | 30 | 024:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051600015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1449 | 2022-05-16 | 43470 | keep | 0 | May | 2022 | 0.029607 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:14 | 2231 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-16 | 8924 | keep | 0 | May | 2022 | 0.0060781 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:14 | 1923 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-16 | 7692 | keep | 0 | May | 2022 | 0.005239 | 0.0013097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1923
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:14 | 1066 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-16 | 4264 | keep | 0 | May | 2022 | 0.0029042 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:14 | 141 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-16 | 564 | keep | 0 | May | 2022 | 0.00038414 | 9.6034e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 141
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:22 | 425 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-05-16 | 5100 | keep | 0 | May | 2022 | 0.0034736 | 0.00028947 | Sustained | FALSE | FALSE | Not_TMED_Event | 425
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:22 | 1494 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-05-16 | 17928 | keep | 0 | May | 2022 | 0.012211 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:22 | 3654 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-05-16 | 43848 | keep | 0 | May | 2022 | 0.029865 | 0.0024887 | Sustained | FALSE | FALSE | Not_TMED_Event | 3654
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:22 | 2888 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-05-16 | 34656 | keep | 0 | May | 2022 | 0.023604 | 0.001967 | Sustained | FALSE | FALSE | Not_TMED_Event | 2888
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:14 | 2107 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-16 | 8428 | keep | 0 | May | 2022 | 0.0057403 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:14 | 308 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-16 | 1232 | keep | 0 | May | 2022 | 0.00083911 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:14 | 2697 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-16 | 10788 | keep | 0 | May | 2022 | 0.0073477 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:14 | 67 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-16 | 268 | keep | 0 | May | 2022 | 0.00018253 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:15 | 1879 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-16 | 9395 | keep | 0 | May | 2022 | 0.0063989 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:15 | 2777 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-16 | 13885 | keep | 0 | May | 2022 | 0.009457 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:15 | 2 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-16 | 10 | keep | 0 | May | 2022 | 6.811e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:15 | 2839 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-16 | 14195 | keep | 0 | May | 2022 | 0.0096681 | 0.0019336 | Momentary | FALSE | FALSE | Not_TMED_Event | 2839
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:15 | 1160 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-16 | 5800 | keep | 0 | May | 2022 | 0.0039504 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
ARECIBO | 2022-05-16 06:10 | 2022-05-16 06:15 | 1860 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CAUSO QUE SE ABRIERA EL BANCO DE 115 A 38KV DE MANATI TC | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-16 | 9300 | keep | 0 | May | 2022 | 0.0063342 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
CANOVANAS | 2022-05-16 06:14 | 2022-05-16 14:04 | 3 | 007:50 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22051600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 470 | 2022-05-16 | 1410 | keep | 0 | May | 2022 | 0.00096034 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-05-16 06:14 | 2022-05-16 18:31 | 15 | 012:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA DE TRANSFORMADOR AVERIADA SE ABRIO CORTE DE LINEA PARA REMPLAZARLA | A22051600275 | New_Event | Cutout Failure | Include | Include | Equipment | 737 | 2022-05-16 | 11055 | keep | 0 | May | 2022 | 0.0075295 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-05-16 06:59 | 2022-05-16 07:00 | 215 | 000:01 | T | MAL TIEMPO/LLUVIA O VIENTO | SE CERRO POR CONTROL | B22051600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-05-16 | 215 | keep | 0 | May | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-05-16 07:00 | 2022-05-16 15:05 | 200 | 008:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L POR FUERTE LLUVIA | B22051600006 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 485 | 2022-05-16 | 97000 | keep | 0 | May | 2022 | 0.066066 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-16 07:13 | 2022-05-16 09:20 | 70 | 002:07 | P | ANIMAL | 1X50 EN C/L & SE RETIRO AVE | B22051600009 | New_Event | Animals | Include | Include | Wildlife | 127 | 2022-05-16 | 8890 | keep | 0 | May | 2022 | 0.0060549 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-05-16 07:14 | 2022-05-16 12:17 | 40 | 005:03 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | R22051600005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 303 | 2022-05-16 | 12120 | keep | 0 | May | 2022 | 0.0082549 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-05-16 07:21 | 2022-05-16 07:22 | 4132 | 000:01 | T | DESGANCHE | RECIERRE CARGA POR 4006-05 | P22051600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-16 | 4132 | keep | 0 | May | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-05-16 07:21 | 2022-05-16 07:22 | 4279 | 000:01 | T | DESGANCHE | RECIERRE CARGA POR 4006-05 | P22051600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-16 | 4279 | keep | 0 | May | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-05-16 07:21 | 2022-05-16 07:22 | 464 | 000:01 | T | DESGANCHE | RECIERRE LLEVA CARGA DE 4003-01,02 | P22051600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-16 | 464 | keep | 0 | May | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-05-16 07:36 | 2022-05-16 09:20 | 67 | 001:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22051600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-05-16 | 6968 | keep | 0 | May | 2022 | 0.0047459 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
AGUADILLA | 2022-05-16 07:51 | 2022-05-16 13:27 | 1 | 005:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | M22051600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 336 | 2022-05-16 | 336 | keep | 0 | May | 2022 | 0.00022885 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-16 07:53 | 2022-05-16 10:30 | 35 | 002:37 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA SE RETIRO PALOMA CRUZADA CON FASE | P22051600012 | New_Event | Animals | Include | Include | Wildlife | 157 | 2022-05-16 | 5495 | keep | 0 | May | 2022 | 0.0037426 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-05-16 08:02 | 2022-05-16 08:03 | 4641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 4641 | keep | 0 | May | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
ARECIBO | 2022-05-16 08:11 | 2022-05-16 17:16 | 40 | 009:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22051600089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 545 | 2022-05-16 | 21800 | keep | 0 | May | 2022 | 0.014848 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-16 08:15 | 2022-05-16 08:16 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | C22051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 2178 | keep | 0 | May | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CANOVANAS | 2022-05-16 08:27 | 2022-05-16 14:53 | 86 | 006:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R22051600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 386 | 2022-05-16 | 33196 | keep | 0 | May | 2022 | 0.02261 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
BAYAMON | 2022-05-16 08:31 | 2022-05-16 12:48 | 4 | 004:17 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L SE REEMPLAZO CAJA PRIMARIA | S22051600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 257 | 2022-05-16 | 1028 | keep | 0 | May | 2022 | 0.00070017 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-05-16 08:32 | 2022-05-16 11:30 | 20 | 002:58 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA ARBOL CAYO Y CAUSO CRUCE DE LINEAS | A22051600100 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 178 | 2022-05-16 | 3560 | keep | 0 | May | 2022 | 0.0024247 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-16 08:33 | 2022-05-16 08:43 | 1879 | 000:10 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LA LINEA 2200 PARA SECCIONALIZAR PUENTE ABIERTO EN LA MISMA | A22051600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-16 | 18790 | keep | 0 | May | 2022 | 0.012798 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-16 08:33 | 2022-05-16 08:43 | 2777 | 000:10 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LA LINEA 2200 PARA SECCIONALIZAR PUENTE ABIERTO EN LA MISMA | A22051600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-16 | 27770 | keep | 0 | May | 2022 | 0.018914 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-16 08:33 | 2022-05-16 08:43 | 2 | 000:10 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LA LINEA 2200 PARA SECCIONALIZAR PUENTE ABIERTO EN LA MISMA | A22051600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-05-16 | 20 | keep | 0 | May | 2022 | 1.3622e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-16 08:33 | 2022-05-16 08:35 | 2839 | 000:02 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LA LINEA 2200 PARA SECCIONALIZAR PUENTE ABIERTO EN LA MISMA | A22051600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-16 | 5678 | keep | 0 | May | 2022 | 0.0038673 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-16 08:33 | 2022-05-16 08:35 | 1160 | 000:02 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LA LINEA 2200 PARA SECCIONALIZAR PUENTE ABIERTO EN LA MISMA | A22051600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-16 | 2320 | keep | 0 | May | 2022 | 0.0015801 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-16 08:33 | 2022-05-16 08:35 | 1860 | 000:02 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LA LINEA 2200 PARA SECCIONALIZAR PUENTE ABIERTO EN LA MISMA | A22051600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-16 | 3720 | keep | 0 | May | 2022 | 0.0025337 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-16 08:43 | 2022-05-16 08:44 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 & 4800 | C22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 2725 | keep | 0 | May | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-05-16 08:43 | 2022-05-16 08:44 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 & 4800 | C22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 1834 | keep | 0 | May | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-05-16 08:43 | 2022-05-16 08:44 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 & 4800 | C22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 1437 | keep | 0 | May | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-05-16 08:43 | 2022-05-16 08:44 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 & 4800 | C22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 2565 | keep | 0 | May | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-05-16 08:43 | 2022-05-16 08:44 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 & 4800 | C22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 3565 | keep | 0 | May | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-05-16 08:43 | 2022-05-16 08:44 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1606 | keep | 0 | May | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BAYAMON | 2022-05-16 08:46 | 2022-05-16 10:48 | 1 | 002:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X40 EN C/L SE REMPLAZO CAJA PRIMARIA | B22051600015 | New_Event | Cutout Failure | Include | Include | Equipment | 122 | 2022-05-16 | 122 | keep | 0 | May | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-16 08:58 | 2022-05-16 13:30 | 165 | 004:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA FUERTES LLUVIAS | C22051600046 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 272 | 2022-05-16 | 44880 | keep | 0 | May | 2022 | 0.030568 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
ARECIBO | 2022-05-16 09:00 | 2022-05-17 13:14 | 12 | 028:14 | P | EMPALME SOTERRADO AVERIADO | SE REEMPLAZARON DOS TERMINACIONES SOTERRADAS | A22051600118 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 1694 | 2022-05-16 | 20328 | keep | 0 | May | 2022 | 0.013845 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-05-16 09:09 | 2022-05-16 14:00 | 88 | 004:51 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P22050160019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2022-05-16 | 25608 | keep | 0 | May | 2022 | 0.017441 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
SAN JUAN | 2022-05-16 09:10 | 2022-05-16 11:11 | 207 | 002:01 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | S22051600018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-05-16 | 25047 | keep | 0 | May | 2022 | 0.017059 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
MAYAGÃœEZ | 2022-05-16 09:12 | 2022-05-16 11:35 | 1 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER A.A.A | M22051600056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2022-05-16 | 143 | keep | 0 | May | 2022 | 9.7397e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-16 09:22 | 2022-05-16 16:54 | 6 | 007:32 | P | TERMINACION SOTERRADA AVERIADA | SE REMPLAZARON 2 TERMINACIONES DE RISER @ SU-1 | B22051600025 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 452 | 2022-05-16 | 2712 | keep | 0 | May | 2022 | 0.0018471 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-16 09:22 | 2022-05-16 16:03 | 35 | 006:41 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22051600046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 401 | 2022-05-16 | 14035 | keep | 0 | May | 2022 | 0.0095592 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2022-05-16 09:34 | 2022-05-16 14:29 | 16 | 004:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP PARTIDO | R22051600017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 295 | 2022-05-16 | 4720 | keep | 0 | May | 2022 | 0.0032148 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-05-16 09:41 | 2022-05-16 12:38 | 80 | 002:57 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R22051600018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-05-16 | 14160 | keep | 0 | May | 2022 | 0.0096443 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-05-16 09:48 | 2022-05-16 12:40 | 180 | 002:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22051600020 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2022-05-16 | 30960 | keep | 0 | May | 2022 | 0.021087 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
ARECIBO | 2022-05-16 09:49 | 2022-05-16 12:58 | 1879 | 003:09 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA DE LA SUBESTACION Y SE REPARO PUENTE ABIERTO EN LA LINEA 2200 | A22051600139 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2022-05-16 | 355131 | keep | 0 | May | 2022 | 0.24188 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-16 09:49 | 2022-05-16 12:58 | 2777 | 003:09 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA DE LA SUBESTACION Y SE REPARO PUENTE ABIERTO EN LA LINEA 2200 | A22051600139 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2022-05-16 | 524853 | keep | 0 | May | 2022 | 0.35747 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-16 09:49 | 2022-05-16 12:58 | 2 | 003:09 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA DE LA SUBESTACION Y SE REPARO PUENTE ABIERTO EN LA LINEA 2200 | A22051600139 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2022-05-16 | 378 | keep | 0 | May | 2022 | 0.00025745 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-16 09:51 | 2022-05-16 09:52 | 6197 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | C22051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 6197 | keep | 0 | May | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
BAYAMON | 2022-05-16 09:51 | 2022-05-16 09:52 | 1 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LUEGO DE CONFIRMAR CON LA ING. KESLIN ORTIZ - DIRECTORA DE PLANTA A.A.A. - REGION BAYAMON | B22051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1 | keep | 0 | May | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-16 09:54 | 2022-05-16 09:55 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051600067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 3458 | keep | 0 | May | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
SAN JUAN | 2022-05-16 09:57 | 2022-05-16 16:12 | 77 | 006:15 | P | DESGANCHE | 1X 80 EN C/L DESGANCHE | S22051600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2022-05-16 | 28875 | keep | 0 | May | 2022 | 0.019667 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
CANOVANAS | 2022-05-16 10:08 | 2022-05-16 11:22 | 15 | 001:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DEL 37.5 X 37.5KVA | R22051600025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 74 | 2022-05-16 | 1110 | keep | 0 | May | 2022 | 0.00075602 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-16 10:13 | 2022-05-16 11:49 | 2 | 001:36 | P | ANIMAL | 1X25 EN C/L & 1X15 EN XMER - SE RETIRO IGUANA DE LA LINEA | S22051600022 | New_Event | Animals | Include | Include | Wildlife | 96 | 2022-05-16 | 192 | keep | 0 | May | 2022 | 0.00013077 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-05-16 10:31 | 2022-05-16 16:47 | 70 | 006:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051600154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2022-05-16 | 26320 | keep | 0 | May | 2022 | 0.017926 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-05-16 10:53 | 2022-05-16 11:53 | 2839 | 001:00 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LA LINEA 2200 POR AVERIA EN EL INTERRUPTOR 2284 SE ENERGIZO LA SUBESTACION POR EL INTERRUPTOR 2252 | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 60 | 2022-05-16 | 170340 | keep | 0 | May | 2022 | 0.11602 | 0.0019336 | Sustained | FALSE | FALSE | Not_TMED_Event | 2839
ARECIBO | 2022-05-16 10:53 | 2022-05-16 11:53 | 1160 | 001:00 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LA LINEA 2200 POR AVERIA EN EL INTERRUPTOR 2284 SE ENERGIZO LA SUBESTACION POR EL INTERRUPTOR 2252 | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 60 | 2022-05-16 | 69600 | keep | 0 | May | 2022 | 0.047404 | 0.00079007 | Sustained | FALSE | FALSE | Not_TMED_Event | 1160
ARECIBO | 2022-05-16 10:53 | 2022-05-16 11:53 | 1860 | 001:00 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LA LINEA 2200 POR AVERIA EN EL INTERRUPTOR 2284 SE ENERGIZO LA SUBESTACION POR EL INTERRUPTOR 2252 | A22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 60 | 2022-05-16 | 111600 | keep | 0 | May | 2022 | 0.07601 | 0.0012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 1860
MAYAGÃœEZ | 2022-05-16 10:56 | 2022-05-16 15:56 | 200 | 005:00 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE RETEZARON LINEAS | M22051600078 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 300 | 2022-05-16 | 60000 | keep | 0 | May | 2022 | 0.040866 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-05-16 11:03 | 2022-05-16 14:00 | 30 | 002:57 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A22051600172 | New_Event | Animals | Include | Include | Wildlife | 177 | 2022-05-16 | 5310 | keep | 0 | May | 2022 | 0.0036166 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-16 11:28 | 2022-05-16 14:14 | 50 | 002:46 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 Y 1 X 50 EN CORTE DE LINEA SE CORRIGIO LINEAS CRUZADAS | A22051600183 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 166 | 2022-05-16 | 8300 | keep | 0 | May | 2022 | 0.0056531 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-16 11:34 | 2022-05-16 18:40 | 140 | 007:06 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22051600086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 426 | 2022-05-16 | 59640 | keep | 0 | May | 2022 | 0.040621 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2022-05-16 11:36 | 2022-05-16 19:21 | 120 | 007:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L SE REEMPLAZO CAJA PRIMARIA | B22051600038 | New_Event | Cutout Failure | Include | Include | Equipment | 465 | 2022-05-16 | 55800 | keep | 0 | May | 2022 | 0.038005 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-05-16 11:38 | 2022-05-16 14:30 | 124 | 002:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22050160040 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2022-05-16 | 21328 | keep | 0 | May | 2022 | 0.014526 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
BAYAMON | 2022-05-16 11:38 | 2022-05-16 13:27 | 4 | 001:49 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO | S22051600026 | New_Event | Primary Pole Failure | Include | Include | Equipment | 109 | 2022-05-16 | 436 | keep | 0 | May | 2022 | 0.00029696 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-05-16 11:40 | 2022-05-16 11:43 | 906 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | C22051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-16 | 2718 | keep | 0 | May | 2022 | 0.0018512 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
BAYAMON | 2022-05-16 11:44 | 2022-05-16 12:22 | 3 | 000:38 | P | SECUNDARIA/DESGANCHE | SE REMPLAZARON CONECTORES EN BAJANTE DE XMER & SE LIMPIO ENRREDADERA EN SECUNDARIA | B22051600040 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 38 | 2022-05-16 | 114 | keep | 0 | May | 2022 | 7.7645e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-05-16 12:01 | 2022-05-16 12:03 | 6244 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-16 | 12488 | keep | 0 | May | 2022 | 0.0085055 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
MAYAGÃœEZ | 2022-05-16 12:06 | 2022-05-16 12:07 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22051600099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 12:06 | 2022-05-16 12:07 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051600099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 12:09 | 2022-05-16 12:10 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22051600101 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 12:09 | 2022-05-16 12:10 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051600101 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 12:13 | 2022-05-16 17:34 | 40 | 005:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZARON CAJAS PRIMARIAS | M22051600105 | New_Event | Cutout Failure | Include | Include | Equipment | 321 | 2022-05-16 | 12840 | keep | 0 | May | 2022 | 0.0087453 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-16 12:15 | 2022-05-16 16:30 | 120 | 004:15 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA | C22051600100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2022-05-16 | 30600 | keep | 0 | May | 2022 | 0.020842 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-05-16 12:17 | 2022-05-16 13:15 | 225 | 000:58 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE BKR SE TRANSFIRIO CARGA AL 1908-03 POR PROBLEMAS CON EL BKR CARGA POR EL 1303-05 | S22051600033 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 58 | 2022-05-16 | 13050 | keep | 0 | May | 2022 | 0.0088883 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-16 12:17 | 2022-05-16 13:15 | 870 | 000:58 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE BKR SE TRANSFIRIO CARGA AL 1908-03 POR PROBLEMAS CON EL BKR LLEVA EL 1303-04 | S22051600033 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 58 | 2022-05-16 | 50460 | keep | 0 | May | 2022 | 0.034368 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2022-05-16 12:25 | 2022-05-16 13:35 | 10 | 001:10 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR PARA REMPLAZO SECUNDARIA | C22051600101 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 70 | 2022-05-16 | 700 | keep | 0 | May | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-16 12:29 | 2022-05-16 13:21 | 4 | 000:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA PARTIDA | B22051600050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2022-05-16 | 208 | keep | 0 | May | 2022 | 0.00014167 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-05-16 12:34 | 2022-05-17 13:20 | 1 | 024:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M22051600112 | New_Event | Primary Wire Break | Include | Include | Equipment | 1486 | 2022-05-16 | 1486 | keep | 0 | May | 2022 | 0.0010121 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-16 12:36 | 2022-05-16 14:36 | 60 | 002:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y SE RETIRO RAMA | R22051600044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-05-16 | 7200 | keep | 0 | May | 2022 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-16 12:42 | 2022-05-16 14:28 | 70 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22051600052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-05-16 | 7420 | keep | 0 | May | 2022 | 0.0050537 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-05-16 12:47 | 2022-05-16 12:48 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DE 6014-03 | M22051600115 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 12:47 | 2022-05-16 12:48 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051600115 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
HUMACAO | 2022-05-16 12:58 | 2022-05-16 16:10 | 100 | 003:12 | P | DESGANCHE | 2 X 65 Y 1 X 80 EN CORTES DE LINEAS SE REPORTA AVERIA POR DESGANCHE | C22051600116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-05-16 | 19200 | keep | 0 | May | 2022 | 0.013077 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-16 13:06 | 2022-05-16 15:42 | 1 | 002:36 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | S22051600064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-05-16 | 156 | keep | 0 | May | 2022 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-16 13:16 | 2022-05-16 16:09 | 100 | 002:53 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051600129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-05-16 | 17300 | keep | 0 | May | 2022 | 0.011783 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-16 13:18 | 2022-05-16 15:45 | 1360 | 002:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA DEFECTUOSA, NO FUNDIO FUSIBLE. | C22051600121 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2022-05-16 | 199920 | keep | 0 | May | 2022 | 0.13616 | 0.00092629 | Sustained | FALSE | FALSE | Not_TMED_Event | 1360
HUMACAO | 2022-05-16 13:37 | 2022-05-16 16:40 | 110 | 003:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | C22051600128 | New_Event | Primary Wire Break | Include | Include | Equipment | 183 | 2022-05-16 | 20130 | keep | 0 | May | 2022 | 0.01371 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
PONCE | 2022-05-16 13:37 | 2022-05-16 16:30 | 300 | 002:53 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | P22051600053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2022-05-16 | 51900 | keep | 0 | May | 2022 | 0.035349 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-05-16 13:37 | 2022-05-16 13:38 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600138 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 13:37 | 2022-05-16 13:38 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600138 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
AGUADILLA | 2022-05-16 13:53 | 2022-05-16 14:08 | 1036 | 000:15 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | M22051600153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-05-16 | 15540 | keep | 0 | May | 2022 | 0.010584 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
GUAYAMA | 2022-05-16 13:54 | 2022-05-16 16:20 | 1 | 002:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMRE PRIMARIO PARTIDO | P22051600054 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2022-05-16 | 146 | keep | 0 | May | 2022 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-16 14:01 | 2022-05-16 17:50 | 60 | 003:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051600222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2022-05-16 | 13740 | keep | 0 | May | 2022 | 0.0093583 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-16 14:02 | 2022-05-16 14:03 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600161 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 14:02 | 2022-05-16 14:03 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600161 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
CAGUAS | 2022-05-16 14:04 | 2022-05-16 19:05 | 50 | 005:01 | P | ARBOL SOBRE LINEA | 1 X 65 EN C/L Y SE REPARO LINEA PRIMARIA POR ARBOL SOBRE LINEA | C22051600140 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 301 | 2022-05-16 | 15050 | keep | 0 | May | 2022 | 0.01025 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-16 14:10 | 2022-05-16 14:11 | 906 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22051600143 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 906 | keep | 0 | May | 2022 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
PONCE | 2022-05-16 14:10 | 2022-05-16 16:02 | 16 | 001:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22051600057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 112 | 2022-05-16 | 1792 | keep | 0 | May | 2022 | 0.0012205 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-05-16 14:13 | 2022-05-16 14:14 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600172 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 14:13 | 2022-05-16 14:14 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600172 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 14:13 | 2022-05-16 22:15 | 200 | 008:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051600169 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 482 | 2022-05-16 | 96400 | keep | 0 | May | 2022 | 0.065658 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-16 14:16 | 2022-05-16 14:17 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600175 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 14:16 | 2022-05-16 14:17 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600175 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 14:17 | 2022-05-17 13:30 | 200 | 023:13 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051600176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1393 | 2022-05-16 | 278600 | keep | 0 | May | 2022 | 0.18975 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-16 14:22 | 2022-05-16 14:23 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600181 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 14:22 | 2022-05-16 14:23 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600181 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
FAJARDO | 2022-05-16 14:23 | 2022-05-16 14:24 | 2041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 2041 | keep | 0 | May | 2022 | 0.0013901 | 0.0013901 | Momentary | FALSE | FALSE | Not_TMED_Event | 2041
BAYAMON | 2022-05-16 14:24 | 2022-05-16 16:49 | 10 | 002:25 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B22051600071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-05-16 | 1450 | keep | 0 | May | 2022 | 0.00098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-05-16 14:25 | 2022-05-16 16:15 | 120 | 001:50 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO QUEMADO | R22051600053 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 110 | 2022-05-16 | 13200 | keep | 0 | May | 2022 | 0.0089905 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-05-16 14:29 | 2022-05-16 14:30 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600190 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 14:29 | 2022-05-16 14:30 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600190 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 14:30 | 2022-05-16 14:31 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 14:30 | 2022-05-16 14:31 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 14:32 | 2022-05-16 14:33 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600191 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 14:32 | 2022-05-16 14:33 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600191 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 14:39 | 2022-05-16 14:40 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600196 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 14:39 | 2022-05-16 14:40 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600196 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
ARECIBO | 2022-05-16 14:40 | 2022-05-16 17:55 | 20 | 003:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22051600227 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 195 | 2022-05-16 | 3900 | keep | 0 | May | 2022 | 0.0026563 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-16 14:49 | 2022-05-16 15:05 | 90 | 000:16 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C22051600102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 16 | 2022-05-16 | 1440 | keep | 0 | May | 2022 | 0.00098078 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-05-16 14:52 | 2022-05-16 15:43 | 974 | 000:51 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE DISPARO INTERRUPTOR A PETICION DE JOSE DE JESUS AUTORIZADO DE SU SUPERVISOR Y EL INGENIERO DE AREA, PARA CERRAR PUENTES ABIERTOS Y MACHETES PARA NORMALIZAR TRABAJOS REALIZADOS A CAUSA DE AVERIA. | M22051600041 | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 51 | 2022-05-16 | 49674 | keep | 0 | May | 2022 | 0.033833 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-16 14:52 | 2022-05-17 03:40 | 100 | 012:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051600219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 768 | 2022-05-16 | 76800 | keep | 0 | May | 2022 | 0.052308 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-16 15:06 | 2022-05-16 23:00 | 75 | 007:54 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B22051600077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 474 | 2022-05-16 | 35550 | keep | 0 | May | 2022 | 0.024213 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 1339 | keep | 0 | May | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 470 | keep | 0 | May | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 2483 | keep | 0 | May | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 2190 | keep | 0 | May | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 3006 | keep | 0 | May | 2022 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 179 | keep | 0 | May | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 107 | keep | 0 | May | 2022 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 1666 | keep | 0 | May | 2022 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 4387 | keep | 0 | May | 2022 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 3147 | keep | 0 | May | 2022 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-05-16 15:09 | 2022-05-16 15:10 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 FUE CERRADA POR SCADA | M22051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-16 | 4304 | keep | 0 | May | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
CANOVANAS | 2022-05-16 15:14 | 2022-05-16 17:12 | 60 | 001:58 | P | PARARRAYOS DEFECTUOSO | 1 X 15 Y 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO QUEMADO Y CAJA QUEMADA | R22051600056 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 118 | 2022-05-16 | 7080 | keep | 0 | May | 2022 | 0.0048222 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-16 15:20 | 2022-05-16 15:21 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 15:20 | 2022-05-16 15:21 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 15:21 | 2022-05-16 15:22 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600244 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 15:21 | 2022-05-16 15:22 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600244 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
HUMACAO | 2022-05-16 15:24 | 2022-05-16 17:59 | 5 | 002:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA REEMPLAZO DOS CAJA PRIMARIAS QUEMADAS | C22051600161 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2022-05-16 | 775 | keep | 0 | May | 2022 | 0.00052785 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-05-16 15:24 | 2022-05-16 17:52 | 110 | 002:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22051600163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-05-16 | 16280 | keep | 0 | May | 2022 | 0.011088 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2022-05-16 15:29 | 2022-05-16 15:30 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600253 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 15:29 | 2022-05-16 15:30 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600253 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 15:30 | 2022-05-16 19:15 | 25 | 003:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA Y SE REMPLAZO POSTE PARTIDO | M22051600146 | New_Event | Primary Pole Failure | Include | Include | Equipment | 225 | 2022-05-16 | 5625 | keep | 0 | May | 2022 | 0.0038312 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-05-16 15:33 | 2022-05-16 15:34 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051600063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
YAUCO | 2022-05-16 15:38 | 2022-05-16 17:00 | 50 | 001:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO FUERTES VIENTOS | P22051600064 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 82 | 2022-05-16 | 4100 | keep | 0 | May | 2022 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-16 15:46 | 2022-05-16 20:00 | 175 | 004:14 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051600239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-05-16 | 44450 | keep | 0 | May | 2022 | 0.030275 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
CAGUAS | 2022-05-16 15:53 | 2022-05-16 17:23 | 80 | 001:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REPORTA AVERIA POR DESGANCHE | C22051600180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-05-16 | 7200 | keep | 0 | May | 2022 | 0.0049039 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-16 15:55 | 2022-05-16 15:56 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600265 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 15:55 | 2022-05-16 15:56 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600265 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
UTUADO | 2022-05-16 16:00 | 2022-05-16 19:15 | 30 | 003:15 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A22051600243 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 195 | 2022-05-16 | 5850 | keep | 0 | May | 2022 | 0.0039844 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-16 16:08 | 2022-05-17 16:06 | 400 | 023:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22051600270 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1438 | 2022-05-16 | 575200 | keep | 0 | May | 2022 | 0.39177 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
ARECIBO | 2022-05-16 16:10 | 2022-05-16 20:13 | 150 | 004:03 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22051600247 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2022-05-16 | 36450 | keep | 0 | May | 2022 | 0.024826 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-16 16:24 | 2022-05-16 16:25 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22051600281 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-16 16:24 | 2022-05-16 16:25 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22051600281 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-16 16:24 | 2022-05-16 16:25 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22051600281 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-16 | 1097 | keep | 0 | May | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
UTUADO | 2022-05-16 16:26 | 2022-05-16 21:15 | 12 | 004:49 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22051600253 | New_Event | Primary Wire Break | Include | Include | Equipment | 289 | 2022-05-16 | 3468 | keep | 0 | May | 2022 | 0.002362 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-05-16 16:39 | 2022-05-16 19:29 | 4 | 002:50 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR PM | R22051600069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2022-05-16 | 680 | keep | 0 | May | 2022 | 0.00046314 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-16 16:53 | 2022-05-16 18:04 | 15 | 001:11 | P | ANIMAL | 1 X 15 EN PROVISIONAL SE RETIRO IGUANA | B22051600084 | New_Event | Animals | Include | Include | Wildlife | 71 | 2022-05-16 | 1065 | keep | 0 | May | 2022 | 0.00072537 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-05-16 17:04 | 2022-05-16 18:40 | 30 | 001:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051600261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-05-16 | 2880 | keep | 0 | May | 2022 | 0.0019616 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-16 17:15 | 2022-05-16 17:16 | 1 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S22051600013 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-16 | 1 | keep | 0 | May | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-05-16 17:16 | 2022-05-16 18:56 | 35 | 001:40 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P22051600076 | New_Event | Animals | Include | Include | Wildlife | 100 | 2022-05-16 | 3500 | keep | 0 | May | 2022 | 0.0023838 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-05-16 17:18 | 2022-05-17 10:56 | 690 | 017:38 | P | DESCONECTIVO DEFECTUOSO | DOS MACHETES QUEMADOS EN EL TRONCAL DEL ALIMENATDOR | M22051600310 | New_Event | Switch Failure | Include | Include | Equipment | 1058 | 2022-05-16 | 730020 | keep | 0 | May | 2022 | 0.49721 | 0.00046996 | Sustained | FALSE | FALSE | Not_TMED_Event | 690
AGUADILLA | 2022-05-16 17:31 | 2022-05-16 18:29 | 1 | 000:58 | P | ANIMAL | 3 X 80 EN CORTE DE LINEA SE ENCONTRO GALLINAS DE PALO QUEMADAS | M22051600013 | New_Event | Animals | Include | Include | Wildlife | 58 | 2022-05-16 | 58 | keep | 0 | May | 2022 | 3.9504e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-16 17:36 | 2022-05-16 21:18 | 20 | 003:42 | P | DESGANCHE | 1 X50 EN C/L SE DESGANCHO | B22051600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2022-05-16 | 4440 | keep | 0 | May | 2022 | 0.0030241 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-16 17:38 | 2022-05-16 18:21 | 1483 | 000:43 | P | ANIMAL | SE REMOVIO AVE EN TRONCAL SE CERRO POR SCADA 30% DE LA CARGA POR EL 1336-08 | S22051600293 | New_Event | Animals | Include | Include | Wildlife | 43 | 2022-05-16 | 63769 | keep | 0 | May | 2022 | 0.043433 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-16 17:38 | 2022-05-16 18:21 | 5290 | 000:43 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE REMOVIO AVE EN TRONCAL SE CERRO POR SCADA LLEVA EL 1336-09 Y 30% VDEL 1204-04 | S22051600293 | New_Event |  |  | Include | Wildlife | 43 | 2022-05-16 | 227470 | keep | 0 | May | 2022 | 0.15493 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-05-16 17:38 | 2022-05-16 18:21 | 207 | 000:43 | T | ANIMAL | SE REMOVIO AVE EN TRONCAL SE CERRO POR SCADA CARGA POR EL 1336-08 | S22051600293 | New_Event | Animals | Include | Include | Wildlife | 43 | 2022-05-16 | 8901 | keep | 0 | May | 2022 | 0.0060624 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
BAYAMON | 2022-05-16 17:38 | 2022-05-16 17:39 | 3941 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRRUPTOR | B22051600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-16 | 3941 | keep | 0 | May | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-05-16 17:39 | 2022-05-16 19:56 | 200 | 002:17 | P | DESGANCHE | 1 X 80 EN C/L DESGACHE Y REEMPLAZO CAJA PRIMARIA | B22051600096 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-05-16 | 27400 | keep | 0 | May | 2022 | 0.018662 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-16 17:50 | 2022-05-16 18:25 | 59 | 000:35 | P | DESGANCHE | SE ABRIO CL PARA REALIZAR DESGANCHE DE EMERGENCIA ARBOL COGIO FUEGO | S22051600214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2022-05-16 | 2065 | keep | 0 | May | 2022 | 0.0014065 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
CAGUAS | 2022-05-16 17:54 | 2022-05-17 11:43 | 90 | 017:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 20 EN CORTE DE LINEA Y TRANSFORMADOR SE REEMPLAZO PIN POLE TOP | C22051600201 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1069 | 2022-05-16 | 96210 | keep | 0 | May | 2022 | 0.065528 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-05-16 18:11 | 2022-05-17 10:19 | 67 | 016:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X65 EN C/L & SE REMPLAZO EL PORTAFUSIBLE | S22051600251 | New_Event | Cutout Failure | Include | Include | Equipment | 968 | 2022-05-16 | 64856 | keep | 0 | May | 2022 | 0.044173 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2022-05-16 18:17 | 2022-05-17 01:35 | 80 | 007:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051600329 | New_Event | Vegetation Contact | Include | Include | Vegetation | 438 | 2022-05-16 | 35040 | keep | 0 | May | 2022 | 0.023866 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-05-16 18:28 | 2022-05-17 10:58 | 14 | 016:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22051600204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 990 | 2022-05-16 | 13860 | keep | 0 | May | 2022 | 0.00944 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-05-16 18:31 | 2022-05-16 19:15 | 40 | 000:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CAJA PRIMARIA DE TRANSFORMADOR AVERIADA | A22051600275 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2022-05-16 | 1760 | keep | 0 | May | 2022 | 0.0011987 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-16 18:43 | 2022-05-16 18:57 | 50 | 000:14 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22051600232 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2022-05-16 | 700 | keep | 0 | May | 2022 | 0.00047677 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-16 19:24 | 2022-05-17 07:28 | 10 | 012:04 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR SE ENCONTRO PAJARO QUEMADO | A22051600288 | New_Event | Animals | Include | Include | Wildlife | 724 | 2022-05-16 | 7240 | keep | 0 | May | 2022 | 0.0049311 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-16 19:31 | 2022-05-16 21:21 | 25 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22051600289 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2022-05-16 | 2750 | keep | 0 | May | 2022 | 0.001873 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-16 19:54 | 2022-05-16 22:20 | 19 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN XMR EN MONTURA DE XMR | S22051600349 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-05-16 | 2774 | keep | 0 | May | 2022 | 0.0018894 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2022-05-16 20:07 | 2022-05-17 09:30 | 80 | 013:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22051600214 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 803 | 2022-05-16 | 64240 | keep | 0 | May | 2022 | 0.043754 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-16 20:20 | 2022-05-17 07:20 | 224 | 011:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO EN TRONCAL A MACHETE | C22051600218 | New_Event | Primary Wire Break | Include | Include | Equipment | 660 | 2022-05-16 | 147840 | keep | 0 | May | 2022 | 0.10069 | 0.00015257 | Sustained | FALSE | FALSE | Not_TMED_Event | 224
CAGUAS | 2022-05-16 21:05 | 2022-05-17 13:20 | 120 | 016:15 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C22051600224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 975 | 2022-05-16 | 117000 | keep | 0 | May | 2022 | 0.079688 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-05-16 21:28 | 2022-05-17 11:11 | 80 | 013:43 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU-D, AVERIA DEL T15 AL T16 SE CERRO N/O EN SU-J AL T14 | C22051600227 | New_Event | UG Cable Fault | Include | Include | Equipment | 823 | 2022-05-16 | 65840 | keep | 0 | May | 2022 | 0.044843 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-05-16 22:02 | 2022-05-17 02:36 | 35 | 004:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22051600226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2022-05-16 | 9590 | keep | 0 | May | 2022 | 0.0065317 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-05-16 22:14 | 2022-05-16 23:44 | 4176 | 001:30 | T | SOBRECARGA | SE ABRIO INTERRUPTOR SOLICITADO POR PERSONAL DE CONSERVACION DE SUBESTACIONES YA QUE LA PORTATIL #7 ESTABA BIEN CALIENTE. HABIA TIRADO ALARMA DE WINDING TEMP. - ABANICOS DE LA PORTATIL NO ENCENDIERON | B22051600129 | New_Event | Trip Due To Overload | Include | Include | Other | 90 | 2022-05-16 | 375840 | keep | 0 | May | 2022 | 0.25598 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-05-16 22:20 | 2022-05-16 23:17 | 120 | 000:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22051600132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-05-16 | 6840 | keep | 0 | May | 2022 | 0.0046587 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-05-16 22:35 | 2022-05-17 13:22 | 14 | 014:47 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22051600395 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 887 | 2022-05-16 | 12418 | keep | 0 | May | 2022 | 0.0084578 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-05-16 23:50 | 2022-05-17 09:47 | 71 | 009:57 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22051600174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 597 | 2022-05-16 | 42387 | keep | 0 | May | 2022 | 0.02887 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
AGUADILLA | 2022-05-16 23:50 | 2022-05-17 02:07 | 1047 | 002:17 | T | TRANSFORMADOR AVERIADO | SE SECCIONALIZO TRANSFORMADOR AVERIADO CALLE 24 URB VISTA VERDE | M22051600429 | New_Event | Service Transformer Failure | Include | Include | Equipment | 137 | 2022-05-16 | 143439 | keep | 0 | May | 2022 | 0.097696 | 0.00071311 | Sustained | FALSE | FALSE | Not_TMED_Event | 1047
BARRANQUITAS | 2022-05-17 00:28 | 2022-05-17 12:48 | 70 | 012:20 | P | DESGANCHE | 1 X 50 EN C/L - DESGANCHO Y SE REMPLAZO PARARRAYO | C22051700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 740 | 2022-05-17 | 51800 | keep | 0 | May | 2022 | 0.035281 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-05-17 02:07 | 2022-05-17 10:33 | 349 | 008:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN EL TRONCAL DEL ALIMENTADOR | M22051600431 | New_Event | Primary Wire Break | Include | Include | Equipment | 506 | 2022-05-17 | 176594 | keep | 0 | May | 2022 | 0.12028 | 0.0002377 | Sustained | FALSE | FALSE | Not_TMED_Event | 349
HUMACAO | 2022-05-17 05:40 | 2022-05-17 05:41 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 3025 | keep | 0 | May | 2022 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
BAYAMON | 2022-05-17 05:48 | 2022-05-17 05:49 | 2735 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR EN SERVICIO | B22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 2735 | keep | 0 | May | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
VEGA BAJA | 2022-05-17 05:52 | 2022-05-17 10:06 | 27 | 004:14 | T | EMPALME SOTERRADO AVERIADO | DISPARO INTERRUPTOR SE SECCIONALIZO SE ABRIO DEL MH-4N @ MH-2C | B22051700015 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 254 | 2022-05-17 | 6858 | keep | 0 | May | 2022 | 0.004671 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-05-17 06:17 | 2022-05-17 14:59 | 8 | 008:42 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR DESGANCHE SE RETEZO LINEA | S22051700003 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 522 | 2022-05-17 | 4176 | keep | 0 | May | 2022 | 0.0028443 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-05-17 06:37 | 2022-05-17 08:54 | 50 | 002:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22051700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-05-17 | 6850 | keep | 0 | May | 2022 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-17 06:37 | 2022-05-17 12:46 | 2 | 006:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 8 EN TRANSFORMADOR POR FUERTE VIENTO | M22051700040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 369 | 2022-05-17 | 738 | keep | 0 | May | 2022 | 0.00050265 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-05-17 06:41 | 2022-05-17 08:03 | 60 | 001:22 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA 1 X65 ENTRADA RISER 1 X 50 EN SALIDA RISER PARARRAYO CRUZADO | P22051700001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 82 | 2022-05-17 | 4920 | keep | 0 | May | 2022 | 0.003351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-17 07:02 | 2022-05-17 07:04 | 2900 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C2205170000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-17 | 5800 | keep | 0 | May | 2022 | 0.0039504 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
CANOVANAS | 2022-05-17 07:38 | 2022-05-17 13:30 | 1 | 005:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REMPLAZO PORTAFUSIBLE | R22051700003 | New_Event | Cutout Failure | Include | Include | Equipment | 352 | 2022-05-17 | 352 | keep | 0 | May | 2022 | 0.00023975 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-17 07:46 | 2022-05-17 07:47 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-05 | S22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 225 | keep | 0 | May | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-17 07:46 | 2022-05-17 07:47 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-04 | S22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-05-17 07:46 | 2022-05-17 07:47 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-04 | S22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1598 | keep | 0 | May | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-05-17 07:47 | 2022-05-17 12:34 | 1 | 004:47 | P | NO SE REPORTO CAUSA | 3 X 40 EN RISER PARA BANCO DE XMR | S22051700026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2022-05-17 | 287 | keep | 0 | May | 2022 | 0.00019547 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-17 08:05 | 2022-05-17 12:23 | 60 | 004:18 | P | NO SE REPORTO CAUSA | 1X80 DE RISER @ SU-1 | B22051700045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2022-05-17 | 15480 | keep | 0 | May | 2022 | 0.010543 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-05-17 08:06 | 2022-05-17 10:39 | 150 | 002:33 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA NO CAUSA | P22051700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2022-05-17 | 22950 | keep | 0 | May | 2022 | 0.015631 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-05-17 08:09 | 2022-05-17 13:16 | 1 | 005:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA PARA BOMBAS DE A.A.A | A22051700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2022-05-17 | 307 | keep | 0 | May | 2022 | 0.0002091 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-17 08:10 | 2022-05-17 11:16 | 6 | 003:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22051700006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-05-17 | 1116 | keep | 0 | May | 2022 | 0.0007601 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-17 08:24 | 2022-05-17 13:15 | 1 | 004:51 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | A22051700008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2022-05-17 | 291 | keep | 0 | May | 2022 | 0.0001982 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-17 08:35 | 2022-05-17 11:49 | 18 | 003:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA POR LLUVIAS | A22051700009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 194 | 2022-05-17 | 3492 | keep | 0 | May | 2022 | 0.0023784 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-05-17 08:37 | 2022-05-17 12:05 | 15 | 003:28 | P | TRANSFORMADOR AVERIADO | SE SECCIONALIZO AREA PARA REEMPLAZO DE PM T-40 | S22051700019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 208 | 2022-05-17 | 3120 | keep | 0 | May | 2022 | 0.002125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-05-17 08:40 | 2022-05-17 08:41 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22051700055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 3387 | keep | 0 | May | 2022 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
BAYAMON | 2022-05-17 08:45 | 2022-05-17 14:20 | 15 | 005:35 | P | ANIMAL | 1 X 20 EN RISER CRUCE POR IGUANA | B22051700057 | New_Event | Animals | Include | Include | Wildlife | 335 | 2022-05-17 | 5025 | keep | 0 | May | 2022 | 0.0034225 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-05-17 09:04 | 2022-05-17 12:59 | 20 | 003:55 | P | NO SE REPORTO CAUSA | 1X20 EN RISER | B22051700060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2022-05-17 | 4700 | keep | 0 | May | 2022 | 0.0032011 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-17 09:07 | 2022-05-17 14:00 | 1 | 004:53 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | R22051700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2022-05-17 | 293 | keep | 0 | May | 2022 | 0.00019956 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-17 09:19 | 2022-05-17 09:20 | 817 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 817 | keep | 0 | May | 2022 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
HUMACAO | 2022-05-17 09:24 | 2022-05-17 10:15 | 11 | 000:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO SULFATADO | C22051700028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2022-05-17 | 561 | keep | 0 | May | 2022 | 0.00038209 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-05-17 09:40 | 2022-05-17 19:29 | 200 | 009:49 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR CONDUCTOR ABIERTO | B22051700074 | New_Event | Primary Wire Break | Include | Include | Equipment | 589 | 2022-05-17 | 117800 | keep | 0 | May | 2022 | 0.080233 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-17 09:49 | 2022-05-17 15:00 | 12 | 005:11 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5 KVA X 37.5KVA | S22051700025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 311 | 2022-05-17 | 3732 | keep | 0 | May | 2022 | 0.0025418 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-17 09:50 | 2022-05-17 11:56 | 7 | 002:06 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C22051700033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-05-17 | 882 | keep | 0 | May | 2022 | 0.00060073 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-05-17 09:50 | 2022-05-17 11:15 | 6 | 001:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO ROTO | M22051600055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2022-05-17 | 510 | keep | 0 | May | 2022 | 0.00034736 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-05-17 09:51 | 2022-05-17 09:52 | 778 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 778 | keep | 0 | May | 2022 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
VEGA BAJA | 2022-05-17 10:06 | 2022-05-17 11:25 | 5 | 001:19 | P | EMPALME SOTERRADO AVERIADO | SE REPARO TERMINACIONES TIPO PISTOLA EN CAJAS SECAS EN MH3 | B22051700015 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 79 | 2022-05-17 | 395 | keep | 0 | May | 2022 | 0.00026903 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-17 10:18 | 2022-05-17 14:29 | 2 | 004:11 | P | SECUNDARIA/DESGANCHE | SE REEMPLAZO BAJANTE SECUNDARIO Y DESGANCHE SECUNDARIO | S22051700032 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 251 | 2022-05-17 | 502 | keep | 0 | May | 2022 | 0.00034191 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-05-17 10:33 | 2022-05-17 11:10 | 1047 | 000:37 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M22051700112 | New_Event | Cutout Failure | Include | Include | Equipment | 37 | 2022-05-17 | 38739 | keep | 0 | May | 2022 | 0.026385 | 0.00071311 | Sustained | FALSE | FALSE | Not_TMED_Event | 1047
CAGUAS | 2022-05-17 10:36 | 2022-05-17 10:37 | 2859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 2859 | keep | 0 | May | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
BAYAMON | 2022-05-17 10:42 | 2022-05-17 15:41 | 110 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22051700086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2022-05-17 | 32890 | keep | 0 | May | 2022 | 0.022401 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2022-05-17 10:48 | 2022-05-17 14:22 | 6 | 003:34 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C22051700041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 214 | 2022-05-17 | 1284 | keep | 0 | May | 2022 | 0.00087453 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-05-17 10:56 | 2022-05-17 10:57 | 2859 | 000:01 | T | DESGANCHE | RECIERRE | C22051700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-17 | 2859 | keep | 0 | May | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
AGUADILLA | 2022-05-17 10:56 | 2022-05-17 13:14 | 1036 | 002:18 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REMPLAZAR DOS MACHETES QUEMADOS EN EL TRONCAL DEL ALIMENTADOR | M22051700124 | Additional_clients | Switch Failure | Include | Include | Equipment | 138 | 2022-05-17 | 142968 | keep | 0 | May | 2022 | 0.097375 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-17 11:04 | 2022-05-17 11:05 | 2859 | 000:01 | T | DESGANCHE | RECIERRE | C22051700000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-17 | 2859 | keep | 0 | May | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CAGUAS | 2022-05-17 11:06 | 2022-05-17 11:07 | 2859 | 000:01 | T | DESGANCHE | RECIERRE | C22051700000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-17 | 2859 | keep | 0 | May | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CAGUAS | 2022-05-17 11:07 | 2022-05-17 12:42 | 2859 | 001:35 | T | DESGANCHE | DISPARO | C22051700044 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-05-17 | 271605 | keep | 0 | May | 2022 | 0.18499 | 0.0019473 | Sustained | FALSE | FALSE | Not_TMED_Event | 2859
AGUADILLA | 2022-05-17 11:10 | 2022-05-17 11:54 | 647 | 000:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR Y SE CERRO LOS MACHETES | M22051700112 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 44 | 2022-05-17 | 28468 | keep | 0 | May | 2022 | 0.019389 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-17 11:16 | 2022-05-17 13:15 | 50 | 001:59 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE | R22051700018 | New_Event | Animals | Include | Include | Wildlife | 119 | 2022-05-17 | 5950 | keep | 0 | May | 2022 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-05-17 11:25 | 2022-05-17 11:26 | 27 | 000:01 | T | EMPALME SOTERRADO AVERIADO | DISPARO INTERRUPTOR PERSONAL REALIZANDO OPERACIONES EN LAZO SOTERRADO DEL MH-4N @ MH-2C | B22051700015 | Additional_clients | UG Cable Splice Failure | Include | Include | Equipment | 1 | 2022-05-17 | 27 | keep | 0 | May | 2022 | 1.839e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-05-17 11:26 | 2022-05-17 16:44 | 5 | 005:18 | P | EMPALME SOTERRADO AVERIADO | SE REPARO TERMINACIONES TIPO PISTOLA EN CAJAS SECAS EN MH3 | B22051700015 | 1st_after_momentary | UG Cable Splice Failure | Include | Include | Equipment | 318 | 2022-05-17 | 1590 | keep | 0 | May | 2022 | 0.0010829 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-05-17 11:38 | 2022-05-17 14:40 | 30 | 003:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L FUERTES VIENTOS | P22051700032 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 182 | 2022-05-17 | 5460 | keep | 0 | May | 2022 | 0.0037188 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-17 11:49 | 2022-05-17 22:30 | 100 | 010:41 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE INSTALO POSTE PRIMARIO PARTIDO | S22051700042 | New_Event | Primary Pole Failure | Include | Include | Equipment | 641 | 2022-05-17 | 64100 | keep | 0 | May | 2022 | 0.043658 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-17 11:50 | 2022-05-17 15:30 | 30 | 003:40 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR PARA REPARAR SECUNDARIA EN VARIOS PUNTOS | R22051700076 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 220 | 2022-05-17 | 6600 | keep | 0 | May | 2022 | 0.0044952 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-05-17 11:54 | 2022-05-17 12:29 | 1047 | 000:35 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE DISPARO EL INTERRUPTOR AL CERRAR MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR AVERIA | M22051700149 | Additional_clients | Cutout Failure | Include | Include | Equipment | 35 | 2022-05-17 | 36645 | keep | 0 | May | 2022 | 0.024959 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-17 12:00 | 2022-05-17 12:01 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22051700152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-17 12:00 | 2022-05-17 12:01 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M22051700152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2022-05-17 12:05 | 2022-05-17 14:56 | 15 | 002:51 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22051700048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-05-17 | 2565 | keep | 0 | May | 2022 | 0.001747 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-05-17 12:18 | 2022-05-17 14:57 | 6 | 002:39 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L NO CAUSA | C22051700061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2022-05-17 | 954 | keep | 0 | May | 2022 | 0.00064977 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-05-17 12:19 | 2022-05-17 16:06 | 50 | 003:47 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO SAFADO EN RISER DE PROVICIONAL AEREO | P22051700038 | New_Event | Primary Wire Break | Include | Include | Equipment | 227 | 2022-05-17 | 11350 | keep | 0 | May | 2022 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-17 12:19 | 2022-05-17 12:20 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22051700166 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-17 12:19 | 2022-05-17 12:20 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M22051700166 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-17 12:21 | 2022-05-17 12:22 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22051700168 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-17 12:21 | 2022-05-17 12:22 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M22051700167 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
PONCE | 2022-05-17 12:22 | 2022-05-17 14:13 | 100 | 001:51 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P22051700039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-05-17 | 11100 | keep | 0 | May | 2022 | 0.0075602 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-17 12:26 | 2022-05-17 12:27 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22051700172 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-17 12:26 | 2022-05-17 12:27 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M22051700172 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-17 12:31 | 2022-05-17 12:32 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22051700180 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-17 12:31 | 2022-05-17 12:32 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M22051700180 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
CANOVANAS | 2022-05-17 12:33 | 2022-05-17 17:30 | 20 | 004:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER SE REMPLAZO PORTAFUSIBLE | R22051700023 | New_Event | Cutout Failure | Include | Include | Equipment | 297 | 2022-05-17 | 5940 | keep | 0 | May | 2022 | 0.0040457 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-17 12:34 | 2022-05-17 19:37 | 20 | 007:03 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR SE ENCONTRO PALOMA QUEMADA | A22051700026 | New_Event | Animals | Include | Include | Wildlife | 423 | 2022-05-17 | 8460 | keep | 0 | May | 2022 | 0.0057621 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-17 12:42 | 2022-05-17 13:38 | 571 | 000:56 | T | DESGANCHE | SE RETIRARON BAMBUAS SOBRE LINEAS | C22051700044 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-05-17 | 31976 | keep | 0 | May | 2022 | 0.021779 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-17 12:44 | 2022-05-17 15:22 | 3 | 002:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051700190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-05-17 | 474 | keep | 0 | May | 2022 | 0.00032284 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-05-17 12:47 | 2022-05-17 15:12 | 6 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22051700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-05-17 | 870 | keep | 0 | May | 2022 | 0.00059255 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-17 12:56 | 2022-05-17 14:55 | 4 | 001:59 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA RELOCALIZARLO A POSTE NUEVO. | S22051700053 | New_Event | Primary Pole Failure | Include | Include | Equipment | 119 | 2022-05-17 | 476 | keep | 0 | May | 2022 | 0.0003242 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-05-17 12:58 | 2022-05-17 17:49 | 225 | 004:51 | P | CONDUCTOR ROTO O ABIERTO | ABRIO C/L PARA LEVANTAR CONDUCTOR GOI CG-220517-02 | C22051700049 | New_Event | Primary Wire Break | Include | Include | Equipment | 291 | 2022-05-17 | 65475 | keep | 0 | May | 2022 | 0.044595 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
CAGUAS | 2022-05-17 13:05 | 2022-05-17 13:06 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1702 | keep | 0 | May | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
VEGA BAJA | 2022-05-17 13:05 | 2022-05-17 13:06 | 538 | 000:01 | T | ARBOL SOBRE LINEA | RECIERRE | B22051700115 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-05-17 | 538 | keep | 0 | May | 2022 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2022-05-17 13:06 | 2022-05-17 17:40 | 250 | 004:34 | P | ARBOL SOBRE LINEA | 1 X 100, 2 X 80 Y 1 X 65 EN CORTES DE LINEAS SE RETIRO ARBOL SOBRE LINEAS | B22051700137 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 274 | 2022-05-17 | 68500 | keep | 0 | May | 2022 | 0.046655 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2022-05-17 13:26 | 2022-05-17 18:28 | 80 | 005:02 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051700206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2022-05-17 | 24160 | keep | 0 | May | 2022 | 0.016455 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-17 13:38 | 2022-05-17 15:10 | 10 | 001:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA AVERIADA | B22051700128 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2022-05-17 | 920 | keep | 0 | May | 2022 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-17 13:46 | 2022-05-17 15:15 | 10 | 001:29 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051700028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-05-17 | 890 | keep | 0 | May | 2022 | 0.00060617 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-17 13:51 | 2022-05-17 13:52 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051700211 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-17 13:51 | 2022-05-17 13:52 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6012-05 NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051700211 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-17 13:58 | 2022-05-17 13:59 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051700215 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-17 13:58 | 2022-05-17 13:59 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6012-05 NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051700215 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
BAYAMON | 2022-05-17 14:02 | 2022-05-17 16:47 | 80 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22051700134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-05-17 | 13200 | keep | 0 | May | 2022 | 0.0089905 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-05-17 14:07 | 2022-05-17 15:43 | 8 | 001:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | C22051700081 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2022-05-17 | 768 | keep | 0 | May | 2022 | 0.00052308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-17 14:07 | 2022-05-17 14:08 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051700220 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-17 14:07 | 2022-05-17 14:08 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6012-05 NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051700220 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2022-05-17 14:11 | 2022-05-17 14:12 | 837 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR SU CARGA POR 1401-07 | S22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 837 | keep | 0 | May | 2022 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-05-17 14:11 | 2022-05-17 14:12 | 908 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 1401-06 | S22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 908 | keep | 0 | May | 2022 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
MAYAGÃœEZ | 2022-05-17 14:16 | 2022-05-17 14:17 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051700222 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-17 14:16 | 2022-05-17 14:17 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6012-05 NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M22051700222 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2022-05-17 14:29 | 2022-05-17 18:46 | 97 | 004:17 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S22051700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 257 | 2022-05-17 | 24929 | keep | 0 | May | 2022 | 0.016979 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
SAN JUAN | 2022-05-17 14:53 | 2022-05-17 16:30 | 8 | 001:37 | P | CAUSAS EXTERNAS | SE ABRIO PUENTE PARA REPARAR MENSAJERO PARTIDO | S22051700066 | New_Event | Damage From Public | Include | Include | Public | 97 | 2022-05-17 | 776 | keep | 0 | May | 2022 | 0.00052853 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-05-17 15:10 | 2022-05-17 17:59 | 95 | 002:49 | P | DESGANCHE | 2 X 50 EN C/L | C22051700087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-05-17 | 16055 | keep | 0 | May | 2022 | 0.010935 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
VEGA BAJA | 2022-05-17 15:13 | 2022-05-17 18:58 | 110 | 003:45 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B22051700143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-05-17 | 24750 | keep | 0 | May | 2022 | 0.016857 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
SAN JUAN | 2022-05-17 15:30 | 2022-05-17 16:00 | 12 | 000:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | R22051700024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-05-17 | 360 | keep | 0 | May | 2022 | 0.00024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-17 15:45 | 2022-05-18 16:25 | 6 | 024:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONECTORES DE BAJANTE SECUNDARIO | A22051700117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1480 | 2022-05-17 | 8880 | keep | 0 | May | 2022 | 0.0060481 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-17 15:56 | 2022-05-17 19:49 | 100 | 003:53 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22051700039 | New_Event | Primary Wire Break | Include | Include | Equipment | 233 | 2022-05-17 | 23300 | keep | 0 | May | 2022 | 0.01587 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-17 15:59 | 2022-05-17 20:00 | 50 | 004:01 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN PROVISIONAL AEREO. AVERIA NUEVA T-4 @ T-5 Y AVERIA VIEJA T-6 @ 5 | B22051700157 | New_Event | UG Cable Fault | Include | Include | Equipment | 241 | 2022-05-17 | 12050 | keep | 0 | May | 2022 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-17 16:17 | 2022-05-17 16:18 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | A22051700047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1227 | keep | 0 | May | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-05-17 16:17 | 2022-05-17 19:36 | 3431 | 003:19 | T | MAL TIEMPO/RAYOS | SE REMPLAZO CUATRO AISLADORES ROTOS A CAUSA DE RAYOS ELECTRICOS | A22051700046 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 199 | 2022-05-17 | 682769 | keep | 0 | May | 2022 | 0.46503 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-05-17 16:21 | 2022-05-17 19:27 | 2379 | 003:06 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA LA CARGA SE ENCUENTRA POR 7404-07 QUE ES SPARE | A22051700054 | New_Event | Primary Wire Break | Include | Include | Equipment | 186 | 2022-05-17 | 442494 | keep | 0 | May | 2022 | 0.30138 | 0.0016203 | Sustained | FALSE | FALSE | Not_TMED_Event | 2379
VEGA BAJA | 2022-05-17 16:44 | 2022-05-17 16:47 | 1526 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200/7800 | B22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-17 | 4578 | keep | 0 | May | 2022 | 0.0031181 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2022-05-17 16:44 | 2022-05-17 16:47 | 308 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200/7800 | B22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-17 | 924 | keep | 0 | May | 2022 | 0.00062933 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-05-17 16:44 | 2022-05-17 16:47 | 1397 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200/7800 | B22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-17 | 4191 | keep | 0 | May | 2022 | 0.0028545 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2022-05-17 16:44 | 2022-05-17 16:47 | 2926 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200/7800 | B22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-17 | 8778 | keep | 0 | May | 2022 | 0.0059787 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
VEGA BAJA | 2022-05-17 16:44 | 2022-05-17 16:47 | 27 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200/7800 | B22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-17 | 81 | keep | 0 | May | 2022 | 5.5169e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2022-05-17 16:44 | 2022-05-17 16:47 | 603 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200/7800 | B22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-17 | 1809 | keep | 0 | May | 2022 | 0.0012321 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-05-17 16:44 | 2022-05-17 16:47 | 6 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200/7800 | B22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-17 | 18 | keep | 0 | May | 2022 | 1.226e-05 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-05-17 16:44 | 2022-05-17 16:47 | 325 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200/7800 | B22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-17 | 975 | keep | 0 | May | 2022 | 0.00066407 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2022-05-17 16:44 | 2022-05-17 16:47 | 172 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200/7800 | B22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-17 | 516 | keep | 0 | May | 2022 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
VEGA BAJA | 2022-05-17 16:47 | 2022-05-18 12:29 | 5 | 019:42 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACIONES TIPO PISTOLA EN CAJAS SECAS EN MH3 | B22051700015 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1182 | 2022-05-17 | 5910 | keep | 0 | May | 2022 | 0.0040253 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-05-17 16:53 | 2022-05-17 19:29 | 90 | 002:36 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22051700187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2022-05-17 | 14040 | keep | 0 | May | 2022 | 0.0095626 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2022-05-17 17:01 | 2022-05-17 17:47 | 20 | 000:46 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE EN SUELO SE ABRE PUENTES SE TRABAJAR PARA EL PROXIMO DIA | P22051700065 | New_Event | Primary Wire Break | Include | Include | Equipment | 46 | 2022-05-17 | 920 | keep | 0 | May | 2022 | 0.00062661 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-05-17 17:17 | 2022-05-17 23:00 | 7 | 005:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ABIERTA | P22051700066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 343 | 2022-05-17 | 2401 | keep | 0 | May | 2022 | 0.0016353 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-17 17:43 | 2022-05-17 18:01 | 15 | 000:18 | P | ANIMAL | 1 X 20 EN CORTE DE LINEA CRUCE POR AVE | B22051700111 | New_Event | Animals | Include | Include | Wildlife | 18 | 2022-05-17 | 270 | keep | 0 | May | 2022 | 0.0001839 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-05-17 17:47 | 2022-05-18 11:42 | 35 | 017:55 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE PRIMARIO Y SE CERRARON PUENTES | P22051800219 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1075 | 2022-05-17 | 37625 | keep | 0 | May | 2022 | 0.025626 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-17 17:50 | 2022-05-18 09:47 | 50 | 015:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22051700118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 957 | 2022-05-17 | 47850 | keep | 0 | May | 2022 | 0.03259 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-17 17:57 | 2022-05-17 19:01 | 10 | 001:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | S22051700079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2022-05-17 | 640 | keep | 0 | May | 2022 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-17 18:07 | 2022-05-17 23:00 | 80 | 004:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | M22051700250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 293 | 2022-05-17 | 23440 | keep | 0 | May | 2022 | 0.015965 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-17 18:24 | 2022-05-17 18:25 | 318 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1711-03 LLEVANDO 20% 1711-01 | B22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 318 | keep | 0 | May | 2022 | 0.00021659 | 0.00021659 | Momentary | FALSE | FALSE | Not_TMED_Event | 318
BAYAMON | 2022-05-17 18:24 | 2022-05-17 18:25 | 13 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1711-03 LLEVANDO 20% 1711-01 | B22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 13 | keep | 0 | May | 2022 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 1253 | keep | 0 | May | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 1266 | keep | 0 | May | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 411 | keep | 0 | May | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 1617 | keep | 0 | May | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 1017 | keep | 0 | May | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 828 | keep | 0 | May | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 863 | keep | 0 | May | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 309 | keep | 0 | May | 2022 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 176 | keep | 0 | May | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-17 18:28 | 2022-05-17 18:29 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22051700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-17 | 974 | keep | 0 | May | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
MAYAGÃœEZ | 2022-05-17 18:29 | 2022-05-17 19:35 | 80 | 001:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051700206 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-05-17 | 5280 | keep | 0 | May | 2022 | 0.0035962 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-17 18:33 | 2022-05-17 18:34 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051700103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1702 | keep | 0 | May | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
MAYAGÃœEZ | 2022-05-17 19:38 | 2022-05-17 19:39 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22051700270 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 2999 | keep | 0 | May | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
BAYAMON | 2022-05-17 19:42 | 2022-05-18 12:01 | 93 | 016:19 | P | DESGANCHE | 1 X 65 EN C.L Y DESGANCHE | S22051700120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 979 | 2022-05-17 | 91047 | keep | 0 | May | 2022 | 0.062012 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2022-05-17 19:42 | 2022-05-18 00:03 | 130 | 004:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051700271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2022-05-17 | 33930 | keep | 0 | May | 2022 | 0.02311 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2022-05-17 19:46 | 2022-05-18 14:25 | 20 | 018:39 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S22051700311 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 1119 | 2022-05-17 | 22380 | keep | 0 | May | 2022 | 0.015243 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-17 19:54 | 2022-05-17 21:11 | 643 | 001:17 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1530-07 LLEVANDO LA CARGA DEL 1530-06 Y 1526-02. SE SECCIONALIZO ENTRANDO 80% EN SERVICIO 1530-07, 100 EN SERVICIO DEL 1526-02 Y 1530-06 SIGUE FUERA. | S22051700132 | New_Event | Primary Wire Break | Include | Include | Equipment | 77 | 2022-05-17 | 49511 | keep | 0 | May | 2022 | 0.033722 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
BAYAMON | 2022-05-17 19:54 | 2022-05-17 22:56 | 437 | 003:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1530-07 QUE LLEVA A SU VEZ LA CARGA DEL 1530-06. SE SECCIONALIZO Y SE LEVANTO LINEA PRIMARIA. | S22051700132 | New_Event | Primary Wire Break | Include | Include | Equipment | 182 | 2022-05-17 | 79534 | keep | 0 | May | 2022 | 0.05417 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-05-17 19:54 | 2022-05-17 21:11 | 643 | 001:17 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1530-07 LLEVANDO LA CARGA DEL 1530-06 Y 1530-07. SE SECCIONALIZO ENTRANDO 80% EN SERVICIO 1530-07, 100 EN SERVICIO DEL 1526-02 Y 1530-06 SIGUE FUERA. | S22051700132 | New_Event | Primary Wire Break | Include | Include | Equipment | 77 | 2022-05-17 | 49511 | keep | 0 | May | 2022 | 0.033722 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
GUAYAMA | 2022-05-17 19:57 | 2022-05-17 22:53 | 30 | 002:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22051700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-05-17 | 5280 | keep | 0 | May | 2022 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-17 19:57 | 2022-05-17 20:43 | 40 | 000:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A22051700156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 46 | 2022-05-17 | 1840 | keep | 0 | May | 2022 | 0.0012532 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-17 20:00 | 2022-05-18 16:42 | 10 | 020:42 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE A T5 | B22051700157 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1242 | 2022-05-17 | 12420 | keep | 0 | May | 2022 | 0.0084592 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-17 20:03 | 2022-05-17 20:07 | 2708 | 000:04 | S | SOBRECARGA | DISPARO 0010 | R22051700000 | New_Event | Trip Due To Overload | Include | Include | Other | 4 | 2022-05-17 | 10832 | keep | 0 | May | 2022 | 0.0073776 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-05-17 20:03 | 2022-05-17 20:07 | 2524 | 000:04 | S | SOBRECARGA | DISPARO 0010 | R22051700000 | New_Event | Trip Due To Overload | Include | Include | Other | 4 | 2022-05-17 | 10096 | keep | 0 | May | 2022 | 0.0068763 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-05-17 20:03 | 2022-05-17 20:07 | 1648 | 000:04 | S | SOBRECARGA | DISPARO 0010 | R22051700000 | New_Event | Trip Due To Overload | Include | Include | Other | 4 | 2022-05-17 | 6592 | keep | 0 | May | 2022 | 0.0044898 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
AGUADILLA | 2022-05-17 20:14 | 2022-05-19 01:22 | 10 | 029:08 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR UNO DE 50KVA | M22051700275 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1748 | 2022-05-17 | 17480 | keep | 0 | May | 2022 | 0.011906 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-05-17 20:27 | 2022-05-18 07:23 | 25 | 010:56 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22051700272 | New_Event | Vegetation Contact | Include | Include | Vegetation | 656 | 2022-05-17 | 16400 | keep | 0 | May | 2022 | 0.01117 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-05-17 20:36 | 2022-05-17 20:37 | 2747 | 000:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | P22051700079 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-05-17 | 2747 | keep | 0 | May | 2022 | 0.001871 | 0.001871 | Momentary | FALSE | FALSE | Not_TMED_Event | 2747
YAUCO | 2022-05-17 20:37 | 2022-05-17 22:26 | 915 | 001:49 | P | CONDUCTOR ROTO O ABIERTO | FASE PRIMARIA EN TRONCAL PARTIDA SE ABRE INTERRUPTOR INTERRUPCION CONTINUA | P22051700079 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 109 | 2022-05-17 | 99735 | keep | 0 | May | 2022 | 0.067929 | 0.0006232 | Sustained | FALSE | FALSE | Not_TMED_Event | 915
ARECIBO | 2022-05-17 20:43 | 2022-05-18 04:04 | 50 | 007:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | A22051700277 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 441 | 2022-05-17 | 22050 | keep | 0 | May | 2022 | 0.015018 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-05-17 20:45 | 2022-05-17 22:43 | 2708 | 001:58 | T | SOBRECARGA | DISPARO POR SOBRE CARGA | R22051700277 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 118 | 2022-05-17 | 319544 | keep | 0 | May | 2022 | 0.21764 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-05-17 20:45 | 2022-05-17 22:46 | 2524 | 002:01 | T | SOBRECARGA | DISPARO POR SOBRE CARGA | R22051700277 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 121 | 2022-05-17 | 305404 | keep | 0 | May | 2022 | 0.20801 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-05-17 20:45 | 2022-05-17 22:47 | 1648 | 002:02 | T | SOBRECARGA | DISPARO POR SOBRE CARGA | R22051700277 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 122 | 2022-05-17 | 201056 | keep | 0 | May | 2022 | 0.13694 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
MAYAGÃœEZ | 2022-05-17 20:45 | 2022-05-18 16:40 | 50 | 019:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22051700278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1195 | 2022-05-17 | 59750 | keep | 0 | May | 2022 | 0.040695 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-17 20:59 | 2022-05-17 21:00 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | A22051700163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 1494 | keep | 0 | May | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2022-05-17 21:00 | 2022-05-17 23:33 | 100 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | A22051700170 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 153 | 2022-05-17 | 15300 | keep | 0 | May | 2022 | 0.010421 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-05-17 21:02 | 2022-05-17 21:03 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 824 | keep | 0 | May | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-05-17 21:11 | 2022-05-17 22:51 | 129 | 001:40 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO Y SE LEVANTO LINEA PRIMARIA | S22051700132 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 100 | 2022-05-17 | 12900 | keep | 0 | May | 2022 | 0.0087861 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-17 21:27 | 2022-05-18 07:05 | 187 | 009:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 Y 1 X 50 EN CORTES DE LINEA FUERTES VIENTOS | C22051700124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 578 | 2022-05-17 | 108086 | keep | 0 | May | 2022 | 0.073617 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
PONCE | 2022-05-17 21:30 | 2022-05-18 00:05 | 400 | 002:35 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA PARTIDA SE ABREN MACHETES PARA SECCIONALIZAR AVERIA | P22051700104 | New_Event | Primary Wire Break | Include | Include | Equipment | 155 | 2022-05-17 | 62000 | keep | 0 | May | 2022 | 0.042228 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-05-17 21:45 | 2022-05-18 11:52 | 15 | 014:07 | P | CONDUCTOR ROTO O ABIERTO | SE LLEVO BAJANTE DE CAJA A XMR Y 1 X 15 EN XMR | S22051700273 | New_Event | Primary Wire Break | Include | Include | Equipment | 847 | 2022-05-17 | 12705 | keep | 0 | May | 2022 | 0.0086533 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-17 22:05 | 2022-05-17 22:06 | 151 | 000:01 | P | CONDUCTOR ROTO O ABIERTO | CERRAR PUENTE DE LINEA A MACHETE | S22051700080 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-05-17 | 151 | keep | 0 | May | 2022 | 0.00010285 | 0.00010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 151
YAUCO | 2022-05-17 22:26 | 2022-05-18 04:16 | 2747 | 005:50 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE COLOCO INTERRUPTOR EN SERVICIO | P22051700082 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 350 | 2022-05-17 | 961450 | keep | 0 | May | 2022 | 0.65484 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-17 22:47 | 2022-05-18 12:38 | 14 | 013:51 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S22051700311 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 831 | 2022-05-17 | 11634 | keep | 0 | May | 2022 | 0.0079239 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-05-17 22:50 | 2022-05-17 22:51 | 75 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22051700301 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-17 | 75 | keep | 0 | May | 2022 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-05-17 22:54 | 2022-05-18 06:10 | 143 | 007:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22051700147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 436 | 2022-05-17 | 62348 | keep | 0 | May | 2022 | 0.042465 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
CANOVANAS | 2022-05-17 23:00 | 2022-05-18 00:12 | 1648 | 001:12 | T | SOBRECARGA | SE ABRIO BKR POR SOBRECARGA DE LA SUB 2302-00 Y SE NORMALIZO LA CARGA DEL 2402-02 | R22051700000 | Partial_restoration | Trip Due To Overload | Include | Include | Other | 72 | 2022-05-17 | 118656 | keep | 0 | May | 2022 | 0.080816 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-17 23:00 | 2022-05-18 11:22 | 3 | 012:22 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | B22081700359 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 742 | 2022-05-17 | 2226 | keep | 0 | May | 2022 | 0.0015161 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-05-17 23:05 | 2022-05-18 11:40 | 33 | 012:35 | P | DESGANCHE | 1 X 50 EN C/L Y SE REALIZO DESGANCHE | S22051700318 | New_Event | Vegetation Contact | Include | Include | Vegetation | 755 | 2022-05-17 | 24915 | keep | 0 | May | 2022 | 0.016969 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
SAN JUAN | 2022-05-17 23:31 | 2022-05-18 13:37 | 10 | 014:06 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S22051700328 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 846 | 2022-05-17 | 8460 | keep | 0 | May | 2022 | 0.0057621 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-17 23:45 | 2022-05-18 10:45 | 3 | 011:00 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR | A22051700181 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 660 | 2022-05-17 | 1980 | keep | 0 | May | 2022 | 0.0013486 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-05-18 00:05 | 2022-05-18 01:13 | 1663 | 001:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRARON MACHETES | P22051700104 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 68 | 2022-05-18 | 113084 | keep | 0 | May | 2022 | 0.077021 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-05-18 00:26 | 2022-05-18 00:27 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 2286 | keep | 0 | May | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
BAYAMON | 2022-05-18 00:39 | 2022-05-18 00:40 | 3597 | 000:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | B22051800000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-18 | 3597 | keep | 0 | May | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-05-18 00:40 | 2022-05-18 11:33 | 150 | 010:53 | P | ANIMAL | 1 X 200 EN C/L AVE CRUZO LINEAS | B22051800069 | 1st_after_momentary | Animals | Include | Include | Wildlife | 653 | 2022-05-18 | 97950 | keep | 0 | May | 2022 | 0.066713 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-05-18 01:39 | 2022-05-18 01:40 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22051800017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 2450 | keep | 0 | May | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
FAJARDO | 2022-05-18 02:59 | 2022-05-18 07:03 | 76 | 004:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE REEMPLAZO DISCO QUEMADO Y MACHETE DE RISER QUEMADO DEL 2005-11 Y SE NORMALIZO ALIMENTADOR. | R22051800040 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 244 | 2022-05-18 | 18544 | keep | 0 | May | 2022 | 0.01263 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
VEGA BAJA | 2022-05-18 03:06 | 2022-05-18 03:07 | 3000 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | B22051800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-18 | 3000 | keep | 0 | May | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2022-05-18 03:07 | 2022-05-18 12:26 | 36 | 009:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y 1 X 80 EN C/L | B22051800038 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 559 | 2022-05-18 | 20124 | keep | 0 | May | 2022 | 0.013706 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2022-05-18 04:02 | 2022-05-18 15:34 | 250 | 011:32 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN TRONCAL CON GOI BY-220518-01A | B22051800044 | New_Event | Primary Wire Break | Include | Include | Equipment | 692 | 2022-05-18 | 173000 | keep | 0 | May | 2022 | 0.11783 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
HUMACAO | 2022-05-18 05:28 | 2022-05-18 05:29 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 824 | keep | 0 | May | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
SAN JUAN | 2022-05-18 06:12 | 2022-05-18 12:59 | 61 | 006:47 | P | DESGANCHE | 1 X 140 EN C/L Y DESGANCHE | S22051800060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2022-05-18 | 24827 | keep | 0 | May | 2022 | 0.01691 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
MAYAGÃœEZ | 2022-05-18 06:34 | 2022-05-18 11:50 | 50 | 005:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | M22051800024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2022-05-18 | 15800 | keep | 0 | May | 2022 | 0.010761 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-18 07:02 | 2022-05-18 17:52 | 17 | 010:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5KVA CRUCETA Y PARARRAYOS | S22051800069 | New_Event | Service Transformer Failure | Include | Include | Equipment | 650 | 2022-05-18 | 11050 | keep | 0 | May | 2022 | 0.0075261 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2022-05-18 07:11 | 2022-05-18 10:57 | 40 | 003:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22051800028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2022-05-18 | 9040 | keep | 0 | May | 2022 | 0.0061571 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-18 08:01 | 2022-05-19 17:10 | 15 | 033:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS TRANSFORMADOR, AUNQUE SE ABRIO A LAS 14:42 DEL DIA 19 LOS CLIENTES ESTABAN CON PROBLEMAS DESDE EL DIA 18 | A22051800011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1989 | 2022-05-18 | 29835 | keep | 0 | May | 2022 | 0.02032 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-05-18 08:16 | 2022-05-18 14:23 | 6 | 006:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 25 KVA A 2400 VOLT QUE NO REGULABA | P22051800177 | New_Event | Service Transformer Failure | Include | Include | Equipment | 367 | 2022-05-18 | 2202 | keep | 0 | May | 2022 | 0.0014998 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-05-18 08:17 | 2022-05-18 15:27 | 1 | 007:10 | P | NO SE REPORTO CAUSA | 2 X 10 EN MONTURA XMR | B22051800138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 430 | 2022-05-18 | 430 | keep | 0 | May | 2022 | 0.00029287 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-18 08:19 | 2022-05-18 12:12 | 50 | 003:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22051800012 | New_Event | Cutout Failure | Include | Include | Equipment | 233 | 2022-05-18 | 11650 | keep | 0 | May | 2022 | 0.0079348 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-18 08:21 | 2022-05-18 10:07 | 49 | 001:46 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 50 EN SU3 1 X 40 EN AEREO PROVISINAL Y 1 X 10 DE SU 3B A T11. SE REPARO PORTAFUSIBLE Y SE REPARO PUENTE EN SU3 | B22051800040 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 106 | 2022-05-18 | 5194 | keep | 0 | May | 2022 | 0.0035376 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
CAGUAS | 2022-05-18 08:52 | 2022-05-18 08:53 | 1017 | 000:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO INTERRUPTOR EN SERVICIO | C22051800049 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-05-18 | 1017 | keep | 0 | May | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
BAYAMON | 2022-05-18 08:53 | 2022-05-18 20:19 | 15 | 011:26 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTES PRIMARIOS PARA REMPLAZO POSTE EN MAL ESTADO Y RELOCALIZAR TRANSFORMADOR | B22051800159 | New_Event | Primary Pole Failure | Include | Include | Equipment | 686 | 2022-05-18 | 10290 | keep | 0 | May | 2022 | 0.0070085 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-05-18 08:53 | 2022-05-18 15:02 | 157 | 006:09 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SE ABRIO MACHETES PARA REPARAR | C22051800075 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 369 | 2022-05-18 | 57933 | keep | 0 | May | 2022 | 0.039458 | 0.00010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 157
HUMACAO | 2022-05-18 08:59 | 2022-05-18 22:43 | 519 | 013:44 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD DE LA LINEA 12600 Y SE REMPLAZO VARIOS TRAMOS DE LINEA PRIMARIA | C22051800077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 824 | 2022-05-18 | 427656 | keep | 0 | May | 2022 | 0.29127 | 0.00035349 | Sustained | FALSE | FALSE | Not_TMED_Event | 519
HUMACAO | 2022-05-18 08:59 | 2022-05-18 22:43 | 1117 | 013:44 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD DE LA LINEA 12600 Y SE REMPLAZO VARIOS TRAMOS DE LINEA PRIMARIA | C22051800077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 824 | 2022-05-18 | 920408 | keep | 0 | May | 2022 | 0.62689 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
HUMACAO | 2022-05-18 08:59 | 2022-05-18 23:32 | 2126 | 014:33 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD DE LA LINEA 12600 Y SE REMPLAZO VARIOS TRAMOS DE LINEA PRIMARIA | C22051800077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 873 | 2022-05-18 | 1855998 | keep | 0 | May | 2022 | 1.2641 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-05-18 08:59 | 2022-05-18 23:15 | 551 | 014:16 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD DE LA LINEA 12600 Y SE REMPLAZO VARIOS TRAMOS DE LINEA PRIMARIA | C22051800077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 856 | 2022-05-18 | 471656 | keep | 0 | May | 2022 | 0.32124 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2022-05-18 08:59 | 2022-05-18 22:51 | 2450 | 013:52 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD DE LA LINEA 12600 Y SE REMPLAZO VARIOS TRAMOS DE LINEA PRIMARIA | C22051800077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 832 | 2022-05-18 | 2038400 | keep | 0 | May | 2022 | 1.3883 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-05-18 08:59 | 2022-05-18 22:51 | 640 | 013:52 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD DE LA LINEA 12600 Y SE REMPLAZO VARIOS TRAMOS DE LINEA PRIMARIA | C22051800077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 832 | 2022-05-18 | 532480 | keep | 0 | May | 2022 | 0.36267 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
HUMACAO | 2022-05-18 09:00 | 2022-05-18 12:12 | 5630 | 003:12 | T | LINEA DE TRANSMISION 38KV | SE TRANSFIRIO EL 70% DE LA CARGA DEL 2603-08 AL 3205-07 POR AVERIA DEL RISER DE SALIDA A CAUSA DE LINEA 12600 CG-220518-01 | C22051800130 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 192 | 2022-05-18 | 1080960 | keep | 0 | May | 2022 | 0.73624 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
ARECIBO | 2022-05-18 09:00 | 2022-05-18 10:24 | 75 | 001:24 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A22051800017 | New_Event | Animals | Include | Include | Wildlife | 84 | 2022-05-18 | 6300 | keep | 0 | May | 2022 | 0.0042909 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-05-18 09:01 | 2022-05-18 09:02 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M22051800067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 312 | keep | 0 | May | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2022-05-18 09:03 | 2022-05-18 09:08 | 87 | 000:05 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA 20% DE LA CARGA POR EL 1658-14 | R22051800000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 5 | 2022-05-18 | 435 | keep | 0 | May | 2022 | 0.00029628 | 5.9255e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 87
SAN JUAN | 2022-05-18 09:03 | 2022-05-18 09:08 | 1 | 000:05 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA LLEVA UN 20% DEL 1657-02 | R22051800000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 5 | 2022-05-18 | 5 | keep | 0 | May | 2022 | 3.4055e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-18 09:03 | 2022-05-18 09:08 | 1 | 000:05 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA | R22051800000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 5 | 2022-05-18 | 5 | keep | 0 | May | 2022 | 3.4055e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-18 09:16 | 2022-05-18 10:07 | 14 | 000:51 | P | ANIMAL | 1 X 50 EN C/L SE RETIRO IGUANA | B22051800171 | New_Event | Animals | Include | Include | Wildlife | 51 | 2022-05-18 | 714 | keep | 0 | May | 2022 | 0.0004863 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-05-18 09:17 | 2022-05-18 09:18 | 1483 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 30% DE LA CARGA POR EL 1336-08 | S22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 1483 | keep | 0 | May | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-18 09:17 | 2022-05-18 09:18 | 1500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL CARGA POR EL 1336-08 | S22051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 1500 | keep | 0 | May | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-05-18 09:17 | 2022-05-18 09:18 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1336-09, 30% DEL 1204-04 | S22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 5290 | keep | 0 | May | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-05-18 09:17 | 2022-05-18 09:18 | 207 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1336-08 | S22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 207 | keep | 0 | May | 2022 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
GUAYAMA | 2022-05-18 09:20 | 2022-05-18 10:30 | 20 | 001:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22051800208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-05-18 | 1400 | keep | 0 | May | 2022 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-18 09:22 | 2022-05-18 16:30 | 5 | 007:08 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22051800114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 428 | 2022-05-18 | 2140 | keep | 0 | May | 2022 | 0.0014575 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-05-18 09:27 | 2022-05-18 09:28 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051800214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 2379 | keep | 0 | May | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
MAYAGÃœEZ | 2022-05-18 09:32 | 2022-05-18 13:00 | 1 | 003:28 | P | ANIMAL | 2 X 10 EN MONTURA TRIFASICA CRUCE DE FASE EN EQUIPO DE MEDICION POR AVE | M22051800057 | New_Event | Animals | Include | Include | Wildlife | 208 | 2022-05-18 | 208 | keep | 0 | May | 2022 | 0.00014167 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-18 09:35 | 2022-05-18 14:40 | 10 | 005:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22051800023 | New_Event | Cutout Failure | Include | Include | Equipment | 305 | 2022-05-18 | 3050 | keep | 0 | May | 2022 | 0.0020773 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-18 09:40 | 2022-05-18 10:15 | 10 | 000:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR CONECTORES EN BAJANTE SECUNDARIO | C22051700019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-05-18 | 350 | keep | 0 | May | 2022 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-18 09:42 | 2022-05-18 15:15 | 20 | 005:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M22051800023 | New_Event | Primary Wire Break | Include | Include | Equipment | 333 | 2022-05-18 | 6660 | keep | 0 | May | 2022 | 0.0045361 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-18 09:45 | 2022-05-18 09:57 | 87 | 000:12 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA 20% DE LA CARGA POR EL 1658-14 | R22051800000 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 12 | 2022-05-18 | 1044 | keep | 0 | May | 2022 | 0.00071106 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-18 09:45 | 2022-05-18 09:57 | 1 | 000:12 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA LLEVA UN 20% DEL 1657-02 | R22051800000 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 12 | 2022-05-18 | 12 | keep | 0 | May | 2022 | 8.1731e-06 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-18 09:45 | 2022-05-18 09:57 | 1 | 000:12 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA | R22051800000 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 12 | 2022-05-18 | 12 | keep | 0 | May | 2022 | 8.1731e-06 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-18 09:45 | 2022-05-18 09:46 | 2446 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051800220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 2446 | keep | 0 | May | 2022 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2022-05-18 09:45 | 2022-05-18 09:46 | 5069 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051800220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 5069 | keep | 0 | May | 2022 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
SAN JUAN | 2022-05-18 09:51 | 2022-05-18 09:55 | 1452 | 000:04 | T | CONDUCTOR ROTO O ABIERTO | SE PICO LINEA DEL TRONCAL POR EMERGENCIA (NO TIENE CLIENTES ) SE ABRIO BKR A PETICION DE JUAN C RAMOS POR SITUACION PELIGROSA Y SE CERRO POR SCADA | S22051800065 | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2022-05-18 | 5808 | keep | 0 | May | 2022 | 0.0039558 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-05-18 10:00 | 2022-05-18 10:25 | 87 | 000:25 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA TERMINACION Y MACHETE QUEMADA EN EL SU62 HACIA SU5 DEL 1558-15 20% DE SU CARGA POR EL 1658-14 | R22051800000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 25 | 2022-05-18 | 2175 | keep | 0 | May | 2022 | 0.0014814 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
SAN JUAN | 2022-05-18 10:00 | 2022-05-18 10:25 | 1 | 000:25 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA LLEVA UN 20% DEL 1657-02 TERMINACION Y MACHETE QUEMADA EN EL SU62 HACIA SU5 1658-15 | R22051800000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 25 | 2022-05-18 | 25 | keep | 0 | May | 2022 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-18 10:00 | 2022-05-18 10:25 | 1 | 000:25 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA TERMINACION Y MACHETE QUEMADA EN EL SU62 HACIA SU5 | R22051800000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 25 | 2022-05-18 | 25 | keep | 0 | May | 2022 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-18 10:07 | 2022-05-18 10:11 | 4431 | 000:04 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO INTERRUPTOR PARA RETIRAR PUENTES PRIMARIOS Y PORTAFUSIBLE EN SU3 EN FUEGO | B22051800000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 4 | 2022-05-18 | 17724 | keep | 0 | May | 2022 | 0.012072 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
SAN JUAN | 2022-05-18 10:10 | 2022-05-18 14:33 | 100 | 004:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22051800127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2022-05-18 | 26300 | keep | 0 | May | 2022 | 0.017913 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-18 10:11 | 2022-05-18 10:30 | 14 | 000:19 | P | ANIMAL | 1 X 50 EN C/L SE RETIRO IGUANA | B22051800171 | New_Event | Animals | Include | Include | Wildlife | 19 | 2022-05-18 | 266 | keep | 0 | May | 2022 | 0.00018117 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-05-18 10:11 | 2022-05-18 14:00 | 49 | 003:49 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 50 EN SU3 1 X 40 EN AEREO PROVISINAL Y 1 X 10 DE SU 3B A T11. SE REPARO PORTAFUSIBLE Y SE REPARO PUENTE EN SU3 | B22051800040 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 229 | 2022-05-18 | 11221 | keep | 0 | May | 2022 | 0.0076426 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
MAYAGÃœEZ | 2022-05-18 10:16 | 2022-05-18 15:20 | 2 | 005:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051800065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2022-05-18 | 608 | keep | 0 | May | 2022 | 0.00041411 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-05-18 10:18 | 2022-05-18 13:50 | 40 | 003:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REMPLAZO CAJA EN RISER | B22051800212 | New_Event | Cutout Failure | Include | Include | Equipment | 212 | 2022-05-18 | 8480 | keep | 0 | May | 2022 | 0.0057757 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-05-18 10:24 | 2022-05-18 11:14 | 3973 | 000:50 | T | CONDUCTOR ARRIADO O CRUZADO | SE ABRE INTERRUPTOR A PEDIDO DE JESUS JAIME POR LIGADURA SAFADA Y LA LINEA SOBRE CRUCETA | P22051800238 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 50 | 2022-05-18 | 198650 | keep | 0 | May | 2022 | 0.1353 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
BARRANQUITAS | 2022-05-18 10:36 | 2022-05-18 13:03 | 67 | 002:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22051800162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-05-18 | 9849 | keep | 0 | May | 2022 | 0.0067081 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-05-18 11:00 | 2022-05-18 11:01 | 4176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4100 PORTATIL 7 CONECTADA | B22051800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-18 | 4176 | keep | 0 | May | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-05-18 11:00 | 2022-05-18 11:01 | 252 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4100 PORTATIL 7 CONECTADA | B22051800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-18 | 252 | keep | 0 | May | 2022 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
PONCE | 2022-05-18 11:01 | 2022-05-18 13:55 | 100 | 002:54 | P | DESGANCHE | 1 X 100 EN CONVERTIDOR SE HIZO DESGANCHE | P22051800258 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-05-18 | 17400 | keep | 0 | May | 2022 | 0.011851 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-18 11:03 | 2022-05-18 12:56 | 90 | 001:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22051800173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-05-18 | 10170 | keep | 0 | May | 2022 | 0.0069267 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-05-18 11:08 | 2022-05-18 11:30 | 7 | 000:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22051700099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 22 | 2022-05-18 | 154 | keep | 0 | May | 2022 | 0.00010489 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-05-18 11:09 | 2022-05-18 16:50 | 100 | 005:41 | P | CONDUCTOR ARRIADO O CRUZADO | SE REPARO CONDUCTOR ARRIADO | A22051800033 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 341 | 2022-05-18 | 34100 | keep | 0 | May | 2022 | 0.023225 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-05-18 11:15 | 2022-05-18 11:16 | 1604 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22051800180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-18 | 1604 | keep | 0 | May | 2022 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2022-05-18 11:16 | 2022-05-18 14:05 | 116 | 002:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE POR PENCA DE PALMA | C22051800217 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-05-18 | 19604 | keep | 0 | May | 2022 | 0.013352 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
YAUCO | 2022-05-18 11:20 | 2022-05-18 12:39 | 2003 | 001:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABREN MACHETES PARA SECIONALIZAR AVERIA DE AISLADOR ROTO | P22051800270 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 79 | 2022-05-18 | 158237 | keep | 0 | May | 2022 | 0.10777 | 0.0013642 | Sustained | FALSE | FALSE | Not_TMED_Event | 2003
ARECIBO | 2022-05-18 11:21 | 2022-05-18 11:22 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22051800034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 2697 | keep | 0 | May | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
GUAYAMA | 2022-05-18 11:25 | 2022-05-18 18:20 | 50 | 006:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CIERRA CORTE DE LINEA | P22051800272 | New_Event | Primary Wire Break | Include | Include | Equipment | 415 | 2022-05-18 | 20750 | keep | 0 | May | 2022 | 0.014133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-18 11:28 | 2022-05-18 14:35 | 1 | 003:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | C22051800187 | New_Event | Cutout Failure | Include | Include | Equipment | 187 | 2022-05-18 | 187 | keep | 0 | May | 2022 | 0.00012736 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-18 11:30 | 2022-05-18 12:57 | 10 | 001:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA HACER DESGANCHE Y LEVANTAR LA MISMA | P22051800275 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2022-05-18 | 870 | keep | 0 | May | 2022 | 0.00059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-05-18 11:30 | 2022-05-18 12:35 | 15 | 001:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA EN TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22051700275 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2022-05-18 | 975 | keep | 0 | May | 2022 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-18 11:37 | 2022-05-18 13:26 | 2861 | 001:49 | T | DESGANCHE | SE RETIRO RAMA CRUZANDO LINEAS Y SE CERRO POR SCADA | B22051800249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-05-18 | 311849 | keep | 0 | May | 2022 | 0.2124 | 0.0019486 | Sustained | FALSE | FALSE | Not_TMED_Event | 2861
ARECIBO | 2022-05-18 11:40 | 2022-05-18 16:00 | 13 | 004:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | A22051800039 | New_Event | Cutout Failure | Include | Include | Equipment | 260 | 2022-05-18 | 3380 | keep | 0 | May | 2022 | 0.0023021 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2022-05-18 11:40 | 2022-05-18 14:41 | 11 | 003:01 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA A XMR NO FUNDIO | B22051800250 | New_Event | Primary Wire Break | Include | Include | Equipment | 181 | 2022-05-18 | 1991 | keep | 0 | May | 2022 | 0.0013561 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-05-18 11:54 | 2022-05-18 11:55 | 300 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN AEREO PROVISIONAL | B22051800192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 300 | keep | 0 | May | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-05-18 12:10 | 2022-05-18 12:12 | 4634 | 000:02 | T | INTERRUPTOR DE POSTE DEFECTUOSO O AVERIADO | SE ABRIO INTERRUPTOR PARA PODER CERRAR BY PASS DEL INTELLIRRUPTER 3205-07B, INTELLIRRUPTER ESTA DEFECTUOSO | C22051800203 | New_Event | Pole Breaker Failure | Include | Include | Equipment | 2 | 2022-05-18 | 9268 | keep | 0 | May | 2022 | 0.0063124 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
HUMACAO | 2022-05-18 12:12 | 2022-05-19 00:05 | 1689 | 011:53 | P | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD DE LA LINEA 12600 CRUZANDO LA DISTRIBUCION Y SE REMPLAZO VARIOS TRAMOS DE LINEAS PRIMARIAS, SE TRANSFIRIO PARTE DE LA CARGA AL 3205-07 | C22051800130 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 713 | 2022-05-18 | 1204257 | keep | 0 | May | 2022 | 0.82021 | 0.0011504 | Sustained | FALSE | FALSE | Not_TMED_Event | 1689
GUAYAMA | 2022-05-18 12:12 | 2022-05-18 13:48 | 40 | 001:36 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P22051800291 | New_Event | Animals | Include | Include | Wildlife | 96 | 2022-05-18 | 3840 | keep | 0 | May | 2022 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-05-18 12:16 | 2022-05-18 13:39 | 1 | 001:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA QUEMADA DE CORTE DE LINEA DE LA FINCA | P22051800292 | New_Event | Cutout Failure | Include | Include | Equipment | 83 | 2022-05-18 | 83 | keep | 0 | May | 2022 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-05-18 12:22 | 2022-05-18 12:29 | 3701 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A NAGUABO PUEBLO | C22051800210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-18 | 25907 | keep | 0 | May | 2022 | 0.017645 | 0.0025207 | Sustained | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-05-18 12:22 | 2022-05-18 12:29 | 989 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A NAGUABO PUEBLO | C22051800210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-18 | 6923 | keep | 0 | May | 2022 | 0.0047152 | 0.0006736 | Sustained | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2022-05-18 12:22 | 2022-05-18 12:29 | 1467 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A NAGUABO PUEBLO | C22051800210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-05-18 | 10269 | keep | 0 | May | 2022 | 0.0069942 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
PONCE | 2022-05-18 12:28 | 2022-05-18 15:41 | 20 | 003:13 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 50 EN C/L SE REMPLAZO POSTE PRIMARIO PARTIDO | P22051800286 | New_Event | Primary Pole Failure | Include | Include | Equipment | 193 | 2022-05-18 | 3860 | keep | 0 | May | 2022 | 0.002629 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-05-18 12:39 | 2022-05-18 13:05 | 2003 | 000:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE ABREN MACHETES PARA SECIONALIZAR AVERIA DE AISLADOR ROTO | P22051800271 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 26 | 2022-05-18 | 52078 | keep | 0 | May | 2022 | 0.03547 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-18 12:45 | 2022-05-18 13:42 | 10 | 000:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22051800025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2022-05-18 | 570 | keep | 0 | May | 2022 | 0.00038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-05-18 12:50 | 2022-05-18 16:00 | 90 | 003:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051800082 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 190 | 2022-05-18 | 17100 | keep | 0 | May | 2022 | 0.011647 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-05-18 12:55 | 2022-05-18 18:30 | 3 | 005:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | M22051800084 | New_Event | Cutout Failure | Include | Include | Equipment | 335 | 2022-05-18 | 1005 | keep | 0 | May | 2022 | 0.0006845 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-05-18 12:56 | 2022-05-18 14:34 | 15 | 001:38 | P | SECUNDARIA/OTROS | SE REPARO TOMA Y PEDESTAL | P22051800312 | New_Event |  |  |  |  | 98 | 2022-05-18 | 1470 | keep | 0 | May | 2022 | 0.0010012 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-18 13:07 | 2022-05-18 13:08 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 1 | keep | 0 | May | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-05-18 13:14 | 2022-05-18 13:16 | 2722 | 000:02 | T | TERMINACION SOTERRADA AVERIADA | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR PELIGRO EN MAHOLE DENTRO DE LA SUBESTACION TERMINACIONES QUEMADAS EN MH DENTRO DE LA SUBESTACION | R22051800114 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 2 | 2022-05-18 | 5444 | keep | 0 | May | 2022 | 0.0037079 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
BAYAMON | 2022-05-18 13:14 | 2022-05-18 13:15 | 2735 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 2735 | keep | 0 | May | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
FAJARDO | 2022-05-18 13:15 | 2022-05-18 13:34 | 76 | 000:19 | T | TERMINACION SOTERRADA AVERIADA | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR PELIGRO EN MAHOLE DENTRO DE LA SUBESTACION TERMINACIONES QUEMADAS EN MH DENTRO DE LA SUBESTACION | R22051800114 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 19 | 2022-05-18 | 1444 | keep | 0 | May | 2022 | 0.0009835 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
BAYAMON | 2022-05-18 13:15 | 2022-05-18 19:10 | 147 | 005:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22051800388 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 355 | 2022-05-18 | 52185 | keep | 0 | May | 2022 | 0.035543 | 0.00010012 | Sustained | FALSE | FALSE | Not_TMED_Event | 147
MAYAGÃœEZ | 2022-05-18 13:34 | 2022-05-18 14:10 | 4892 | 000:36 | T | PARARRAYOS DEFECTUOSO | DISPARO DEL INTERRUPTOR PARARRAYOS DEFECTUOSO | M22051800097 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 36 | 2022-05-18 | 176112 | keep | 0 | May | 2022 | 0.11995 | 0.0033319 | Sustained | FALSE | FALSE | Not_TMED_Event | 4892
CAGUAS | 2022-05-18 13:41 | 2022-05-18 13:48 | 3 | 000:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22051800289 | New_Event | Secondary Wire Break | Include | Include | Equipment | 7 | 2022-05-18 | 21 | keep | 0 | May | 2022 | 1.4303e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-05-18 13:52 | 2022-05-18 13:53 | 315 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR SCADA | S22051800181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 315 | keep | 0 | May | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
ARECIBO | 2022-05-18 14:12 | 2022-05-18 14:13 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22051800049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
PONCE | 2022-05-18 14:19 | 2022-05-18 14:33 | 4 | 000:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22051800239 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2022-05-18 | 56 | keep | 0 | May | 2022 | 3.8141e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-18 14:21 | 2022-05-18 19:05 | 10 | 004:44 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S22051800184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2022-05-18 | 2840 | keep | 0 | May | 2022 | 0.0019343 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-05-18 14:31 | 2022-05-18 14:32 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051800342 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
ARECIBO | 2022-05-18 14:40 | 2022-05-18 17:41 | 10 | 003:01 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR DE 50KVA POR UNO DE 50KVA | A22051800023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 181 | 2022-05-18 | 1810 | keep | 0 | May | 2022 | 0.0012328 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-18 15:02 | 2022-05-18 17:18 | 473 | 002:16 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA CERRAR PUENTE DE LINEA A LINEA EN EL TRONCAL | C22051800075 | New_Event | Primary Wire Break | Include | Include | Equipment | 136 | 2022-05-18 | 64328 | keep | 0 | May | 2022 | 0.043814 | 0.00032216 | Sustained | FALSE | FALSE | Not_TMED_Event | 473
BAYAMON | 2022-05-18 15:04 | 2022-05-18 16:18 | 10 | 001:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIAS | B22051800372 | New_Event | Secondary Wire Break | Include | Include | Equipment | 74 | 2022-05-18 | 740 | keep | 0 | May | 2022 | 0.00050401 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-18 15:08 | 2022-05-18 16:48 | 4176 | 001:40 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA A SUBESTACION PORTATIL # 7 PARA REPARAR PUENTE PRIMARIO EN LINEA 4100 | B22051800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2022-05-18 | 417600 | keep | 0 | May | 2022 | 0.28443 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-05-18 15:08 | 2022-05-18 16:48 | 252 | 001:40 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA A SUBESTACION PORTATIL # 7 PARA REPARAR PUENTE PRIMARIO EN LINEA 4100 | B22051800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2022-05-18 | 25200 | keep | 0 | May | 2022 | 0.017164 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
CANOVANAS | 2022-05-18 15:09 | 2022-05-18 15:10 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 2106 | keep | 0 | May | 2022 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
SAN JUAN | 2022-05-18 15:13 | 2022-05-18 15:14 | 4481 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 30% DE SU CARGA POR 1619-2 | S22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 4481 | keep | 0 | May | 2022 | 0.003052 | 0.003052 | Momentary | FALSE | FALSE | Not_TMED_Event | 4481
BAYAMON | 2022-05-18 15:21 | 2022-05-19 10:17 | 1 | 018:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 1 X 40 EN SU | B22051800384 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1136 | 2022-05-18 | 1136 | keep | 0 | May | 2022 | 0.00077372 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-18 15:45 | 2022-05-18 16:44 | 8 | 000:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO TIERRA DE BANCO DE TRANSFORMADOR | S22051800094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2022-05-18 | 472 | keep | 0 | May | 2022 | 0.00032148 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-05-18 15:48 | 2022-05-18 16:01 | 10 | 000:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | B22051800294 | New_Event | Secondary Wire Break | Include | Include | Equipment | 13 | 2022-05-18 | 130 | keep | 0 | May | 2022 | 8.8542e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-18 15:52 | 2022-05-18 18:15 | 2124 | 002:23 | S | NO SE REPORTO CAUSA | DISPARO 0050 Y MAIN DIO LOCKOUT TRIP SE PASO CARGA ABRIENDO MH-1510 Y SE CERRO N/O CONTRA 1657-04 | S22051800223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2022-05-18 | 303732 | keep | 0 | May | 2022 | 0.20687 | 0.0014466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2124
BAYAMON | 2022-05-18 15:55 | 2022-05-18 22:00 | 1825 | 006:05 | S | NO SE REPORTO CAUSA | DISPARO 0050 Y MAIN DIO LOCKOUT SE HIZO PRUEBA DE TTR SE ENERGIZO Y SE QUEDO EN SERVICIO | S22051800233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 365 | 2022-05-18 | 666125 | keep | 0 | May | 2022 | 0.45369 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-05-18 15:55 | 2022-05-18 18:58 | 4398 | 003:03 | S | NO SE REPORTO CAUSA | DISPARO 0050 Y MAIN DIO LOCKOUT TRIP SE TRANSFIRIO CARGA AL 1657-04 CERRANDO N/O 118-07 7 9 CALLE LOIZA 100% EN SERVICIO | S22051800233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-05-18 | 804834 | keep | 0 | May | 2022 | 0.54817 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2022-05-18 15:55 | 2022-05-18 21:07 | 2782 | 005:12 | S | NO SE REPORTO CAUSA | DISPARO 0050 Y MAIN DIO LOCKOUT SE HIZO PRUEBA DE TTR DIO BIEN Y SE ENERGIZO | S22051800233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 312 | 2022-05-18 | 867984 | keep | 0 | May | 2022 | 0.59118 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
CAGUAS | 2022-05-18 16:01 | 2022-05-18 16:10 | 3 | 000:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO DE TRANSFORMADORES PARA REPARAR SECUNDARIA | C22051800196 | New_Event | Secondary Wire Break | Include | Include | Equipment | 9 | 2022-05-18 | 27 | keep | 0 | May | 2022 | 1.839e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-05-18 16:02 | 2022-05-18 19:32 | 40 | 003:30 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22051800028 | New_Event | Primary Wire Break | Include | Include | Equipment | 210 | 2022-05-18 | 8400 | keep | 0 | May | 2022 | 0.0057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-18 16:09 | 2022-05-18 19:30 | 20 | 003:21 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051800069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-05-18 | 4020 | keep | 0 | May | 2022 | 0.002738 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-18 16:09 | 2022-05-18 18:13 | 25 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22051800399 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-05-18 | 3100 | keep | 0 | May | 2022 | 0.0021114 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-05-18 16:11 | 2022-05-18 19:32 | 50 | 003:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A22051800070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2022-05-18 | 10050 | keep | 0 | May | 2022 | 0.006845 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-18 16:26 | 2022-05-18 19:43 | 844 | 003:17 | T | DESGANCHE | DISPARO SE RETIRO GALLINA PALO Y ENREDADERA SE CERRO BKR ABRIENDO N/O LLEVA 20% DEL 1342-01 | S22051800245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-05-18 | 166268 | keep | 0 | May | 2022 | 0.11324 | 0.00057484 | Sustained | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2022-05-18 16:26 | 2022-05-18 21:19 | 79 | 004:53 | P | DESGANCHE | SE RETIRO RAMA SOBRE LINEA Y SE CERRO N/O CONTRA 1330-04 | S22051800245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2022-05-18 | 23147 | keep | 0 | May | 2022 | 0.015765 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
MAYAGÃœEZ | 2022-05-18 16:34 | 2022-05-18 20:09 | 100 | 003:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 200 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051800140 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 215 | 2022-05-18 | 21500 | keep | 0 | May | 2022 | 0.014644 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-18 16:38 | 2022-05-18 16:40 | 2405 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 50% 1710-01 SE CERRO POR SCADA | B22051800405 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-18 | 4810 | keep | 0 | May | 2022 | 0.0032761 | 0.001638 | Momentary | FALSE | FALSE | Not_TMED_Event | 2405
BAYAMON | 2022-05-18 16:38 | 2022-05-18 16:40 | 1812 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 50% 1710-01 SE CERRO POR SCADA | B22051800405 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-18 | 3624 | keep | 0 | May | 2022 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
CANOVANAS | 2022-05-18 16:47 | 2022-05-18 21:46 | 12 | 004:59 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO DE 75 KVA X 75 KVA | R22051800171 | New_Event | Service Transformer Failure | Include | Include | Equipment | 299 | 2022-05-18 | 3588 | keep | 0 | May | 2022 | 0.0024438 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-05-18 16:53 | 2022-05-18 21:59 | 50 | 005:06 | P | DESGANCHE | 1 X 40 EN C/L | R22051800181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2022-05-18 | 15300 | keep | 0 | May | 2022 | 0.010421 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-18 16:55 | 2022-05-18 17:43 | 20 | 000:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIO Y REPARAR CONECTOR | S22051800268 | New_Event | Secondary Wire Break | Include | Include | Equipment | 48 | 2022-05-18 | 960 | keep | 0 | May | 2022 | 0.00065385 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-18 17:01 | 2022-05-18 17:02 | 1709 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO INTERRUPTOR EN SERVICIO | C22051800270 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-05-18 | 1709 | keep | 0 | May | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2022-05-18 17:01 | 2022-05-19 09:16 | 214 | 016:15 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SE VA ABRIR CORTE DE LINEA TOTAL PARA REPARAR | C22051800269 | New_Event | Primary Wire Break | Include | Include | Equipment | 975 | 2022-05-18 | 208650 | keep | 0 | May | 2022 | 0.14211 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
CAGUAS | 2022-05-18 17:02 | 2022-05-19 10:10 | 73 | 017:08 | P | CABLE SOTERRADO AVERIADO | 1 X 140 EN RISER AVERIA NUEVA DEL SU-18A AL SU-19, AVERIA VIEJA DEL SU-18A AL SU-19 QUEDO FUERA EL T-34 Y T-44 | C22051800287 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1028 | 2022-05-18 | 75044 | keep | 0 | May | 2022 | 0.051112 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2022-05-18 17:20 | 2022-05-19 11:28 | 1 | 018:08 | P | DESGANCHE | 1 X 20 EN SU-A 1 X 30 EN RISER SE REALIZO DESGANCHE | R22051800196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1088 | 2022-05-18 | 1088 | keep | 0 | May | 2022 | 0.00074103 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-18 17:30 | 2022-05-18 18:45 | 120 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | A22051800080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-05-18 | 9000 | keep | 0 | May | 2022 | 0.0061299 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-05-18 17:52 | 2022-05-18 17:53 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22051800153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 990 | keep | 0 | May | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
CAGUAS | 2022-05-18 18:04 | 2022-05-18 18:05 | 2486 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22051800293 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 2486 | keep | 0 | May | 2022 | 0.0016932 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
CAGUAS | 2022-05-18 18:25 | 2022-05-19 12:00 | 5 | 017:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C22051800296 | New_Event | Cutout Failure | Include | Include | Equipment | 1055 | 2022-05-18 | 5275 | keep | 0 | May | 2022 | 0.0035928 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-18 18:40 | 2022-05-18 20:47 | 30 | 002:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO 2 TOMAS Y BAJANTE SECUNDARIO | S22051800294 | New_Event | Secondary Wire Break | Include | Include | Equipment | 127 | 2022-05-18 | 3810 | keep | 0 | May | 2022 | 0.002595 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-18 18:43 | 2022-05-18 18:46 | 1483 | 000:03 | P | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 30% SU CARGA POR 1336-8 | S22051800000 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-05-18 | 4449 | keep | 0 | May | 2022 | 0.0030302 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-18 18:43 | 2022-05-18 18:46 | 1500 | 000:03 | P | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1336-8 | S22051800000 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-05-18 | 4500 | keep | 0 | May | 2022 | 0.0030649 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-05-18 18:43 | 2022-05-18 18:46 | 5290 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1336-9 Y 30% DEL 1204-5 Y PARTE DEL 1204-5 | S22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-18 | 15870 | keep | 0 | May | 2022 | 0.010809 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-05-18 18:43 | 2022-05-18 18:46 | 207 | 000:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1336-8 | S22051800000 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-05-18 | 621 | keep | 0 | May | 2022 | 0.00042296 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
BARRANQUITAS | 2022-05-18 18:45 | 2022-05-18 21:40 | 10 | 002:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE 40 PIES DE SECUNDARIA Y REPARAR OTRO TRAMO | C22051800251 | New_Event | Secondary Wire Break | Include | Include | Equipment | 175 | 2022-05-18 | 1750 | keep | 0 | May | 2022 | 0.0011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-18 18:46 | 2022-05-19 00:07 | 350 | 005:21 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO PLANCHA EN MACHETE Y SE CERRO PUENTE DE LINEA A MACHETE | S22051800389 | New_Event | Primary Wire Break | Include | Include | Equipment | 321 | 2022-05-18 | 112350 | keep | 0 | May | 2022 | 0.076521 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2022-05-18 18:58 | 2022-05-19 00:15 | 68 | 005:17 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1102-01 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1102-04, 1102-05 Y 1105-05, 1105-04. SE SECCIONALIZO AVERIA Y SE CERRO AMARRE CONTRA 1106-05 | S22051800426 | New_Event | UG Cable Fault | Include | Include | Equipment | 317 | 2022-05-18 | 21556 | keep | 0 | May | 2022 | 0.014682 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-05-18 18:58 | 2022-05-18 19:00 | 171 | 000:02 | S | CABLE SOTERRADO AVERIADO | DISPARO 1102-01 Y AL PROBARLO DISPARO LINEA 6700 | S22051800000 | New_Event | UG Cable Fault | Include | Include | Equipment | 2 | 2022-05-18 | 342 | keep | 0 | May | 2022 | 0.00023293 | 0.00011647 | Momentary | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-05-18 18:58 | 2022-05-18 19:00 | 1837 | 000:02 | S | CABLE SOTERRADO AVERIADO | DISPARO 1102-01 Y AL PROBARLO DISPARO LINEA 6700 | S22051800000 | New_Event | UG Cable Fault | Include | Include | Equipment | 2 | 2022-05-18 | 3674 | keep | 0 | May | 2022 | 0.0025023 | 0.0012512 | Momentary | FALSE | FALSE | Not_TMED_Event | 1837
BAYAMON | 2022-05-18 18:58 | 2022-05-19 00:15 | 536 | 005:17 | S | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1102-01 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1102-04, 1102-05 Y 1105-05, 1105-04. SE SECCIONALIZO AVERIA Y SE CERRO AMARRE CONTRA 1106-05 | S22051800000 | New_Event | UG Cable Fault | Include | Include | Equipment | 317 | 2022-05-18 | 169912 | keep | 0 | May | 2022 | 0.11573 | 0.00036507 | Sustained | FALSE | FALSE | Not_TMED_Event | 536
BAYAMON | 2022-05-18 18:58 | 2022-05-19 00:15 | 348 | 005:17 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1102-01 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1102-04, 1102-05 Y 1105-05, 1105-04. SE SECCIONALIZO AVERIA Y SE CERRO AMARRE CONTRA 1106-05 | S22051800426 | New_Event | UG Cable Fault | Include | Include | Equipment | 317 | 2022-05-18 | 110316 | keep | 0 | May | 2022 | 0.075136 | 0.00023702 | Sustained | FALSE | FALSE | Not_TMED_Event | 348
BAYAMON | 2022-05-18 18:58 | 2022-05-19 00:59 | 559 | 006:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1102-01 QUE A SU VEZ LLEVA LA CARGA DE EL ALIMENTADOR 1105-04. SE SECCIONALIZO AVERIA Y SE CERRO AMARRE CONTRA 1133-04 ENTRA UN 100% | S22051800426 | New_Event | UG Cable Fault | Include | Include | Equipment | 361 | 2022-05-18 | 201799 | keep | 0 | May | 2022 | 0.13744 | 0.00038073 | Sustained | FALSE | FALSE | Not_TMED_Event | 559
BAYAMON | 2022-05-18 18:58 | 2022-05-19 00:59 | 370 | 006:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1102-01 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1102-04, 1102-05 Y 1105-05, 1105-04. SE SECCIONALIZO AVERIA Y SE CERRO AMARRE CONTRA 1106-05 ENTRA UN 50% | S22051800426 | New_Event | UG Cable Fault | Include | Include | Equipment | 361 | 2022-05-18 | 133570 | keep | 0 | May | 2022 | 0.090974 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
HUMACAO | 2022-05-18 19:13 | 2022-05-19 11:00 | 150 | 015:47 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | C22051800309 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 947 | 2022-05-18 | 142050 | keep | 0 | May | 2022 | 0.09675 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-05-18 19:31 | 2022-05-18 19:32 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22051800162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 1827 | keep | 0 | May | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
VEGA BAJA | 2022-05-18 19:35 | 2022-05-18 22:45 | 40 | 003:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE RETIRO RAMA | B22051800438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-05-18 | 7600 | keep | 0 | May | 2022 | 0.0051763 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-18 19:39 | 2022-05-19 11:12 | 32 | 015:33 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22051800325 | New_Event | Animals | Include | Include | Wildlife | 933 | 2022-05-18 | 29856 | keep | 0 | May | 2022 | 0.020335 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2022-05-18 20:11 | 2022-05-19 06:56 | 187 | 010:45 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65, 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE LEVANTO LINEA PRIMARIA | C22051800346 | New_Event | Primary Wire Break | Include | Include | Equipment | 645 | 2022-05-18 | 120615 | keep | 0 | May | 2022 | 0.08215 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
ARECIBO | 2022-05-18 20:19 | 2022-05-19 10:40 | 20 | 014:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA POR LA MISMA CAPACIDAD | A22051900093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 861 | 2022-05-18 | 17220 | keep | 0 | May | 2022 | 0.011728 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-18 20:49 | 2022-05-18 22:20 | 130 | 001:31 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA CAUSA REPORTADA POR FOREMAN SOBRE CARGA POR ALTAS TEMPERATURAS (2220) | A22051800096 | New_Event | Trip Due To Overload | Include | Include | Other | 91 | 2022-05-18 | 11830 | keep | 0 | May | 2022 | 0.0080574 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2022-05-18 20:54 | 2022-05-19 20:11 | 195 | 023:17 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE EN MAL ESTADO, SE LEVANTO CONDUCTOR, SE RELOCALIZO XMR Y SE CERR0 PUENTES PRIMARIOS | B22051800452 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1397 | 2022-05-18 | 272415 | keep | 0 | May | 2022 | 0.18554 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
ARECIBO | 2022-05-18 20:58 | 2022-05-18 23:17 | 12 | 002:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A22051800100 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2022-05-18 | 1668 | keep | 0 | May | 2022 | 0.0011361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-18 21:04 | 2022-05-19 03:25 | 300 | 006:21 | P | SOBRECARGA | 1 X 200 EN CORTE DE LINEA CAUSA REPORTADA POR JOURNEY LINEMAN SOBRE CARGA POR ALTAS TEMPERATURAS | M22051800174 | New_Event | Trip Due To Overload | Include | Include | Other | 381 | 2022-05-18 | 114300 | keep | 0 | May | 2022 | 0.077849 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-05-18 21:05 | 2022-05-18 22:10 | 131 | 001:05 | P | DESGANCHE | 1 X 100 EN C/L | R22051800244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2022-05-18 | 8515 | keep | 0 | May | 2022 | 0.0057995 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
SAN JUAN | 2022-05-18 21:17 | 2022-05-18 21:38 | 858 | 000:21 | P | CONDUCTOR ROTO O ABIERTO | DISPARO NO RECERRO 20% POR 1303-02 | S22051800711 | New_Event | Primary Wire Break | Include | Include | Equipment | 21 | 2022-05-18 | 18018 | keep | 0 | May | 2022 | 0.012272 | 0.00058438 | Sustained | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-18 21:17 | 2022-05-18 21:38 | 2435 | 000:21 | T | CONDUCTOR ROTO O ABIERTO | DISPARO NO RECERRO LLEVA 20% DEL 1204-2 Y PARTE POR 1206-4 SE PROBO QUEDO EN SERVICIO | S22051800711 | New_Event | Primary Wire Break | Include | Include | Equipment | 21 | 2022-05-18 | 51135 | keep | 0 | May | 2022 | 0.034828 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-05-18 21:26 | 2022-05-19 07:54 | 50 | 010:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA. NO FUNDIO FUSIBLE | B22051800480 | New_Event | Cutout Failure | Include | Include | Equipment | 628 | 2022-05-18 | 31400 | keep | 0 | May | 2022 | 0.021386 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-18 21:38 | 2022-05-19 11:11 | 286 | 013:33 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO TRONCAL ALIMENTADOR | S22051900371 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 813 | 2022-05-18 | 232518 | keep | 0 | May | 2022 | 0.15837 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-18 21:38 | 2022-05-19 11:11 | 811 | 013:33 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO TRONCAL ALIMENTADOR | S22051900371 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 813 | 2022-05-18 | 659343 | keep | 0 | May | 2022 | 0.44908 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-18 21:38 | 2022-05-19 10:38 | 10 | 013:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CABLE SECUNDARIO | B22051800483 | New_Event | Secondary Wire Break | Include | Include | Equipment | 780 | 2022-05-18 | 7800 | keep | 0 | May | 2022 | 0.0053125 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-18 21:58 | 2022-05-18 23:36 | 70 | 001:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A22051800124 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2022-05-18 | 6860 | keep | 0 | May | 2022 | 0.0046723 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-05-18 22:07 | 2022-05-19 06:19 | 390 | 008:12 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 100 EN CORTES DE LINEA | B22051800491 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 492 | 2022-05-18 | 191880 | keep | 0 | May | 2022 | 0.13069 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2022-05-18 22:08 | 2022-05-18 22:13 | 171 | 000:05 | T | CABLE SOTERRADO AVERIADO | DISPARO 1102-01 Y AL PROBARLO DISPARO LINEA 6700 | S22051800000 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 5 | 2022-05-18 | 855 | keep | 0 | May | 2022 | 0.00058234 | 0.00011647 | Momentary | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-05-18 22:08 | 2022-05-18 22:13 | 1837 | 000:05 | S | CABLE SOTERRADO AVERIADO | SE REALIZO PRUEBA AL INTERRUPTOR 1102-01 Y SE LLEVA INTERRUPTOR DE ALTA LINEA 6700 | S22051800000 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 5 | 2022-05-18 | 9185 | keep | 0 | May | 2022 | 0.0062559 | 0.0012512 | Momentary | FALSE | FALSE | Not_TMED_Event | 1837
ARECIBO | 2022-05-18 22:30 | 2022-05-18 23:56 | 40 | 001:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22051800131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2022-05-18 | 3440 | keep | 0 | May | 2022 | 0.002343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-18 22:45 | 2022-05-18 23:18 | 70 | 000:33 | P | SOBRECARGA | 1 X 50 EN CORTE DE LINEA CAUSA REPORTADA POR JORNEY LINEAMAN SOBRE CARGA POR ALTAS TEMPERATURAS | A22051800133 | New_Event | Trip Due To Overload | Include | Include | Other | 33 | 2022-05-18 | 2310 | keep | 0 | May | 2022 | 0.0015733 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-05-18 22:52 | 2022-05-18 22:53 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-18 | 341 | keep | 0 | May | 2022 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
CAGUAS | 2022-05-18 23:15 | 2022-05-19 11:56 | 45 | 012:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE DE BAMBUA | C22051800395 | New_Event | Vegetation Contact | Include | Include | Vegetation | 761 | 2022-05-18 | 34245 | keep | 0 | May | 2022 | 0.023324 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-05-19 | 2022-05-19 19:40 | 1 | 019:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA @4KV/7KV POR UNO DE LA MISMA CAPACIDAD | A22051900077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1180 | 2022-05-19 | 1180 | keep | 0 | May | 2022 | 0.00080369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-05-19 00:05 | 2022-05-19 10:15 | 454 | 010:10 | P | LINEA DE TRANSMISION 38KV | SE LE REALIZO PRUEBA AL 2603-08G QUE ESTA FUERA DESDE EL CRUCE DEL OVERD HEAD CON EL 2603-08 | C22051900028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 610 | 2022-05-19 | 276940 | keep | 0 | May | 2022 | 0.18862 | 0.00030922 | Sustained | FALSE | FALSE | Not_TMED_Event | 454
BAYAMON | 2022-05-19 00:59 | 2022-05-19 21:01 | 280 | 020:02 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL 1102-01 | S22051800426 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1202 | 2022-05-19 | 336560 | keep | 0 | May | 2022 | 0.22923 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-19 02:45 | 2022-05-19 05:00 | 530 | 002:15 | T | CAUSAS EXTERNAS | DISPARO DE INTERRUPTOR POR POSTE IMPACTADO POR AUTO EN FINAL DE LINEA Y AMARRE CONTRA 1418-02 | S22051900077 | New_Event | Damage From Public | Include | Include | Public | 135 | 2022-05-19 | 71550 | keep | 0 | May | 2022 | 0.048732 | 0.00036098 | Sustained | FALSE | FALSE | Not_TMED_Event | 530
CANOVANAS | 2022-05-19 04:08 | 2022-05-19 04:09 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22051900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 1894 | keep | 0 | May | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CAGUAS | 2022-05-19 04:12 | 2022-05-19 12:13 | 383 | 008:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22051900013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 481 | 2022-05-19 | 184223 | keep | 0 | May | 2022 | 0.12547 | 0.00026086 | Sustained | FALSE | FALSE | Not_TMED_Event | 383
SAN JUAN | 2022-05-19 04:20 | 2022-05-19 05:30 | 671 | 001:10 | P | CAUSAS EXTERNAS | SE SECCIONALZO AVERIA POSTE IMPACTADO POR AUTO. SE ABRIO PUENTE Y QUEDAN DOS CLIENTES FUERA SJ-220519-01 | S22051900077 | New_Event | Damage From Public | Include | Include | Public | 70 | 2022-05-19 | 46970 | keep | 0 | May | 2022 | 0.031991 | 0.00045702 | Sustained | FALSE | FALSE | Not_TMED_Event | 671
AGUADILLA | 2022-05-19 05:12 | 2022-05-19 10:50 | 28 | 005:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | M22051900009 | New_Event | Primary Wire Break | Include | Include | Equipment | 338 | 2022-05-19 | 9464 | keep | 0 | May | 2022 | 0.0064459 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2022-05-19 05:16 | 2022-05-19 16:53 | 14 | 011:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 75 KVA AVERIADO | B22051900024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 697 | 2022-05-19 | 9758 | keep | 0 | May | 2022 | 0.0066461 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-05-19 05:30 | 2022-05-19 19:54 | 2 | 014:24 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE, SE CERRARON PUENTES Y SE CERRO CAJAS DE TRANSFORMADOR. ACCIDENTE VEHICULAR SJ-220519-01 | S22051900077 | Partial_restoration | Damage From Public | Include | Include | Public | 864 | 2022-05-19 | 1728 | keep | 0 | May | 2022 | 0.0011769 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-19 05:50 | 2022-05-19 05:51 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22051900025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 2725 | keep | 0 | May | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-05-19 05:50 | 2022-05-19 05:51 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22051900025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 1834 | keep | 0 | May | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-05-19 05:50 | 2022-05-19 05:51 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22051900025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 1437 | keep | 0 | May | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-05-19 05:50 | 2022-05-19 05:51 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22051900027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 2565 | keep | 0 | May | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-05-19 05:50 | 2022-05-19 05:51 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C22051900027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 3565 | keep | 0 | May | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-05-19 05:50 | 2022-05-19 05:51 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22051900028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 2751 | keep | 0 | May | 2022 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-05-19 05:50 | 2022-05-19 05:51 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22051900028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 576 | keep | 0 | May | 2022 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-05-19 05:50 | 2022-05-19 05:51 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22051900028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 2584 | keep | 0 | May | 2022 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-05-19 05:50 | 2022-05-19 05:51 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22051900028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 1606 | keep | 0 | May | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-05-19 05:50 | 2022-05-19 05:51 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22051900028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 29 | keep | 0 | May | 2022 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2022-05-19 05:50 | 2022-05-19 05:51 | 4035 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22051900028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 4035 | keep | 0 | May | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-05-19 05:50 | 2022-05-19 05:51 | 3718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P22051900028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-19 | 3718 | keep | 0 | May | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
VEGA BAJA | 2022-05-19 06:25 | 2022-05-19 07:10 | 4702 | 000:45 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR PARA REMPLAZO DE AISLADOR Y SE CERRO POR SCADA. 11% EN SERVICIO | B22051900026 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 45 | 2022-05-19 | 211590 | keep | 0 | May | 2022 | 0.14411 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
BAYAMON | 2022-05-19 06:37 | 2022-05-19 08:52 | 10 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22051900028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2022-05-19 | 1350 | keep | 0 | May | 2022 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-19 06:38 | 2022-05-19 06:39 | 1307 | 000:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22051900034 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-19 | 1307 | keep | 0 | May | 2022 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2022-05-19 06:39 | 2022-05-19 14:38 | 125 | 007:59 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22051900129 | 1st_after_momentary | Animals | Include | Include | Wildlife | 479 | 2022-05-19 | 59875 | keep | 0 | May | 2022 | 0.040781 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-05-19 06:48 | 2022-05-19 09:10 | 80 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 10O EN C/L | S22051900172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-05-19 | 11360 | keep | 0 | May | 2022 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-05-19 06:55 | 2022-05-19 06:56 | 4085 | 000:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR LLEVA EL 2404-06 | R22051900000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-19 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-05-19 06:55 | 2022-05-19 06:56 | 7621 | 000:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR CARGA POR EL 2402-03 | R22051900000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-19 | 7621 | keep | 0 | May | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2022-05-19 06:56 | 2022-05-19 09:40 | 100 | 002:44 | P | ANIMAL | 1 X 100 EN C/L AVE | R22051900006 | 1st_after_momentary | Animals | Include | Include | Wildlife | 164 | 2022-05-19 | 16400 | keep | 0 | May | 2022 | 0.01117 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-05-19 07:10 | 2022-05-19 10:18 | 4185 | 003:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZARON 4 AISLADORES, SE FIJO LINEA PRIMARIA Y SE CERRO MACHETES | B22051900033 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 188 | 2022-05-19 | 786780 | keep | 0 | May | 2022 | 0.53587 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-19 07:11 | 2022-05-19 12:34 | 1 | 005:23 | P | ANIMAL | 3 X 65 EN RISER ESCUELA SE RETIRO RANA CRUZANDO SUBESTACION DE LA ESCUELA | B22051900032 | New_Event | Animals | Include | Include | Wildlife | 323 | 2022-05-19 | 323 | keep | 0 | May | 2022 | 0.00021999 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-19 07:28 | 2022-05-19 11:21 | 20 | 003:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22051900035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2022-05-19 | 4660 | keep | 0 | May | 2022 | 0.0031739 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-19 07:31 | 2022-05-19 12:35 | 181 | 005:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S22051900201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 304 | 2022-05-19 | 55024 | keep | 0 | May | 2022 | 0.037477 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
MAYAGÃœEZ | 2022-05-19 07:40 | 2022-05-19 16:33 | 9 | 008:53 | P | SECUNDARIA/DESGANCHE | SE REPARO LINEA SECUNDARIA ROTA A CAUSA DE DESGANCHE SE RETIRO RAMAS SOBRE LAS LINEAS | M22051900021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 533 | 2022-05-19 | 4797 | keep | 0 | May | 2022 | 0.0032672 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2022-05-19 07:44 | 2022-05-19 11:15 | 390 | 003:31 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B22051900038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-05-19 | 82290 | keep | 0 | May | 2022 | 0.056047 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
MAYAGÃœEZ | 2022-05-19 07:58 | 2022-05-20 15:30 | 20 | 031:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | M22051900024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1892 | 2022-05-19 | 37840 | keep | 0 | May | 2022 | 0.025773 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-19 07:59 | 2022-05-19 08:00 | 1702 | 000:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22051900058 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-19 | 1702 | keep | 0 | May | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-05-19 08:00 | 2022-05-19 12:00 | 140 | 004:00 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUE POR AVE | C22051900056 | 1st_after_momentary | Animals | Include | Include | Wildlife | 240 | 2022-05-19 | 33600 | keep | 0 | May | 2022 | 0.022885 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CAGUAS | 2022-05-19 08:10 | 2022-05-19 08:11 | 2092 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 2092 | keep | 0 | May | 2022 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2022-05-19 08:11 | 2022-05-19 15:09 | 10 | 006:58 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C22051900089 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 418 | 2022-05-19 | 4180 | keep | 0 | May | 2022 | 0.002847 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-19 08:36 | 2022-05-19 08:37 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22051900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 2697 | keep | 0 | May | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
HUMACAO | 2022-05-19 08:47 | 2022-05-19 17:27 | 12 | 008:40 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C22051900076 | New_Event | Animals | Include | Include | Wildlife | 520 | 2022-05-19 | 6240 | keep | 0 | May | 2022 | 0.00425 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-05-19 08:57 | 2022-05-19 08:58 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051900053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
BAYAMON | 2022-05-19 08:58 | 2022-05-20 10:01 | 419 | 025:03 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN CONVETIDOR PARA ABRIR PUENTE EN RAMAL CARR 836 PARA DESGANCHE Y LEVANTAR CONDUCTOR | B22051900456 | New_Event | Primary Wire Break | Include | Include | Equipment | 1503 | 2022-05-19 | 629757 | keep | 0 | May | 2022 | 0.42892 | 0.00028538 | Sustained | FALSE | FALSE | Not_TMED_Event | 419
CAGUAS | 2022-05-19 09:16 | 2022-05-19 10:02 | 760 | 000:46 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA TOTAL PARA CERRAR DOS PUENTES DE LINEA A LINEA | C22051800269 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 46 | 2022-05-19 | 34960 | keep | 0 | May | 2022 | 0.023811 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-19 09:18 | 2022-05-19 09:19 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 863 | keep | 0 | May | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
BAYAMON | 2022-05-19 09:19 | 2022-05-19 10:27 | 30 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22051900059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-05-19 | 2040 | keep | 0 | May | 2022 | 0.0013894 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-19 09:25 | 2022-05-19 09:54 | 4 | 000:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA AJUSTAR CONEXIONES SECUNDARIAS Y SE REMPLAZO CONECTOR | B22051800427 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2022-05-19 | 116 | keep | 0 | May | 2022 | 7.9007e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-19 09:26 | 2022-05-19 14:05 | 1 | 004:39 | P | NO SE REPORTO CAUSA | 2 X 15 EN RISER | B22051900070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2022-05-19 | 279 | keep | 0 | May | 2022 | 0.00019003 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-19 09:31 | 2022-05-19 13:50 | 1 | 004:19 | P | NO SE REPORTO CAUSA | 2 X 15 EN MONTURA TRIFASICA NO SE ENCONTRO CAUSA | P22051900062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2022-05-19 | 259 | keep | 0 | May | 2022 | 0.0001764 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-19 09:32 | 2022-05-19 13:14 | 10 | 003:42 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | C22051900101 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2022-05-19 | 2220 | keep | 0 | May | 2022 | 0.001512 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-05-19 09:45 | 2022-05-19 14:40 | 233 | 004:55 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO Y SE REEMPLAZO CAJA PRIMARIA | C22051900111 | New_Event | Primary Wire Break | Include | Include | Equipment | 295 | 2022-05-19 | 68735 | keep | 0 | May | 2022 | 0.046815 | 0.0001587 | Sustained | FALSE | FALSE | Not_TMED_Event | 233
MAYAGÃœEZ | 2022-05-19 09:50 | 2022-05-19 12:26 | 10 | 002:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | M22051900051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 156 | 2022-05-19 | 1560 | keep | 0 | May | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-19 09:51 | 2022-05-20 10:04 | 1 | 024:13 | P | DESGANCHE | SE DESGANCHO Y 1 X 80 EN C/L | S22051900292 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1453 | 2022-05-19 | 1453 | keep | 0 | May | 2022 | 0.00098963 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-19 09:54 | 2022-05-19 16:09 | 4 | 006:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO EN TRANSPATIO HACIA CAJA PRIMARIA | S22051900296 | New_Event | Primary Wire Break | Include | Include | Equipment | 375 | 2022-05-19 | 1500 | keep | 0 | May | 2022 | 0.0010216 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-05-19 09:55 | 2022-05-19 12:10 | 1 | 002:15 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A22051900030 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 135 | 2022-05-19 | 135 | keep | 0 | May | 2022 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-19 10:10 | 2022-05-19 10:11 | 1709 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO INTERRUPTOR EN SERVICIO PERSONAL REALIZANDO PRUEBA A RISER | C22051900124 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-05-19 | 1709 | keep | 0 | May | 2022 | 0.001164 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-19 10:11 | 2022-05-20 20:13 | 75 | 034:02 | P | CABLE SOTERRADO AVERIADO | SE TIRO PROVICIONAL T45 AL T44 ENERGIZARON DEL T44 SE ENERGIZO AL SU18A, DEL SU18A SE ENERGIZO EL T34. | C22051900287 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 2042 | 2022-05-19 | 153150 | keep | 0 | May | 2022 | 0.10431 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-05-19 10:15 | 2022-05-19 13:25 | 151 | 003:10 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO EN N/O DEL 2603-10 CON 2603-08 | C22051900028 | New_Event | Switch Failure | Include | Include | Equipment | 190 | 2022-05-19 | 28690 | keep | 0 | May | 2022 | 0.019541 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
SAN JUAN | 2022-05-19 10:16 | 2022-05-19 13:41 | 21 | 003:25 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S22051900318 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2022-05-19 | 4305 | keep | 0 | May | 2022 | 0.0029321 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-05-19 10:27 | 2022-05-19 10:28 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22051900067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 3438 | keep | 0 | May | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2022-05-19 10:28 | 2022-05-19 11:22 | 30 | 000:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22051900059 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 54 | 2022-05-19 | 1620 | keep | 0 | May | 2022 | 0.0011034 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-19 10:36 | 2022-05-19 13:00 | 143 | 002:24 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | S22051900328 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-05-19 | 20592 | keep | 0 | May | 2022 | 0.014025 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
BAYAMON | 2022-05-19 10:42 | 2022-05-19 16:26 | 29 | 005:44 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22051900077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2022-05-19 | 9976 | keep | 0 | May | 2022 | 0.0067946 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
UTUADO | 2022-05-19 10:52 | 2022-05-19 18:00 | 30 | 007:08 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA @ 4KV POR UNO DE LA MISMA CAPACIDAD | A22051900022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 428 | 2022-05-19 | 12840 | keep | 0 | May | 2022 | 0.0087453 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-19 10:55 | 2022-05-19 10:56 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 390 | keep | 0 | May | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
PONCE | 2022-05-19 11:00 | 2022-05-19 14:36 | 15 | 003:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CONVERTIDOR 13KV A 4KV | P22051900089 | New_Event | Cutout Failure | Include | Include | Equipment | 216 | 2022-05-19 | 3240 | keep | 0 | May | 2022 | 0.0022067 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-19 11:11 | 2022-05-19 12:12 | 858 | 001:01 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO EN TRONCAL 20% POR 1303-2 | S22051900371 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 61 | 2022-05-19 | 52338 | keep | 0 | May | 2022 | 0.035647 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-19 11:11 | 2022-05-19 12:12 | 2435 | 001:01 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO EN LINEA TRONCAL | S22051900371 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 61 | 2022-05-19 | 148535 | keep | 0 | May | 2022 | 0.10117 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-05-19 11:21 | 2022-05-19 14:13 | 19 | 002:52 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50KVA X 50KVA | R22051900027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 172 | 2022-05-19 | 3268 | keep | 0 | May | 2022 | 0.0022258 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-05-19 11:22 | 2022-05-19 11:34 | 3438 | 000:12 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR POR CONTROL. PERSONAL DE LUMA ATENDIENDO UN EVENTO AL REPONER EN C/L CERRARON MAL LA CAJA PRIMARIA Y SE LES PRENDIO EN FUEGO. SE REMPLAZO CAJA | B22051900081 | New_Event | Human Error | Include | Include | Other | 12 | 2022-05-19 | 41256 | keep | 0 | May | 2022 | 0.028099 | 0.0023416 | Sustained | FALSE | FALSE | Not_TMED_Event | 3438
UTUADO | 2022-05-19 11:52 | 2022-05-19 12:45 | 60 | 000:53 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2022-05-19 | 3180 | keep | 0 | May | 2022 | 0.0021659 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-19 11:57 | 2022-05-19 20:56 | 200 | 008:59 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA CON CG-220519-01 HACIENDO REFERENCIA A LA VIA LIBRE D2022-00831 QUE SE VA A TRABAJAR EN OTRO MOMENTO | C22051900182 | New_Event | Primary Pole Failure | Include | Include | Equipment | 539 | 2022-05-19 | 107800 | keep | 0 | May | 2022 | 0.073422 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-05-19 11:59 | 2022-05-19 16:08 | 244 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22051900161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2022-05-19 | 60756 | keep | 0 | May | 2022 | 0.041381 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
BAYAMON | 2022-05-19 12:00 | 2022-05-19 12:35 | 27 | 000:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR SECUNDARIA Y TOMA | S22051900243 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-05-19 | 945 | keep | 0 | May | 2022 | 0.00064364 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
HUMACAO | 2022-05-19 12:04 | 2022-05-20 07:05 | 45 | 019:01 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C22051900162 | New_Event | Animals | Include | Include | Wildlife | 1141 | 2022-05-19 | 51345 | keep | 0 | May | 2022 | 0.034971 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-05-19 12:07 | 2022-05-19 12:45 | 5 | 000:38 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A22051900010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 38 | 2022-05-19 | 190 | keep | 0 | May | 2022 | 0.00012941 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-19 12:47 | 2022-05-19 17:28 | 45 | 004:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22051900086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2022-05-19 | 12645 | keep | 0 | May | 2022 | 0.0086125 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-05-19 12:50 | 2022-05-19 15:58 | 8 | 003:08 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22051900178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-05-19 | 1504 | keep | 0 | May | 2022 | 0.0010244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-05-19 12:52 | 2022-05-19 12:53 | 2735 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 2735 | keep | 0 | May | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
FAJARDO | 2022-05-19 12:59 | 2022-05-19 15:13 | 40 | 002:14 | P | DESGANCHE | 1 X 40 EN C/L | R22051900030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-05-19 | 5360 | keep | 0 | May | 2022 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-05-19 13:05 | 2022-05-19 18:00 | 19 | 004:55 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C22051900181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 295 | 2022-05-19 | 5605 | keep | 0 | May | 2022 | 0.0038175 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2022-05-19 13:14 | 2022-05-19 13:24 | 1 | 000:10 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22051900031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-05-19 | 10 | keep | 0 | May | 2022 | 6.811e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-19 13:39 | 2022-05-19 16:40 | 5 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22051900057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-05-19 | 905 | keep | 0 | May | 2022 | 0.00061639 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-05-19 13:55 | 2022-05-19 16:33 | 7 | 002:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22051900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-05-19 | 1106 | keep | 0 | May | 2022 | 0.00075329 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-05-19 14:00 | 2022-05-19 15:40 | 6 | 001:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22051900041 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 100 | 2022-05-19 | 600 | keep | 0 | May | 2022 | 0.00040866 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-19 14:10 | 2022-05-20 00:12 | 200 | 010:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051900103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 602 | 2022-05-19 | 120400 | keep | 0 | May | 2022 | 0.082004 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-19 14:23 | 2022-05-19 14:25 | 23 | 000:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | S22051900000 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-05-19 | 46 | keep | 0 | May | 2022 | 3.133e-05 | 1.5665e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2022-05-19 14:40 | 2022-05-19 14:42 | 23 | 000:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | S22051900000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2022-05-19 | 46 | keep | 0 | May | 2022 | 3.133e-05 | 1.5665e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2022-05-19 14:42 | 2022-05-19 15:50 | 5 | 001:08 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR DEL SUELO | S22051900000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 68 | 2022-05-19 | 340 | keep | 0 | May | 2022 | 0.00023157 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-19 14:44 | 2022-05-19 15:20 | 20 | 000:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO LINEA SECUNDARIA DEL SUELO | S22051900435 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2022-05-19 | 720 | keep | 0 | May | 2022 | 0.00049039 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-19 14:44 | 2022-05-19 18:27 | 250 | 003:43 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 65 EN CORTE DE LINEA. SE ABRIO PUENTES PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO. | A22051900046 | New_Event | Primary Pole Failure | Include | Include | Equipment | 223 | 2022-05-19 | 55750 | keep | 0 | May | 2022 | 0.037971 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2022-05-19 14:52 | 2022-05-20 15:53 | 50 | 025:01 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHO Y REMPLAZO PIN POLE TOP | C22051900203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1501 | 2022-05-19 | 75050 | keep | 0 | May | 2022 | 0.051116 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-05-19 14:55 | 2022-05-19 14:56 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22051900094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 527 | keep | 0 | May | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CAGUAS | 2022-05-19 15:05 | 2022-05-19 16:13 | 5 | 001:08 | P | ANIMAL | 1 X 25 EN TRANSFORMADOR CRUCE POR AVE | C22051900206 | New_Event | Animals | Include | Include | Wildlife | 68 | 2022-05-19 | 340 | keep | 0 | May | 2022 | 0.00023157 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-05-19 15:05 | 2022-05-19 15:33 | 14 | 000:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22051900050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2022-05-19 | 392 | keep | 0 | May | 2022 | 0.00026699 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-05-19 15:06 | 2022-05-19 15:09 | 1483 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL CARGA POR EL 1336-08 | S22051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-19 | 4449 | keep | 0 | May | 2022 | 0.0030302 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-19 15:06 | 2022-05-19 15:09 | 1500 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL CARGA POR EL 1336-08 | S22051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-19 | 4500 | keep | 0 | May | 2022 | 0.0030649 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-05-19 15:06 | 2022-05-19 15:09 | 5290 | 000:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 SE CERRO POR CONTROL LLEVA 1336-09 | S22051900000 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-05-19 | 15870 | keep | 0 | May | 2022 | 0.010809 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-05-19 15:06 | 2022-05-19 15:09 | 207 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 SE CERRO POR CONTROL LLEVA 1336-09 | S22051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-19 | 621 | keep | 0 | May | 2022 | 0.00042296 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-05-19 15:07 | 2022-05-19 20:53 | 40 | 005:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | S22051900640 | New_Event | Cutout Failure | Include | Include | Equipment | 346 | 2022-05-19 | 13840 | keep | 0 | May | 2022 | 0.0094264 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-05-19 15:25 | 2022-05-19 15:32 | 60 | 000:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA VIENTOS FUERTES | B22051900104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 7 | 2022-05-19 | 420 | keep | 0 | May | 2022 | 0.00028606 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-05-19 15:46 | 2022-05-19 17:13 | 10 | 001:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONEXIONES SECUNDARIAS | B22051900098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2022-05-19 | 870 | keep | 0 | May | 2022 | 0.00059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-19 15:50 | 2022-05-19 16:13 | 23 | 000:23 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO DESPUES DEL RISER DE SALIDA | S22051900000 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 23 | 2022-05-19 | 529 | keep | 0 | May | 2022 | 0.0003603 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-19 16:13 | 2022-05-19 18:22 | 5 | 002:09 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR DEL SUELO | S22051900000 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 129 | 2022-05-19 | 645 | keep | 0 | May | 2022 | 0.00043931 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-19 16:19 | 2022-05-19 17:37 | 22 | 001:18 | P | ANIMAL | 1 X 65 EN C/L SE RETIRO AVE | B22051900108 | New_Event | Animals | Include | Include | Wildlife | 78 | 2022-05-19 | 1716 | keep | 0 | May | 2022 | 0.0011688 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
FAJARDO | 2022-05-19 16:27 | 2022-05-19 17:30 | 4 | 001:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | R22051900037 | New_Event | Cutout Failure | Include | Include | Equipment | 63 | 2022-05-19 | 252 | keep | 0 | May | 2022 | 0.00017164 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-05-19 16:34 | 2022-05-19 17:21 | 4634 | 000:47 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR PUENTE ABIERTO LLEVA 60%DEL 2603-08 CERRADO POR CONTROL | C22051900220 | New_Event | Primary Wire Break | Include | Include | Equipment | 47 | 2022-05-19 | 217798 | keep | 0 | May | 2022 | 0.14834 | 0.0031562 | Sustained | FALSE | FALSE | Not_TMED_Event | 4634
HUMACAO | 2022-05-19 16:41 | 2022-05-19 17:46 | 551 | 001:05 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR PUENTE ABIERTO DE MACHETE A LINEA SE SECCIONALIZO | C22051900219 | New_Event | Primary Wire Break | Include | Include | Equipment | 65 | 2022-05-19 | 35815 | keep | 0 | May | 2022 | 0.024393 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
SAN JUAN | 2022-05-19 16:48 | 2022-05-19 18:51 | 10 | 002:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO SULFATADO | S22051900466 | New_Event | Secondary Wire Break | Include | Include | Equipment | 123 | 2022-05-19 | 1230 | keep | 0 | May | 2022 | 0.00083775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-05-19 16:54 | 2022-05-19 19:09 | 390 | 002:15 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | B22051900122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-05-19 | 52650 | keep | 0 | May | 2022 | 0.03586 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
UTUADO | 2022-05-19 16:56 | 2022-05-20 14:31 | 4 | 021:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22051900064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1295 | 2022-05-19 | 5180 | keep | 0 | May | 2022 | 0.0035281 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-05-19 17:08 | 2022-05-19 18:50 | 25 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S22051900471 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2022-05-19 | 2550 | keep | 0 | May | 2022 | 0.0017368 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-05-19 17:15 | 2022-05-19 20:00 | 25 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22051900069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-05-19 | 4125 | keep | 0 | May | 2022 | 0.0028095 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-05-19 17:21 | 2022-05-19 18:21 | 7 | 001:00 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN XMR REMPLAZO PARARRAYO | R22051900043 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 60 | 2022-05-19 | 420 | keep | 0 | May | 2022 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-05-19 17:21 | 2022-05-19 20:15 | 1544 | 002:54 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE MACHETE A LINEA | C22051900303 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 174 | 2022-05-19 | 268656 | keep | 0 | May | 2022 | 0.18298 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-19 17:21 | 2022-05-19 18:53 | 20 | 001:32 | P | SECUNDARIA/OTROS | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR PEDESTAL Y BARRA SECUNDARIA | A22051900067 | New_Event |  |  |  |  | 92 | 2022-05-19 | 1840 | keep | 0 | May | 2022 | 0.0012532 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-19 17:25 | 2022-05-19 20:45 | 150 | 003:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | M22051900138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2022-05-19 | 30000 | keep | 0 | May | 2022 | 0.020433 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-05-19 17:26 | 2022-05-19 19:00 | 77 | 001:34 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | R22051900044 | New_Event | Animals | Include | Include | Wildlife | 94 | 2022-05-19 | 7238 | keep | 0 | May | 2022 | 0.0049298 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
MAYAGÃœEZ | 2022-05-19 17:35 | 2022-05-19 17:36 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6014-02 | M22051900142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 1444 | keep | 0 | May | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-05-19 17:35 | 2022-05-19 17:36 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22051900142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 3630 | keep | 0 | May | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-05-19 17:36 | 2022-05-20 05:31 | 35 | 011:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | M22051900078 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 715 | 2022-05-19 | 25025 | keep | 0 | May | 2022 | 0.017044 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-05-19 17:37 | 2022-05-19 17:38 | 2092 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22051900288 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 2092 | keep | 0 | May | 2022 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
HUMACAO | 2022-05-19 17:46 | 2022-05-19 19:27 | 454 | 001:41 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE MACHETE A LINEA SE CERRO MACHETES | C22051900219 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 101 | 2022-05-19 | 45854 | keep | 0 | May | 2022 | 0.031231 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-19 17:52 | 2022-05-19 20:45 | 150 | 002:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22051900147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 173 | 2022-05-19 | 25950 | keep | 0 | May | 2022 | 0.017674 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-19 17:53 | 2022-05-19 17:56 | 68 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1705-05 LLEVANDO 1705-04 Y 10% 1705-02. 85% DE SU CARGA POR 1705-02. SE CERRO POR SCADA | B22051900131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-19 | 204 | keep | 0 | May | 2022 | 0.00013894 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2022-05-19 17:53 | 2022-05-19 17:56 | 67 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1705-05 LLEVANDO 1705-04 Y 10% 1705-02. 85% DE SU CARGA POR 1705-02. SE CERRO POR SCADA | B22051900131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-19 | 201 | keep | 0 | May | 2022 | 0.0001369 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-05-19 17:53 | 2022-05-19 17:56 | 95 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1705-05 LLEVANDO 1705-04 Y 10% 1705-02. 85% DE SU CARGA POR 1705-02. SE CERRO POR SCADA | B22051900131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-19 | 285 | keep | 0 | May | 2022 | 0.00019411 | 6.4704e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 95
BAYAMON | 2022-05-19 17:53 | 2022-05-19 17:54 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 4431 | keep | 0 | May | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
HUMACAO | 2022-05-19 18:34 | 2022-05-19 18:35 | 776 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22051900349 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-19 | 776 | keep | 0 | May | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
PONCE | 2022-05-19 18:37 | 2022-05-19 22:43 | 53 | 004:06 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN RISER SE DEJA DEL T-67 AL T-68 DESCONECTADO AVERIA HACIA T-68 | P22051900112 | New_Event | UG Cable Fault | Include | Include | Equipment | 246 | 2022-05-19 | 13038 | keep | 0 | May | 2022 | 0.0088801 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BAYAMON | 2022-05-19 19:01 | 2022-05-19 21:39 | 5 | 002:38 | P | ANIMAL | SE REPARO BAJANTE PRIMARIO LINEA A CAJA 1 X 15 BANCO XMR Y 1 X 140 EN C/L SE RETIRO NIDO Y AVE CRUZANDO LINEAS | B22051900136 | New_Event | Animals | Include | Include | Wildlife | 158 | 2022-05-19 | 790 | keep | 0 | May | 2022 | 0.00053807 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-19 19:18 | 2022-05-19 19:27 | 24 | 000:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L REMPLAZO PORTAFUSIBLE PARTIDO | R22051900049 | New_Event | Cutout Failure | Include | Include | Equipment | 9 | 2022-05-19 | 216 | keep | 0 | May | 2022 | 0.00014712 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CANOVANAS | 2022-05-19 19:20 | 2022-05-19 20:18 | 60 | 000:58 | P | DESGANCHE | 1 X 80 EN C/L | R22051900051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-05-19 | 3480 | keep | 0 | May | 2022 | 0.0023702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-19 19:34 | 2022-05-20 10:00 | 12 | 014:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA LIMPIAR BARRAS SECUNDARIAS | A22051900079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 866 | 2022-05-19 | 10392 | keep | 0 | May | 2022 | 0.0070779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-05-19 20:12 | 2022-05-20 11:47 | 80 | 015:35 | P | DESGANCHE | DESGANCHE SE REPUSO 1 X 100 Y 1 X 65 EN C/L | B22051900142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 935 | 2022-05-19 | 74800 | keep | 0 | May | 2022 | 0.050946 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-05-19 20:12 | 2022-05-19 21:48 | 100 | 001:36 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B22051900142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-05-19 | 9600 | keep | 0 | May | 2022 | 0.0065385 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-19 20:18 | 2022-05-19 22:15 | 1732 | 001:57 | S | AVERIA EN BARRA DE DISTRIBUCION | 2 AISLADORES Y 1 MACHETE QUEMADOS EN EL #5 50% DE SU CARGA POR EL 2302-01 | R22051900055 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 117 | 2022-05-19 | 202644 | keep | 0 | May | 2022 | 0.13802 | 0.0011797 | Sustained | FALSE | FALSE | Not_TMED_Event | 1732
CANOVANAS | 2022-05-19 20:18 | 2022-05-19 22:15 | 2675 | 001:57 | S | AVERIA EN BARRA DE DISTRIBUCION | 2 AISLADORES Y 1 MACHETE QUEMADOS EN EL #5 | R22051900055 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 117 | 2022-05-19 | 312975 | keep | 0 | May | 2022 | 0.21317 | 0.0018219 | Sustained | FALSE | FALSE | Not_TMED_Event | 2675
ARECIBO | 2022-05-19 20:49 | 2022-05-19 21:20 | 150 | 000:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A22051900084 | New_Event | Cutout Failure | Include | Include | Equipment | 31 | 2022-05-19 | 4650 | keep | 0 | May | 2022 | 0.0031671 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-05-19 20:54 | 2022-05-19 20:56 | 3157 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11400 | A22051900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-19 | 6314 | keep | 0 | May | 2022 | 0.0043004 | 0.0021502 | Momentary | FALSE | FALSE | Not_TMED_Event | 3157
ARECIBO | 2022-05-19 20:54 | 2022-05-19 20:56 | 35 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11400 | A22051900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-19 | 70 | keep | 0 | May | 2022 | 4.7677e-05 | 2.3838e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-05-19 20:54 | 2022-05-19 20:56 | 2916 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11400 | A22051900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-19 | 5832 | keep | 0 | May | 2022 | 0.0039721 | 0.0019861 | Momentary | FALSE | FALSE | Not_TMED_Event | 2916
HUMACAO | 2022-05-19 21:07 | 2022-05-20 10:09 | 30 | 013:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | C22051900541 | New_Event | Cutout Failure | Include | Include | Equipment | 782 | 2022-05-19 | 23460 | keep | 0 | May | 2022 | 0.015978 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-19 21:52 | 2022-05-20 06:03 | 90 | 008:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEAS | C22051900551 | New_Event | Vegetation Contact | Include | Include | Vegetation | 491 | 2022-05-19 | 44190 | keep | 0 | May | 2022 | 0.030098 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-05-19 22:10 | 2022-05-20 08:21 | 60 | 010:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | C22051900553 | New_Event | Cutout Failure | Include | Include | Equipment | 611 | 2022-05-19 | 36660 | keep | 0 | May | 2022 | 0.024969 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-19 22:10 | 2022-05-20 02:10 | 25 | 004:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA ROTA A CAUSA DE DESGANCHE SE RETIRO RAMAS SOBRE LAS LINEAS | A22051900152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-05-19 | 6000 | keep | 0 | May | 2022 | 0.0040866 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-05-19 22:15 | 2022-05-20 09:55 | 60 | 011:40 | P | DESGANCHE | 1 X 80 EN C/L | R22051900051 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 700 | 2022-05-19 | 42000 | keep | 0 | May | 2022 | 0.028606 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-19 22:35 | 2022-05-20 10:15 | 350 | 011:40 | P | DESGANCHE | 1 X 80 EN C/L | R22051900118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 700 | 2022-05-19 | 245000 | keep | 0 | May | 2022 | 0.16687 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
AGUADILLA | 2022-05-19 22:51 | 2022-05-20 03:00 | 200 | 004:09 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | M22051900182 | New_Event | Primary Wire Break | Include | Include | Equipment | 249 | 2022-05-19 | 49800 | keep | 0 | May | 2022 | 0.033919 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-05-19 23:03 | 2022-05-20 00:07 | 120 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | A22051900178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-05-19 | 7680 | keep | 0 | May | 2022 | 0.0052308 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-05-19 23:07 | 2022-05-20 15:35 | 7 | 016:28 | P | CABLE SOTERRADO AVERIADO | CABLE SOTERRADO DE T# 67 A T#68 AVERIADO | P22051900141 | New_Event | UG Cable Fault | Include | Include | Equipment | 988 | 2022-05-19 | 6916 | keep | 0 | May | 2022 | 0.0047105 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-05-19 23:31 | 2022-05-20 06:46 | 100 | 007:15 | P | DESGANCHE | 2 X 50 EN CORTES DE LINEAS | C22051900563 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2022-05-19 | 43500 | keep | 0 | May | 2022 | 0.029628 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-20 01:13 | 2022-05-20 04:07 | 150 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M22052000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-05-20 | 26100 | keep | 0 | May | 2022 | 0.017777 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-20 01:14 | 2022-05-21 10:10 | 100 | 032:56 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS Y SE REPARO LINEA PRIMARIA ARRIADA | M22052000002 | New_Event | Primary Wire Break | Include | Include | Equipment | 1976 | 2022-05-20 | 197600 | keep | 0 | May | 2022 | 0.13458 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-05-20 01:27 | 2022-05-20 08:12 | 60 | 006:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER 1 X 40 C/L | B22052000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 405 | 2022-05-20 | 24300 | keep | 0 | May | 2022 | 0.016551 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-20 04:27 | 2022-05-20 04:28 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | A22052000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-20 | 5042 | keep | 0 | May | 2022 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
CAGUAS | 2022-05-20 05:07 | 2022-05-20 05:09 | 817 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | C22052000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-20 | 1634 | keep | 0 | May | 2022 | 0.0011129 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
UTUADO | 2022-05-20 05:46 | 2022-05-20 10:11 | 25 | 004:25 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22052000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2022-05-20 | 6625 | keep | 0 | May | 2022 | 0.0045123 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-20 05:57 | 2022-05-20 09:00 | 50 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22052000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-05-20 | 9150 | keep | 0 | May | 2022 | 0.006232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 858 | 000:01 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV 20% DE LA CARGA POR EL 1303-02 | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 858 | keep | 0 | May | 2022 | 0.00058438 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 108 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 108 | keep | 0 | May | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 1368 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 1368 | keep | 0 | May | 2022 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 2064 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 2064 | keep | 0 | May | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 1681 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV CARGA POR EL 1303-04 | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 1681 | keep | 0 | May | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 2435 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV LLEVA 20% DEL 1204-02 | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 2435 | keep | 0 | May | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 726 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV LLEVA EL 1346-04 | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 726 | keep | 0 | May | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 225 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV CARGA ESTA POR EL 1303-05 Y LLEVA 1303-01 , 1346-06 | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 225 | keep | 0 | May | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 870 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV LLEVA LA CARGA DEL 1303-04 | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 3932 | 000:01 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV CARGA POR EL 1303-03 | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 3932 | keep | 0 | May | 2022 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2022-05-20 06:21 | 2022-05-20 06:22 | 1598 | 000:01 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 3 MONACILLO 115KV CARGA POR EL 1303-04 | S22052000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-05-20 | 1598 | keep | 0 | May | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
MAYAGÃœEZ | 2022-05-20 06:57 | 2022-05-20 10:30 | 1 | 003:33 | P | ANIMAL | 1 X 30 EN RISER AVE | M22052000007 | New_Event | Animals | Include | Include | Wildlife | 213 | 2022-05-20 | 213 | keep | 0 | May | 2022 | 0.00014507 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-20 07:27 | 2022-05-20 10:24 | 6 | 002:57 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22052000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2022-05-20 | 1062 | keep | 0 | May | 2022 | 0.00072332 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-05-20 07:33 | 2022-05-20 09:24 | 5 | 001:51 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | C22052000016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-05-20 | 555 | keep | 0 | May | 2022 | 0.00037801 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-05-20 07:39 | 2022-05-20 10:54 | 90 | 003:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22052000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-05-20 | 17550 | keep | 0 | May | 2022 | 0.011953 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-05-20 07:42 | 2022-05-20 12:16 | 30 | 004:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22052000024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2022-05-20 | 8220 | keep | 0 | May | 2022 | 0.0055986 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-20 07:56 | 2022-05-20 09:09 | 1 | 001:13 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR | A22052000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-05-20 | 73 | keep | 0 | May | 2022 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-20 07:59 | 2022-05-20 12:52 | 615 | 004:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO PUENTE | S22052000010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 293 | 2022-05-20 | 180195 | keep | 0 | May | 2022 | 0.12273 | 0.00041887 | Sustained | FALSE | FALSE | Not_TMED_Event | 615
SAN JUAN | 2022-05-20 08:17 | 2022-05-20 11:18 | 1 | 003:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S22052000014 | New_Event | Primary Wire Break | Include | Include | Equipment | 181 | 2022-05-20 | 181 | keep | 0 | May | 2022 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-20 08:22 | 2022-05-20 11:15 | 200 | 002:53 | P | PROBLEMA DEL CLIENTE | 1 X 80 EN CORTE DE LINEA TRANSFORMADOR PRIVADO AVERIADO | M22052000015 | New_Event | Customer-Related Interruption | Include | Include | Public | 173 | 2022-05-20 | 34600 | keep | 0 | May | 2022 | 0.023566 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-05-20 08:34 | 2022-05-20 12:05 | 40 | 003:31 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22052000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-05-20 | 8440 | keep | 0 | May | 2022 | 0.0057484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-05-20 08:37 | 2022-05-20 16:05 | 65 | 007:28 | P | CAUSAS EXTERNAS | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE SE RETEZO LINEA PRIMARIA Y SE REINSTALO CAJA PRIMARIA QUE SE ZAFO CAUSADO POR CAMION QUE IMPACTO TRONCAL DE TELEFONO | M22052000019 | New_Event | Damage From Public | Include | Include | Public | 448 | 2022-05-20 | 29120 | keep | 0 | May | 2022 | 0.019833 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2022-05-20 08:43 | 2022-05-20 09:30 | 50 | 000:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22052000018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-05-20 | 2350 | keep | 0 | May | 2022 | 0.0016006 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-20 08:53 | 2022-05-21 09:55 | 20 | 025:02 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22052000026 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 1502 | 2022-05-20 | 30040 | keep | 0 | May | 2022 | 0.02046 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-20 08:59 | 2022-05-20 13:56 | 23 | 004:57 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22052000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-05-20 | 6831 | keep | 0 | May | 2022 | 0.0046526 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
FAJARDO | 2022-05-20 09:06 | 2022-05-20 12:20 | 50 | 003:14 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 Y 1 X 25 EN C/L SE RETEZO LINEA PRIMARIA | R22052000023 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 194 | 2022-05-20 | 9700 | keep | 0 | May | 2022 | 0.0066066 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-05-20 09:06 | 2022-05-20 12:30 | 1 | 003:24 | P | DESGANCHE | 1X25 EN C/L | B22052000041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-05-20 | 204 | keep | 0 | May | 2022 | 0.00013894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-20 09:14 | 2022-05-21 14:35 | 1 | 029:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA EVENTO DEL DIA 20 | A22052000041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1761 | 2022-05-20 | 1761 | keep | 0 | May | 2022 | 0.0011994 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-20 09:23 | 2022-05-21 10:03 | 50 | 024:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22052000089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1480 | 2022-05-20 | 74000 | keep | 0 | May | 2022 | 0.050401 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-20 09:23 | 2022-05-20 13:14 | 10 | 003:51 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO SE REPORTO CAUSA | C22052000030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2022-05-20 | 2310 | keep | 0 | May | 2022 | 0.0015733 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-20 09:25 | 2022-05-20 14:52 | 8 | 005:27 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | S22052000030 | New_Event | Primary Pole Failure | Include | Include | Equipment | 327 | 2022-05-20 | 2616 | keep | 0 | May | 2022 | 0.0017817 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-20 09:28 | 2022-05-20 12:50 | 4 | 003:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SECUNDARIA AVERIADA | M22052000028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 202 | 2022-05-20 | 808 | keep | 0 | May | 2022 | 0.00055033 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-05-20 09:31 | 2022-05-20 20:40 | 12 | 011:09 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 50 KVA A 4160VOLTS AVERIADO | P22052000011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 669 | 2022-05-20 | 8028 | keep | 0 | May | 2022 | 0.0054678 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-20 09:43 | 2022-05-20 16:14 | 11 | 006:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22052000033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 391 | 2022-05-20 | 4301 | keep | 0 | May | 2022 | 0.0029294 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2022-05-20 09:52 | 2022-05-20 10:55 | 347 | 001:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETE PARA REMPLAZAR AISLADOR PARTIDO | B22052000051 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 63 | 2022-05-20 | 21861 | keep | 0 | May | 2022 | 0.014889 | 0.00023634 | Sustained | FALSE | FALSE | Not_TMED_Event | 347
SAN JUAN | 2022-05-20 09:54 | 2022-05-20 09:59 | 614 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22052000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-20 | 3070 | keep | 0 | May | 2022 | 0.002091 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-05-20 09:54 | 2022-05-20 09:59 | 770 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22052000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-20 | 3850 | keep | 0 | May | 2022 | 0.0026222 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-05-20 09:54 | 2022-05-20 09:59 | 1271 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22052000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-20 | 6355 | keep | 0 | May | 2022 | 0.0043284 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2022-05-20 09:54 | 2022-05-20 09:59 | 247 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22052000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-20 | 1235 | keep | 0 | May | 2022 | 0.00084115 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
BAYAMON | 2022-05-20 10:01 | 2022-05-20 14:50 | 260 | 004:49 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTE PRIMARIO, LUEGO DE HABER CERRADO EN CONVERTIDOR, SE DESGANCHO, SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO Y SE VOLVIO A ABRIR EN CONVERTIDOR PARA CERRAR NUEVAMENTE EN PUENTE PRIMARIO | B22051900456 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 289 | 2022-05-20 | 75140 | keep | 0 | May | 2022 | 0.051178 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-20 10:07 | 2022-05-21 00:45 | 8 | 014:38 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA | M22052000034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 878 | 2022-05-20 | 7024 | keep | 0 | May | 2022 | 0.004784 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-20 10:26 | 2022-05-20 21:48 | 8 | 011:22 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | M22052000037 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 682 | 2022-05-20 | 5456 | keep | 0 | May | 2022 | 0.0037161 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-05-20 10:29 | 2022-05-20 11:13 | 10 | 000:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTE SECUNDARIO EN XMR | C22052000038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2022-05-20 | 440 | keep | 0 | May | 2022 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-20 10:36 | 2022-05-20 14:15 | 80 | 003:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22052000042 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2022-05-20 | 17520 | keep | 0 | May | 2022 | 0.011933 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-05-20 10:38 | 2022-05-20 11:08 | 4 | 000:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR CONECTORES EN BAJANTE SECUNDARIO | C22052000013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-05-20 | 120 | keep | 0 | May | 2022 | 8.1731e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-05-20 10:43 | 2022-05-20 12:46 | 233 | 002:03 | P | CAUSAS EXTERNAS | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR CABLES CRUZADOS POR VEHICULO Y PERSONA CON CONTACTO ELECTRICO. PERSONAL DE MUNICIPIO INTENTANDO RETIRAR VEHICULO CRUZADO CON LINEAS DE CABLE TV TUVO CONTACTO ELECTRICO. | C22052000060 | New_Event | Damage From Public | Include | Include | Public | 123 | 2022-05-20 | 28659 | keep | 0 | May | 2022 | 0.01952 | 0.0001587 | Sustained | FALSE | FALSE | Not_TMED_Event | 233
HUMACAO | 2022-05-20 10:51 | 2022-05-20 14:53 | 1 | 004:02 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22052000041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 242 | 2022-05-20 | 242 | keep | 0 | May | 2022 | 0.00016483 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-20 11:08 | 2022-05-20 15:40 | 20 | 004:32 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA SE RETIRO GLOBO DE LA LINEA | R22052000047 | New_Event | Damage From Public | Include | Include | Public | 272 | 2022-05-20 | 5440 | keep | 0 | May | 2022 | 0.0037052 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-20 11:09 | 2022-05-21 13:13 | 1 | 026:04 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | B22052000062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1564 | 2022-05-20 | 1564 | keep | 0 | May | 2022 | 0.0010652 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-20 11:34 | 2022-05-20 12:59 | 8 | 001:25 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR SECUNDARIA | B22052000053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 85 | 2022-05-20 | 680 | keep | 0 | May | 2022 | 0.00046314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-05-20 11:46 | 2022-05-20 15:50 | 23 | 004:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | S22052000061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 244 | 2022-05-20 | 5612 | keep | 0 | May | 2022 | 0.0038223 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
ARECIBO | 2022-05-20 11:52 | 2022-05-23 12:30 | 1 | 072:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN TRANSFORMADOR SE REPARO SECUNDARIA | A22052000045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 4358 | 2022-05-20 | 4358 | keep | 0 | May | 2022 | 0.0029682 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-20 11:58 | 2022-05-20 14:00 | 100 | 002:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | A22052000046 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2022-05-20 | 12200 | keep | 0 | May | 2022 | 0.0083094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-20 12:16 | 2022-05-20 12:22 | 1977 | 000:06 | P | ERROR HUMANO | PERSONAL DE PROTECCION TIRO LOCKOUT LA BARRA 4 MONACILLO 115KV 40% DE LA CARGA POR EL 1206-04 | S22052000000 | New_Event | Human Error | Include | Include | Other | 6 | 2022-05-20 | 11862 | keep | 0 | May | 2022 | 0.0080792 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-05-20 12:16 | 2022-05-20 12:22 | 641 | 000:06 | S | ERROR HUMANO | PERSONAL DE PROTECCION TIRO LOCKOUT LA BARRA 4 MONACILLO 115KV LLEVA EL 1206-02 | S22052000000 | New_Event | Human Error | Include | Include | Other | 6 | 2022-05-20 | 3846 | keep | 0 | May | 2022 | 0.0026195 | 0.00043658 | Sustained | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-05-20 12:16 | 2022-05-20 12:22 | 733 | 000:06 | S | ERROR HUMANO | PERSONAL DE PROTECCION TIRO LOCKOUT LA BARRA 4 MONACILLO 115KV CARGA POR EL 1206-01 | S22052000000 | New_Event | Human Error | Include | Include | Other | 6 | 2022-05-20 | 4398 | keep | 0 | May | 2022 | 0.0029955 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-05-20 12:16 | 2022-05-20 12:22 | 4133 | 000:06 | S | ERROR HUMANO | PERSONAL DE PROTECCION TIRO LOCKOUT LA BARRA 4 MONACILLO 115KV | S22052000000 | New_Event | Human Error | Include | Include | Other | 6 | 2022-05-20 | 24798 | keep | 0 | May | 2022 | 0.01689 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-05-20 12:16 | 2022-05-20 12:22 | 1799 | 000:06 | S | ERROR HUMANO | PERSONAL DE PROTECCION TIRO LOCKOUT LA BARRA 4 MONACILLO 115KV LLEVA 20% DEL 1303-02, 40% DEL 1204-04, 60% DEL 1204-03 | S22052000000 | New_Event | Human Error | Include | Include | Other | 6 | 2022-05-20 | 10794 | keep | 0 | May | 2022 | 0.0073517 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-20 12:17 | 2022-05-20 12:22 | 828 | 000:05 | P | ERROR HUMANO | PERSONAL DE PROTECCION TIRO LOCKOUT LA BARRA 4 MONACILLO 115KV 60% DE LA CARGA POR EL 1206-04 | S22052000000 | New_Event | Human Error | Include | Include | Other | 5 | 2022-05-20 | 4140 | keep | 0 | May | 2022 | 0.0028197 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
CAGUAS | 2022-05-20 12:32 | 2022-05-20 20:56 | 5 | 008:24 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO Y REPARO SECUNDARIA | C22052000058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 504 | 2022-05-20 | 2520 | keep | 0 | May | 2022 | 0.0017164 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-20 12:39 | 2022-05-20 12:40 | 487 | 000:01 | P | ERROR HUMANO | PERSONAL DE PROTECCION TIRO LOCKOUT LA BARRA 115KV 20% DE LA CARGA POR EL 1206-04 | S22052000000 | New_Event | Human Error | Include | Include | Other | 1 | 2022-05-20 | 487 | keep | 0 | May | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
CAGUAS | 2022-05-20 12:46 | 2022-05-20 19:15 | 234 | 006:29 | P | CONDUCTOR ARRIADO O CRUZADO | ABRIO C/L PARA INSTALAR POSTE Y LEVANTAR LINEAS QUE ESTABAN SUMAMENTE ARRIADAS | C22052000069 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 389 | 2022-05-20 | 91026 | keep | 0 | May | 2022 | 0.061997 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
BAYAMON | 2022-05-20 13:04 | 2022-05-20 14:55 | 40 | 001:51 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22052000072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-05-20 | 4440 | keep | 0 | May | 2022 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-05-20 13:20 | 2022-05-20 14:21 | 7 | 001:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R22052000052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2022-05-20 | 427 | keep | 0 | May | 2022 | 0.00029083 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-05-20 13:44 | 2022-05-20 15:14 | 10 | 001:30 | P | NO SE REPORTO CAUSA | 1X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22052000063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2022-05-20 | 900 | keep | 0 | May | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-05-20 13:54 | 2022-05-21 10:30 | 10 | 020:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES SECUNDARIAS EN LOS BAJANTES DEL TRANSFORMADOR | M22052000085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1236 | 2022-05-20 | 12360 | keep | 0 | May | 2022 | 0.0084183 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-20 14:01 | 2022-05-20 19:30 | 100 | 005:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 30 EN CORTES DE LINEAS SE REALIZO DESGANCHE Y SE REMPLAZO CAJA PRIMARIA AVERIADA | M22052000088 | New_Event | Cutout Failure | Include | Include | Equipment | 329 | 2022-05-20 | 32900 | keep | 0 | May | 2022 | 0.022408 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-20 14:11 | 2022-05-20 15:28 | 16 | 001:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR CONTAMINACION EN PORTAFUSIBLE | R22052000074 | New_Event | Cutout Failure | Include | Include | Equipment | 77 | 2022-05-20 | 1232 | keep | 0 | May | 2022 | 0.00083911 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-05-20 14:17 | 2022-05-20 22:10 | 92 | 007:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA UL2 NO REPORTO CAUSA | M22052000092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 473 | 2022-05-20 | 43516 | keep | 0 | May | 2022 | 0.029639 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
CANOVANAS | 2022-05-20 14:19 | 2022-05-20 17:03 | 1 | 002:44 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22052000075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-05-20 | 164 | keep | 0 | May | 2022 | 0.0001117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-20 14:38 | 2022-05-20 16:21 | 70 | 001:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR VIENTOS | A22052000069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 103 | 2022-05-20 | 7210 | keep | 0 | May | 2022 | 0.0049107 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-05-20 14:50 | 2022-05-20 16:36 | 419 | 001:46 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTE, SE SUBIO CONDUCTOR PRIMARIO DEL SUELO, SE ABRIO NUEVAMENTE EN CONVERTIDOR PARA VOLVER A CERRAR PUENTE PRIMARIO, SE RETIRARON TIERRAS Y SE VOLVIO A CERRAR EN CONVERTIDOR | B22051900456 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 106 | 2022-05-20 | 44414 | keep | 0 | May | 2022 | 0.03025 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-20 14:56 | 2022-05-20 14:58 | 3295 | 000:02 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO POR CONTROL | B22052000079 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-05-20 | 6590 | keep | 0 | May | 2022 | 0.0044884 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-05-20 14:58 | 2022-05-20 20:37 | 150 | 005:39 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO & SE REMPLAZARON DOS DISCOS PARTIDOS MEDIANTE G.O.I. BY-220520-01 | B22052000081 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 339 | 2022-05-20 | 50850 | keep | 0 | May | 2022 | 0.034634 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-05-20 14:59 | 2022-05-20 16:34 | 20 | 001:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO Y SE CERRO CORTE DE LINEA | A22052000071 | New_Event | Primary Wire Break | Include | Include | Equipment | 95 | 2022-05-20 | 1900 | keep | 0 | May | 2022 | 0.0012941 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-20 15:02 | 2022-05-20 19:30 | 15 | 004:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22052000072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 268 | 2022-05-20 | 4020 | keep | 0 | May | 2022 | 0.002738 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-20 15:28 | 2022-05-20 16:16 | 1 | 000:48 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22052000091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2022-05-20 | 48 | keep | 0 | May | 2022 | 3.2693e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-05-20 16:31 | 2022-05-20 16:42 | 1 | 000:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22052000086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-05-20 | 11 | keep | 0 | May | 2022 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-20 17:17 | 2022-05-20 17:18 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22052000087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-20 | 3046 | keep | 0 | May | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
AGUADILLA | 2022-05-20 17:30 | 2022-05-21 02:35 | 50 | 009:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22052000136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 545 | 2022-05-20 | 27250 | keep | 0 | May | 2022 | 0.01856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-20 17:41 | 2022-05-21 11:19 | 10 | 017:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DE XMR ABIERTO. NO FUNDIO FUSIBLE. | R22052000090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1058 | 2022-05-20 | 10580 | keep | 0 | May | 2022 | 0.007206 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-05-20 17:52 | 2022-05-20 20:30 | 40 | 002:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22052000137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-05-20 | 6320 | keep | 0 | May | 2022 | 0.0043045 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-20 18:00 | 2022-05-20 19:25 | 10 | 001:25 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA DE EMERGENCIA POR ARBOL QUE CAYO SOBRE LAS LINEAS Y ESTABA PRENDIDO EN FUEGO SE RETIRO EL ARBOL DE LAS LINEAS SE REALIZO DESGANCHE Y SE VOLVIO A CERRAR EL CORTE DE LINEA | M22052000145 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 85 | 2022-05-20 | 850 | keep | 0 | May | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-20 18:20 | 2022-05-21 12:10 | 3 | 017:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C22052000076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1070 | 2022-05-20 | 3210 | keep | 0 | May | 2022 | 0.0021863 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-05-20 18:35 | 2022-05-20 19:50 | 14 | 001:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA LEVANTAR SECUNDARIA | S22052000138 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2022-05-20 | 1050 | keep | 0 | May | 2022 | 0.00071515 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2022-05-20 18:38 | 2022-05-21 09:32 | 11 | 014:54 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22052000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 894 | 2022-05-20 | 9834 | keep | 0 | May | 2022 | 0.0066979 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2022-05-20 18:48 | 2022-05-20 18:49 | 3766 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR EN SERVICIO | R22052000097 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-20 | 3766 | keep | 0 | May | 2022 | 0.002565 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
CANOVANAS | 2022-05-20 18:49 | 2022-05-20 21:10 | 247 | 002:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | R22502000098 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 141 | 2022-05-20 | 34827 | keep | 0 | May | 2022 | 0.023721 | 0.00016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 247
SAN JUAN | 2022-05-20 19:11 | 2022-05-20 22:03 | 15 | 002:52 | P | DESGANCHE | 1 X 15 EN XMR SE REEMPLAZO CAJA PRIMARIA DESGANCHE | S22052000143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-05-20 | 2580 | keep | 0 | May | 2022 | 0.0017572 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-05-20 19:14 | 2022-05-20 19:15 | 2446 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052000060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-20 | 2446 | keep | 0 | May | 2022 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2022-05-20 19:14 | 2022-05-20 19:15 | 5069 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA DE 5011-03 | P22052000060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-20 | 5069 | keep | 0 | May | 2022 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
FAJARDO | 2022-05-20 19:25 | 2022-05-20 21:40 | 27 | 002:15 | P | ANIMAL | 1 X 30 Y 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | R22052000108 | New_Event | Animals | Include | Include | Wildlife | 135 | 2022-05-20 | 3645 | keep | 0 | May | 2022 | 0.0024826 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2022-05-20 19:38 | 2022-05-20 20:15 | 85 | 000:37 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA SE RETIRO CHIRINGA DE LA LINEA | R22052000110 | New_Event | Damage From Public | Include | Include | Public | 37 | 2022-05-20 | 3145 | keep | 0 | May | 2022 | 0.002142 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
MAYAGÃœEZ | 2022-05-20 19:38 | 2022-05-21 11:00 | 12 | 015:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22052000154 | New_Event | Secondary Wire Break | Include | Include | Equipment | 922 | 2022-05-20 | 11064 | keep | 0 | May | 2022 | 0.0075356 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-20 19:51 | 2022-05-21 06:05 | 10 | 010:14 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A TRANSFORMADOR | C22052000083 | New_Event | Primary Wire Break | Include | Include | Equipment | 614 | 2022-05-20 | 6140 | keep | 0 | May | 2022 | 0.0041819 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-20 19:51 | 2022-05-21 09:50 | 25 | 013:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22052000078 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 839 | 2022-05-20 | 20975 | keep | 0 | May | 2022 | 0.014286 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-05-20 20:32 | 2022-05-20 22:20 | 600 | 001:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA UL2 NO REPORTO CAUSA | A22052000083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2022-05-20 | 64800 | keep | 0 | May | 2022 | 0.044135 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
CAGUAS | 2022-05-20 20:45 | 2022-05-22 10:37 | 5 | 037:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTE SECUNDARIO EN BANCO DE XMR | C22052000085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 2272 | 2022-05-20 | 11360 | keep | 0 | May | 2022 | 0.0077372 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-05-20 22:09 | 2022-05-20 23:48 | 129 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22052000074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-05-20 | 12771 | keep | 0 | May | 2022 | 0.0086983 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
ARECIBO | 2022-05-20 22:35 | 2022-05-20 23:35 | 200 | 001:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBU | A22052000093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-05-20 | 12000 | keep | 0 | May | 2022 | 0.0081731 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-05-20 22:49 | 2022-05-21 08:40 | 12 | 009:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REEMPLAZO CAJA PRIMARIA DE XMR | R22052000125 | New_Event | Cutout Failure | Include | Include | Equipment | 591 | 2022-05-20 | 7092 | keep | 0 | May | 2022 | 0.0048303 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-20 23:19 | 2022-05-21 09:20 | 8 | 010:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLES | A22052000095 | New_Event | Cutout Failure | Include | Include | Equipment | 601 | 2022-05-20 | 4808 | keep | 0 | May | 2022 | 0.0032747 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-05-20 23:22 | 2022-05-21 10:14 | 113 | 010:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR Y PIN POLE TOP | C22052000089 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 652 | 2022-05-20 | 73676 | keep | 0 | May | 2022 | 0.05018 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
PONCE | 2022-05-20 23:33 | 2022-05-21 08:09 | 50 | 008:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22052000077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 516 | 2022-05-20 | 25800 | keep | 0 | May | 2022 | 0.017572 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-21 00:28 | 2022-05-21 00:30 | 125 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22052100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-21 | 250 | keep | 0 | May | 2022 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-05-21 03:31 | 2022-05-21 07:47 | 100 | 004:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-05-21 | 25600 | keep | 0 | May | 2022 | 0.017436 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-05-21 06:27 | 2022-05-21 07:10 | 50 | 000:43 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P22052100010 | New_Event | Animals | Include | Include | Wildlife | 43 | 2022-05-21 | 2150 | keep | 0 | May | 2022 | 0.0014644 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-21 06:39 | 2022-05-21 09:20 | 30 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22052100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-05-21 | 4830 | keep | 0 | May | 2022 | 0.0032897 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-21 07:06 | 2022-05-21 11:39 | 10 | 004:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S22052100008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 273 | 2022-05-21 | 2730 | keep | 0 | May | 2022 | 0.0018594 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-05-21 07:14 | 2022-05-21 09:12 | 50 | 001:58 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P22052100013 | New_Event | Animals | Include | Include | Wildlife | 118 | 2022-05-21 | 5900 | keep | 0 | May | 2022 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-21 07:21 | 2022-05-21 07:22 | 2076 | 000:01 | P | NO SE REPORTO CAUSA | FEEDER 1718-03 RECERRO Y LLEVA 40% DEL 1710-05 | B22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 2076 | keep | 0 | May | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-05-21 07:21 | 2022-05-21 07:22 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 40% 1710-05 | B22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 2605 | keep | 0 | May | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-05-21 07:21 | 2022-05-21 07:22 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 73 | keep | 0 | May | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
ARECIBO | 2022-05-21 07:21 | 2022-05-21 12:00 | 200 | 004:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22052100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-05-21 | 55800 | keep | 0 | May | 2022 | 0.038005 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-21 07:33 | 2022-05-21 07:34 | 3046 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22052100009 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-21 | 3046 | keep | 0 | May | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-05-21 07:34 | 2022-05-21 14:51 | 85 | 007:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L REMPLAZO CAJA QUEMADA | R22052100029 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 437 | 2022-05-21 | 37145 | keep | 0 | May | 2022 | 0.025299 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2022-05-21 07:34 | 2022-05-21 14:03 | 5 | 006:29 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 SMU 20 DE 80 AMP EN EL SU - 22A CONTAMINACION SU - 22A REQUIERE MANTENIMIENTO | R22052100024 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 389 | 2022-05-21 | 1945 | keep | 0 | May | 2022 | 0.0013247 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-05-21 07:44 | 2022-05-21 08:45 | 153 | 001:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE POR RAMA | C22052100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-05-21 | 9333 | keep | 0 | May | 2022 | 0.0063567 | 0.00010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 153
AGUADILLA | 2022-05-21 07:45 | 2022-05-21 14:41 | 30 | 006:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN CORTE DE LINEA POR VIENTOS | M22052100018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 416 | 2022-05-21 | 12480 | keep | 0 | May | 2022 | 0.0085001 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-21 08:02 | 2022-05-21 08:05 | 1500 | 000:03 | P | DESGANCHE | DISPARO INTERRUPTOR 1620-05 LLEVANDO PARTE 1206-03 | S22052100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-05-21 | 4500 | keep | 0 | May | 2022 | 0.0030649 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-05-21 08:02 | 2022-05-21 08:05 | 1615 | 000:03 | T | DESGANCHE | DISPARO INTERRUPTOR 1620-05 LLEVANDO PARTE 1206-03 | S22052100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-05-21 | 4845 | keep | 0 | May | 2022 | 0.0032999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2022-05-21 08:05 | 2022-05-21 09:46 | 95 | 001:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHO | R22052100020 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-05-21 | 9595 | keep | 0 | May | 2022 | 0.0065351 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
SAN JUAN | 2022-05-21 08:05 | 2022-05-21 09:20 | 150 | 001:15 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA Y RETIRO RAMA SOBRE LINEA | R22052100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-05-21 | 11250 | keep | 0 | May | 2022 | 0.0076623 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-05-21 08:08 | 2022-05-21 08:09 | 1467 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR EN SERVICIO | C22052100011 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-21 | 1467 | keep | 0 | May | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-05-21 08:09 | 2022-05-21 11:46 | 1 | 003:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 40 EN RISER SE REEMPLAZO CAJA PRIMARIA QUEMADA | C22052100040 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 217 | 2022-05-21 | 217 | keep | 0 | May | 2022 | 0.0001478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-21 08:29 | 2022-05-21 12:20 | 304 | 003:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22052100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2022-05-21 | 70224 | keep | 0 | May | 2022 | 0.047829 | 0.00020705 | Sustained | FALSE | FALSE | Not_TMED_Event | 304
MAYAGÃœEZ | 2022-05-21 09:00 | 2022-05-21 10:42 | 30 | 001:42 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-05-21 | 3060 | keep | 0 | May | 2022 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-05-21 09:04 | 2022-05-21 09:05 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 1827 | keep | 0 | May | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CAGUAS | 2022-05-21 09:06 | 2022-05-21 10:15 | 283 | 001:09 | P | CAUSAS EXTERNAS | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE RETIRO GLOBO DE LA LINEA | C22052100021 | New_Event | Damage From Public | Include | Include | Public | 69 | 2022-05-21 | 19527 | keep | 0 | May | 2022 | 0.0133 | 0.00019275 | Sustained | FALSE | FALSE | Not_TMED_Event | 283
ARECIBO | 2022-05-21 09:06 | 2022-05-21 11:00 | 60 | 001:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | A22052100016 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2022-05-21 | 6840 | keep | 0 | May | 2022 | 0.0046587 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-21 09:11 | 2022-05-21 13:44 | 80 | 004:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN C/L | S22052100017 | New_Event | Primary Wire Break | Include | Include | Equipment | 273 | 2022-05-21 | 21840 | keep | 0 | May | 2022 | 0.014875 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-05-21 09:39 | 2022-05-21 11:49 | 3449 | 002:10 | T | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO EN TRONCAL DE ALIMENTADOR | M22052100052 | New_Event | Primary Wire Break | Include | Include | Equipment | 130 | 2022-05-21 | 448370 | keep | 0 | May | 2022 | 0.30538 | 0.0023491 | Sustained | FALSE | FALSE | Not_TMED_Event | 3449
BAYAMON | 2022-05-21 09:40 | 2022-05-21 10:10 | 15 | 000:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22052000068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-05-21 | 450 | keep | 0 | May | 2022 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-05-21 09:43 | 2022-05-21 11:41 | 80 | 001:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 30 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | R22052100023 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 118 | 2022-05-21 | 9440 | keep | 0 | May | 2022 | 0.0064295 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-21 10:01 | 2022-05-22 16:50 | 200 | 030:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052100058 | New_Event | Primary Wire Break | Include | Include | Equipment | 1849 | 2022-05-21 | 369800 | keep | 0 | May | 2022 | 0.25187 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-21 10:06 | 2022-05-21 12:13 | 10 | 002:07 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22052100059 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 127 | 2022-05-21 | 1270 | keep | 0 | May | 2022 | 0.00086499 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-21 10:55 | 2022-05-21 12:00 | 21 | 001:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA FUERTES VIENTOS | C22052100045 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 65 | 2022-05-21 | 1365 | keep | 0 | May | 2022 | 0.0009297 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-05-21 11:19 | 2022-05-21 14:40 | 60 | 003:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO | B22052100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-05-21 | 12060 | keep | 0 | May | 2022 | 0.008214 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-21 11:24 | 2022-05-21 18:38 | 80 | 007:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE DE BAMBUAS | M22052100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2022-05-21 | 34720 | keep | 0 | May | 2022 | 0.023648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-21 11:28 | 2022-05-21 12:29 | 9 | 001:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22052100013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2022-05-21 | 549 | keep | 0 | May | 2022 | 0.00037392 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-05-21 11:35 | 2022-05-21 11:46 | 1 | 000:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA CERRAR NEUTRAL | S22052000038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 11 | 2022-05-21 | 11 | keep | 0 | May | 2022 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-05-21 11:49 | 2022-05-21 14:00 | 4882 | 002:11 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR POR PUENTE PRIMARIO ABIERTO EN TRONCAL DE ALIMENTADOR | M22052100085 | New_Event | Primary Wire Break | Include | Include | Equipment | 131 | 2022-05-21 | 639542 | keep | 0 | May | 2022 | 0.43559 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
BAYAMON | 2022-05-21 12:04 | 2022-05-21 12:24 | 21 | 000:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA Y SE SUBIO TAPS DE 1 AL 3 121V POR FASE | S22052100024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-05-21 | 420 | keep | 0 | May | 2022 | 0.00028606 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
VEGA BAJA | 2022-05-21 13:01 | 2022-05-21 14:50 | 30 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22052100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-05-21 | 3270 | keep | 0 | May | 2022 | 0.0022272 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-05-21 13:03 | 2022-05-21 13:04 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 752 | keep | 0 | May | 2022 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2022-05-21 13:10 | 2022-05-21 14:11 | 21 | 001:01 | P | PROBLEMA DEL CLIENTE | SE ABRE TRANSFORMADOR PARA DESCONECTAR TOMA AVERIA DE CLIENTE Y SE CERRO TRANSFORMADOR | S22052100024 | New_Event | Customer-Related Interruption | Include | Include | Public | 61 | 2022-05-21 | 1281 | keep | 0 | May | 2022 | 0.00087248 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BARRANQUITAS | 2022-05-21 13:18 | 2022-05-21 21:35 | 2 | 008:17 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 5 KVA X 37.5 KVA | C22052100055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 497 | 2022-05-21 | 994 | keep | 0 | May | 2022 | 0.00067701 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-05-21 13:19 | 2022-05-21 13:49 | 11 | 000:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C22052100056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-05-21 | 330 | keep | 0 | May | 2022 | 0.00022476 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-05-21 13:26 | 2022-05-21 20:53 | 23 | 007:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE DE RAMAS | C22052100059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 447 | 2022-05-21 | 10281 | keep | 0 | May | 2022 | 0.0070023 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2022-05-21 13:30 | 2022-05-21 14:35 | 50 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22052100027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-05-21 | 3250 | keep | 0 | May | 2022 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-21 13:54 | 2022-05-21 19:49 | 50 | 005:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA REQUIERE DESGANCHE | M22052100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2022-05-21 | 17750 | keep | 0 | May | 2022 | 0.012089 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-05-21 13:55 | 2022-05-21 14:49 | 22 | 000:54 | P | DESGANCHE | 1 X 30 EN C/L | R22052100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-05-21 | 1188 | keep | 0 | May | 2022 | 0.00080914 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
FAJARDO | 2022-05-21 14:11 | 2022-05-21 17:36 | 150 | 003:25 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA SE ELIMINO PARARRAYO CRUCE POR AVE | R22052100035 | New_Event | Animals | Include | Include | Wildlife | 205 | 2022-05-21 | 30750 | keep | 0 | May | 2022 | 0.020944 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-05-21 14:20 | 2022-05-21 14:21 | 3502 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN ON SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | A22052100030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 3502 | keep | 0 | May | 2022 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
YAUCO | 2022-05-21 14:22 | 2022-05-21 16:15 | 173 | 001:53 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA SE REMOVIO GLOBO DE HELIO | P22052100039 | New_Event | Damage From Public | Include | Include | Public | 113 | 2022-05-21 | 19549 | keep | 0 | May | 2022 | 0.013315 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
HUMACAO | 2022-05-21 14:34 | 2022-05-21 20:55 | 10 | 006:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22052100084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 381 | 2022-05-21 | 3810 | keep | 0 | May | 2022 | 0.002595 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-05-21 14:35 | 2022-05-21 14:36 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 3420 | keep | 0 | May | 2022 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
GUAYAMA | 2022-05-21 14:38 | 2022-05-21 16:50 | 315 | 002:12 | P | TERMINACION SOTERRADA AVERIADA | SE ABRE RISER DE ENTRADA Y SALIDA Y SE CIERRA N/O CON 4003-02 AVERIA EN RISER DE ENTRADA SEGUN LA INFORMACION SON LAS TERMINACIONES | P22052100045 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 132 | 2022-05-21 | 41580 | keep | 0 | May | 2022 | 0.02832 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
ARECIBO | 2022-05-21 15:06 | 2022-05-21 16:10 | 250 | 001:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A22052100034 | New_Event | Primary Wire Break | Include | Include | Equipment | 64 | 2022-05-21 | 16000 | keep | 0 | May | 2022 | 0.010898 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2022-05-21 15:26 | 2022-05-21 15:27 | 1017 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | M22052100119 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-05-21 | 1017 | keep | 0 | May | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-21 15:27 | 2022-05-21 15:52 | 691 | 000:25 | P | DESCONECTIVO DEFECTUOSO | MACHETES DE SALIDA QUEMADOS | M22052100135 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 25 | 2022-05-21 | 17275 | keep | 0 | May | 2022 | 0.011766 | 0.00047064 | Sustained | FALSE | FALSE | Not_TMED_Event | 691
MAYAGÃœEZ | 2022-05-21 15:29 | 2022-05-21 15:31 | 863 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052100121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-21 | 1726 | keep | 0 | May | 2022 | 0.0011756 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
HUMACAO | 2022-05-21 15:30 | 2022-05-21 15:33 | 1089 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C22052100065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-21 | 3267 | keep | 0 | May | 2022 | 0.0022251 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-05-21 15:30 | 2022-05-21 15:33 | 3896 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C22052100065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-21 | 11688 | keep | 0 | May | 2022 | 0.0079606 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-05-21 15:30 | 2022-05-21 15:33 | 1467 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C22052100065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-21 | 4401 | keep | 0 | May | 2022 | 0.0029975 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
MAYAGÃœEZ | 2022-05-21 15:30 | 2022-05-21 18:12 | 50 | 002:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA | M22052100120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-05-21 | 8100 | keep | 0 | May | 2022 | 0.0055169 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-21 15:32 | 2022-05-21 17:48 | 40 | 002:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A22052100035 | New_Event | Cutout Failure | Include | Include | Equipment | 136 | 2022-05-21 | 5440 | keep | 0 | May | 2022 | 0.0037052 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-05-21 15:36 | 2022-05-21 15:37 | 1843 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 1843 | keep | 0 | May | 2022 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
MAYAGÃœEZ | 2022-05-21 15:37 | 2022-05-21 15:39 | 863 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052100126 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-21 | 1726 | keep | 0 | May | 2022 | 0.0011756 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
HUMACAO | 2022-05-21 15:39 | 2022-05-21 16:34 | 15 | 000:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C22052100039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-05-21 | 825 | keep | 0 | May | 2022 | 0.0005619 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-05-21 15:39 | 2022-05-21 18:47 | 10 | 003:08 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22052100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2022-05-21 | 1880 | keep | 0 | May | 2022 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-21 15:39 | 2022-05-21 19:17 | 15 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CONVERTIDOR SE REMPLAZO PORTAFUSIBLES AVERIADO | A22052100037 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2022-05-21 | 3270 | keep | 0 | May | 2022 | 0.0022272 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-05-21 15:43 | 2022-05-21 15:46 | 1089 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO SM C.C.E. CERRARON DE RIO BLANCO HACIA PUEBLITO DEL RIO, DEJARON ABIERTO HACIA JUNCOS | C22052100068 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-21 | 3267 | keep | 0 | May | 2022 | 0.0022251 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-05-21 15:43 | 2022-05-21 15:46 | 3896 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO SM C.C.E. CERRARON DE RIO BLANCO HACIA PUEBLITO DEL RIO, DEJARON ABIERTO HACIA JUNCOS | C22052100068 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-21 | 11688 | keep | 0 | May | 2022 | 0.0079606 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-05-21 15:43 | 2022-05-21 15:46 | 1467 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO SM C.C.E. CERRARON DE RIO BLANCO HACIA PUEBLITO DEL RIO, DEJARON ABIERTO HACIA JUNCOS | C22052100068 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-21 | 4401 | keep | 0 | May | 2022 | 0.0029975 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
MAYAGÃœEZ | 2022-05-21 15:52 | 2022-05-21 19:35 | 1017 | 003:43 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR POR MACHETES DE SALIDA QUEMADOS | M22052100135 | Additional_clients | Switch Failure | Include | Include | Equipment | 223 | 2022-05-21 | 226791 | keep | 0 | May | 2022 | 0.15447 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-05-21 15:56 | 2022-05-22 07:46 | 41 | 015:50 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | B22052100034 | New_Event | Primary Wire Break | Include | Include | Equipment | 950 | 2022-05-21 | 38950 | keep | 0 | May | 2022 | 0.026529 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
ARECIBO | 2022-05-21 16:05 | 2022-05-21 16:25 | 12 | 000:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A22052100041 | New_Event | Cutout Failure | Include | Include | Equipment | 20 | 2022-05-21 | 240 | keep | 0 | May | 2022 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-21 16:13 | 2022-05-21 16:14 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052100153 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 863 | keep | 0 | May | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2022-05-21 16:59 | 2022-05-21 17:01 | 1483 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 30% POR 1336-08 | S22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-21 | 2966 | keep | 0 | May | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-21 16:59 | 2022-05-21 17:01 | 1500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE POR 1336-08 | S22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-21 | 3000 | keep | 0 | May | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-05-21 16:59 | 2022-05-21 17:01 | 5290 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1336-9 Y LLEVA 30% DEL 1204-4 Y PARTE DEL 1204-5 | S22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-21 | 10580 | keep | 0 | May | 2022 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-05-21 16:59 | 2022-05-21 17:01 | 207 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1336-08 | S22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-21 | 414 | keep | 0 | May | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
BAYAMON | 2022-05-21 17:30 | 2022-05-21 17:55 | 18 | 000:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22052100040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-05-21 | 450 | keep | 0 | May | 2022 | 0.00030649 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-05-21 17:50 | 2022-05-21 18:30 | 6 | 000:40 | P | ANIMAL | 1 X 140 EN CORTE DE LINEA CRUCE POR AVE | C22052100075 | New_Event | Animals | Include | Include | Wildlife | 40 | 2022-05-21 | 240 | keep | 0 | May | 2022 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-05-21 18:02 | 2022-05-21 19:33 | 39 | 001:31 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22052100076 | New_Event | Animals | Include | Include | Wildlife | 91 | 2022-05-21 | 3549 | keep | 0 | May | 2022 | 0.0024172 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2022-05-21 18:16 | 2022-05-21 18:17 | 3005 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052100077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 3005 | keep | 0 | May | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
PONCE | 2022-05-21 18:26 | 2022-05-21 20:29 | 15 | 002:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA Y 2 X 10 EN TRANSFORMADOR | P22052100057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 123 | 2022-05-21 | 1845 | keep | 0 | May | 2022 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-21 18:51 | 2022-05-21 18:55 | 828 | 000:04 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA AMARRAR CARGA DEL 6201-02 | M22052100000 | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2022-05-21 | 3312 | keep | 0 | May | 2022 | 0.0022558 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
AGUADILLA | 2022-05-21 19:00 | 2022-05-22 02:16 | 60 | 007:16 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASES | M22052100202 | New_Event | Animals | Include | Include | Wildlife | 436 | 2022-05-21 | 26160 | keep | 0 | May | 2022 | 0.017817 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-21 19:05 | 2022-05-21 22:40 | 200 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22052100055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2022-05-21 | 43000 | keep | 0 | May | 2022 | 0.029287 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-21 19:10 | 2022-05-21 23:10 | 100 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | M22052100203 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2022-05-21 | 24000 | keep | 0 | May | 2022 | 0.016346 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-21 19:35 | 2022-05-21 20:07 | 500 | 000:32 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR POR MACHETES DE SALIDA QUEMADOS SE AMARRO 6201-02 CON EL 6201-03 | M22052100135 | Partial_restoration | Switch Failure | Include | Include | Equipment | 32 | 2022-05-21 | 16000 | keep | 0 | May | 2022 | 0.010898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-21 20:30 | 2022-05-21 20:31 | 2859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052100077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 2859 | keep | 0 | May | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
MAYAGÃœEZ | 2022-05-21 20:34 | 2022-05-23 12:58 | 517 | 040:24 | P | CONDUCTOR ROTO O ABIERTO | 2 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M22052100219 | New_Event | Primary Wire Break | Include | Include | Equipment | 2424 | 2022-05-21 | 1253208 | keep | 0 | May | 2022 | 0.85355 | 0.00035213 | Sustained | FALSE | FALSE | Not_TMED_Event | 517
BARRANQUITAS | 2022-05-21 21:26 | 2022-05-22 08:15 | 45 | 010:49 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA REEMPLAZO PARARRAYO | C22052100087 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 649 | 2022-05-21 | 29205 | keep | 0 | May | 2022 | 0.019891 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-05-21 21:38 | 2022-05-22 08:22 | 28 | 010:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22052100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 644 | 2022-05-21 | 18032 | keep | 0 | May | 2022 | 0.012282 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
CANOVANAS | 2022-05-21 21:40 | 2022-05-22 13:00 | 15 | 015:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5KVA | R22052100052 | New_Event | Service Transformer Failure | Include | Include | Equipment | 920 | 2022-05-21 | 13800 | keep | 0 | May | 2022 | 0.0093991 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-05-21 23:26 | 2022-05-21 23:27 | 2694 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22052100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-21 | 2694 | keep | 0 | May | 2022 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
SAN JUAN | 2022-05-22 00:02 | 2022-05-22 09:40 | 10 | 009:38 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER A T-1 | S22052200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 578 | 2022-05-22 | 5780 | keep | 0 | May | 2022 | 0.0039367 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-05-22 01:19 | 2022-05-22 15:43 | 9 | 014:24 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR & SE LIMPIO ENRREADERA DEL POSTE | B22052200001 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 864 | 2022-05-22 | 7776 | keep | 0 | May | 2022 | 0.0052962 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-05-22 03:40 | 2022-05-22 03:41 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 108 | keep | 0 | May | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2022-05-22 03:43 | 2022-05-22 08:42 | 16 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN AEREO PROVISIONAL | B22052200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2022-05-22 | 4784 | keep | 0 | May | 2022 | 0.0032584 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2022-05-22 05:09 | 2022-05-22 12:28 | 40 | 007:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22052200003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 439 | 2022-05-22 | 17560 | keep | 0 | May | 2022 | 0.01196 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-22 05:52 | 2022-05-22 09:13 | 90 | 003:21 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA POR SOBRECARGA Y CONTAMINACION | A22052200057 | New_Event | Trip Due To Overload | Include | Include | Other | 201 | 2022-05-22 | 18090 | keep | 0 | May | 2022 | 0.012321 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-05-22 06:00 | 2022-05-22 10:59 | 40 | 004:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22052200010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 299 | 2022-05-22 | 11960 | keep | 0 | May | 2022 | 0.0081459 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-22 06:08 | 2022-05-22 10:56 | 50 | 004:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PARTIDO | A22052200012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 288 | 2022-05-22 | 14400 | keep | 0 | May | 2022 | 0.0098078 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-22 06:15 | 2022-05-22 09:10 | 60 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M22052200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2022-05-22 | 10500 | keep | 0 | May | 2022 | 0.0071515 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-22 06:17 | 2022-05-23 21:18 | 50 | 039:01 | P | DESGANCHE | 1 X 65 EN C/L SE ENDEREZO CAJA PRIMARIA DESGANCHE | S22052200127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2341 | 2022-05-22 | 117050 | keep | 0 | May | 2022 | 0.079722 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-22 06:20 | 2022-05-22 15:53 | 20 | 009:33 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22052200005 | New_Event | Animals | Include | Include | Wildlife | 573 | 2022-05-22 | 11460 | keep | 0 | May | 2022 | 0.0078054 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-22 06:29 | 2022-05-22 06:30 | 513 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO 20% POR 1118-10 | S22052200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 513 | keep | 0 | May | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-05-22 06:29 | 2022-05-22 06:30 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 20% DEL 1111-1 | S22052200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 2782 | keep | 0 | May | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
GUAYAMA | 2022-05-22 06:54 | 2022-05-22 08:03 | 8 | 001:09 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVE | P22052200008 | New_Event | Animals | Include | Include | Wildlife | 69 | 2022-05-22 | 552 | keep | 0 | May | 2022 | 0.00037596 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-05-22 06:54 | 2022-05-22 06:55 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 3744 | keep | 0 | May | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
SAN JUAN | 2022-05-22 07:00 | 2022-05-22 07:02 | 1500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO PARTE POR 1620-05 | S22052200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-22 | 3000 | keep | 0 | May | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-05-22 07:00 | 2022-05-22 07:02 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA PARTE 1206-3 | S22052200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-22 | 3230 | keep | 0 | May | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
HUMACAO | 2022-05-22 07:18 | 2022-05-22 10:18 | 100 | 003:00 | P | ANIMAL | 1 X 50 Y 1 X 30 EN CORTES DE LINEAS CRUCE POR AVE | C22052200043 | New_Event | Animals | Include | Include | Wildlife | 180 | 2022-05-22 | 18000 | keep | 0 | May | 2022 | 0.01226 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-22 07:21 | 2022-05-22 09:40 | 50 | 002:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR FUERTES VIENTOS | A22052200019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2022-05-22 | 6950 | keep | 0 | May | 2022 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-22 07:44 | 2022-05-22 12:15 | 30 | 004:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22052200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-05-22 | 8130 | keep | 0 | May | 2022 | 0.0055373 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-22 07:50 | 2022-05-22 07:51 | 125 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22052200047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 125 | keep | 0 | May | 2022 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-05-22 07:52 | 2022-05-22 07:54 | 2073 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M22052200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-22 | 4146 | keep | 0 | May | 2022 | 0.0028238 | 0.0014119 | Momentary | FALSE | FALSE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2022-05-22 07:52 | 2022-05-22 07:54 | 637 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M22052200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-22 | 1274 | keep | 0 | May | 2022 | 0.00086772 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-05-22 07:52 | 2022-05-22 07:54 | 1491 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M22052200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-22 | 2982 | keep | 0 | May | 2022 | 0.002031 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
BAYAMON | 2022-05-22 08:03 | 2022-05-22 08:04 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22052200040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 73 | keep | 0 | May | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
CAGUAS | 2022-05-22 08:05 | 2022-05-22 09:28 | 85 | 001:23 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22052200049 | New_Event | Animals | Include | Include | Wildlife | 83 | 2022-05-22 | 7055 | keep | 0 | May | 2022 | 0.0048051 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
ARECIBO | 2022-05-22 08:12 | 2022-05-22 10:50 | 120 | 002:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA POR PORTAFUSIBLES AVERIADOS | A22052200026 | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2022-05-22 | 18960 | keep | 0 | May | 2022 | 0.012914 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-05-22 08:14 | 2022-05-22 11:54 | 90 | 003:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M22052200014 | New_Event | Cutout Failure | Include | Include | Equipment | 220 | 2022-05-22 | 19800 | keep | 0 | May | 2022 | 0.013486 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-05-22 08:28 | 2022-05-22 09:55 | 80 | 001:27 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | R22052200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-05-22 | 6960 | keep | 0 | May | 2022 | 0.0047404 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-22 08:39 | 2022-05-22 08:40 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22052200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 863 | keep | 0 | May | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
FAJARDO | 2022-05-22 08:44 | 2022-05-22 14:36 | 1 | 005:52 | P | DESGANCHE | 1 X 30 EN C/L | R22052200066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2022-05-22 | 352 | keep | 0 | May | 2022 | 0.00023975 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-22 08:48 | 2022-05-22 10:17 | 65 | 001:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22052200055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-05-22 | 5785 | keep | 0 | May | 2022 | 0.0039401 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-05-22 09:02 | 2022-05-22 09:03 | 125 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22052200056 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 125 | keep | 0 | May | 2022 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-05-22 09:18 | 2022-05-23 11:20 | 100 | 026:02 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052200025 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1562 | 2022-05-22 | 156200 | keep | 0 | May | 2022 | 0.10639 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-05-22 09:22 | 2022-05-23 09:50 | 10 | 024:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA QUEMADA EN C/L | P22052200017 | New_Event | Cutout Failure | Include | Include | Equipment | 1468 | 2022-05-22 | 14680 | keep | 0 | May | 2022 | 0.0099985 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-22 09:42 | 2022-05-22 14:24 | 10 | 004:42 | P | SECUNDARIA/DESGANCHE | SE RETIRO ARBOL SOBRE LINEA, SE REMPLAZARON 150' DE ALAMBRE SECUNDARIO CALIBRE # 3/2 Y REMPLAZO TOMA DE SERVICIO DE UN CLIENTE | B22052200046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 282 | 2022-05-22 | 2820 | keep | 0 | May | 2022 | 0.0019207 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-22 09:52 | 2022-05-22 11:13 | 62 | 001:21 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22052200058 | New_Event | Animals | Include | Include | Wildlife | 81 | 2022-05-22 | 5022 | keep | 0 | May | 2022 | 0.0034205 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2022-05-22 10:04 | 2022-05-22 10:05 | 72 | 000:01 | P | ANIMAL | 1 X 50 EN PROVISIONAL AVE CRUZO FASE | B22052200034 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-22 | 72 | keep | 0 | May | 2022 | 4.9039e-05 | 4.9039e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 72
ARECIBO | 2022-05-22 11:06 | 2022-05-22 13:51 | 1 | 002:45 | P | DESGANCHE | 1 X 20 EN RISER SE RETIRO ENREDADERA | A22052200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-05-22 | 165 | keep | 0 | May | 2022 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-22 11:15 | 2022-05-22 11:30 | 3 | 000:15 | P | PROBLEMA DEL CLIENTE | SE ABRIO MH-14 PARA CONECTAR TOMA DE CLIENTE PROA | S22052200188 | New_Event | Customer-Related Interruption | Include | Include | Public | 15 | 2022-05-22 | 45 | keep | 0 | May | 2022 | 3.0649e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-05-22 12:22 | 2022-05-22 13:23 | 35 | 001:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22052200072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-05-22 | 2135 | keep | 0 | May | 2022 | 0.0014541 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-05-22 12:51 | 2022-05-22 17:22 | 50 | 004:31 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR RAYOS | A22052200059 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 271 | 2022-05-22 | 13550 | keep | 0 | May | 2022 | 0.0092288 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-22 12:59 | 2022-05-22 13:01 | 650 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A22052200060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-22 | 1300 | keep | 0 | May | 2022 | 0.00088542 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
SAN JUAN | 2022-05-22 13:26 | 2022-05-22 13:28 | 686 | 000:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22052200079 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-05-22 | 1372 | keep | 0 | May | 2022 | 0.00093446 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2022-05-22 13:28 | 2022-05-23 20:00 | 239 | 030:32 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ABIRENDO MACHETES PARA REEMPLAZO DE ALAMBRE PRIMARIO PARTIDO Y SE NORMALIZO 100% EN SERVICIO | S22052200083 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1832 | 2022-05-22 | 437848 | keep | 0 | May | 2022 | 0.29822 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
HUMACAO | 2022-05-22 13:29 | 2022-05-22 14:15 | 8 | 000:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22052200064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2022-05-22 | 368 | keep | 0 | May | 2022 | 0.00025064 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-05-22 13:33 | 2022-05-22 13:34 | 67 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22052200062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 67 | keep | 0 | May | 2022 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
UTUADO | 2022-05-22 13:34 | 2022-05-22 15:03 | 60 | 001:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | A22052200061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 89 | 2022-05-22 | 5340 | keep | 0 | May | 2022 | 0.003637 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-05-22 13:36 | 2022-05-22 14:49 | 1 | 001:13 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22052200051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-05-22 | 73 | keep | 0 | May | 2022 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-22 13:45 | 2022-05-22 21:35 | 7 | 007:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25KVA | A22052200064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 470 | 2022-05-22 | 3290 | keep | 0 | May | 2022 | 0.0022408 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-05-22 13:48 | 2022-05-22 16:18 | 6 | 002:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 15 EN TRANSFORMADOR POR LLUVIAS | A22052200065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 150 | 2022-05-22 | 900 | keep | 0 | May | 2022 | 0.00061299 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-05-22 13:51 | 2022-05-22 14:34 | 19 | 000:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO NEUTRAL EN BAJANTE DE XMER, SE SUBIERON TAPS DE XMER | B22052200052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2022-05-22 | 817 | keep | 0 | May | 2022 | 0.00055645 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2022-05-22 14:13 | 2022-05-22 19:08 | 30 | 004:55 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052200062 | New_Event | Primary Wire Break | Include | Include | Equipment | 295 | 2022-05-22 | 8850 | keep | 0 | May | 2022 | 0.0060277 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-22 14:14 | 2022-05-22 16:27 | 2 | 002:13 | P | SECUNDARIA/DESGANCHE | 1X10 EN XMER & SE LIMPIO ENRREDADERA EN EL POSTE | B22052200054 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 133 | 2022-05-22 | 266 | keep | 0 | May | 2022 | 0.00018117 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-05-22 14:16 | 2022-05-22 15:46 | 3 | 001:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR POR LLUVIAS | A22052200070 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 90 | 2022-05-22 | 270 | keep | 0 | May | 2022 | 0.0001839 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2022-05-22 14:18 | 2022-05-22 19:22 | 50 | 005:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A22052200071 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 304 | 2022-05-22 | 15200 | keep | 0 | May | 2022 | 0.010353 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-05-22 14:35 | 2022-05-22 19:18 | 30 | 004:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X40 EN C/L SE REMPLAZO AISLADOR PIN-POLE TOP | B22052200055 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 283 | 2022-05-22 | 8490 | keep | 0 | May | 2022 | 0.0057825 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-05-22 14:40 | 2022-05-22 15:40 | 1 | 001:00 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22052200068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-05-22 | 60 | keep | 0 | May | 2022 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-22 14:41 | 2022-05-22 14:42 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052200074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 3458 | keep | 0 | May | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2022-05-22 14:46 | 2022-05-23 11:20 | 150 | 020:34 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052200076 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1234 | 2022-05-22 | 185100 | keep | 0 | May | 2022 | 0.12607 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-05-22 14:48 | 2022-05-22 20:13 | 100 | 005:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | A22052200075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 325 | 2022-05-22 | 32500 | keep | 0 | May | 2022 | 0.022136 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-22 14:50 | 2022-05-23 00:12 | 200 | 009:22 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 Y 1 X 140 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052200079 | New_Event | Primary Wire Break | Include | Include | Equipment | 562 | 2022-05-22 | 112400 | keep | 0 | May | 2022 | 0.076555 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-05-22 14:52 | 2022-05-22 14:53 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052200025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 3744 | keep | 0 | May | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
AGUADILLA | 2022-05-22 14:54 | 2022-05-22 14:55 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052200083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 1827 | keep | 0 | May | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
MAYAGÃœEZ | 2022-05-22 14:58 | 2022-05-22 21:38 | 50 | 006:40 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | M22052200085 | New_Event | Primary Pole Failure | Include | Include | Equipment | 400 | 2022-05-22 | 20000 | keep | 0 | May | 2022 | 0.013622 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-05-22 15:02 | 2022-05-22 17:40 | 300 | 002:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22052200086 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2022-05-22 | 47400 | keep | 0 | May | 2022 | 0.032284 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
FAJARDO | 2022-05-22 15:05 | 2022-05-22 18:00 | 50 | 002:55 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | R22052200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-05-22 | 8750 | keep | 0 | May | 2022 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-22 15:10 | 2022-05-22 17:46 | 150 | 002:36 | P | DESGANCHE | 1X80 EN C/L, 2X50 EN RISER & 2X40 EN OTRO RISER & SE REALIZO DESGANCHE PRIMARIO | B22052200057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-05-22 | 23400 | keep | 0 | May | 2022 | 0.015938 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-05-22 15:24 | 2022-05-23 09:11 | 2 | 017:47 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22052200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1067 | 2022-05-22 | 2134 | keep | 0 | May | 2022 | 0.0014535 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-05-22 15:26 | 2022-05-22 20:04 | 100 | 004:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22052200083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 278 | 2022-05-22 | 27800 | keep | 0 | May | 2022 | 0.018934 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-22 15:27 | 2022-05-22 21:01 | 26 | 005:34 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S22052200105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 334 | 2022-05-22 | 8684 | keep | 0 | May | 2022 | 0.0059146 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CANOVANAS | 2022-05-22 15:29 | 2022-05-22 21:48 | 1 | 006:19 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 Y 1X 65 EN CORTES DE LINEA SE CERRO PUENTE DE LINEA A CAJA PRIMARIA | R22052200077 | New_Event | Primary Wire Break | Include | Include | Equipment | 379 | 2022-05-22 | 379 | keep | 0 | May | 2022 | 0.00025814 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-22 15:31 | 2022-05-23 09:53 | 60 | 018:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22052200088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1102 | 2022-05-22 | 66120 | keep | 0 | May | 2022 | 0.045034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-22 15:38 | 2022-05-22 15:39 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-5 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22052200108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 225 | keep | 0 | May | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-22 15:38 | 2022-05-22 15:39 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1303-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22052200108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2022-05-22 15:53 | 2022-05-22 15:54 | 4641 | 000:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | M22052200103 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-22 | 4641 | keep | 0 | May | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-05-22 15:54 | 2022-05-22 20:45 | 20 | 004:51 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22052200005 | 1st_after_momentary | Animals | Include | Include | Wildlife | 291 | 2022-05-22 | 5820 | keep | 0 | May | 2022 | 0.003964 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-22 16:05 | 2022-05-22 16:06 | 179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 179 | keep | 0 | May | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
BAYAMON | 2022-05-22 16:36 | 2022-05-22 18:25 | 12 | 001:49 | P | NO SE REPORTO CAUSA | 1X15 EN XMER | B22052200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-05-22 | 1308 | keep | 0 | May | 2022 | 0.00089087 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-22 17:00 | 2022-05-22 17:01 | 67 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22052200107 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 67 | keep | 0 | May | 2022 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-05-22 17:16 | 2022-05-22 18:15 | 3114 | 000:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE RETIRO PORCION DE LA PERILLA DEL POSTE QUE SE HABIA INCENDIADO & SE RELOCALIZO AISLADOR PIN-POLE TOP MEDIANTE G.O.I. BY-220522-01 | B22052200082 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 59 | 2022-05-22 | 183726 | keep | 0 | May | 2022 | 0.12513 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2022-05-22 17:21 | 2022-05-22 22:46 | 40 | 005:25 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | B22052200083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2022-05-22 | 13000 | keep | 0 | May | 2022 | 0.0088542 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-22 17:22 | 2022-05-22 17:23 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22052200113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 2697 | keep | 0 | May | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
UTUADO | 2022-05-22 17:23 | 2022-05-22 18:07 | 20 | 000:44 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA POR RAYOS | A22052200112 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 44 | 2022-05-22 | 880 | keep | 0 | May | 2022 | 0.00059936 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-05-22 17:37 | 2022-05-22 23:22 | 110 | 005:45 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA PRIMARIA DE CORTE DE LINEA | R22052200080 | New_Event | Primary Wire Break | Include | Include | Equipment | 345 | 2022-05-22 | 37950 | keep | 0 | May | 2022 | 0.025848 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
SAN JUAN | 2022-05-22 17:49 | 2022-05-24 09:17 | 25 | 039:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S22052200140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2368 | 2022-05-22 | 59200 | keep | 0 | May | 2022 | 0.040321 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-22 17:54 | 2022-05-22 17:55 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1909-08 | S22052200142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 2435 | keep | 0 | May | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-05-22 17:54 | 2022-05-22 17:55 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1907-05 | S22052200142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 2956 | keep | 0 | May | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-05-22 18:04 | 2022-05-22 18:06 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22052200128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-22 | 4468 | keep | 0 | May | 2022 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
AGUADILLA | 2022-05-22 18:11 | 2022-05-22 18:12 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052200128 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-22 | 1827 | keep | 0 | May | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BARRANQUITAS | 2022-05-22 18:11 | 2022-05-23 16:18 | 200 | 022:07 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA LEVANTAR CONDUCTOR | C22052200076 | New_Event | Primary Wire Break | Include | Include | Equipment | 1327 | 2022-05-22 | 265400 | keep | 0 | May | 2022 | 0.18076 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-22 18:14 | 2022-05-23 21:20 | 15 | 027:06 | P | CABLE SOTERRADO AVERIADO | SE INSTALO POSTE Y PROVISIONAL PARA DAR SERVICIO AL T-7 Y T-6 | B22052200133 | New_Event | UG Cable Fault | Include | Include | Equipment | 1626 | 2022-05-22 | 24390 | keep | 0 | May | 2022 | 0.016612 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-22 18:15 | 2022-05-22 20:22 | 1157 | 002:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE RETIRO PORCION DE LA PERILLA DEL POSTE QUE SE HABIA INCENDIADO & SE RELOCALIZO AISLADOR PIN-POLE TOP MEDIANTE G.O.I. BY-220522-01 | B22052200082 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 127 | 2022-05-22 | 146939 | keep | 0 | May | 2022 | 0.10008 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-05-22 18:43 | 2022-05-23 08:41 | 10 | 013:58 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | R22052200081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 838 | 2022-05-22 | 8380 | keep | 0 | May | 2022 | 0.0057076 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-22 18:50 | 2022-05-22 18:56 | 2999 | 000:06 | T | CAUSAS EXTERNAS | SE ABRIO INTERRUPTOR POR SEGURIDAD A PETICION DEL SUPERVISOR FELIX CASIANO PARA RETIRAR PELIGRO DE NEUTRAL PRIMARIO ROTO A PUNTO DE CRUZAR CON LA LINEA VIVA EN CARR 119 INT CARR 361 BO HOCONUCO SAN GERMAN CAUSADO POR MAQUINARIA | M22052200137 | New_Event | Damage From Public | Include | Include | Public | 6 | 2022-05-22 | 17994 | keep | 0 | May | 2022 | 0.012256 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
SAN JUAN | 2022-05-22 19:07 | 2022-05-22 20:21 | 4 | 001:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REMPLAZAR 65 PIES SECUNDARIA | S22052200087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 74 | 2022-05-22 | 296 | keep | 0 | May | 2022 | 0.0002016 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-05-22 19:19 | 2022-05-23 02:33 | 1 | 007:14 | P | ANIMAL | 1 X 20 EN CORTE DE LINEA CRUCE X AVE | C22052200081 | New_Event | Animals | Include | Include | Wildlife | 434 | 2022-05-22 | 434 | keep | 0 | May | 2022 | 0.0002956 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-22 19:22 | 2022-05-22 19:24 | 68 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 | S22052200165 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-22 | 136 | keep | 0 | May | 2022 | 9.2629e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-05-22 19:22 | 2022-05-22 19:24 | 171 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 | S22052200165 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-22 | 342 | keep | 0 | May | 2022 | 0.00023293 | 0.00011647 | Momentary | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-05-22 19:22 | 2022-05-22 19:24 | 1837 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 | S22052200165 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-22 | 3674 | keep | 0 | May | 2022 | 0.0025023 | 0.0012512 | Momentary | FALSE | FALSE | Not_TMED_Event | 1837
BAYAMON | 2022-05-22 19:22 | 2022-05-22 19:24 | 536 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 | S22052200165 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-22 | 1072 | keep | 0 | May | 2022 | 0.00073013 | 0.00036507 | Momentary | FALSE | FALSE | Not_TMED_Event | 536
BAYAMON | 2022-05-22 19:22 | 2022-05-22 19:24 | 348 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 | S22052200165 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-22 | 696 | keep | 0 | May | 2022 | 0.00047404 | 0.00023702 | Momentary | FALSE | FALSE | Not_TMED_Event | 348
BAYAMON | 2022-05-22 19:22 | 2022-05-23 08:54 | 300 | 013:32 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO SIN CARGA | B22052200176 | New_Event | Primary Wire Break | Include | Include | Equipment | 812 | 2022-05-22 | 243600 | keep | 0 | May | 2022 | 0.16591 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-05-22 19:32 | 2022-05-23 09:02 | 5 | 013:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052200160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 810 | 2022-05-22 | 4050 | keep | 0 | May | 2022 | 0.0027584 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-22 19:32 | 2022-05-23 09:54 | 40 | 014:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22052200159 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 862 | 2022-05-22 | 34480 | keep | 0 | May | 2022 | 0.023484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-22 19:35 | 2022-05-23 08:45 | 50 | 013:10 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052200132 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 790 | 2022-05-22 | 39500 | keep | 0 | May | 2022 | 0.026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-22 19:52 | 2022-05-23 10:33 | 90 | 014:41 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052200137 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 881 | 2022-05-22 | 79290 | keep | 0 | May | 2022 | 0.054004 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-05-22 19:55 | 2022-05-23 05:23 | 10 | 009:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIAS | A22052200138 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 568 | 2022-05-22 | 5680 | keep | 0 | May | 2022 | 0.0038686 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-22 20:26 | 2022-05-24 11:50 | 5 | 039:24 | P | OTRAS CAUSAS | 1 X 15 EN XMR. FUSIBLE CORROIDO | R22052200088 | New_Event | Other Causes | Include | Include | Other | 2364 | 2022-05-22 | 11820 | keep | 0 | May | 2022 | 0.0080505 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-05-22 20:48 | 2022-05-23 02:43 | 12 | 005:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | M22052200174 | New_Event | Secondary Wire Break | Include | Include | Equipment | 355 | 2022-05-22 | 4260 | keep | 0 | May | 2022 | 0.0029015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-22 20:49 | 2022-05-22 21:32 | 25 | 000:43 | P | SOBRECARGA | 1 X 30 EN CORTE DE LINEA EL JOURNEY LINEMAN INFORMO QUE LA CAUSA FUE POR SOBRECARGA | M22052200176 | New_Event | Trip Due To Overload | Include | Include | Other | 43 | 2022-05-22 | 1075 | keep | 0 | May | 2022 | 0.00073218 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-05-22 21:09 | 2022-05-23 03:00 | 50 | 005:51 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE REPARO ALAMBRE PRIMARIO PARTIDO | P22052200055 | New_Event | Primary Wire Break | Include | Include | Equipment | 351 | 2022-05-22 | 17550 | keep | 0 | May | 2022 | 0.011953 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-22 21:27 | 2022-05-23 15:15 | 1 | 017:48 | P | DESGANCHE | 1 X 100 EN C/L SE DESGANCHO | C22052200085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1068 | 2022-05-22 | 1068 | keep | 0 | May | 2022 | 0.00072741 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-22 21:30 | 2022-05-23 13:00 | 12 | 015:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR SE REMPLAZO CAJAS DEL TRANSFORMADOR | M22052200182 | New_Event | Cutout Failure | Include | Include | Equipment | 930 | 2022-05-22 | 11160 | keep | 0 | May | 2022 | 0.007601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-22 21:31 | 2022-05-23 17:57 | 25 | 020:26 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PARTIDO | M22052200085 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1226 | 2022-05-22 | 30650 | keep | 0 | May | 2022 | 0.020876 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-22 21:42 | 2022-05-23 11:37 | 74 | 013:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22052200222 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 835 | 2022-05-22 | 61790 | keep | 0 | May | 2022 | 0.042085 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
MAYAGÃœEZ | 2022-05-22 21:53 | 2022-05-23 00:06 | 100 | 002:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | M22052200059 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 133 | 2022-05-22 | 13300 | keep | 0 | May | 2022 | 0.0090586 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-22 22:22 | 2022-05-23 09:45 | 10 | 011:23 | P | DESGANCHE | DESGANCHE PRIMARIO Y 1 X 20 EN TRANSFORMADOR | S22052200201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 683 | 2022-05-22 | 6830 | keep | 0 | May | 2022 | 0.0046519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-05-22 22:33 | 2022-05-23 07:47 | 6 | 009:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REEMPLAZO PORTAFUSIBLE | C22052200086 | New_Event | Cutout Failure | Include | Include | Equipment | 554 | 2022-05-22 | 3324 | keep | 0 | May | 2022 | 0.002264 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-22 22:50 | 2022-05-23 11:56 | 10 | 013:06 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052200149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 786 | 2022-05-22 | 7860 | keep | 0 | May | 2022 | 0.0053534 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-23 00:04 | 2022-05-23 10:05 | 3766 | 010:01 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | INTERRUPTOR RECERRO 3 VECES SE PATRULLO NO SE ENCONTRO NADA. NO QUIZO CERRAR NI POR SCADA, NI EN LA SUBESTACION. SE TRANSFIRIO LA CARGA AL 2302-03 | R22052300002 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 601 | 2022-05-23 | 2263366 | keep | 0 | May | 2022 | 1.5416 | 0.002565 | Sustained | FALSE | FALSE | Not_TMED_Event | 3766
CANOVANAS | 2022-05-23 00:05 | 2022-05-23 03:26 | 539 | 003:21 | S | DESGANCHE | DISPARO MAIN BREAKER NO ESTA CARGANDO Y SE ENCONTRO UNA BAMBUA EN EL 2305-04 QUE LLEVA LA CARGA DEL 2306-02 | R22052300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-05-23 | 108339 | keep | 0 | May | 2022 | 0.073789 | 0.00036711 | Sustained | FALSE | FALSE | Not_TMED_Event | 539
CANOVANAS | 2022-05-23 00:05 | 2022-05-23 03:26 | 3012 | 003:21 | S | DESGANCHE | DISPARO MAIN BREAKER NO ESTA CARGANDO Y SE ENCONTRO UNA BAMBUA EN EL 2305-04 QUE LLEVA LA CARGA DEL 2306-02 | R22052300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-05-23 | 605412 | keep | 0 | May | 2022 | 0.41234 | 0.0020515 | Sustained | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2022-05-23 00:05 | 2022-05-23 03:26 | 2106 | 003:21 | S | DESGANCHE | DISPARO MAIN BREAKER NO ESTA CARGANDO Y SE ENCONTRO UNA BAMBUA EN EL 2305-04 QUE LLEVA LA CARGA DEL 2306-02 | R22052300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-05-23 | 423306 | keep | 0 | May | 2022 | 0.28831 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2022-05-23 00:05 | 2022-05-23 02:56 | 635 | 002:51 | S | DESGANCHE | DISPARO MAIN BREAKER NO ESTA CARGANDO Y SE ENCONTRO UNA BAMBUA EN EL 2305-04 QUE LLEVA LA CARGA DEL 2306-02 | R22052300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-05-23 | 108585 | keep | 0 | May | 2022 | 0.073957 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2022-05-23 00:05 | 2022-05-23 02:56 | 1380 | 002:51 | T | DESGANCHE | DISPARO SE ENCONTRO UNA BAMBUA EN EL 2305-04 QUE LLEVA SU CARGA | R22052300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-05-23 | 235980 | keep | 0 | May | 2022 | 0.16072 | 0.00093991 | Sustained | FALSE | FALSE | Not_TMED_Event | 1380
SAN JUAN | 2022-05-23 00:59 | 2022-05-23 01:00 | 676 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 80% DE SU CARGA | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 676 | keep | 0 | May | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
BAYAMON | 2022-05-23 01:02 | 2022-05-23 01:05 | 1715 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERUPTOR SE CERRO POR CONTROL CARGA POR EL 1708-03 | B22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-23 | 5145 | keep | 0 | May | 2022 | 0.0035042 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2022-05-23 01:02 | 2022-05-23 01:05 | 1498 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERUPTOR SE CERRO POR CONTROL LLEVA CARGA DEL 1708-02 | B22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-23 | 4494 | keep | 0 | May | 2022 | 0.0030608 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2022-05-23 01:12 | 2022-05-23 03:45 | 297 | 002:33 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1335-05 SE REALIZO DESGANCHE DE RAMA DE ARBOL DE MANGO SOBRE LINEA CON VARETA Y SE CERRO EL INTERRUPTOR 100% EN SERVICIO LLEVA 40% 1301-02 | S22052300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-05-23 | 45441 | keep | 0 | May | 2022 | 0.03095 | 0.00020229 | Sustained | FALSE | FALSE | Not_TMED_Event | 297
SAN JUAN | 2022-05-23 01:12 | 2022-05-23 03:45 | 314 | 002:33 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE DE RAMA DE ARBOL DE MANGO SOBRE LINEA CON BARETA Y SE CERRO EL INTERRUPTOR 100% EN SERVICIO LLEVA 40% 1301-02 | S22052300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-05-23 | 48042 | keep | 0 | May | 2022 | 0.032721 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
SAN JUAN | 2022-05-23 01:14 | 2022-05-23 01:15 | 676 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 80% DE SU CARGA | S22052300003 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 676 | keep | 0 | May | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
BAYAMON | 2022-05-23 01:21 | 2022-05-23 01:23 | 1860 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTTROL | S22052300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-23 | 3720 | keep | 0 | May | 2022 | 0.0025337 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
SAN JUAN | 2022-05-23 01:22 | 2022-05-23 01:24 | 36 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERURPTOR SE CERRO POR CONTROL CARGA POR EL 1620-03 | S22052300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-23 | 72 | keep | 0 | May | 2022 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-05-23 01:22 | 2022-05-23 01:24 | 1073 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERURPTOR SE CERRO POR CONTROL LLEVA EL 1620-01 | S22052300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-23 | 2146 | keep | 0 | May | 2022 | 0.0014616 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
BAYAMON | 2022-05-23 01:22 | 2022-05-23 01:25 | 2905 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTORL 50% POR EL 1716-03 | B22052300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-23 | 8715 | keep | 0 | May | 2022 | 0.0059357 | 0.0019786 | Momentary | FALSE | FALSE | Not_TMED_Event | 2905
BAYAMON | 2022-05-23 01:22 | 2022-05-23 01:25 | 1812 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 50% 1710-01 | B22052300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-23 | 5436 | keep | 0 | May | 2022 | 0.0037024 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
CAGUAS | 2022-05-23 01:23 | 2022-05-23 01:24 | 329 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 329 | keep | 0 | May | 2022 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
ARECIBO | 2022-05-23 01:23 | 2022-05-23 08:35 | 100 | 007:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22052300002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 432 | 2022-05-23 | 43200 | keep | 0 | May | 2022 | 0.029423 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-23 01:35 | 2022-05-23 10:13 | 87 | 008:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22052300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 518 | 2022-05-23 | 45066 | keep | 0 | May | 2022 | 0.030694 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
FAJARDO | 2022-05-23 01:40 | 2022-05-23 11:44 | 8 | 010:04 | P | SECUNDARIA/DESGANCHE | 1X10 EN XMER SE REALIZO DESGANCHE EN SECUNDARIA | R22052300087 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 604 | 2022-05-23 | 4832 | keep | 0 | May | 2022 | 0.0032911 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-23 01:49 | 2022-05-23 04:42 | 150 | 002:53 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S22052300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-05-23 | 25950 | keep | 0 | May | 2022 | 0.017674 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-05-23 02:01 | 2022-05-23 02:02 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2450 | keep | 0 | May | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
SAN JUAN | 2022-05-23 02:03 | 2022-05-23 02:04 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S22052300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2203 | keep | 0 | May | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2022-05-23 02:27 | 2022-05-23 02:28 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR 1909-08 | B22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2435 | keep | 0 | May | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-05-23 02:27 | 2022-05-23 02:28 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA DEL 1907-05 | B22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2956 | keep | 0 | May | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
SAN JUAN | 2022-05-23 02:29 | 2022-05-23 11:11 | 3046 | 008:42 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE PRIMARIO MEDIANTE G.O.I. SJ-220523-51 | R22052300114 | New_Event | Switch Failure | Include | Include | Equipment | 522 | 2022-05-23 | 1590012 | keep | 0 | May | 2022 | 1.0829 | 0.0020746 | Sustained | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-05-23 02:30 | 2022-05-23 02:33 | 858 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-02 SE CERRO POR CONTROL LLEVA 30% DEL 1204-04, 20% DEL 1206-04, 20% DEL 1204-02 | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-23 | 2574 | keep | 0 | May | 2022 | 0.0017531 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-23 02:30 | 2022-05-23 02:33 | 1483 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-02 SE CERRO POR CONTROL LLEVA 30% DEL 1204-04, 20% DEL 1206-04, 20% DEL 1204-02 | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-23 | 4449 | keep | 0 | May | 2022 | 0.0030302 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-23 02:30 | 2022-05-23 02:33 | 360 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-02 SE CERRO POR CONTROL LLEVA 30% DEL 1204-04, 20% DEL 1206-04, 20% DEL 1204-02 | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-23 | 1080 | keep | 0 | May | 2022 | 0.00073558 | 0.00024519 | Momentary | FALSE | FALSE | Not_TMED_Event | 360
SAN JUAN | 2022-05-23 02:30 | 2022-05-23 02:33 | 2335 | 000:03 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1303-02 SE CERRO POR CONTROL LLEVA 30% DEL 1204-04, 20% DEL 1204-02 PARTE POR 1206-04 | S22052300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-05-23 | 7005 | keep | 0 | May | 2022 | 0.0047711 | 0.0015904 | Momentary | FALSE | FALSE | Not_TMED_Event | 2335
SAN JUAN | 2022-05-23 02:33 | 2022-05-23 06:00 | 627 | 003:27 | P | DESGANCHE | DISPARO DE INTERRUPTOR POLE BREAKER 1303-02A SE RETIRO BAMBUA SOBRE LA LINEA Y SE CERRO POR SCADA | S22052300030 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-05-23 | 129789 | keep | 0 | May | 2022 | 0.088399 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
HUMACAO | 2022-05-23 02:33 | 2022-05-23 02:38 | 2126 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-05-23 | 10630 | keep | 0 | May | 2022 | 0.00724 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-05-23 02:38 | 2022-05-23 06:45 | 1 | 004:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | C22052200081 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 247 | 2022-05-23 | 247 | keep | 0 | May | 2022 | 0.00016823 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-23 03:26 | 2022-05-23 03:28 | 635 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SPARE 2306-03 LLEVANDO LA CARGA DEL 2305-04 Y 2306-02 | R22052300028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-23 | 1270 | keep | 0 | May | 2022 | 0.00086499 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2022-05-23 03:26 | 2022-05-23 03:28 | 1380 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SPARE 2306-03 QUE LLEVA EL 2305-04 Y 2306-02 | R22052300028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-23 | 2760 | keep | 0 | May | 2022 | 0.0018798 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
ARECIBO | 2022-05-23 03:42 | 2022-05-23 07:50 | 75 | 004:08 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052300003 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 248 | 2022-05-23 | 18600 | keep | 0 | May | 2022 | 0.012668 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-05-23 03:50 | 2022-05-23 03:51 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052300006 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2450 | keep | 0 | May | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
CAGUAS | 2022-05-23 04:35 | 2022-05-23 06:21 | 60 | 001:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22052300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-05-23 | 6360 | keep | 0 | May | 2022 | 0.0043318 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-23 05:06 | 2022-05-23 08:14 | 120 | 003:08 | P | ANIMAL | 2 X 100 EN CORTE DE LINEA CRUCE X AVE | C22052300009 | New_Event | Animals | Include | Include | Wildlife | 188 | 2022-05-23 | 22560 | keep | 0 | May | 2022 | 0.015366 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2022-05-23 05:12 | 2022-05-23 10:46 | 90 | 005:34 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C22052300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2022-05-23 | 30060 | keep | 0 | May | 2022 | 0.020474 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-05-23 05:15 | 2022-05-23 05:16 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 4188 | keep | 0 | May | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
PONCE | 2022-05-23 05:40 | 2022-05-23 05:41 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052300030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 3718 | keep | 0 | May | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2022-05-23 05:41 | 2022-05-23 10:31 | 50 | 004:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO SE REPORTO CAUSA | P22052300033 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 290 | 2022-05-23 | 14500 | keep | 0 | May | 2022 | 0.0098759 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-05-23 05:55 | 2022-05-23 08:30 | 40 | 002:35 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | R22052300234 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2022-05-23 | 6200 | keep | 0 | May | 2022 | 0.0042228 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-23 06:00 | 2022-05-23 06:02 | 858 | 000:02 | P | DESGANCHE | SE CERRO POR SCADA 1303-02. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. | S22052300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-23 | 1716 | keep | 0 | May | 2022 | 0.0011688 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-23 06:00 | 2022-05-23 06:02 | 1483 | 000:02 | P | DESGANCHE | SE CERRO POR SCADA 1303-02. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. | S22052300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-23 | 2966 | keep | 0 | May | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-05-23 06:00 | 2022-05-23 06:02 | 1681 | 000:02 | T | DESGANCHE | SE CERRO POR SCADA. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. SE RESETEO BANDERAS Y SE CERRO REMOTO. | S22052300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-23 | 3362 | keep | 0 | May | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-23 06:00 | 2022-05-23 06:02 | 2435 | 000:02 | T | DESGANCHE | SE CERRO POR SCADA. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. | S22052300000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-23 | 4870 | keep | 0 | May | 2022 | 0.0033169 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-23 06:00 | 2022-05-23 06:02 | 1598 | 000:02 | T | DESGANCHE | SE CERRO POR SCADA. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. SE RESETEO BANDERAS Y SE CERRO REMOTO. | S22052300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-23 | 3196 | keep | 0 | May | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-05-23 06:02 | 2022-05-23 06:30 | 627 | 000:28 | P | DESGANCHE | DISPARO DE INTERRUPTOR POLE BREAKER 1303-02A SE RETIRO BAMBUA SOBRE LA LINEA Y SE CERRO POR SCADA | S22052300030 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-05-23 | 17556 | keep | 0 | May | 2022 | 0.011957 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
VEGA BAJA | 2022-05-23 06:12 | 2022-05-23 08:54 | 18 | 002:42 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER | B22052300013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2022-05-23 | 2916 | keep | 0 | May | 2022 | 0.0019861 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-05-23 06:30 | 2022-05-23 06:31 | 858 | 000:01 | P | DESGANCHE | SE CERRO POR SCADA 1303-02. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. | S22052300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-23 | 858 | keep | 0 | May | 2022 | 0.00058438 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-23 06:30 | 2022-05-23 06:31 | 3460 | 000:01 | P | DESGANCHE | SE CERRO POR SCADA 1303-02. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. | S22052300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-23 | 3460 | keep | 0 | May | 2022 | 0.0023566 | 0.0023566 | Momentary | FALSE | FALSE | Not_TMED_Event | 3460
SAN JUAN | 2022-05-23 06:30 | 2022-05-23 06:43 | 1681 | 000:13 | T | DESGANCHE | SE CERRO POR SCADA. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. SE RESETEO BANDERAS Y SE CERRO REMOTO. | S22052300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 13 | 2022-05-23 | 21853 | keep | 0 | May | 2022 | 0.014884 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-23 06:30 | 2022-05-23 06:31 | 2435 | 000:01 | T | DESGANCHE | SE CERRO POR SCADA. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. | S22052300000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-23 | 2435 | keep | 0 | May | 2022 | 0.0016585 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-23 06:30 | 2022-05-23 06:43 | 1598 | 000:13 | T | DESGANCHE | SE CERRO POR SCADA. RELACIONADO A LA PRUEBA DEL POLE BREAKER EL CUAL PROBO MALO. SE RESETEO BANDERAS Y SE CERRO REMOTO. | S22052300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 13 | 2022-05-23 | 20774 | keep | 0 | May | 2022 | 0.014149 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2022-05-23 06:35 | 2022-05-23 17:14 | 8 | 010:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22052300014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 639 | 2022-05-23 | 5112 | keep | 0 | May | 2022 | 0.0034818 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-05-23 06:35 | 2022-05-24 12:26 | 5 | 029:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA @4 KV POR UNO DE 37.5 KVA @ 4KV | A22052300045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1791 | 2022-05-23 | 8955 | keep | 0 | May | 2022 | 0.0060992 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-05-23 06:38 | 2022-05-23 12:20 | 100 | 005:42 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22052300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2022-05-23 | 34200 | keep | 0 | May | 2022 | 0.023293 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-23 06:47 | 2022-05-23 11:40 | 100 | 004:53 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052300010 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 293 | 2022-05-23 | 29300 | keep | 0 | May | 2022 | 0.019956 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-23 06:53 | 2022-05-23 11:30 | 30 | 004:37 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052300012 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 277 | 2022-05-23 | 8310 | keep | 0 | May | 2022 | 0.0056599 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-23 07:06 | 2022-05-23 07:07 | 2466 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2466 | keep | 0 | May | 2022 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
ARECIBO | 2022-05-23 07:09 | 2022-05-23 10:35 | 10 | 003:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22052300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2022-05-23 | 2060 | keep | 0 | May | 2022 | 0.0014031 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-23 07:17 | 2022-05-23 14:43 | 539 | 007:26 | T | POWER TRANSFORMER AVERIADO | REMPLAZO BUSHING DE LA BAJA DEL TRANSFORMADOR DE LA PORTATIL #20 POR DERRAME DE ACEITE | R22052300028 | New_Event | Power Transformer Failure | Include | Include | Equipment | 446 | 2022-05-23 | 240394 | keep | 0 | May | 2022 | 0.16373 | 0.00036711 | Sustained | FALSE | FALSE | Not_TMED_Event | 539
GUAYAMA | 2022-05-23 07:17 | 2022-05-23 09:15 | 50 | 001:58 | P | ANIMAL | 1 X 80 EN C/L AVE CRUZO LINEAS | P22052300043 | New_Event | Animals | Include | Include | Wildlife | 118 | 2022-05-23 | 5900 | keep | 0 | May | 2022 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-05-23 07:18 | 2022-05-23 07:56 | 3012 | 000:38 | T | POWER TRANSFORMER AVERIADO | REMPLAZO BUSHING DE LA BAJA DEL TRANSFORMADOR DE LA PORTATIL #20 POR DERRAME DE ACEITE SE TRANSFIRIO AL 2005-10 | R22052300028 | New_Event | Power Transformer Failure | Include | Include | Equipment | 38 | 2022-05-23 | 114456 | keep | 0 | May | 2022 | 0.077955 | 0.0020515 | Sustained | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2022-05-23 07:18 | 2022-05-23 14:45 | 2106 | 7:27 | T | POWER TRANSFORMER AVERIADO | REMPLAZO BUSHING DE LA BAJA DEL TRANSFORMADOR DE LA PORTATIL #20 POR DERRAME DE ACEITE | R22052300028 | New_Event | Power Transformer Failure | Include | Include | Equipment | 447 | 2022-05-23 | 941382 | keep | 0 | May | 2022 | 0.64117 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2022-05-23 07:18 | 2022-05-23 07:56 | 635 | 0:38 | T | POWER TRANSFORMER AVERIADO | REMPLAZO BUSHING DE LA BAJA DEL TRANSFORMADOR DE LA PORTATIL #20 POR DERRAME DE ACEITE SE TRANSFIRIO AL 2005-10 A TRAVES DEL 2305-02 | R22052300028 | New_Event | Power Transformer Failure | Include | Include | Equipment | 38 | 2022-05-23 | 24130 | keep | 0 | May | 2022 | 0.016435 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2022-05-23 07:18 | 2022-05-23 07:56 | 1380 | 0:38 | T | POWER TRANSFORMER AVERIADO | REMPLAZO BUSHING DE LA BAJA DEL TRANSFORMADOR DE LA PORTATIL #20 POR DERRAME DE ACEITE SE TRANSFIRIO AL 2005-10 A TRAVES DEL 2305-02 | R22052300028 | New_Event | Power Transformer Failure | Include | Include | Equipment | 38 | 2022-05-23 | 52440 | keep | 0 | May | 2022 | 0.035717 | 0.00093991 | Sustained | FALSE | FALSE | Not_TMED_Event | 1380
CAGUAS | 2022-05-23 07:21 | 2022-05-23 11:24 | 65 | 004:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | C22052300026 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 243 | 2022-05-23 | 15795 | keep | 0 | May | 2022 | 0.010758 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-05-23 07:32 | 2022-05-23 07:33 | 2067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22052300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2067 | keep | 0 | May | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
SAN JUAN | 2022-05-23 07:37 | 2022-05-23 17:26 | 17 | 009:49 | P | DESGANCHE | 2 X 25 EN C/L Y 1 X 40 EN C/L SE DESGANCHO | S22052300179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 589 | 2022-05-23 | 10013 | keep | 0 | May | 2022 | 0.0068198 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2022-05-23 07:39 | 2022-05-23 07:40 | 1250 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22052300028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1250 | keep | 0 | May | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
CANOVANAS | 2022-05-23 07:40 | 2022-05-23 07:41 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2708 | keep | 0 | May | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
UTUADO | 2022-05-23 07:49 | 2022-05-23 17:30 | 4 | 009:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 15KVA POR 37.5KVA SE SUBIO LA CAPACIDAD PORQUE NO HABIAN DISPONIBLES DE LA MISMA CAPACIDAD O DE 25KVA | A22052300018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 581 | 2022-05-23 | 2324 | keep | 0 | May | 2022 | 0.0015829 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-05-23 07:53 | 2022-05-23 14:15 | 9 | 006:22 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER PERSONAL NO IDENTIFICO CAUSA | M22052300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 382 | 2022-05-23 | 3438 | keep | 0 | May | 2022 | 0.0023416 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-05-23 07:53 | 2022-05-23 10:26 | 3 | 002:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO | A22052300020 | New_Event | Primary Wire Break | Include | Include | Equipment | 153 | 2022-05-23 | 459 | keep | 0 | May | 2022 | 0.00031262 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-05-23 07:58 | 2022-05-23 07:59 | 1403 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22052300031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1403 | keep | 0 | May | 2022 | 0.00095558 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
GUAYAMA | 2022-05-23 08:08 | 2022-05-23 08:45 | 30 | 000:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA QUEMADA EN C/L | P22052300056 | New_Event | Cutout Failure | Include | Include | Equipment | 37 | 2022-05-23 | 1110 | keep | 0 | May | 2022 | 0.00075602 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-23 08:48 | 2022-05-23 08:49 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22052300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2708 | keep | 0 | May | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CAGUAS | 2022-05-23 08:48 | 2022-05-23 12:22 | 90 | 003:34 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | C22052300038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2022-05-23 | 19260 | keep | 0 | May | 2022 | 0.013118 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-05-23 08:52 | 2022-05-23 08:53 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22052300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2708 | keep | 0 | May | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
BAYAMON | 2022-05-23 08:54 | 2022-05-23 11:06 | 1834 | 002:12 | S | PROTECCION DEFECTUOSA | 1 X 175 E STD EN ALTA DE XMR 9203-00 SE ENCONTRO PROTECCION DEL 9203-02 MEDIA SUELTA SE AJUSTO Y SE NORMALIZO CARGAS | B22052300116 | New_Event | Protection Miscoordination | Include | Include | Other | 132 | 2022-05-23 | 242088 | keep | 0 | May | 2022 | 0.16489 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2022-05-23 08:54 | 2022-05-23 11:06 | 2324 | 002:12 | S | PROTECCION DEFECTUOSA | 1 X 175 E STD EN ALTA DE XMR 9203-00 SE ENCONTRO PROTECCION DEL 9203-02 MEDIA SUELTA SE AJUSTO Y SE NORMALIZO CARGAS | B22052300116 | New_Event | Protection Miscoordination | Include | Include | Other | 132 | 2022-05-23 | 306768 | keep | 0 | May | 2022 | 0.20894 | 0.0015829 | Sustained | FALSE | FALSE | Not_TMED_Event | 2324
VEGA BAJA | 2022-05-23 08:54 | 2022-05-23 11:06 | 1570 | 002:12 | S | PROTECCION DEFECTUOSA | 1 X 175 E STD EN ALTA DE XMR 9203-00 SE ENCONTRO PROTECCION DEL 9203-02 MEDIA SUELTA SE AJUSTO Y SE NORMALIZO CARGAS | B22052300116 | New_Event | Protection Miscoordination | Include | Include | Other | 132 | 2022-05-23 | 207240 | keep | 0 | May | 2022 | 0.14115 | 0.0010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 1570
SAN JUAN | 2022-05-23 08:56 | 2022-05-23 14:40 | 45 | 005:44 | P | DESGANCHE | 1X80 EN C/L | S22052300195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2022-05-23 | 15480 | keep | 0 | May | 2022 | 0.010543 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-05-23 09:02 | 2022-05-23 09:03 | 552 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04. LLEVA LA CARGAS PARCIALES DE 20% 1303-02, 40% 1204-04, 60% 1204-03. | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 552 | keep | 0 | May | 2022 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2022-05-23 09:02 | 2022-05-23 09:03 | 2966 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04. LLEVA LA CARGAS PARCIALES DE 20% 1303-02, 40% 1204-04, 60% 1204-03. | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2966 | keep | 0 | May | 2022 | 0.0020201 | 0.0020201 | Momentary | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2022-05-23 09:02 | 2022-05-23 09:03 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04. LLEVA LA CARGAS PARCIALES DE 20% 1303-02, 40% 1204-04, 60% 1204-03. | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1799 | keep | 0 | May | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-23 09:02 | 2022-05-23 09:03 | 1948 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04. LLEVA LA CARGAS PARCIALES DE 20% 1303-02, 40% 1204-04, 60% 1204-03. | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1948 | keep | 0 | May | 2022 | 0.0013268 | 0.0013268 | Momentary | FALSE | FALSE | Not_TMED_Event | 1948
UTUADO | 2022-05-23 09:29 | 2022-05-23 15:30 | 2 | 006:01 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052300032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 361 | 2022-05-23 | 722 | keep | 0 | May | 2022 | 0.00049175 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-05-23 09:41 | 2022-05-23 18:25 | 60 | 008:44 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22052300047 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 524 | 2022-05-23 | 31440 | keep | 0 | May | 2022 | 0.021414 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-05-23 09:42 | 2022-05-23 12:44 | 50 | 003:02 | P | DESGANCHE | 1 X 65 EN C/L RAMA | B22052300136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-05-23 | 9100 | keep | 0 | May | 2022 | 0.006198 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-23 09:47 | 2022-05-23 18:50 | 6 | 009:03 | P | TERMINACION SOTERRADA AVERIADA | 1 X 15 EN RISER SE REMPLAZO PISTOLA | C22052300051 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 543 | 2022-05-23 | 3258 | keep | 0 | May | 2022 | 0.002219 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-05-23 09:50 | 2022-05-23 12:32 | 210 | 002:42 | P | ANIMAL | 1 X 65, 1 X 80 Y 1 X 100 EN CORTES DE LINEAS CRUCE POR AVE | C22052300053 | New_Event | Animals | Include | Include | Wildlife | 162 | 2022-05-23 | 34020 | keep | 0 | May | 2022 | 0.023171 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
HUMACAO | 2022-05-23 10:00 | 2022-05-23 16:25 | 30 | 006:25 | P | ANIMAL | 1 X 40 EN C/L SE RETIRO AVE | C22052300057 | New_Event | Animals | Include | Include | Wildlife | 385 | 2022-05-23 | 11550 | keep | 0 | May | 2022 | 0.0078667 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-23 10:01 | 2022-05-23 14:31 | 25 | 004:30 | P | TRANSFORMADOR AVERIADO | REEEMPLAZO DE TRANSFORMADOR POR DERRAME | S22052300210 | New_Event | Service Transformer Failure | Include | Include | Equipment | 270 | 2022-05-23 | 6750 | keep | 0 | May | 2022 | 0.0045974 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-23 10:05 | 2022-05-23 12:03 | 5 | 001:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE | B22052300152 | New_Event | Secondary Wire Break | Include | Include | Equipment | 118 | 2022-05-23 | 590 | keep | 0 | May | 2022 | 0.00040185 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-05-23 10:10 | 2022-05-23 11:28 | 1681 | 001:18 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-01 QUE A SU VEZ LLEVA LA CARGA DEL 1346-06. SE ABRIO MACHETES EN CAMINO LUIS VIGOREAUX Y SE CERRO INTERRUPTOR POR SCADA | S22052300226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-05-23 | 131118 | keep | 0 | May | 2022 | 0.089304 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-23 10:10 | 2022-05-23 11:28 | 1598 | 001:18 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-01 QUE A SU VEZ LLEVA LA CARGA DEL 1346-06. SE ABRIO MACHETES EN CAMINO LUIS VIGOREAUX Y SE CERRO INTERRUPTOR POR SCADA | S22052300226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-05-23 | 124644 | keep | 0 | May | 2022 | 0.084894 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
HUMACAO | 2022-05-23 10:12 | 2022-05-23 13:27 | 11 | 003:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22052300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2022-05-23 | 2145 | keep | 0 | May | 2022 | 0.0014609 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-05-23 10:14 | 2022-05-24 10:12 | 58 | 023:58 | P | ARBOL SOBRE LINEA | 1X40 EN C/L MONOFASICO, SE REMOVIO ARBOL (COMPLETO) DE LA PRIMARIA & SE REPARO TRAMO SECUNDARIO | C22052300062 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1438 | 2022-05-23 | 83404 | keep | 0 | May | 2022 | 0.056806 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
CAGUAS | 2022-05-23 10:22 | 2022-05-23 15:10 | 30 | 004:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO TRAMO SECUNDARIO | C22052100037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 288 | 2022-05-23 | 8640 | keep | 0 | May | 2022 | 0.0058847 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-23 10:25 | 2022-05-23 11:10 | 635 | 0:45 | T | POWER TRANSFORMER AVERIADO | REMPLAZO BUSHING DE LA BAJA DEL TRANSFORMADOR DE LA PORTATIL #20 POR DERRAME DE ACEITE SE TRANSFIRIO AL 2306-01 A SU VEZ POR 2302-03 | R22052300028 | New_Event | Power Transformer Failure | Include | Include | Equipment | 45 | 2022-05-23 | 28575 | keep | 0 | May | 2022 | 0.019462 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2022-05-23 10:25 | 2022-05-23 11:10 | 1380 | 0:45 | T | POWER TRANSFORMER AVERIADO | SE TRANSFIRIO AL 2306-01 A SU VEZ POR 2302-03 POR AVERIA EN PORTATIL #20 | R22052300028 | New_Event | Power Transformer Failure | Include | Include | Equipment | 45 | 2022-05-23 | 62100 | keep | 0 | May | 2022 | 0.042296 | 0.00093991 | Sustained | FALSE | FALSE | Not_TMED_Event | 1380
UTUADO | 2022-05-23 10:31 | 2022-05-23 14:30 | 120 | 003:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN DOS TRANSFORMADORES Y 2 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A22052300039 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 239 | 2022-05-23 | 28680 | keep | 0 | May | 2022 | 0.019534 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-05-23 10:39 | 2022-05-23 14:12 | 3432 | 003:33 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR LLEVA SOLO EL 80% DE SU CARGA. SE ABRIO MACHETES PARA PROBAR TRAMO 3% EN SERVICIO | S22052300246 | New_Event | Primary Wire Break | Include | Include | Equipment | 213 | 2022-05-23 | 731016 | keep | 0 | May | 2022 | 0.49789 | 0.0023375 | Sustained | FALSE | FALSE | Not_TMED_Event | 3432
CAGUAS | 2022-05-23 10:40 | 2022-05-23 11:19 | 15 | 000:39 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR PARA REPARAR SECUNDARIA CRUZADA | C22052300034 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 39 | 2022-05-23 | 585 | keep | 0 | May | 2022 | 0.00039844 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-23 10:45 | 2022-05-23 12:45 | 553 | 002:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1204-01 LLEVANDO EL 40% 1204-03. EL 1204-01 ES SPARE. SE SECCIONALIZO ENTRANDO 90% EN SERVICIO | S22052300246 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 120 | 2022-05-23 | 66360 | keep | 0 | May | 2022 | 0.045197 | 0.00037665 | Sustained | FALSE | FALSE | Not_TMED_Event | 553
ARECIBO | 2022-05-23 10:48 | 2022-05-23 11:50 | 150 | 001:02 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052300041 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 62 | 2022-05-23 | 9300 | keep | 0 | May | 2022 | 0.0063342 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-05-23 10:52 | 2022-05-23 11:19 | 4 | 000:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REGULO XMR Y SE REPARO BAJANTE SECUNDARARIO | P22052300096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2022-05-23 | 108 | keep | 0 | May | 2022 | 7.3558e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-05-23 10:56 | 2022-05-23 12:09 | 55 | 001:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22052300071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-05-23 | 4015 | keep | 0 | May | 2022 | 0.0027346 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2022-05-23 11:02 | 2022-05-23 13:58 | 1 | 002:56 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA | C22052300072 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 176 | 2022-05-23 | 176 | keep | 0 | May | 2022 | 0.00011987 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-23 11:06 | 2022-05-23 15:25 | 300 | 004:19 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO SIN CARGA | B22052200176 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 259 | 2022-05-23 | 77700 | keep | 0 | May | 2022 | 0.052921 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-05-23 11:06 | 2022-05-23 16:03 | 18 | 004:57 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER | B22052300013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2022-05-23 | 5346 | keep | 0 | May | 2022 | 0.0036411 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-05-23 11:11 | 2022-05-23 11:13 | 353 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22052300277 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-23 | 706 | keep | 0 | May | 2022 | 0.00048085 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
SAN JUAN | 2022-05-23 11:11 | 2022-05-23 12:51 | 305 | 001:40 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE PRIMARIO MEDIANTE G.O.I. SJ-220523-51 | R22052300114 | New_Event | Switch Failure | Include | Include | Equipment | 100 | 2022-05-23 | 30500 | keep | 0 | May | 2022 | 0.020773 | 0.00020773 | Sustained | FALSE | FALSE | Not_TMED_Event | 305
FAJARDO | 2022-05-23 11:21 | 2022-05-24 21:00 | 20 | 033:39 | P | CABLE SOTERRADO AVERIADO | CONSTRUIR AEREO PROVICIONAL EN TRAMO RADIAL PARA ENERGIZAR T-7 AL T-6 | R22052301028 | New_Event | UG Cable Fault | Include | Include | Equipment | 2019 | 2022-05-23 | 40380 | keep | 0 | May | 2022 | 0.027503 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-23 11:28 | 2022-05-23 11:45 | 420 | 000:17 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | S22052300226 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 17 | 2022-05-23 | 7140 | keep | 0 | May | 2022 | 0.004863 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-23 11:28 | 2022-05-25 12:49 | 1 | 049:21 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO DE 10 KVA X 37.5 KVA | C22052300079 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2961 | 2022-05-23 | 2961 | keep | 0 | May | 2022 | 0.0020167 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-23 11:32 | 2022-05-23 11:33 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 225 | keep | 0 | May | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-23 11:32 | 2022-05-23 11:33 | 870 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S22052300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-23 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2022-05-23 11:32 | 2022-05-23 14:53 | 10 | 003:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR LLUVIAS | M22052300068 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 201 | 2022-05-23 | 2010 | keep | 0 | May | 2022 | 0.001369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 858 | 000:01 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 CARGA DEL 1204-02 A TRAVES DEL 1303-02 UN 20%. | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 858 | keep | 0 | May | 2022 | 0.00058438 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 3460 | 000:01 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 CARGA DEL 1204-04 A TRAVES DEL 1303-02 UN 30%. | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 3460 | keep | 0 | May | 2022 | 0.0023566 | 0.0023566 | Momentary | FALSE | FALSE | Not_TMED_Event | 3460
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 108 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 108 | keep | 0 | May | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 1368 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 1368 | keep | 0 | May | 2022 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 2064 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 2064 | keep | 0 | May | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 1681 | 000:01 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 CARGA DEL 1346-06 ATRAVES DEL 1303-04. LA INTERRUPCION ES PARCIAL DEBIDO A LA AVERIA QUE EXISTENTE DEL 1303-01 | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 1681 | keep | 0 | May | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 2435 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 2435 | keep | 0 | May | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 726 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 726 | keep | 0 | May | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 225 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 225 | keep | 0 | May | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 870 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 3932 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 CARGA DEL 1346-04 A TRAVES DEL 1303-03. | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 3932 | keep | 0 | May | 2022 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2022-05-23 11:45 | 2022-05-23 11:46 | 1598 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 CARGA DEL 1346-06 ATRAVES DEL 1303-04 | S22052300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 1598 | keep | 0 | May | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-05-23 11:46 | 2022-05-23 13:04 | 420 | 001:18 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | S22052300226 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-05-23 | 32760 | keep | 0 | May | 2022 | 0.022313 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-23 11:54 | 2022-05-23 14:30 | 1 | 002:36 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR | C22052300083 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 156 | 2022-05-23 | 156 | keep | 0 | May | 2022 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-23 11:58 | 2022-05-23 14:00 | 50 | 002:02 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | C22052300085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-05-23 | 6100 | keep | 0 | May | 2022 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-23 12:00 | 2022-05-23 12:03 | 870 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C22052300086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-23 | 2610 | keep | 0 | May | 2022 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2022-05-23 12:17 | 2022-05-23 15:40 | 22 | 003:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO | B22052300182 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 203 | 2022-05-23 | 4466 | keep | 0 | May | 2022 | 0.0030418 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
FAJARDO | 2022-05-23 12:18 | 2022-05-23 13:52 | 10 | 001:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X10 EN XMER & SE REMPLAZO PORTAFUSIBLE | R22052300784 | New_Event | Cutout Failure | Include | Include | Equipment | 94 | 2022-05-23 | 940 | keep | 0 | May | 2022 | 0.00064023 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-05-23 12:23 | 2022-05-23 14:45 | 20 | 002:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE RELOCALIZO LINEA SECUNDARIA A POSTE NUEVO | P22052300116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 142 | 2022-05-23 | 2840 | keep | 0 | May | 2022 | 0.0019343 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-05-23 12:25 | 2022-05-23 16:20 | 7 | 003:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES EN LINEA SECUNDARIA | P22052300117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 235 | 2022-05-23 | 1645 | keep | 0 | May | 2022 | 0.0011204 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-05-23 12:27 | 2022-05-23 12:28 | 225 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S22052300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-23 | 225 | keep | 0 | May | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-23 12:27 | 2022-05-23 12:28 | 870 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S22052300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-23 | 870 | keep | 0 | May | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-05-23 12:30 | 2022-05-23 16:48 | 225 | 004:18 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-05 SE TRABAJO CONDICION DE DESGANCHE Y 2 AISLADORES QUEMADOS. SE CERRO POR CONTROL 95% EN SERVICIO DEL 1303-04 | S22052300337 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 258 | 2022-05-23 | 58050 | keep | 0 | May | 2022 | 0.039538 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-05-23 12:30 | 2022-05-23 14:07 | 870 | 001:37 | T | DESGANCHE | SE DISPARO BKR LLEVA EL 1303-04 | S22052300337 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-05-23 | 84390 | keep | 0 | May | 2022 | 0.057478 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
FAJARDO | 2022-05-23 12:32 | 2022-05-23 15:18 | 60 | 002:46 | P | NO SE REPORTO CAUSA | 1X100 EN C/L PRINCIPAL & 1X65 EN RISER | R22052300803 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-05-23 | 9960 | keep | 0 | May | 2022 | 0.0067837 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-23 12:35 | 2022-05-23 16:30 | 200 | 003:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22052300091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2022-05-23 | 47000 | keep | 0 | May | 2022 | 0.032011 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-05-23 12:40 | 2022-05-23 13:01 | 50 | 000:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L & SE REMPLAZO PORTAFUSIBLE | R22052300814 | New_Event | Cutout Failure | Include | Include | Equipment | 21 | 2022-05-23 | 1050 | keep | 0 | May | 2022 | 0.00071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-23 12:45 | 2022-05-23 16:58 | 178 | 004:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO PARA REEMPLAZAR ASILADOR EN PIN POLE TOP PARTIDO Y POSTE PARTIDO 99% ENTRO EN SERVICIO SOLO QUEDA FUERA 1 XMR Y 1 BOMBAS AAA | S22052300246 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 253 | 2022-05-23 | 45034 | keep | 0 | May | 2022 | 0.030672 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-23 12:49 | 2022-05-23 14:40 | 40 | 001:51 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | M22052300077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-05-23 | 4440 | keep | 0 | May | 2022 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-23 12:51 | 2022-05-23 13:46 | 3046 | 000:55 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE PRIMARIO MEDIANTE G.O.I. SJ-220523-51 | R22052300114 | Additional_clients | Switch Failure | Include | Include | Equipment | 55 | 2022-05-23 | 167530 | keep | 0 | May | 2022 | 0.1141 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-23 12:51 | 2022-05-23 12:52 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22052300824 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
ARECIBO | 2022-05-23 12:51 | 2022-05-23 12:52 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 1 | keep | 0 | May | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-05-23 12:51 | 2022-05-23 12:52 | 2266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 2266 | keep | 0 | May | 2022 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2022-05-23 12:51 | 2022-05-23 12:52 | 1399 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-23 | 1399 | keep | 0 | May | 2022 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
ARECIBO | 2022-05-23 12:51 | 2022-05-23 15:00 | 30 | 002:09 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA GLOBO CRUZO FASE A TIERRA | A22052300060 | New_Event | Damage From Public | Include | Include | Public | 129 | 2022-05-23 | 3870 | keep | 0 | May | 2022 | 0.0026358 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-23 12:52 | 2022-05-23 12:53 | 3511 | 000:01 | T | DESGANCHE | RECIERRE | B22052300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-23 | 3511 | keep | 0 | May | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2022-05-23 12:55 | 2022-05-23 12:56 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 4176 | keep | 0 | May | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 1253 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 62650 | keep | 0 | May | 2022 | 0.042671 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 1266 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 63300 | keep | 0 | May | 2022 | 0.043113 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 411 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 20550 | keep | 0 | May | 2022 | 0.013997 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 1617 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 80850 | keep | 0 | May | 2022 | 0.055067 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 1017 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 50850 | keep | 0 | May | 2022 | 0.034634 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 828 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 41400 | keep | 0 | May | 2022 | 0.028197 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 863 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 43150 | keep | 0 | May | 2022 | 0.029389 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 309 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 15450 | keep | 0 | May | 2022 | 0.010523 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 176 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 8800 | keep | 0 | May | 2022 | 0.0059936 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-23 12:58 | 2022-05-23 13:48 | 974 | 000:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-05-23 | 48700 | keep | 0 | May | 2022 | 0.033169 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
BAYAMON | 2022-05-23 12:59 | 2022-05-23 14:37 | 3511 | 001:38 | T | DESGANCHE | SE SECCIONALIZO EN LOS PALACIOS Y SE CERRO POR SCADA BY-220523-02 | B22052300187 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 98 | 2022-05-23 | 344078 | keep | 0 | May | 2022 | 0.23435 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
MAYAGÃœEZ | 2022-05-23 13:00 | 2022-05-23 16:33 | 100 | 003:33 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA POR AVE | M22052300084 | New_Event | Animals | Include | Include | Wildlife | 213 | 2022-05-23 | 21300 | keep | 0 | May | 2022 | 0.014507 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-23 13:08 | 2022-05-23 15:38 | 30 | 002:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22052300066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-05-23 | 4500 | keep | 0 | May | 2022 | 0.0030649 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-23 13:10 | 2022-05-23 13:11 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22052300098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1702 | keep | 0 | May | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
AGUADILLA | 2022-05-23 13:12 | 2022-05-23 15:48 | 2366 | 002:36 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO Y SE CERRO INTERRUPTOR | M22052300134 | New_Event | Primary Wire Break | Include | Include | Equipment | 156 | 2022-05-23 | 369096 | keep | 0 | May | 2022 | 0.25139 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2022-05-23 13:25 | 2022-05-23 16:44 | 12 | 003:19 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22052300072 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 199 | 2022-05-23 | 2388 | keep | 0 | May | 2022 | 0.0016265 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-23 13:26 | 2022-05-23 13:27 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | M22052300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1287 | keep | 0 | May | 2022 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
BARRANQUITAS | 2022-05-23 13:27 | 2022-05-23 18:06 | 70 | 004:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L SE REPORTAN FUERTES VIENTOS | C22052300101 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 279 | 2022-05-23 | 19530 | keep | 0 | May | 2022 | 0.013302 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-05-23 13:45 | 2022-05-23 13:46 | 128 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 3009-02 LLEVANDO LA CARGA DEL 3009-03 Y 3009-04 | C22052300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 128 | keep | 0 | May | 2022 | 8.718e-05 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2022-05-23 13:45 | 2022-05-23 13:46 | 273 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 3009-02 LLEVANDO LA CARGA DEL 3009-03 Y 3009-04 | C22052300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 273 | keep | 0 | May | 2022 | 0.00018594 | 0.00018594 | Momentary | FALSE | FALSE | Not_TMED_Event | 273
CAGUAS | 2022-05-23 13:45 | 2022-05-23 13:46 | 1772 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 3009-02 LLEVANDO LA CARGA DEL 3009-03 Y 3009-04 | C22052300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1772 | keep | 0 | May | 2022 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
UTUADO | 2022-05-23 13:46 | 2022-05-23 18:50 | 65 | 005:04 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CONVERTIDOR POR DESCARGAS ELECTRICAS | A22052300075 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 304 | 2022-05-23 | 19760 | keep | 0 | May | 2022 | 0.013458 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-05-23 13:47 | 2022-05-23 16:19 | 80 | 002:32 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22052300076 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 152 | 2022-05-23 | 12160 | keep | 0 | May | 2022 | 0.0082821 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-23 13:48 | 2022-05-23 20:09 | 517 | 006:21 | P | CONDUCTOR ROTO O ABIERTO | 2 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M22052100219 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 381 | 2022-05-23 | 196977 | keep | 0 | May | 2022 | 0.13416 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-23 13:57 | 2022-05-23 16:30 | 100 | 002:33 | P | NO SE REPORTO CAUSA | 1X80 EN C/L & 1X65 EN OTRO C/L | R22052300887 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2022-05-23 | 15300 | keep | 0 | May | 2022 | 0.010421 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-23 13:57 | 2022-05-23 18:20 | 80 | 004:23 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22052300080 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 263 | 2022-05-23 | 21040 | keep | 0 | May | 2022 | 0.01433 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-05-23 14:03 | 2022-05-23 20:15 | 35 | 006:12 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA Y 2 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052300082 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 372 | 2022-05-23 | 13020 | keep | 0 | May | 2022 | 0.0088679 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-05-23 14:05 | 2022-05-24 10:48 | 65 | 020:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA QUEMADA | S22052300410 | New_Event | Cutout Failure | Include | Include | Equipment | 1243 | 2022-05-23 | 80795 | keep | 0 | May | 2022 | 0.055029 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-05-23 14:07 | 2022-05-23 15:47 | 850 | 001:40 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE REALIZO DESGANCHE DE RAMAS SOBRE LINEA Y SE REEMPLAZARON 2 AISLADORES 2% EN SERVICIO 1303-05, SIGUE FUERA EL 1303-04 | S22052300337 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-05-23 | 85000 | keep | 0 | May | 2022 | 0.057893 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-23 14:12 | 2022-05-23 15:37 | 3329 | 001:25 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PARA PROBAR TRAMO 50% EN SERVICIO | S22052300246 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 85 | 2022-05-23 | 282965 | keep | 0 | May | 2022 | 0.19273 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-23 14:12 | 2022-05-23 14:13 | 1417 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052300206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1417 | keep | 0 | May | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
ARECIBO | 2022-05-23 14:13 | 2022-05-23 20:40 | 80 | 006:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22052300086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 387 | 2022-05-23 | 30960 | keep | 0 | May | 2022 | 0.021087 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-23 14:13 | 2022-05-23 14:21 | 2861 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9400 | B22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-05-23 | 22888 | keep | 0 | May | 2022 | 0.015589 | 0.0019486 | Sustained | FALSE | FALSE | Not_TMED_Event | 2861
BAYAMON | 2022-05-23 14:13 | 2022-05-23 14:21 | 2096 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9400 | B22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-05-23 | 16768 | keep | 0 | May | 2022 | 0.011421 | 0.0014276 | Sustained | FALSE | FALSE | Not_TMED_Event | 2096
BAYAMON | 2022-05-23 14:13 | 2022-05-23 14:21 | 493 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9400 | B22052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-05-23 | 3944 | keep | 0 | May | 2022 | 0.0026862 | 0.00033578 | Sustained | FALSE | FALSE | Not_TMED_Event | 493
MAYAGÃœEZ | 2022-05-23 14:15 | 2022-05-23 14:16 | 2067 | 000:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | M22052300212 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-05-23 | 2067 | keep | 0 | May | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2022-05-23 14:16 | 2022-05-24 09:25 | 9 | 019:09 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER PERSONAL NO IDENTIFICO CAUSA | M22052300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1149 | 2022-05-23 | 10341 | keep | 0 | May | 2022 | 0.0070432 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2022-05-23 14:17 | 2022-05-23 18:45 | 30 | 004:28 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052300087 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 268 | 2022-05-23 | 8040 | keep | 0 | May | 2022 | 0.005476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-23 14:21 | 2022-05-23 14:47 | 4664 | 000:26 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR | M22052300219 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 26 | 2022-05-23 | 121264 | keep | 0 | May | 2022 | 0.082592 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
ARECIBO | 2022-05-23 14:22 | 2022-05-23 19:29 | 50 | 005:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22052300090 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 307 | 2022-05-23 | 15350 | keep | 0 | May | 2022 | 0.010455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-23 14:26 | 2022-05-23 23:00 | 50 | 008:34 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA SE ENCONTRO AVE QUEMADA | M22052300227 | New_Event | Animals | Include | Include | Wildlife | 514 | 2022-05-23 | 25700 | keep | 0 | May | 2022 | 0.017504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-23 14:26 | 2022-05-23 15:51 | 50 | 001:25 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA VEHICULO SE ENRREDO EN LINEAS DE TELEFONO CAUSANDO MOVIMIENTO DE POSTES Y CRUCE DE LINEAS | A22052300092 | New_Event | Damage From Public | Include | Include | Public | 85 | 2022-05-23 | 4250 | keep | 0 | May | 2022 | 0.0028947 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-23 14:37 | 2022-05-23 16:47 | 3335 | 002:10 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES EN LOS PALACIOS BY-220523-02 | B22052300187 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-05-23 | 433550 | keep | 0 | May | 2022 | 0.29529 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-05-23 14:40 | 2022-05-23 22:16 | 60 | 007:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22052300248 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 456 | 2022-05-23 | 27360 | keep | 0 | May | 2022 | 0.018635 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-05-23 14:40 | 2022-05-24 11:50 | 100 | 021:10 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052300250 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1270 | 2022-05-23 | 127000 | keep | 0 | May | 2022 | 0.086499 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-05-23 14:42 | 2022-05-23 16:44 | 86 | 002:02 | P | ANIMAL | 1X40 EN C/L (POR CRUCE DE AVE) | R22052300916 | New_Event | Animals | Include | Include | Wildlife | 122 | 2022-05-23 | 10492 | keep | 0 | May | 2022 | 0.0071461 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
MAYAGÃœEZ | 2022-05-23 14:45 | 2022-05-24 09:35 | 100 | 018:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22052300259 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1130 | 2022-05-23 | 113000 | keep | 0 | May | 2022 | 0.076964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-23 14:49 | 2022-05-23 22:30 | 12 | 007:41 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN XMR SE ENCONTRO BARRAS DE PEDESTAL CRUZADAS | R22052300921 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 461 | 2022-05-23 | 5532 | keep | 0 | May | 2022 | 0.0037678 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-23 14:49 | 2022-05-23 16:30 | 8 | 001:41 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO BAJANTE A CAJA PRIMARIA EN TRANSFORMADOR | P22052300138 | New_Event | Primary Wire Break | Include | Include | Equipment | 101 | 2022-05-23 | 808 | keep | 0 | May | 2022 | 0.00055033 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-05-23 14:49 | 2022-05-23 14:50 | 1227 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A22052300104 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-23 | 1227 | keep | 0 | May | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-05-23 14:50 | 2022-05-23 15:51 | 30 | 001:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A22052300117 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 61 | 2022-05-23 | 1830 | keep | 0 | May | 2022 | 0.0012464 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-23 14:51 | 2022-05-23 17:38 | 15 | 002:47 | P | NO SE REPORTO CAUSA | 2 X 25 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22052300106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2022-05-23 | 2505 | keep | 0 | May | 2022 | 0.0017061 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-05-23 14:51 | 2022-05-23 21:30 | 2 | 006:39 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052300105 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 399 | 2022-05-23 | 798 | keep | 0 | May | 2022 | 0.00054351 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-05-23 14:52 | 2022-05-23 17:50 | 2 | 002:58 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052300107 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 178 | 2022-05-23 | 356 | keep | 0 | May | 2022 | 0.00024247 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-05-23 15:00 | 2022-05-23 16:52 | 100 | 001:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LAS LINEAS | A22052300110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-05-23 | 11200 | keep | 0 | May | 2022 | 0.0076283 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-23 15:03 | 2022-05-23 21:16 | 6 | 006:13 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052300113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 373 | 2022-05-23 | 2238 | keep | 0 | May | 2022 | 0.0015243 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-23 15:12 | 2022-05-23 19:08 | 179 | 003:56 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | S22052300488 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 236 | 2022-05-23 | 42244 | keep | 0 | May | 2022 | 0.028772 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
FAJARDO | 2022-05-23 15:12 | 2022-05-23 16:04 | 1 | 000:52 | P | ANIMAL | 1X25 EN C/L & 2X15 EN RISER (IGUANA CRUZO LA PRIMARIA) | R22052300929 | New_Event | Animals | Include | Include | Wildlife | 52 | 2022-05-23 | 52 | keep | 0 | May | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-23 15:20 | 2022-05-23 16:34 | 137 | 001:14 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO BKR 1201-01 POR EMERGENCIA A PETICION DE JOSE BURGOS POSTE SE PARTIO CAYENDO ENCIMA DE LINEA MIENTRAS TRABAJABAN CON LA CONDICION DEL 1204-03. SE SECCIONALIZO ENTRANDO UN 50% EN SERVICIO | S22052300246 | New_Event | Primary Pole Failure | Include | Include | Equipment | 74 | 2022-05-23 | 10138 | keep | 0 | May | 2022 | 0.0069049 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
BAYAMON | 2022-05-23 15:32 | 2022-05-23 21:49 | 108 | 006:17 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22052300343 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2022-05-23 | 40716 | keep | 0 | May | 2022 | 0.027731 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2022-05-23 15:33 | 2022-05-23 16:19 | 1253 | 000:46 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PARTIDA EN TRONCAL Y SE CERRO INTERRUPTOR LLEVA CARGA DEL 6010-02 | M22052300304 | New_Event | Primary Wire Break | Include | Include | Equipment | 46 | 2022-05-23 | 57638 | keep | 0 | May | 2022 | 0.039257 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-23 15:33 | 2022-05-23 16:19 | 1266 | 000:46 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PARTIDA EN TRONCAL Y SE CERRO INTERRUPTOR CARGA POR 6010-01 | M22052300304 | New_Event | Primary Wire Break | Include | Include | Equipment | 46 | 2022-05-23 | 58236 | keep | 0 | May | 2022 | 0.039664 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
ARECIBO | 2022-05-23 15:33 | 2022-05-23 17:53 | 30 | 002:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22052300118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-05-23 | 4200 | keep | 0 | May | 2022 | 0.0028606 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-05-23 15:36 | 2022-05-23 15:41 | 2500 | 000:05 | P | NO SE REPORTO CAUSA | ALIMENTADOR 2603-10 DISPARO Y SE CERRO POR CONTROL LLEVA EL 40% DEL 2603-08 | C22052300127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-05-23 | 12500 | keep | 0 | May | 2022 | 0.0085137 | 0.0017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 2500
HUMACAO | 2022-05-23 15:36 | 2022-05-23 15:41 | 551 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 40% DEL 2603-08 | C22052300127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-05-23 | 2755 | keep | 0 | May | 2022 | 0.0018764 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
SAN JUAN | 2022-05-23 15:37 | 2022-05-23 16:20 | 1716 | 000:43 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PARA TRABAJAR ELIMINANDO GUY WIRE PEGADO A A PARARRAYO Y REPARAR PUENTE PRIMARIO Y TIERRA EN PARARRAYO. SE CERRO MACHETES 100% EN SERVICIO DEL 80% QUE LLEVA DE SU CARGA | S22052300246 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 43 | 2022-05-23 | 73788 | keep | 0 | May | 2022 | 0.050257 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-23 15:38 | 2022-05-24 09:41 | 100 | 018:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22052300344 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1083 | 2022-05-23 | 108300 | keep | 0 | May | 2022 | 0.073763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-23 15:40 | 2022-05-23 16:40 | 40 | 001:00 | P | DESGANCHE | SE ABRIO C/L SE DESGANCHO Y SE CERRO C/L SE TRABAJO CON BY-220523-02 | B22052300187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-05-23 | 2400 | keep | 0 | May | 2022 | 0.0016346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-23 15:47 | 2022-05-23 16:13 | 870 | 000:26 | T | DESGANCHE | SE DISPARO BKR NUEVAMENTE AL CERRAR MACHETES. SE SECCIONALIZO ALIMENTADOR PARA PROBAR TRAMO 80% EN SERVICIO DEL 1303-05, SIGUE FUERA LA CARGA 1303-04 | S22052300337 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 26 | 2022-05-23 | 22620 | keep | 0 | May | 2022 | 0.015406 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-05-23 15:48 | 2022-05-23 16:50 | 10 | 001:02 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO PARARRAYO Y SE REEMPLAZO BAJANTE PRIMARIO | M22052300328 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 62 | 2022-05-23 | 620 | keep | 0 | May | 2022 | 0.00042228 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-23 15:50 | 2022-05-23 16:50 | 2 | 001:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22052300352 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-05-23 | 120 | keep | 0 | May | 2022 | 8.1731e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-05-23 15:51 | 2022-05-24 05:05 | 20 | 013:14 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA CONDUCTORES CRUZADOS | M22052300325 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 794 | 2022-05-23 | 15880 | keep | 0 | May | 2022 | 0.010816 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-23 15:51 | 2022-05-23 15:52 | 1227 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A22052300127 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-23 | 1227 | keep | 0 | May | 2022 | 0.0008357 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-23 15:51 | 2022-05-23 15:52 | 3431 | 000:01 | T | CAUSAS EXTERNAS | RECIERRE DE INTERRUPTOR | A22052300128 | Additional_clients | Damage From Public | Include | Include | Public | 1 | 2022-05-23 | 3431 | keep | 0 | May | 2022 | 0.0023368 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-23 15:52 | 2022-05-24 11:09 | 40 | 019:17 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052300327 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1157 | 2022-05-23 | 46280 | keep | 0 | May | 2022 | 0.031521 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-23 15:52 | 2022-05-23 19:15 | 30 | 003:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A22052300117 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 203 | 2022-05-23 | 6090 | keep | 0 | May | 2022 | 0.0041479 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-23 15:52 | 2022-05-23 16:14 | 50 | 000:22 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA VEHICULO SE ENRREDO EN LINEAS DE TELEFONO CAUSANDO MOVIMIENTO DE POSTES Y CRUCE DE LINEAS | A22052300092 | 1st_after_momentary | Damage From Public | Include | Include | Public | 22 | 2022-05-23 | 1100 | keep | 0 | May | 2022 | 0.0007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-23 15:55 | 2022-05-23 16:21 | 10 | 000:26 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | R22052300942 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-05-23 | 260 | keep | 0 | May | 2022 | 0.00017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-23 16:10 | 2022-05-23 22:00 | 168 | 005:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X65 EN C/L & 1X65 EN C/L & SE REMPLAZO AISLADOR PIN-POLE TOP | R22052300947 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 350 | 2022-05-23 | 58800 | keep | 0 | May | 2022 | 0.040048 | 0.00011442 | Sustained | FALSE | FALSE | Not_TMED_Event | 168
SAN JUAN | 2022-05-23 16:13 | 2022-05-23 16:48 | 174 | 000:35 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR PARA PROBAR EL TRAMO ENTRANDO 100% EN SERVICIO 1303-05 Y 95% DEL 1303-04 | S22052300337 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 35 | 2022-05-23 | 6090 | keep | 0 | May | 2022 | 0.0041479 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-05-23 16:21 | 2022-05-24 08:20 | 1 | 015:59 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA | B22052300365 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 959 | 2022-05-23 | 959 | keep | 0 | May | 2022 | 0.00065317 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-23 16:21 | 2022-05-24 07:40 | 30 | 015:19 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | B22052300325 | New_Event | Vegetation Contact | Include | Include | Vegetation | 919 | 2022-05-23 | 27570 | keep | 0 | May | 2022 | 0.018778 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-05-23 16:24 | 2022-05-23 23:30 | 10 | 007:06 | P | NO SE REPORTO CAUSA | 1 X 20 SU-2 @ T-2 | R22052300953 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 426 | 2022-05-23 | 4260 | keep | 0 | May | 2022 | 0.0029015 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-23 16:30 | 2022-05-23 16:31 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22052300957 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 4085 | keep | 0 | May | 2022 | 0.0027823 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-23 16:31 | 2022-05-23 17:03 | 100 | 000:32 | P | NO SE REPORTO CAUSA | 1X80 EN C/L & 1X65 EN OTRO C/L | R22052300887 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 32 | 2022-05-23 | 3200 | keep | 0 | May | 2022 | 0.0021795 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-05-23 16:31 | 2022-05-23 16:32 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052300173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1475 | keep | 0 | May | 2022 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2022-05-23 16:32 | 2022-05-23 17:40 | 159 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | P22052300185 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-05-23 | 10812 | keep | 0 | May | 2022 | 0.007364 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
SAN JUAN | 2022-05-23 16:34 | 2022-05-23 17:38 | 69 | 001:04 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO PARA REEMPLAZAR POSTE PARTIDO Y SE TRANSFIRIO 45% DE LA CARGA AL 1342-04. 95% EN SERVICIO | S22052300246 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 64 | 2022-05-23 | 4416 | keep | 0 | May | 2022 | 0.0030077 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-23 16:41 | 2022-05-23 16:42 | 552 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04. LLEVA LA CARGAS PARCIALES DE 20% 1303-02, 40% 1204-04, 60% 1204-03. | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 552 | keep | 0 | May | 2022 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2022-05-23 16:41 | 2022-05-23 16:42 | 2966 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04. LLEVA LA CARGAS PARCIALES DE 20% 1303-02, 40% 1204-04, 60% 1204-03. | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 2966 | keep | 0 | May | 2022 | 0.0020201 | 0.0020201 | Momentary | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2022-05-23 16:41 | 2022-05-23 16:42 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04. LLEVA LA CARGAS PARCIALES DE 20% 1303-02, 40% 1204-04, 60% 1204-03. | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1799 | keep | 0 | May | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-23 16:41 | 2022-05-23 16:42 | 487 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04. LLEVA LA CARGAS PARCIALES DE 20% 1303-02, 40% 1204-04, 60% 1204-03. | S22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 487 | keep | 0 | May | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
VEGA BAJA | 2022-05-23 16:41 | 2022-05-24 09:39 | 2 | 016:58 | P | NO SE REPORTO CAUSA | 2 X 30 EN C/L | B22052300378 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1018 | 2022-05-23 | 2036 | keep | 0 | May | 2022 | 0.0013867 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-05-23 16:44 | 2022-05-23 16:45 | 2708 | 000:01 | T | ANIMAL | RECIERRE | R22052300000 | Additional_clients | Animals | Include | Include | Wildlife | 1 | 2022-05-23 | 2708 | keep | 0 | May | 2022 | 0.0018444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-23 16:45 | 2022-05-23 20:23 | 86 | 003:38 | P | ANIMAL | 1X40 EN C/L (POR CRUCE DE AVE) | R22052300916 | 1st_after_momentary | Animals | Include | Include | Wildlife | 218 | 2022-05-23 | 18748 | keep | 0 | May | 2022 | 0.012769 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
SAN JUAN | 2022-05-23 16:48 | 2022-05-23 18:07 | 12 | 001:19 | P | DESGANCHE | SE SECCIONALIZO PARA REALIZAR DESGANCHE 100% EN SERVICIO | S22052300337 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-05-23 | 948 | keep | 0 | May | 2022 | 0.00064568 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-05-23 16:55 | 2022-05-23 18:05 | 93 | 001:10 | P | ANIMAL | 1X 100 EN CORTE DE LINEA PALOMA CRUZO FASE | P22052300176 | New_Event | Animals | Include | Include | Wildlife | 70 | 2022-05-23 | 6510 | keep | 0 | May | 2022 | 0.0044339 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
GUAYAMA | 2022-05-23 16:57 | 2022-05-23 19:50 | 10 | 002:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | P22052300178 | New_Event | Cutout Failure | Include | Include | Equipment | 173 | 2022-05-23 | 1730 | keep | 0 | May | 2022 | 0.0011783 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-23 16:57 | 2022-05-23 16:58 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 4176 | keep | 0 | May | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
SAN JUAN | 2022-05-23 16:58 | 2022-05-24 03:49 | 2 | 010:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO POSTE PARTIDO Y SE CERRARON MACHETES EN EL 1201-01 | S22052300246 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 651 | 2022-05-23 | 1302 | keep | 0 | May | 2022 | 0.00088679 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-23 17:00 | 2022-05-23 17:30 | 100 | 000:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22052300151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-05-23 | 3000 | keep | 0 | May | 2022 | 0.0020433 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-23 17:03 | 2022-05-23 19:20 | 10 | 002:17 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN XMR LA TIERRA DEL PARARRAYO SE PEGO A LA CAJA DEL XMR | S22052300564 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 137 | 2022-05-23 | 1370 | keep | 0 | May | 2022 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-05-23 17:14 | 2022-05-23 19:03 | 1 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | B22052300383 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-05-23 | 109 | keep | 0 | May | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-23 17:24 | 2022-05-23 22:24 | 167 | 005:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22052300385 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 300 | 2022-05-23 | 50100 | keep | 0 | May | 2022 | 0.034123 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
SAN JUAN | 2022-05-23 17:38 | 2022-05-24 04:13 | 7 | 010:35 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO Y SE CERRARON MACHETES | S22052300246 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 635 | 2022-05-23 | 4445 | keep | 0 | May | 2022 | 0.0030275 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-23 17:38 | 2022-05-23 20:50 | 100 | 003:12 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A22052300155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-05-23 | 19200 | keep | 0 | May | 2022 | 0.013077 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-05-23 17:43 | 2022-05-23 19:35 | 2 | 001:52 | P | CONDUCTOR ROTO O ABIERTO | 1X50 EN C/L & SE REPARO BAJANTE PRIMARIO QUE ESTABA TOCANDO LA CRUCETA | R22052300976 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2022-05-23 | 224 | keep | 0 | May | 2022 | 0.00015257 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-05-23 17:43 | 2022-05-24 10:30 | 150 | 016:47 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052300398 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1007 | 2022-05-23 | 151050 | keep | 0 | May | 2022 | 0.10288 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-05-23 18:19 | 2022-05-23 22:25 | 10 | 004:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIAS FUERTES | A22052300165 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 246 | 2022-05-23 | 2460 | keep | 0 | May | 2022 | 0.0016755 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-05-23 18:23 | 2022-05-23 19:52 | 15 | 001:29 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CONVERTIDOR POR DESCARGAS ELECTRICAS | A22052300166 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 89 | 2022-05-23 | 1335 | keep | 0 | May | 2022 | 0.00090926 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-05-23 18:23 | 2022-05-24 17:25 | 10 | 023:02 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 50KVA | A22052300166 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1382 | 2022-05-23 | 13820 | keep | 0 | May | 2022 | 0.0094127 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-23 18:23 | 2022-05-24 11:37 | 8 | 017:14 | P | NO SE REPORTO CAUSA | 1 X 15 XMR | B22052300398 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1034 | 2022-05-23 | 8272 | keep | 0 | May | 2022 | 0.005634 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-05-23 18:32 | 2022-05-23 20:23 | 63 | 001:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU#3 NO SE ENCONTRO NADA | P22052300195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-05-23 | 6993 | keep | 0 | May | 2022 | 0.0047629 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
MAYAGÃœEZ | 2022-05-23 18:33 | 2022-05-24 15:30 | 45 | 020:57 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M22052300419 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1257 | 2022-05-23 | 56565 | keep | 0 | May | 2022 | 0.038526 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-05-23 18:46 | 2022-05-23 22:02 | 75 | 003:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | M22052300423 | New_Event | Primary Wire Break | Include | Include | Equipment | 196 | 2022-05-23 | 14700 | keep | 0 | May | 2022 | 0.010012 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-05-23 18:49 | 2022-05-24 09:25 | 7 | 014:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON BAJANTES SECUNDARIOS DE XMR (NO FUNDIO) | C22052300163 | New_Event | Secondary Wire Break | Include | Include | Equipment | 876 | 2022-05-23 | 6132 | keep | 0 | May | 2022 | 0.0041765 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-05-23 18:50 | 2022-05-23 20:17 | 1 | 001:27 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE SE DEJO UN TAP ABIERTO HACIA MONTE | B22052300402 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-05-23 | 87 | keep | 0 | May | 2022 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-23 18:52 | 2022-05-24 09:50 | 15 | 014:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052300427 | New_Event | Vegetation Contact | Include | Include | Vegetation | 898 | 2022-05-23 | 13470 | keep | 0 | May | 2022 | 0.0091744 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-05-23 18:53 | 2022-05-23 20:22 | 10 | 001:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR FUERTE LLUVIA | P22052300199 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 89 | 2022-05-23 | 890 | keep | 0 | May | 2022 | 0.00060617 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-23 19:00 | 2022-05-24 12:50 | 40 | 017:50 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052300429 | New_Event | Primary Wire Break | Include | Include | Equipment | 1070 | 2022-05-23 | 42800 | keep | 0 | May | 2022 | 0.029151 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-23 19:06 | 2022-05-24 10:15 | 15 | 015:09 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052300433 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 909 | 2022-05-23 | 13635 | keep | 0 | May | 2022 | 0.0092867 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-23 19:20 | 2022-05-24 02:17 | 210 | 006:57 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA A CAUSA DE DESGANCHE SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052300440 | New_Event | Vegetation Contact | Include | Include | Vegetation | 417 | 2022-05-23 | 87570 | keep | 0 | May | 2022 | 0.059644 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
BAYAMON | 2022-05-23 19:24 | 2022-05-23 19:26 | 4176 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO SE QUEDO FUERA Y SE CERRO POR SCADA | B22052300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-23 | 8352 | keep | 0 | May | 2022 | 0.0056885 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
MAYAGÃœEZ | 2022-05-23 19:37 | 2022-05-24 11:40 | 8 | 016:03 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052300447 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 963 | 2022-05-23 | 7704 | keep | 0 | May | 2022 | 0.0052472 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-05-23 19:40 | 2022-05-23 21:56 | 10 | 002:16 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052300173 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 136 | 2022-05-23 | 1360 | keep | 0 | May | 2022 | 0.00092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-23 19:42 | 2022-05-24 13:50 | 40 | 018:08 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052300448 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1088 | 2022-05-23 | 43520 | keep | 0 | May | 2022 | 0.029641 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-05-23 19:49 | 2022-05-23 20:12 | 1500 | 000:23 | P | CRUCETA DEFECTUOSA O AVERIADA | SE INSTALO CRUCETA MAS LARGA YA QUE CONDUCTOR ESTABA HACIENDO CONTACTO CON TENSORES Y CAUSO AVERIA | M22052300452 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 23 | 2022-05-23 | 34500 | keep | 0 | May | 2022 | 0.023498 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
UTUADO | 2022-05-23 20:03 | 2022-05-24 11:54 | 6 | 015:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22052300180 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 951 | 2022-05-23 | 5706 | keep | 0 | May | 2022 | 0.0038863 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-23 20:09 | 2022-05-24 10:00 | 200 | 013:51 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO EVENTO DEL DIA 21 CON CONTINUACION | M22052100219 | New_Event | Primary Wire Break | Include | Include | Equipment | 831 | 2022-05-23 | 166200 | keep | 0 | May | 2022 | 0.1132 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-23 20:12 | 2022-05-24 08:55 | 1 | 012:43 | P | ANIMAL | 1 X 40 RISER AVE | B22052300430 | New_Event | Animals | Include | Include | Wildlife | 763 | 2022-05-23 | 763 | keep | 0 | May | 2022 | 0.00051968 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-05-23 20:12 | 2022-05-23 20:18 | 2493 | 000:06 | T | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO INTERRUPTOR PARA SECIONALIZAR AREA DONDE LINEA ESTA PEGANDO A TENSOR | M22052300459 | Additional_clients | Primary Crossarm Failure | Include | Include | Equipment | 6 | 2022-05-23 | 14958 | keep | 0 | May | 2022 | 0.010188 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-05-23 20:18 | 2022-05-23 22:22 | 1500 | 002:04 | P | CRUCETA DEFECTUOSA O AVERIADA | SE INSTALO CRUCETA MAS LARGA YA QUE CONDUCTOR ESTABA HACIENDO CONTACTO CON TENSORES Y CAUSO AVERIA | M22052300452 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 124 | 2022-05-23 | 186000 | keep | 0 | May | 2022 | 0.12668 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-23 20:30 | 2022-05-24 00:13 | 200 | 003:43 | P | DESGANCHE | 1 X 140 EN C/L SE REALIZO DESGANCHE | B22052300445 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2022-05-23 | 44600 | keep | 0 | May | 2022 | 0.030377 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-05-23 20:38 | 2022-05-24 18:12 | 5 | 021:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REEMPLAZO PORTAFUSIBLE | C22052300172 | New_Event | Cutout Failure | Include | Include | Equipment | 1294 | 2022-05-23 | 6470 | keep | 0 | May | 2022 | 0.0044067 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-05-23 20:40 | 2022-05-23 21:12 | 144 | 000:32 | P | NO SE REPORTO CAUSA | 1X50 EN C/L & 1X10 EN XMER | R22052301003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 32 | 2022-05-23 | 4608 | keep | 0 | May | 2022 | 0.0031385 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
BARRANQUITAS | 2022-05-23 20:43 | 2022-05-24 14:44 | 10 | 018:01 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | C22052300173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1081 | 2022-05-23 | 10810 | keep | 0 | May | 2022 | 0.0073626 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-05-23 21:07 | 2022-05-24 10:40 | 30 | 013:33 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052300486 | New_Event | Vegetation Contact | Include | Include | Vegetation | 813 | 2022-05-23 | 24390 | keep | 0 | May | 2022 | 0.016612 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-05-23 21:17 | 2022-05-24 10:15 | 10 | 012:58 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R22052301011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 778 | 2022-05-23 | 7780 | keep | 0 | May | 2022 | 0.0052989 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-05-23 21:19 | 2022-05-24 16:42 | 2 | 019:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO (NO FUNDIO) | C22052300175 | New_Event | Primary Wire Break | Include | Include | Equipment | 1163 | 2022-05-23 | 2326 | keep | 0 | May | 2022 | 0.0015842 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-05-23 21:29 | 2022-05-24 10:12 | 42 | 012:43 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN AEREO @ T-9, AVERIA DE T-9- @ T-10 Y AVERIA VIEJA DEL T-10 @ T-7 | B22052300456 | New_Event | UG Cable Fault | Include | Include | Equipment | 763 | 2022-05-23 | 32046 | keep | 0 | May | 2022 | 0.021826 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2022-05-23 21:33 | 2022-05-23 21:35 | 514 | 000:02 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL 20% CARGA POR EL 1118-10 | S22052300000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-05-23 | 1028 | keep | 0 | May | 2022 | 0.00070017 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-05-23 21:33 | 2022-05-23 21:35 | 2782 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 20% DEL 1111-01 | S22052300000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-05-23 | 5564 | keep | 0 | May | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2022-05-23 21:46 | 2022-05-23 21:47 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22052300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-23 | 1746 | keep | 0 | May | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
FAJARDO | 2022-05-23 21:51 | 2022-05-24 10:55 | 7 | 013:04 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | R22052301017 | New_Event | Animals | Include | Include | Wildlife | 784 | 2022-05-23 | 5488 | keep | 0 | May | 2022 | 0.0037379 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-05-23 22:10 | 2022-05-24 11:40 | 100 | 013:30 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052300503 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 810 | 2022-05-23 | 81000 | keep | 0 | May | 2022 | 0.055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-23 22:13 | 2022-05-24 10:27 | 21 | 012:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22052300466 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 734 | 2022-05-23 | 15414 | keep | 0 | May | 2022 | 0.010498 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BARRANQUITAS | 2022-05-23 22:15 | 2022-05-24 14:29 | 12 | 016:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X10 EN XMR - SE REMPLAZO CAJA Y BAJANTE PRIMARIOS, PARARRAYOS | C22052300176 | New_Event | Cutout Failure | Include | Include | Equipment | 974 | 2022-05-23 | 11688 | keep | 0 | May | 2022 | 0.0079606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-05-23 22:16 | 2022-05-24 09:16 | 10 | 011:00 | P | NO SE REPORTO CAUSA | 1 X 15 EN PROVISIONAL AEREO | R22052301021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 660 | 2022-05-23 | 6600 | keep | 0 | May | 2022 | 0.0044952 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-23 22:20 | 2022-05-23 22:22 | 514 | 000:02 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL 20% CARGA POR EL 1118-10 | S22052300000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 2 | 2022-05-23 | 1028 | keep | 0 | May | 2022 | 0.00070017 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-05-23 22:20 | 2022-05-23 22:22 | 2782 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 20% DEL 1111-01 | S22052300000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 2 | 2022-05-23 | 5564 | keep | 0 | May | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2022-05-23 22:33 | 2022-05-23 22:35 | 514 | 000:02 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL 20% CARGA POR EL 1118-10 | S22052300000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 2 | 2022-05-23 | 1028 | keep | 0 | May | 2022 | 0.00070017 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-05-23 22:33 | 2022-05-23 22:35 | 2782 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 20% DEL 1111-01 | S22052300000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 2 | 2022-05-23 | 5564 | keep | 0 | May | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2022-05-23 22:40 | 2022-05-24 01:58 | 514 | 003:18 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1118-10 SE REEMPLAZO MACHETE QUEMADO Y SE ENERGIZO 20% CARGA POR EL 1118-10 | S22052300000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 198 | 2022-05-23 | 101772 | keep | 0 | May | 2022 | 0.069316 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-05-23 22:40 | 2022-05-24 00:34 | 2782 | 001:54 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 20% DEL 1111-01. SE SECCIONALIZO 90% EN SERVICIO | S22052300000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 114 | 2022-05-23 | 317148 | keep | 0 | May | 2022 | 0.21601 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2022-05-23 22:52 | 2022-05-24 04:04 | 3798 | 005:12 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE PROBO TRAMO 25% EN SERVICIO | B22052300467 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 312 | 2022-05-23 | 1184976 | keep | 0 | May | 2022 | 0.80708 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
SAN JUAN | 2022-05-23 23:11 | 2022-05-24 08:39 | 110 | 009:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-8C @ SU-2 | R22052301027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 568 | 2022-05-23 | 62480 | keep | 0 | May | 2022 | 0.042555 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
FAJARDO | 2022-05-23 23:21 | 2022-05-24 11:47 | 35 | 012:26 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN CORTE DE LINEA AVERIA T-7 @ T-8. QUEDO FUERA T-7 Y T-6 | R22052301028 | New_Event | UG Cable Fault | Include | Include | Equipment | 746 | 2022-05-23 | 26110 | keep | 0 | May | 2022 | 0.017783 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-05-24 00:01 | 2022-05-24 00:02 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22052400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 1827 | keep | 0 | May | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
ARECIBO | 2022-05-24 00:03 | 2022-05-24 14:29 | 2 | 014:26 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | A22052400001 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 866 | 2022-05-24 | 1732 | keep | 0 | May | 2022 | 0.0011797 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-05-24 00:03 | 2022-05-24 18:08 | 2 | 018:05 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25KVA POR UNO DE 37.5KVA | A22052400126 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1085 | 2022-05-24 | 2170 | keep | 0 | May | 2022 | 0.001478 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-05-24 00:13 | 2022-05-24 06:49 | 50 | 006:36 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | P22052400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 396 | 2022-05-24 | 19800 | keep | 0 | May | 2022 | 0.013486 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-24 00:23 | 2022-05-24 04:04 | 429 | 003:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/ L & SE REMPLAZO CAJA PRIMARIA | C22052400001 | New_Event | Cutout Failure | Include | Include | Equipment | 221 | 2022-05-24 | 94809 | keep | 0 | May | 2022 | 0.064574 | 0.00029219 | Sustained | FALSE | FALSE | Not_TMED_Event | 429
SAN JUAN | 2022-05-24 00:34 | 2022-05-24 01:58 | 278 | 001:24 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO Y SE CERRARON MACHETES 100% EN SERVICIO 1118-10 Y EL 20% QUE LLEVA DEL 1111-01 EN SERVICIO. | S22052300000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 84 | 2022-05-24 | 23352 | keep | 0 | May | 2022 | 0.015905 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-24 01:03 | 2022-05-24 01:04 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | C22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 1606 | keep | 0 | May | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
ARECIBO | 2022-05-24 01:18 | 2022-05-24 11:05 | 80 | 009:47 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22052400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 587 | 2022-05-24 | 46960 | keep | 0 | May | 2022 | 0.031984 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-05-24 01:25 | 2022-05-24 01:26 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | C22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 1702 | keep | 0 | May | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CANOVANAS | 2022-05-24 01:59 | 2022-05-24 04:46 | 4154 | 002:47 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR 30% EN SERVICIO | R22052400001 | New_Event | Primary Wire Break | Include | Include | Equipment | 167 | 2022-05-24 | 693718 | keep | 0 | May | 2022 | 0.47249 | 0.0028293 | Sustained | FALSE | FALSE | Not_TMED_Event | 4154
BAYAMON | 2022-05-24 02:08 | 2022-05-24 02:09 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 1834 | keep | 0 | May | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
VEGA BAJA | 2022-05-24 02:08 | 2022-05-24 02:09 | 603 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR 9206-08 LLEVA CARGA DEL 9206-09 | B22052400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-24 | 603 | keep | 0 | May | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-05-24 02:08 | 2022-05-24 02:09 | 6 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR 9206-08 LLEVA CARGA DEL 9206-09 | B22052400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-24 | 6 | keep | 0 | May | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-05-24 02:09 | 2022-05-24 13:34 | 176 | 011:25 | P | DESGANCHE | 1 X 80 SE RETIRO PALMA | B22052400021 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 685 | 2022-05-24 | 120560 | keep | 0 | May | 2022 | 0.082113 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
BAYAMON | 2022-05-24 02:14 | 2022-05-24 08:16 | 1834 | 006:02 | T | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA | B22052400017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 362 | 2022-05-24 | 663908 | keep | 0 | May | 2022 | 0.45218 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2022-05-24 03:40 | 2022-05-24 08:38 | 140 | 004:58 | P | NO SE REPORTO CAUSA | 1 X 50 RISER | B22052400032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 298 | 2022-05-24 | 41720 | keep | 0 | May | 2022 | 0.028415 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2022-05-24 04:04 | 2022-05-24 05:18 | 3132 | 001:14 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE PROBO TRAMO ADICIONAL 35% EN SERVICIO | B22052300467 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-05-24 | 231768 | keep | 0 | May | 2022 | 0.15786 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-24 04:32 | 2022-05-24 04:33 | 125 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | C22052400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 125 | keep | 0 | May | 2022 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-05-24 04:36 | 2022-05-24 06:12 | 101 | 001:36 | P | ANIMAL | 1X80 EN C/L (POR CRUCE DE AVE) | C22052400005 | New_Event | Animals | Include | Include | Wildlife | 96 | 2022-05-24 | 9696 | keep | 0 | May | 2022 | 0.0066039 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
CANOVANAS | 2022-05-24 04:46 | 2022-05-24 09:11 | 2908 | 004:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR ROTO Y CERRO MACHETES | R22052400001 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 265 | 2022-05-24 | 770620 | keep | 0 | May | 2022 | 0.52487 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-24 05:08 | 2022-05-24 12:49 | 77 | 007:41 | P | DESGANCHE | 1X40 EN C/L (SE DESGANCHO ARBOL DE PANA) | C22052400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 461 | 2022-05-24 | 35497 | keep | 0 | May | 2022 | 0.024177 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
SAN JUAN | 2022-05-24 05:09 | 2022-05-24 13:40 | 25 | 008:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y SE REEMPLAZO PORTA FUSIBLE QUEMADO | S22052400021 | New_Event | Cutout Failure | Include | Include | Equipment | 511 | 2022-05-24 | 12775 | keep | 0 | May | 2022 | 0.008701 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-24 05:18 | 2022-05-24 06:00 | 2714 | 000:42 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE PROBO TRAMO ADICIONAL 80% EN SERVICIO | B22052300467 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 42 | 2022-05-24 | 113988 | keep | 0 | May | 2022 | 0.077637 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-24 05:26 | 2022-05-24 08:01 | 4176 | 002:35 | T | DESGANCHE | SE REALIZO DESGANCHE EN CARR. 164 SECT. LA MARINA Y SE CERRO BKR POR SCADA | B22052400050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-05-24 | 647280 | keep | 0 | May | 2022 | 0.44086 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
MAYAGÃœEZ | 2022-05-24 05:34 | 2022-05-24 15:00 | 100 | 009:26 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052400010 | New_Event | Primary Wire Break | Include | Include | Equipment | 566 | 2022-05-24 | 56600 | keep | 0 | May | 2022 | 0.03855 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-24 05:52 | 2022-05-25 16:00 | 20 | 034:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22052400013 | New_Event | Primary Wire Break | Include | Include | Equipment | 2048 | 2022-05-24 | 40960 | keep | 0 | May | 2022 | 0.027898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-05-24 05:53 | 2022-05-24 14:12 | 45 | 008:19 | P | ANIMAL | 1 X 30 EN C/L AVE | R22052400033 | New_Event | Animals | Include | Include | Wildlife | 499 | 2022-05-24 | 22455 | keep | 0 | May | 2022 | 0.015294 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-05-24 05:54 | 2022-05-24 15:49 | 25 | 009:55 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22052400022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 595 | 2022-05-24 | 14875 | keep | 0 | May | 2022 | 0.010131 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-24 06:00 | 2022-05-24 06:27 | 835 | 000:27 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE PROBO TRAMO ADICIONAL 90% EN SERVICIO | B22052300467 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 27 | 2022-05-24 | 22545 | keep | 0 | May | 2022 | 0.015355 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-24 06:03 | 2022-05-24 11:50 | 60 | 005:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22052400007 | New_Event | Cutout Failure | Include | Include | Equipment | 347 | 2022-05-24 | 20820 | keep | 0 | May | 2022 | 0.01418 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-05-24 06:04 | 2022-05-24 09:54 | 210 | 003:50 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO EN TRONCAL | C22052400011 | New_Event | Primary Wire Break | Include | Include | Equipment | 230 | 2022-05-24 | 48300 | keep | 0 | May | 2022 | 0.032897 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
CANOVANAS | 2022-05-24 06:05 | 2022-05-24 15:51 | 15 | 009:46 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN XMR Y SE REPARO SECUNDARIA | R22052400034 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 586 | 2022-05-24 | 8790 | keep | 0 | May | 2022 | 0.0059868 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-05-24 06:17 | 2022-05-24 06:18 | 327 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA TRANSFERIDA AL 2604-01 | C22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 327 | keep | 0 | May | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2022-05-24 06:17 | 2022-05-24 06:18 | 824 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE LLEVA TRANSFERIDA LA CARGA DEL 2603-07 Y 65% DE SU CARGA POR 2604-03 | C22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 824 | keep | 0 | May | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
UTUADO | 2022-05-24 06:26 | 2022-05-24 10:13 | 5 | 003:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIARON TODAS LAS CONEXIONES DE TRANSFORMADOR SE REEMPLAZO PORTA FUSIBLE | A22052400008 | New_Event | Cutout Failure | Include | Include | Equipment | 227 | 2022-05-24 | 1135 | keep | 0 | May | 2022 | 0.00077304 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-05-24 06:27 | 2022-05-24 06:32 | 418 | 000:05 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE PROBO TRAMO ADICIONAL FINAL 100% EN SERVICIO | B22052300467 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-05-24 | 2090 | keep | 0 | May | 2022 | 0.0014235 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-24 06:34 | 2022-05-24 09:11 | 43 | 002:37 | P | DESGANCHE | 1 X 30 EN C/L SE RETIRO DESGANCHE | B22052400079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-05-24 | 6751 | keep | 0 | May | 2022 | 0.0045981 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2022-05-24 06:39 | 2022-05-24 14:46 | 7 | 008:07 | P | ANIMAL | 1 X 10 EN XMR DE BAJO TAPS DEL 4 @ 1 SE DEJO VOLTAJE BUENO Y SE REPARO SECUNDARIA CRUCE POR RATA | R22052400039 | New_Event | Animals | Include | Include | Wildlife | 487 | 2022-05-24 | 3409 | keep | 0 | May | 2022 | 0.0023219 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-24 06:47 | 2022-05-24 11:14 | 30 | 004:27 | P | ANIMAL | 1 X 20 EN BANCO Y 1 X 40 EN SU AVE CRUZO LINEAS | B22052400160 | New_Event | Animals | Include | Include | Wildlife | 267 | 2022-05-24 | 8010 | keep | 0 | May | 2022 | 0.0054556 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-24 06:49 | 2022-05-24 06:50 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 2234 | keep | 0 | May | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
UTUADO | 2022-05-24 06:55 | 2022-05-24 10:45 | 4 | 003:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA @ 4/7 KV POR 37.5 KVA @ 4/7 KV | A22052400012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 230 | 2022-05-24 | 920 | keep | 0 | May | 2022 | 0.00062661 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-05-24 06:57 | 2022-05-24 11:34 | 91 | 004:37 | P | DESGANCHE | 2X80 EN C/L (SE RETIRARON BAMBUAS DE LA PRIMARIA) | C22052400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2022-05-24 | 25207 | keep | 0 | May | 2022 | 0.017168 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
CANOVANAS | 2022-05-24 07:05 | 2022-05-24 11:52 | 65 | 004:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22052400048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2022-05-24 | 18655 | keep | 0 | May | 2022 | 0.012706 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-05-24 07:05 | 2022-05-24 09:23 | 125 | 002:18 | P | DESGANCHE | 1 X 80 Y 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22052400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-05-24 | 17250 | keep | 0 | May | 2022 | 0.011749 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
UTUADO | 2022-05-24 07:07 | 2022-05-24 13:19 | 12 | 006:12 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE DE BAMBUAS | A22052400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2022-05-24 | 4464 | keep | 0 | May | 2022 | 0.0030404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-24 07:09 | 2022-05-24 07:10 | 5069 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22052400029 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-24 | 5069 | keep | 0 | May | 2022 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2022-05-24 07:10 | 2022-05-24 09:53 | 118 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | P22052400053 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 163 | 2022-05-24 | 19234 | keep | 0 | May | 2022 | 0.0131 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
BAYAMON | 2022-05-24 07:17 | 2022-05-24 17:46 | 8 | 010:29 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL @ T-368 | B22052400092 | New_Event | UG Cable Fault | Include | Include | Equipment | 629 | 2022-05-24 | 5032 | keep | 0 | May | 2022 | 0.0034273 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-05-24 07:19 | 2022-05-24 15:16 | 30 | 007:57 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | C22052400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 477 | 2022-05-24 | 14310 | keep | 0 | May | 2022 | 0.0097465 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-05-24 07:20 | 2022-05-24 09:37 | 75 | 002:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | P22052400032 | New_Event | Cutout Failure | Include | Include | Equipment | 137 | 2022-05-24 | 10275 | keep | 0 | May | 2022 | 0.0069983 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-05-24 07:34 | 2022-05-24 12:07 | 1 | 004:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L AISLADOR | B22052400100 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 273 | 2022-05-24 | 273 | keep | 0 | May | 2022 | 0.00018594 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-24 07:36 | 2022-05-24 15:40 | 20 | 008:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR LLUVIAS | A22052400025 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 484 | 2022-05-24 | 9680 | keep | 0 | May | 2022 | 0.006593 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-24 07:37 | 2022-05-24 16:50 | 50 | 009:13 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400029 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 553 | 2022-05-24 | 27650 | keep | 0 | May | 2022 | 0.018832 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-05-24 07:44 | 2022-05-24 14:16 | 60 | 006:32 | P | ANIMAL | 1X50 EN C/L (SE RETIRO IGUANA DE LA PRIMARIA) | C22052400030 | New_Event | Animals | Include | Include | Wildlife | 392 | 2022-05-24 | 23520 | keep | 0 | May | 2022 | 0.016019 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-24 07:52 | 2022-05-24 10:55 | 1261 | 003:03 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIERON/DEJARON ABIERTOS FUSIBLES (CUT-OUT) DE LA MEDICION REMOTA PARA FUTURA REPARACION - MEDIANTE G.O.I. CG-220524-01 | C22052400039 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2022-05-24 | 230763 | keep | 0 | May | 2022 | 0.15717 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
CAGUAS | 2022-05-24 07:52 | 2022-05-24 10:55 | 1922 | 003:03 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIERON/DEJARON ABIERTOS FUSIBLES (CUT-OUT) DE LA MEDICION REMOTA PARA FUTURA REPARACION - MEDIANTE G.O.I. CG-220524-01 | C22052400039 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2022-05-24 | 351726 | keep | 0 | May | 2022 | 0.23956 | 0.0013091 | Sustained | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2022-05-24 07:52 | 2022-05-24 10:55 | 853 | 003:03 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIERON/DEJARON ABIERTOS FUSIBLES (CUT-OUT) DE LA MEDICION REMOTA PARA FUTURA REPARACION - MEDIANTE G.O.I. CG-220524-01 | C22052400039 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2022-05-24 | 156099 | keep | 0 | May | 2022 | 0.10632 | 0.00058097 | Sustained | FALSE | FALSE | Not_TMED_Event | 853
CAGUAS | 2022-05-24 07:52 | 2022-05-24 10:55 | 2900 | 003:03 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIERON/DEJARON ABIERTOS FUSIBLES (CUT-OUT) DE LA MEDICION REMOTA PARA FUTURA REPARACION - MEDIANTE G.O.I. CG-220524-01 | C22052400039 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2022-05-24 | 530700 | keep | 0 | May | 2022 | 0.36146 | 0.0019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 2900
CAGUAS | 2022-05-24 07:52 | 2022-05-24 10:55 | 2178 | 003:03 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIERON/DEJARON ABIERTOS FUSIBLES (CUT-OUT) DE LA MEDICION REMOTA PARA FUTURA REPARACION - MEDIANTE G.O.I. CG-220524-01 | C22052400039 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2022-05-24 | 398574 | keep | 0 | May | 2022 | 0.27147 | 0.0014834 | Sustained | FALSE | FALSE | Not_TMED_Event | 2178
SAN JUAN | 2022-05-24 07:56 | 2022-05-24 12:15 | 1 | 004:19 | P | DESGANCHE | 1 X 15 EN BANCO DE XMR | R22052400063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-05-24 | 259 | keep | 0 | May | 2022 | 0.0001764 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-24 08:01 | 2022-05-24 11:02 | 13 | 003:01 | P | DESGANCHE | 1 X 80 EN C/L | B22052400158 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-05-24 | 2353 | keep | 0 | May | 2022 | 0.0016026 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-24 08:16 | 2022-05-24 15:21 | 1742 | 007:05 | P | LINEA DE TRANSMISION 38KV | SE SUBIO LINEAS AVERIADAS POR OHGW DE LINEA 7800 Y SE CERRO MACHETES | B22052400017 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 425 | 2022-05-24 | 740350 | keep | 0 | May | 2022 | 0.50425 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-05-24 08:22 | 2022-05-24 14:27 | 10 | 006:05 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZARON BAJANTES PRIMARIOS DE TRANSFORMADOR | M22052400036 | New_Event | Primary Wire Break | Include | Include | Equipment | 365 | 2022-05-24 | 3650 | keep | 0 | May | 2022 | 0.002486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-24 08:31 | 2022-05-24 13:10 | 1 | 004:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22052400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-05-24 | 279 | keep | 0 | May | 2022 | 0.00019003 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-05-24 08:40 | 2022-05-24 14:54 | 50 | 006:14 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22052400042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2022-05-24 | 18700 | keep | 0 | May | 2022 | 0.012736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-24 08:42 | 2022-05-24 10:40 | 35 | 001:58 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA @ LINEA (NO FUNDIO) | C22052400072 | New_Event | Primary Wire Break | Include | Include | Equipment | 118 | 2022-05-24 | 4130 | keep | 0 | May | 2022 | 0.0028129 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-05-24 08:55 | 2022-05-24 09:16 | 2402 | 000:21 | S | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO LINEA Y LA ENERGIZARON | B22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 21 | 2022-05-24 | 50442 | keep | 0 | May | 2022 | 0.034356 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-05-24 08:55 | 2022-05-24 09:16 | 767 | 000:21 | P | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO LINEA Y LA ENERGIZARON 1909-07 LLEVA 50% DEL 1709-03 LINEA 37500 | B22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 21 | 2022-05-24 | 16107 | keep | 0 | May | 2022 | 0.01097 | 0.0005224 | Sustained | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-05-24 08:55 | 2022-05-24 09:16 | 767 | 000:21 | P | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO LINEA Y LA ENERGIZARON 1909-07 LLEVA 50% DEL 1709-03 LINEA 37500 | B22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 21 | 2022-05-24 | 16107 | keep | 0 | May | 2022 | 0.01097 | 0.0005224 | Sustained | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-05-24 08:55 | 2022-05-24 09:16 | 2364 | 000:21 | S | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO LINEA Y LA ENERGIZARON LINEA 37500 | B22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 21 | 2022-05-24 | 49644 | keep | 0 | May | 2022 | 0.033812 | 0.0016101 | Sustained | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2022-05-24 08:55 | 2022-05-24 09:16 | 6136 | 000:21 | S | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO LINEA 37500 Y SE CERRO LINEA | S22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 21 | 2022-05-24 | 128856 | keep | 0 | May | 2022 | 0.087763 | 0.0041792 | Sustained | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2022-05-24 08:55 | 2022-05-24 09:16 | 1 | 000:21 | S | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO LINEA 37500 Y SE CERRO LINEA | S22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 21 | 2022-05-24 | 21 | keep | 0 | May | 2022 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-24 08:55 | 2022-05-24 10:20 | 222 | 001:25 | S | LINEA DE TRANSMISION 115KV | SE ENERGIZO LINEA 37500 | S22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-05-24 | 18870 | keep | 0 | May | 2022 | 0.012852 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-05-24 08:55 | 2022-05-24 10:20 | 2466 | 001:25 | S | LINEA DE TRANSMISION 115KV | SE ENERGIZO LINEA 37500 | S22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-05-24 | 209610 | keep | 0 | May | 2022 | 0.14276 | 0.0016796 | Sustained | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2022-05-24 08:55 | 2022-05-24 10:20 | 2435 | 001:25 | S | LINEA DE TRANSMISION 115KV | SE ENERGIZO LINEA 37500 | S22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-05-24 | 206975 | keep | 0 | May | 2022 | 0.14097 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-05-24 08:55 | 2022-05-24 10:20 | 1139 | 001:25 | S | LINEA DE TRANSMISION 115KV | SE ENERGIZO LINEA 37500 1909-07 LLEVANDO 50% DEL 1709-03 | S22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-05-24 | 96815 | keep | 0 | May | 2022 | 0.06594 | 0.00077577 | Sustained | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2022-05-24 08:55 | 2022-05-24 10:20 | 2956 | 001:25 | S | LINEA DE TRANSMISION 115KV | SE ENERGIZO LINEA 37500 | S22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-05-24 | 251260 | keep | 0 | May | 2022 | 0.17113 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-05-24 08:55 | 2022-05-24 10:20 | 4456 | 001:25 | S | LINEA DE TRANSMISION 115KV | SE ENERGIZO LINEA 37500 | S22052400123 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-05-24 | 378760 | keep | 0 | May | 2022 | 0.25797 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
MAYAGÃœEZ | 2022-05-24 09:10 | 2022-05-24 10:22 | 8 | 001:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22052400051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 72 | 2022-05-24 | 576 | keep | 0 | May | 2022 | 0.00039231 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-24 09:14 | 2022-05-24 09:56 | 50 | 000:42 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400055 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 42 | 2022-05-24 | 2100 | keep | 0 | May | 2022 | 0.0014303 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-24 09:19 | 2022-05-24 12:53 | 85 | 003:34 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22052400038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2022-05-24 | 18190 | keep | 0 | May | 2022 | 0.012389 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2022-05-24 09:25 | 2022-05-24 13:59 | 300 | 004:34 | P | NO SE REPORTO CAUSA | 2 X 150 EN C/L | B22052400145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2022-05-24 | 82200 | keep | 0 | May | 2022 | 0.055986 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-05-24 09:28 | 2022-05-24 11:25 | 14 | 001:57 | P | TERMINACION SOTERRADA AVERIADA | 1 X 15 EN PROVISIONAL SE REMPLAZO PISTOLA AVERIADA EN PM | B22052400148 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 117 | 2022-05-24 | 1638 | keep | 0 | May | 2022 | 0.0011156 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2022-05-24 09:34 | 2022-05-24 09:35 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 2926 | keep | 0 | May | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
SAN JUAN | 2022-05-24 09:45 | 2022-05-24 17:23 | 90 | 007:38 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGANCHE SE CERRO PUENTE PRIMARIO | S22052400156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 458 | 2022-05-24 | 41220 | keep | 0 | May | 2022 | 0.028075 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2022-05-24 09:49 | 2022-05-24 12:59 | 160 | 003:10 | P | CONDUCTOR ROTO O ABIERTO | 1 X 140 EN C/L SE REPARO VIVO Y NEUTRAL | B22052400156 | New_Event | Primary Wire Break | Include | Include | Equipment | 190 | 2022-05-24 | 30400 | keep | 0 | May | 2022 | 0.020705 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
MAYAGÃœEZ | 2022-05-24 09:56 | 2022-05-24 14:00 | 12 | 004:04 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400065 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 244 | 2022-05-24 | 2928 | keep | 0 | May | 2022 | 0.0019942 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-24 09:59 | 2022-05-24 14:16 | 1 | 004:17 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B22052400147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-05-24 | 257 | keep | 0 | May | 2022 | 0.00017504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-05-24 10:08 | 2022-05-24 13:46 | 50 | 003:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 Y 1 X 25 EN CORTES DE LINEAS REEMPLAZO AISLADOR ROTO Y CAJA PRIMARIA QUEMADA | R22052400078 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 218 | 2022-05-24 | 10900 | keep | 0 | May | 2022 | 0.0074239 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-24 10:12 | 2022-05-25 15:12 | 10 | 028:60 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN C/L AEREO PROVISIONAL Y 1 X 15 EN XMR SE CONSTRUYO AEREO PROVISIONAL A T-10 | B22052300456 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1740 | 2022-05-24 | 17400 | keep | 0 | May | 2022 | 0.011851 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-24 10:20 | 2022-05-24 17:20 | 1 | 007:00 | P | ANIMAL | 1 X 40 RISER AVE | B22052300430 | Partial_restoration | Animals | Include | Include | Wildlife | 420 | 2022-05-24 | 420 | keep | 0 | May | 2022 | 0.00028606 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-24 10:22 | 2022-05-24 13:43 | 1 | 003:21 | P | ANIMAL | 1 X 25 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22052400062 | New_Event | Animals | Include | Include | Wildlife | 201 | 2022-05-24 | 201 | keep | 0 | May | 2022 | 0.0001369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-24 10:36 | 2022-05-24 16:36 | 100 | 006:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON DOS CAJAS PRIMARIAS | M22052400073 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2022-05-24 | 36000 | keep | 0 | May | 2022 | 0.024519 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-05-24 10:44 | 2022-05-24 12:27 | 10 | 001:43 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | C22052400119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-05-24 | 1030 | keep | 0 | May | 2022 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-24 10:48 | 2022-05-24 11:09 | 390 | 000:21 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA REEMPLAZO DE CAJA QUEMADA EN AZOTEA VIEJO SAN JUAN | S22052300410 | Additional_clients | Cutout Failure | Include | Include | Equipment | 21 | 2022-05-24 | 8190 | keep | 0 | May | 2022 | 0.0055782 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 10:55 | 2022-05-24 14:00 | 3 | 003:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA POR UNO DE 25KVA Y SE REPARARON CONEXIONES SECUNDARIAS | M22052400078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 185 | 2022-05-24 | 555 | keep | 0 | May | 2022 | 0.00037801 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-05-24 11:09 | 2022-05-24 14:00 | 157 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU-2 | B22052400192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-05-24 | 26847 | keep | 0 | May | 2022 | 0.018285 | 0.00010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 157
ARECIBO | 2022-05-24 11:11 | 2022-05-24 15:36 | 12 | 004:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO AISLADOR PARTIDO | A22052400055 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 265 | 2022-05-24 | 3180 | keep | 0 | May | 2022 | 0.0021659 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-24 11:30 | 2022-05-24 12:45 | 100 | 001:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M22052400095 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 75 | 2022-05-24 | 7500 | keep | 0 | May | 2022 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-24 11:39 | 2022-05-24 13:35 | 8 | 001:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22052400213 | New_Event | Secondary Wire Break | Include | Include | Equipment | 116 | 2022-05-24 | 928 | keep | 0 | May | 2022 | 0.00063206 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-05-24 11:41 | 2022-05-24 13:41 | 60 | 002:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22052400084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-05-24 | 7200 | keep | 0 | May | 2022 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-05-24 11:44 | 2022-05-24 12:12 | 6 | 000:28 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R22052400085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-05-24 | 168 | keep | 0 | May | 2022 | 0.00011442 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-05-24 11:54 | 2022-05-24 14:37 | 50 | 002:43 | P | DESGANCHE | 1 X 65 EN C/L | S22052400312 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-05-24 | 8150 | keep | 0 | May | 2022 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-05-24 11:55 | 2022-05-24 20:35 | 23 | 008:40 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22052400216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 520 | 2022-05-24 | 11960 | keep | 0 | May | 2022 | 0.0081459 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2022-05-24 12:01 | 2022-05-24 14:11 | 7 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22052400217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-05-24 | 910 | keep | 0 | May | 2022 | 0.0006198 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-05-24 12:08 | 2022-05-24 15:17 | 30 | 003:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR VIENTOS SE VERIFICO EN OMS CORREGIDO | A22052400063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2022-05-24 | 5670 | keep | 0 | May | 2022 | 0.0038618 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-05-24 12:15 | 2022-05-24 18:16 | 100 | 006:01 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052400102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2022-05-24 | 36100 | keep | 0 | May | 2022 | 0.024588 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-24 12:33 | 2022-05-24 15:32 | 36 | 002:59 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B22052400229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-05-24 | 6444 | keep | 0 | May | 2022 | 0.004389 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CANOVANAS | 2022-05-24 12:43 | 2022-05-24 15:38 | 1 | 002:55 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN RISER Y SE REEMPLAZO PARARRAYO | R22052400088 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 175 | 2022-05-24 | 175 | keep | 0 | May | 2022 | 0.00011919 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-05-24 13:00 | 2022-05-24 15:15 | 8 | 002:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 25KVA A 2.4KV POR UNO DEL MISMA CAPACIDAD Y CAJA PRIMARIA | P22052400100 | New_Event | Service Transformer Failure | Include | Include | Equipment | 135 | 2022-05-24 | 1080 | keep | 0 | May | 2022 | 0.00073558 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-24 13:03 | 2022-05-24 17:52 | 10 | 004:49 | P | TRANSFORMADOR AVERIADO | 2 X 20 EN XMR SE REMMPLAZO XMR 37.5KVA X 37.5KVA Y SE REPARO PUENTE PRIMARIO. | S22052400325 | New_Event | Service Transformer Failure | Include | Include | Equipment | 289 | 2022-05-24 | 2890 | keep | 0 | May | 2022 | 0.0019684 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-05-24 13:04 | 2022-05-24 16:54 | 250 | 003:50 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE PRIMARIO DE XMR (NO FUNDIO) | C22052400156 | New_Event | Primary Wire Break | Include | Include | Equipment | 230 | 2022-05-24 | 57500 | keep | 0 | May | 2022 | 0.039163 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
VEGA BAJA | 2022-05-24 13:04 | 2022-05-24 13:05 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 9101-02 (SPARE) QUE LLEVA 9101-04 | B22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 1494 | keep | 0 | May | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
CAGUAS | 2022-05-24 13:08 | 2022-05-24 15:03 | 1 | 001:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X10 EN XMR & SE REMPLAZO TOMA DE SERVICIO DE LA ESCUELA | C22052400158 | New_Event | Secondary Wire Break | Include | Include | Equipment | 115 | 2022-05-24 | 115 | keep | 0 | May | 2022 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-24 13:09 | 2022-05-24 14:40 | 3458 | 001:31 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR SE VRIFICO EL AREA Y LO QUE SE ENCONTRO FUE MAL TIEMPO DESCARGAS ELECTRICAS SE CERRO EL INTERRUPTOR | M22052400110 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 91 | 2022-05-24 | 314678 | keep | 0 | May | 2022 | 0.21433 | 0.0023552 | Sustained | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 1339 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 4017 | keep | 0 | May | 2022 | 0.002736 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 470 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 CARGA 6601-03 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 1410 | keep | 0 | May | 2022 | 0.00096034 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 2483 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 LLEVA CARGA DE 6601-02 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 7449 | keep | 0 | May | 2022 | 0.0050735 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 2190 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 6570 | keep | 0 | May | 2022 | 0.0044748 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 3006 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 9018 | keep | 0 | May | 2022 | 0.0061421 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 179 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 537 | keep | 0 | May | 2022 | 0.00036575 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 107 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 321 | keep | 0 | May | 2022 | 0.00021863 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 1666 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 4998 | keep | 0 | May | 2022 | 0.0034041 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 4387 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 13161 | keep | 0 | May | 2022 | 0.0089639 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 3147 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 CARGA POR 6704-01 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 9441 | keep | 0 | May | 2022 | 0.0064302 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-05-24 13:10 | 2022-05-24 13:13 | 4304 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-05-24 | 12912 | keep | 0 | May | 2022 | 0.0087943 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
AGUADILLA | 2022-05-24 13:10 | 2022-05-24 15:04 | 2366 | 001:54 | T | MAL TIEMPO/RAYOS | SE ABRIO MACHETES Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | M22052400293 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 114 | 2022-05-24 | 269724 | keep | 0 | May | 2022 | 0.18371 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
UTUADO | 2022-05-24 13:10 | 2022-05-24 14:08 | 1527 | 000:58 | T | DESGANCHE | SE RETIRO BAMBUA CRUZADO FASES DE LINEAS PRIMARIAS | A22052400072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-05-24 | 88566 | keep | 0 | May | 2022 | 0.060322 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
MAYAGÃœEZ | 2022-05-24 13:13 | 2022-05-24 13:30 | 1 | 000:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22052400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2022-05-24 | 17 | keep | 0 | May | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-24 13:19 | 2022-05-24 13:20 | 934 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 | M22052400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 934 | keep | 0 | May | 2022 | 0.00063614 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-05-24 13:19 | 2022-05-24 13:20 | 4 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 | M22052400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 4 | keep | 0 | May | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-05-24 13:19 | 2022-05-24 13:20 | 1479 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 | M22052400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 1479 | keep | 0 | May | 2022 | 0.0010073 | 0.0010073 | Momentary | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-05-24 13:19 | 2022-05-24 13:20 | 1841 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 | M22052400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 1841 | keep | 0 | May | 2022 | 0.0012539 | 0.0012539 | Momentary | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-05-24 13:19 | 2022-05-24 13:20 | 1950 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 | M22052400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 1950 | keep | 0 | May | 2022 | 0.0013281 | 0.0013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 1950
UTUADO | 2022-05-24 13:20 | 2022-05-24 13:24 | 12 | 000:04 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE DE BAMBUAS | A22052400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-05-24 | 48 | keep | 0 | May | 2022 | 3.2693e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-05-24 13:21 | 2022-05-25 09:02 | 50 | 019:41 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN SU-14 2 X 25 EN SU-15 Y SE CAMBIARON 2 PARARRAYOS EN LA SUBESTACION DE LA ESCUELA 1 X 65 EN CORTE DE LINEA | P22052400105 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1181 | 2022-05-24 | 59050 | keep | 0 | May | 2022 | 0.040219 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-24 13:24 | 2022-05-24 13:26 | 934 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | M22052400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-24 | 1868 | keep | 0 | May | 2022 | 0.0012723 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-05-24 13:24 | 2022-05-24 13:26 | 4 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | M22052400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-24 | 8 | keep | 0 | May | 2022 | 5.4488e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-05-24 13:24 | 2022-05-24 13:26 | 1479 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | M22052400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-24 | 2958 | keep | 0 | May | 2022 | 0.0020147 | 0.0010073 | Momentary | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-05-24 13:24 | 2022-05-24 13:26 | 1841 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | M22052400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-24 | 3682 | keep | 0 | May | 2022 | 0.0025078 | 0.0012539 | Momentary | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-05-24 13:24 | 2022-05-24 13:26 | 1950 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | M22052400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-24 | 3900 | keep | 0 | May | 2022 | 0.0026563 | 0.0013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 1950
BAYAMON | 2022-05-24 13:26 | 2022-05-24 14:38 | 7 | 001:12 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22052400247 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2022-05-24 | 504 | keep | 0 | May | 2022 | 0.00034327 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-05-24 13:26 | 2022-05-24 14:50 | 12 | 001:24 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE DE BAMBUAS | A22052400019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-05-24 | 1008 | keep | 0 | May | 2022 | 0.00068654 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-05-24 13:50 | 2022-05-24 20:05 | 40 | 006:15 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052400150 | New_Event | Primary Wire Break | Include | Include | Equipment | 375 | 2022-05-24 | 15000 | keep | 0 | May | 2022 | 0.010216 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-24 13:51 | 2022-05-24 20:43 | 4 | 006:52 | P | DESGANCHE | 1 X 80 DESGANCHE | S22052400336 | New_Event | Vegetation Contact | Include | Include | Vegetation | 412 | 2022-05-24 | 1648 | keep | 0 | May | 2022 | 0.0011224 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-05-24 13:55 | 2022-05-24 17:14 | 10 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22052400098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-05-24 | 1990 | keep | 0 | May | 2022 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 LLEVA CARGA DE 6010-02 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 1253 | keep | 0 | May | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 CARGA POR 6010-01 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 1266 | keep | 0 | May | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 411 | keep | 0 | May | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 1617 | keep | 0 | May | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 CARGA POR 6201-03 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 1017 | keep | 0 | May | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 LLEVA LA CARGA DE 6201-02 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 828 | keep | 0 | May | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 863 | keep | 0 | May | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 309 | keep | 0 | May | 2022 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 176 | keep | 0 | May | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-24 14:00 | 2022-05-24 14:01 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-24 | 974 | keep | 0 | May | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
MAYAGÃœEZ | 2022-05-24 14:01 | 2022-05-24 14:06 | 3 | 000:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA POR UNO DE 25KVA Y SE REPARARON CONEXIONES SECUNDARIAS | M22052400078 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 5 | 2022-05-24 | 15 | keep | 0 | May | 2022 | 1.0216e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 1253 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 LLEVA CARGA DE 6010-02 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 43855 | keep | 0 | May | 2022 | 0.029869 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 1266 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 CARGA POR 6010-01 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 44310 | keep | 0 | May | 2022 | 0.030179 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 411 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 14385 | keep | 0 | May | 2022 | 0.0097976 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 1617 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 56595 | keep | 0 | May | 2022 | 0.038547 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 1017 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 CARGA POR 6201-03 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 35595 | keep | 0 | May | 2022 | 0.024244 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 828 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 LLEVA LA CARGA DE 6201-02 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 28980 | keep | 0 | May | 2022 | 0.019738 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 863 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 30205 | keep | 0 | May | 2022 | 0.020572 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 309 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 10815 | keep | 0 | May | 2022 | 0.007366 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 176 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 6160 | keep | 0 | May | 2022 | 0.0041955 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-24 14:06 | 2022-05-24 14:41 | 974 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2022-05-24 | 34090 | keep | 0 | May | 2022 | 0.023219 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
SAN JUAN | 2022-05-24 14:32 | 2022-05-24 17:38 | 30 | 003:06 | P | DESGANCHE | 2 X 100 EN C/L SE DESGANCHO BAMBUA | R22052400103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-05-24 | 5580 | keep | 0 | May | 2022 | 0.0038005 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-24 14:35 | 2022-05-24 14:36 | 1444 | 000:01 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 6014-02 CON EL RECIERRE EN ON SE VERIFICO NO PERSONAL EN LA LINEAS Y SE CERRO EL INTERRUPTOR CARGA POR 6014-02 | M22052400000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-24 | 1444 | keep | 0 | May | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-05-24 14:35 | 2022-05-24 14:36 | 3630 | 000:01 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR CON EL RECIERRE EN ON SE VERIFICO NO PERSONAL EN LA LINEAS Y SE CERRO EL INTERRUPTOR LLEVA CARGA DE 6014-01 | M22052400000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-24 | 3630 | keep | 0 | May | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-05-24 14:36 | 2022-05-24 18:10 | 50 | 003:34 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400485 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 214 | 2022-05-24 | 10700 | keep | 0 | May | 2022 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-24 14:37 | 2022-05-24 18:25 | 7 | 003:48 | P | MAL TIEMPO/RAYOS | 2 X 5 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052400219 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 228 | 2022-05-24 | 1596 | keep | 0 | May | 2022 | 0.001087 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-05-24 14:41 | 2022-05-24 14:48 | 3 | 000:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA POR UNO DE 25KVA Y SE REPARARON CONEXIONES SECUNDARIAS | M22052400078 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 7 | 2022-05-24 | 21 | keep | 0 | May | 2022 | 1.4303e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 14:45 | 2022-05-24 14:47 | 179 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-05-24 | 358 | keep | 0 | May | 2022 | 0.00024383 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-05-24 14:48 | 2022-05-24 15:38 | 1617 | 000:50 | S | MAL TIEMPO/RAYOS | SUBESTACION FUNDIO LOS TRES FUSIBLE DE LA ALTA DEL TRANSFORMADOR POR DESCARGA ELECTRICA INFORMADO POR ANGEL SAN ANTONIO DE SUBESTACIONES SE REMPLAZARON LOS FUSIBLES Y SE RESTABLECIO EL SERVICIO | M22052400505 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 50 | 2022-05-24 | 80850 | keep | 0 | May | 2022 | 0.055067 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-05-24 14:48 | 2022-05-24 21:31 | 1017 | 006:43 | S | MAL TIEMPO/RAYOS | SUBESTACION FUNDIO LOS TRES FUSIBLE DE LA ALTA DEL TRANSFORMADOR POR DESCARGA ELECTRICA INFORMADO POR ANGEL SAN ANTONIO DE SUBESTACIONES SE REMPLAZARON LOS FUSIBLES Y SE RESTABLECIO EL SERVICIO CARGA POR 6201-03 | M22052400505 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 403 | 2022-05-24 | 409851 | keep | 0 | May | 2022 | 0.27915 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-24 14:48 | 2022-05-24 21:31 | 828 | 006:43 | S | MAL TIEMPO/RAYOS | SUBESTACION FUNDIO LOS TRES FUSIBLE DE LA ALTA DEL TRANSFORMADOR POR DESCARGA ELECTRICA INFORMADO POR ANGEL SAN ANTONIO DE SUBESTACIONES SE REMPLAZARON LOS FUSIBLES Y SE RESTABLECIO EL SERVICIO LLEVA LA CARGA DE 6201-02 | M22052400505 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 403 | 2022-05-24 | 333684 | keep | 0 | May | 2022 | 0.22727 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
ARECIBO | 2022-05-24 14:49 | 2022-05-24 19:09 | 90 | 004:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE LINEA SE REEMPLAZO PORTAFUSIBLE | A22052400098 | New_Event | Cutout Failure | Include | Include | Equipment | 260 | 2022-05-24 | 23400 | keep | 0 | May | 2022 | 0.015938 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2022-05-24 14:52 | 2022-05-24 14:53 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052400121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 4035 | keep | 0 | May | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-05-24 14:52 | 2022-05-24 17:44 | 400 | 002:52 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE PRIMARIO Y 1 X 80 EN CL | P22052400118 | New_Event | Primary Wire Break | Include | Include | Equipment | 172 | 2022-05-24 | 68800 | keep | 0 | May | 2022 | 0.046859 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
AGUADILLA | 2022-05-24 14:54 | 2022-05-24 17:40 | 80 | 002:46 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400261 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 166 | 2022-05-24 | 13280 | keep | 0 | May | 2022 | 0.0090449 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-05-24 15:02 | 2022-05-24 18:56 | 1337 | 003:54 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REMPLAZO AISLADOR ROTO EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M22052400284 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 234 | 2022-05-24 | 312858 | keep | 0 | May | 2022 | 0.21309 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
ARECIBO | 2022-05-24 15:02 | 2022-05-24 15:44 | 75 | 000:42 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A22052400106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2022-05-24 | 3150 | keep | 0 | May | 2022 | 0.0021455 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-05-24 15:04 | 2022-05-24 16:15 | 1500 | 001:11 | P | MAL TIEMPO/RAYOS | SE CERRARON LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LO QUE SE REPORTO FUE DESCARGAS ELECTRICAS | M22052400293 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 71 | 2022-05-24 | 106500 | keep | 0 | May | 2022 | 0.072537 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-24 15:09 | 2022-05-24 15:10 | 766 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1909-07 LLEVANDO 50% DEL 1709-03 | S22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 766 | keep | 0 | May | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-05-24 15:09 | 2022-05-24 15:10 | 1139 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1909-07 LLEVANDO 50% DEL 1709-03 | S22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 1139 | keep | 0 | May | 2022 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
MAYAGÃœEZ | 2022-05-24 15:09 | 2022-05-24 15:10 | 1352 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M22052400000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-24 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-24 15:09 | 2022-05-24 15:10 | 871 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M22052400000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-24 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-24 15:10 | 2022-05-24 15:11 | 1352 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M22052400000 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-24 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-24 15:10 | 2022-05-24 15:11 | 871 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M22052400000 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-24 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-24 15:16 | 2022-05-24 16:31 | 1253 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA LINEA Y SE ENERGIZO LA SUBESTACION LLEVA CARGA DE 6010-02 | M22052400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-05-24 | 93975 | keep | 0 | May | 2022 | 0.064006 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 15:16 | 2022-05-24 16:31 | 1266 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA LINEA Y SE ENERGIZO LA SUBESTACION CARGA POR 6010-01 | M22052400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-05-24 | 94950 | keep | 0 | May | 2022 | 0.06467 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 15:16 | 2022-05-24 16:31 | 411 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA LINEA Y SE ENERGIZO LA SUBESTACION | M22052400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-05-24 | 30825 | keep | 0 | May | 2022 | 0.020995 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 15:16 | 2022-05-24 16:31 | 863 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA LINEA Y SE ENERGIZO LA SUBESTACION | M22052400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-05-24 | 64725 | keep | 0 | May | 2022 | 0.044084 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 15:16 | 2022-05-24 16:31 | 309 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA LINEA Y SE ENERGIZO LA SUBESTACION | M22052400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-05-24 | 23175 | keep | 0 | May | 2022 | 0.015784 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 15:16 | 2022-05-24 16:31 | 176 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA LINEA Y SE ENERGIZO LA SUBESTACION | M22052400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-05-24 | 13200 | keep | 0 | May | 2022 | 0.0089905 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 15:16 | 2022-05-24 16:31 | 974 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA LINEA Y SE ENERGIZO LA SUBESTACION | M22052400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-05-24 | 73050 | keep | 0 | May | 2022 | 0.049754 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-24 15:20 | 2022-05-24 15:21 | 1352 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M22052400000 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-24 | 1352 | keep | 0 | May | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-05-24 15:20 | 2022-05-24 15:21 | 871 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M22052400000 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-24 | 871 | keep | 0 | May | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-05-24 15:21 | 2022-05-24 18:37 | 100 | 003:16 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400521 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 196 | 2022-05-24 | 19600 | keep | 0 | May | 2022 | 0.013349 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-24 15:23 | 2022-05-25 17:45 | 7 | 026:22 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22052400113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1582 | 2022-05-24 | 11074 | keep | 0 | May | 2022 | 0.0075425 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-05-24 15:23 | 2022-05-26 16:39 | 75 | 049:16 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052400113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2956 | 2022-05-24 | 221700 | keep | 0 | May | 2022 | 0.151 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-05-24 15:28 | 2022-05-24 16:39 | 12 | 001:11 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | A22052400115 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 71 | 2022-05-24 | 852 | keep | 0 | May | 2022 | 0.00058029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-05-24 15:30 | 2022-05-24 22:46 | 30 | 007:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | S22052400367 | New_Event | Cutout Failure | Include | Include | Equipment | 436 | 2022-05-24 | 13080 | keep | 0 | May | 2022 | 0.0089087 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-24 15:32 | 2022-05-24 15:33 | 767 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 1909-07 QUE LLEVA 50% DEL 1709-03 | S22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 767 | keep | 0 | May | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-05-24 15:32 | 2022-05-24 15:33 | 1139 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1909-07 QUE LLEVA 50% DEL 1709-03 | S22052400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 1139 | keep | 0 | May | 2022 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
SAN JUAN | 2022-05-24 15:33 | 2022-05-24 15:39 | 1825 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 RTU ESTA DOWN | S22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-05-24 | 10950 | keep | 0 | May | 2022 | 0.007458 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-05-24 15:33 | 2022-05-24 15:39 | 47 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 RTU ESTA DOWN | S22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-05-24 | 282 | keep | 0 | May | 2022 | 0.00019207 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-05-24 15:33 | 2022-05-24 15:39 | 315 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 RTU ESTA DOWN | S22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-05-24 | 1890 | keep | 0 | May | 2022 | 0.0012873 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-05-24 15:33 | 2022-05-24 15:39 | 2 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 RTU ESTA DOWN | S22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-05-24 | 12 | keep | 0 | May | 2022 | 8.1731e-06 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-05-24 15:33 | 2022-05-24 15:39 | 2391 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 RTU ESTA DOWN | S22052400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-05-24 | 14346 | keep | 0 | May | 2022 | 0.009771 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2022-05-24 15:33 | 2022-05-24 15:39 | 2276 | 000:06 | S | LINEA DE TRANSMISION 38KV | OPERACION BREAKER 3030 (LINEA 3,000) | C22052400020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-05-24 | 13656 | keep | 0 | May | 2022 | 0.009301 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-05-24 15:33 | 2022-05-24 15:39 | 777 | 000:06 | S | LINEA DE TRANSMISION 38KV | OPERACION BREAKER 3030 (LINEA 3,000) | C22052400020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-05-24 | 4662 | keep | 0 | May | 2022 | 0.0031753 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-05-24 15:33 | 2022-05-24 15:39 | 12 | 000:06 | S | LINEA DE TRANSMISION 38KV | OPERACION BREAKER 3030 (LINEA 3,000) | C22052400020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-05-24 | 72 | keep | 0 | May | 2022 | 4.9039e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-24 15:33 | 2022-05-24 15:39 | 1290 | 000:06 | S | LINEA DE TRANSMISION 38KV | OPERACION BREAKER 3030 (LINEA 3,000) | C22052400020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-05-24 | 7740 | keep | 0 | May | 2022 | 0.0052717 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
CAGUAS | 2022-05-24 15:37 | 2022-05-24 18:08 | 111 | 002:31 | P | MAL TIEMPO/RAYOS | 1X80 EN C/L (POR RAYO) | C22052400194 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 151 | 2022-05-24 | 16761 | keep | 0 | May | 2022 | 0.011416 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
MAYAGÃœEZ | 2022-05-24 15:38 | 2022-05-24 16:56 | 50 | 001:18 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400055 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 78 | 2022-05-24 | 3900 | keep | 0 | May | 2022 | 0.0026563 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-24 15:40 | 2022-05-24 19:16 | 40 | 003:36 | P | SECUNDARIA/DESGANCHE | ABRIR XMR PARA REPARAR SECUNDARIA Y DESGANCHE | S22052400295 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 216 | 2022-05-24 | 8640 | keep | 0 | May | 2022 | 0.0058847 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-24 15:43 | 2022-05-24 16:55 | 928 | 001:12 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERUPTOR 1338-02 SE SECCIONALIZO ALAMBRE EN EL SUELO LLEVA 10% 1422-03 Y 10% 1422-05 | S22052400384 | New_Event | Primary Wire Break | Include | Include | Equipment | 72 | 2022-05-24 | 66816 | keep | 0 | May | 2022 | 0.045508 | 0.00063206 | Sustained | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2022-05-24 15:43 | 2022-05-24 16:55 | 38 | 001:12 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERUPTOR 1338-02 SE SECCIONALIZO ALAMBRE EN EL SUELO LLEVA 10% 1422-03 Y 10% 1422-05 | S22052400384 | New_Event | Primary Wire Break | Include | Include | Equipment | 72 | 2022-05-24 | 2736 | keep | 0 | May | 2022 | 0.0018635 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
SAN JUAN | 2022-05-24 15:43 | 2022-05-24 18:33 | 64 | 002:50 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE DEL SUELO Y SE CERRARON MACHETES | S22052400384 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2022-05-24 | 10880 | keep | 0 | May | 2022 | 0.0074103 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2022-05-24 15:48 | 2022-05-24 21:43 | 97 | 005:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN C/L Y 2 X 20 EN XMR | S22052400392 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 355 | 2022-05-24 | 34435 | keep | 0 | May | 2022 | 0.023454 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
HUMACAO | 2022-05-24 15:57 | 2022-05-24 17:05 | 10 | 001:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO CONDUCTOR SECUNDARIO (NO FUNDIO) | C22052400205 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2022-05-24 | 680 | keep | 0 | May | 2022 | 0.00046314 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-05-24 16:01 | 2022-05-24 20:21 | 10 | 004:20 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR NO CAUSA | P22052400142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2022-05-24 | 2600 | keep | 0 | May | 2022 | 0.0017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-05-24 16:06 | 2022-05-24 18:07 | 6 | 002:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | P22052400143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-05-24 | 726 | keep | 0 | May | 2022 | 0.00049448 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-05-24 16:10 | 2022-05-25 09:25 | 5 | 017:15 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22052400210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1035 | 2022-05-24 | 5175 | keep | 0 | May | 2022 | 0.0035247 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-05-24 16:12 | 2022-05-24 18:19 | 289 | 002:07 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | S22052400416 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2022-05-24 | 36703 | keep | 0 | May | 2022 | 0.024998 | 0.00019684 | Sustained | FALSE | FALSE | Not_TMED_Event | 289
GUAYAMA | 2022-05-24 16:15 | 2022-05-24 16:16 | 4132 | 000:01 | T | ANIMAL | RECIERRE | P22052400153 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-24 | 4132 | keep | 0 | May | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-05-24 16:15 | 2022-05-24 16:16 | 4279 | 000:01 | T | ANIMAL | RECIERRE | P22052400153 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-24 | 4279 | keep | 0 | May | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-05-24 16:15 | 2022-05-24 16:16 | 464 | 000:01 | T | ANIMAL | RECIERRE | P22052400153 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-24 | 464 | keep | 0 | May | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-05-24 16:16 | 2022-05-24 16:57 | 35 | 000:41 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE | P22052400154 | 1st_after_momentary | Animals | Include | Include | Wildlife | 41 | 2022-05-24 | 1435 | keep | 0 | May | 2022 | 0.00097737 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2022-05-24 16:17 | 2022-05-24 17:21 | 80 | 001:04 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA POR RAYOS | A22052400131 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 64 | 2022-05-24 | 5120 | keep | 0 | May | 2022 | 0.0034872 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-24 16:23 | 2022-05-25 15:10 | 260 | 022:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22052400451 | New_Event | Primary Wire Break | Include | Include | Equipment | 1367 | 2022-05-24 | 355420 | keep | 0 | May | 2022 | 0.24207 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
BARRANQUITAS | 2022-05-24 16:25 | 2022-05-24 17:27 | 20 | 001:02 | P | MAL TIEMPO/RAYOS | 1X10 EN XMR (MAL TIEMPO/RAYOS) | C22052400213 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 62 | 2022-05-24 | 1240 | keep | 0 | May | 2022 | 0.00084456 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-24 16:33 | 2022-05-24 20:20 | 15 | 003:47 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR POR RAYOS | A22052400133 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 227 | 2022-05-24 | 3405 | keep | 0 | May | 2022 | 0.0023191 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-05-24 16:34 | 2022-05-25 17:20 | 10 | 024:46 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22052400134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1486 | 2022-05-24 | 14860 | keep | 0 | May | 2022 | 0.010121 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-24 16:45 | 2022-05-25 12:20 | 2 | 019:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR UNO DE 25KVA | A22052400137 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1175 | 2022-05-24 | 2350 | keep | 0 | May | 2022 | 0.0016006 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-05-24 16:55 | 2022-05-24 19:50 | 100 | 002:55 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400496 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 175 | 2022-05-24 | 17500 | keep | 0 | May | 2022 | 0.011919 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-24 16:56 | 2022-05-24 21:31 | 12 | 004:35 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400065 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 275 | 2022-05-24 | 3300 | keep | 0 | May | 2022 | 0.0022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-24 16:57 | 2022-05-25 16:20 | 50 | 023:23 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A22052400141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1403 | 2022-05-24 | 70150 | keep | 0 | May | 2022 | 0.047779 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-24 17:00 | 2022-05-24 17:30 | 6 | 000:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CERRO PUENTE ABIERTO SECUNDARIO | B22052400290 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-05-24 | 180 | keep | 0 | May | 2022 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-24 17:03 | 2022-05-24 19:50 | 85 | 002:47 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400511 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 167 | 2022-05-24 | 14195 | keep | 0 | May | 2022 | 0.0096681 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
MAYAGÃœEZ | 2022-05-24 17:06 | 2022-05-24 20:43 | 50 | 003:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22052400514 | New_Event | Cutout Failure | Include | Include | Equipment | 217 | 2022-05-24 | 10850 | keep | 0 | May | 2022 | 0.0073899 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-24 17:06 | 2022-05-25 11:35 | 6 | 018:29 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052400515 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1109 | 2022-05-24 | 6654 | keep | 0 | May | 2022 | 0.004532 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-24 17:11 | 2022-05-24 17:12 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 LLEVA 1909-09 | S22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 222 | keep | 0 | May | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-05-24 17:11 | 2022-05-24 17:12 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 LLEVA 1909-09 | S22052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 4456 | keep | 0 | May | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
CANOVANAS | 2022-05-24 17:17 | 2022-05-24 18:18 | 40 | 001:01 | P | ANIMAL | 1 X 5O EN C/L Y 1 X 15 EN XMR AVE | R22052400119 | New_Event | Animals | Include | Include | Wildlife | 61 | 2022-05-24 | 2440 | keep | 0 | May | 2022 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-05-24 17:21 | 2022-05-24 19:03 | 25 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22052400120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2022-05-24 | 2550 | keep | 0 | May | 2022 | 0.0017368 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-24 17:26 | 2022-05-24 23:25 | 50 | 005:59 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052400532 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2022-05-24 | 17950 | keep | 0 | May | 2022 | 0.012226 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-24 17:32 | 2022-05-24 18:19 | 12 | 000:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRA EN PEDESTAL | S22052400464 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2022-05-24 | 564 | keep | 0 | May | 2022 | 0.00038414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-24 17:38 | 2022-05-24 20:50 | 25 | 003:12 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA Y 2 X 15 EN TRANSFORMADOR POR RAYOS | A22052400151 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 192 | 2022-05-24 | 4800 | keep | 0 | May | 2022 | 0.0032693 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-24 17:43 | 2022-05-25 10:54 | 100 | 017:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22052400471 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1031 | 2022-05-24 | 103100 | keep | 0 | May | 2022 | 0.070221 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-24 17:43 | 2022-05-24 17:44 | 386 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRRE DE INTERRUPTOR | S22052400472 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 386 | keep | 0 | May | 2022 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
BARRANQUITAS | 2022-05-24 17:46 | 2022-05-25 15:50 | 20 | 022:04 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L NO CAUSA | C22052400221 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1324 | 2022-05-24 | 26480 | keep | 0 | May | 2022 | 0.018035 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-24 17:50 | 2022-05-24 18:53 | 56 | 001:03 | P | ANIMAL | 2 X 50 C/L AVE | B22052400291 | New_Event | Animals | Include | Include | Wildlife | 63 | 2022-05-24 | 3528 | keep | 0 | May | 2022 | 0.0024029 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2022-05-24 18:01 | 2022-05-24 20:30 | 53 | 002:29 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22052400294 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-05-24 | 7897 | keep | 0 | May | 2022 | 0.0053786 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BAYAMON | 2022-05-24 18:04 | 2022-05-25 12:49 | 60 | 018:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y SE REEMPLAZO CAJA EN RISER | S22052400123 | New_Event | Cutout Failure | Include | Include | Equipment | 1125 | 2022-05-24 | 67500 | keep | 0 | May | 2022 | 0.045974 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-24 18:05 | 2022-05-24 19:02 | 125 | 000:57 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052400549 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-05-24 | 7125 | keep | 0 | May | 2022 | 0.0048528 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
PONCE | 2022-05-24 18:15 | 2022-05-24 18:16 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052400192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-24 | 3114 | keep | 0 | May | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2022-05-24 18:30 | 2022-05-25 03:52 | 1746 | 009:22 | T | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR SE REPARO TERMINACION SOTERRADA EN MH-2 Y SE CERRO POR CONTROL | B22052400299 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 562 | 2022-05-24 | 981252 | keep | 0 | May | 2022 | 0.66833 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
MAYAGÃœEZ | 2022-05-24 18:36 | 2022-05-25 14:39 | 33 | 020:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22052400561 | New_Event | Primary Wire Break | Include | Include | Equipment | 1203 | 2022-05-24 | 39699 | keep | 0 | May | 2022 | 0.027039 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2022-05-24 19:02 | 2022-05-25 11:10 | 60 | 016:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052400570 | New_Event | Vegetation Contact | Include | Include | Vegetation | 968 | 2022-05-24 | 58080 | keep | 0 | May | 2022 | 0.039558 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-24 19:06 | 2022-05-25 05:50 | 15 | 010:44 | P | DESGANCHE | 2 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22052400573 | New_Event | Vegetation Contact | Include | Include | Vegetation | 644 | 2022-05-24 | 9660 | keep | 0 | May | 2022 | 0.0065794 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-05-24 19:22 | 2022-05-24 21:20 | 200 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 140 EN CONVERTIDOR | B22052400330 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2022-05-24 | 23600 | keep | 0 | May | 2022 | 0.016074 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-24 19:34 | 2022-05-25 05:30 | 3 | 009:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | M22052400585 | New_Event | Secondary Wire Break | Include | Include | Equipment | 596 | 2022-05-24 | 1788 | keep | 0 | May | 2022 | 0.0012178 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-05-24 19:42 | 2022-05-25 07:21 | 62 | 011:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22052400229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 699 | 2022-05-24 | 43338 | keep | 0 | May | 2022 | 0.029517 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
PONCE | 2022-05-24 19:43 | 2022-05-25 06:32 | 15 | 010:49 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 2 X 15 EN TRANSFORMADOR SE RETESO SECUNDARIA | P22052400212 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 649 | 2022-05-24 | 9735 | keep | 0 | May | 2022 | 0.0066305 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-05-24 19:46 | 2022-05-25 13:11 | 70 | 017:25 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN CORTE DE LINEA Y 3 X 15 EN TRANSFORMADOR SE REPARO BUSHING PRIMARIO TRANSFORMADOR | A22052400163 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1045 | 2022-05-24 | 73150 | keep | 0 | May | 2022 | 0.049822 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-05-24 19:47 | 2022-05-25 07:43 | 22 | 011:56 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C22052400232 | New_Event | Animals | Include | Include | Wildlife | 716 | 2022-05-24 | 15752 | keep | 0 | May | 2022 | 0.010729 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2022-05-24 19:52 | 2022-05-24 20:15 | 10 | 000:23 | P | TRANSFORMADOR AVERIADO | SE AJUSTARON BUSHING SECUNDARIOS DE TRANSFORMADOR YA QUE SE ENCONTRABAN SUELTOS | M22052400546 | New_Event | Service Transformer Failure | Include | Include | Equipment | 23 | 2022-05-24 | 230 | keep | 0 | May | 2022 | 0.00015665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-24 19:55 | 2022-05-25 07:37 | 35 | 011:42 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22052400490 | New_Event | Vegetation Contact | Include | Include | Vegetation | 702 | 2022-05-24 | 24570 | keep | 0 | May | 2022 | 0.016735 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-05-24 20:00 | 2022-05-24 20:02 | 1444 | 000:02 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 6014-02 | M22052400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-24 | 2888 | keep | 0 | May | 2022 | 0.001967 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-05-24 20:00 | 2022-05-24 20:02 | 3630 | 000:02 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DE 6014-01 | M22052400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-05-24 | 7260 | keep | 0 | May | 2022 | 0.0049448 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-05-24 20:02 | 2022-05-24 21:15 | 200 | 001:13 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052400600 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-05-24 | 14600 | keep | 0 | May | 2022 | 0.009944 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-24 20:04 | 2022-05-25 19:00 | 1000 | 022:56 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22052400592 | New_Event | Primary Wire Break | Include | Include | Equipment | 1376 | 2022-05-24 | 1376000 | keep | 0 | May | 2022 | 0.93719 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
MAYAGÃœEZ | 2022-05-24 20:11 | 2022-05-25 19:35 | 1 | 023:24 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M22052400598 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1404 | 2022-05-24 | 1404 | keep | 0 | May | 2022 | 0.00095626 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-24 20:25 | 2022-05-24 20:45 | 150 | 000:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052400616 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-05-24 | 3000 | keep | 0 | May | 2022 | 0.0020433 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-05-24 20:31 | 2022-05-25 03:16 | 1 | 006:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS. EN SCADA APARECE ALIMENTADOR CON SOLO 1 CLIENTE PERO EL PERSONAL DE CAMPO MENCIONA QUE HAY MUCHO MAS. EN ESTA INTERRUPCION HAY CERCA DE 150 CLIENTES SEGUN FUE CONFIRMADO CON PERSONAL DE CAMPO | M22052400605 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2022-05-24 | 405 | keep | 0 | May | 2022 | 0.00027584 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-24 20:38 | 2022-05-24 21:51 | 13 | 001:13 | P | CONDUCTOR ARRIADO O CRUZADO | SE CERRO PUENTE ABIERTO | R22052400128 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 73 | 2022-05-24 | 949 | keep | 0 | May | 2022 | 0.00064636 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-05-24 21:00 | 2022-05-25 10:15 | 1 | 013:15 | P | MAL TIEMPO/RAYOS | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052400026 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 795 | 2022-05-24 | 795 | keep | 0 | May | 2022 | 0.00054147 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-24 21:12 | 2022-05-25 15:59 | 6 | 018:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO SECUNDARIA | S22052400504 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1127 | 2022-05-24 | 6762 | keep | 0 | May | 2022 | 0.0046056 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-24 21:31 | 2022-05-25 11:45 | 300 | 014:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON PUENTES PRIMARIOS ABIERTOS | M22052400634 | New_Event | Primary Wire Break | Include | Include | Equipment | 854 | 2022-05-24 | 256200 | keep | 0 | May | 2022 | 0.1745 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-05-24 21:31 | 2022-05-25 12:56 | 3 | 015:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA POR UNO DE 25KVA Y SE REPARARON CONEXIONES SECUNDARIAS | M22052400078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 925 | 2022-05-24 | 2775 | keep | 0 | May | 2022 | 0.00189 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-05-24 21:54 | 2022-05-25 12:56 | 200 | 015:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052400637 | New_Event | Primary Wire Break | Include | Include | Equipment | 902 | 2022-05-24 | 180400 | keep | 0 | May | 2022 | 0.12287 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-24 21:59 | 2022-05-25 00:55 | 726 | 002:56 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR 1303-03 SE REALIZARON OPERACIONES Y SE ENCONTRO AVERIA EN EL N/O DEL SU-1 LLEVA EL 1346-04. | S22052400508 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 176 | 2022-05-24 | 127776 | keep | 0 | May | 2022 | 0.087028 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-05-24 21:59 | 2022-05-25 00:55 | 3932 | 002:56 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR 1303-03 SE REALIZARON OPERACIONES Y SE ENCONTRO AVERIA EN EL N/O DEL SU-1 LLEVA EL 1346-04. | S22052400508 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 176 | 2022-05-24 | 692032 | keep | 0 | May | 2022 | 0.47134 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
ARECIBO | 2022-05-24 22:07 | 2022-05-25 17:24 | 20 | 019:17 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22052400170 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1157 | 2022-05-24 | 23140 | keep | 0 | May | 2022 | 0.015761 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-05-24 22:17 | 2022-05-25 06:15 | 683 | 007:58 | P | NO SE REPORTO CAUSA | 1 X 140 EN CONVERTIDOR Y 1 X 100 EN C/L | B22052400364 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 478 | 2022-05-24 | 326474 | keep | 0 | May | 2022 | 0.22236 | 0.00046519 | Sustained | FALSE | FALSE | Not_TMED_Event | 683
MAYAGÃœEZ | 2022-05-24 22:28 | 2022-05-25 11:01 | 60 | 012:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052400643 | New_Event | Vegetation Contact | Include | Include | Vegetation | 753 | 2022-05-24 | 45180 | keep | 0 | May | 2022 | 0.030772 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-05-24 23:27 | 2022-05-25 08:07 | 45 | 008:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR POR AISLADOR RIGIDO | B22052400369 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 520 | 2022-05-24 | 23400 | keep | 0 | May | 2022 | 0.015938 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-05-24 23:36 | 2022-05-25 10:23 | 18 | 010:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 SMU 10 AMP. SE AJUSTO SECUNDARIA EN LA BARRA DEL TRANSFORMADOR | R22052400132 | New_Event | Secondary Wire Break | Include | Include | Equipment | 647 | 2022-05-24 | 11646 | keep | 0 | May | 2022 | 0.007932 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-05-24 23:38 | 2022-05-25 00:09 | 150 | 000:31 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | S22052400551 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 31 | 2022-05-24 | 4650 | keep | 0 | May | 2022 | 0.0031671 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-05-25 00:55 | 2022-05-25 00:56 | 603 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-08 LLEVA 9206-09 | B22052500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 603 | keep | 0 | May | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-05-25 00:55 | 2022-05-25 00:56 | 6 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-08 LLEVA 9206-09 | B22052500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 6 | keep | 0 | May | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-25 01:30 | 2022-05-25 01:31 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22052500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 312 | keep | 0 | May | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
ARECIBO | 2022-05-25 01:38 | 2022-05-25 10:30 | 25 | 008:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22052500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 532 | 2022-05-25 | 13300 | keep | 0 | May | 2022 | 0.0090586 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-25 01:44 | 2022-05-25 01:45 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22052500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 990 | keep | 0 | May | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
ARECIBO | 2022-05-25 03:40 | 2022-05-25 03:41 | 67 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | A22052500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 67 | keep | 0 | May | 2022 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-05-25 03:44 | 2022-05-25 09:45 | 231 | 006:01 | P | ANIMAL | 1 X 80 Y 1 X 65 C/L AVE | B22052500008 | New_Event | Animals | Include | Include | Wildlife | 361 | 2022-05-25 | 83391 | keep | 0 | May | 2022 | 0.056797 | 0.00015733 | Sustained | FALSE | FALSE | Not_TMED_Event | 231
ARECIBO | 2022-05-25 03:50 | 2022-05-25 07:15 | 40 | 003:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 30 EN RISER REQUIERE DESGANCHE | A22052500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2022-05-25 | 8200 | keep | 0 | May | 2022 | 0.005585 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-25 04:09 | 2022-05-25 04:19 | 40 | 000:10 | P | NO SE REPORTO CAUSA | 1SMU X 20 EN SU-10 | B22052500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-05-25 | 400 | keep | 0 | May | 2022 | 0.00027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-25 04:19 | 2022-05-25 04:22 | 1746 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B22052500012 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-05-25 | 5238 | keep | 0 | May | 2022 | 0.0035676 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-25 04:22 | 2022-05-25 12:00 | 21 | 007:38 | P | NO SE REPORTO CAUSA | 1 X 125 EN SU-13 | B22052500021 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 458 | 2022-05-25 | 9618 | keep | 0 | May | 2022 | 0.0065508 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
ARECIBO | 2022-05-25 05:41 | 2022-05-25 14:13 | 800 | 008:32 | P | MAL TIEMPO/RAYOS | 3 X 200 EN ENTRADA DE CONVERTIDOR SE LE HIZO PRUEBAS AL CONVERTIDOR POR PERSONAL DE SUBESTACIONES SE DETERMINO QUE FUE POR DESCARGAS ELECTRICAS | A22052500038 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 512 | 2022-05-25 | 409600 | keep | 0 | May | 2022 | 0.27898 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
VEGA BAJA | 2022-05-25 06:03 | 2022-05-25 10:40 | 150 | 004:37 | P | ANIMAL | 1 X 100 EN C/L 1 X 50 AVE | B22052500018 | New_Event | Animals | Include | Include | Wildlife | 277 | 2022-05-25 | 41550 | keep | 0 | May | 2022 | 0.0283 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-05-25 06:10 | 2022-05-25 07:38 | 50 | 001:28 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P22052500005 | New_Event | Animals | Include | Include | Wildlife | 88 | 2022-05-25 | 4400 | keep | 0 | May | 2022 | 0.0029968 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-25 06:22 | 2022-05-25 09:15 | 70 | 002:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REMPLAZO AISLADOR ROTO | A22052500041 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 173 | 2022-05-25 | 12110 | keep | 0 | May | 2022 | 0.0082481 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-05-25 06:56 | 2022-05-25 21:30 | 30 | 014:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052500011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 874 | 2022-05-25 | 26220 | keep | 0 | May | 2022 | 0.017858 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-05-25 06:57 | 2022-05-25 09:15 | 175 | 002:18 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R22052500003 | New_Event | Animals | Include | Include | Wildlife | 138 | 2022-05-25 | 24150 | keep | 0 | May | 2022 | 0.016448 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
MAYAGÃœEZ | 2022-05-25 07:11 | 2022-05-25 18:31 | 1 | 011:20 | P | MAL TIEMPO/RAYOS | 2 X 25 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22052500012 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 680 | 2022-05-25 | 680 | keep | 0 | May | 2022 | 0.00046314 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-25 07:16 | 2022-05-26 10:21 | 4 | 027:05 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052500013 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1625 | 2022-05-25 | 6500 | keep | 0 | May | 2022 | 0.0044271 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-05-25 07:34 | 2022-05-25 15:00 | 40 | 007:26 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052500032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 446 | 2022-05-25 | 17840 | keep | 0 | May | 2022 | 0.012151 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-25 07:37 | 2022-05-25 07:39 | 1825 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22052500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 3650 | keep | 0 | May | 2022 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-05-25 07:37 | 2022-05-25 07:39 | 47 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22052500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 94 | keep | 0 | May | 2022 | 6.4023e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-05-25 07:37 | 2022-05-25 07:39 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22052500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 630 | keep | 0 | May | 2022 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-05-25 07:37 | 2022-05-25 07:39 | 2 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22052500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 4 | keep | 0 | May | 2022 | 2.7244e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-05-25 07:37 | 2022-05-25 07:39 | 2391 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22052500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 4782 | keep | 0 | May | 2022 | 0.003257 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2022-05-25 07:37 | 2022-05-25 07:39 | 2276 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C22052500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 4552 | keep | 0 | May | 2022 | 0.0031003 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-05-25 07:37 | 2022-05-25 07:39 | 777 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C22052500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 1554 | keep | 0 | May | 2022 | 0.0010584 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-05-25 07:37 | 2022-05-25 07:39 | 12 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C22052500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 24 | keep | 0 | May | 2022 | 1.6346e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-25 07:37 | 2022-05-25 07:39 | 1290 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C22052500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 2580 | keep | 0 | May | 2022 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2022-05-25 07:39 | 2022-05-26 11:33 | 35 | 027:54 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22052400490 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1674 | 2022-05-25 | 58590 | keep | 0 | May | 2022 | 0.039905 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-25 07:51 | 2022-05-25 12:00 | 32 | 004:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22052500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-05-25 | 7968 | keep | 0 | May | 2022 | 0.005427 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
UTUADO | 2022-05-25 07:51 | 2022-05-25 20:10 | 7 | 012:19 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 25 EN CONVERTIDOR BACK TO BACK SE REMPLAZO POSTE PRIMARIO PARTIDO QUE CAUSO AVERIA SE REPARO LINEA PRIMARIA ROTA Y SE REMPLAZO UNO DE LOS TRANSFORMADORES AVERIADO DEL BACK TO BACK DE 25KVA POR LA MISMA CAPACIDAD | A22052500066 | New_Event | Primary Pole Failure | Include | Include | Equipment | 739 | 2022-05-25 | 5173 | keep | 0 | May | 2022 | 0.0035233 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-05-25 08:01 | 2022-05-25 15:15 | 40 | 007:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE URGENTE | M22052500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2022-05-25 | 17360 | keep | 0 | May | 2022 | 0.011824 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-25 08:04 | 2022-05-25 12:26 | 45 | 004:22 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22052500046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-05-25 | 11790 | keep | 0 | May | 2022 | 0.0080301 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-05-25 08:17 | 2022-05-25 12:00 | 30 | 003:43 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052500032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 223 | 2022-05-25 | 6690 | keep | 0 | May | 2022 | 0.0045565 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-25 08:29 | 2022-05-26 01:20 | 15 | 016:51 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | M22052500034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1011 | 2022-05-25 | 15165 | keep | 0 | May | 2022 | 0.010329 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-05-25 08:46 | 2022-05-25 10:48 | 44 | 002:02 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C22052500014 | New_Event | Animals | Include | Include | Wildlife | 122 | 2022-05-25 | 5368 | keep | 0 | May | 2022 | 0.0036561 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BARRANQUITAS | 2022-05-25 08:47 | 2022-05-25 16:19 | 141 | 007:32 | P | DESGANCHE | 2 X 50 EN C/L | C22052500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 452 | 2022-05-25 | 63732 | keep | 0 | May | 2022 | 0.043408 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
CAGUAS | 2022-05-25 08:49 | 2022-05-25 14:15 | 1 | 005:26 | P | DESGANCHE | 1 X 50 EN RISER | C22052500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2022-05-25 | 326 | keep | 0 | May | 2022 | 0.00022204 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-05-25 09:02 | 2022-05-25 09:03 | 396 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | P22052500021 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-05-25 | 396 | keep | 0 | May | 2022 | 0.00026971 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-25 09:03 | 2022-05-25 11:22 | 50 | 002:19 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN SU-14 2 X 25 EN SU-15 Y SE CAMBIARON 2 PARARRAYOS EN LA SUBESTACION DE LA ESCUELA 1 X 65 EN CORTE DE LINEA | P22052400105 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 139 | 2022-05-25 | 6950 | keep | 0 | May | 2022 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-25 09:04 | 2022-05-25 14:30 | 25 | 005:26 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052500049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2022-05-25 | 8150 | keep | 0 | May | 2022 | 0.0055509 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-25 09:07 | 2022-05-25 19:45 | 7 | 010:38 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052500050 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 638 | 2022-05-25 | 4466 | keep | 0 | May | 2022 | 0.0030418 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-25 09:12 | 2022-05-25 11:30 | 163 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22052500037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2022-05-25 | 22494 | keep | 0 | May | 2022 | 0.015321 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
VEGA BAJA | 2022-05-25 09:28 | 2022-05-25 11:34 | 50 | 002:06 | P | DESGANCHE | 2 X 30 EN C/L RAMA | B22052500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-05-25 | 6300 | keep | 0 | May | 2022 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-25 09:31 | 2022-05-25 12:10 | 10 | 002:39 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052500060 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 159 | 2022-05-25 | 1590 | keep | 0 | May | 2022 | 0.0010829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-25 09:33 | 2022-05-25 13:45 | 50 | 004:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22052500061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 252 | 2022-05-25 | 12600 | keep | 0 | May | 2022 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-25 09:57 | 2022-05-25 12:57 | 3 | 003:00 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA DE LA CAJA PRIMARIA | A22052500096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-05-25 | 540 | keep | 0 | May | 2022 | 0.00036779 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-05-25 10:00 | 2022-05-25 11:20 | 10 | 001:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR CONECTORES QUEMADOS EN BAJANTE SECUNDARIO SUBIO TAP 2 AL 4 QUEDO 123/146 | C22052300164 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2022-05-25 | 800 | keep | 0 | May | 2022 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-25 10:23 | 2022-05-26 11:28 | 100 | 025:05 | P | MAL TIEMPO/RAYOS | 1 X 50 Y 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS RELACIONADO A EVENTO A22052500227 | A22052600077 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1505 | 2022-05-25 | 150500 | keep | 0 | May | 2022 | 0.1025 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-25 10:35 | 2022-05-25 10:43 | 74 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS ESTA MANEJANDO EL 50% DE LA CARGA DEL 1529-13 POR VIA LIBRE EN CAMBIO DE POSTE. SU CARGA POR 1529-11 | S22052500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-05-25 | 592 | keep | 0 | May | 2022 | 0.00040321 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2022-05-25 10:35 | 2022-05-25 10:43 | 1370 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS ESTA MANEJANDO EL 50% DE LA CARGA DEL 1529-13 POR VIA LIBRE EN CAMBIO DE POSTE. | S22052500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-05-25 | 10960 | keep | 0 | May | 2022 | 0.0074648 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2022-05-25 10:35 | 2022-05-25 10:43 | 99 | 000:08 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-11 Y SE CERRO POR SCADA. ADEMAS ESTA MANEJANDO EL 50% DE LA CARGA DEL 1529-13 POR VIA LIBRE EN CAMBIO DE POSTE. | S22052500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-05-25 | 792 | keep | 0 | May | 2022 | 0.00053943 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
GUAYAMA | 2022-05-25 10:45 | 2022-05-25 13:40 | 4 | 002:55 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR POR AVE | P22052500035 | New_Event | Animals | Include | Include | Wildlife | 175 | 2022-05-25 | 700 | keep | 0 | May | 2022 | 0.00047677 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-05-25 10:46 | 2022-05-25 11:14 | 1 | 000:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN C/L NO CAUSA | C22052500034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2022-05-25 | 28 | keep | 0 | May | 2022 | 1.9071e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-25 10:52 | 2022-05-25 14:35 | 7 | 003:43 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO GUY PEGADO A PARARRAYO SE REMPLAZO PARARRAYOS SE REMPLAZO SECUNDARIA | B22052500061 | New_Event | Primary Wire Break | Include | Include | Equipment | 223 | 2022-05-25 | 1561 | keep | 0 | May | 2022 | 0.0010632 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-05-25 10:53 | 2022-05-25 12:57 | 8 | 002:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA EN PEDESTAL | R22052500021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 124 | 2022-05-25 | 992 | keep | 0 | May | 2022 | 0.00067565 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-05-25 11:04 | 2022-05-25 13:27 | 36 | 002:23 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO POR LOCKOUT. SE REPARO CAJA QUEMADA EN LA BARRA DE DISTRIBUCION QUE SUPLE AL TRANSFORMADOR DE MEDICION REMOTA | S22052500077 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-05-25 | 5148 | keep | 0 | May | 2022 | 0.0035063 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-05-25 11:04 | 2022-05-25 13:27 | 3718 | 002:23 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO POR LOCKOUT. SE REPARO CAJA QUEMADA EN LA BARRA DE DISTRIBUCION QUE SUPLE AL TRANSFORMADOR DE MEDICION REMOTA | S22052500077 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-05-25 | 531674 | keep | 0 | May | 2022 | 0.36212 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-05-25 11:04 | 2022-05-25 13:27 | 1073 | 002:23 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO POR LOCKOUT. SE REPARO CAJA QUEMADA EN LA BARRA DE DISTRIBUCION QUE SUPLE AL TRANSFORMADOR DE MEDICION REMOTA | S22052500077 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-05-25 | 153439 | keep | 0 | May | 2022 | 0.10451 | 0.00073082 | Sustained | FALSE | FALSE | Not_TMED_Event | 1073
SAN JUAN | 2022-05-25 11:04 | 2022-05-25 13:27 | 172 | 002:23 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO POR LOCKOUT. SE REPARO CAJA QUEMADA EN LA BARRA DE DISTRIBUCION QUE SUPLE AL TRANSFORMADOR DE MEDICION REMOTA | S22052500077 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-05-25 | 24596 | keep | 0 | May | 2022 | 0.016752 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-05-25 11:04 | 2022-05-25 13:27 | 1615 | 002:23 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO POR LOCKOUT. SE REPARO CAJA QUEMADA EN LA BARRA DE DISTRIBUCION QUE SUPLE AL TRANSFORMADOR DE MEDICION REMOTA | S22052500077 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-05-25 | 230945 | keep | 0 | May | 2022 | 0.1573 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
BAYAMON | 2022-05-25 11:18 | 2022-05-25 17:05 | 25 | 005:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPAZO CAJA PRIMARIA Y 1 X 50 EN C/L | B22052500064 | New_Event | Cutout Failure | Include | Include | Equipment | 347 | 2022-05-25 | 8675 | keep | 0 | May | 2022 | 0.0059085 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-25 11:19 | 2022-05-25 16:30 | 7 | 005:11 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052500091 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 311 | 2022-05-25 | 2177 | keep | 0 | May | 2022 | 0.0014827 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-05-25 11:23 | 2022-05-25 15:52 | 1 | 004:29 | P | DESGANCHE | 1 X 25 EN C/L | C22052500040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2022-05-25 | 269 | keep | 0 | May | 2022 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-25 11:34 | 2022-05-25 16:40 | 23 | 005:06 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN XMR REPARO SECUNDARIA CRUZADA | C22052500046 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 306 | 2022-05-25 | 7038 | keep | 0 | May | 2022 | 0.0047935 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2022-05-25 11:35 | 2022-05-25 14:21 | 74 | 002:46 | T | ERROR HUMANO | DISPARO REALIZANDO OPERACIONES POR V/L D2022-00319 NO SE TOMO EN CUENTA CALIBRE DEL CNDUCTOR SJ-220525-01 CARGA POR EL 1529-11 | S22052500103 | New_Event | Human Error | Include | Include | Other | 166 | 2022-05-25 | 12284 | keep | 0 | May | 2022 | 0.0083666 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2022-05-25 11:35 | 2022-05-25 14:21 | 1370 | 002:46 | T | ERROR HUMANO | DISPARO REALIZANDO OPERACIONES POR V/L D2022-00319 NO SE TOMO EN CUENTA CALIBRE DEL CNDUCTOR SJ-220525-01 LLEVA LA CARGA DEL 1521-02 | S22052500103 | New_Event | Human Error | Include | Include | Other | 166 | 2022-05-25 | 227420 | keep | 0 | May | 2022 | 0.15489 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2022-05-25 11:47 | 2022-05-25 16:49 | 122 | 005:02 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | B22052500117 | New_Event | Animals | Include | Include | Wildlife | 302 | 2022-05-25 | 36844 | keep | 0 | May | 2022 | 0.025094 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
ARECIBO | 2022-05-25 12:05 | 2022-05-25 12:15 | 5 | 000:10 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22052500121 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 10 | 2022-05-25 | 50 | keep | 0 | May | 2022 | 3.4055e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-05-25 12:07 | 2022-05-25 13:21 | 15 | 001:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE VCAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22052500044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 74 | 2022-05-25 | 1110 | keep | 0 | May | 2022 | 0.00075602 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-05-25 12:14 | 2022-05-25 14:42 | 40 | 002:28 | P | ANIMAL | 1 X 40 EN C/L Y 1 X 10 EN XMR CRUCE X AVE | C22052500057 | New_Event | Animals | Include | Include | Wildlife | 148 | 2022-05-25 | 5920 | keep | 0 | May | 2022 | 0.0040321 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-25 12:15 | 2022-05-25 15:54 | 1 | 003:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 15 EN TRANSFORMADOR POR FUERTES LLUVIAS | M22052500107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 219 | 2022-05-25 | 219 | keep | 0 | May | 2022 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-25 12:21 | 2022-05-25 12:22 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 6014-02 NO SE REPORTO CAUSA CARGA POR 6014-02 | M22052500111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 1444 | keep | 0 | May | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-05-25 12:21 | 2022-05-25 12:22 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-1 | M22052500111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 3630 | keep | 0 | May | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
HUMACAO | 2022-05-25 12:30 | 2022-05-25 13:39 | 10 | 001:09 | P | OTRAS CAUSAS | ABRIO XMR PARA REMPLAZAR PERNO Y FIJARLO | C22052500059 | New_Event | Other Causes | Include | Include | Other | 69 | 2022-05-25 | 690 | keep | 0 | May | 2022 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-25 12:39 | 2022-05-26 19:37 | 2 | 030:58 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA ROTA Y SE CERRO PUENTES RELACIONADO AL EVENTO A220525000128 | A22052600163 | New_Event | Primary Wire Break | Include | Include | Equipment | 1858 | 2022-05-25 | 3716 | keep | 0 | May | 2022 | 0.002531 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-05-25 12:39 | 2022-05-25 19:55 | 20 | 007:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA ROTA | A22052500128 | New_Event | Primary Wire Break | Include | Include | Equipment | 436 | 2022-05-25 | 8720 | keep | 0 | May | 2022 | 0.0059392 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-05-25 12:45 | 2022-05-25 14:55 | 11 | 002:10 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA CRUZADA | A22052500062 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 130 | 2022-05-25 | 1430 | keep | 0 | May | 2022 | 0.00097397 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2022-05-25 12:52 | 2022-05-25 14:50 | 3654 | 001:58 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE PATRULLO Y NO SE ENCONTRO CAUSA SE RESETEO BANDERAS Y SE PROBO SIN CARGA Y PROBO BUENO LUEGO SE CERRO CON CARGA Y QUEDO EN SERVICIO | A22052500132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2022-05-25 | 431172 | keep | 0 | May | 2022 | 0.29367 | 0.0024887 | Sustained | FALSE | FALSE | Not_TMED_Event | 3654
CAGUAS | 2022-05-25 12:55 | 2022-05-25 20:22 | 69 | 007:27 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE NO FUNDIO | C22052500062 | New_Event | Primary Wire Break | Include | Include | Equipment | 447 | 2022-05-25 | 30843 | keep | 0 | May | 2022 | 0.021007 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 1253 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 LLEVA CARGA DE 6010-02 | M22052500136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 21301 | keep | 0 | May | 2022 | 0.014508 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 1266 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 CARGA POR 6010-01 | M22052500136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 21522 | keep | 0 | May | 2022 | 0.014659 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 411 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052500136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 6987 | keep | 0 | May | 2022 | 0.0047588 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 1617 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 27489 | keep | 0 | May | 2022 | 0.018723 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 1017 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 17289 | keep | 0 | May | 2022 | 0.011775 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 828 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 14076 | keep | 0 | May | 2022 | 0.0095871 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 863 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052500139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 14671 | keep | 0 | May | 2022 | 0.0099924 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 309 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052500139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 5253 | keep | 0 | May | 2022 | 0.0035778 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 176 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052500139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 2992 | keep | 0 | May | 2022 | 0.0020378 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-05-25 12:56 | 2022-05-25 13:13 | 974 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22052500140 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-05-25 | 16558 | keep | 0 | May | 2022 | 0.011278 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
GUAYAMA | 2022-05-25 13:04 | 2022-05-25 16:22 | 60 | 003:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | P22052500050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2022-05-25 | 11880 | keep | 0 | May | 2022 | 0.0080914 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-05-25 13:05 | 2022-05-25 15:01 | 15 | 001:56 | P | SECUNDARIA/DESGANCHE | 1 X 5 EN TRANSFORMADOR SE REALIZO DESGANCHE | P22052500030 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 116 | 2022-05-25 | 1740 | keep | 0 | May | 2022 | 0.0011851 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-05-25 13:11 | 2022-05-25 13:12 | 1054 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22052500136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 1054 | keep | 0 | May | 2022 | 0.00071787 | 0.00071787 | Momentary | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2022-05-25 13:12 | 2022-05-26 15:30 | 70 | 026:18 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN CORTE DE LINEA Y 3 X 15 EN TRANSFORMADOR SE REPARO BUSHING PRIMARIO TRANSFORMADOR | A22052600163 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1578 | 2022-05-25 | 110460 | keep | 0 | May | 2022 | 0.075234 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:13 | 2022-05-25 13:51 | 200 | 000:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052400637 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 38 | 2022-05-25 | 7600 | keep | 0 | May | 2022 | 0.0051763 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-25 13:14 | 2022-05-25 13:15 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052500053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 752 | keep | 0 | May | 2022 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2022-05-25 13:15 | 2022-05-25 15:35 | 200 | 002:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | P22052500052 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2022-05-25 | 28000 | keep | 0 | May | 2022 | 0.019071 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-05-25 13:22 | 2022-05-25 13:23 | 551 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22052500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 551 | keep | 0 | May | 2022 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
MAYAGÃœEZ | 2022-05-25 13:25 | 2022-05-25 18:18 | 2 | 004:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052500142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2022-05-25 | 586 | keep | 0 | May | 2022 | 0.00039912 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-05-25 13:27 | 2022-05-25 16:40 | 30 | 003:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS | P22052500054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-05-25 | 5790 | keep | 0 | May | 2022 | 0.0039435 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-05-25 13:32 | 2022-05-25 13:33 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052500055 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 752 | keep | 0 | May | 2022 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
AGUADILLA | 2022-05-25 13:32 | 2022-05-25 16:29 | 2366 | 002:57 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR SE ABRIERON PUENTES PRIMARIOS PARA SECCIONALIZAR AVERIA DE LINEAS PRIMARIAS CRUZADAS Y DESGANCHE | M22052500147 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 177 | 2022-05-25 | 418782 | keep | 0 | May | 2022 | 0.28523 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2022-05-25 13:35 | 2022-05-25 16:14 | 4 | 002:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR POR FUERTES LLUVIAS | M22052500148 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2022-05-25 | 636 | keep | 0 | May | 2022 | 0.00043318 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-05-25 13:38 | 2022-05-25 16:15 | 151 | 002:37 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | R22052500142 | New_Event | Primary Pole Failure | Include | Include | Equipment | 157 | 2022-05-25 | 23707 | keep | 0 | May | 2022 | 0.016147 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 1253 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 LLEVA CARGA DE 6010-02 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 5012 | keep | 0 | May | 2022 | 0.0034137 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 1266 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 CARGA POR 6010-01 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 5064 | keep | 0 | May | 2022 | 0.0034491 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 411 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 1644 | keep | 0 | May | 2022 | 0.0011197 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 1617 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 6468 | keep | 0 | May | 2022 | 0.0044053 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 1017 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 4068 | keep | 0 | May | 2022 | 0.0027707 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 828 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 3312 | keep | 0 | May | 2022 | 0.0022558 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 863 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 3452 | keep | 0 | May | 2022 | 0.0023511 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 309 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 1236 | keep | 0 | May | 2022 | 0.00084183 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 176 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 704 | keep | 0 | May | 2022 | 0.00047949 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 13:55 | 974 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22052500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-05-25 | 3896 | keep | 0 | May | 2022 | 0.0026535 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:51 | 2022-05-25 19:30 | 40 | 005:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052500158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2022-05-25 | 13560 | keep | 0 | May | 2022 | 0.0092357 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-25 13:55 | 2022-05-25 18:12 | 500 | 004:17 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIERON PUENTES PRIMARIOS PARA SECCIONALIZAR AVERIA DE LINEAS PARTIDAS Y DESGANCHE. 30% EN SERVICIO | M22052500100 | New_Event | Primary Wire Break | Include | Include | Equipment | 257 | 2022-05-25 | 128500 | keep | 0 | May | 2022 | 0.087521 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2022-05-25 13:55 | 2022-05-25 18:06 | 200 | 004:11 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA SE ANADIERON PARCIALES YA QUE HAY TOTALES DEL ALIMENTADOR POR MEDIO | M22052400637 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 251 | 2022-05-25 | 50200 | keep | 0 | May | 2022 | 0.034191 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 13:55 | 2022-05-26 12:49 | 3 | 022:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA POR UNO DE 25KVA Y SE REPARARON CONEXIONES SECUNDARIAS | M22052400078 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1374 | 2022-05-25 | 4122 | keep | 0 | May | 2022 | 0.0028075 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-25 13:59 | 2022-05-25 18:05 | 4 | 004:06 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | REPARO BAJANTE SECUNDARIO NO FUNDIO | C22052500074 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 246 | 2022-05-25 | 984 | keep | 0 | May | 2022 | 0.0006702 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-05-25 14:00 | 2022-05-25 14:02 | 229 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2900 LLEVA LA CARGA DEL 9901-02 | C22052500075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 458 | keep | 0 | May | 2022 | 0.00031194 | 0.00015597 | Momentary | FALSE | FALSE | Not_TMED_Event | 229
BARRANQUITAS | 2022-05-25 14:00 | 2022-05-25 14:02 | 1246 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2900 CARGAS X 9901-01 | C22052500075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-25 | 2492 | keep | 0 | May | 2022 | 0.0016973 | 0.00084864 | Momentary | FALSE | FALSE | Not_TMED_Event | 1246
CANOVANAS | 2022-05-25 14:05 | 2022-05-25 17:25 | 148 | 003:20 | P | ANIMAL | 1 X 100 Y 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R22052500149 | New_Event | Animals | Include | Include | Wildlife | 200 | 2022-05-25 | 29600 | keep | 0 | May | 2022 | 0.02016 | 0.0001008 | Sustained | FALSE | FALSE | Not_TMED_Event | 148
BARRANQUITAS | 2022-05-25 14:09 | 2022-05-25 14:10 | 2635 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | C22052500083 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-05-25 | 2635 | keep | 0 | May | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-05-25 14:10 | 2022-05-25 16:33 | 200 | 002:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 65 EN C/L REMPLAZO PIN | C22052500103 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 143 | 2022-05-25 | 28600 | keep | 0 | May | 2022 | 0.019479 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-05-25 14:11 | 2022-05-25 15:28 | 63 | 001:17 | P | DESGANCHE | 1 X 50 EN C/L | C22052500080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-05-25 | 4851 | keep | 0 | May | 2022 | 0.003304 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
SAN JUAN | 2022-05-25 14:12 | 2022-05-25 16:30 | 1 | 002:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO BAJANTE PRIMARIO Y CAJA PRIMARIA | R22052500152 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2022-05-25 | 138 | keep | 0 | May | 2022 | 9.3991e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-05-25 14:13 | 2022-05-26 14:16 | 30 | 024:03 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B22052500089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1443 | 2022-05-25 | 43290 | keep | 0 | May | 2022 | 0.029485 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-05-25 14:18 | 2022-05-26 09:10 | 183 | 018:52 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA RAYOS EN EL AREA | C22052500088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1132 | 2022-05-25 | 207156 | keep | 0 | May | 2022 | 0.14109 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
BAYAMON | 2022-05-25 14:21 | 2022-05-25 19:19 | 274 | 004:58 | P | ERROR HUMANO | SE SECCIONALIZO TRAMO PARA LEVANTAR LINEA REEMPLAZAR MACHETES Y CERRAR PUENTE ABIERTO DEBIDO A OPERACIONES DE VL D2022-00319 SJ-220525-01 | S22052500103 | Partial_restoration | Human Error | Include | Include | Other | 298 | 2022-05-25 | 81652 | keep | 0 | May | 2022 | 0.055613 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-25 14:25 | 2022-05-25 16:12 | 65 | 001:47 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REPARO CRUCETA PARTIDA | S22052500200 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 107 | 2022-05-25 | 6955 | keep | 0 | May | 2022 | 0.004737 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-05-25 14:25 | 2022-05-25 17:16 | 53 | 002:51 | P | DESGANCHE | 1 X 80 3N C/L Y DESGANCHE | S22052500034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-05-25 | 9063 | keep | 0 | May | 2022 | 0.0061728 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
ARECIBO | 2022-05-25 14:34 | 2022-05-25 19:40 | 100 | 005:06 | P | ARBOL SOBRE LINEA | 2 X 30 Y 2 X 50 EN CORTES DE LINEAS SE RETIRO ARBOL CAIDO SOBRE LAS LINEAS | A22052500157 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 306 | 2022-05-25 | 30600 | keep | 0 | May | 2022 | 0.020842 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-05-25 14:35 | 2022-05-25 15:31 | 7 | 000:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR CONTAMINACION EN PORTAFUSIBLE | R22052500157 | New_Event | Cutout Failure | Include | Include | Equipment | 56 | 2022-05-25 | 392 | keep | 0 | May | 2022 | 0.00026699 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-05-25 14:35 | 2022-05-25 15:18 | 5 | 000:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22052500036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2022-05-25 | 215 | keep | 0 | May | 2022 | 0.00014644 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-05-25 14:38 | 2022-05-26 08:22 | 10 | 017:44 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052500158 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1064 | 2022-05-25 | 10640 | keep | 0 | May | 2022 | 0.0072469 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-05-25 14:41 | 2022-05-25 18:20 | 150 | 003:39 | P | MAL TIEMPO/RAYOS | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052500203 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 219 | 2022-05-25 | 32850 | keep | 0 | May | 2022 | 0.022374 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-25 14:53 | 2022-05-25 15:45 | 1 | 000:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO PUENTE PRIMARIO Y SE REMPLAZO CAJA | S22052500209 | New_Event | Cutout Failure | Include | Include | Equipment | 52 | 2022-05-25 | 52 | keep | 0 | May | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-25 15:03 | 2022-05-25 15:04 | 1615 | 000:01 | T | ANIMAL | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22052500000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-05-25 | 1615 | keep | 0 | May | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
HUMACAO | 2022-05-25 15:03 | 2022-05-25 17:56 | 150 | 002:53 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L Y 1 X 10 EN XMR NO CAUSA | C22052500126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2022-05-25 | 25950 | keep | 0 | May | 2022 | 0.017674 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-05-25 15:04 | 2022-05-25 17:00 | 300 | 001:56 | P | ANIMAL | 2 X 100 EN CORTE DE LINEA CRUCE POR AVE | R22052500160 | 1st_after_momentary | Animals | Include | Include | Wildlife | 116 | 2022-05-25 | 34800 | keep | 0 | May | 2022 | 0.023702 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
UTUADO | 2022-05-25 15:04 | 2022-05-25 22:14 | 10 | 007:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 50 EN CORTE DE LINEA, 2 X 15 Y 1 X 20 EN TRANSFORMADOR A CAUSA DE MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22052500169 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 430 | 2022-05-25 | 4300 | keep | 0 | May | 2022 | 0.0029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-05-25 15:05 | 2022-05-25 15:06 | 3041 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M22052500000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-25 | 3041 | keep | 0 | May | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2022-05-25 15:06 | 2022-05-25 15:07 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1206-02 | S22052500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 641 | keep | 0 | May | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-05-25 15:06 | 2022-05-25 15:07 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1206-01 | S22052500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 733 | keep | 0 | May | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
AGUADILLA | 2022-05-25 15:06 | 2022-05-25 17:00 | 25 | 001:54 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052500247 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 114 | 2022-05-25 | 2850 | keep | 0 | May | 2022 | 0.0019411 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-05-25 15:06 | 2022-05-25 15:07 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052500220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 390 | keep | 0 | May | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
ARECIBO | 2022-05-25 15:08 | 2022-05-26 20:45 | 6 | 029:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA @ 4/7 KV POR LA MISMA CAPACIDAD | A22052500172 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1777 | 2022-05-25 | 10662 | keep | 0 | May | 2022 | 0.0072618 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-25 15:10 | 2022-05-25 15:11 | 759 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22052500178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 759 | keep | 0 | May | 2022 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2022-05-25 15:10 | 2022-05-25 15:11 | 1500 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22052500179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 1500 | keep | 0 | May | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
ARECIBO | 2022-05-25 15:11 | 2022-05-25 17:35 | 60 | 002:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22052500177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-05-25 | 8640 | keep | 0 | May | 2022 | 0.0058847 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-05-25 15:11 | 2022-05-25 19:15 | 15 | 004:04 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052500180 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 244 | 2022-05-25 | 3660 | keep | 0 | May | 2022 | 0.0024928 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-25 15:14 | 2022-05-25 19:05 | 20 | 003:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR UNO DE 25KVA | M22052500227 | New_Event | Service Transformer Failure | Include | Include | Equipment | 231 | 2022-05-25 | 4620 | keep | 0 | May | 2022 | 0.0031467 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-05-25 15:19 | 2022-05-25 18:04 | 20 | 002:45 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C22052500140 | New_Event | Animals | Include | Include | Wildlife | 165 | 2022-05-25 | 3300 | keep | 0 | May | 2022 | 0.0022476 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-05-25 15:20 | 2022-05-25 22:47 | 3 | 007:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 15KVA POR UNO DE 15KVA | M22052500339 | New_Event | Service Transformer Failure | Include | Include | Equipment | 447 | 2022-05-25 | 1341 | keep | 0 | May | 2022 | 0.00091335 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-05-25 15:25 | 2022-05-25 15:26 | 1607 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A22052500000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-05-25 | 1607 | keep | 0 | May | 2022 | 0.0010945 | 0.0010945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1607
ARECIBO | 2022-05-25 15:26 | 2022-05-25 20:03 | 10 | 004:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A22052500204 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 277 | 2022-05-25 | 2770 | keep | 0 | May | 2022 | 0.0018866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-25 15:27 | 2022-05-25 17:54 | 364 | 002:27 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | S22052500227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-05-25 | 53508 | keep | 0 | May | 2022 | 0.036444 | 0.00024792 | Sustained | FALSE | FALSE | Not_TMED_Event | 364
SAN JUAN | 2022-05-25 15:32 | 2022-05-25 15:33 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1206-02 | S22052500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 641 | keep | 0 | May | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-05-25 15:32 | 2022-05-25 15:33 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1206-01 | S22052500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 733 | keep | 0 | May | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
UTUADO | 2022-05-25 15:34 | 2022-05-25 18:11 | 50 | 002:37 | P | MAL TIEMPO/RAYOS | 1 X 15 EN 4 TRANSFORMADORES DISTINTOS POR DESCARGAS ELECTRICAS | A22052500197 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 157 | 2022-05-25 | 7850 | keep | 0 | May | 2022 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-25 15:36 | 2022-05-25 15:37 | 4381 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M22052500239 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-25 | 4381 | keep | 0 | May | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
ARECIBO | 2022-05-25 15:40 | 2022-05-25 15:41 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22052500205 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 2697 | keep | 0 | May | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2022-05-25 15:45 | 2022-05-25 18:59 | 60 | 003:14 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052500209 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 194 | 2022-05-25 | 11640 | keep | 0 | May | 2022 | 0.007928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-05-25 15:49 | 2022-05-25 22:48 | 150 | 006:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22052500216 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 419 | 2022-05-25 | 62850 | keep | 0 | May | 2022 | 0.042807 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-25 15:53 | 2022-05-25 17:50 | 50 | 001:57 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052500250 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 117 | 2022-05-25 | 5850 | keep | 0 | May | 2022 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-25 15:53 | 2022-05-26 10:23 | 30 | 018:30 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052500227 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1110 | 2022-05-25 | 33300 | keep | 0 | May | 2022 | 0.02268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-25 15:54 | 2022-05-25 17:33 | 10 | 001:39 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052500252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-05-25 | 990 | keep | 0 | May | 2022 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-25 15:59 | 2022-05-26 15:16 | 30 | 023:17 | P | MAL TIEMPO/RAYOS | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052500232 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1397 | 2022-05-25 | 41910 | keep | 0 | May | 2022 | 0.028545 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-05-25 16:07 | 2022-05-25 19:40 | 75 | 003:33 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22052500240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-05-25 | 15975 | keep | 0 | May | 2022 | 0.01088 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-05-25 16:08 | 2022-05-25 18:29 | 6 | 002:21 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA | B22052400446 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 141 | 2022-05-25 | 846 | keep | 0 | May | 2022 | 0.00057621 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-25 16:08 | 2022-05-25 20:16 | 25 | 004:08 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22052500242 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 248 | 2022-05-25 | 6200 | keep | 0 | May | 2022 | 0.0042228 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-05-25 16:09 | 2022-05-25 16:14 | 2163 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18000 | P22052500094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-25 | 10815 | keep | 0 | May | 2022 | 0.007366 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
PONCE | 2022-05-25 16:09 | 2022-05-25 16:14 | 1340 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18000 | P22052500094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-25 | 6700 | keep | 0 | May | 2022 | 0.0045633 | 0.00091267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1340
PONCE | 2022-05-25 16:09 | 2022-05-25 16:14 | 2039 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18000 | P22052500094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-25 | 10195 | keep | 0 | May | 2022 | 0.0069438 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2022-05-25 16:09 | 2022-05-25 16:14 | 485 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18000 | P22052500094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-25 | 2425 | keep | 0 | May | 2022 | 0.0016517 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
PONCE | 2022-05-25 16:09 | 2022-05-25 16:14 | 732 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18000 | P22052500094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-05-25 | 3660 | keep | 0 | May | 2022 | 0.0024928 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
MAYAGÃœEZ | 2022-05-25 16:10 | 2022-05-25 16:11 | 3458 | 000:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M22052500256 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-25 | 3458 | keep | 0 | May | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2022-05-25 16:11 | 2022-05-25 17:07 | 1 | 000:56 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052500051 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 56 | 2022-05-25 | 56 | keep | 0 | May | 2022 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-25 16:12 | 2022-05-25 20:40 | 120 | 004:28 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22052500243 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 268 | 2022-05-25 | 32160 | keep | 0 | May | 2022 | 0.021904 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-05-25 16:15 | 2022-05-27 19:28 | 147 | 051:13 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZARON 2 POSTES PARTIDOS Y CERRO PUENTES | R22052500142 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 3073 | 2022-05-25 | 451731 | keep | 0 | May | 2022 | 0.30767 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-05-25 16:18 | 2022-05-25 16:30 | 11 | 000:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22052500189 | New_Event | Secondary Wire Break | Include | Include | Equipment | 12 | 2022-05-25 | 132 | keep | 0 | May | 2022 | 8.9905e-05 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-05-25 16:19 | 2022-05-25 16:20 | 2937 | 000:01 | T | DESGANCHE | RECIERRE | C22052500187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-25 | 2937 | keep | 0 | May | 2022 | 0.0020004 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
BARRANQUITAS | 2022-05-25 16:20 | 2022-05-25 20:53 | 141 | 004:33 | P | DESGANCHE | 2 X 50 EN C/L | C22052500015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 273 | 2022-05-25 | 38493 | keep | 0 | May | 2022 | 0.026217 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
AGUADILLA | 2022-05-25 16:29 | 2022-05-25 20:25 | 20 | 003:56 | P | CONDUCTOR ARRIADO O CRUZADO | SE REPARO LINEAS PRIMARIAS CRUZADAS | M22052500212 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 236 | 2022-05-25 | 4720 | keep | 0 | May | 2022 | 0.0032148 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-25 16:34 | 2022-05-25 19:50 | 27 | 003:16 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR (NO FUNDIO) | S22052500257 | New_Event | Primary Wire Break | Include | Include | Equipment | 196 | 2022-05-25 | 5292 | keep | 0 | May | 2022 | 0.0036044 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2022-05-25 16:35 | 2022-05-25 21:48 | 4 | 005:13 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S22052500242 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2022-05-25 | 1252 | keep | 0 | May | 2022 | 0.00085273 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-05-25 16:46 | 2022-05-26 18:18 | 10 | 025:32 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22052500266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1532 | 2022-05-25 | 15320 | keep | 0 | May | 2022 | 0.010434 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-05-25 16:46 | 2022-05-25 21:14 | 183 | 004:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y 2 X 65 EN C/L'S REMPLAZO CAJA QUEMADA | C22052500204 | New_Event | Cutout Failure | Include | Include | Equipment | 268 | 2022-05-25 | 49044 | keep | 0 | May | 2022 | 0.033404 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
ARECIBO | 2022-05-25 16:49 | 2022-05-26 12:07 | 7 | 019:18 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052500275 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1158 | 2022-05-25 | 8106 | keep | 0 | May | 2022 | 0.005521 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-05-25 17:03 | 2022-05-25 18:23 | 20 | 001:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22052500119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2022-05-25 | 1600 | keep | 0 | May | 2022 | 0.0010898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-05-25 17:05 | 2022-05-25 18:10 | 25 | 001:05 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22052500277 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 65 | 2022-05-25 | 1625 | keep | 0 | May | 2022 | 0.0011068 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-05-25 17:09 | 2022-05-25 17:10 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22052500218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 3744 | keep | 0 | May | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
UTUADO | 2022-05-25 17:12 | 2022-05-26 13:16 | 4 | 020:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA @ 4 KV POR UNO DE 37.5 KVA | A22052500280 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1204 | 2022-05-25 | 4816 | keep | 0 | May | 2022 | 0.0032802 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-05-25 17:14 | 2022-05-25 17:15 | 3131 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22052500224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 3131 | keep | 0 | May | 2022 | 0.0021325 | 0.0021325 | Momentary | FALSE | FALSE | Not_TMED_Event | 3131
BARRANQUITAS | 2022-05-25 17:14 | 2022-05-25 22:33 | 78 | 005:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA | C22052500221 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 319 | 2022-05-25 | 24882 | keep | 0 | May | 2022 | 0.016947 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
BAYAMON | 2022-05-25 17:15 | 2022-05-25 17:55 | 15 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN AEREO PROVISIONAL | B22052500118 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2022-05-25 | 600 | keep | 0 | May | 2022 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-25 17:31 | 2022-05-25 17:55 | 8 | 000:24 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO BAJANTE PRIMARIO DE LINEA A CAJA | R22052500164 | New_Event | Primary Wire Break | Include | Include | Equipment | 24 | 2022-05-25 | 192 | keep | 0 | May | 2022 | 0.00013077 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-05-25 17:31 | 2022-05-25 19:34 | 450 | 002:03 | P | MAL TIEMPO/RAYOS | 1 X 80 Y 1 X 200 EN CORTES DE LINEAS Y 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22052500292 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2022-05-25 | 55350 | keep | 0 | May | 2022 | 0.037699 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
CAGUAS | 2022-05-25 17:34 | 2022-05-25 19:55 | 34 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C22052500237 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2022-05-25 | 4794 | keep | 0 | May | 2022 | 0.0032652 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
PONCE | 2022-05-25 17:36 | 2022-05-25 19:50 | 2163 | 002:14 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LINEA 18000 PARA CERRAR PUENTE 38 KV | P22052500182 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2022-05-25 | 289842 | keep | 0 | May | 2022 | 0.19741 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-25 17:36 | 2022-05-25 19:50 | 1340 | 002:14 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LINEA 18000 PARA CERRAR PUENTE 38 KV | P22052500182 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2022-05-25 | 179560 | keep | 0 | May | 2022 | 0.1223 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-25 17:36 | 2022-05-25 19:50 | 2039 | 002:14 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LINEA 18000 PARA CERRAR PUENTE 38 KV | P22052500182 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2022-05-25 | 273226 | keep | 0 | May | 2022 | 0.18609 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-25 17:36 | 2022-05-25 19:50 | 485 | 002:14 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LINEA 18000 PARA CERRAR PUENTE 38 KV | P22052500182 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2022-05-25 | 64990 | keep | 0 | May | 2022 | 0.044264 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-25 17:36 | 2022-05-25 19:50 | 732 | 002:14 | S | LINEA DE TRANSMISION 38KV | SE ABRIO LINEA 18000 PARA CERRAR PUENTE 38 KV | P22052500182 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2022-05-25 | 98088 | keep | 0 | May | 2022 | 0.066807 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-25 17:43 | 2022-05-26 08:00 | 2 | 014:17 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | P22052500163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 857 | 2022-05-25 | 1714 | keep | 0 | May | 2022 | 0.0011674 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-05-25 17:49 | 2022-05-26 09:48 | 25 | 015:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22052500123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 959 | 2022-05-25 | 23975 | keep | 0 | May | 2022 | 0.016329 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-05-25 17:56 | 2022-05-26 07:50 | 100 | 013:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES QUEMADO | A22052500308 | New_Event | Cutout Failure | Include | Include | Equipment | 834 | 2022-05-25 | 83400 | keep | 0 | May | 2022 | 0.056803 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-25 18:02 | 2022-05-26 13:08 | 5 | 019:06 | P | DESGANCHE | 1 X10 EN XMR DESGANCHE | B22052500125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1146 | 2022-05-25 | 5730 | keep | 0 | May | 2022 | 0.0039027 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-25 18:12 | 2022-05-26 17:11 | 350 | 022:59 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22052600057 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1379 | 2022-05-25 | 482650 | keep | 0 | May | 2022 | 0.32873 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-25 18:15 | 2022-05-25 20:35 | 40 | 002:20 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052500306 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 140 | 2022-05-25 | 5600 | keep | 0 | May | 2022 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-25 18:23 | 2022-05-26 12:26 | 20 | 018:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22052500318 | New_Event | Cutout Failure | Include | Include | Equipment | 1083 | 2022-05-25 | 21660 | keep | 0 | May | 2022 | 0.014753 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-05-25 18:32 | 2022-05-26 12:31 | 10 | 017:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE | S22052500256 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1079 | 2022-05-25 | 10790 | keep | 0 | May | 2022 | 0.007349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-05-25 18:34 | 2022-05-26 10:15 | 8 | 015:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | P22052500205 | New_Event | Secondary Wire Break | Include | Include | Equipment | 941 | 2022-05-25 | 7528 | keep | 0 | May | 2022 | 0.0051273 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-05-25 18:45 | 2022-05-25 19:38 | 17 | 000:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | A22052500337 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2022-05-25 | 901 | keep | 0 | May | 2022 | 0.00061367 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2022-05-25 18:49 | 2022-05-26 01:44 | 100 | 006:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22052500312 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 415 | 2022-05-25 | 41500 | keep | 0 | May | 2022 | 0.028265 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-25 18:50 | 2022-05-25 18:51 | 650 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN ON SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | A22052500333 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 650 | keep | 0 | May | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
ARECIBO | 2022-05-25 18:56 | 2022-05-26 13:56 | 100 | 019:00 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052500338 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1140 | 2022-05-25 | 114000 | keep | 0 | May | 2022 | 0.077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-05-25 18:59 | 2022-05-26 11:57 | 12 | 016:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRA SECUNDARIA QUEMADA EN PEDESTAL, SECUNDARIA AVERIADA DE PEDESTAL A PEDESTAL | R22052500165 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1018 | 2022-05-25 | 12216 | keep | 0 | May | 2022 | 0.0083203 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-05-25 19:05 | 2022-05-26 10:21 | 28 | 015:16 | P | DESGANCHE | 1 X 65 EN C/L | R22052500166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 916 | 2022-05-25 | 25648 | keep | 0 | May | 2022 | 0.017469 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
MAYAGÃœEZ | 2022-05-25 19:06 | 2022-05-26 04:47 | 50 | 009:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052500317 | New_Event | Vegetation Contact | Include | Include | Vegetation | 581 | 2022-05-25 | 29050 | keep | 0 | May | 2022 | 0.019786 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-25 19:15 | 2022-05-26 10:35 | 14 | 015:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA DEL TRANSFORMADOR | A22052500344 | New_Event | Cutout Failure | Include | Include | Equipment | 920 | 2022-05-25 | 12880 | keep | 0 | May | 2022 | 0.0087725 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-05-25 19:30 | 2022-05-26 08:23 | 2 | 012:53 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052500325 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 773 | 2022-05-25 | 1546 | keep | 0 | May | 2022 | 0.001053 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-05-25 19:46 | 2022-05-25 22:15 | 135 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22052500134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-05-25 | 20115 | keep | 0 | May | 2022 | 0.0137 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
UTUADO | 2022-05-25 19:46 | 2022-05-26 11:00 | 10 | 015:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA @ 4 KV POR UNO DE 37.5 KVA @ 4 KV | A22052500315 | New_Event | Service Transformer Failure | Include | Include | Equipment | 914 | 2022-05-25 | 9140 | keep | 0 | May | 2022 | 0.0062252 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-05-25 19:48 | 2022-05-26 13:20 | 65 | 017:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA. SE REALIZO DESGANCHE MASIVO Y SE REEMPLAZO CAJA | S22052500269 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1052 | 2022-05-25 | 68380 | keep | 0 | May | 2022 | 0.046573 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-05-25 20:02 | 2022-05-26 15:02 | 19 | 019:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA | C22052500325 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1140 | 2022-05-25 | 21660 | keep | 0 | May | 2022 | 0.014753 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2022-05-25 20:03 | 2022-05-26 08:40 | 91 | 012:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22052500326 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 757 | 2022-05-25 | 68887 | keep | 0 | May | 2022 | 0.046919 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
ARECIBO | 2022-05-25 20:17 | 2022-05-25 21:26 | 18 | 001:09 | P | MAL TIEMPO/RAYOS | 1 X 15 EN DOS TRANSFORMADORES POR DESCARGAS ELECTRICAS | A22052500362 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 69 | 2022-05-25 | 1242 | keep | 0 | May | 2022 | 0.00084592 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-05-25 20:17 | 2022-05-25 20:18 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22052500138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-25 | 1834 | keep | 0 | May | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
MAYAGÃœEZ | 2022-05-25 21:05 | 2022-05-26 01:54 | 60 | 004:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052500338 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-05-25 | 17340 | keep | 0 | May | 2022 | 0.01181 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-25 21:16 | 2022-05-26 17:57 | 60 | 020:41 | P | CABLE SOTERRADO AVERIADO | SE REGO LINEA PRIMARIA AEREA PROVISIONAL 350' | M22052500340 | New_Event | UG Cable Fault | Include | Include | Equipment | 1241 | 2022-05-25 | 74460 | keep | 0 | May | 2022 | 0.050714 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-05-25 21:17 | 2022-05-26 07:42 | 232 | 010:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN SALIDA DEL CONVERTIDOR | C22052500345 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 625 | 2022-05-25 | 145000 | keep | 0 | May | 2022 | 0.098759 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
ARECIBO | 2022-05-25 21:21 | 2022-05-27 16:01 | 150 | 042:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZARON DOS TRANSFORMADORES AVERIADOS 25KVA. | A22052500377 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2560 | 2022-05-25 | 384000 | keep | 0 | May | 2022 | 0.26154 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-25 21:32 | 2022-05-26 13:46 | 60 | 016:14 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN C/L DESGANCHE Y SE RETEZO LINEAS | B22052500147 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 974 | 2022-05-25 | 58440 | keep | 0 | May | 2022 | 0.039803 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-05-25 21:42 | 2022-05-25 22:20 | 4 | 000:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 25KVA | R22052500130 | New_Event | Service Transformer Failure | Include | Include | Equipment | 38 | 2022-05-25 | 152 | keep | 0 | May | 2022 | 0.00010353 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-05-25 21:43 | 2022-05-26 11:46 | 100 | 014:03 | P | DESGANCHE | 1 X 100 EN C/L | R22052500171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 843 | 2022-05-25 | 84300 | keep | 0 | May | 2022 | 0.057416 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-05-25 22:03 | 2022-05-26 12:26 | 158 | 014:23 | P | MAL TIEMPO/RAYOS | 1 X 50, 3X 40 Y 1 X 30 EN CORTES DE LINEAS Y 1 X 15 EN BANCO DE TRANSFORMADORES DESCARGAS ELECTRICAS | C22052500351 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 863 | 2022-05-25 | 136354 | keep | 0 | May | 2022 | 0.09287 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
CAGUAS | 2022-05-25 22:11 | 2022-05-26 15:58 | 3 | 017:47 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C22052500354 | New_Event | Animals | Include | Include | Wildlife | 1067 | 2022-05-25 | 3201 | keep | 0 | May | 2022 | 0.0021802 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-05-26 02:05 | 2022-05-26 16:04 | 30 | 013:59 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO | M22052600011 | New_Event | Primary Pole Failure | Include | Include | Equipment | 839 | 2022-05-26 | 25170 | keep | 0 | May | 2022 | 0.017143 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-05-26 02:20 | 2022-05-26 05:57 | 30 | 003:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | P22052600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-05-26 | 6510 | keep | 0 | May | 2022 | 0.0044339 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-26 02:47 | 2022-05-26 11:30 | 65 | 008:43 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S22052600004 | New_Event | Primary Wire Break | Include | Include | Equipment | 523 | 2022-05-26 | 33995 | keep | 0 | May | 2022 | 0.023154 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-05-26 03:28 | 2022-05-26 05:24 | 65 | 001:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-05-26 | 7540 | keep | 0 | May | 2022 | 0.0051355 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-05-26 04:34 | 2022-05-26 09:23 | 40 | 004:49 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600006 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 289 | 2022-05-26 | 11560 | keep | 0 | May | 2022 | 0.0078735 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-26 05:45 | 2022-05-26 10:31 | 40 | 004:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22052600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2022-05-26 | 11440 | keep | 0 | May | 2022 | 0.0077917 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-26 05:56 | 2022-05-26 11:00 | 6 | 005:04 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052600011 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 304 | 2022-05-26 | 1824 | keep | 0 | May | 2022 | 0.0012423 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-05-26 06:05 | 2022-05-26 15:05 | 16 | 009:00 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22052600013 | New_Event | Animals | Include | Include | Wildlife | 540 | 2022-05-26 | 8640 | keep | 0 | May | 2022 | 0.0058847 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-05-26 06:52 | 2022-05-26 18:20 | 172 | 011:28 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA (NO FUNDIO) | B22052600005 | New_Event | Primary Wire Break | Include | Include | Equipment | 688 | 2022-05-26 | 118336 | keep | 0 | May | 2022 | 0.080598 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-05-26 07:08 | 2022-05-26 15:06 | 24 | 007:58 | P | NO SE REPORTO CAUSA | 1 X 100 C/L | S22052600017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 478 | 2022-05-26 | 11472 | keep | 0 | May | 2022 | 0.0078135 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
PONCE | 2022-05-26 07:08 | 2022-05-26 12:30 | 1 | 005:22 | P | ANIMAL | 1 X 65 EN RISER AVE | P22052600010 | New_Event | Animals | Include | Include | Wildlife | 322 | 2022-05-26 | 322 | keep | 0 | May | 2022 | 0.00021931 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-26 07:13 | 2022-05-26 13:25 | 4 | 006:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA @ 4.8KV POR LA MISMA CAPACIDAD | A22052600092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 372 | 2022-05-26 | 1488 | keep | 0 | May | 2022 | 0.0010135 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-05-26 07:15 | 2022-05-26 10:58 | 40 | 003:43 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE ABIERTO | A22052600020 | New_Event | Primary Wire Break | Include | Include | Equipment | 223 | 2022-05-26 | 8920 | keep | 0 | May | 2022 | 0.0060754 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-26 07:28 | 2022-05-26 20:23 | 65 | 012:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22052600030 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 775 | 2022-05-26 | 50375 | keep | 0 | May | 2022 | 0.03431 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2022-05-26 07:38 | 2022-05-26 11:35 | 10 | 003:57 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22082600030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2022-05-26 | 2370 | keep | 0 | May | 2022 | 0.0016142 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-26 07:47 | 2022-05-26 08:48 | 80 | 001:01 | P | MAL TIEMPO/RAYOS | 1 X 25, 1 X 30, 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052500005 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 61 | 2022-05-26 | 4880 | keep | 0 | May | 2022 | 0.0033237 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-05-26 07:54 | 2022-05-26 18:26 | 200 | 010:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22052600035 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 632 | 2022-05-26 | 126400 | keep | 0 | May | 2022 | 0.08609 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-05-26 07:56 | 2022-05-26 08:24 | 5809 | 000:28 | T | DESGANCHE | DISPARO NO SE VIO CONDICION Y SE CERRO POR SCADA | B22052600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-05-26 | 162652 | keep | 0 | May | 2022 | 0.11078 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
MAYAGÃœEZ | 2022-05-26 08:05 | 2022-05-26 11:37 | 30 | 003:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052600043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-05-26 | 6360 | keep | 0 | May | 2022 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-26 08:08 | 2022-05-26 13:41 | 35 | 005:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REPORTA DESGANCHE | S22052600028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2022-05-26 | 11655 | keep | 0 | May | 2022 | 0.0079382 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-05-26 08:12 | 2022-05-26 08:32 | 80 | 000:20 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA CERRAR PUENTE PRIMARIO | P22052600017 | New_Event | Primary Wire Break | Include | Include | Equipment | 20 | 2022-05-26 | 1600 | keep | 0 | May | 2022 | 0.0010898 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-26 08:19 | 2022-05-26 14:56 | 50 | 006:37 | P | NO SE REPORTO CAUSA | 1 X 30 Y 1 X 50 EN C/L | B22052600069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 397 | 2022-05-26 | 19850 | keep | 0 | May | 2022 | 0.01352 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-26 08:19 | 2022-05-26 13:46 | 300 | 005:27 | P | MAL TIEMPO/RAYOS | 1 X 100 Y 1 X 140 EN C/L RAYOS | B22052600216 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 327 | 2022-05-26 | 98100 | keep | 0 | May | 2022 | 0.066815 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-05-26 08:27 | 2022-05-26 08:29 | 262 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-26 | 524 | keep | 0 | May | 2022 | 0.00035689 | 0.00017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 262
SAN JUAN | 2022-05-26 08:27 | 2022-05-26 08:29 | 296 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-26 | 592 | keep | 0 | May | 2022 | 0.00040321 | 0.0002016 | Momentary | FALSE | FALSE | Not_TMED_Event | 296
SAN JUAN | 2022-05-26 08:27 | 2022-05-26 08:29 | 79 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-26 | 158 | keep | 0 | May | 2022 | 0.00010761 | 5.3807e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2022-05-26 08:27 | 2022-05-26 08:29 | 1129 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-26 | 2258 | keep | 0 | May | 2022 | 0.0015379 | 0.00076896 | Momentary | FALSE | FALSE | Not_TMED_Event | 1129
SAN JUAN | 2022-05-26 08:27 | 2022-05-26 08:29 | 1573 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-05-26 | 3146 | keep | 0 | May | 2022 | 0.0021427 | 0.0010714 | Momentary | FALSE | FALSE | Not_TMED_Event | 1573
UTUADO | 2022-05-26 08:27 | 2022-05-26 10:30 | 60 | 002:03 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052600033 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2022-05-26 | 7380 | keep | 0 | May | 2022 | 0.0050265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-05-26 08:32 | 2022-05-26 08:47 | 120 | 000:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO Y SE CERRO C/L | P22052600017 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 15 | 2022-05-26 | 1800 | keep | 0 | May | 2022 | 0.001226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-26 08:40 | 2022-05-26 09:46 | 5809 | 001:06 | T | DESGANCHE | SE RETIRO PENCA EN IRLANDA HEIGHTS Y SE CERRO POR SCADA | B22052600000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-05-26 | 383394 | keep | 0 | May | 2022 | 0.26113 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-26 08:46 | 2022-05-26 08:47 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 Y SE CERRO POR SCADA LLEVANDO 1711-05 | B22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 723 | keep | 0 | May | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-05-26 08:46 | 2022-05-26 08:47 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 Y SE CERRO POR SCADA LLEVANDO 1711-05 | B22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 1976 | keep | 0 | May | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
CANOVANAS | 2022-05-26 08:54 | 2022-05-26 11:52 | 174 | 002:58 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R22052600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-05-26 | 30972 | keep | 0 | May | 2022 | 0.021095 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
VEGA BAJA | 2022-05-26 09:15 | 2022-05-26 12:22 | 60 | 003:07 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22052600138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2022-05-26 | 11220 | keep | 0 | May | 2022 | 0.0076419 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-05-26 09:28 | 2022-05-26 15:24 | 40 | 005:56 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | C22052600063 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 356 | 2022-05-26 | 14240 | keep | 0 | May | 2022 | 0.0096988 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-26 09:46 | 2022-05-26 12:20 | 1 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | A22052600053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-05-26 | 154 | keep | 0 | May | 2022 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-05-26 09:51 | 2022-05-26 11:00 | 6 | 001:09 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | R22052600012 | New_Event | Animals | Include | Include | Wildlife | 69 | 2022-05-26 | 414 | keep | 0 | May | 2022 | 0.00028197 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-05-26 09:59 | 2022-05-26 15:32 | 2 | 005:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA | C22052600076 | New_Event | Primary Wire Break | Include | Include | Equipment | 333 | 2022-05-26 | 666 | keep | 0 | May | 2022 | 0.00045361 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-05-26 10:03 | 2022-05-26 21:40 | 50 | 011:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 5O EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22052600080 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 697 | 2022-05-26 | 34850 | keep | 0 | May | 2022 | 0.023736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-05-26 10:10 | 2022-05-26 10:11 | 2722 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22052600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 2722 | keep | 0 | May | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
BAYAMON | 2022-05-26 10:23 | 2022-05-26 17:55 | 131 | 007:32 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZARON 2 POSTES PRIMARIOS PARTIDOS. 10 CLIENTES FUERA PARA LEVANTAR SECUNDARIA | B22052600192 | New_Event | Primary Pole Failure | Include | Include | Equipment | 452 | 2022-05-26 | 59212 | keep | 0 | May | 2022 | 0.040329 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
SAN JUAN | 2022-05-26 10:30 | 2022-05-26 13:05 | 40 | 002:35 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | S22052600074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-05-26 | 6200 | keep | 0 | May | 2022 | 0.0042228 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-26 10:32 | 2022-05-26 13:54 | 40 | 003:22 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600063 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 202 | 2022-05-26 | 8080 | keep | 0 | May | 2022 | 0.0055033 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-05-26 10:43 | 2022-05-26 14:48 | 18 | 004:05 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | C22052600088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 245 | 2022-05-26 | 4410 | keep | 0 | May | 2022 | 0.0030036 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-05-26 10:51 | 2022-05-26 19:50 | 12 | 008:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22052600196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 539 | 2022-05-26 | 6468 | keep | 0 | May | 2022 | 0.0044053 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-26 10:58 | 2022-05-26 11:16 | 60 | 000:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO SE CERRO CORTE DE LINEA | A22052600020 | New_Event | Primary Wire Break | Include | Include | Equipment | 18 | 2022-05-26 | 1080 | keep | 0 | May | 2022 | 0.00073558 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-26 11:00 | 2022-05-26 11:01 | 5809 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 5809 | keep | 0 | May | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
CAGUAS | 2022-05-26 11:00 | 2022-05-26 13:30 | 15 | 002:30 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE CERRO CORTE DE LINEA | C22052600105 | New_Event | Primary Wire Break | Include | Include | Equipment | 150 | 2022-05-26 | 2250 | keep | 0 | May | 2022 | 0.0015325 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-05-26 11:01 | 2022-05-26 11:40 | 1 | 000:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | R22052600018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-05-26 | 39 | keep | 0 | May | 2022 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-26 11:08 | 2022-05-26 13:38 | 80 | 002:30 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | B22052600199 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 150 | 2022-05-26 | 12000 | keep | 0 | May | 2022 | 0.0081731 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-05-26 11:13 | 2022-05-27 15:34 | 50 | 028:21 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A22052600075 | New_Event | Primary Wire Break | Include | Include | Equipment | 1701 | 2022-05-26 | 85050 | keep | 0 | May | 2022 | 0.057927 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-05-26 11:18 | 2022-05-26 12:15 | 67 | 000:57 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L MAL TIEMPO DESCARGAS ELECTRICAS | B22052600203 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 57 | 2022-05-26 | 3819 | keep | 0 | May | 2022 | 0.0026011 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-05-26 11:21 | 2022-05-26 12:38 | 25 | 001:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22052600089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-05-26 | 1925 | keep | 0 | May | 2022 | 0.0013111 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-05-26 11:28 | 2022-05-26 15:19 | 14 | 003:51 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHAR Y REPARAR TIERRRA DEL XMR | S22052600094 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 231 | 2022-05-26 | 3234 | keep | 0 | May | 2022 | 0.0022027 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2022-05-26 11:28 | 2022-05-26 11:29 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22052600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 3114 | keep | 0 | May | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
ARECIBO | 2022-05-26 11:36 | 2022-05-26 21:10 | 30 | 009:34 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600083 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 574 | 2022-05-26 | 17220 | keep | 0 | May | 2022 | 0.011728 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-26 11:37 | 2022-05-26 13:17 | 23 | 001:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BARRA EN PEDESTAL | C22052500192 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2022-05-26 | 2300 | keep | 0 | May | 2022 | 0.0015665 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2022-05-26 11:41 | 2022-05-26 12:35 | 7 | 000:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO | C22052600046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2022-05-26 | 378 | keep | 0 | May | 2022 | 0.00025745 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-05-26 11:45 | 2022-05-26 13:10 | 10 | 001:25 | P | ANIMAL | 1 X 30 EN TRANSFORMADOR CRUCE DE FASE POR IGUANA | P22052600050 | New_Event | Animals | Include | Include | Wildlife | 85 | 2022-05-26 | 850 | keep | 0 | May | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-05-26 11:46 | 2022-05-26 11:47 | 2708 | 000:01 | T | DESGANCHE | RECIERRE | R22052600024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-26 | 2708 | keep | 0 | May | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
SAN JUAN | 2022-05-26 11:47 | 2022-05-26 11:48 | 829 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE ADEMAS LLEVA EL 60% DEL 1204-03 | S22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 829 | keep | 0 | May | 2022 | 0.00056463 | 0.00056463 | Momentary | FALSE | FALSE | Not_TMED_Event | 829
SAN JUAN | 2022-05-26 11:47 | 2022-05-26 11:48 | 1978 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE ADEMAS LLEVA EL 40% DEL 1204-04 | S22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 1978 | keep | 0 | May | 2022 | 0.0013472 | 0.0013472 | Momentary | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2022-05-26 11:47 | 2022-05-26 11:48 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04. LLEVA LA CARGAS PARCIALES DE 20% 1303-02, 40% 1204-04, 60% 1204-03. | S22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 1799 | keep | 0 | May | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-05-26 11:47 | 2022-05-26 11:48 | 487 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE ADEMAS LLEVA EL 20% DEL 1303-02 | S22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 487 | keep | 0 | May | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
CANOVANAS | 2022-05-26 11:47 | 2022-05-26 13:00 | 100 | 001:13 | P | DESGANCHE | 1 X 100 EN C/L | R22052500171 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-05-26 | 7300 | keep | 0 | May | 2022 | 0.004972 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-05-26 11:55 | 2022-05-26 15:04 | 10 | 003:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA 4/8 KV POR UNO DE 37.5 KVA | A22052600087 | New_Event | Service Transformer Failure | Include | Include | Equipment | 189 | 2022-05-26 | 1890 | keep | 0 | May | 2022 | 0.0012873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-05-26 11:57 | 2022-06-02 09:54 | 1 | 165:57 | P | PROBLEMA DEL CLIENTE | 1 X 30 EN RISER PARARRAYO AVERIADO EN SUBESTACION DEL CLIENTE | A22052600090 | New_Event | Customer-Related Interruption | Include | Include | Public | 9957 | 2022-05-26 | 9957 | keep | 0 | May | 2022 | 0.0067817 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-05-26 11:57 | 2022-05-26 13:59 | 8 | 002:02 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 37.5 KVA | C22052600107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 122 | 2022-05-26 | 976 | keep | 0 | May | 2022 | 0.00066475 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-26 12:04 | 2022-05-26 12:30 | 15 | 000:26 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2022-05-26 | 390 | keep | 0 | May | 2022 | 0.00026563 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-05-26 12:31 | 2022-05-26 12:32 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 3718 | keep | 0 | May | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BARRANQUITAS | 2022-05-26 12:31 | 2022-05-26 15:55 | 45 | 003:24 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | C22052600114 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 204 | 2022-05-26 | 9180 | keep | 0 | May | 2022 | 0.0062525 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-05-26 12:32 | 2022-05-26 21:15 | 10 | 008:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE | S22052500256 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 523 | 2022-05-26 | 5230 | keep | 0 | May | 2022 | 0.0035621 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-26 12:33 | 2022-05-27 18:30 | 1 | 029:57 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 15 X 25 KVA | M22052600132 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1797 | 2022-05-26 | 1797 | keep | 0 | May | 2022 | 0.0012239 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-26 12:34 | 2022-05-26 19:22 | 50 | 006:48 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052600135 | New_Event | Primary Wire Break | Include | Include | Equipment | 408 | 2022-05-26 | 20400 | keep | 0 | May | 2022 | 0.013894 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-26 12:37 | 2022-05-27 15:40 | 4 | 027:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA | A22052600098 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1623 | 2022-05-26 | 6492 | keep | 0 | May | 2022 | 0.0044217 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-05-26 12:38 | 2022-05-26 13:00 | 1 | 000:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO | C22052600093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 22 | 2022-05-26 | 22 | keep | 0 | May | 2022 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-26 12:49 | 2022-05-27 17:42 | 50 | 028:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22052600100 | New_Event | Primary Wire Break | Include | Include | Equipment | 1733 | 2022-05-26 | 86650 | keep | 0 | May | 2022 | 0.059017 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-05-26 12:56 | 2022-05-27 17:26 | 30 | 028:30 | P | MAL TIEMPO/RAYOS | 6 X 15 EN TRANSFORMADORES MAL TIEMPO DESCARGAS ELECTRICAS | A22052600144 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1710 | 2022-05-26 | 51300 | keep | 0 | May | 2022 | 0.03494 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-05-26 13:00 | 2022-05-26 18:22 | 4 | 005:22 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600204 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 322 | 2022-05-26 | 1288 | keep | 0 | May | 2022 | 0.00087725 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-05-26 13:13 | 2022-05-26 17:46 | 250 | 004:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C22052600127 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 273 | 2022-05-26 | 68250 | keep | 0 | May | 2022 | 0.046485 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
UTUADO | 2022-05-26 13:14 | 2022-05-26 13:15 | 650 | 000:01 | T | DESGANCHE | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A22052600104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-26 | 650 | keep | 0 | May | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-05-26 13:15 | 2022-05-26 18:15 | 10 | 005:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22052600170 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-05-26 | 3000 | keep | 0 | May | 2022 | 0.0020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-05-26 13:17 | 2022-05-26 14:00 | 18 | 000:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22052600129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2022-05-26 | 774 | keep | 0 | May | 2022 | 0.00052717 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2022-05-26 13:26 | 2022-05-26 16:16 | 90 | 002:50 | P | DESGANCHE | 2 X 100 EN CL POR DESGANCHE | P22052600054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-05-26 | 15300 | keep | 0 | May | 2022 | 0.010421 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-05-26 13:26 | 2022-05-26 13:30 | 3087 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M22052600159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-05-26 | 12348 | keep | 0 | May | 2022 | 0.0084102 | 0.0021025 | Momentary | FALSE | FALSE | Not_TMED_Event | 3087
AGUADILLA | 2022-05-26 13:29 | 2022-05-26 14:45 | 2 | 001:16 | P | ARBOL SOBRE LINEA | 2 X 100 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | M22052600160 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 76 | 2022-05-26 | 152 | keep | 0 | May | 2022 | 0.00010353 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-05-26 13:30 | 2022-05-26 15:21 | 70 | 001:51 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTES DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052600023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-05-26 | 7770 | keep | 0 | May | 2022 | 0.0052921 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-05-26 13:36 | 2022-05-26 19:00 | 250 | 005:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22052600163 | New_Event | Primary Wire Break | Include | Include | Equipment | 324 | 2022-05-26 | 81000 | keep | 0 | May | 2022 | 0.055169 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2022-05-26 13:37 | 2022-05-26 14:53 | 1337 | 001:16 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE OPERO MANUALMENTE | M22052600176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2022-05-26 | 101612 | keep | 0 | May | 2022 | 0.069207 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2022-05-26 13:39 | 2022-05-26 15:35 | 150 | 001:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22052600165 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2022-05-26 | 17400 | keep | 0 | May | 2022 | 0.011851 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-26 13:40 | 2022-05-26 13:41 | 810 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 810 | keep | 0 | May | 2022 | 0.00055169 | 0.00055169 | Momentary | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2022-05-26 13:40 | 2022-05-26 13:41 | 1235 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 1235 | keep | 0 | May | 2022 | 0.00084115 | 0.00084115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2022-05-26 13:40 | 2022-05-26 13:41 | 93 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 93 | keep | 0 | May | 2022 | 6.3342e-05 | 6.3342e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2022-05-26 13:40 | 2022-05-26 13:41 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 1825 | keep | 0 | May | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2022-05-26 13:40 | 2022-05-26 13:41 | 3230 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 5600 | M22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 3230 | keep | 0 | May | 2022 | 0.0021999 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
PONCE | 2022-05-26 13:43 | 2022-05-26 15:54 | 179 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 1 X 65 EN CL | P22052600058 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2022-05-26 | 23449 | keep | 0 | May | 2022 | 0.015971 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
BAYAMON | 2022-05-26 13:46 | 2022-05-26 13:47 | 1715 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 1715 | keep | 0 | May | 2022 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2022-05-26 13:46 | 2022-05-26 13:47 | 1498 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 1498 | keep | 0 | May | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2022-05-26 13:46 | 2022-05-26 13:47 | 1221 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 1221 | keep | 0 | May | 2022 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2022-05-26 13:46 | 2022-05-26 13:47 | 1100 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 1100 | keep | 0 | May | 2022 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2022-05-26 13:46 | 2022-05-26 13:47 | 1514 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 1514 | keep | 0 | May | 2022 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-05-26 13:46 | 2022-05-26 13:47 | 1105 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B22052600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-26 | 1105 | keep | 0 | May | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2022-05-26 13:46 | 2022-05-26 13:50 | 4176 | 000:04 | T | MAL TIEMPO/RAYOS | DISPARO SE VERIFICO PERSONAL EN SUB. Y SE CERRO POR SCADA | B22052600000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 4 | 2022-05-26 | 16704 | keep | 0 | May | 2022 | 0.011377 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-05-26 13:47 | 2022-05-26 22:22 | 60 | 008:35 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN C/L DESGANCHE Y SE RETEZO LINEAS | B22052500147 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 515 | 2022-05-26 | 30900 | keep | 0 | May | 2022 | 0.021046 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-05-26 13:47 | 2022-05-27 09:40 | 1 | 019:53 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052600172 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1193 | 2022-05-26 | 1193 | keep | 0 | May | 2022 | 0.00081255 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-26 13:50 | 2022-05-26 16:43 | 300 | 002:53 | P | MAL TIEMPO/RAYOS | 1 X 100 Y 1 X 140 EN C/L RAYOS | B22052600216 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 173 | 2022-05-26 | 51900 | keep | 0 | May | 2022 | 0.035349 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
UTUADO | 2022-05-26 13:54 | 2022-05-26 16:50 | 3 | 002:56 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600115 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 176 | 2022-05-26 | 528 | keep | 0 | May | 2022 | 0.00035962 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-05-26 13:55 | 2022-05-26 20:40 | 60 | 006:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22052600180 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 405 | 2022-05-26 | 24300 | keep | 0 | May | 2022 | 0.016551 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-05-26 13:59 | 2022-05-26 14:05 | 229 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 9901-02 SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | C22052600159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-05-26 | 1374 | keep | 0 | May | 2022 | 0.00093583 | 0.00015597 | Sustained | FALSE | FALSE | Not_TMED_Event | 229
BARRANQUITAS | 2022-05-26 13:59 | 2022-05-26 14:05 | 1246 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 9901-01 SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | C22052600159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-05-26 | 7476 | keep | 0 | May | 2022 | 0.0050919 | 0.00084864 | Sustained | FALSE | FALSE | Not_TMED_Event | 1246
AGUADILLA | 2022-05-26 14:01 | 2022-05-26 17:26 | 30 | 003:25 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA CAMION IMPACTO POSTE Y CRUZO LINEAS | M22052600189 | New_Event | Damage From Public | Include | Include | Public | 205 | 2022-05-26 | 6150 | keep | 0 | May | 2022 | 0.0041887 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-05-26 14:05 | 2022-05-26 14:42 | 10 | 000:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | R22052600038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2022-05-26 | 370 | keep | 0 | May | 2022 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-05-26 14:05 | 2022-05-26 16:15 | 8 | 002:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 37.5 KVA | C22052600107 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 130 | 2022-05-26 | 1040 | keep | 0 | May | 2022 | 0.00070834 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-26 14:09 | 2022-05-26 14:30 | 5 | 000:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO TOMAS SECUNDARIAS EN PEDESTAL | B22052600091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2022-05-26 | 105 | keep | 0 | May | 2022 | 7.1515e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-05-26 14:12 | 2022-05-26 15:50 | 113 | 001:38 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO CORTE DE LINEA PARA ELIMINAR CONDUCTOR PRIMARIO VACANTE CRUZADO ENTRE LAS FASES | C22052600152 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 98 | 2022-05-26 | 11074 | keep | 0 | May | 2022 | 0.0075425 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
AGUADILLA | 2022-05-26 14:16 | 2022-05-26 18:43 | 200 | 004:27 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052600202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 267 | 2022-05-26 | 53400 | keep | 0 | May | 2022 | 0.03637 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-26 14:19 | 2022-05-26 19:24 | 45 | 005:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L Y SE REEMPLAZO PORTA FUSIBLE | S22052600117 | New_Event | Cutout Failure | Include | Include | Equipment | 305 | 2022-05-26 | 13725 | keep | 0 | May | 2022 | 0.009348 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-05-26 14:21 | 2022-05-26 14:48 | 8 | 000:27 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR REMPLAZO XMR AVERIADO DE 25 KVA X 37.5 KVA | C22052600158 | New_Event | Service Transformer Failure | Include | Include | Equipment | 27 | 2022-05-26 | 216 | keep | 0 | May | 2022 | 0.00014712 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-05-26 14:22 | 2022-05-27 15:28 | 10 | 025:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA | A22052600122 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1506 | 2022-05-26 | 15060 | keep | 0 | May | 2022 | 0.010257 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-05-26 14:26 | 2022-05-26 20:50 | 100 | 006:24 | P | ARBOL SOBRE LINEA | 3 X 200 EN CORTE DE LINEA SE REMPLAZO CRUCETAS, AISLADORES, Y LINEAS, AVERIA CAUSADA POR ARBOL SOBRE LINEAS EL CUAL SE RETIRO | A22052600123 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 384 | 2022-05-26 | 38400 | keep | 0 | May | 2022 | 0.026154 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-26 14:34 | 2022-05-26 16:24 | 8 | 001:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO TOMA TRASPATIO | B22052400268 | New_Event | Secondary Wire Break | Include | Include | Equipment | 110 | 2022-05-26 | 880 | keep | 0 | May | 2022 | 0.00059936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-26 14:37 | 2022-05-27 09:56 | 200 | 019:19 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052600588 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1159 | 2022-05-26 | 231800 | keep | 0 | May | 2022 | 0.15788 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-05-26 14:40 | 2022-05-26 19:25 | 40 | 004:45 | P | DESGANCHE | 1 X 50 C/L Y 2 X 25 Y DESGANCHE | S22052600123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-05-26 | 11400 | keep | 0 | May | 2022 | 0.0077645 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-05-26 14:42 | 2022-05-26 18:01 | 74 | 003:19 | P | DESGANCHE | DESGANCHE 2 X 50 EN C/L | B22052600255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-05-26 | 14726 | keep | 0 | May | 2022 | 0.01003 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
CAGUAS | 2022-05-26 14:44 | 2022-05-26 16:32 | 155 | 001:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO MUCHA LLUVIA | C22052600167 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 108 | 2022-05-26 | 16740 | keep | 0 | May | 2022 | 0.011402 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
MAYAGÃœEZ | 2022-05-26 14:44 | 2022-05-26 17:49 | 20 | 003:05 | P | ARBOL SOBRE LINEA | 1 X 30 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | M22052600230 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 185 | 2022-05-26 | 3700 | keep | 0 | May | 2022 | 0.0025201 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-26 14:46 | 2022-05-27 05:28 | 200 | 014:42 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052600235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 882 | 2022-05-26 | 176400 | keep | 0 | May | 2022 | 0.12015 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-05-26 14:47 | 2022-05-26 14:48 | 1597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 1597 | keep | 0 | May | 2022 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
ARECIBO | 2022-05-26 14:48 | 2022-05-26 18:43 | 40 | 003:55 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052600135 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 235 | 2022-05-26 | 9400 | keep | 0 | May | 2022 | 0.0064023 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-05-26 14:48 | 2022-05-26 14:49 | 2635 | 000:01 | T | MAL TIEMPO/RAYOS | RECERRO INTERRUPTOR MAL TIEMPO CON DESCARGAS ELECTRICAS EN EL AREA | C22052600173 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-05-26 | 2635 | keep | 0 | May | 2022 | 0.0017947 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-26 14:49 | 2022-05-26 18:30 | 18 | 003:41 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | C22052600088 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 221 | 2022-05-26 | 3978 | keep | 0 | May | 2022 | 0.0027094 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2022-05-26 14:49 | 2022-05-27 18:47 | 8 | 027:58 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR REMPLAZO XMR AVERIADO DE 25 KVA X 37.5 KVA | C22052600158 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1678 | 2022-05-26 | 13424 | keep | 0 | May | 2022 | 0.009143 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-05-26 14:50 | 2022-05-26 14:51 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 2999 | keep | 0 | May | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2022-05-26 14:50 | 2022-05-26 16:40 | 80 | 001:50 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052600243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-05-26 | 8800 | keep | 0 | May | 2022 | 0.0059936 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-05-26 14:52 | 2022-05-26 14:53 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052600072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 4035 | keep | 0 | May | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
ARECIBO | 2022-05-26 14:55 | 2022-05-26 21:42 | 15 | 006:47 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600140 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 407 | 2022-05-26 | 6105 | keep | 0 | May | 2022 | 0.0041581 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-26 14:56 | 2022-05-26 21:35 | 200 | 006:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052600259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 399 | 2022-05-26 | 79800 | keep | 0 | May | 2022 | 0.054351 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-05-26 14:58 | 2022-05-26 23:20 | 250 | 008:22 | P | ARBOL SOBRE LINEA | 3 X 80 CORTE DE LINEA REMPLAZO DE POSTE PRIMARIO PARTIDO POR ARBOL | P22052600073 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 502 | 2022-05-26 | 125500 | keep | 0 | May | 2022 | 0.085477 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-05-26 14:58 | 2022-05-26 15:01 | 2858 | 000:03 | T | OTRAS CAUSAS | ABRIR BKR A PETICION CCE PARA ABRIR # 1 SUBESTACION SIN CARGA. REFERENTE A V/L D2022-00745. SE ABRIO EN SUBESTACION POR RTU DOWN | B22052600000 | New_Event | Other Causes | Include | Include | Other | 3 | 2022-05-26 | 8574 | keep | 0 | May | 2022 | 0.0058397 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
PONCE | 2022-05-26 15:00 | 2022-05-26 18:35 | 40 | 003:35 | P | CONDUCTOR ROTO O ABIERTO | SE LLEVO BAJANTE PRIMARIO A CAJA DE CORTE DE LINEA Y SE CERRO CL | P22052600076 | New_Event | Primary Wire Break | Include | Include | Equipment | 215 | 2022-05-26 | 8600 | keep | 0 | May | 2022 | 0.0058574 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-05-26 15:01 | 2022-05-26 15:02 | 234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052600079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 234 | keep | 0 | May | 2022 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2022-05-26 15:01 | 2022-05-26 15:02 | 2468 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052600079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 2468 | keep | 0 | May | 2022 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
CAGUAS | 2022-05-26 15:02 | 2022-05-26 15:03 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22052600179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 1879 | keep | 0 | May | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
PONCE | 2022-05-26 15:02 | 2022-05-27 07:50 | 30 | 016:48 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN C/L CONDUCTOR PRIMARIO CRUZADO | P22052600078 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1008 | 2022-05-26 | 30240 | keep | 0 | May | 2022 | 0.020596 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-05-26 15:02 | 2022-05-26 16:00 | 80 | 000:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600145 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 58 | 2022-05-26 | 4640 | keep | 0 | May | 2022 | 0.0031603 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-05-26 15:10 | 2022-05-26 16:52 | 30 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22052600184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2022-05-26 | 3060 | keep | 0 | May | 2022 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-26 15:11 | 2022-05-27 11:30 | 150 | 020:19 | P | MAL TIEMPO/RAYOS | 1 X 50 Y 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052600277 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1219 | 2022-05-26 | 182850 | keep | 0 | May | 2022 | 0.12454 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-05-26 15:12 | 2022-05-26 15:13 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22052600085 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 4035 | keep | 0 | May | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
CANOVANAS | 2022-05-26 15:13 | 2022-05-26 21:11 | 10 | 005:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | R22052600041 | New_Event | Cutout Failure | Include | Include | Equipment | 358 | 2022-05-26 | 3580 | keep | 0 | May | 2022 | 0.0024383 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-26 15:16 | 2022-05-27 04:28 | 25 | 013:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 Y 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22052600285 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 792 | 2022-05-26 | 19800 | keep | 0 | May | 2022 | 0.013486 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-26 15:19 | 2022-05-26 20:27 | 70 | 005:08 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052600291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2022-05-26 | 21560 | keep | 0 | May | 2022 | 0.014684 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-05-26 15:23 | 2022-05-26 17:58 | 320 | 002:35 | T | DESGANCHE | SE RETIRO RAMA CON VARETA ENCIMA DE LINEAS Y SE CERRO POR SCADA | B22052600266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-05-26 | 49600 | keep | 0 | May | 2022 | 0.033782 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
MAYAGÃœEZ | 2022-05-26 15:29 | 2022-05-26 15:30 | 1818 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 1818 | keep | 0 | May | 2022 | 0.0012382 | 0.0012382 | Momentary | FALSE | FALSE | Not_TMED_Event | 1818
MAYAGÃœEZ | 2022-05-26 15:29 | 2022-05-26 15:35 | 4381 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-05-26 | 26286 | keep | 0 | May | 2022 | 0.017903 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
BAYAMON | 2022-05-26 15:30 | 2022-05-26 15:38 | 1 | 000:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE RETIRO SECUNDARIA VACANTE ENCIMA DE BAJANTE CAJA A LINEA EN XMR | B22052600269 | New_Event | Secondary Wire Break | Include | Include | Equipment | 8 | 2022-05-26 | 8 | keep | 0 | May | 2022 | 5.4488e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-05-26 15:35 | 2022-05-26 22:26 | 50 | 006:51 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE DEJO 2 CLIENTES FUERA MANANA SE REMPLAZARA POSTE SECUNDARIO SE RETIRO PELIGRO | C22052600198 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 411 | 2022-05-26 | 20550 | keep | 0 | May | 2022 | 0.013997 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-05-26 15:35 | 2022-05-26 18:31 | 100 | 002:56 | P | DESGANCHE | 1 X 50 Y 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22052600154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-05-26 | 17600 | keep | 0 | May | 2022 | 0.011987 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-05-26 15:44 | 2022-05-26 16:34 | 10 | 000:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE SUBIO SECUNDARIA PARTIDA | B22052600085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-05-26 | 500 | keep | 0 | May | 2022 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-26 15:49 | 2022-05-26 16:57 | 40 | 001:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052600346 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-05-26 | 2720 | keep | 0 | May | 2022 | 0.0018526 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-05-26 15:50 | 2022-05-27 09:05 | 40 | 017:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C22052600204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1035 | 2022-05-26 | 41400 | keep | 0 | May | 2022 | 0.028197 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-05-26 15:51 | 2022-05-26 22:09 | 90 | 006:18 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22052600348 | New_Event | Primary Wire Break | Include | Include | Equipment | 378 | 2022-05-26 | 34020 | keep | 0 | May | 2022 | 0.023171 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-05-26 15:57 | 2022-05-26 15:58 | 1590 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052600211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 1590 | keep | 0 | May | 2022 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
ARECIBO | 2022-05-26 15:59 | 2022-05-27 17:30 | 20 | 025:31 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052600165 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1531 | 2022-05-26 | 30620 | keep | 0 | May | 2022 | 0.020855 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-26 16:00 | 2022-05-27 00:50 | 15 | 008:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22052600361 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 530 | 2022-05-26 | 7950 | keep | 0 | May | 2022 | 0.0054147 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-05-26 16:00 | 2022-05-26 18:38 | 3 | 002:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA ROTA | M22052600359 | New_Event | Secondary Wire Break | Include | Include | Equipment | 158 | 2022-05-26 | 474 | keep | 0 | May | 2022 | 0.00032284 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-05-26 16:04 | 2022-05-26 21:22 | 38 | 005:18 | P | DESGANCHE | DESGANCHE 1 X 30 Y 1 X 65 EN C/L | B22052600135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2022-05-26 | 12084 | keep | 0 | May | 2022 | 0.0082304 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BARRANQUITAS | 2022-05-26 16:12 | 2022-05-26 20:39 | 50 | 004:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22052600222 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 267 | 2022-05-26 | 13350 | keep | 0 | May | 2022 | 0.0090926 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-05-26 16:13 | 2022-05-26 18:18 | 2 | 002:05 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR Y SE RELOCALIZO SECUNDARIA PARA LUEGO REEMPLAZAR POSTE SECUNDARIO EN MAL ESTADO. | C22052600224 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 125 | 2022-05-26 | 250 | keep | 0 | May | 2022 | 0.00017027 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-05-26 16:14 | 2022-05-26 21:21 | 35 | 005:07 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052600348 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2022-05-26 | 10745 | keep | 0 | May | 2022 | 0.0073184 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-05-26 16:15 | 2022-05-26 16:16 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 1606 | keep | 0 | May | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
ARECIBO | 2022-05-26 16:17 | 2022-05-26 19:40 | 60 | 003:23 | P | MAL TIEMPO/RAYOS | 3 X 65 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052600173 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 203 | 2022-05-26 | 12180 | keep | 0 | May | 2022 | 0.0082957 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-05-26 16:21 | 2022-05-26 17:16 | 12 | 000:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZARON BARRAS SECUNDARIAS EN PEDESTAL | B22052600138 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-05-26 | 660 | keep | 0 | May | 2022 | 0.00044952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-05-26 16:25 | 2022-05-27 16:24 | 10 | 023:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25KVA | A22052600175 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1439 | 2022-05-26 | 14390 | keep | 0 | May | 2022 | 0.009801 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-05-26 16:26 | 2022-05-26 16:27 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052600228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 181 | keep | 0 | May | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
MAYAGÃœEZ | 2022-05-26 16:27 | 2022-05-27 12:20 | 35 | 019:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052600392 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1193 | 2022-05-26 | 41755 | keep | 0 | May | 2022 | 0.028439 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-05-26 16:28 | 2022-05-26 16:45 | 40 | 000:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22052600303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2022-05-26 | 680 | keep | 0 | May | 2022 | 0.00046314 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-26 16:30 | 2022-05-26 16:32 | 737 | 000:02 | P | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 60% DE SU CARGA POR EL 1529-15 LLEVA 5% DEL 1346-03 | S22052600000 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 2 | 2022-05-26 | 1474 | keep | 0 | May | 2022 | 0.0010039 | 0.00050197 | Momentary | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2022-05-26 16:30 | 2022-05-26 16:32 | 121 | 000:02 | P | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 5% POR EL 1346-02 | S22052600000 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 2 | 2022-05-26 | 242 | keep | 0 | May | 2022 | 0.00016483 | 8.2413e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 121
MAYAGÃœEZ | 2022-05-26 16:32 | 2022-05-27 16:30 | 20 | 023:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | M22052300399 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1438 | 2022-05-26 | 28760 | keep | 0 | May | 2022 | 0.019588 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-05-26 16:33 | 2022-05-26 21:56 | 80 | 005:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052600400 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2022-05-26 | 25840 | keep | 0 | May | 2022 | 0.0176 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-05-26 16:39 | 2022-05-26 19:55 | 14 | 003:16 | P | ANIMAL | 1 25 EN CORTE DE LINEA AVE CRUZO FASE | C22052600233 | New_Event | Animals | Include | Include | Wildlife | 196 | 2022-05-26 | 2744 | keep | 0 | May | 2022 | 0.0018689 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-05-26 16:47 | 2022-05-27 08:19 | 1 | 015:32 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052600181 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 932 | 2022-05-26 | 932 | keep | 0 | May | 2022 | 0.00063478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-26 16:50 | 2022-05-26 16:52 | 737 | 000:02 | P | TERMINACION SOTERRADA AVERIADA | SE DISPARO ALIMENTADOR A PETICION DE EDWARD BEAN POR SITUACION DE EMERGENCIA BALT-T EN SUELO ENERGIZADO | S22052600000 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 2 | 2022-05-26 | 1474 | keep | 0 | May | 2022 | 0.0010039 | 0.00050197 | Momentary | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2022-05-26 16:50 | 2022-05-26 16:52 | 121 | 000:02 | P | TERMINACION SOTERRADA AVERIADA | SE DISPARO ALIMENTADOR A PETICION DE EDWARD BEAN POR SITUACION DE EMERGIA BALL,T EN SUELO ENERGIZADO SU CARGA POR 1346-02 | S22052600000 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 2 | 2022-05-26 | 242 | keep | 0 | May | 2022 | 0.00016483 | 8.2413e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 121
SAN JUAN | 2022-05-26 17:05 | 2022-05-27 13:01 | 1 | 019:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S22052600149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1196 | 2022-05-26 | 1196 | keep | 0 | May | 2022 | 0.00081459 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-26 17:11 | 2022-05-26 18:41 | 1617 | 001:30 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA PODER CERRAR PUENTES PRIMARIOS ABIERTOS EN TRONCAL DEL INTERRUPTOR | M22052600428 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 90 | 2022-05-26 | 145530 | keep | 0 | May | 2022 | 0.09912 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-05-26 17:16 | 2022-05-27 08:57 | 2 | 015:41 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | R22052600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 941 | 2022-05-26 | 1882 | keep | 0 | May | 2022 | 0.0012818 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-05-26 17:16 | 2022-05-27 08:37 | 6 | 015:21 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADORES MAL TIEMPO DESCARGAS ELECTRICAS | A22052600187 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 921 | 2022-05-26 | 5526 | keep | 0 | May | 2022 | 0.0037637 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-05-26 17:18 | 2022-05-26 20:36 | 19 | 003:18 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B22052600293 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2022-05-26 | 3762 | keep | 0 | May | 2022 | 0.0025623 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
UTUADO | 2022-05-26 17:21 | 2022-05-27 16:12 | 25 | 022:51 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600190 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1371 | 2022-05-26 | 34275 | keep | 0 | May | 2022 | 0.023345 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-26 17:25 | 2022-05-26 19:31 | 80 | 002:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22052600439 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 126 | 2022-05-26 | 10080 | keep | 0 | May | 2022 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-05-26 17:29 | 2022-05-26 22:48 | 45 | 005:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA EN EL AREA | C22052600245 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 319 | 2022-05-26 | 14355 | keep | 0 | May | 2022 | 0.0097771 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2022-05-26 17:29 | 2022-05-26 22:15 | 60 | 004:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22052600196 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 286 | 2022-05-26 | 17160 | keep | 0 | May | 2022 | 0.011688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-05-26 17:49 | 2022-05-27 04:57 | 1 | 011:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C22052600250 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 668 | 2022-05-26 | 668 | keep | 0 | May | 2022 | 0.00045497 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-26 17:50 | 2022-05-26 20:12 | 10 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | M22052600093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-05-26 | 1420 | keep | 0 | May | 2022 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-26 17:55 | 2022-05-26 21:26 | 10 | 003:31 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REPARO Y SE LEVANTO SECUNDARIA QUE SE ENCONTRABA EN POSTES PRIMARIOS REMPLAZADOS | B22052600192 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 211 | 2022-05-26 | 2110 | keep | 0 | May | 2022 | 0.0014371 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-05-26 17:58 | 2022-05-26 20:39 | 8 | 002:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TANSFORMADOR QUEMADO DE 15 KVA X 37.5 KVA | C22052600253 | New_Event | Service Transformer Failure | Include | Include | Equipment | 161 | 2022-05-26 | 1288 | keep | 0 | May | 2022 | 0.00087725 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-05-26 18:03 | 2022-05-27 09:34 | 30 | 015:31 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052600474 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 931 | 2022-05-26 | 27930 | keep | 0 | May | 2022 | 0.019023 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-05-26 18:09 | 2022-05-26 19:24 | 300 | 001:15 | P | ANIMAL | 1 X 65 1 X 50 Y 1 X 40 EN CORTES DE LINEA CRUCE POR AVE | R22052600056 | New_Event | Animals | Include | Include | Wildlife | 75 | 2022-05-26 | 22500 | keep | 0 | May | 2022 | 0.015325 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
YAUCO | 2022-05-26 18:13 | 2022-05-27 10:13 | 1 | 016:00 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR RAYOS | P22052600135 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 960 | 2022-05-26 | 960 | keep | 0 | May | 2022 | 0.00065385 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-26 18:35 | 2022-05-27 00:35 | 50 | 006:00 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA A CAUSA DE DESGANCHE SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052600498 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2022-05-26 | 18000 | keep | 0 | May | 2022 | 0.01226 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-05-26 18:48 | 2022-05-27 08:19 | 2 | 013:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22052600128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 811 | 2022-05-26 | 1622 | keep | 0 | May | 2022 | 0.0011047 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-05-26 18:51 | 2022-05-26 22:08 | 25 | 003:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22052600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-05-26 | 4925 | keep | 0 | May | 2022 | 0.0033544 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-05-26 18:51 | 2022-05-26 19:55 | 10 | 001:04 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | A22052600213 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 64 | 2022-05-26 | 640 | keep | 0 | May | 2022 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-05-26 18:53 | 2022-05-26 19:48 | 5 | 000:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRA SECUNDARIA EN PEDESTAL | B22052600061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-05-26 | 275 | keep | 0 | May | 2022 | 0.0001873 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-05-26 19:02 | 2022-05-26 22:38 | 60 | 003:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22052600509 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 216 | 2022-05-26 | 12960 | keep | 0 | May | 2022 | 0.008827 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-05-26 19:11 | 2022-05-26 22:16 | 50 | 003:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22052600513 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 185 | 2022-05-26 | 9250 | keep | 0 | May | 2022 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-05-26 19:21 | 2022-05-27 17:59 | 6 | 022:38 | P | SECUNDARIA/DESGANCHE | SE RETIRO ENREDADERA EN XMR Y 1 X 15 EN XMR | B22052600302 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1358 | 2022-05-26 | 8148 | keep | 0 | May | 2022 | 0.0055496 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-05-26 19:21 | 2022-05-27 11:24 | 30 | 016:03 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22052600068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 963 | 2022-05-26 | 28890 | keep | 0 | May | 2022 | 0.019677 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-05-26 19:41 | 2022-05-26 21:42 | 100 | 002:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S22052600163 | New_Event | Primary Wire Break | Include | Include | Equipment | 121 | 2022-05-26 | 12100 | keep | 0 | May | 2022 | 0.0082413 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-05-26 19:41 | 2022-05-27 00:43 | 100 | 005:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO ZAFADO | M22052600535 | New_Event | Primary Wire Break | Include | Include | Equipment | 302 | 2022-05-26 | 30200 | keep | 0 | May | 2022 | 0.020569 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-05-26 19:43 | 2022-05-26 20:25 | 3 | 000:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA @ 4/7 KV POR UNO DE 37.5 KVA @ 4/7 KV | A22052600223 | New_Event | Service Transformer Failure | Include | Include | Equipment | 42 | 2022-05-26 | 126 | keep | 0 | May | 2022 | 8.5818e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-05-26 19:47 | 2022-05-26 19:57 | 20 | 000:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22052600274 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-05-26 | 200 | keep | 0 | May | 2022 | 0.00013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-05-26 19:50 | 2022-05-27 12:44 | 1 | 016:54 | P | DESGANCHE | 1 X 30 EN C/L | C22052600273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1014 | 2022-05-26 | 1014 | keep | 0 | May | 2022 | 0.00069063 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-05-26 19:53 | 2022-05-27 11:18 | 7 | 015:25 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO 3 JUEGOS DE DISCO, 2 AISLADORE Y PIN POLE TOP, 1 PARARRAYO, SE REPARO BAJANTE PRIMARIO Y RETIRO ENREDADERA | R22052600065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 925 | 2022-05-26 | 6475 | keep | 0 | May | 2022 | 0.0044101 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-05-26 19:57 | 2022-05-26 19:58 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052600276 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 5630 | keep | 0 | May | 2022 | 0.0038346 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-05-26 20:02 | 2022-05-27 05:59 | 31 | 009:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | P22052600149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 597 | 2022-05-26 | 18507 | keep | 0 | May | 2022 | 0.012605 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
HUMACAO | 2022-05-26 20:23 | 2022-05-26 20:24 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22052600279 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 5630 | keep | 0 | May | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-05-26 20:24 | 2022-05-27 10:18 | 20 | 013:54 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22052600274 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 834 | 2022-05-26 | 16680 | keep | 0 | May | 2022 | 0.011361 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-05-26 20:26 | 2022-05-27 11:15 | 200 | 014:49 | P | DESGANCHE | 1 X 80 EN C/L SE RETIRO RAMA | P22052600154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 889 | 2022-05-26 | 177800 | keep | 0 | May | 2022 | 0.1211 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-05-26 20:28 | 2022-05-27 01:23 | 30 | 004:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | M22052600562 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 295 | 2022-05-26 | 8850 | keep | 0 | May | 2022 | 0.0060277 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-05-26 20:42 | 2022-05-26 20:43 | 817 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22052600285 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-26 | 817 | keep | 0 | May | 2022 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
ARECIBO | 2022-05-26 20:54 | 2022-05-27 09:45 | 30 | 012:51 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600230 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 771 | 2022-05-26 | 23130 | keep | 0 | May | 2022 | 0.015754 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-05-26 21:18 | 2022-05-27 10:32 | 10 | 013:14 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052600583 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 794 | 2022-05-26 | 7940 | keep | 0 | May | 2022 | 0.0054079 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-05-26 21:26 | 2022-05-27 10:48 | 15 | 013:22 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600234 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 802 | 2022-05-26 | 12030 | keep | 0 | May | 2022 | 0.0081936 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-05-26 21:27 | 2022-05-26 23:18 | 86 | 001:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22052600307 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-05-26 | 9546 | keep | 0 | May | 2022 | 0.0065017 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
AGUADILLA | 2022-05-26 21:28 | 2022-05-27 11:05 | 4 | 013:37 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS CRUZADAS | M22052600588 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 817 | 2022-05-26 | 3268 | keep | 0 | May | 2022 | 0.0022258 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-26 21:31 | 2022-05-27 11:00 | 65 | 013:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22052600308 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 809 | 2022-05-26 | 52585 | keep | 0 | May | 2022 | 0.035815 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-05-26 21:56 | 2022-05-27 09:48 | 50 | 011:52 | P | DESGANCHE | 1 X 80 EN C/L SE RETIRO RAMA | P22052600164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 712 | 2022-05-26 | 35600 | keep | 0 | May | 2022 | 0.024247 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-26 22:07 | 2022-05-27 02:47 | 100 | 004:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22052600591 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 280 | 2022-05-26 | 28000 | keep | 0 | May | 2022 | 0.019071 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-05-26 22:18 | 2022-05-27 07:29 | 20 | 009:11 | P | NO SE REPORTO CAUSA | 1 X SMU 20 DE 40A EN EL SU - 4 NO CAUSA | C22052600302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 551 | 2022-05-26 | 11020 | keep | 0 | May | 2022 | 0.0075057 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-05-26 22:39 | 2022-05-27 15:45 | 25 | 017:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052600596 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1026 | 2022-05-26 | 25650 | keep | 0 | May | 2022 | 0.01747 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-05-26 23:10 | 2022-05-27 08:37 | 75 | 009:27 | P | DESGANCHE | 2 X 50 EN C/L | C22052600306 | New_Event | Vegetation Contact | Include | Include | Vegetation | 567 | 2022-05-26 | 42525 | keep | 0 | May | 2022 | 0.028964 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-05-26 23:11 | 2022-05-27 09:09 | 40 | 009:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052600238 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 598 | 2022-05-26 | 23920 | keep | 0 | May | 2022 | 0.016292 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-05-27 00:01 | 2022-05-27 09:47 | 30 | 009:46 | P | OTRAS CAUSAS | 1 X 50 EN CORTE DE LINEA CONTAMINACION (SALITRE) FUSIBLE | A22052700001 | New_Event | Other Causes | Include | Include | Other | 586 | 2022-05-27 | 17580 | keep | 0 | May | 2022 | 0.011974 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-05-27 01:17 | 2022-05-27 12:52 | 60 | 011:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22052700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 695 | 2022-05-27 | 41700 | keep | 0 | May | 2022 | 0.028402 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-05-27 01:41 | 2022-05-27 01:45 | 1106 | 000:04 | P | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1529-15 LLEVANDO 60% 1346-02. SE CERRO POR SCADA | S22052700000 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 4 | 2022-05-27 | 4424 | keep | 0 | May | 2022 | 0.0030132 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
BAYAMON | 2022-05-27 01:41 | 2022-05-27 01:45 | 1802 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 LLEVANDO 60% 1346-02. SE CERRO POR SCADA | S22052700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-05-27 | 7208 | keep | 0 | May | 2022 | 0.0049093 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
CAGUAS | 2022-05-27 02:25 | 2022-05-27 02:26 | 1655 | 000:01 | T | DESGANCHE | RECERRO | C22052700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-05-27 | 1655 | keep | 0 | May | 2022 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-05-27 02:26 | 2022-05-27 15:27 | 100 | 013:01 | P | DESGANCHE | 2 X 65 EN C/L | C22052700093 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 781 | 2022-05-27 | 78100 | keep | 0 | May | 2022 | 0.053194 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-27 02:43 | 2022-05-27 02:44 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22052700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-27 | 3458 | keep | 0 | May | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2022-05-27 03:39 | 2022-05-27 15:37 | 51 | 011:58 | P | DESGANCHE | 1 X 100 EN C/L | C22052700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 718 | 2022-05-27 | 36618 | keep | 0 | May | 2022 | 0.02494 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
CAGUAS | 2022-05-27 04:43 | 2022-05-27 08:54 | 200 | 004:11 | P | MAL TIEMPO/RAYOS | 2 X 65 EN C/L 1 X 40 EN RISER 1 X 65 EN C/L 1 X 20 EN XMR MAL TIEMPO DESCARGAS ELECTRICAS | C22052700012 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 251 | 2022-05-27 | 50200 | keep | 0 | May | 2022 | 0.034191 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-05-27 04:57 | 2022-05-27 04:58 | 2276 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3000 | C22052700013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 2276 | keep | 0 | May | 2022 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-05-27 04:57 | 2022-05-27 04:58 | 777 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3000 | C22052700013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 777 | keep | 0 | May | 2022 | 0.00052921 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-05-27 04:57 | 2022-05-27 04:58 | 12 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3000 | C22052700013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 12 | keep | 0 | May | 2022 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-05-27 04:57 | 2022-05-27 04:58 | 1290 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3000 | C22052700013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 1290 | keep | 0 | May | 2022 | 0.00087861 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
CAGUAS | 2022-05-27 04:58 | 2022-05-27 14:08 | 1 | 009:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C22052600250 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 550 | 2022-05-27 | 550 | keep | 0 | May | 2022 | 0.0003746 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-05-27 05:26 | 2022-05-27 05:27 | 125 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22052800012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-27 | 125 | keep | 0 | May | 2022 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-05-27 05:35 | 2022-05-27 14:48 | 150 | 009:13 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S22052700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 553 | 2022-05-27 | 82950 | keep | 0 | May | 2022 | 0.056497 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-05-27 06:16 | 2022-05-27 12:05 | 29 | 005:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22052700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 349 | 2022-05-27 | 10121 | keep | 0 | May | 2022 | 0.0068934 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2022-05-27 06:43 | 2022-05-28 08:08 | 11 | 025:25 | P | ANIMAL | 1X20 EN XMER (POR NIDO DE AVES EN EL 13KV) | B22052700006 | New_Event | Animals | Include | Include | Wildlife | 1525 | 2022-05-27 | 16775 | keep | 0 | May | 2022 | 0.011425 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-05-27 06:45 | 2022-05-27 16:00 | 60 | 009:15 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052700010 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 555 | 2022-05-27 | 33300 | keep | 0 | May | 2022 | 0.02268 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-05-27 06:49 | 2022-05-27 12:10 | 2 | 005:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A22052700003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 321 | 2022-05-27 | 642 | keep | 0 | May | 2022 | 0.00043726 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-05-27 07:01 | 2022-05-27 07:02 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1711-02 Y SE CERRO POR SCADA LLEVA 1711-05 | B22052700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-27 | 723 | keep | 0 | May | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-05-27 07:01 | 2022-05-27 07:02 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1711-02 Y SE CERRO POR SCADA LLEVA 1711-05 | B22052700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-27 | 1976 | keep | 0 | May | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
MAYAGÃœEZ | 2022-05-27 07:11 | 2022-05-27 16:00 | 40 | 008:49 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052700014 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 529 | 2022-05-27 | 21160 | keep | 0 | May | 2022 | 0.014412 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-27 07:16 | 2022-05-27 07:17 | 75 | 000:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600. 45% DE SU CARGA TRANSFERIDA AL 1342-04 | S22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 75 | keep | 0 | May | 2022 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-05-27 07:16 | 2022-05-27 07:17 | 457 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 457 | keep | 0 | May | 2022 | 0.00031126 | 0.00031126 | Momentary | FALSE | FALSE | Not_TMED_Event | 457
SAN JUAN | 2022-05-27 07:16 | 2022-05-27 07:17 | 3433 | 000:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600. 20% DE SU CARGA TRANSFERIDA AL 1303-02 | S22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 3433 | keep | 0 | May | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
SAN JUAN | 2022-05-27 07:16 | 2022-05-27 07:17 | 414 | 000:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600. 70% DE SU CARGA TRANSFERIDA A 1303-2 Y 1336-08 | S22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 414 | keep | 0 | May | 2022 | 0.00028197 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
SAN JUAN | 2022-05-27 07:18 | 2022-05-27 07:19 | 10211 | 000:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | S22052700000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-05-27 | 10211 | keep | 0 | May | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-05-27 07:18 | 2022-05-27 07:19 | 4133 | 000:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | S22052700000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-05-27 | 4133 | keep | 0 | May | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
HUMACAO | 2022-05-27 07:18 | 2022-05-27 09:36 | 40 | 002:18 | P | DESGANCHE | 1 X 40 EN C/L | C22052700039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-05-27 | 5520 | keep | 0 | May | 2022 | 0.0037596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-05-27 07:19 | 2022-05-27 11:10 | 1101 | 003:51 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA TRONCAL EN MACHETE | S22052700012 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 231 | 2022-05-27 | 254331 | keep | 0 | May | 2022 | 0.17322 | 0.00074989 | Sustained | FALSE | FALSE | Not_TMED_Event | 1101
SAN JUAN | 2022-05-27 07:20 | 2022-05-27 12:57 | 80 | 005:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22052700015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2022-05-27 | 26960 | keep | 0 | May | 2022 | 0.018362 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-05-27 07:20 | 2022-05-27 22:00 | 30 | 014:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22052700097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 880 | 2022-05-27 | 26400 | keep | 0 | May | 2022 | 0.017981 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-05-27 07:22 | 2022-05-27 08:30 | 7 | 001:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR MAL TIEMPO GRANIZO | C22052700040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 68 | 2022-05-27 | 476 | keep | 0 | May | 2022 | 0.0003242 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-05-27 07:38 | 2022-05-27 07:39 | 1225 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 1225 | keep | 0 | May | 2022 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-05-27 07:38 | 2022-05-27 07:39 | 1452 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 1452 | keep | 0 | May | 2022 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-05-27 07:38 | 2022-05-27 07:39 | 616 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 616 | keep | 0 | May | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
ARECIBO | 2022-05-27 07:59 | 2022-05-27 08:00 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22052700015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-27 | 2697 | keep | 0 | May | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
UTUADO | 2022-05-27 08:01 | 2022-05-28 10:15 | 70 | 026:14 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052700014 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1574 | 2022-05-27 | 110180 | keep | 0 | May | 2022 | 0.075043 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2022-05-27 08:28 | 2022-05-27 11:55 | 1 | 003:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN BANCO DE TRANSFORMADORES SE REEMPLAZO PORTAFUSIBLE | R22052700004 | New_Event | Cutout Failure | Include | Include | Equipment | 207 | 2022-05-27 | 207 | keep | 0 | May | 2022 | 0.00014099 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-27 08:30 | 2022-05-29 19:50 | 20 | 059:20 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA PERSONAL DE LIBERTY REALIZANDO TRABAJOS CRUZO FASES | M22052900004 | New_Event | Damage From Public | Include | Include | Public | 3560 | 2022-05-27 | 71200 | keep | 0 | May | 2022 | 0.048494 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-05-27 08:34 | 2022-05-27 11:40 | 25 | 003:06 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 50 KVA X 50 KVA | R22052700005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 186 | 2022-05-27 | 4650 | keep | 0 | May | 2022 | 0.0031671 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-27 08:36 | 2022-05-27 16:00 | 1 | 007:24 | P | MAL TIEMPO/RAYOS | 2 X 20 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22052700034 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 444 | 2022-05-27 | 444 | keep | 0 | May | 2022 | 0.00030241 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-27 08:42 | 2022-05-27 09:29 | 77 | 000:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22052700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-05-27 | 3619 | keep | 0 | May | 2022 | 0.0024649 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2022-05-27 08:44 | 2022-05-27 15:29 | 37 | 006:45 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B22052700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2022-05-27 | 14985 | keep | 0 | May | 2022 | 0.010206 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CANOVANAS | 2022-05-27 08:54 | 2022-05-27 10:46 | 3838 | 001:52 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SUBESTACION SIN RTU CERRADO EN LA SUBESTACION | R22052700076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2022-05-27 | 429856 | keep | 0 | May | 2022 | 0.29277 | 0.002614 | Sustained | FALSE | FALSE | Not_TMED_Event | 3838
BAYAMON | 2022-05-27 08:59 | 2022-05-28 11:54 | 25 | 026:55 | P | CONDUCTOR ROTO O ABIERTO | 1X80 EN C/L & SE CERRO PUENTE PRIMARIO DE CAJA @ LINEA | B22052700020 | New_Event | Primary Wire Break | Include | Include | Equipment | 1615 | 2022-05-27 | 40375 | keep | 0 | May | 2022 | 0.027499 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-05-27 09:01 | 2022-05-27 10:45 | 1105 | 001:44 | T | TRANSFORMADOR AVERIADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 40% EN SERVICIO | B22052700021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 104 | 2022-05-27 | 114920 | keep | 0 | May | 2022 | 0.078271 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
UTUADO | 2022-05-27 09:05 | 2022-05-27 10:26 | 1 | 001:21 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A22052700028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 81 | 2022-05-27 | 81 | keep | 0 | May | 2022 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-05-27 09:06 | 2022-05-27 20:00 | 2 | 010:54 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR QUEMADO 15 KVA SE RELOCALIZO SECUNDARIA | M22052700045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 654 | 2022-05-27 | 1308 | keep | 0 | May | 2022 | 0.00089087 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-05-27 09:07 | 2022-05-27 19:40 | 1 | 010:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE IDENTIFICO CAUSA | M22052700047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 633 | 2022-05-27 | 633 | keep | 0 | May | 2022 | 0.00043113 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-27 09:21 | 2022-05-27 20:15 | 3 | 010:54 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052700030 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 654 | 2022-05-27 | 1962 | keep | 0 | May | 2022 | 0.0013363 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-05-27 09:27 | 2022-05-27 13:17 | 77 | 003:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN C/L REMPLAZO AISLADOR ROTO | C22052700075 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 230 | 2022-05-27 | 17710 | keep | 0 | May | 2022 | 0.012062 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
CAGUAS | 2022-05-27 09:29 | 2022-05-27 11:33 | 65 | 002:04 | P | DESGANCHE | 1 X 80 EN C/L | C22052700077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-05-27 | 8060 | keep | 0 | May | 2022 | 0.0054896 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-05-27 09:29 | 2022-05-27 11:40 | 181 | 002:11 | P | DESGANCHE | 1 X 65 Y 2 X 50 EN C/L'S | C22052700269 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-05-27 | 23711 | keep | 0 | May | 2022 | 0.016149 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
UTUADO | 2022-05-27 09:37 | 2022-05-27 13:32 | 50 | 003:55 | P | DESGANCHE | 1 X 40 EN CONVERTIDOR Y 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22052700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-05-27 | 11750 | keep | 0 | May | 2022 | 0.0080029 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-05-27 09:45 | 2022-05-27 10:42 | 250 | 000:57 | P | PROTECCION DEFECTUOSA | DISPARO DE UNIDAD PORTATIL #8 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1348-08 UN 100%, 1348-06 UN 20%, 1336-08 UN 20%. | S22052700000 | New_Event | Protection Miscoordination | Include | Include | Other | 57 | 2022-05-27 | 14250 | keep | 0 | May | 2022 | 0.0097056 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-05-27 09:45 | 2022-05-27 10:42 | 1290 | 000:57 | T | PROTECCION DEFECTUOSA | DISPARO DE UNIDAD PORTATIL #8 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1348-08 UN 100%, 1348-06 UN 20%, 1336-08 UN 20%. | S22052700000 | New_Event | Protection Miscoordination | Include | Include | Other | 57 | 2022-05-27 | 73530 | keep | 0 | May | 2022 | 0.050081 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2022-05-27 09:52 | 2022-05-27 14:35 | 1 | 004:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER PRIVADO | B22052700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2022-05-27 | 283 | keep | 0 | May | 2022 | 0.00019275 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-27 10:05 | 2022-05-27 12:26 | 50 | 002:21 | P | CAUSAS EXTERNAS | 1 X 80 EN C/L DESGANCHE NO CONTRATADO | S22052700169 | New_Event | Damage From Public | Include | Include | Public | 141 | 2022-05-27 | 7050 | keep | 0 | May | 2022 | 0.0048017 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-05-27 10:15 | 2022-05-27 13:45 | 40 | 003:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22052700067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-05-27 | 8400 | keep | 0 | May | 2022 | 0.0057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-05-27 10:16 | 2022-05-27 12:24 | 6 | 002:08 | P | MAL TIEMPO/RAYOS | 2 X 5 EN TRANSFORMADOR RAYOS | P22052700027 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 128 | 2022-05-27 | 768 | keep | 0 | May | 2022 | 0.00052308 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-05-27 10:31 | 2022-05-27 13:15 | 1 | 002:44 | P | NO SE REPORTO CAUSA | 2 X 10 EN MONTURA PARA BOMBAS (AAA) | A22052700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-05-27 | 164 | keep | 0 | May | 2022 | 0.0001117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-05-27 10:45 | 2022-05-27 11:49 | 663 | 001:04 | P | TRANSFORMADOR AVERIADO | DISPARO DE ALIMENTADOR AL CERRAR MACHETES EN CARR 167 FRENYE A LOS CHECOS. SE DEJO ABIERTO Y SE CERRO POR SCADA 40% EN SERVICIO | B22052700021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 64 | 2022-05-27 | 42432 | keep | 0 | May | 2022 | 0.0289 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
SAN JUAN | 2022-05-27 11:00 | 2022-05-27 14:38 | 1058 | 003:38 | P | NO SE REPORTO CAUSA | DISPARO PORTATIL# 8 SE INSPECCION DIO FASE A A TIERRA Y SE RESETO Y SE CERRO PORTATIL QUEDO EN SERVICIO | S22052700272 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2022-05-27 | 230644 | keep | 0 | May | 2022 | 0.15709 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2022-05-27 11:00 | 2022-05-27 14:38 | 250 | 003:38 | P | PROTECCION DEFECTUOSA | DISPARO PORTATIL# 8 SE INSPECCION DIO FASE A A TIERRA Y SE RESETO Y SE CERRO PORTATIL QUEDO EN SERVICIO | S22052700272 | New_Event | Protection Miscoordination | Include | Include | Other | 218 | 2022-05-27 | 54500 | keep | 0 | May | 2022 | 0.03712 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-05-27 11:00 | 2022-05-27 14:38 | 1290 | 003:38 | T | PROTECCION DEFECTUOSA | DISPARO PORTATIL# 8 SE INSPECCION DIO FASE A A TIERRA Y SE RESETO Y SE CERRO PORTATIL QUEDO EN SERVICIO | S22052700272 | New_Event | Protection Miscoordination | Include | Include | Other | 218 | 2022-05-27 | 281220 | keep | 0 | May | 2022 | 0.19154 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
CAGUAS | 2022-05-27 11:34 | 2022-05-28 09:28 | 20 | 021:54 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22052700102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1314 | 2022-05-27 | 26280 | keep | 0 | May | 2022 | 0.017899 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-05-27 11:35 | 2022-05-28 15:30 | 1 | 027:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 37.5 KVA | A22052700050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1675 | 2022-05-27 | 1675 | keep | 0 | May | 2022 | 0.0011408 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-05-27 11:37 | 2022-05-27 12:26 | 150 | 000:49 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22052700095 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 49 | 2022-05-27 | 7350 | keep | 0 | May | 2022 | 0.0050061 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-05-27 11:47 | 2022-05-27 12:22 | 5 | 000:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA DEFECTUOSA | A22052700052 | New_Event | Cutout Failure | Include | Include | Equipment | 35 | 2022-05-27 | 175 | keep | 0 | May | 2022 | 0.00011919 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-05-27 11:49 | 2022-05-27 11:50 | 1105 | 000:01 | T | TRANSFORMADOR AVERIADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 40% EN SERVICIO | B22052700021 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-05-27 | 1105 | keep | 0 | May | 2022 | 0.00075261 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-27 11:50 | 2022-05-27 12:07 | 663 | 000:17 | P | TRANSFORMADOR AVERIADO | DISPARO DE ALIMENTADOR AL CERRAR MACHETES EN CARR 167 FRENYE A LOS CHECOS. SE DEJO ABIERTO Y SE CERRO POR SCADA 40% EN SERVICIO | B22052700021 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 17 | 2022-05-27 | 11271 | keep | 0 | May | 2022 | 0.0076766 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
AGUADILLA | 2022-05-27 11:51 | 2022-05-27 19:30 | 100 | 007:39 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | M22052700098 | New_Event | Primary Wire Break | Include | Include | Equipment | 459 | 2022-05-27 | 45900 | keep | 0 | May | 2022 | 0.031262 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-05-27 12:01 | 2022-05-27 12:02 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22052700102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-27 | 4381 | keep | 0 | May | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
BAYAMON | 2022-05-27 12:07 | 2022-05-27 12:08 | 1105 | 000:01 | T | TRANSFORMADOR AVERIADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 40% EN SERVICIO | B22052700021 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-05-27 | 1105 | keep | 0 | May | 2022 | 0.00075261 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-05-27 12:08 | 2022-05-27 12:43 | 663 | 000:35 | P | TRANSFORMADOR AVERIADO | SE CERRO MACHETES EN CARR 167 FRENTE A LOS CHECOS ABRIENDO ENTRADA DE CONVERTIDOR EN CARR 167 FRENTE A AREA DE PESCA Y ABRIENDO EN CARR 812 KM 0.4 60% EN SERVICIO | B22052700021 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 35 | 2022-05-27 | 23205 | keep | 0 | May | 2022 | 0.015805 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
MAYAGÃœEZ | 2022-05-27 12:09 | 2022-05-27 19:10 | 45 | 007:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22052700106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2022-05-27 | 18945 | keep | 0 | May | 2022 | 0.012903 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-05-27 12:09 | 2022-05-28 13:21 | 59 | 025:12 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | B22052700050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1512 | 2022-05-27 | 89208 | keep | 0 | May | 2022 | 0.060759 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
CAGUAS | 2022-05-27 12:13 | 2022-05-28 13:18 | 7 | 025:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22052700178 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1505 | 2022-05-27 | 10535 | keep | 0 | May | 2022 | 0.0071753 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-05-27 12:28 | 2022-05-27 13:13 | 40 | 000:45 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | M22052700056 | New_Event | Primary Wire Break | Include | Include | Equipment | 45 | 2022-05-27 | 1800 | keep | 0 | May | 2022 | 0.001226 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-05-27 12:30 | 2022-05-27 13:33 | 55 | 001:03 | P | DESGANCHE | 1 X 65 EN C/L | R22052700085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-05-27 | 3465 | keep | 0 | May | 2022 | 0.00236 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2022-05-27 12:41 | 2022-05-27 15:28 | 7 | 002:47 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052700058 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 167 | 2022-05-27 | 1169 | keep | 0 | May | 2022 | 0.0007962 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-05-27 12:43 | 2022-05-27 12:45 | 442 | 000:02 | P | TRANSFORMADOR AVERIADO | SE CERRO MACHETES EN CARR 812 KM 0.4 BO DAJAOS DEJANDO ABIERTO ENTRADA DE CONVERTIDOR CARR 167 90% EN SERVICIO | B22052700021 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 2 | 2022-05-27 | 884 | keep | 0 | May | 2022 | 0.00060209 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-05-27 12:44 | 2022-05-27 20:29 | 4 | 007:45 | P | MAL TIEMPO/RAYOS | 1 X 15 TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22052700059 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 465 | 2022-05-27 | 1860 | keep | 0 | May | 2022 | 0.0012668 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-05-27 12:45 | 2022-05-28 16:30 | 80 | 027:45 | P | TRANSFORMADOR AVERIADO | SE TRANSFIRIO LA CARGA DEL CONVERTIDOR (QUEMADO) AL 9801-01 | B22052700021 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 1665 | 2022-05-27 | 133200 | keep | 0 | May | 2022 | 0.090722 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-05-27 12:45 | 2022-05-27 18:45 | 1 | 006:00 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22052700060 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 360 | 2022-05-27 | 360 | keep | 0 | May | 2022 | 0.00024519 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-05-27 12:48 | 2022-05-27 12:49 | 1058 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE UNIDAD PORTATIL #8 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1348-08 UN 100%, 1348-06 UN 20%, 1336-08 UN 20%. | S22052700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-05-27 | 1058 | keep | 0 | May | 2022 | 0.0007206 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
MAYAGÃœEZ | 2022-05-27 12:48 | 2022-05-27 20:50 | 8 | 008:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M22052700117 | New_Event | Primary Wire Break | Include | Include | Equipment | 482 | 2022-05-27 | 3856 | keep | 0 | May | 2022 | 0.0026263 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-05-27 12:59 | 2022-05-27 14:08 | 54 | 001:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REMPLAZO CAJA QUEMADA | C22052700113 | New_Event | Cutout Failure | Include | Include | Equipment | 69 | 2022-05-27 | 3726 | keep | 0 | May | 2022 | 0.0025378 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
PONCE | 2022-05-27 13:00 | 2022-05-27 17:18 | 25 | 004:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P22052700042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2022-05-27 | 6450 | keep | 0 | May | 2022 | 0.0043931 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-05-27 13:01 | 2022-05-29 15:15 | 50 | 050:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | M22052700121 | New_Event | Primary Wire Break | Include | Include | Equipment | 3014 | 2022-05-27 | 150700 | keep | 0 | May | 2022 | 0.10264 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-05-27 13:05 | 2022-05-27 14:35 | 166 | 001:30 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L CAMION DE TELEFONIA MOVIO LINEAS | R22052700086 | New_Event | Damage From Public | Include | Include | Public | 90 | 2022-05-27 | 14940 | keep | 0 | May | 2022 | 0.010176 | 0.00011306 | Sustained | FALSE | FALSE | Not_TMED_Event | 166
BARRANQUITAS | 2022-05-27 13:07 | 2022-05-27 17:51 | 10 | 004:44 | P | NO SE REPORTO CAUSA | 1 X 10 XMR NO CAUSA | C22052700115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 284 | 2022-05-27 | 2840 | keep | 0 | May | 2022 | 0.0019343 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-05-27 13:13 | 2022-05-27 14:00 | 300 | 000:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA | M22052700125 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 47 | 2022-05-27 | 14100 | keep | 0 | May | 2022 | 0.0096034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-05-27 13:15 | 2022-05-27 14:40 | 15 | 001:25 | P | CAUSAS EXTERNAS | SE ABRE MONTURA PARA INSTALAR VARILLA ESTABA FLOTANTE | S22052700069 | New_Event | Damage From Public | Include | Include | Public | 85 | 2022-05-27 | 1275 | keep | 0 | May | 2022 | 0.0008684 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-05-27 13:16 | 2022-05-28 16:40 | 150 | 027:24 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 Y 1 X 100 EN CORTES DE LINEAS SE REALIZO DESGANCHE Y SE REPARO LINEA PRIMARIA ROTA | M22052700124 | New_Event | Primary Wire Break | Include | Include | Equipment | 1644 | 2022-05-27 | 246600 | keep | 0 | May | 2022 | 0.16796 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-05-27 13:22 | 2022-05-28 08:50 | 1 | 019:28 | P | MAL TIEMPO/RAYOS | 1 X 8 EN MONTURA DE TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22052700126 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1168 | 2022-05-27 | 1168 | keep | 0 | May | 2022 | 0.00079552 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-05-27 13:32 | 2022-05-27 18:29 | 4 | 004:57 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22052700035 | New_Event | Primary Wire Break | Include | Include | Equipment | 297 | 2022-05-27 | 1188 | keep | 0 | May | 2022 | 0.00080914 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-05-27 13:35 | 2022-05-27 13:36 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 1253 | keep | 0 | May | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-05-27 13:35 | 2022-05-27 13:36 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 1266 | keep | 0 | May | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-05-27 13:35 | 2022-05-27 13:36 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 411 | keep | 0 | May | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-05-27 13:35 | 2022-05-27 13:36 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 1617 | keep | 0 | May | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-05-27 13:35 | 2022-05-27 13:36 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 1017 | keep | 0 | May | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-05-27 13:35 | 2022-05-27 13:36 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-05-27 | 828 | keep | 0 | May | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828