GUAYAMA | 2022-12-28 11:54 | 2022-12-28 13:46 | 20 | 1:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO VIENTOS | P22122800062 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 112 | 2022-12-28 | 2240 | keep | 0 | Dec | 2022 | 0.0015257 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-12-28 12:00 | 2022-12-28 13:40 | 20 | 1:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA | B22122800076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 100 | 2022-12-28 | 2000 | keep | 0 | Dec | 2022 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-12-28 12:31 | 2022-12-28 15:40 | 11 | 3:09 | P | CONDUCTOR ROTO O ABIERTO | ABRIR XMR CERRAR PUENTE DE CAJA A XMR | B22122800126 | New_Event | Primary Wire Break | Include | Include | Equipment | 189 | 2022-12-28 | 2079 | keep | 0 | Dec | 2022 | 0.001416 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2022-12-28 12:40 | 2022-12-28 14:55 | 15 | 2:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M22122800149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-12-28 | 2025 | keep | 0 | Dec | 2022 | 0.0013792 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-12-28 12:56 | 2022-12-28 19:18 | 30 | 6:22 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L SE CERRO PUENTE PRIMARIO Y SE REPARO BAJANTE SECUNDARIO | S22122800345 | New_Event | Primary Wire Break | Include | Include | Equipment | 382 | 2022-12-28 | 11460 | keep | 0 | Dec | 2022 | 0.0078054 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-12-28 13:00 | 2022-12-28 14:00 | 8 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARAN CONEXIONES | A22122800045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-12-28 | 480 | keep | 0 | Dec | 2022 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-12-28 13:00 | 2022-12-28 14:00 | 8 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS AVERIADAS | M22122800098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-12-28 | 480 | keep | 0 | Dec | 2022 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-12-28 13:17 | 2022-12-28 20:20 | 40 | 7:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PARTIDO | A22122800053 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 423 | 2022-12-28 | 16920 | keep | 0 | Dec | 2022 | 0.011524 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-12-28 13:20 | 2022-12-28 14:36 | 56 | 1:16 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S22122800348 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-12-28 | 4256 | keep | 0 | Dec | 2022 | 0.0028987 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
AGUADILLA | 2022-12-28 13:20 | 2022-12-28 19:45 | 80 | 6:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22122800161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 385 | 2022-12-28 | 30800 | keep | 0 | Dec | 2022 | 0.020978 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-12-28 13:20 | 2022-12-28 14:00 | 250 | 0:40 | P | CAUSAS EXTERNAS | 2 X 50 EN CORTE DE LINEA POR CARPA | A22122800055 | New_Event | Damage From Public | Include | Include | Public | 40 | 2022-12-28 | 10000 | keep | 0 | Dec | 2022 | 0.006811 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2022-12-28 13:23 | 2022-12-28 13:24 | 3046 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR 1646-03 LLEVANDO CARGA 1647-10 Y 15% 1647-09 | R2212280000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-12-28 | 3046 | keep | 0 | Dec | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2022-12-28 13:23 | 2022-12-28 13:24 | 307 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1646-03 LLEVANDO CARGA 1647-10 Y 15% 1647-09 | R2212280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-28 | 307 | keep | 0 | Dec | 2022 | 0.0002091 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
CANOVANAS | 2022-12-28 13:23 | 2022-12-28 13:24 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1646-03 LLEVANDO CARGA 1647-10 Y 15% 1647-09 | R2212280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-28 | 61 | keep | 0 | Dec | 2022 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2022-12-28 13:24 | 2022-12-28 14:35 | 113 | 1:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22122800049 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-12-28 | 8023 | keep | 0 | Dec | 2022 | 0.0054644 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
CAGUAS | 2022-12-28 13:42 | 2022-12-28 14:55 | 2 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 5 EN XMR | C22122800094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-12-28 | 146 | keep | 0 | Dec | 2022 | 9.944e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-12-28 13:43 | 2022-12-28 14:43 | 12 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | P22122800077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-12-28 | 720 | keep | 0 | Dec | 2022 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-12-28 13:46 | 2022-12-28 17:20 | 77 | 3:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 50 EN CORTE DE LINEA | P22122800079 | New_Event | Cutout Failure | Include | Include | Equipment | 214 | 2022-12-28 | 16478 | keep | 0 | Dec | 2022 | 0.011223 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
VEGA BAJA | 2022-12-28 13:55 | 2022-12-29 08:25 | 15 | 18:30 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR POR CAUSA DE UNA AVERIA DE LINEA PRIMARIA ROTA DEL DIA DE AYER | A22122900010 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1110 | 2022-12-28 | 16650 | keep | 0 | Dec | 2022 | 0.01134 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-28 14:05 | 2022-12-29 16:55 | 23 | 26:50 | P | CABLE SOTERRADO AVERIADO | BY-221228-01 SE REPARO TRAMO SOTERRADO DEL T-81 @ T-80 SE REMPLAZO SUMERGIBLE QUE FUE AVERIADO REALIZANDO OPERACIONES | B22122700151 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1610 | 2022-12-28 | 37030 | keep | 0 | Dec | 2022 | 0.025221 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-12-28 14:09 | 2022-12-28 16:50 | 60 | 2:41 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A22122800062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-12-28 | 9660 | keep | 0 | Dec | 2022 | 0.0065794 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-12-28 14:14 | 2022-12-28 21:04 | 6 | 6:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZA TRANSFORMADOR DE 50KVA | A22122800063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 410 | 2022-12-28 | 2460 | keep | 0 | Dec | 2022 | 0.0016755 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-12-28 14:18 | 2022-12-28 14:43 | 5 | 0:25 | P | CONDUCTOR ROTO O ABIERTO | 1 X 25 EN TRANSFORMADOR POR LINEA PARTIDA | A22122800064 | New_Event | Primary Wire Break | Include | Include | Equipment | 25 | 2022-12-28 | 125 | keep | 0 | Dec | 2022 | 8.5137e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-12-28 14:24 | 2022-12-28 15:18 | 2 | 0:54 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | R22122800059 | New_Event | Primary Wire Break | Include | Include | Equipment | 54 | 2022-12-28 | 108 | keep | 0 | Dec | 2022 | 7.3558e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-12-28 14:25 | 2022-12-28 15:07 | 1 | 0:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22122800156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 42 | 2022-12-28 | 42 | keep | 0 | Dec | 2022 | 2.8606e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-12-28 14:42 | 2022-12-28 16:40 | 6 | 1:58 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | 1 X 8 EN TRANSFORMADOR Y SE SECCIONALIZO POSTE SECUNDARIO ROTO | M22122800174 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 118 | 2022-12-28 | 708 | keep | 0 | Dec | 2022 | 0.00048222 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-12-28 14:48 | 2022-12-28 14:50 | 3718 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | S22122800370 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-12-28 | 7436 | keep | 0 | Dec | 2022 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2022-12-28 15:16 | 2022-12-28 17:32 | 12 | 2:16 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P22122800097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-12-28 | 1632 | keep | 0 | Dec | 2022 | 0.0011115 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-12-28 15:34 | 2022-12-28 20:58 | 100 | 5:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22122800178 | New_Event | Primary Wire Break | Include | Include | Equipment | 324 | 2022-12-28 | 32400 | keep | 0 | Dec | 2022 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-12-28 15:49 | 2022-12-28 19:01 | 10 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | 4 X 15 Y 1 X 10 EN TRANSFORMADOR Y 1 X 30 EN CORTE DE LINEA POR LINEA PARTIDA | A22122800073 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2022-12-28 | 1920 | keep | 0 | Dec | 2022 | 0.0013077 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-12-28 15:56 | 2022-12-28 17:30 | 60 | 1:34 | P | CAUSAS EXTERNAS | 1 X 80 EN CORTE DE LINEA CAMION SACUDIO LAS LINEAS | B22122800115 | New_Event | Damage From Public | Include | Include | Public | 94 | 2022-12-28 | 5640 | keep | 0 | Dec | 2022 | 0.0038414 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-12-28 16:00 | 2022-12-28 16:45 | 15 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR PUENTE SECUNDARIO ABIERTO | M22122800170 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-12-28 | 675 | keep | 0 | Dec | 2022 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-12-28 16:00 | 2022-12-28 17:00 | 10 | 1:00 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REPARO BUSHING SECUNDARIO | B22122800182 | New_Event | Service Transformer Failure | Include | Include | Equipment | 60 | 2022-12-28 | 600 | keep | 0 | Dec | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-12-28 16:08 | 2022-12-28 17:46 | 120 | 1:38 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | B22122800183 | New_Event | Animals | Include | Include | Wildlife | 98 | 2022-12-28 | 11760 | keep | 0 | Dec | 2022 | 0.0080097 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-12-28 16:21 | 2022-12-28 18:40 | 33 | 2:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22122800068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-12-28 | 4587 | keep | 0 | Dec | 2022 | 0.0031242 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
FAJARDO | 2022-12-28 16:30 | 2022-12-28 18:15 | 10 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO DOS BARRAS EN PEDESTAL | R22122800069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2022-12-28 | 1050 | keep | 0 | Dec | 2022 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-12-28 16:38 | 2022-12-28 16:39 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2212280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-28 | 45 | keep | 0 | Dec | 2022 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-12-28 16:39 | 2022-12-28 17:43 | 1 | 1:04 | P | DESGANCHE | SE REPUSO 1 X 8 EN XMR SE CERRO PUENTE DE LINEA A CAJA DE XMR Y SE HIZO DESGANCHE. | R22122800074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-12-28 | 64 | keep | 0 | Dec | 2022 | 4.359e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-12-28 16:59 | 2022-12-28 18:32 | 60 | 1:33 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P22122800111 | New_Event | Animals | Include | Include | Wildlife | 93 | 2022-12-28 | 5580 | keep | 0 | Dec | 2022 | 0.0038005 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-12-28 17:07 | 2022-12-28 17:35 | 12 | 0:28 | P | SECUNDARIA/DESGANCHE | ABRIR XMR DESGANCHE | B22122800195 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 28 | 2022-12-28 | 336 | keep | 0 | Dec | 2022 | 0.00022885 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-12-28 17:09 | 2022-12-29 10:05 | 1 | 16:56 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | S22122800393 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1016 | 2022-12-28 | 1016 | keep | 0 | Dec | 2022 | 0.00069199 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-12-28 17:19 | 2022-12-28 17:38 | 1 | 0:19 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO BEJUCO | R22122800052 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 19 | 2022-12-28 | 19 | keep | 0 | Dec | 2022 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-12-28 17:30 | 2022-12-28 17:31 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2212280000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-28 | 45 | keep | 0 | Dec | 2022 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-12-28 17:32 | 2022-12-28 22:10 | 65 | 4:38 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22122800082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 278 | 2022-12-28 | 18070 | keep | 0 | Dec | 2022 | 0.012307 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-12-28 17:41 | 2022-12-28 17:42 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2212280000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-28 | 45 | keep | 0 | Dec | 2022 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-12-28 17:43 | 2022-12-28 22:55 | 8 | 5:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO SECUNDARIA DEL SUELO | S22122800400 | New_Event | Secondary Wire Break | Include | Include | Equipment | 312 | 2022-12-28 | 2496 | keep | 0 | Dec | 2022 | 0.0017 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-12-28 18:05 | 2022-12-28 19:14 | 50 | 1:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22122800088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-12-28 | 3450 | keep | 0 | Dec | 2022 | 0.0023498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-12-28 18:12 | 2022-12-28 19:19 | 40 | 1:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22122800192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-12-28 | 2680 | keep | 0 | Dec | 2022 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-12-28 18:43 | 2022-12-28 18:47 | 1879 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 3006-02 LLEVA EL 3006-05 | C2212280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-12-28 | 7516 | keep | 0 | Dec | 2022 | 0.0051191 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2022-12-28 18:43 | 2022-12-28 18:47 | 3005 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR CARGA POR EL 3006-05 | C2212280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2022-12-28 | 12020 | keep | 0 | Dec | 2022 | 0.0081868 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
MAYAGÃœEZ | 2022-12-28 18:49 | 2022-12-28 21:45 | 80 | 2:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22122800199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2022-12-28 | 14080 | keep | 0 | Dec | 2022 | 0.0095898 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-12-28 19:20 | 2022-12-28 19:50 | 12 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REEMPLAZO DE CONEXIONES SECUNDARIAS SULFATADAS | P22122800130 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-12-28 | 360 | keep | 0 | Dec | 2022 | 0.00024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-12-28 19:27 | 2022-12-28 19:28 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2212280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-28 | 1307 | keep | 0 | Dec | 2022 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
FAJARDO | 2022-12-28 19:35 | 2022-12-28 20:00 | 8 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | R22122800087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-12-28 | 200 | keep | 0 | Dec | 2022 | 0.00013622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-12-28 19:55 | 2022-12-28 21:15 | 45 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR C/L PARA REPARAR SECUNDARIA POR ENCIMA DEL XMR | S22122800375 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2022-12-28 | 3600 | keep | 0 | Dec | 2022 | 0.0024519 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-12-28 19:57 | 2022-12-28 20:08 | 854 | 0:11 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR 1115-01 LLEVA 1119-04 Y LLEVA 99% DEL 1119-02 SE CERRO POR CONTROL | S22122800411 | New_Event | Feeder Load Transferred | Include | Include | Other | 11 | 2022-12-28 | 9394 | keep | 0 | Dec | 2022 | 0.0063982 | 0.00058166 | Sustained | FALSE | FALSE | Not_TMED_Event | 854
SAN JUAN | 2022-12-28 19:57 | 2022-12-28 20:08 | 2720 | 0:11 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR 1115-01 LLEVA 1119-04 Y LLEVA 99% DEL 1119-02 SE CERRO POR CONTROL | S22122800411 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-12-28 | 29920 | keep | 0 | Dec | 2022 | 0.020378 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
CANOVANAS | 2022-12-28 21:04 | 2022-12-28 21:05 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2212280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-28 | 2039 | keep | 0 | Dec | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
VEGA BAJA | 2022-12-28 21:41 | 2022-12-29 07:55 | 9 | 10:14 | P | CONDUCTOR ROTO O ABIERTO | 1 X 8 EN TRANSFORMADOR POR CAUSA DE UNA AVERIA DE LINEA PRIMARIA ROTA DEL DIA DE AYER | A22122800099 | New_Event | Primary Wire Break | Include | Include | Equipment | 614 | 2022-12-28 | 5526 | keep | 0 | Dec | 2022 | 0.0037637 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 1225 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA | S22122800444 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 2450 | keep | 0 | Dec | 2022 | 0.0016687 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 1452 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA | S22122800444 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 2904 | keep | 0 | Dec | 2022 | 0.0019779 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 616 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA LLEVA 25% DEL 1342-02 | S22122800444 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 1232 | keep | 0 | Dec | 2022 | 0.00083911 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 295 | 0:02 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE MONACILLOS A SABANA LLANA 35% DE LA CARGA POR EL 1345-05 | S2212280000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 590 | keep | 0 | Dec | 2022 | 0.00040185 | 0.00020092 | Momentary | FALSE | FALSE | Not_TMED_Event | 295
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 790 | 0:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA CARGA POR EL 1345-03 | S2212280000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 1580 | keep | 0 | Dec | 2022 | 0.0010761 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:00 | 98 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA CARGA POR EL 1203-01 | S22122800444 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-28 | 98 | keep | 0 | Dec | 2022 | 6.6747e-05 | 6.6747e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 98
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 660 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA | S22122800444 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 1320 | keep | 0 | Dec | 2022 | 0.00089905 | 0.00044952 | Momentary | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 435 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA LLEVA EL 80% DEL 1342-04 | S22122800444 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 870 | keep | 0 | Dec | 2022 | 0.00059255 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 259 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA LLEVA EL 1342-02 | S22122800444 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 518 | keep | 0 | Dec | 2022 | 0.00035281 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 686 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA | S22122800444 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 1372 | keep | 0 | Dec | 2022 | 0.00093446 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2022-12-28 21:59 | 2022-12-28 22:01 | 953 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA LLEVA 35% DE LA CARGA DEL 1330-04 | S22122800444 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-12-28 | 1906 | keep | 0 | Dec | 2022 | 0.0012982 | 0.00064908 | Momentary | FALSE | FALSE | Not_TMED_Event | 953
CANOVANAS | 2022-12-28 21:59 | 2022-12-28 22:00 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R2212280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-28 | 1026 | keep | 0 | Dec | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2022-12-28 22:00 | 2022-12-28 22:01 | 312 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE MONACILLOS A SABANA LLANA 80% DE LA CARGA POR EL 1345-02 | S2212280044 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-28 | 312 | keep | 0 | Dec | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2022-12-28 23:23 | 2022-12-29 13:36 | 60 | 14:13 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22122800450 | New_Event | Vegetation Contact | Include | Include | Vegetation | 853 | 2022-12-28 | 51180 | keep | 0 | Dec | 2022 | 0.034858 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-12-28 23:41 | 2022-12-28 23:44 | 723 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVANDO CARGA DEL 1711-05 LLEVANDO CARGA 10% DEL 1711-04 | B2212180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-12-28 | 2169 | keep | 0 | Dec | 2022 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-12-28 23:41 | 2022-12-28 23:44 | 198 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL 10% DE LA CARGA POR EL 1711-02 | B2212180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2022-12-28 | 594 | keep | 0 | Dec | 2022 | 0.00040457 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-28 23:41 | 2022-12-28 23:44 | 1976 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL CARGA POR EL 1711-02 | B2212180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2022-12-28 | 5928 | keep | 0 | Dec | 2022 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-12-28 23:41 | 2022-12-28 23:44 | 1812 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | B22122800221 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-12-28 | 5436 | keep | 0 | Dec | 2022 | 0.0037024 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
CANOVANAS | 2022-12-28 23:51 | 2022-12-29 09:25 | 83 | 9:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 65 EN C/L | R22122800091 | New_Event | Cutout Failure | Include | Include | Equipment | 574 | 2022-12-28 | 47642 | keep | 0 | Dec | 2022 | 0.032449 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
VEGA BAJA | 2022-12-28 23:55 | 2022-12-29 00:14 | 30 | 0:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22122800227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2022-12-28 | 570 | keep | 0 | Dec | 2022 | 0.00038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-12-29 00:14 | 2022-12-29 00:16 | 4702 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | B2212290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-12-29 | 9404 | keep | 0 | Dec | 2022 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2022-12-29 00:16 | 2022-12-29 08:25 | 30 | 8:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22122800227 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 489 | 2022-12-29 | 14670 | keep | 0 | Dec | 2022 | 0.0099917 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-12-29 00:22 | 2022-12-29 06:02 | 50 | 5:40 | P | DESGANCHE | SE RETIRO RAMA DE LINEA Y 1 X 30 EN C/L | R22122900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2022-12-29 | 17000 | keep | 0 | Dec | 2022 | 0.011579 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-12-29 00:26 | 2022-12-29 00:31 | 414 | 0:05 | P | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL 30% DE LA CARGA POR EL 1204-01 | S2212290000X | New_Event | Primary Wire Break | Include | Include | Equipment | 5 | 2022-12-29 | 2070 | keep | 0 | Dec | 2022 | 0.0014099 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
SAN JUAN | 2022-12-29 00:31 | 2022-12-29 03:13 | 138 | 2:42 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR EN EL SUELO 30% DE LA CARGA POR EL 1204-01 | S2212290000X | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 162 | 2022-12-29 | 22356 | keep | 0 | Dec | 2022 | 0.015227 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-12-29 01:05 | 2022-12-29 10:20 | 30 | 9:15 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | R22122900007 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 555 | 2022-12-29 | 16650 | keep | 0 | Dec | 2022 | 0.01134 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-12-29 02:11 | 2022-12-29 02:12 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22122900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 3332 | keep | 0 | Dec | 2022 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
ARECIBO | 2022-12-29 02:15 | 2022-12-29 11:50 | 10 | 9:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA Y SE REPARO LINEA SECUNDARIA | A22122900002 | New_Event | Cutout Failure | Include | Include | Equipment | 575 | 2022-12-29 | 5750 | keep | 0 | Dec | 2022 | 0.0039163 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-12-29 02:18 | 2022-12-29 16:21 | 72 | 14:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | S22122900010 | New_Event | Cutout Failure | Include | Include | Equipment | 843 | 2022-12-29 | 60696 | keep | 0 | Dec | 2022 | 0.04134 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
MAYAGÃœEZ | 2022-12-29 02:18 | 2022-12-29 02:19 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22122900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 3458 | keep | 0 | Dec | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
FAJARDO | 2022-12-29 02:31 | 2022-12-29 04:35 | 234 | 2:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | R22122900013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-12-29 | 29016 | keep | 0 | Dec | 2022 | 0.019763 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
SAN JUAN | 2022-12-29 02:44 | 2022-12-29 02:46 | 316 | 0:02 | T | PARARRAYOS DEFECTUOSO | DISPARO SE CERRO POR CONTROL LLEVANDO 25% DE LA CAGA DEL 1119-04 LLEVANDO 25% DE LA CARGA DEL 1119-02 | S22122900011 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2022-12-29 | 632 | keep | 0 | Dec | 2022 | 0.00043045 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
SAN JUAN | 2022-12-29 02:44 | 2022-12-29 02:46 | 215 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL 25% DE LA CAGA POR EL 1117-09 | S22122900011 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2022-12-29 | 430 | keep | 0 | Dec | 2022 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2022-12-29 02:44 | 2022-12-29 02:46 | 698 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL 25% DE LA CAGA POR EL 1117-09 | S22122900011 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2022-12-29 | 1396 | keep | 0 | Dec | 2022 | 0.00095081 | 0.0004754 | Momentary | FALSE | FALSE | Not_TMED_Event | 698
SAN JUAN | 2022-12-29 02:46 | 2022-12-29 16:45 | 176 | 13:59 | P | PARARRAYOS DEFECTUOSO | SE REPUSO 2 FUSIBLE DE 140 EN C/L SE REEMPAZO PARARRAYOS | S22122900012 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 839 | 2022-12-29 | 147664 | keep | 0 | Dec | 2022 | 0.10057 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
SAN JUAN | 2022-12-29 02:46 | 2022-12-29 11:36 | 176 | 8:50 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO Y SE REPUSO 2 FUSIBLE DE 140 EN C/L. | S22122900012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 530 | 2022-12-29 | 93280 | keep | 0 | Dec | 2022 | 0.063533 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
VEGA BAJA | 2022-12-29 02:46 | 2022-12-29 08:30 | 128 | 5:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22122900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2022-12-29 | 44032 | keep | 0 | Dec | 2022 | 0.02999 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
VEGA BAJA | 2022-12-29 02:47 | 2022-12-29 02:48 | 2468 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2212290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 2468 | keep | 0 | Dec | 2022 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
HUMACAO | 2022-12-29 03:06 | 2022-12-29 09:34 | 50 | 6:28 | P | DESGANCHE | 1 X 50 CL DESGANCHE | C22122900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 388 | 2022-12-29 | 19400 | keep | 0 | Dec | 2022 | 0.013213 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-12-29 03:10 | 2022-12-29 03:12 | 215 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL | B2212290000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-12-29 | 430 | keep | 0 | Dec | 2022 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-12-29 03:12 | 2022-12-29 09:43 | 100 | 6:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | B22122900007 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 391 | 2022-12-29 | 39100 | keep | 0 | Dec | 2022 | 0.026631 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-12-29 03:13 | 2022-12-29 03:17 | 414 | 0:04 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO 30% DE LA CARGA POR EL 1204-01 | S2212290000X | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2022-12-29 | 1656 | keep | 0 | Dec | 2022 | 0.0011279 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
VEGA BAJA | 2022-12-29 03:44 | 2022-12-29 10:30 | 10 | 6:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA FUERTE VIENTO | A22122900004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 406 | 2022-12-29 | 4060 | keep | 0 | Dec | 2022 | 0.0027652 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-12-29 04:45 | 2022-12-29 08:15 | 5630 | 3:30 | S | POWER TRANSFORMER AVERIADO | SUBESTACION SE FUE A LOCK OUT SE ENCONTRO RABIZA CRUZADA DE PRESSURE RELIEF SE TRANSFIRIO 70% DE LA CARGA AL 3205-07 SF CG-221229-01 | C22122900012 | New_Event | Power Transformer Failure | Include | Include | Equipment | 210 | 2022-12-29 | 1182300 | keep | 0 | Dec | 2022 | 0.80526 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-12-29 04:45 | 2022-12-29 08:22 | 2126 | 3:37 | S | POWER TRANSFORMER AVERIADO | SUBESTACION SE FUE A LOCK OUT SE ENCONTRO RABIZA CRUZADA DE PRESSURE RELIEF SE TRANSFIRIO 70% DE LA CARGA AL 2605-01 SF CG-221229-01 | C22122900012 | New_Event | Power Transformer Failure | Include | Include | Equipment | 217 | 2022-12-29 | 461342 | keep | 0 | Dec | 2022 | 0.31422 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-12-29 04:45 | 2022-12-29 08:51 | 551 | 4:06 | S | POWER TRANSFORMER AVERIADO | SUBESTACION SE FUE A LOCK OUT SE ENCONTRO RABIZA CRUZADA DE PRESSURE RELIEF SF CG-221229-01 | C22122900012 | New_Event | Power Transformer Failure | Include | Include | Equipment | 246 | 2022-12-29 | 135546 | keep | 0 | Dec | 2022 | 0.09232 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
SAN JUAN | 2022-12-29 05:41 | 2022-12-29 13:15 | 3 | 7:34 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MACHETE PARA LEVANTAR TRAMO RADIAL | S2212290002 | New_Event | Primary Wire Break | Include | Include | Equipment | 454 | 2022-12-29 | 1362 | keep | 0 | Dec | 2022 | 0.00092765 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2022-12-29 06:12 | 2022-12-29 11:00 | 30 | 4:48 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO ENCONTRO CAUSA | P22122900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2022-12-29 | 8640 | keep | 0 | Dec | 2022 | 0.0058847 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-12-29 07:52 | 2022-12-29 10:54 | 90 | 3:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO PIN POLE TOP 1 X 50 CL | C22122900023 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 182 | 2022-12-29 | 16380 | keep | 0 | Dec | 2022 | 0.011156 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-12-29 08:14 | 2022-12-29 09:10 | 35 | 0:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22122900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-12-29 | 1960 | keep | 0 | Dec | 2022 | 0.0013349 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2022-12-29 08:15 | 2022-12-29 08:51 | 1689 | 0:36 | P | POWER TRANSFORMER AVERIADO | SUBESTACION SE FUE A LOCK OUT SE ENCONTRO RABIZA CRUZADA DE PRESSURE RELIEF SE CORRIJIO AVERIA SE CERRO BKR SE NORMALIZARON LAS CARGAS 100% EN SERVICIO SF CG-221229-01 | C22122900012 | Partial_restoration | Power Transformer Failure | Include | Include | Equipment | 36 | 2022-12-29 | 60804 | keep | 0 | Dec | 2022 | 0.041413 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-12-29 08:15 | 2022-12-29 10:33 | 100 | 2:18 | P | ANIMAL | 1 X 65 Y 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M22122900009 | New_Event | Animals | Include | Include | Wildlife | 138 | 2022-12-29 | 13800 | keep | 0 | Dec | 2022 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-12-29 08:22 | 2022-12-29 08:51 | 637 | 0:29 | P | POWER TRANSFORMER AVERIADO | SUBESTACION SE FUE A LOCK OUT SE ENCONTRO RABIZA CRUZADA DE PRESSURE RELIEF 100% EN SERVICIO SF CG-221229-01 | C22122900012 | Partial_restoration | Power Transformer Failure | Include | Include | Equipment | 29 | 2022-12-29 | 18473 | keep | 0 | Dec | 2022 | 0.012582 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-12-29 08:29 | 2022-12-29 11:11 | 5 | 2:42 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22122900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2022-12-29 | 810 | keep | 0 | Dec | 2022 | 0.00055169 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-12-29 08:32 | 2022-12-29 10:20 | 40 | 1:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22122900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-12-29 | 4320 | keep | 0 | Dec | 2022 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-12-29 08:33 | 2022-12-29 08:55 | 12 | 0:22 | P | ANIMAL | 1 X 15 EN XMR RATON | A22122900016 | New_Event | Animals | Include | Include | Wildlife | 22 | 2022-12-29 | 264 | keep | 0 | Dec | 2022 | 0.00017981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-12-29 08:40 | 2022-12-29 11:15 | 578 | 2:35 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE LA CARGA | B22122900116 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 155 | 2022-12-29 | 89590 | keep | 0 | Dec | 2022 | 0.061019 | 0.00039367 | Sustained | FALSE | FALSE | Not_TMED_Event | 578
BAYAMON | 2022-12-29 08:40 | 2022-12-29 09:28 | 198 | 0:48 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | New_Event | Feeder Load Transferred | Include | Include | Other | 48 | 2022-12-29 | 9504 | keep | 0 | Dec | 2022 | 0.0064731 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-29 08:40 | 2022-12-29 09:28 | 1976 | 0:48 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | New_Event | Feeder Load Transferred | Include | Include | Other | 48 | 2022-12-29 | 94848 | keep | 0 | Dec | 2022 | 0.064601 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
AGUADILLA | 2022-12-29 08:53 | 2022-12-29 11:05 | 10 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER NO SE ENCONTRO CAUSA | A22122900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2022-12-29 | 1320 | keep | 0 | Dec | 2022 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-12-29 08:54 | 2022-12-29 08:55 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INERRUPTOR EN SERVICIO | S2212290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 45 | keep | 0 | Dec | 2022 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-12-29 09:06 | 2022-12-29 12:50 | 1 | 3:44 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA PAJARO CRUZO FASE | P22122900042 | New_Event | Animals | Include | Include | Wildlife | 224 | 2022-12-29 | 224 | keep | 0 | Dec | 2022 | 0.00015257 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-12-29 09:10 | 2022-12-29 10:00 | 6 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTES Y CONEXIONES SECUNDARIOS | A22122900008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-12-29 | 300 | keep | 0 | Dec | 2022 | 0.00020433 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-12-29 09:19 | 2022-12-29 15:20 | 12 | 6:01 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 37.5 KVA A 7620 VOLTS AVERIADO | P22122900048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 361 | 2022-12-29 | 4332 | keep | 0 | Dec | 2022 | 0.0029505 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-12-29 09:24 | 2022-12-29 09:25 | 1879 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22122900024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-29 | 1879 | keep | 0 | Dec | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
VEGA BAJA | 2022-12-29 09:24 | 2022-12-29 09:25 | 2777 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22122900024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-29 | 2777 | keep | 0 | Dec | 2022 | 0.0018914 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
VEGA BAJA | 2022-12-29 09:24 | 2022-12-29 09:25 | 2 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22122900024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-29 | 2 | keep | 0 | Dec | 2022 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-12-29 09:24 | 2022-12-29 09:25 | 2839 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22122900025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-29 | 2839 | keep | 0 | Dec | 2022 | 0.0019336 | 0.0019336 | Momentary | FALSE | FALSE | Not_TMED_Event | 2839
VEGA BAJA | 2022-12-29 09:24 | 2022-12-29 09:25 | 1160 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22122900025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-29 | 1160 | keep | 0 | Dec | 2022 | 0.00079007 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
VEGA BAJA | 2022-12-29 09:24 | 2022-12-29 09:25 | 1860 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22122900025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-29 | 1860 | keep | 0 | Dec | 2022 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
VEGA BAJA | 2022-12-29 09:25 | 2022-12-31 17:19 | 1 | 55:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN RISER | A22122100050 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 3354 | 2022-12-29 | 3354 | keep | 0 | Dec | 2022 | 0.0022844 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-12-29 09:26 | 2022-12-29 10:47 | 60 | 1:21 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | C22122900066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-12-29 | 4860 | keep | 0 | Dec | 2022 | 0.0033101 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-12-29 09:37 | 2022-12-29 12:03 | 20 | 2:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN CL | C22122900070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-12-29 | 2920 | keep | 0 | Dec | 2022 | 0.0019888 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-12-29 09:40 | 2022-12-29 11:04 | 10 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPAR LINEA SECUNDARIA | S22122900046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2022-12-29 | 840 | keep | 0 | Dec | 2022 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-12-29 09:47 | 2022-12-29 16:40 | 50 | 6:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REEMPLAZO SECUNDARIA | C22122900073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 413 | 2022-12-29 | 20650 | keep | 0 | Dec | 2022 | 0.014065 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-12-29 09:59 | 2022-12-29 13:27 | 10 | 3:28 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | B22122900110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-12-29 | 2080 | keep | 0 | Dec | 2022 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-12-29 10:06 | 2022-12-29 12:00 | 30 | 1:54 | P | ANIMAL | 1 X 65 EN RISER AVE CRUZO FASE | P22122900064 | New_Event | Animals | Include | Include | Wildlife | 114 | 2022-12-29 | 3420 | keep | 0 | Dec | 2022 | 0.0023293 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-12-29 10:10 | 2022-12-29 11:50 | 10 | 1:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMAFOR PARA REPARAR LINEA SECUNDARIA | P22122800064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2022-12-29 | 1000 | keep | 0 | Dec | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-12-29 10:15 | 2022-12-29 14:40 | 21 | 4:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22122900058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 265 | 2022-12-29 | 5565 | keep | 0 | Dec | 2022 | 0.0037903 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-12-29 10:35 | 2022-12-29 17:15 | 4 | 6:40 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | ABRIR XMR PARA REMPLAZO POSTE SECUNDARIO Y SE RELOCALIZO SECUNDARIA | B22122900126 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 400 | 2022-12-29 | 1600 | keep | 0 | Dec | 2022 | 0.0010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-12-29 10:40 | 2022-12-29 13:00 | 70 | 2:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22122900031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-12-29 | 9800 | keep | 0 | Dec | 2022 | 0.0066747 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-12-29 10:41 | 2022-12-29 10:43 | 1488 | 0:02 | P | POWER TRANSFORMER AVERIADO | SF CG-221229-01 SE ABRIO BKR PARA NORMALIZAR 70% DE LA CARGA DEL 2603-09 QUE ESTABA A TRAVEZ DEL 2605-01 DEBIDO QUE NO FASEABA | C22122900012 | New_Event | Power Transformer Failure | Include | Include | Equipment | 2 | 2022-12-29 | 2976 | keep | 0 | Dec | 2022 | 0.0020269 | 0.0010135 | Momentary | FALSE | FALSE | Not_TMED_Event | 1488
SAN JUAN | 2022-12-29 10:45 | 2022-12-29 11:31 | 6 | 0:46 | P | NO SE REPORTO CAUSA | 2 X 20 EN XMR | S22122800082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 46 | 2022-12-29 | 276 | keep | 0 | Dec | 2022 | 0.00018798 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-12-29 10:55 | 2022-12-29 10:56 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 198 | keep | 0 | Dec | 2022 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-29 10:55 | 2022-12-29 10:56 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 1976 | keep | 0 | Dec | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
HUMACAO | 2022-12-29 10:56 | 2022-12-29 14:07 | 40 | 3:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L Y SE REEMPLAZO PORTAFUSIBLE | C22122900091 | New_Event | Cutout Failure | Include | Include | Equipment | 191 | 2022-12-29 | 7640 | keep | 0 | Dec | 2022 | 0.0052036 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-12-29 11:00 | 2022-12-29 11:35 | 12 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | B22122900135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-12-29 | 420 | keep | 0 | Dec | 2022 | 0.00028606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-12-29 11:15 | 2022-12-29 13:09 | 144 | 1:54 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 20% DE SU CARGA | B22122900116 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 114 | 2022-12-29 | 16416 | keep | 0 | Dec | 2022 | 0.011181 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
BARRANQUITAS | 2022-12-29 11:16 | 2022-12-29 13:57 | 51 | 2:41 | P | DESGANCHE | 1 X 80 EN CL | C22122900097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-12-29 | 8211 | keep | 0 | Dec | 2022 | 0.0055925 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
VEGA BAJA | 2022-12-29 11:27 | 2022-12-29 14:01 | 25 | 2:34 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B22122900147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-12-29 | 3850 | keep | 0 | Dec | 2022 | 0.0026222 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-12-29 11:36 | 2022-12-29 11:39 | 2720 | 0:03 | T | PARARRAYOS DEFECTUOSO | SE VERIFICO CON PERSONAL ORDEN 6000 Y ESA DISPARO DE BKR CARGA 1117-9 ESTA POR 1119-04 QUE A SU VEZ ESTA POR 1115-1, SE VERIFICO CON LUIS LOPEZ Y SE PROCEDIO A CERRAR INTERRUPTOR QUEDO EN SERVICIO | S2212290000X | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 3 | 2022-12-29 | 8160 | keep | 0 | Dec | 2022 | 0.0055577 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2022-12-29 11:39 | 2022-12-29 16:45 | 176 | 5:06 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO Y SE REPUSO 2 FUSIBLE DE 140 EN C/L. | S22122900012 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 306 | 2022-12-29 | 53856 | keep | 0 | Dec | 2022 | 0.036681 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
AGUADILLA | 2022-12-29 12:19 | 2022-12-29 15:26 | 8 | 3:07 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN TRANSFORMADOR SE RETIRO SECUNDARIA POR TUBO DE CONDULETO AVERIADO | M22122900038 | New_Event | Customer-Related Interruption | Include | Include | Public | 187 | 2022-12-29 | 1496 | keep | 0 | Dec | 2022 | 0.0010189 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-12-29 12:37 | 2022-12-29 13:30 | 3 | 0:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO CONECTORES DE BAJANTE DE XMR | S22122900073 | New_Event | Primary Wire Break | Include | Include | Equipment | 53 | 2022-12-29 | 159 | keep | 0 | Dec | 2022 | 0.00010829 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-12-29 12:38 | 2022-12-29 17:36 | 7 | 4:58 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | A22122900052 | New_Event | Primary Wire Break | Include | Include | Equipment | 298 | 2022-12-29 | 2086 | keep | 0 | Dec | 2022 | 0.0014208 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-12-29 12:39 | 2022-12-29 14:51 | 8 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22122900053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2022-12-29 | 1056 | keep | 0 | Dec | 2022 | 0.00071924 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-12-29 12:40 | 2022-12-29 15:05 | 10 | 2:25 | P | SECUNDARIA/DESGANCHE | SE ABRE MONTURA DE TRANSFORMADOR Y SE REALIZA DESGANCHE Y REPARA SECUNDARIA | M22122800196 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 145 | 2022-12-29 | 1450 | keep | 0 | Dec | 2022 | 0.00098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-12-29 12:50 | 2022-12-29 15:30 | 50 | 2:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A22122900054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-12-29 | 8000 | keep | 0 | Dec | 2022 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-12-29 12:51 | 2022-12-29 12:52 | 1271 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2212290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 1271 | keep | 0 | Dec | 2022 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
HUMACAO | 2022-12-29 12:56 | 2022-12-29 12:59 | 3420 | 0:03 | T | NO SE REPORTO CAUSA | RECIERRE | C2212290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-12-29 | 10260 | keep | 0 | Dec | 2022 | 0.006988 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
BAYAMON | 2022-12-29 13:09 | 2022-12-29 13:11 | 578 | 0:02 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE SU CARGA | B22122900116 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 2 | 2022-12-29 | 1156 | keep | 0 | Dec | 2022 | 0.00078735 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-29 13:09 | 2022-12-29 13:11 | 198 | 0:02 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2022-12-29 | 396 | keep | 0 | Dec | 2022 | 0.00026971 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-29 13:09 | 2022-12-29 13:11 | 1976 | 0:02 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2022-12-29 | 3952 | keep | 0 | Dec | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
HUMACAO | 2022-12-29 13:09 | 2022-12-29 15:05 | 1 | 1:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REEMPLAZO DE CAJA PRIMARIA | C22122900160 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2022-12-29 | 116 | keep | 0 | Dec | 2022 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-12-29 13:11 | 2022-12-29 14:58 | 144 | 1:47 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 20% DE SU CARGA | B22122900116 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 107 | 2022-12-29 | 15408 | keep | 0 | Dec | 2022 | 0.010494 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
SAN JUAN | 2022-12-29 13:15 | 2022-12-29 13:55 | 20 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MACHETE PARA LEVANTAR TRAMO RADIAL | S2212290002 | New_Event | Primary Wire Break | Include | Include | Equipment | 40 | 2022-12-29 | 800 | keep | 0 | Dec | 2022 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-12-29 13:33 | 2022-12-29 15:02 | 34 | 1:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO C/L Y SE REEMPLAZO CAJA PRIMARIA Y PORTA FUSIBLE | C22122900144 | New_Event | Cutout Failure | Include | Include | Equipment | 89 | 2022-12-29 | 3026 | keep | 0 | Dec | 2022 | 0.002061 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2022-12-29 13:40 | 2022-12-29 15:29 | 100 | 1:49 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y SE CERRO N/O CONTRA EL 1305-01 | S2212270000X | New_Event | Primary Wire Break | Include | Include | Equipment | 109 | 2022-12-29 | 10900 | keep | 0 | Dec | 2022 | 0.0074239 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-12-29 13:45 | 2022-12-29 17:17 | 10 | 3:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD RELACIONADO WR6288788 | A22122900058 | New_Event | Service Transformer Failure | Include | Include | Equipment | 212 | 2022-12-29 | 2120 | keep | 0 | Dec | 2022 | 0.0014439 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-12-29 13:49 | 2022-12-29 14:43 | 10 | 0:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A22122900035 | New_Event | Primary Wire Break | Include | Include | Equipment | 54 | 2022-12-29 | 540 | keep | 0 | Dec | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-12-29 13:55 | 2022-12-29 14:13 | 1 | 0:18 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C22122900135 | New_Event | Animals | Include | Include | Wildlife | 18 | 2022-12-29 | 18 | keep | 0 | Dec | 2022 | 1.226e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-12-29 14:00 | 2022-12-29 15:15 | 10 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPAPAR LINEAS SECUNDARIAS | M22122900040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2022-12-29 | 750 | keep | 0 | Dec | 2022 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-12-29 14:01 | 2022-12-29 17:02 | 100 | 3:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | M22122900055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-12-29 | 18100 | keep | 0 | Dec | 2022 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-12-29 14:05 | 2022-12-29 14:07 | 30 | 0:02 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22122900153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-12-29 | 60 | keep | 0 | Dec | 2022 | 4.0866e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-12-29 14:09 | 2022-12-29 15:17 | 50 | 1:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A22122900062 | New_Event | Primary Wire Break | Include | Include | Equipment | 68 | 2022-12-29 | 3400 | keep | 0 | Dec | 2022 | 0.0023157 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-12-29 14:14 | 2022-12-29 14:27 | 1 | 0:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R22122900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-12-29 | 13 | keep | 0 | Dec | 2022 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-12-29 14:22 | 2022-12-29 16:15 | 5 | 1:53 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR IGUANA | M22122900064 | New_Event | Animals | Include | Include | Wildlife | 113 | 2022-12-29 | 565 | keep | 0 | Dec | 2022 | 0.00038482 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-12-29 14:33 | 2022-12-29 18:39 | 80 | 4:06 | P | NO SE REPORTO CAUSA | 3 X 65 EN C/L | B22122900172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2022-12-29 | 19680 | keep | 0 | Dec | 2022 | 0.013404 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-12-29 14:40 | 2022-12-29 14:44 | 164 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA QUEDO EN SERVICIO | S2212290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-12-29 | 656 | keep | 0 | Dec | 2022 | 0.0004468 | 0.0001117 | Momentary | FALSE | FALSE | Not_TMED_Event | 164
CANOVANAS | 2022-12-29 14:44 | 2022-12-29 15:36 | 1 | 0:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R22122900049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-12-29 | 52 | keep | 0 | Dec | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-12-29 14:45 | 2022-12-29 16:46 | 84 | 2:01 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22122900166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-12-29 | 10164 | keep | 0 | Dec | 2022 | 0.0069227 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
SAN JUAN | 2022-12-29 14:50 | 2022-12-29 18:20 | 349 | 3:30 | P | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEA SE CERRO PB QUEDO EN SERVICIO | S22122900140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-12-29 | 73290 | keep | 0 | Dec | 2022 | 0.049917 | 0.0002377 | Sustained | FALSE | FALSE | Not_TMED_Event | 349
FAJARDO | 2022-12-29 14:52 | 2022-12-29 16:25 | 12 | 1:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN AEREO PROVISIONAL Y SE REPARO BAJANTE LINEA A CAJA | R22122900052 | New_Event | Primary Wire Break | Include | Include | Equipment | 93 | 2022-12-29 | 1116 | keep | 0 | Dec | 2022 | 0.0007601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-12-29 14:58 | 2022-12-29 14:59 | 578 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE SU CARGA | B22122900116 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 1 | 2022-12-29 | 578 | keep | 0 | Dec | 2022 | 0.00039367 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-29 14:58 | 2022-12-29 14:59 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 10% DE SU CARGA, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 198 | keep | 0 | Dec | 2022 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-29 14:58 | 2022-12-29 14:59 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 1976 | keep | 0 | Dec | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-12-29 14:59 | 2022-12-29 15:07 | 144 | 0:08 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 20% DE SU CARGA | B22122900116 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 8 | 2022-12-29 | 1152 | keep | 0 | Dec | 2022 | 0.00078462 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
SAN JUAN | 2022-12-29 15:02 | 2022-12-29 17:37 | 164 | 2:35 | T | DESGANCHE | DISPARO SE PATRULLO SE ENCONTRO RAMA CRUZANDO SPACER CON VARETA DE PISO Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S22122900149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-12-29 | 25420 | keep | 0 | Dec | 2022 | 0.017313 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2022-12-29 15:07 | 2022-12-29 15:08 | 578 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE LA CARGA | B22122900116 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 1 | 2022-12-29 | 578 | keep | 0 | Dec | 2022 | 0.00039367 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-29 15:07 | 2022-12-29 15:08 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 10% DE SU CARGA, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 198 | keep | 0 | Dec | 2022 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-29 15:07 | 2022-12-29 15:08 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 1976 | keep | 0 | Dec | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-12-29 15:08 | 2022-12-29 16:06 | 144 | 0:58 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 20% DE SU CARGA | B22122900116 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 58 | 2022-12-29 | 8352 | keep | 0 | Dec | 2022 | 0.0056885 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
PONCE | 2022-12-29 15:09 | 2022-12-29 15:10 | 860 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22122900096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 860 | keep | 0 | Dec | 2022 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
HUMACAO | 2022-12-29 15:11 | 2022-12-29 17:30 | 15 | 2:19 | P | DESGANCHE | 1 X 30 Y 1 X 50 EN C/L DESGANJCHE | C22122900169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-12-29 | 2085 | keep | 0 | Dec | 2022 | 0.0014201 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-12-29 15:14 | 2022-12-29 15:45 | 1 | 0:31 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR POR AVERIA DE LINEA PRIMARIA PARTIDA | M22122900067 | New_Event | Primary Wire Break | Include | Include | Equipment | 31 | 2022-12-29 | 31 | keep | 0 | Dec | 2022 | 2.1114e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-12-29 15:15 | 2022-12-29 16:15 | 1 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA TRIFASICA PARA REPARAR LINEA SECUNDARIA | P22122900095 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-12-29 | 60 | keep | 0 | Dec | 2022 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-12-29 15:27 | 2022-12-29 15:28 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S2212290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 2466 | keep | 0 | Dec | 2022 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
SAN JUAN | 2022-12-29 15:30 | 2022-12-30 05:23 | 545 | 13:53 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S22122900135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 833 | 2022-12-29 | 453985 | keep | 0 | Dec | 2022 | 0.30921 | 0.0003712 | Sustained | FALSE | FALSE | Not_TMED_Event | 545
CAGUAS | 2022-12-29 15:49 | 2022-12-29 17:50 | 136 | 2:01 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C22122900175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-12-29 | 16456 | keep | 0 | Dec | 2022 | 0.011208 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
BARRANQUITAS | 2022-12-29 15:52 | 2022-12-29 15:53 | 214 | 0:01 | P | CAUSAS EXTERNAS | CG-221229-04 SE REEMPLAZO POSTE PRIMARIO IMPACTADO POR CAMION DE LA TELEFONICA | C22122900149 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-12-29 | 214 | keep | 0 | Dec | 2022 | 0.00014575 | 0.00014575 | Momentary | FALSE | FALSE | Not_TMED_Event | 214
AGUADILLA | 2022-12-29 15:59 | 2022-12-29 17:30 | 50 | 1:31 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | M22122900080 | New_Event | Primary Wire Break | Include | Include | Equipment | 91 | 2022-12-29 | 4550 | keep | 0 | Dec | 2022 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-12-29 16:01 | 2022-12-29 20:42 | 65 | 4:41 | P | CONDUCTOR ROTO O ABIERTO | SE HIZO DESGANCHE MASIVO Y SE LEVANTO CONDUCTOR PRIMARIO. EN SERVICIO | S22122900162 | New_Event | Primary Wire Break | Include | Include | Equipment | 281 | 2022-12-29 | 18265 | keep | 0 | Dec | 2022 | 0.01244 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2022-12-29 16:03 | 2022-12-29 17:50 | 75 | 1:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22122900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-12-29 | 8025 | keep | 0 | Dec | 2022 | 0.0054658 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-12-29 16:06 | 2022-12-29 16:07 | 578 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE SU CARGA | B22122900116 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 1 | 2022-12-29 | 578 | keep | 0 | Dec | 2022 | 0.00039367 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-29 16:06 | 2022-12-29 16:07 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 10% DE SU CARGA, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 198 | keep | 0 | Dec | 2022 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-29 16:06 | 2022-12-29 16:07 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 1976 | keep | 0 | Dec | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-12-29 16:07 | 2022-12-29 16:09 | 144 | 0:02 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 20% DE SU CARGA | B22122900116 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 2 | 2022-12-29 | 288 | keep | 0 | Dec | 2022 | 0.00019616 | 9.8078e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 144
CAGUAS | 2022-12-29 16:14 | 2022-12-29 18:16 | 190 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L MAL TIEMPO VIENTOS | C22122900182 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2022-12-29 | 23180 | keep | 0 | Dec | 2022 | 0.015788 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
BAYAMON | 2022-12-29 16:29 | 2022-12-30 01:12 | 7 | 8:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA | B22122900202 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 523 | 2022-12-29 | 3661 | keep | 0 | Dec | 2022 | 0.0024935 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-12-29 16:30 | 2022-12-30 09:52 | 40 | 17:22 | P | NO SE REPORTO CAUSA | 1X 65 EN C/L | S22122900189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1042 | 2022-12-29 | 41680 | keep | 0 | Dec | 2022 | 0.028388 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-12-29 16:56 | 2022-12-30 10:44 | 2 | 17:48 | P | DESGANCHE | DESGANCHE 1 X 40 EN PROVISIONAL 1 X 30 EN RISER @ XMR | B22122900211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1068 | 2022-12-29 | 2136 | keep | 0 | Dec | 2022 | 0.0014548 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-12-29 17:05 | 2022-12-29 19:30 | 195 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22122900213 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-12-29 | 28275 | keep | 0 | Dec | 2022 | 0.019258 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
BAYAMON | 2022-12-29 17:09 | 2022-12-29 17:10 | 578 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE SU CARGA | B22122900116 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1 | 2022-12-29 | 578 | keep | 0 | Dec | 2022 | 0.00039367 | 0.00039367 | Momentary | FALSE | FALSE | Not_TMED_Event | 578
BAYAMON | 2022-12-29 17:09 | 2022-12-29 17:10 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 10% DE SU CARGA, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 198 | keep | 0 | Dec | 2022 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-29 17:09 | 2022-12-29 17:10 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 1976 | keep | 0 | Dec | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-12-29 17:10 | 2022-12-29 18:33 | 144 | 1:23 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 20% DE SU CARGA | B22122900116 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 83 | 2022-12-29 | 11952 | keep | 0 | Dec | 2022 | 0.0081405 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
CANOVANAS | 2022-12-29 17:22 | 2022-12-29 19:17 | 2 | 1:55 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R22122900064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-12-29 | 230 | keep | 0 | Dec | 2022 | 0.00015665 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-12-29 17:27 | 2022-12-29 21:03 | 573 | 3:36 | P | ANIMAL | 1 X 140 EN EN EL RISER PRINCIPAL Y 1 X 80 EN EL OTRO RISER CRUCE POR IGUANA | B22122900229 | New_Event | Animals | Include | Include | Wildlife | 216 | 2022-12-29 | 123768 | keep | 0 | Dec | 2022 | 0.084298 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
YAUCO | 2022-12-29 17:37 | 2022-12-29 19:31 | 25 | 1:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR VIENTOS | P22122900104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 114 | 2022-12-29 | 2850 | keep | 0 | Dec | 2022 | 0.0019411 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-12-29 17:42 | 2022-12-29 19:10 | 50 | 1:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | M22122900091 | New_Event | Primary Wire Break | Include | Include | Equipment | 88 | 2022-12-29 | 4400 | keep | 0 | Dec | 2022 | 0.0029968 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-12-29 17:42 | 2022-12-29 23:07 | 50 | 5:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BEJUCO | B22122900231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2022-12-29 | 16250 | keep | 0 | Dec | 2022 | 0.011068 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-12-29 17:54 | 2022-12-30 10:30 | 2 | 16:36 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CAJA TRANSFORMADOR | A22122900085 | New_Event | Primary Wire Break | Include | Include | Equipment | 996 | 2022-12-29 | 1992 | keep | 0 | Dec | 2022 | 0.0013567 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-12-29 18:14 | 2022-12-29 19:40 | 130 | 1:26 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN C/LS DESGANCHE | C22122900212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-12-29 | 11180 | keep | 0 | Dec | 2022 | 0.0076146 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
YAUCO | 2022-12-29 18:14 | 2022-12-29 20:37 | 100 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR VIENTOS | M22122900097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2022-12-29 | 14300 | keep | 0 | Dec | 2022 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-12-29 18:18 | 2022-12-30 04:38 | 115 | 10:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA Y 1 X 10 EN PROVISIONAL AEREO MAL TIEMPO | B22122900241 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 620 | 2022-12-29 | 71300 | keep | 0 | Dec | 2022 | 0.048562 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
BAYAMON | 2022-12-29 18:28 | 2022-12-30 08:55 | 10 | 14:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22122900247 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 867 | 2022-12-29 | 8670 | keep | 0 | Dec | 2022 | 0.0059051 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-12-29 18:33 | 2022-12-29 18:34 | 578 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE SU CARGA | B22122900116 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 1 | 2022-12-29 | 578 | keep | 0 | Dec | 2022 | 0.00039367 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-29 18:33 | 2022-12-29 18:34 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 10% DE SU CARGA, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 198 | keep | 0 | Dec | 2022 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-29 18:33 | 2022-12-29 18:34 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 1976 | keep | 0 | Dec | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-12-29 18:34 | 2022-12-29 19:32 | 144 | 0:58 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 20% DE SU CARGA | B22122900116 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 58 | 2022-12-29 | 8352 | keep | 0 | Dec | 2022 | 0.0056885 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
AGUADILLA | 2022-12-29 18:37 | 2022-12-29 21:50 | 15 | 3:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22122900103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 193 | 2022-12-29 | 2895 | keep | 0 | Dec | 2022 | 0.0019718 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-12-29 18:41 | 2022-12-29 22:13 | 20 | 3:32 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22122900105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-12-29 | 4240 | keep | 0 | Dec | 2022 | 0.0028878 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-12-29 18:52 | 2022-12-30 00:35 | 125 | 5:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | S22122900266 | New_Event | Cutout Failure | Include | Include | Equipment | 343 | 2022-12-29 | 42875 | keep | 0 | Dec | 2022 | 0.029202 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
AGUADILLA | 2022-12-29 19:20 | 2022-12-29 20:20 | 10 | 1:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75KVA POR LA MISMA CAPACIDAD | A22122900092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 60 | 2022-12-29 | 600 | keep | 0 | Dec | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-12-29 19:21 | 2022-12-29 21:29 | 10 | 2:08 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A22122900093 | New_Event | Animals | Include | Include | Wildlife | 128 | 2022-12-29 | 1280 | keep | 0 | Dec | 2022 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-12-29 19:23 | 2022-12-29 19:25 | 3709 | 0:02 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR EN SERVICIO | S2212290000X | New_Event | Primary To Primary Contact | Include | Include | Equipment | 2 | 2022-12-29 | 7418 | keep | 0 | Dec | 2022 | 0.0050524 | 0.0025262 | Momentary | FALSE | FALSE | Not_TMED_Event | 3709
BAYAMON | 2022-12-29 19:32 | 2022-12-29 19:37 | 578 | 0:05 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE SU CARGA | B22122900116 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 5 | 2022-12-29 | 2890 | keep | 0 | Dec | 2022 | 0.0019684 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-29 19:32 | 2022-12-29 19:37 | 198 | 0:05 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 10% DE SU CARGA, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 5 | 2022-12-29 | 990 | keep | 0 | Dec | 2022 | 0.00067428 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-29 19:32 | 2022-12-29 19:37 | 1976 | 0:05 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 5 | 2022-12-29 | 9880 | keep | 0 | Dec | 2022 | 0.0067292 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-12-29 19:37 | 2022-12-29 19:57 | 144 | 0:20 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE SU CARGA | B22122900116 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 20 | 2022-12-29 | 2880 | keep | 0 | Dec | 2022 | 0.0019616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-12-29 19:43 | 2022-12-29 19:44 | 125 | 0:01 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | R22122900071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-12-29 | 125 | keep | 0 | Dec | 2022 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-12-29 19:53 | 2022-12-29 22:49 | 97 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN AEREO PROVISIONAL MAL TIEMPO LLUVIA | B22122900271 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2022-12-29 | 17072 | keep | 0 | Dec | 2022 | 0.011628 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
AGUADILLA | 2022-12-29 19:54 | 2022-12-30 09:35 | 6 | 13:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REALIZO DESGANCHE SE REPARO BAJANTE PRIMARIO ABIERTO Y SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M22122900114 | New_Event | Cutout Failure | Include | Include | Equipment | 821 | 2022-12-29 | 4926 | keep | 0 | Dec | 2022 | 0.0033551 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-12-29 19:57 | 2022-12-29 19:59 | 578 | 0:02 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 80% DE SU CARGA | B22122900116 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 2 | 2022-12-29 | 1156 | keep | 0 | Dec | 2022 | 0.00078735 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-29 19:57 | 2022-12-29 19:59 | 198 | 0:02 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR 10% DE SU CARGA, AVERIA DEL 1711-02 | B22122900116 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2022-12-29 | 396 | keep | 0 | Dec | 2022 | 0.00026971 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-29 19:57 | 2022-12-29 19:59 | 1976 | 0:02 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR, AVERIA DEL 1711-02 | B22122900116 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2022-12-29 | 3952 | keep | 0 | Dec | 2022 | 0.0026917 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-29 19:59 | 2022-12-29 21:03 | 144 | 1:04 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR ENTRO 10% ADICIONAL PARA UN 90% EN SERVICIO | B22122900116 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 64 | 2022-12-29 | 9216 | keep | 0 | Dec | 2022 | 0.006277 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
CAGUAS | 2022-12-29 20:13 | 2022-12-30 16:10 | 300 | 19:57 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO EN RISER | C22122900222 | New_Event | UG Cable Fault | Include | Include | Equipment | 1197 | 2022-12-29 | 359100 | keep | 0 | Dec | 2022 | 0.24458 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
YAUCO | 2022-12-29 20:14 | 2022-12-29 21:44 | 200 | 1:30 | P | SOBRECARGA | 1 X 140 EN CORTE DE LINEA POR CARGA NO HAY ESTUDIO DE CARGA | M22122900128 | New_Event | Trip Due To Overload | Include | Include | Other | 90 | 2022-12-29 | 18000 | keep | 0 | Dec | 2022 | 0.01226 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-12-29 20:27 | 2022-12-29 20:28 | 414 | 0:01 | P | DESGANCHE | DISPARO DEL 1204-01 QUE LLEVA 30% 1204-03 EN SERVICIO | S221229000OX | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-12-29 | 414 | keep | 0 | Dec | 2022 | 0.00028197 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
SAN JUAN | 2022-12-29 20:28 | 2022-12-30 02:55 | 125 | 6:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S22122900356 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 387 | 2022-12-29 | 48375 | keep | 0 | Dec | 2022 | 0.032948 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-12-29 20:50 | 2022-12-29 20:51 | 1725 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C22122900228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 1725 | keep | 0 | Dec | 2022 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
AGUADILLA | 2022-12-29 20:53 | 2022-12-29 22:00 | 100 | 1:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M22122900142 | New_Event | Cutout Failure | Include | Include | Equipment | 67 | 2022-12-29 | 6700 | keep | 0 | Dec | 2022 | 0.0045633 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-12-29 21:03 | 2022-12-29 21:35 | 72 | 0:32 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR CONDUCTOR CRUZADO POR TENSOR ENTRO 10% ADICIONAL PARA UN 100% EN SERVICIO | B22122900116 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 32 | 2022-12-29 | 2304 | keep | 0 | Dec | 2022 | 0.0015692 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-12-29 21:17 | 2022-12-29 23:33 | 60 | 2:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22122900230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-12-29 | 8160 | keep | 0 | Dec | 2022 | 0.0055577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-12-29 21:28 | 2022-12-29 21:29 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE 1206-03 LLEVA 85% 1204-05 EN SERVICIO | S2212290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-29 | 8679 | keep | 0 | Dec | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-12-29 21:28 | 2022-12-29 21:29 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1206-03 LLEVA 85% 1204-05 EN SERVICIO | S2212290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 4133 | keep | 0 | Dec | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
ARECIBO | 2022-12-29 21:45 | 2022-12-30 11:38 | 8 | 13:53 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN CL PARARRAYO CRUZADO | A22122900101 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 833 | 2022-12-29 | 6664 | keep | 0 | Dec | 2022 | 0.0045388 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-12-29 22:16 | 2022-12-29 22:45 | 3709 | 0:29 | T | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO INTERRUPTOR POR EMERGENCIA, NEUTRAL ENREDADO EN RISER DEL 4 KV SE RETIRO NEUTRAL CON VARETA | S2212290000X | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 29 | 2022-12-29 | 107561 | keep | 0 | Dec | 2022 | 0.073259 | 0.0025262 | Sustained | FALSE | FALSE | Not_TMED_Event | 3709
SAN JUAN | 2022-12-29 22:16 | 2022-12-29 22:30 | 620 | 0:14 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR A PETICION DEL FORMAN POR EMERGENCIA, DE NEUTRAL CRUZADO EN RISER, SIN EMBARGO LLAMO PARA DARLE PARA ATRAS PORQUE NO ERA EL ALIMENTADOR. CARGA POR EL 1133-02 | S2212290000X | New_Event | Human Error | Include | Include | Other | 14 | 2022-12-29 | 8680 | keep | 0 | Dec | 2022 | 0.0059119 | 0.00042228 | Sustained | FALSE | FALSE | Not_TMED_Event | 620
SAN JUAN | 2022-12-29 22:16 | 2022-12-29 22:30 | 451 | 0:14 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR A PETICION DEL FORMAN POR EMERGENCIA, DE NEUTRAL CRUZADO EN RISER, SIN EMBARGO LLAMO PARA DARLE PARA ATRAS PORQUE NO ERA EL ALIMENTADOR. LLEVA 35% DEL 1104-03 Y 100% 1133-01 | S2212290000X | New_Event | Human Error | Include | Include | Other | 14 | 2022-12-29 | 6314 | keep | 0 | Dec | 2022 | 0.0043004 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
MAYAGÃœEZ | 2022-12-29 22:47 | 2022-12-30 11:01 | 40 | 12:14 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO FASE A TIERRA | M22122900156 | New_Event | Animals | Include | Include | Wildlife | 734 | 2022-12-29 | 29360 | keep | 0 | Dec | 2022 | 0.019997 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-12-29 23:22 | 2022-12-29 23:23 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22122900157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-29 | 108 | keep | 0 | Dec | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
ARECIBO | 2022-12-29 23:56 | 2022-12-30 08:56 | 50 | 9:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CL FUERTES VIENTOS | A22122900106 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 540 | 2022-12-29 | 27000 | keep | 0 | Dec | 2022 | 0.01839 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-12-30 00:13 | 2022-12-30 00:14 | 4882 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | M22123000001 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-12-30 | 4882 | keep | 0 | Dec | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2022-12-30 00:14 | 2022-12-30 01:38 | 100 | 1:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO MASETILLA QUEMADA | M22123000005 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 84 | 2022-12-30 | 8400 | keep | 0 | Dec | 2022 | 0.0057212 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-12-30 00:56 | 2022-12-30 06:03 | 10 | 5:07 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22123000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2022-12-30 | 3070 | keep | 0 | Dec | 2022 | 0.002091 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-12-30 01:01 | 2022-12-30 01:02 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22123000022 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 108 | keep | 0 | Dec | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
AGUADILLA | 2022-12-30 01:02 | 2022-12-30 09:12 | 80 | 8:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL FUERTES VIENTOS | A22123000002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 490 | 2022-12-30 | 39200 | keep | 0 | Dec | 2022 | 0.026699 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-12-30 01:11 | 2022-12-30 12:24 | 40 | 11:13 | P | DESGANCHE | DESGANGHE 1 X 50 EN CORTE DE LINEA | S22123000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 673 | 2022-12-30 | 26920 | keep | 0 | Dec | 2022 | 0.018335 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-12-30 01:24 | 2022-12-30 01:26 | 215 | 0:02 | T | DESGANCHE | DISPARO INTERRUPTOR CERRADO POR CONTROL | B2212300000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-12-30 | 430 | keep | 0 | Dec | 2022 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
ARECIBO | 2022-12-30 01:25 | 2022-12-30 01:26 | 1227 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR CAJA PORTAFUSIBLE AVERIADO | A22123000004 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-12-30 | 1227 | keep | 0 | Dec | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-12-30 01:26 | 2022-12-30 08:59 | 60 | 7:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CL SE REMPLAZO PORTA FUSIBLE | A22123000014 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 453 | 2022-12-30 | 27180 | keep | 0 | Dec | 2022 | 0.018512 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-12-30 01:26 | 2022-12-30 07:13 | 60 | 5:47 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | B22123000003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 347 | 2022-12-30 | 20820 | keep | 0 | Dec | 2022 | 0.01418 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-12-30 01:28 | 2022-12-30 01:29 | 853 | 0:01 | T | ANIMAL | RECIERRE | C2212300000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-12-30 | 853 | keep | 0 | Dec | 2022 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
BAYAMON | 2022-12-30 01:28 | 2022-12-30 01:29 | 320 | 0:01 | T | DESGANCHE | DISPARO INTERRUPTOR CERRADO POR CONTROL | B2212300000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-12-30 | 320 | keep | 0 | Dec | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
CAGUAS | 2022-12-30 01:29 | 2022-12-30 08:07 | 22 | 6:38 | P | ANIMAL | 1 X 30 EN RISER CRUCE POR IGUANA | C22123000005 | 1st_after_momentary | Animals | Include | Include | Wildlife | 398 | 2022-12-30 | 8756 | keep | 0 | Dec | 2022 | 0.0059637 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2022-12-30 01:29 | 2022-12-30 11:00 | 60 | 9:31 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22123000005 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 571 | 2022-12-30 | 34260 | keep | 0 | Dec | 2022 | 0.023334 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-12-30 02:20 | 2022-12-30 07:50 | 50 | 5:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CL FUERTES VIENTOS | A22123000009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 330 | 2022-12-30 | 16500 | keep | 0 | Dec | 2022 | 0.011238 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-12-30 03:16 | 2022-12-30 11:14 | 72 | 7:58 | P | TERMINACION SOTERRADA AVERIADA | 1 X 65 EN RISER A T-18 SE QUEDO FUERA T-21 T-22 A T-27 | S22123000014 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 478 | 2022-12-30 | 34416 | keep | 0 | Dec | 2022 | 0.023441 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2022-12-30 04:21 | 2022-12-30 11:08 | 102 | 6:47 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO FASE PRIMARIA | S22123000017 | New_Event | Primary Wire Break | Include | Include | Equipment | 407 | 2022-12-30 | 41514 | keep | 0 | Dec | 2022 | 0.028275 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
SAN JUAN | 2022-12-30 04:24 | 2022-12-30 12:23 | 100 | 7:59 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO 1 X 15 EN TRANSFORMADOR | S2212300018 | New_Event | Primary Wire Break | Include | Include | Equipment | 479 | 2022-12-30 | 47900 | keep | 0 | Dec | 2022 | 0.032624 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-12-30 04:32 | 2022-12-30 10:05 | 80 | 5:33 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO 1 X 40 EN C/L | B22123000008 | New_Event | Primary Wire Break | Include | Include | Equipment | 333 | 2022-12-30 | 26640 | keep | 0 | Dec | 2022 | 0.018144 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-12-30 04:54 | 2022-12-30 15:45 | 24 | 10:51 | P | DESGANCHE | DESGANCHE 1 X 50 EN C/L | B22123000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 651 | 2022-12-30 | 15624 | keep | 0 | Dec | 2022 | 0.010641 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2022-12-30 04:58 | 2022-12-30 09:20 | 25 | 4:22 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | M22123000028 | New_Event | Primary Wire Break | Include | Include | Equipment | 262 | 2022-12-30 | 6550 | keep | 0 | Dec | 2022 | 0.0044612 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-12-30 05:23 | 2022-12-30 09:45 | 15 | 4:22 | P | DESGANCHE | 1 X 65 C/L1 X 40 C/L DESGANCHE | R22123000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-12-30 | 3930 | keep | 0 | Dec | 2022 | 0.0026767 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-12-30 05:26 | 2022-12-30 05:27 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22123000016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 2697 | keep | 0 | Dec | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
CANOVANAS | 2022-12-30 05:54 | 2022-12-30 12:33 | 15 | 6:39 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO Y 2 X 40 EN C/L | R22123000004 | New_Event | Primary Wire Break | Include | Include | Equipment | 399 | 2022-12-30 | 5985 | keep | 0 | Dec | 2022 | 0.0040764 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-12-30 06:02 | 2022-12-30 06:05 | 2610 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO CONTROL | B221230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-12-30 | 7830 | keep | 0 | Dec | 2022 | 0.005333 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2022-12-30 06:09 | 2022-12-30 07:29 | 23 | 1:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22123000014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2022-12-30 | 1840 | keep | 0 | Dec | 2022 | 0.0012532 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
AGUADILLA | 2022-12-30 06:18 | 2022-12-30 11:49 | 200 | 5:31 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | M22123000032 | New_Event | Primary Wire Break | Include | Include | Equipment | 331 | 2022-12-30 | 66200 | keep | 0 | Dec | 2022 | 0.045089 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-12-30 06:27 | 2022-12-30 11:05 | 15 | 4:38 | P | TRANSFORMADOR AVERIADO | SE CAMBIO XMR 50 KVA Y SE REPUSO 1 X 10 | S22123000025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 278 | 2022-12-30 | 4170 | keep | 0 | Dec | 2022 | 0.0028402 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-12-30 06:55 | 2022-12-30 09:44 | 25 | 2:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L LLUVIA | B22123000016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 169 | 2022-12-30 | 4225 | keep | 0 | Dec | 2022 | 0.0028776 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-12-30 07:13 | 2022-12-30 07:14 | 215 | 0:01 | T | DESGANCHE | DISPARO CERADO POR CONTROL | B2212300000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-12-30 | 215 | keep | 0 | Dec | 2022 | 0.00014644 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-12-30 07:14 | 2022-12-30 08:16 | 60 | 1:02 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | B22123000003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-12-30 | 3720 | keep | 0 | Dec | 2022 | 0.0025337 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-12-30 07:43 | 2022-12-30 09:11 | 1830 | 1:28 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | RECERRO INTERRUPTOR QUEDO FUERA, SE REALIZO PRUEBA SIN CARGA Y PROBO MALO. SE TRANSFIRIO CARGA AL 2201-01 SWF SJ-221230-50 | R22123000012 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 88 | 2022-12-30 | 161040 | keep | 0 | Dec | 2022 | 0.10968 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
ARECIBO | 2022-12-30 07:57 | 2022-12-30 15:50 | 45 | 7:53 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN CL BAJANTE PRIMARIO CRUZADO CON CASCO TRANSFORMADOR | A22123000027 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 473 | 2022-12-30 | 21285 | keep | 0 | Dec | 2022 | 0.014497 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-12-30 07:59 | 2022-12-30 08:00 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1206-03 | S2212300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-30 | 8679 | keep | 0 | Dec | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-12-30 07:59 | 2022-12-30 08:00 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 4133 | keep | 0 | Dec | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2022-12-30 08:01 | 2022-12-30 12:38 | 20 | 4:37 | P | DESGANCHE | 1 X 25 EN C/L SE DESGANCHO | B22123000019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2022-12-30 | 5540 | keep | 0 | Dec | 2022 | 0.0037733 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-12-30 08:01 | 2022-12-30 12:53 | 20 | 4:52 | P | DESGANCHE | 1 X 25 EN C/L | B22123000019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2022-12-30 | 5840 | keep | 0 | Dec | 2022 | 0.0039776 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-12-30 08:09 | 2022-12-30 09:21 | 1 | 1:12 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A RISER | B22123000023 | New_Event | Primary Wire Break | Include | Include | Equipment | 72 | 2022-12-30 | 72 | keep | 0 | Dec | 2022 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-12-30 08:12 | 2022-12-30 11:48 | 524 | 3:36 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S22123000137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-12-30 | 113184 | keep | 0 | Dec | 2022 | 0.077089 | 0.00035689 | Sustained | FALSE | FALSE | Not_TMED_Event | 524
YAUCO | 2022-12-30 08:31 | 2022-12-30 11:37 | 50 | 3:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P22123000027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-12-30 | 9300 | keep | 0 | Dec | 2022 | 0.0063342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-12-30 08:53 | 2022-12-30 10:30 | 5 | 1:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO DE CAJA DE TRANSFORMADOR | P22123000031 | New_Event | Primary Wire Break | Include | Include | Equipment | 97 | 2022-12-30 | 485 | keep | 0 | Dec | 2022 | 0.00033033 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-12-30 09:17 | 2022-12-30 11:17 | 15 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | S22123000047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2022-12-30 | 1800 | keep | 0 | Dec | 2022 | 0.001226 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-12-30 09:30 | 2022-12-30 13:57 | 60 | 4:27 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN C/L 1 X EN C/L AVERIA T-4 @ T-3 | B22123000032 | New_Event | UG Cable Fault | Include | Include | Equipment | 267 | 2022-12-30 | 16020 | keep | 0 | Dec | 2022 | 0.010911 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-12-30 09:37 | 2022-12-30 12:00 | 4 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L MAL TIEMPO | S22123000051 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2022-12-30 | 572 | keep | 0 | Dec | 2022 | 0.00038959 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-12-30 09:41 | 2022-12-30 14:30 | 12 | 4:49 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR NO SE ENCONTRO CAUSA | A22123000041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 289 | 2022-12-30 | 3468 | keep | 0 | Dec | 2022 | 0.002362 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-12-30 09:43 | 2022-12-30 11:47 | 50 | 2:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 40 EN C/L | R22123000040 | New_Event | Cutout Failure | Include | Include | Equipment | 124 | 2022-12-30 | 6200 | keep | 0 | Dec | 2022 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-12-30 09:52 | 2022-12-30 11:45 | 3 | 1:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR REEMPLAZAR LOS BAJANTES SECUNDARIOS | C22123000028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 113 | 2022-12-30 | 339 | keep | 0 | Dec | 2022 | 0.00023089 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-12-30 10:05 | 2022-12-30 15:48 | 20 | 5:43 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE CERRO PUENTE PRIMARIO | B22123000008 | New_Event | Primary Wire Break | Include | Include | Equipment | 343 | 2022-12-30 | 6860 | keep | 0 | Dec | 2022 | 0.0046723 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-12-30 10:17 | 2022-12-30 13:17 | 1 | 3:00 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANSFORMADOR 25KVA A 2400 | P22123000050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 180 | 2022-12-30 | 180 | keep | 0 | Dec | 2022 | 0.0001226 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-12-30 10:18 | 2022-12-30 11:12 | 1337 | 0:54 | T | DESGANCHE | SE CERRO INTERRUPTOR MANUALMENTE EN LA SUBESTACION YA QUE EL MISMO DISPARO Y NO ENVIA SEÃ‘AL DE DISPARO POR SCADA RAMA CAYO Y CRUZO FASES | M22123000052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-12-30 | 72198 | keep | 0 | Dec | 2022 | 0.049174 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
CANOVANAS | 2022-12-30 10:19 | 2022-12-30 12:07 | 8 | 1:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO Y SECUNDARIA EN VARIOS PUNTOS | R22123000027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 108 | 2022-12-30 | 864 | keep | 0 | Dec | 2022 | 0.00058847 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-12-30 10:20 | 2022-12-30 10:45 | 20 | 0:25 | P | DESGANCHE | DESGANCHE Y 1 X 80 EN C/L | R22123000048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2022-12-30 | 500 | keep | 0 | Dec | 2022 | 0.00034055 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-12-30 10:30 | 2022-12-30 13:45 | 60 | 3:15 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | M22123000057 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 195 | 2022-12-30 | 11700 | keep | 0 | Dec | 2022 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-12-30 10:40 | 2022-12-30 14:45 | 10 | 4:05 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A22123000048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-12-30 | 2450 | keep | 0 | Dec | 2022 | 0.0016687 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-12-30 10:44 | 2022-12-30 15:55 | 75 | 5:11 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | A22123000049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-12-30 | 23325 | keep | 0 | Dec | 2022 | 0.015887 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-12-30 10:45 | 2022-12-30 11:00 | 10 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS QUEMADOS | M22123000047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2022-12-30 | 150 | keep | 0 | Dec | 2022 | 0.00010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-12-30 10:54 | 2022-12-30 15:18 | 1 | 4:24 | P | NO SE REPORTO CAUSA | 2 X 15 EN BANCO DE XMR | R22123000053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 264 | 2022-12-30 | 264 | keep | 0 | Dec | 2022 | 0.00017981 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-12-30 10:56 | 2022-12-30 16:41 | 50 | 5:45 | P | DESGANCHE | 1 X 65 SE RETIRO BAMBUA | C22123000042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2022-12-30 | 17250 | keep | 0 | Dec | 2022 | 0.011749 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-12-30 11:01 | 2022-12-30 11:02 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 1702 | keep | 0 | Dec | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
SAN JUAN | 2022-12-30 11:05 | 2022-12-30 12:20 | 50 | 1:15 | P | DESGANCHE | 1 X 50 DESGANCHE | S22123000069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-12-30 | 3750 | keep | 0 | Dec | 2022 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-12-30 11:10 | 2022-12-30 13:38 | 40 | 2:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y 1 X 40 EN C/L | R22123000058 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 148 | 2022-12-30 | 5920 | keep | 0 | Dec | 2022 | 0.0040321 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-12-30 11:14 | 2022-12-31 15:46 | 45 | 28:32 | P | TERMINACION SOTERRADA AVERIADA | SE REALIZO EMPALME | S22123000014 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1712 | 2022-12-30 | 77040 | keep | 0 | Dec | 2022 | 0.052472 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-12-30 11:15 | 2022-12-30 11:30 | 3 | 0:15 | P | NO SE REPORTO CAUSA | 2 X 30 EN CL NO SE ENCONTRO CAUSA | A22123000058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-12-30 | 45 | keep | 0 | Dec | 2022 | 3.0649e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-12-30 11:18 | 2022-12-30 17:25 | 38 | 6:07 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE CERRO PUENTE ABIERTO | B22123000053 | New_Event | Primary Wire Break | Include | Include | Equipment | 367 | 2022-12-30 | 13946 | keep | 0 | Dec | 2022 | 0.0094986 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CANOVANAS | 2022-12-30 11:26 | 2022-12-30 14:15 | 14 | 2:49 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L Y 1 X 15 EN XMR | R22123000062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-12-30 | 2366 | keep | 0 | Dec | 2022 | 0.0016115 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-12-30 11:47 | 2022-12-30 11:48 | 414 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1204-01 SPARE QUE LLEVA 30% DEL 1204-03 | S2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 414 | keep | 0 | Dec | 2022 | 0.00028197 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
BAYAMON | 2022-12-30 11:48 | 2022-12-30 11:49 | 2466 | 0:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | S2212300000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-12-30 | 2466 | keep | 0 | Dec | 2022 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2022-12-30 11:49 | 2022-12-30 11:56 | 524 | 0:07 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S22123000137 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-12-30 | 3668 | keep | 0 | Dec | 2022 | 0.0024983 | 0.00035689 | Sustained | FALSE | FALSE | Not_TMED_Event | 524
VEGA BAJA | 2022-12-30 11:50 | 2022-12-30 11:52 | 2610 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22123000054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-12-30 | 5220 | keep | 0 | Dec | 2022 | 0.0035553 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
SAN JUAN | 2022-12-30 11:53 | 2022-12-30 11:57 | 828 | 0:04 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S2212300000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-12-30 | 3312 | keep | 0 | Dec | 2022 | 0.0022558 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-12-30 11:53 | 2022-12-30 11:57 | 1977 | 0:04 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S2212300000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-12-30 | 7908 | keep | 0 | Dec | 2022 | 0.0053861 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-12-30 11:53 | 2022-12-30 11:57 | 8679 | 0:04 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S2212300000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-12-30 | 34716 | keep | 0 | Dec | 2022 | 0.023645 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-12-30 11:53 | 2022-12-30 11:57 | 338 | 0:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S2212300000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-12-30 | 1352 | keep | 0 | Dec | 2022 | 0.00092084 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2022-12-30 11:53 | 2022-12-30 11:57 | 733 | 0:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S2212300000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-12-30 | 2932 | keep | 0 | Dec | 2022 | 0.001997 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-12-30 11:53 | 2022-12-30 11:57 | 4133 | 0:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S2212300000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-12-30 | 16532 | keep | 0 | Dec | 2022 | 0.01126 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-12-30 11:53 | 2022-12-30 11:57 | 1799 | 0:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S2212300000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-12-30 | 7196 | keep | 0 | Dec | 2022 | 0.0049012 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-12-30 11:54 | 2022-12-30 11:56 | 1681 | 0:02 | T | NO SE REPORTO CAUSA | SE PROBO POR CONTROL QUEDO EN SERVICIO | S2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-12-30 | 3362 | keep | 0 | Dec | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-12-30 11:54 | 2022-12-30 11:56 | 225 | 0:02 | T | NO SE REPORTO CAUSA | SE PROBO POR CONTROL QUEDO EN SERVICIO | S2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-12-30 | 450 | keep | 0 | Dec | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-12-30 11:54 | 2022-12-30 11:56 | 1598 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO 1303-04 SE CERRO POR CONTROL QUEDO EN SERVICIO | S2212300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2022-12-30 | 3196 | keep | 0 | Dec | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2022-12-30 11:56 | 2022-12-30 11:57 | 2466 | 0:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | S2212300000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-12-30 | 2466 | keep | 0 | Dec | 2022 | 0.0016796 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-12-30 11:57 | 2022-12-30 13:03 | 248 | 1:06 | P | ALIMENTADOR AMARRADO | SE ENCONTRO PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR 1206-04 | S2212300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 66 | 2022-12-30 | 16368 | keep | 0 | Dec | 2022 | 0.011148 | 0.00016891 | Sustained | FALSE | FALSE | Not_TMED_Event | 248
SAN JUAN | 2022-12-30 11:57 | 2022-12-30 13:03 | 593 | 1:06 | P | ALIMENTADOR AMARRADO | SE ENCONTRO PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR 1206-04 | S2212300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 66 | 2022-12-30 | 39138 | keep | 0 | Dec | 2022 | 0.026657 | 0.00040389 | Sustained | FALSE | FALSE | Not_TMED_Event | 593
SAN JUAN | 2022-12-30 11:57 | 2022-12-30 13:03 | 600 | 1:06 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR | S2212300000X | New_Event | Primary Wire Break | Include | Include | Equipment | 66 | 2022-12-30 | 39600 | keep | 0 | Dec | 2022 | 0.026971 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2022-12-30 11:57 | 2022-12-30 15:36 | 524 | 3:39 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S22123000137 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-12-30 | 114756 | keep | 0 | Dec | 2022 | 0.07816 | 0.00035689 | Sustained | FALSE | FALSE | Not_TMED_Event | 524
AGUADILLA | 2022-12-30 11:57 | 2022-12-30 13:07 | 6 | 1:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO SE ENCONTRO CAUSA | A22123000069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2022-12-30 | 420 | keep | 0 | Dec | 2022 | 0.00028606 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-12-30 12:05 | 2022-12-30 12:21 | 10 | 0:16 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO Y RETEZO TOMA SECUNDARIA | B22123000057 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 16 | 2022-12-30 | 160 | keep | 0 | Dec | 2022 | 0.00010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-12-30 12:14 | 2022-12-30 14:05 | 1 | 1:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CL FUERTES VIENTOS | A22123000073 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 111 | 2022-12-30 | 111 | keep | 0 | Dec | 2022 | 7.5602e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-12-30 12:16 | 2022-12-30 17:23 | 75 | 5:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M22123000083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 307 | 2022-12-30 | 23025 | keep | 0 | Dec | 2022 | 0.015682 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-12-30 12:17 | 2022-12-30 15:10 | 70 | 2:53 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE | A22123000074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-12-30 | 12110 | keep | 0 | Dec | 2022 | 0.0082481 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-12-30 12:20 | 2022-12-30 12:21 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 3511 | keep | 0 | Dec | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
CAGUAS | 2022-12-30 12:29 | 2022-12-30 14:36 | 8 | 2:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BARRAS EN PEDESTAL | C22123000057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 127 | 2022-12-30 | 1016 | keep | 0 | Dec | 2022 | 0.00069199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-12-30 12:36 | 2022-12-30 19:54 | 50 | 7:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIA | S22123000176 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 438 | 2022-12-30 | 21900 | keep | 0 | Dec | 2022 | 0.014916 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-12-30 12:37 | 2022-12-30 13:33 | 1 | 0:56 | P | MAL TIEMPO/RAYOS | 1 X 30 EN RISER MAL TIEMPO RAYOS | C22123000058 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 56 | 2022-12-30 | 56 | keep | 0 | Dec | 2022 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-12-30 12:49 | 2022-12-30 16:35 | 70 | 3:46 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | A22123000083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-12-30 | 15820 | keep | 0 | Dec | 2022 | 0.010775 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-12-30 12:53 | 2022-12-31 09:07 | 10 | 20:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPAARO BAJANTE DE CAJA A XMR | S22123000184 | New_Event | Primary Wire Break | Include | Include | Equipment | 1214 | 2022-12-30 | 12140 | keep | 0 | Dec | 2022 | 0.0082685 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-12-30 12:53 | 2022-12-30 14:38 | 2 | 1:45 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESPEJE DE LINEA | R22123000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-12-30 | 210 | keep | 0 | Dec | 2022 | 0.00014303 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-12-30 12:54 | 2022-12-30 14:00 | 25 | 1:06 | P | DESGANCHE | DESGANCHE 1 X 20 EN C/L | B22123000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-12-30 | 1650 | keep | 0 | Dec | 2022 | 0.0011238 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-12-30 13:00 | 2022-12-30 20:10 | 16 | 7:10 | P | DESGANCHE | 1 X 15 EN XMR 1 X 30 EN C/L DESGANCHE | B22123000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 430 | 2022-12-30 | 6880 | keep | 0 | Dec | 2022 | 0.0046859 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-12-30 13:03 | 2022-12-30 13:38 | 828 | 0:35 | P | ALIMENTADOR AMARRADO | SE ENCONTRO PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR 1206-04 | S2212300000X | Additional_clients | Feeder Load Transferred | Include | Include | Other | 35 | 2022-12-30 | 28980 | keep | 0 | Dec | 2022 | 0.019738 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-12-30 13:03 | 2022-12-30 13:38 | 1977 | 0:35 | P | ALIMENTADOR AMARRADO | SE ENCONTRO PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR 1206-04 | S2212300000X | Additional_clients | Feeder Load Transferred | Include | Include | Other | 35 | 2022-12-30 | 69195 | keep | 0 | Dec | 2022 | 0.047128 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-12-30 13:03 | 2022-12-30 13:38 | 1799 | 0:35 | T | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR | S2212300000X | Additional_clients | Primary Wire Break | Include | Include | Equipment | 35 | 2022-12-30 | 62965 | keep | 0 | Dec | 2022 | 0.042885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-12-30 13:05 | 2022-12-30 14:17 | 10 | 1:12 | P | DESGANCHE | 1 X 40 EN C/L DESGACHE | C22123000063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-12-30 | 720 | keep | 0 | Dec | 2022 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-12-30 13:29 | 2022-12-30 16:49 | 50 | 3:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN CL NO SE ENCONTRO CAUSA | A22123000093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2022-12-30 | 10000 | keep | 0 | Dec | 2022 | 0.006811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-12-30 13:30 | 2022-12-30 16:58 | 7 | 3:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | DESGANCHE SE REMPLAZO TRAMO SECUNDARIA 1 X 10 EN TRANSFORMADOR | S22123000346 | New_Event | Secondary Wire Break | Include | Include | Equipment | 208 | 2022-12-30 | 1456 | keep | 0 | Dec | 2022 | 0.00099167 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-12-30 13:31 | 2022-12-30 15:08 | 12 | 1:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22123000066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 97 | 2022-12-30 | 1164 | keep | 0 | Dec | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-12-30 13:35 | 2022-12-30 18:57 | 2 | 5:22 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A22123000096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2022-12-30 | 644 | keep | 0 | Dec | 2022 | 0.00043863 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-12-30 13:40 | 2022-12-30 15:52 | 40 | 2:12 | P | DESGANCHE | DESGANCHE 1 X 65 EN C/L 1 X 80 EN C/L | S22123000304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-12-30 | 5280 | keep | 0 | Dec | 2022 | 0.0035962 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-12-30 13:49 | 2022-12-30 13:50 | 842 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | S2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 842 | keep | 0 | Dec | 2022 | 0.00057348 | 0.00057348 | Momentary | FALSE | FALSE | Not_TMED_Event | 842
SAN JUAN | 2022-12-30 13:54 | 2022-12-30 17:32 | 31 | 3:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22123000321 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2022-12-30 | 6758 | keep | 0 | Dec | 2022 | 0.0046028 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
VEGA BAJA | 2022-12-30 13:55 | 2022-12-30 16:07 | 1 | 2:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CL FUERTES VIENTOS | A22123000100 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 132 | 2022-12-30 | 132 | keep | 0 | Dec | 2022 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-12-30 13:57 | 2022-12-30 20:30 | 10 | 6:33 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DEL T-4 @ T-3 | B22123000032 | New_Event | UG Cable Fault | Include | Include | Equipment | 393 | 2022-12-30 | 3930 | keep | 0 | Dec | 2022 | 0.0026767 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-12-30 14:02 | 2022-12-30 16:36 | 2 | 2:34 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO HOT CLAM | S22123000327 | New_Event | Primary Wire Break | Include | Include | Equipment | 154 | 2022-12-30 | 308 | keep | 0 | Dec | 2022 | 0.00020978 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2022-12-30 14:05 | 2022-12-30 15:04 | 20 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22123000073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2022-12-30 | 1180 | keep | 0 | Dec | 2022 | 0.00080369 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-12-30 14:10 | 2022-12-30 14:21 | 1 | 0:11 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22123000076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 11 | 2022-12-30 | 11 | keep | 0 | Dec | 2022 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-12-30 14:10 | 2022-12-30 16:44 | 8 | 2:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO SE ENCONTRO CAUSA | A22123000105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-12-30 | 1232 | keep | 0 | Dec | 2022 | 0.00083911 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-12-30 14:23 | 2022-12-30 14:40 | 20 | 0:17 | P | MAL TIEMPO/LLUVIA O VIENTO | LLUVIA 1 X 20 EN C/L | B22123000078 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 17 | 2022-12-30 | 340 | keep | 0 | Dec | 2022 | 0.00023157 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-12-30 14:34 | 2022-12-30 14:35 | 3502 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE COLOCA RR EN OFF Y SE REALIZA PRUEBA QUEDANDO INTERRUPTOR EN SERVICIO | A22123000109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 3502 | keep | 0 | Dec | 2022 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-12-30 14:35 | 2022-12-30 20:21 | 100 | 5:46 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CL SE LIGO LINEA PRIMARIA EN AISLADOR | A22123000108 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 346 | 2022-12-30 | 34600 | keep | 0 | Dec | 2022 | 0.023566 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-12-30 14:39 | 2022-12-30 14:45 | 2435 | 0:06 | T | ALIMENTADOR AMARRADO | RECERRO 1909-08 Y LLEVA 1907-05 | S2212300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2022-12-30 | 14610 | keep | 0 | Dec | 2022 | 0.0099508 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-12-30 14:39 | 2022-12-30 14:45 | 2956 | 0:06 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1907-05 | S2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-12-30 | 17736 | keep | 0 | Dec | 2022 | 0.01208 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-12-30 14:43 | 2022-12-30 15:57 | 50 | 1:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 C/L LLUVIA | B22123000083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 74 | 2022-12-30 | 3700 | keep | 0 | Dec | 2022 | 0.0025201 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-12-30 14:44 | 2022-12-30 15:36 | 1 | 0:52 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | C22123000079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-12-30 | 52 | keep | 0 | Dec | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-12-30 14:47 | 2022-12-30 14:48 | 860 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22123000080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 860 | keep | 0 | Dec | 2022 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
PONCE | 2022-12-30 14:59 | 2022-12-30 16:24 | 95 | 1:25 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P22123000081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-12-30 | 8075 | keep | 0 | Dec | 2022 | 0.0054998 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
PONCE | 2022-12-30 15:00 | 2022-12-30 15:01 | 1109 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22123000083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 1109 | keep | 0 | Dec | 2022 | 0.00075533 | 0.00075533 | Momentary | FALSE | FALSE | Not_TMED_Event | 1109
PONCE | 2022-12-30 15:04 | 2022-12-30 16:57 | 150 | 1:53 | P | DESGANCHE | 1 X 80 EN CONVERTIDOR POR DESGANCHE | P22123000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-12-30 | 16950 | keep | 0 | Dec | 2022 | 0.011545 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-12-30 15:09 | 2022-12-30 20:56 | 12 | 5:47 | P | CAUSAS EXTERNAS | CRUCE POR GLOBOS 1 X 20 EN C/L | B22123000086 | New_Event | Damage From Public | Include | Include | Public | 347 | 2022-12-30 | 4164 | keep | 0 | Dec | 2022 | 0.0028361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-12-30 15:18 | 2022-12-30 15:19 | 407 | 0:01 | P | NO SE REPORTO CAUSA | INTERRUPTOR SOLO LLEVA EL 90% DE SU CARGA | B2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 407 | keep | 0 | Dec | 2022 | 0.00027721 | 0.00027721 | Momentary | FALSE | FALSE | Not_TMED_Event | 407
YAUCO | 2022-12-30 15:22 | 2022-12-30 15:23 | 179 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M22123000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-12-30 | 179 | keep | 0 | Dec | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
YAUCO | 2022-12-30 15:23 | 2022-12-30 18:14 | 170 | 2:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22123000108 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-12-30 | 29070 | keep | 0 | Dec | 2022 | 0.019799 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
PONCE | 2022-12-30 15:25 | 2022-12-30 16:50 | 110 | 1:25 | P | ARBOL SOBRE LINEA | 2 X 50 EN CORTE DE LINEA ARBOL SOBRE LINEA | P22123000095 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 85 | 2022-12-30 | 9350 | keep | 0 | Dec | 2022 | 0.0063682 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
SAN JUAN | 2022-12-30 15:29 | 2022-12-30 19:42 | 5 | 4:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22123000353 | New_Event | Secondary Wire Break | Include | Include | Equipment | 253 | 2022-12-30 | 1265 | keep | 0 | Dec | 2022 | 0.00086159 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-12-30 15:42 | 2022-12-30 17:39 | 10 | 1:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIARON CONECTORES EN CAJA PRIMARIA DE TRANSFORMADOR | P22123000100 | New_Event | Cutout Failure | Include | Include | Equipment | 117 | 2022-12-30 | 1170 | keep | 0 | Dec | 2022 | 0.00079688 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-12-30 15:44 | 2022-12-30 16:14 | 35 | 0:30 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO AEREO PROVISIONAL PARA RETEZAR LINEA PRIMARIA | R22123000082 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 30 | 2022-12-30 | 1050 | keep | 0 | Dec | 2022 | 0.00071515 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-12-30 15:44 | 2022-12-30 19:05 | 16 | 3:21 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE RETIRO ENREDADERA | C22123000085 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 201 | 2022-12-30 | 3216 | keep | 0 | Dec | 2022 | 0.0021904 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2022-12-30 15:47 | 2022-12-30 17:19 | 6 | 1:32 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA RAMA SOBRE LINEA | P22123000102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-12-30 | 552 | keep | 0 | Dec | 2022 | 0.00037596 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-12-30 16:14 | 2022-12-30 18:42 | 10 | 2:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA | S2212300357 | New_Event | Cutout Failure | Include | Include | Equipment | 148 | 2022-12-30 | 1480 | keep | 0 | Dec | 2022 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-12-30 16:22 | 2022-12-30 19:16 | 30 | 2:54 | P | DESGANCHE | 1 X 25 EN C/L EN DESGANCHE | R22123000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-12-30 | 5220 | keep | 0 | Dec | 2022 | 0.0035553 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-12-30 16:47 | 2022-12-30 17:46 | 26 | 0:59 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | R22123000086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-12-30 | 1534 | keep | 0 | Dec | 2022 | 0.0010448 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
HUMACAO | 2022-12-30 16:50 | 2022-12-30 17:45 | 8 | 0:55 | P | ANIMAL | 1 X 25 EN C/L AVE CRUZO LINEA | C22123000089 | New_Event | Animals | Include | Include | Wildlife | 55 | 2022-12-30 | 440 | keep | 0 | Dec | 2022 | 0.00029968 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-12-30 17:05 | 2022-12-31 00:12 | 72 | 7:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | B22123000094 | New_Event | Cutout Failure | Include | Include | Equipment | 427 | 2022-12-30 | 30744 | keep | 0 | Dec | 2022 | 0.02094 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
MAYAGÃœEZ | 2022-12-30 17:40 | 2022-12-30 19:55 | 100 | 2:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA / SE REPARO LINEA ZAFADA DE AISLADOR | M22123000128 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 135 | 2022-12-30 | 13500 | keep | 0 | Dec | 2022 | 0.0091948 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-12-30 18:16 | 2022-12-30 18:17 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 3070 | keep | 0 | Dec | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-12-30 18:19 | 2022-12-30 18:44 | 12 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO REPARO LINEA SECUNDARIA | B22123000110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-12-30 | 300 | keep | 0 | Dec | 2022 | 0.00020433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-12-30 18:35 | 2022-12-30 21:11 | 21 | 2:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22123000091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2022-12-30 | 3276 | keep | 0 | Dec | 2022 | 0.0022313 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
PONCE | 2022-12-30 18:51 | 2022-12-30 21:28 | 25 | 2:37 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTES 1 X 40 EN CORTE DE LINEA POR ALAMBRE PRIMARIO EN EL PISO | P22123000124 | New_Event | Primary Wire Break | Include | Include | Equipment | 157 | 2022-12-30 | 3925 | keep | 0 | Dec | 2022 | 0.0026733 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-12-30 19:02 | 2022-12-30 19:03 | 327 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE INTERRUPTOR CARGA POR EL 2604-01 EN SERVICIO | C2212300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-30 | 327 | keep | 0 | Dec | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2022-12-30 19:02 | 2022-12-30 19:03 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 2604-01 LLEVA 2603-07 | C2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 2354 | keep | 0 | Dec | 2022 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
YAUCO | 2022-12-30 19:03 | 2022-12-30 20:31 | 100 | 1:28 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO DE CAJA DE CORTE DE LINEA 1 X 50 | P22123000128 | New_Event | Primary Wire Break | Include | Include | Equipment | 88 | 2022-12-30 | 8800 | keep | 0 | Dec | 2022 | 0.0059936 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-12-30 19:24 | 2022-12-31 09:15 | 20 | 13:51 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | M22123000158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 831 | 2022-12-30 | 16620 | keep | 0 | Dec | 2022 | 0.01132 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-12-30 19:43 | 2022-12-31 09:30 | 16 | 13:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 15 EN XMR | S22123000369 | New_Event | Cutout Failure | Include | Include | Equipment | 827 | 2022-12-30 | 13232 | keep | 0 | Dec | 2022 | 0.0090123 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-12-30 20:25 | 2022-12-30 20:26 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22123000165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 990 | keep | 0 | Dec | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BARRANQUITAS | 2022-12-30 20:31 | 2022-12-31 09:53 | 6 | 13:22 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR SE REALIZO DESGANCHE | C22123000095 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 802 | 2022-12-30 | 4812 | keep | 0 | Dec | 2022 | 0.0032774 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-12-30 21:07 | 2022-12-31 08:30 | 40 | 11:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22123000147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 683 | 2022-12-30 | 27320 | keep | 0 | Dec | 2022 | 0.018608 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-12-30 21:28 | 2022-12-31 11:48 | 15 | 14:20 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE PRIMARIO Y SE CERRARON PUENTES | P22123000124 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 860 | 2022-12-30 | 12900 | keep | 0 | Dec | 2022 | 0.0087861 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-12-30 21:39 | 2022-12-31 10:50 | 7 | 13:11 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE | A22123000148 | New_Event | Animals | Include | Include | Wildlife | 791 | 2022-12-30 | 5537 | keep | 0 | Dec | 2022 | 0.0037712 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-12-30 21:56 | 2022-12-30 21:58 | 723 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 1711-02 LLEVANDO 10% DE LA CARGA DEL 1711-04 | B2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-12-30 | 1446 | keep | 0 | Dec | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-12-30 21:56 | 2022-12-30 21:58 | 198 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL 10% DE LA CARGA POR EL 1711-02 | B2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-12-30 | 396 | keep | 0 | Dec | 2022 | 0.00026971 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-12-30 21:56 | 2022-12-30 21:58 | 1976 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL CARGA POR EL 1711-02, AVERIA DEL 1711-02 | B2212300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2022-12-30 | 3952 | keep | 0 | Dec | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
SAN JUAN | 2022-12-30 22:10 | 2022-12-30 22:11 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 45 | keep | 0 | Dec | 2022 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-12-30 22:44 | 2022-12-30 22:45 | 450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2212300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 450 | keep | 0 | Dec | 2022 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
YAUCO | 2022-12-30 23:16 | 2022-12-31 10:45 | 8 | 11:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22123000133 | New_Event | Secondary Wire Break | Include | Include | Equipment | 689 | 2022-12-30 | 5512 | keep | 0 | Dec | 2022 | 0.0037542 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-12-30 23:17 | 2022-12-30 23:18 | 171 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 1110-05 | S221230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-30 | 171 | keep | 0 | Dec | 2022 | 0.00011647 | 0.00011647 | Momentary | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-12-30 23:17 | 2022-12-30 23:18 | 1837 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 1110-05 | S221230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-30 | 1837 | keep | 0 | Dec | 2022 | 0.0012512 | 0.0012512 | Momentary | FALSE | FALSE | Not_TMED_Event | 1837
SAN JUAN | 2022-12-30 23:17 | 2022-12-30 23:18 | 348 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 1110-05 | S221230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-30 | 348 | keep | 0 | Dec | 2022 | 0.00023702 | 0.00023702 | Momentary | FALSE | FALSE | Not_TMED_Event | 348
SAN JUAN | 2022-12-30 23:17 | 2022-12-30 23:18 | 283 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO CARGAS DEL 1102-2, 3 Y 5 | S221230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-30 | 283 | keep | 0 | Dec | 2022 | 0.00019275 | 0.00019275 | Momentary | FALSE | FALSE | Not_TMED_Event | 283
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 1225 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 | S22123000379 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 1225 | keep | 0 | Dec | 2022 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 1452 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 | S22123000379 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 1452 | keep | 0 | Dec | 2022 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 154 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 25% DE LA CARGA POR 1342-04 | S22123000380 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 154 | keep | 0 | Dec | 2022 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 334 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 35% DE LA CARGA POR EL 1345-05 | S22123000380 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 334 | keep | 0 | Dec | 2022 | 0.00022749 | 0.00022749 | Momentary | FALSE | FALSE | Not_TMED_Event | 334
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 259 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 CARGA POR EL 1345-03 | S22123000380 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 259 | keep | 0 | Dec | 2022 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 98 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 25% DE LA CARGA POR EL 1203-03 | S22123000379 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 98 | keep | 0 | Dec | 2022 | 6.6747e-05 | 6.6747e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 98
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 312 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 80% DE LA CARGA POR 1345-02 | S22123000380 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 312 | keep | 0 | Dec | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 660 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 | S22123000380 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 660 | keep | 0 | Dec | 2022 | 0.00044952 | 0.00044952 | Momentary | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 435 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 LLEVANDO 80% DEL 1342-04 | S22123000380 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 435 | keep | 0 | Dec | 2022 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 259 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 LLEVANDO EL 1342-02 | S22123000380 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 259 | keep | 0 | Dec | 2022 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 686 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 | S22123000380 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 686 | keep | 0 | Dec | 2022 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2022-12-30 23:37 | 2022-12-30 23:38 | 953 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 LLEVANDO EL 35% DEL 1330-04 | S22123000380 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-30 | 953 | keep | 0 | Dec | 2022 | 0.00064908 | 0.00064908 | Momentary | FALSE | FALSE | Not_TMED_Event | 953
CANOVANAS | 2022-12-30 23:37 | 2022-12-30 23:38 | 1745 | 0:01 | P | CAUSAS EXTERNAS | DISPARO INTERRUPTOR 15% DE LA CARGA POR EL 1646-03 CERRADO POR CONTROL VEHICULO IMPACTO SU-3D VER SJ-221231-50 | R22123000092 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-12-30 | 1745 | keep | 0 | Dec | 2022 | 0.0011885 | 0.0011885 | Momentary | FALSE | FALSE | Not_TMED_Event | 1745
PONCE | 2022-12-30 23:40 | 2022-12-31 08:54 | 70 | 9:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | P22123000136 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 554 | 2022-12-30 | 38780 | keep | 0 | Dec | 2022 | 0.026413 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-12-30 23:43 | 2022-12-31 11:20 | 15 | 11:37 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SECUNDARIAS CRUZADAS | A22123000150 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 697 | 2022-12-30 | 10455 | keep | 0 | Dec | 2022 | 0.0071209 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-12-31 00:03 | 2022-12-31 00:04 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22123100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-31 | 1859 | keep | 0 | Dec | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2022-12-31 00:26 | 2022-12-31 03:53 | 119 | 3:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA 1 X 65 EN RISER MAL TIEMPO | B22123100004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 207 | 2022-12-31 | 24633 | keep | 0 | Dec | 2022 | 0.016777 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
AGUADILLA | 2022-12-31 01:50 | 2022-12-31 10:00 | 6 | 8:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER NO SE IDENTIFICO CAUSA | A22123100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 490 | 2022-12-31 | 2940 | keep | 0 | Dec | 2022 | 0.0020024 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-12-31 02:39 | 2022-12-31 02:56 | 1745 | 0:17 | P | CAUSAS EXTERNAS | SE ABRIO INTERRUPTOR PARA PODER SECCIONALIZAR SU IMPACTADO POR VEHICULO, TENIA 15%YA TRANSFERIDO AL 1646-03 Y AHORA ENTRO 90% DE ESO | R22123100003 | 1st_after_momentary | Damage From Public | Include | Include | Public | 17 | 2022-12-31 | 29665 | keep | 0 | Dec | 2022 | 0.020205 | 0.0011885 | Sustained | FALSE | FALSE | Not_TMED_Event | 1745
CANOVANAS | 2022-12-31 02:56 | 2022-12-31 03:42 | 175 | 0:46 | P | CAUSAS EXTERNAS | SE TRANSFIRIO 10% DE LA CARGA AL 1646-03 PARA DEJAR SECCIONALIZADO SU-3D (SIN CARGA) QUE FUE IMPACTADO POR VEHICULO QUE LO SACO DE LA BASE. EN SERVICIO 100% | R22123100003 | Partial_restoration | Damage From Public | Include | Include | Public | 46 | 2022-12-31 | 8050 | keep | 0 | Dec | 2022 | 0.0054828 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-12-31 04:23 | 2022-12-31 07:30 | 121 | 3:07 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22123100001 | New_Event | Animals | Include | Include | Wildlife | 187 | 2022-12-31 | 22627 | keep | 0 | Dec | 2022 | 0.015411 | 8.2413e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 121
CAGUAS | 2022-12-31 05:11 | 2022-12-31 05:12 | 1893 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22123100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-31 | 1893 | keep | 0 | Dec | 2022 | 0.0012893 | 0.0012893 | Momentary | FALSE | FALSE | Not_TMED_Event | 1893
CANOVANAS | 2022-12-31 05:26 | 2022-12-31 06:25 | 3464 | 0:59 | T | CABLE SOTERRADO AVERIADO | DISPARO DE 2404-08 QUE LLEVA 2404-05, SE SECCIONALIZO RISER DE SALIDA AVERIADO DE 2404-05 Y SE CERRO AMARRE EXTERNO EN AVE. 65.INF CASI ESQUINA CARR. 185 SJ-221231-51 | R22123100016 | New_Event | UG Cable Fault | Include | Include | Equipment | 59 | 2022-12-31 | 204376 | keep | 0 | Dec | 2022 | 0.1392 | 0.0023593 | Sustained | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2022-12-31 05:26 | 2022-12-31 05:58 | 2675 | 0:32 | T | ALIMENTADOR AMARRADO | DISPARO DE 2404-08 QUE LLEVA 2404-05, SE ABRIO AMARRE CONTRA EL 2404-05 Y SE CERRO POR SCADA 2404-08, AVERIA DEL 2404-05 | R22123100016 | New_Event | Feeder Load Transferred | Include | Include | Other | 32 | 2022-12-31 | 85600 | keep | 0 | Dec | 2022 | 0.058302 | 0.0018219 | Sustained | FALSE | FALSE | Not_TMED_Event | 2675
VEGA BAJA | 2022-12-31 05:52 | 2022-12-31 06:52 | 3654 | 1:00 | T | DESGANCHE | DISPARO INTERRUPTOR SE ABRIO MACHETES SECCIONALIZAR ARBOL SOBRE LINEAS PRIMARIAS | A22123100010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-12-31 | 219240 | keep | 0 | Dec | 2022 | 0.14932 | 0.0024887 | Sustained | FALSE | FALSE | Not_TMED_Event | 3654
VEGA BAJA | 2022-12-31 06:52 | 2022-12-31 09:05 | 2009 | 2:13 | P | DESGANCHE | SE RETIRO ARBOL SOBRE LINEAS PRIMARIAS Y SE CERRO MACHETES | A22123100010 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-12-31 | 267197 | keep | 0 | Dec | 2022 | 0.18199 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-12-31 07:12 | 2022-12-31 11:09 | 50 | 3:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REMPLAZO AISLADOR | B22123100014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 237 | 2022-12-31 | 11850 | keep | 0 | Dec | 2022 | 0.008071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-12-31 07:58 | 2022-12-31 09:17 | 10 | 1:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN C/L LLUVIA | B22123100018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 79 | 2022-12-31 | 790 | keep | 0 | Dec | 2022 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-12-31 08:18 | 2022-12-31 10:45 | 77 | 2:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22123100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-12-31 | 11319 | keep | 0 | Dec | 2022 | 0.0077093 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
SAN JUAN | 2022-12-31 08:35 | 2022-12-31 08:36 | 1681 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1303-04 QUE SU CARGA ESTA POR 1303-05 LLEVA LA CARGA DEL 1303-01 Y LLEVA 1346-06 | S2212310000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-31 | 1681 | keep | 0 | Dec | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-12-31 08:35 | 2022-12-31 08:36 | 1598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1303-04 QUE SU CARGA ESTA POR 1303-05 LLEVA LA CARGA DEL 1303-01 Y LLEVA 1346-06 | S2212310000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-31 | 1598 | keep | 0 | Dec | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2022-12-31 09:02 | 2022-12-31 12:55 | 2 | 3:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARO BAJANTE PRIMARIO | A22123100107 | New_Event | Primary Wire Break | Include | Include | Equipment | 233 | 2022-12-31 | 466 | keep | 0 | Dec | 2022 | 0.00031739 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-12-31 09:15 | 2022-12-31 11:27 | 45 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 50 CL NO SE ENCONTRO CAUSA | M22123100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2022-12-31 | 5940 | keep | 0 | Dec | 2022 | 0.0040457 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-12-31 09:22 | 2022-12-31 11:22 | 68 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN SU | S22123100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-12-31 | 8160 | keep | 0 | Dec | 2022 | 0.0055577 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2022-12-31 09:30 | 2022-12-31 10:00 | 15 | 0:30 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE CONECTORES | A22123100112 | New_Event |  |  |  |  | 30 | 2022-12-31 | 450 | keep | 0 | Dec | 2022 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-12-31 09:33 | 2022-12-31 12:32 | 30 | 2:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 PORTAFUSIBLE | B22123100033 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2022-12-31 | 5370 | keep | 0 | Dec | 2022 | 0.0036575 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-12-31 09:38 | 2022-12-31 13:21 | 52 | 3:43 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L SE LEVANTO LINEA PRIMARIA | B22123100034 | New_Event | Primary Wire Break | Include | Include | Equipment | 223 | 2022-12-31 | 11596 | keep | 0 | Dec | 2022 | 0.007898 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
MAYAGÃœEZ | 2022-12-31 09:46 | 2022-12-31 12:47 | 10 | 3:01 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIAS CRUZADAS | M22123100010 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 181 | 2022-12-31 | 1810 | keep | 0 | Dec | 2022 | 0.0012328 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-12-31 10:15 | 2022-12-31 11:07 | 24 | 0:52 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22123100022 | New_Event | Animals | Include | Include | Wildlife | 52 | 2022-12-31 | 1248 | keep | 0 | Dec | 2022 | 0.00085001 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2022-12-31 10:29 | 2022-12-31 12:00 | 1 | 1:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22123100018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 91 | 2022-12-31 | 91 | keep | 0 | Dec | 2022 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-12-31 10:30 | 2022-12-31 13:32 | 2 | 3:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | C22123100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-12-31 | 364 | keep | 0 | Dec | 2022 | 0.00024792 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-12-31 10:30 | 2022-12-31 11:05 | 16 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRA EN PEDESTAL | B22123100040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-12-31 | 560 | keep | 0 | Dec | 2022 | 0.00038141 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-12-31 11:03 | 2022-12-31 12:55 | 11 | 1:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES EN LINEA SECUNDARIAS | M22123100014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 112 | 2022-12-31 | 1232 | keep | 0 | Dec | 2022 | 0.00083911 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2022-12-31 11:36 | 2022-12-31 12:05 | 45 | 0:29 | P | NO SE REPORTO CAUSA | 1 X 50 CL NO SE ENCONTRO CAUSA | M22123100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-12-31 | 1305 | keep | 0 | Dec | 2022 | 0.00088883 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-12-31 11:40 | 2022-12-31 15:24 | 15 | 3:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22123100045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 224 | 2022-12-31 | 3360 | keep | 0 | Dec | 2022 | 0.0022885 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-12-31 12:10 | 2022-12-31 12:45 | 22 | 0:35 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE CONECTORES | A22123100089 | New_Event |  |  |  |  | 35 | 2022-12-31 | 770 | keep | 0 | Dec | 2022 | 0.00052444 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2022-12-31 12:32 | 2022-12-31 17:00 | 80 | 4:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A22123100126 | New_Event | Primary Wire Break | Include | Include | Equipment | 268 | 2022-12-31 | 21440 | keep | 0 | Dec | 2022 | 0.014603 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-12-31 12:49 | 2022-12-31 12:50 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2212310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-31 | 1922 | keep | 0 | Dec | 2022 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
VEGA BAJA | 2022-12-31 12:56 | 2022-12-31 13:55 | 30 | 0:59 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22123100130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2022-12-31 | 1770 | keep | 0 | Dec | 2022 | 0.0012055 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-12-31 13:18 | 2022-12-31 13:54 | 1 | 0:36 | P | ANIMAL | 1 X 65 EN C/L AVE | B22123100053 | New_Event | Animals | Include | Include | Wildlife | 36 | 2022-12-31 | 36 | keep | 0 | Dec | 2022 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-12-31 13:21 | 2022-12-31 16:26 | 300 | 3:05 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO CON GOI BY-221231-01A | B22123100055 | New_Event | Primary Wire Break | Include | Include | Equipment | 185 | 2022-12-31 | 55500 | keep | 0 | Dec | 2022 | 0.037801 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-12-31 13:42 | 2022-12-31 15:12 | 15 | 1:30 | P | PROBLEMA DEL CLIENTE | 1 X 15 XMR SE ELIMINO TOMA DE CLIENTE AVERIADA | B22123100060 | New_Event | Customer-Related Interruption | Include | Include | Public | 90 | 2022-12-31 | 1350 | keep | 0 | Dec | 2022 | 0.00091948 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-12-31 14:13 | 2022-12-31 14:14 | 2286 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22123100084 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-12-31 | 2286 | keep | 0 | Dec | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2022-12-31 14:14 | 2022-12-31 16:59 | 347 | 2:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 3 CAJAS PRIMARIAS 2 X 100 EN C/L | R22123100085 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 165 | 2022-12-31 | 57255 | keep | 0 | Dec | 2022 | 0.038996 | 0.00023634 | Sustained | FALSE | FALSE | Not_TMED_Event | 347
BARRANQUITAS | 2022-12-31 14:24 | 2022-12-31 16:48 | 40 | 2:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C22123100115 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 144 | 2022-12-31 | 5760 | keep | 0 | Dec | 2022 | 0.0039231 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-12-31 14:53 | 2022-12-31 17:00 | 15 | 2:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M22123100049 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 127 | 2022-12-31 | 1905 | keep | 0 | Dec | 2022 | 0.0012975 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-12-31 15:04 | 2022-12-31 17:52 | 15 | 2:48 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO QUEMADO 50KVA X 50KVA | B22123100069 | New_Event | Service Transformer Failure | Include | Include | Equipment | 168 | 2022-12-31 | 2520 | keep | 0 | Dec | 2022 | 0.0017164 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-12-31 15:15 | 2022-12-31 17:20 | 10 | 2:05 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22123100137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-12-31 | 1250 | keep | 0 | Dec | 2022 | 0.00085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-12-31 15:52 | 2022-12-31 17:12 | 1 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIO | S22123100045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2022-12-31 | 80 | keep | 0 | Dec | 2022 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-12-31 16:03 | 2022-12-31 16:52 | 6 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CAMBIARON BAJANTES SECUNDARIOS DE TRANSFORMADOR Y CONECTORES | P22123100074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2022-12-31 | 294 | keep | 0 | Dec | 2022 | 0.00020024 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-12-31 16:22 | 2022-12-31 17:20 | 30 | 0:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22123100144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-12-31 | 1740 | keep | 0 | Dec | 2022 | 0.0011851 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-12-31 16:33 | 2022-12-31 19:15 | 200 | 2:42 | P | ANIMAL | 1 X 140 EN CL IGUANA | M22123100054 | New_Event | Animals | Include | Include | Wildlife | 162 | 2022-12-31 | 32400 | keep | 0 | Dec | 2022 | 0.022067 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-12-31 16:39 | 2022-12-31 18:25 | 30 | 1:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A22123100145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-12-31 | 3180 | keep | 0 | Dec | 2022 | 0.0021659 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-12-31 16:57 | 2022-12-31 16:58 | 320 | 0:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B22123100091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-12-31 | 320 | keep | 0 | Dec | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-12-31 16:58 | 2022-12-31 20:17 | 40 | 3:19 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B22123100093 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-12-31 | 7960 | keep | 0 | Dec | 2022 | 0.0054215 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-12-31 17:00 | 2022-12-31 17:20 | 19 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONECCIONES EN LOS BAJANTES SECUNDARIOS | A22123100149 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-12-31 | 380 | keep | 0 | Dec | 2022 | 0.00025882 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
FAJARDO | 2022-12-31 17:19 | 2022-12-31 18:00 | 22 | 0:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R22123100096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 41 | 2022-12-31 | 902 | keep | 0 | Dec | 2022 | 0.00061435 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
VEGA BAJA | 2022-12-31 17:19 | 2022-12-31 17:20 | 1879 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22123100153 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-31 | 1879 | keep | 0 | Dec | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
VEGA BAJA | 2022-12-31 17:19 | 2022-12-31 17:20 | 2777 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22123100153 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-31 | 2777 | keep | 0 | Dec | 2022 | 0.0018914 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
VEGA BAJA | 2022-12-31 17:19 | 2022-12-31 17:20 | 2 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22123100153 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-31 | 2 | keep | 0 | Dec | 2022 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-12-31 17:19 | 2022-12-31 17:20 | 2839 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22123100154 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-31 | 2839 | keep | 0 | Dec | 2022 | 0.0019336 | 0.0019336 | Momentary | FALSE | FALSE | Not_TMED_Event | 2839
VEGA BAJA | 2022-12-31 17:19 | 2022-12-31 17:20 | 1160 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22123100154 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-31 | 1160 | keep | 0 | Dec | 2022 | 0.00079007 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
VEGA BAJA | 2022-12-31 17:19 | 2022-12-31 17:20 | 1860 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A22123100154 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-12-31 | 1860 | keep | 0 | Dec | 2022 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
VEGA BAJA | 2022-12-31 17:20 | 2023-01-03 20:51 | 1 | 75:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN RISER | A22122100050 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 4531 | 2022-12-31 | 4531 | keep | 0 | Dec | 2022 | 0.003086 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-12-31 17:22 | 2022-12-31 17:23 | 215 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22123100099 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-12-31 | 215 | keep | 0 | Dec | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-12-31 17:24 | 2022-12-31 17:25 | 215 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22123100099 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-12-31 | 215 | keep | 0 | Dec | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BARRANQUITAS | 2022-12-31 18:01 | 2022-12-31 22:51 | 125 | 4:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22123100136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 290 | 2022-12-31 | 36250 | keep | 0 | Dec | 2022 | 0.02469 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
VEGA BAJA | 2022-12-31 18:19 | 2022-12-31 19:58 | 215 | 1:39 | T | DESCONECTIVO DEFECTUOSO | SE SECIONALIZO ALIMENTADOR PUNTO CALIENTE EN MACHETE ENTRO 20% EN SERVICIO | B22123100099 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 99 | 2022-12-31 | 21285 | keep | 0 | Dec | 2022 | 0.014497 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-12-31 18:44 | 2023-01-01 07:42 | 20 | 12:58 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A22123100156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 778 | 2022-12-31 | 15560 | keep | 0 | Dec | 2022 | 0.010598 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-12-31 19:03 | 2023-01-01 09:48 | 50 | 14:45 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A22123100158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 885 | 2022-12-31 | 44250 | keep | 0 | Dec | 2022 | 0.030138 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-12-31 19:10 | 2022-12-31 21:00 | 60 | 1:50 | P | DESGANCHE | 1 X 40 EN C/L | B22123100110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-12-31 | 6600 | keep | 0 | Dec | 2022 | 0.0044952 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-12-31 19:58 | 2022-12-31 20:19 | 172 | 0:21 | P | DESCONECTIVO DEFECTUOSO | SE SECIONALIZO ALIMENTADOR PUNTO CALIENTE EN MACHETE ENTRO 80% DE RESTANTE PARA UN 100% EN SERVICIO | B22123100099 | Partial_restoration | Switch Failure | Include | Include | Equipment | 21 | 2022-12-31 | 3612 | keep | 0 | Dec | 2022 | 0.0024601 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-12-31 20:08 | 2022-12-31 22:47 | 40 | 2:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REMPLAZO AISLADOR ROTO | C22123100146 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 159 | 2022-12-31 | 6360 | keep | 0 | Dec | 2022 | 0.0043318 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-12-31 20:09 | 2022-12-31 20:10 | 3464 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE INTERRUPTOR CARGA POR EL 2404-08 EN SERVICIO | R2212310000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-31 | 3464 | keep | 0 | Dec | 2022 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2022-12-31 20:09 | 2022-12-31 20:10 | 2675 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 2404-08 QUE LLEVA 2404-05 | R2212310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-31 | 2675 | keep | 0 | Dec | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
PONCE | 2022-12-31 20:36 | 2022-12-31 22:00 | 100 | 1:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLASO CAJA QUEMADA EN C/L | P22123100080 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2022-12-31 | 8400 | keep | 0 | Dec | 2022 | 0.0057212 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-12-31 20:37 | 2022-12-31 21:28 | 20 | 0:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 C/L SE REMPLAZO PORTAFUSIBLES | R22123100104 | New_Event | Cutout Failure | Include | Include | Equipment | 51 | 2022-12-31 | 1020 | keep | 0 | Dec | 2022 | 0.00069472 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-12-31 21:53 | 2022-12-31 21:55 | 3296 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22123100154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-12-31 | 6592 | keep | 0 | Dec | 2022 | 0.0044898 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2022-12-31 22:12 | 2023-01-01 08:56 | 99 | 10:44 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22123100155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 644 | 2022-12-31 | 63756 | keep | 0 | Dec | 2022 | 0.043424 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
BAYAMON | 2022-12-31 22:16 | 2023-01-01 05:54 | 4 | 7:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR SE REPARO PUENTE DE CAJA A TRANSFORMADOR | B22123100119 | New_Event | Primary Wire Break | Include | Include | Equipment | 458 | 2022-12-31 | 1832 | keep | 0 | Dec | 2022 | 0.0012478 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-12-31 22:18 | 2022-12-31 22:19 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 1206-02 | S22123100053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-31 | 338 | keep | 0 | Dec | 2022 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2022-12-31 22:18 | 2022-12-31 22:19 | 733 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR CARGA POR EL 1206-01 | S22123100053 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-31 | 733 | keep | 0 | Dec | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-12-31 22:30 | 2023-01-01 09:26 | 115 | 10:56 | P | NO SE REPORTO CAUSA | 1X40 EN PROVICIONAL AEREO | S22123100054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 656 | 2022-12-31 | 75440 | keep | 0 | Dec | 2022 | 0.051382 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
CAGUAS | 2022-12-31 22:47 | 2023-01-01 09:58 | 30 | 11:11 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y CERRO C/L | C22123100146 | New_Event | Primary Wire Break | Include | Include | Equipment | 671 | 2022-12-31 | 20130 | keep | 0 | Dec | 2022 | 0.01371 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-12-31 23:14 | 2022-12-31 23:15 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 85% DE LA CARGA POR EL 1206-03 EN SERVICIO | S2212310000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2022-12-31 | 8679 | keep | 0 | Dec | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-12-31 23:14 | 2022-12-31 23:15 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA 85% DE LA CARGA DEL 1204-05 EN SERVICIO | S2212310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-12-31 | 4133 | keep | 0 | Dec | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
CANOVANAS | 2023-01-01 00:23 | 2023-01-01 03:39 | 40 | 3:16 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LIENEA SE REEMPLAZO POSTE PARTIDO POSTE PARTIDO POR IMPACTO DE VEHICULO | R23010100001 | New_Event | Damage From Public | Include | Include | Public | 196 | 2023-01-01 | 7840 | keep | 0 | Jan | 2023 | 0.0053398 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-01-01 00:30 | 2023-01-01 13:27 | 20 | 12:57 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L MAL TIEMPO RAYOS | B23010100002 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 777 | 2023-01-01 | 15540 | keep | 0 | Jan | 2023 | 0.010584 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-01 00:34 | 2023-01-01 08:51 | 214 | 8:17 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZARON 2 X 100 EN C/L SE REPARO PUENTE PRIMARIO | B23010100003 | New_Event | Primary Wire Break | Include | Include | Equipment | 497 | 2023-01-01 | 106358 | keep | 0 | Jan | 2023 | 0.07244 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
BAYAMON | 2023-01-01 00:40 | 2023-01-01 03:24 | 359 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA LEVANTAR ALAMBRE PRIMARIO | S23010100003 | New_Event | Primary Wire Break | Include | Include | Equipment | 164 | 2023-01-01 | 58876 | keep | 0 | Jan | 2023 | 0.0401 | 0.00024451 | Sustained | FALSE | FALSE | Not_TMED_Event | 359
GUAYAMA | 2023-01-01 00:50 | 2023-01-01 08:21 | 10 | 7:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO DE TRANSFORMADOR | P23010100005 | New_Event | Primary Wire Break | Include | Include | Equipment | 451 | 2023-01-01 | 4510 | keep | 0 | Jan | 2023 | 0.0030717 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-01-01 02:13 | 2023-01-01 09:14 | 142 | 7:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23010100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 421 | 2023-01-01 | 59782 | keep | 0 | Jan | 2023 | 0.040717 | 9.6716e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 142
SAN JUAN | 2023-01-01 03:18 | 2023-01-01 03:19 | 1681 | 0:01 | T | DESGANCHE | DISPARO INTERRUPTOR 1303-04 SU CARGA ESTA POR 1303-05 PERO BKR LLEVA EL 1303-01 Y 1346-06 CERRADO POR CONTROL | S2301010000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-01 | 1681 | keep | 0 | Jan | 2023 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-01-01 03:18 | 2023-01-01 03:19 | 1598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1303-04 SU CARGA ESTA POR 1303-05 PERO BKR LLEVA EL 1303-01 Y 1346-06 CERRADO POR CONTROL | S2301010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-01 | 1598 | keep | 0 | Jan | 2023 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
CANOVANAS | 2023-01-01 03:34 | 2023-01-01 03:35 | 3046 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR 1646-03 LLEVA LA CARGA DEL 1647-10 Y 25% DEL 1647-09 | R2301010000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-01 | 3046 | keep | 0 | Jan | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-01-01 03:34 | 2023-01-01 03:35 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR EN SERVICIO 25% DE LA CARGA POR EL 1646-03 | R2301010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-01 | 513 | keep | 0 | Jan | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
CANOVANAS | 2023-01-01 03:34 | 2023-01-01 03:35 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR EN SERVICIO CARGA POR EL 1646-03 | R2301010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-01 | 61 | keep | 0 | Jan | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2023-01-01 03:35 | 2023-01-01 09:15 | 113 | 5:40 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | R23010100004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 340 | 2023-01-01 | 38420 | keep | 0 | Jan | 2023 | 0.026168 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
CANOVANAS | 2023-01-01 03:39 | 2023-01-01 03:40 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23010100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-01 | 4188 | keep | 0 | Jan | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2023-01-01 03:40 | 2023-01-01 15:03 | 40 | 11:23 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PARTIDO POSTE PARTIDO POR IMPACTO DE VEHICULO | R23010100001 | Partial_restoration | Damage From Public | Include | Include | Public | 683 | 2023-01-01 | 27320 | keep | 0 | Jan | 2023 | 0.018608 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-01 04:05 | 2023-01-01 05:13 | 1681 | 1:08 | T | DESGANCHE | DISPARO INTERRUPTOR 1303-04 PERO SU CARGA POR EL 1303-05, LLEVA EL 1303-01 Y 1346-06. SE HICIERON OPERACIONES CON SWITCHING SJ-230101-01. SE SECCIONALIZO CON 90% EN SERVICIO EL 1303-01 Y 100% EL 1346-06. | S23010100007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-01-01 | 114308 | keep | 0 | Jan | 2023 | 0.077855 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-01-01 04:05 | 2023-01-01 05:13 | 1598 | 1:08 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1303-04 PERO SU CARGA POR EL 1303-05, LLEVA EL 1303-01 Y 1346-06. SE HICIERON OPERACIONES CON SWITCHING SJ-230101-01. SE SECCIONALIZO CON 90% EN SERVICIO EL 1303-01 Y 100% EL 1346-06. | S23010100007 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 68 | 2023-01-01 | 108664 | keep | 0 | Jan | 2023 | 0.074011 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
CAGUAS | 2023-01-01 04:09 | 2023-01-01 10:44 | 58 | 6:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | C23010100007 | New_Event | Cutout Failure | Include | Include | Equipment | 395 | 2023-01-01 | 22910 | keep | 0 | Jan | 2023 | 0.015604 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2023-01-01 05:05 | 2023-01-01 11:18 | 46 | 6:13 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE RETIRO RAMA DE LA LINEA | B23010100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2023-01-01 | 17158 | keep | 0 | Jan | 2023 | 0.011686 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
SAN JUAN | 2023-01-01 05:13 | 2023-01-01 07:09 | 168 | 1:56 | P | DESGANCHE | DISPARO INTERRUPTOR 1303-04 PERO SU CARGA POR EL 1303-05, LLEVA EL 1303-01 Y 1346-06. SE HICIERON OPERACIONES CON SWITCHING SJ-230101-01. ENTRTO EL 10% QUE FALTABA | S23010100007 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-01-01 | 19488 | keep | 0 | Jan | 2023 | 0.013273 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-01 05:28 | 2023-01-01 10:44 | 150 | 5:16 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZA BAJANTE DE LINEA PRIMARIA A CAJA EN CORTE DE LINEA | A23010100003 | New_Event | Primary Wire Break | Include | Include | Equipment | 316 | 2023-01-01 | 47400 | keep | 0 | Jan | 2023 | 0.032284 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-01-01 05:34 | 2023-01-01 07:48 | 25 | 2:14 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23010100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-01-01 | 3350 | keep | 0 | Jan | 2023 | 0.0022817 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-01-01 05:38 | 2023-01-01 11:12 | 71 | 5:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO CAJA AVERIADA | C23010100010 | New_Event | Cutout Failure | Include | Include | Equipment | 334 | 2023-01-01 | 23714 | keep | 0 | Jan | 2023 | 0.016151 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
HUMACAO | 2023-01-01 06:14 | 2023-01-01 06:16 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23010100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-01 | 4252 | keep | 0 | Jan | 2023 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2023-01-01 06:29 | 2023-01-01 12:00 | 15 | 5:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A23010100006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 331 | 2023-01-01 | 4965 | keep | 0 | Jan | 2023 | 0.0033816 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-01-01 07:06 | 2023-01-01 14:30 | 31 | 7:24 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23010100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2023-01-01 | 13764 | keep | 0 | Jan | 2023 | 0.0093746 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-01-01 07:09 | 2023-01-01 07:23 | 12 | 0:14 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23010100007 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 14 | 2023-01-01 | 168 | keep | 0 | Jan | 2023 | 0.00011442 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-01 07:22 | 2023-01-01 12:05 | 130 | 4:43 | P | CABLE SOTERRADO AVERIADO | 1 X 50 Y 1 X 30 EN AEREOS PROVISIONALES AVERIA VIEJA DEL T-117 AL T-118, AVERIA NUEVA DEL T-119 AL T-119A | B23010100008 | New_Event | UG Cable Fault | Include | Include | Equipment | 283 | 2023-01-01 | 36790 | keep | 0 | Jan | 2023 | 0.025058 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
GUAYAMA | 2023-01-01 07:22 | 2023-01-01 10:09 | 5 | 2:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | P23010100012 | New_Event | Primary Wire Break | Include | Include | Equipment | 167 | 2023-01-01 | 835 | keep | 0 | Jan | 2023 | 0.00056871 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-01 07:43 | 2023-01-01 12:43 | 12 | 5:00 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B23010100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 300 | 2023-01-01 | 3600 | keep | 0 | Jan | 2023 | 0.0024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-01 07:45 | 2023-01-01 10:12 | 74 | 2:27 | P | CAUSAS EXTERNAS | 2 X 80 EN CORTE DE LINES CRUCE POR GLOBO | B23010100010 | New_Event | Damage From Public | Include | Include | Public | 147 | 2023-01-01 | 10878 | keep | 0 | Jan | 2023 | 0.007409 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
GUAYAMA | 2023-01-01 08:02 | 2023-01-01 09:26 | 25 | 1:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P23010100015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-01-01 | 2100 | keep | 0 | Jan | 2023 | 0.0014303 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-01-01 08:14 | 2023-01-01 08:15 | 3025 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE BKR | C2301010000X | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-01 | 3025 | keep | 0 | Jan | 2023 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2023-01-01 08:15 | 2023-01-01 14:47 | 169 | 6:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO DISCO Y HERRAJE NO FUNDIO | C23010100036 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 392 | 2023-01-01 | 66248 | keep | 0 | Jan | 2023 | 0.045121 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
GUAYAMA | 2023-01-01 09:02 | 2023-01-01 11:44 | 5 | 2:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES EN SECUNDARIA | P23010100019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 162 | 2023-01-01 | 810 | keep | 0 | Jan | 2023 | 0.00055169 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-01-01 09:07 | 2023-01-01 10:46 | 1 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R23010100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2023-01-01 | 99 | keep | 0 | Jan | 2023 | 6.7428e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-01-01 09:10 | 2023-01-01 10:12 | 25 | 1:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L Y PORTAFUSIBLE | R23010100006 | New_Event | Cutout Failure | Include | Include | Equipment | 62 | 2023-01-01 | 1550 | keep | 0 | Jan | 2023 | 0.0010557 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-01-01 09:31 | 2023-01-01 09:32 | 490 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL EL 81% DE SU CARGA ESTA POR 2403-02 | R23010100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-01 | 490 | keep | 0 | Jan | 2023 | 0.00033374 | 0.00033374 | Momentary | FALSE | FALSE | Not_TMED_Event | 490
CANOVANAS | 2023-01-01 09:38 | 2023-01-01 11:00 | 30 | 1:22 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | R23010100010 | New_Event | Animals | Include | Include | Wildlife | 82 | 2023-01-01 | 2460 | keep | 0 | Jan | 2023 | 0.0016755 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-01-01 09:38 | 2023-01-01 12:36 | 150 | 2:58 | P | ANIMAL | 1 X 65 Y 1 X 40 EN C/L CRUCE X AVE | C23010100040 | New_Event | Animals | Include | Include | Wildlife | 178 | 2023-01-01 | 26700 | keep | 0 | Jan | 2023 | 0.018185 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-01-01 09:45 | 2023-01-01 10:15 | 6 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REMPLAZAO CONEXIONES EN LOS BAJANTES SECUNDARIOS | M22123000104 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-01-01 | 180 | keep | 0 | Jan | 2023 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-01 09:49 | 2023-01-01 17:36 | 60 | 7:47 | P | TERMINACION SOTERRADA AVERIADA | 2 X 65 EN RISER @ SU-1 SE REPARARON TERMINACIONES | S23010100047 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 467 | 2023-01-01 | 28020 | keep | 0 | Jan | 2023 | 0.019084 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-01-01 09:56 | 2023-01-01 16:26 | 40 | 6:30 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23010100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2023-01-01 | 15600 | keep | 0 | Jan | 2023 | 0.010625 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-01-01 10:39 | 2023-01-01 12:15 | 15 | 1:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN CL NO SE ENCONTRO CAUSA | A23010100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2023-01-01 | 1440 | keep | 0 | Jan | 2023 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-01-01 10:42 | 2023-01-01 12:25 | 1 | 1:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN CL NO SE ENCONTRO CAUSA | A23010100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2023-01-01 | 103 | keep | 0 | Jan | 2023 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-01-01 10:43 | 2023-01-01 11:37 | 16 | 0:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA | R23010100014 | New_Event | Cutout Failure | Include | Include | Equipment | 54 | 2023-01-01 | 864 | keep | 0 | Jan | 2023 | 0.00058847 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2023-01-01 10:47 | 2023-01-02 13:58 | 3 | 27:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23010100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1631 | 2023-01-01 | 4893 | keep | 0 | Jan | 2023 | 0.0033326 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-01-01 11:17 | 2023-01-01 11:18 | 1843 | 0:01 | T | DESGANCHE | RECIERRE | C23010100050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-01 | 1843 | keep | 0 | Jan | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-01-01 11:18 | 2023-01-01 16:41 | 400 | 5:23 | P | DESGANCHE | 2 X 140 EN C/L DESGANCHE | C23010100051 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 323 | 2023-01-01 | 129200 | keep | 0 | Jan | 2023 | 0.087998 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
PONCE | 2023-01-01 11:20 | 2023-01-01 12:15 | 190 | 0:55 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEA ARRIADA | P23010100026 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 55 | 2023-01-01 | 10450 | keep | 0 | Jan | 2023 | 0.0071174 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
GUAYAMA | 2023-01-01 11:29 | 2023-01-01 14:07 | 3 | 2:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO SECUNDARIA | P23010100027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 158 | 2023-01-01 | 474 | keep | 0 | Jan | 2023 | 0.00032284 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-01-01 11:36 | 2023-01-01 12:50 | 11 | 1:14 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | B23010100019 | New_Event | Animals | Include | Include | Wildlife | 74 | 2023-01-01 | 814 | keep | 0 | Jan | 2023 | 0.00055441 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2023-01-01 11:49 | 2023-01-01 12:20 | 10 | 0:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23010100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 31 | 2023-01-01 | 310 | keep | 0 | Jan | 2023 | 0.00021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-01-01 11:58 | 2023-01-01 14:20 | 6 | 2:22 | P | DESGANCHE | 2 X 5 EN TRANSFORMADOR SE RETIRO ENREDADERA DE LAS CAJAS DEL TRANSFORMADOR | M23010100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-01-01 | 852 | keep | 0 | Jan | 2023 | 0.00058029 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-01-01 12:05 | 2023-01-01 20:23 | 20 | 8:18 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN C/L SE PREPARO PROVISIONAL @ T-123 | B23010100022 | New_Event | UG Cable Fault | Include | Include | Equipment | 498 | 2023-01-01 | 9960 | keep | 0 | Jan | 2023 | 0.0067837 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-01 12:52 | 2023-01-01 12:53 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S23010100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-01 | 2203 | keep | 0 | Jan | 2023 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2023-01-01 12:53 | 2023-01-01 19:58 | 12 | 7:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23010100076 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 425 | 2023-01-01 | 5100 | keep | 0 | Jan | 2023 | 0.0034736 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-01 12:59 | 2023-01-01 13:00 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23010100059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-01 | 4291 | keep | 0 | Jan | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
VEGA BAJA | 2023-01-01 13:01 | 2023-01-01 15:01 | 6 | 2:00 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23010100023 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 120 | 2023-01-01 | 720 | keep | 0 | Jan | 2023 | 0.00049039 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-01-01 13:05 | 2023-01-01 15:25 | 10 | 2:20 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN TRANSFORMADOR POSIBLE TRANSFORMADR AVERIADO SE REFIERE A CAMBIO TODO CON SERVICIO | P23010100032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 140 | 2023-01-01 | 1400 | keep | 0 | Jan | 2023 | 0.00095353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-01-01 13:08 | 2023-01-01 20:00 | 7 | 6:52 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA 2.4/4.16 KV AVERIADO | A23010100024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 412 | 2023-01-01 | 2884 | keep | 0 | Jan | 2023 | 0.0019643 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-01-01 13:26 | 2023-01-01 18:48 | 50 | 5:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | HACIENDO PRUEBA EN C/L DISPARO ALIMENTADOR | S23010100061 | New_Event | Cutout Failure | Include | Include | Equipment | 322 | 2023-01-01 | 16100 | keep | 0 | Jan | 2023 | 0.010966 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-01 13:32 | 2023-01-01 13:33 | 3941 | 0:01 | T | ANIMAL | RECIERRE | B2301010025 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-01 | 3941 | keep | 0 | Jan | 2023 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2023-01-01 13:33 | 2023-01-02 08:42 | 20 | 19:09 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | B23010100088 | 1st_after_momentary | Animals | Include | Include | Wildlife | 1149 | 2023-01-01 | 22980 | keep | 0 | Jan | 2023 | 0.015652 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-01 14:08 | 2023-01-01 14:09 | 225 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1303-05 LLEVA 1303-04 | S2301010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-01 | 225 | keep | 0 | Jan | 2023 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-01-01 14:08 | 2023-01-01 14:09 | 870 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR 1303-05 LLEVA 1303-04 | S2301010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-01 | 870 | keep | 0 | Jan | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2023-01-01 14:11 | 2023-01-01 14:57 | 40 | 0:46 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA POR GLOBO DE HELIO | P23010100035 | New_Event | Damage From Public | Include | Include | Public | 46 | 2023-01-01 | 1840 | keep | 0 | Jan | 2023 | 0.0012532 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-01-01 14:21 | 2023-01-01 14:22 | 1245 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23010100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-01 | 1245 | keep | 0 | Jan | 2023 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
CANOVANAS | 2023-01-01 14:26 | 2023-01-01 14:27 | 1051 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR CERRADO X CONTROL | R2301010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-01 | 1051 | keep | 0 | Jan | 2023 | 0.00071583 | 0.00071583 | Momentary | FALSE | FALSE | Not_TMED_Event | 1051
BAYAMON | 2023-01-01 14:36 | 2023-01-01 14:37 | 302 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE BKR CERRADO X CONTROL | B2301010000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-01 | 302 | keep | 0 | Jan | 2023 | 0.00020569 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2023-01-01 14:39 | 2023-01-01 18:32 | 302 | 3:53 | T | CONDUCTOR ARRIADO O CRUZADO | CONDUCTOR CRUZADO BY-230101-01 | B23010100026 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 233 | 2023-01-01 | 70366 | keep | 0 | Jan | 2023 | 0.047926 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
VEGA BAJA | 2023-01-01 14:39 | 2023-01-01 14:40 | 3332 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE BKR | B2301010000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-01-01 | 3332 | keep | 0 | Jan | 2023 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2023-01-01 14:40 | 2023-01-01 17:51 | 30 | 3:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN C/L SE REMPLAZO CAJA | B23010100056 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 191 | 2023-01-01 | 5730 | keep | 0 | Jan | 2023 | 0.0039027 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-01-01 14:46 | 2023-01-01 14:47 | 574 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 574 | keep | 0 | Jan | 2023 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2023-01-01 14:46 | 2023-01-01 14:47 | 2493 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 2493 | keep | 0 | Jan | 2023 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2023-01-01 14:46 | 2023-01-01 14:47 | 1415 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 1415 | keep | 0 | Jan | 2023 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2023-01-01 14:46 | 2023-01-01 14:47 | 1428 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 1428 | keep | 0 | Jan | 2023 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2023-01-01 14:46 | 2023-01-01 14:47 | 1036 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 1036 | keep | 0 | Jan | 2023 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2023-01-01 14:46 | 2023-01-01 14:47 | 382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 382 | keep | 0 | Jan | 2023 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-01-01 14:46 | 2023-01-01 14:47 | 39 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 39 | keep | 0 | Jan | 2023 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2023-01-01 14:46 | 2023-01-01 14:47 | 2366 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 2366 | keep | 0 | Jan | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
AGUADILLA | 2023-01-01 14:46 | 2023-01-01 14:47 | 1337 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 1337 | keep | 0 | Jan | 2023 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-01-01 14:46 | 2023-01-01 14:47 | 709 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23010100018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 709 | keep | 0 | Jan | 2023 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
ARECIBO | 2023-01-01 14:50 | 2023-01-02 09:08 | 1 | 18:18 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23010100029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1098 | 2023-01-01 | 1098 | keep | 0 | Jan | 2023 | 0.00074784 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-01 14:53 | 2023-01-01 15:42 | 20 | 0:49 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R23010100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2023-01-01 | 980 | keep | 0 | Jan | 2023 | 0.00066747 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-01-01 15:00 | 2023-01-01 15:42 | 8 | 0:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23010100096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 42 | 2023-01-01 | 336 | keep | 0 | Jan | 2023 | 0.00022885 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-01-01 15:02 | 2023-01-01 17:40 | 129 | 2:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A23010100032 | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2023-01-01 | 20382 | keep | 0 | Jan | 2023 | 0.013882 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
BAYAMON | 2023-01-01 15:14 | 2023-01-01 16:06 | 88 | 0:52 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23010100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2023-01-01 | 4576 | keep | 0 | Jan | 2023 | 0.0031167 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
VEGA BAJA | 2023-01-01 15:24 | 2023-01-01 15:25 | 2610 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE BKR CERRADO X CONTROL | B2301010000X | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1 | 2023-01-01 | 2610 | keep | 0 | Jan | 2023 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
AGUADILLA | 2023-01-01 15:28 | 2023-01-01 19:10 | 1617 | 3:42 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LA LINEA 2000 Y SE TRANSFIRIO LA SUBESTACION A LA LINEA 1500 | M23010100020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 222 | 2023-01-01 | 358974 | keep | 0 | Jan | 2023 | 0.2445 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2023-01-01 15:28 | 2023-01-01 19:10 | 1017 | 3:42 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LA LINEA 2000 Y SE TRANSFIRIO LA SUBESTACION A LA LINEA 1500 | M23010100020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 222 | 2023-01-01 | 225774 | keep | 0 | Jan | 2023 | 0.15377 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2023-01-01 15:28 | 2023-01-01 19:10 | 828 | 3:42 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LA LINEA 2000 Y SE TRANSFIRIO LA SUBESTACION A LA LINEA 1500 | M23010100020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 222 | 2023-01-01 | 183816 | keep | 0 | Jan | 2023 | 0.1252 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2023-01-01 15:28 | 2023-01-01 17:06 | 863 | 1:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA MISMA Y SE ENERGIZO POR LA LINEA 1500 | M23010100021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2023-01-01 | 84574 | keep | 0 | Jan | 2023 | 0.057603 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2023-01-01 15:28 | 2023-01-01 17:06 | 309 | 1:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA MISMA Y SE ENERGIZO POR LA LINEA 1500 | M23010100021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2023-01-01 | 30282 | keep | 0 | Jan | 2023 | 0.020625 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2023-01-01 15:28 | 2023-01-01 17:06 | 176 | 1:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA MISMA Y SE ENERGIZO POR LA LINEA 1500 | M23010100021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2023-01-01 | 17248 | keep | 0 | Jan | 2023 | 0.011748 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2023-01-01 15:28 | 2023-01-01 17:06 | 108 | 1:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA MISMA Y SE ENERGIZO POR LA LINEA 1500 | M23010100022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2023-01-01 | 10584 | keep | 0 | Jan | 2023 | 0.0072087 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2023-01-01 15:28 | 2023-01-01 17:06 | 974 | 1:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 SE SECCIONALIZO LA MISMA Y SE ENERGIZO POR LA LINEA 1500 | M23010100023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2023-01-01 | 95452 | keep | 0 | Jan | 2023 | 0.065012 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
UTUADO | 2023-01-01 15:32 | 2023-01-01 19:35 | 50 | 4:03 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CL DESCARGAS ELECTRICAS | A23010100036 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 243 | 2023-01-01 | 12150 | keep | 0 | Jan | 2023 | 0.0082753 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-01 16:11 | 2023-01-01 16:40 | 15 | 0:29 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S23010100083 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 29 | 2023-01-01 | 435 | keep | 0 | Jan | 2023 | 0.00029628 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-01 16:14 | 2023-01-01 17:20 | 75 | 1:06 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23010100039 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-01-01 | 4950 | keep | 0 | Jan | 2023 | 0.0033714 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-01-01 16:31 | 2023-01-01 18:18 | 5961 | 1:47 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR 1713-05 LLEVA 95% 1717-02 BY-230101-02 | B23010100097 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 107 | 2023-01-01 | 637827 | keep | 0 | Jan | 2023 | 0.43442 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2023-01-01 16:31 | 2023-01-01 18:18 | 865 | 1:47 | P | ALIMENTADOR AMARRADO | 95% DE SU CARGA X 1713-05 BY-230101-02 | B23010100097 | New_Event | Feeder Load Transferred | Include | Include | Other | 107 | 2023-01-01 | 92555 | keep | 0 | Jan | 2023 | 0.063039 | 0.00058915 | Sustained | FALSE | FALSE | Not_TMED_Event | 865
YAUCO | 2023-01-01 17:00 | 2023-01-01 20:25 | 16 | 3:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO DOS CAJAS AVERIADAS Y PARARRAYOS EN TRANSFORMADOR | M23010100056 | New_Event | Cutout Failure | Include | Include | Equipment | 205 | 2023-01-01 | 3280 | keep | 0 | Jan | 2023 | 0.002234 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2023-01-01 17:00 | 2023-01-02 08:17 | 5 | 15:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE TRANSFORMADOR | A23010100050 | New_Event | Primary Wire Break | Include | Include | Equipment | 917 | 2023-01-01 | 4585 | keep | 0 | Jan | 2023 | 0.0031228 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-01-01 17:06 | 2023-01-01 17:07 | 1253 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23010100066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 1253 | keep | 0 | Jan | 2023 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2023-01-01 17:06 | 2023-01-01 17:07 | 1266 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23010100066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 1266 | keep | 0 | Jan | 2023 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2023-01-01 17:06 | 2023-01-01 17:07 | 411 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23010100066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-01 | 411 | keep | 0 | Jan | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
HUMACAO | 2023-01-01 18:10 | 2023-01-01 19:17 | 40 | 1:07 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23010100106 | New_Event | Animals | Include | Include | Wildlife | 67 | 2023-01-01 | 2680 | keep | 0 | Jan | 2023 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-01 18:13 | 2023-01-01 23:00 | 482 | 4:47 | P | DESGANCHE | 1 X 65 EN C/L | B23010100334 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2023-01-01 | 138334 | keep | 0 | Jan | 2023 | 0.094219 | 0.00032829 | Sustained | FALSE | FALSE | Not_TMED_Event | 482
BAYAMON | 2023-01-01 18:18 | 2023-01-01 18:51 | 3576 | 0:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR HAY UN 65% EN SERVICIO BY-230101-02 | B23010100097 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 33 | 2023-01-01 | 118008 | keep | 0 | Jan | 2023 | 0.080375 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-01-01 18:18 | 2023-01-01 19:21 | 17 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO SECUNDARIA | P23010100058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2023-01-01 | 1071 | keep | 0 | Jan | 2023 | 0.00072945 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-01-01 18:23 | 2023-01-01 18:48 | 785 | 0:25 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RETEZAR NEUTRAL PRIMARIO DEL 13KV ENTRE LAS FASES DEL 8KV | B23010100341 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 25 | 2023-01-01 | 19625 | keep | 0 | Jan | 2023 | 0.013366 | 0.00053466 | Sustained | FALSE | FALSE | Not_TMED_Event | 785
MAYAGÃœEZ | 2023-01-01 18:26 | 2023-01-02 12:35 | 50 | 18:09 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CL Y SE CIERRA PUENTE PRIMARIO | M23010100088 | New_Event | Primary Wire Break | Include | Include | Equipment | 1089 | 2023-01-01 | 54450 | keep | 0 | Jan | 2023 | 0.037086 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-01-01 18:29 | 2023-01-01 23:17 | 300 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | 1 X 140 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23010100090 | New_Event | Primary Wire Break | Include | Include | Equipment | 288 | 2023-01-01 | 86400 | keep | 0 | Jan | 2023 | 0.058847 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2023-01-01 18:31 | 2023-01-01 19:21 | 61 | 0:50 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | R23010100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2023-01-01 | 3050 | keep | 0 | Jan | 2023 | 0.0020773 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2023-01-01 18:34 | 2023-01-02 08:21 | 57 | 13:47 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23010100367 | New_Event | Vegetation Contact | Include | Include | Vegetation | 827 | 2023-01-01 | 47139 | keep | 0 | Jan | 2023 | 0.032106 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2023-01-01 18:37 | 2023-01-01 21:50 | 60 | 3:13 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23010100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2023-01-01 | 11580 | keep | 0 | Jan | 2023 | 0.0078871 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-01 18:48 | 2023-01-01 18:56 | 1106 | 0:08 | P | ALIMENTADOR AMARRADO | DISPARO BKR 1529-15 QUE LLEVA 60% DEL 1346-02, PERSONAL HACIENDO PRUEBA. SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA CAJA QUEMADA | S23010100061 | New_Event | Feeder Load Transferred | Include | Include | Other | 8 | 2023-01-01 | 8848 | keep | 0 | Jan | 2023 | 0.0060263 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-01-01 18:48 | 2023-01-01 18:56 | 1802 | 0:08 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO BKR 1529-15 QUE LLEVA 60% DEL 1346-02, PERSONAL HACIENDO PRUEBA. SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA CAJA QUEMADA | S23010100061 | Additional_clients | Cutout Failure | Include | Include | Equipment | 8 | 2023-01-01 | 14416 | keep | 0 | Jan | 2023 | 0.0098187 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-01 18:51 | 2023-01-01 18:54 | 5961 | 0:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR 1713-05 ENTRO UN 40% EN SERVICIO LLEVA 95% 1717-02 BY-230101-02 | B23010100097 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2023-01-01 | 17883 | keep | 0 | Jan | 2023 | 0.01218 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-01 18:51 | 2023-01-01 18:54 | 865 | 0:03 | P | ALIMENTADOR AMARRADO | 95% DE SU CARGA X 1713-05 100% EN SERVICIO BY-230101-02 | B23010100097 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-01 | 2595 | keep | 0 | Jan | 2023 | 0.0017674 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-01 18:54 | 2023-01-01 20:37 | 3576 | 1:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y SE CERRO MACHETE ENTRO EL 60% RESTANTE BY-230101-02 | B23010100097 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 103 | 2023-01-01 | 368328 | keep | 0 | Jan | 2023 | 0.25087 | 0.0024356 | Sustained | FALSE | FALSE | Not_TMED_Event | 3576
SAN JUAN | 2023-01-01 18:56 | 2023-01-01 19:29 | 50 | 0:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | S23010100061 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 33 | 2023-01-01 | 1650 | keep | 0 | Jan | 2023 | 0.0011238 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-01-01 19:04 | 2023-01-01 21:16 | 8 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23010100101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2023-01-01 | 1056 | keep | 0 | Jan | 2023 | 0.00071924 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-01 19:17 | 2023-01-01 19:18 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23010100106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-01 | 990 | keep | 0 | Jan | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BARRANQUITAS | 2023-01-01 20:22 | 2023-01-02 09:35 | 1 | 13:13 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | C23010100107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 793 | 2023-01-01 | 793 | keep | 0 | Jan | 2023 | 0.00054011 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-01 21:15 | 2023-01-01 23:59 | 100 | 2:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A23010100053 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2023-01-01 | 16400 | keep | 0 | Jan | 2023 | 0.01117 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-01 21:47 | 2023-01-01 21:48 | 1681 | 0:01 | T | DESGANCHE | DISPARO DE 1303-04(TRANSFERIDO) PERO LLEVA 1303-01 Y 1346-06 | S2301010000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-01 | 1681 | keep | 0 | Jan | 2023 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-01-01 21:47 | 2023-01-01 21:48 | 1598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE 1303-04(TRANSFERIDO) PERO LLEVA 1303-01 Y 1346-06 | S2301010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-01 | 1598 | keep | 0 | Jan | 2023 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2023-01-01 21:51 | 2023-01-01 23:48 | 1681 | 1:57 | T | DESGANCHE | DISPARO DE BKR 1303-04 SE SECCIONALIZO PARA HACER DESGANCHE LLEVA 1303-01 LLEVA 1346-06 SJ-230101-02 | S23010100109 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-01-01 | 196677 | keep | 0 | Jan | 2023 | 0.13396 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-01-01 21:51 | 2023-01-01 23:48 | 1598 | 1:57 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1303-04 SE SECCIONALIZO PARA HACER DESGANCHE LLEVA 1303-01 LLEVA 1346-06 SJ-230101-02 | S23010100109 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 117 | 2023-01-01 | 186966 | keep | 0 | Jan | 2023 | 0.12734 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2023-01-01 22:33 | 2023-01-01 22:35 | 1066 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S2301010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-01 | 2132 | keep | 0 | Jan | 2023 | 0.0014521 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
FAJARDO | 2023-01-01 22:48 | 2023-01-01 22:49 | 2722 | 0:01 | T | DESGANCHE | RECIERRE | R2301010000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-01 | 2722 | keep | 0 | Jan | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2023-01-01 22:49 | 2023-01-02 01:23 | 937 | 2:34 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA DESGANCHE | R23010100041 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-01-01 | 144298 | keep | 0 | Jan | 2023 | 0.098281 | 0.00063819 | Sustained | FALSE | FALSE | Not_TMED_Event | 937
PONCE | 2023-01-01 23:17 | 2023-01-01 23:18 | 396 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-01 | 396 | keep | 0 | Jan | 2023 | 0.00026971 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
MAYAGÃœEZ | 2023-01-01 23:18 | 2023-01-02 08:20 | 100 | 9:02 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M23010100144 | New_Event | Animals | Include | Include | Wildlife | 542 | 2023-01-01 | 54200 | keep | 0 | Jan | 2023 | 0.036915 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-01 23:44 | 2023-01-02 09:36 | 88 | 9:52 | P | DESGANCHE | 1 X 50 C/L Y 1 X 40 EN C/L DESGANCHE | B23010100441 | New_Event | Vegetation Contact | Include | Include | Vegetation | 592 | 2023-01-01 | 52096 | keep | 0 | Jan | 2023 | 0.035482 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
SAN JUAN | 2023-01-01 23:48 | 2023-01-02 16:36 | 168 | 16:48 | P | DESGANCHE | DISPARO DE BKR 1303-04 SE SECCIONALIZO PARA HACER DESGANCHE Y SE REMPLAZO AISLADOR SJ-230101-02 | S23010100109 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1008 | 2023-01-01 | 169344 | keep | 0 | Jan | 2023 | 0.11534 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-01-02 00:19 | 2023-01-02 08:30 | 24 | 8:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | R23010200003 | New_Event | Cutout Failure | Include | Include | Equipment | 491 | 2023-01-02 | 11784 | keep | 0 | Jan | 2023 | 0.008026 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CANOVANAS | 2023-01-02 00:40 | 2023-01-02 00:41 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23010200007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 4085 | keep | 0 | Jan | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-01-02 00:45 | 2023-01-02 10:17 | 15 | 9:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R23010200008 | New_Event | Cutout Failure | Include | Include | Equipment | 572 | 2023-01-02 | 8580 | keep | 0 | Jan | 2023 | 0.0058438 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-02 01:14 | 2023-01-02 01:15 | 414 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 1204-01 LLEVA EL 30% DEL 1204-03 | S2301020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 414 | keep | 0 | Jan | 2023 | 0.00028197 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
BAYAMON | 2023-01-02 01:24 | 2023-01-02 08:50 | 72 | 7:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | B23010200010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 446 | 2023-01-02 | 32112 | keep | 0 | Jan | 2023 | 0.021871 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2023-01-02 06:08 | 2023-01-02 10:08 | 165 | 4:00 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L Y SE REEMPLAZO PARARRAYO | B23010200012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 240 | 2023-01-02 | 39600 | keep | 0 | Jan | 2023 | 0.026971 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
AGUADILLA | 2023-01-02 06:17 | 2023-01-02 09:30 | 50 | 3:13 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23010200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2023-01-02 | 9650 | keep | 0 | Jan | 2023 | 0.0065726 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-01-02 06:20 | 2023-01-02 08:07 | 2 | 1:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A23010200002 | New_Event | Cutout Failure | Include | Include | Equipment | 107 | 2023-01-02 | 214 | keep | 0 | Jan | 2023 | 0.00014575 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-01-02 07:39 | 2023-01-02 09:17 | 3 | 1:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23010200003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2023-01-02 | 294 | keep | 0 | Jan | 2023 | 0.00020024 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-01-02 07:45 | 2023-01-02 10:32 | 73 | 2:47 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23010200016 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-01-02 | 12191 | keep | 0 | Jan | 2023 | 0.0083032 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2023-01-02 08:39 | 2023-01-02 15:20 | 8 | 6:41 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO Y XMR AVERIADO | B23010200024 | New_Event | Primary Pole Failure | Include | Include | Equipment | 401 | 2023-01-02 | 3208 | keep | 0 | Jan | 2023 | 0.002185 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-01-02 08:48 | 2023-01-02 10:49 | 7 | 2:01 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR CRUCE POR CULEBRA | R23010200021 | New_Event | Animals | Include | Include | Wildlife | 121 | 2023-01-02 | 847 | keep | 0 | Jan | 2023 | 0.00057689 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-01-02 08:51 | 2023-01-02 11:17 | 123 | 2:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23010200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2023-01-02 | 17958 | keep | 0 | Jan | 2023 | 0.012231 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
GUAYAMA | 2023-01-02 09:10 | 2023-01-02 09:35 | 37 | 0:25 | P | PARARRAYOS DEFECTUOSO | SE ELIMINO PARARRAYO CRUZADO | P23010200021 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 25 | 2023-01-02 | 925 | keep | 0 | Jan | 2023 | 0.00063001 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
PONCE | 2023-01-02 09:18 | 2023-01-02 11:38 | 21 | 2:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SECUNDARIA EN EL PISO ROTA SE ABRIO TRANSFORMADOR, SE DIVIDIERON CARGAS Y SE CERRO MONTURA | P23010200022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 140 | 2023-01-02 | 2940 | keep | 0 | Jan | 2023 | 0.0020024 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2023-01-02 09:25 | 2023-01-02 11:44 | 150 | 2:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 50 EN C/L | S23010200084 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2023-01-02 | 20850 | keep | 0 | Jan | 2023 | 0.014201 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-01-02 09:45 | 2023-01-02 10:34 | 10 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES QUEMADOS | A23010200008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-01-02 | 490 | keep | 0 | Jan | 2023 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-02 09:59 | 2023-01-02 17:06 | 91 | 7:07 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L CAMION IMPACTO POSTE Y CRUZO LINEAS | B23010200039 | New_Event | Damage From Public | Include | Include | Public | 427 | 2023-01-02 | 38857 | keep | 0 | Jan | 2023 | 0.026465 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
BAYAMON | 2023-01-02 10:24 | 2023-01-02 11:36 | 20 | 1:12 | P | DESGANCHE | 1 X 140 EN C/L DESGANCHE | B23010200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-01-02 | 1440 | keep | 0 | Jan | 2023 | 0.00098078 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-02 10:35 | 2023-01-02 10:36 | 1356 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE CERRO POR CONTROL | S23010200112 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-02 | 1356 | keep | 0 | Jan | 2023 | 0.00092357 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
YAUCO | 2023-01-02 10:35 | 2023-01-02 12:34 | 1 | 1:59 | P | ANIMAL | 1 X 40 EN CL IGUANA | M23010200040 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-01-02 | 119 | keep | 0 | Jan | 2023 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-02 10:36 | 2023-01-02 16:30 | 300 | 5:54 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO Y SE CERRO PUENTE ABIERTO | S23010200188 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 354 | 2023-01-02 | 106200 | keep | 0 | Jan | 2023 | 0.072332 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-01-02 10:36 | 2023-01-02 11:20 | 8 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23010200049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-01-02 | 352 | keep | 0 | Jan | 2023 | 0.00023975 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-01-02 10:38 | 2023-01-02 15:13 | 9 | 4:35 | P | OTRAS CAUSAS | 1 X 15 EN XMR FUSIBLE FATIGADO | C23010200019 | New_Event | Other Causes | Include | Include | Other | 275 | 2023-01-02 | 2475 | keep | 0 | Jan | 2023 | 0.0016857 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-01-02 10:39 | 2023-01-02 13:32 | 45 | 2:53 | P | ANIMAL | 1 X 15 EN PROVISIONAL SE RETIRO AVE | B23010200050 | New_Event | Animals | Include | Include | Wildlife | 173 | 2023-01-02 | 7785 | keep | 0 | Jan | 2023 | 0.0053023 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-01-02 11:20 | 2023-01-02 11:34 | 9 | 0:14 | P | DESGANCHE | 1 X 30 C/L SE REALIZO DESGANCHE | B23010200063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2023-01-02 | 126 | keep | 0 | Jan | 2023 | 8.5818e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2023-01-02 11:40 | 2023-01-02 12:48 | 3 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | C23010200024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2023-01-02 | 204 | keep | 0 | Jan | 2023 | 0.00013894 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-01-02 11:44 | 2023-01-02 12:07 | 414 | 0:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1204-01 QUE LLEVA EL 30% DEL 1204-03 SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S2301020000X | New_Event | Cutout Failure | Include | Include | Equipment | 23 | 2023-01-02 | 9522 | keep | 0 | Jan | 2023 | 0.0064854 | 0.00028197 | Sustained | FALSE | FALSE | Not_TMED_Event | 414
PONCE | 2023-01-02 11:49 | 2023-01-02 13:13 | 25 | 1:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA VIENTOS | P23010200030 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 84 | 2023-01-02 | 2100 | keep | 0 | Jan | 2023 | 0.0014303 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-02 11:59 | 2023-01-02 13:48 | 16 | 1:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | S23010200167 | New_Event | Secondary Wire Break | Include | Include | Equipment | 109 | 2023-01-02 | 1744 | keep | 0 | Jan | 2023 | 0.0011878 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2023-01-02 12:01 | 2023-01-02 12:47 | 6 | 0:46 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVE | P23010200032 | New_Event | Animals | Include | Include | Wildlife | 46 | 2023-01-02 | 276 | keep | 0 | Jan | 2023 | 0.00018798 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-01-02 12:37 | 2023-01-02 15:27 | 1 | 2:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REEMPLAZO PORTAFUSIBLE | S23010200177 | New_Event | Cutout Failure | Include | Include | Equipment | 170 | 2023-01-02 | 170 | keep | 0 | Jan | 2023 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-02 12:48 | 2023-01-02 13:44 | 1180 | 0:56 | T | DESGANCHE | SE REALIZO DESGANCHE CON VARETA DEL PISO Y SE CERRO POR CONTROL | B23010200072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-01-02 | 66080 | keep | 0 | Jan | 2023 | 0.045007 | 0.00080369 | Sustained | FALSE | FALSE | Not_TMED_Event | 1180
AGUADILLA | 2023-01-02 13:00 | 2023-01-02 15:44 | 5 | 2:44 | P | OTRAS CAUSAS | SE ABRO CAJAS EN TRANSFORMADOR PARA FIJARLO EN PERNO | M23010200047 | New_Event | Other Causes | Include | Include | Other | 164 | 2023-01-02 | 820 | keep | 0 | Jan | 2023 | 0.0005585 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-01-02 13:10 | 2023-01-03 14:40 | 10 | 25:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJAS Y HERRAJES | A23010200031 | New_Event | Cutout Failure | Include | Include | Equipment | 1530 | 2023-01-02 | 15300 | keep | 0 | Jan | 2023 | 0.010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-02 13:15 | 2023-01-02 17:27 | 8 | 4:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIR XMR Y SE REPARARON CONEXIONES SECUNDARIAS | B23010200078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 252 | 2023-01-02 | 2016 | keep | 0 | Jan | 2023 | 0.0013731 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-02 13:25 | 2023-01-02 14:28 | 15 | 1:03 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA ELIMINAR POSTE SECUNDARIO SE RELOCALIZO SECUNDARIA | S23010200194 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 63 | 2023-01-02 | 945 | keep | 0 | Jan | 2023 | 0.00064364 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-01-02 13:44 | 2023-01-02 13:45 | 1825 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA TRES OPERACIONES Y QUEDA EN SERVICIO | M23010200059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 1825 | keep | 0 | Jan | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BARRANQUITAS | 2023-01-02 13:49 | 2023-01-02 16:40 | 1 | 2:51 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23010200039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-01-02 | 171 | keep | 0 | Jan | 2023 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-02 14:11 | 2023-01-02 17:30 | 6 | 3:19 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO Y SE REMPLAZO TOMA | C23010200041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 199 | 2023-01-02 | 1194 | keep | 0 | Jan | 2023 | 0.00081323 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-01-02 14:20 | 2023-01-02 16:54 | 114 | 2:34 | P | DESGANCHE | SE HIZO DESGANCHE Y 1 X 65 EN CORTE DE LINEA | P23010200047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-01-02 | 17556 | keep | 0 | Jan | 2023 | 0.011957 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
MAYAGÃœEZ | 2023-01-02 14:22 | 2023-01-02 16:44 | 30 | 2:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CL SE REMPLAZO CAJA PRIMARIA EN CL | M23010200063 | New_Event | Cutout Failure | Include | Include | Equipment | 142 | 2023-01-02 | 4260 | keep | 0 | Jan | 2023 | 0.0029015 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-02 14:35 | 2023-01-02 15:37 | 1 | 1:02 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X 25 EN RISER CONTAMINACION EN TRANSCLOSURE | R23010200031 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 62 | 2023-01-02 | 62 | keep | 0 | Jan | 2023 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-01-02 14:40 | 2023-01-02 16:30 | 4 | 1:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R23010200032 | New_Event | Cutout Failure | Include | Include | Equipment | 110 | 2023-01-02 | 440 | keep | 0 | Jan | 2023 | 0.00029968 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-01-02 14:45 | 2023-01-02 17:32 | 100 | 2:47 | P | ANIMAL | 1 X 80 EN C/L AVE CRUZO LINEAS | B23010200088 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-01-02 | 16700 | keep | 0 | Jan | 2023 | 0.011374 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-02 15:10 | 2023-01-02 17:09 | 10 | 1:59 | P | DESGANCHE | DESGANCHE PRIMARIO Y 1 X 10 EN XMR | S23010200210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-01-02 | 1190 | keep | 0 | Jan | 2023 | 0.0008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-02 15:12 | 2023-01-02 16:15 | 250 | 1:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO Y SE REEMPLAZO AISLADOR | B23010200089 | New_Event | Primary Wire Break | Include | Include | Equipment | 63 | 2023-01-02 | 15750 | keep | 0 | Jan | 2023 | 0.010727 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2023-01-02 15:14 | 2023-01-02 15:15 | 1261 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 1261 | keep | 0 | Jan | 2023 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
CAGUAS | 2023-01-02 15:14 | 2023-01-02 15:15 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 1922 | keep | 0 | Jan | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
UTUADO | 2023-01-02 15:19 | 2023-01-02 15:23 | 934 | 0:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23010200040 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-02 | 3736 | keep | 0 | Jan | 2023 | 0.0025446 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2023-01-02 15:19 | 2023-01-02 15:23 | 4 | 0:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23010200040 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-02 | 16 | keep | 0 | Jan | 2023 | 1.0898e-05 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-01-02 15:19 | 2023-01-02 15:23 | 1479 | 0:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23010200040 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-02 | 5916 | keep | 0 | Jan | 2023 | 0.0040294 | 0.0010073 | Momentary | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2023-01-02 15:19 | 2023-01-02 15:23 | 1841 | 0:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23010200042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-02 | 7364 | keep | 0 | Jan | 2023 | 0.0050156 | 0.0012539 | Momentary | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2023-01-02 15:19 | 2023-01-02 15:23 | 1950 | 0:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23010200042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-02 | 7800 | keep | 0 | Jan | 2023 | 0.0053125 | 0.0013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 1950
BAYAMON | 2023-01-02 15:20 | 2023-01-02 17:50 | 75 | 2:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE CORTE DE LINEA TOTAL PARA REPARAR POSTE PRIMARIO PARTIDO Y XMR AVERIADO | B23010200024 | New_Event | Primary Pole Failure | Include | Include | Equipment | 150 | 2023-01-02 | 11250 | keep | 0 | Jan | 2023 | 0.0076623 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
GUAYAMA | 2023-01-02 15:21 | 2023-01-02 17:02 | 60 | 1:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA DE CORTE DE LINEA | P23010200055 | New_Event | Primary Wire Break | Include | Include | Equipment | 101 | 2023-01-02 | 6060 | keep | 0 | Jan | 2023 | 0.0041274 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-01-02 15:23 | 2023-01-02 15:24 | 810 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23010200070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-02 | 810 | keep | 0 | Jan | 2023 | 0.00055169 | 0.00055169 | Momentary | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2023-01-02 15:23 | 2023-01-02 15:24 | 1235 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23010200070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-02 | 1235 | keep | 0 | Jan | 2023 | 0.00084115 | 0.00084115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2023-01-02 15:23 | 2023-01-02 15:24 | 93 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23010200070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-02 | 93 | keep | 0 | Jan | 2023 | 6.3342e-05 | 6.3342e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2023-01-02 15:23 | 2023-01-02 15:24 | 1825 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23010200070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-02 | 1825 | keep | 0 | Jan | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2023-01-02 15:23 | 2023-01-02 15:24 | 3230 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23010200070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-02 | 3230 | keep | 0 | Jan | 2023 | 0.0021999 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
PONCE | 2023-01-02 15:46 | 2023-01-02 20:28 | 25 | 4:42 | P | DESGANCHE | DESGANCHE 1 X 40 EN CORTE DE LINEA | P23010200056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2023-01-02 | 7050 | keep | 0 | Jan | 2023 | 0.0048017 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-01-02 16:00 | 2023-01-05 12:22 | 1 | 68:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS CLIENTE SIN SERVICIO DESDE EL DIA 2 INFORMO PERSONAL DE CAMPO EVENTOS M23010200030(9:54)Y LUEGO EVENTO M23010200070(15:28) DE DISPARO DE LINEA 5600 | M23010500036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 4102 | 2023-01-02 | 4102 | keep | 0 | Jan | 2023 | 0.0027939 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-01-02 16:04 | 2023-01-02 19:20 | 30 | 3:16 | P | DESGANCHE | RAMA SOBRE LINEA 1 X 50 EN CORTE DE LINEA | P23010200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-01-02 | 5880 | keep | 0 | Jan | 2023 | 0.0040048 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-02 16:10 | 2023-01-02 17:23 | 15 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23010200204 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-01-02 | 1095 | keep | 0 | Jan | 2023 | 0.0007458 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-01-02 16:13 | 2023-01-03 13:00 | 1 | 20:47 | P | ANIMAL | 2 X 20 EN TRANSFORMADOR IGUANA CRUZO FASES | M23010200076 | New_Event | Animals | Include | Include | Wildlife | 1247 | 2023-01-02 | 1247 | keep | 0 | Jan | 2023 | 0.00084933 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-02 16:37 | 2023-01-02 17:59 | 175 | 1:22 | P | ANIMAL | 1 X 140 EN CORTE DE LINEA CRUCE POR AVE | R23010200037 | New_Event | Animals | Include | Include | Wildlife | 82 | 2023-01-02 | 14350 | keep | 0 | Jan | 2023 | 0.0097737 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
CAGUAS | 2023-01-02 16:39 | 2023-01-02 19:16 | 41 | 2:37 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23010200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-01-02 | 6437 | keep | 0 | Jan | 2023 | 0.0043842 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
ARECIBO | 2023-01-02 17:20 | 2023-01-02 19:20 | 50 | 2:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23010200053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-01-02 | 6000 | keep | 0 | Jan | 2023 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-01-02 17:21 | 2023-01-02 20:15 | 38 | 2:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L Y 1 X 50 EN C/L SE CERRO CAJA QUE NO ESTABA BIEN CERRADA | C23010200054 | New_Event | Cutout Failure | Include | Include | Equipment | 174 | 2023-01-02 | 6612 | keep | 0 | Jan | 2023 | 0.0045034 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2023-01-02 17:47 | 2023-01-02 21:19 | 8 | 3:32 | P | TERMINACION SOTERRADA AVERIADA | SE REPARON TERMINACION EN AEREO PROVISIONAL | B23010200115 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 212 | 2023-01-02 | 1696 | keep | 0 | Jan | 2023 | 0.0011551 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-01-02 17:51 | 2023-01-02 20:57 | 30 | 3:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO CAUSA | C23010200070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2023-01-02 | 5580 | keep | 0 | Jan | 2023 | 0.0038005 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-02 17:56 | 2023-01-02 18:56 | 8 | 1:00 | P | CAUSAS EXTERNAS | 1 X 25 EN C/L SE RETIRO GLOBO METALICO | B23010200116 | New_Event | Damage From Public | Include | Include | Public | 60 | 2023-01-02 | 480 | keep | 0 | Jan | 2023 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-01-02 17:57 | 2023-01-02 20:28 | 70 | 2:31 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | M23010200082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-01-02 | 10570 | keep | 0 | Jan | 2023 | 0.0071992 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-01-02 17:59 | 2023-01-02 18:12 | 1 | 0:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B23010200117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2023-01-02 | 13 | keep | 0 | Jan | 2023 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-02 18:29 | 2023-01-03 06:32 | 56 | 12:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23010200076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 723 | 2023-01-02 | 40488 | keep | 0 | Jan | 2023 | 0.027576 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
PONCE | 2023-01-02 18:54 | 2023-01-02 18:55 | 1078 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 1078 | keep | 0 | Jan | 2023 | 0.00073422 | 0.00073422 | Momentary | FALSE | FALSE | Not_TMED_Event | 1078
ARECIBO | 2023-01-02 19:51 | 2023-01-02 21:13 | 80 | 1:22 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23010200069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2023-01-02 | 6560 | keep | 0 | Jan | 2023 | 0.004468 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-01-02 19:55 | 2023-01-02 19:56 | 327 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 2604-01 LLEVA LA CARGA DEL 2603-07 | C2301020000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-02 | 327 | keep | 0 | Jan | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-02 19:55 | 2023-01-02 19:56 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2603-07 | C2301020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 2354 | keep | 0 | Jan | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
CAGUAS | 2023-01-02 20:16 | 2023-01-03 07:40 | 58 | 11:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 65 EN C/L | C23010200091 | New_Event | Cutout Failure | Include | Include | Equipment | 684 | 2023-01-02 | 39672 | keep | 0 | Jan | 2023 | 0.02702 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
VEGA BAJA | 2023-01-02 20:21 | 2023-01-03 10:15 | 15 | 13:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE ENTRADA EN RISER | A23010200103 | New_Event | Primary Wire Break | Include | Include | Equipment | 834 | 2023-01-02 | 12510 | keep | 0 | Jan | 2023 | 0.0085205 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-01-02 21:13 | 2023-01-03 08:15 | 16 | 11:02 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | C23010200100 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 662 | 2023-01-02 | 10592 | keep | 0 | Jan | 2023 | 0.0072142 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
VEGA BAJA | 2023-01-02 21:32 | 2023-01-02 23:26 | 7 | 1:54 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | A23010200122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2023-01-02 | 798 | keep | 0 | Jan | 2023 | 0.00054351 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-01-02 21:44 | 2023-01-02 21:45 | 508 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 508 | keep | 0 | Jan | 2023 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-01-02 21:44 | 2023-01-02 21:45 | 64 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 64 | keep | 0 | Jan | 2023 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
YAUCO | 2023-01-02 21:45 | 2023-01-03 07:40 | 35 | 9:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23010200080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 595 | 2023-01-02 | 20825 | keep | 0 | Jan | 2023 | 0.014184 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2023-01-02 21:55 | 2023-01-02 21:56 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C23010200105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 5630 | keep | 0 | Jan | 2023 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2023-01-02 21:55 | 2023-01-02 21:56 | 2873 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23010200105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 2873 | keep | 0 | Jan | 2023 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
VEGA BAJA | 2023-01-02 22:29 | 2023-01-03 01:41 | 150 | 3:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23010200129 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 192 | 2023-01-02 | 28800 | keep | 0 | Jan | 2023 | 0.019616 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2023-01-02 23:23 | 2023-01-02 23:24 | 1478 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010200086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-02 | 1478 | keep | 0 | Jan | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
VEGA BAJA | 2023-01-03 00:09 | 2023-01-03 07:38 | 150 | 7:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CL SE REMPLAZA CAJA PRIMARIA AVERIADA | A23010300001 | New_Event | Cutout Failure | Include | Include | Equipment | 449 | 2023-01-03 | 67350 | keep | 0 | Jan | 2023 | 0.045872 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-01-03 00:18 | 2023-01-03 13:07 | 1 | 12:49 | P | ANIMAL | 1 X 65 EN C/L IGUANA | S23010300001 | New_Event | Animals | Include | Include | Wildlife | 769 | 2023-01-03 | 769 | keep | 0 | Jan | 2023 | 0.00052376 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-03 03:56 | 2023-01-03 03:57 | 1225 | 0:01 | P | ANIMAL | RECERRO LLEVA 90% DE SU CARGA | B23010300000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-03 | 1225 | keep | 0 | Jan | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
BAYAMON | 2023-01-03 03:57 | 2023-01-03 09:38 | 14 | 5:41 | P | ANIMAL | SE RETIRO GATO EN SU-8A 1 X 40 EN RISER | B23010300004 | 1st_after_momentary | Animals | Include | Include | Wildlife | 341 | 2023-01-03 | 4774 | keep | 0 | Jan | 2023 | 0.0032515 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2023-01-03 04:39 | 2023-01-03 06:45 | 75 | 2:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | P23010300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-01-03 | 9450 | keep | 0 | Jan | 2023 | 0.0064364 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-01-03 04:59 | 2023-01-03 11:15 | 40 | 6:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M23010300002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 376 | 2023-01-03 | 15040 | keep | 0 | Jan | 2023 | 0.010244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-03 05:02 | 2023-01-03 10:21 | 39 | 5:19 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN RISER AVERIA NUEVA DE T-323 @ T-322 Y AVERIA VIEJA DE T-321 @ T-322 | B23010300005 | New_Event | UG Cable Fault | Include | Include | Equipment | 319 | 2023-01-03 | 12441 | keep | 0 | Jan | 2023 | 0.0084735 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
ARECIBO | 2023-01-03 05:40 | 2023-01-03 09:32 | 35 | 3:52 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A23010300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-01-03 | 8120 | keep | 0 | Jan | 2023 | 0.0055305 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-01-03 05:43 | 2023-01-03 05:44 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R2301030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 2039 | keep | 0 | Jan | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
VEGA BAJA | 2023-01-03 06:28 | 2023-01-03 12:00 | 106 | 5:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L SE REEMPLAZO CAJA PRIMARIA | B23010300006 | New_Event | Cutout Failure | Include | Include | Equipment | 332 | 2023-01-03 | 35192 | keep | 0 | Jan | 2023 | 0.023969 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
FAJARDO | 2023-01-03 06:53 | 2023-01-03 08:05 | 103 | 1:12 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | R23010300003 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-01-03 | 7416 | keep | 0 | Jan | 2023 | 0.005051 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
HUMACAO | 2023-01-03 07:38 | 2023-01-03 09:20 | 72 | 1:42 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR PALOMA | C23010300005 | New_Event | Animals | Include | Include | Wildlife | 102 | 2023-01-03 | 7344 | keep | 0 | Jan | 2023 | 0.005002 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
VEGA BAJA | 2023-01-03 07:38 | 2023-01-03 07:39 | 2697 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23010300029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-01-03 | 2697 | keep | 0 | Jan | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-01-03 07:39 | 2023-01-03 08:32 | 150 | 0:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CL SE REMPLAZA CAJA PRIMARIA AVERIADA | A23010300001 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 53 | 2023-01-03 | 7950 | keep | 0 | Jan | 2023 | 0.0054147 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-03 07:39 | 2023-01-03 11:02 | 150 | 3:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CL FUERTE LLUVIA | A23010300021 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 203 | 2023-01-03 | 30450 | keep | 0 | Jan | 2023 | 0.020739 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-01-03 07:47 | 2023-01-03 11:20 | 30 | 3:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 50 EN C/L MAL TIEMPO VIENTOS | C23010300006 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 213 | 2023-01-03 | 6390 | keep | 0 | Jan | 2023 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-03 08:05 | 2023-01-03 10:01 | 1 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L LLUVIA | B23010300016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2023-01-03 | 116 | keep | 0 | Jan | 2023 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-01-03 08:11 | 2023-01-03 12:57 | 80 | 4:46 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23010300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2023-01-03 | 22880 | keep | 0 | Jan | 2023 | 0.015583 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-03 08:26 | 2023-01-03 10:27 | 150 | 2:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S23010300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-01-03 | 18150 | keep | 0 | Jan | 2023 | 0.012362 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-01-03 08:27 | 2023-01-03 10:25 | 12 | 1:58 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESPEJO LINEA Y SE REPARO SECUNDARIA | B23010300021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 118 | 2023-01-03 | 1416 | keep | 0 | Jan | 2023 | 0.00096443 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-03 08:29 | 2023-01-03 08:30 | 1647 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | B23010300022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 1647 | keep | 0 | Jan | 2023 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
ARECIBO | 2023-01-03 08:36 | 2023-01-03 12:48 | 30 | 4:12 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | A23010300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2023-01-03 | 7560 | keep | 0 | Jan | 2023 | 0.0051491 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-01-03 08:54 | 2023-01-03 14:38 | 12 | 5:44 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | C23010300015 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 344 | 2023-01-03 | 4128 | keep | 0 | Jan | 2023 | 0.0028116 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-03 08:55 | 2023-01-03 13:29 | 12 | 4:34 | P | SECUNDARIA/DESGANCHE | 1X 10 EN XMR DESGANCHE SECUNDARIO | S23010300013 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 274 | 2023-01-03 | 3288 | keep | 0 | Jan | 2023 | 0.0022394 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-01-03 08:58 | 2023-01-03 11:44 | 30 | 2:46 | P | DESGANCHE | I X 30 EN CL DESGANCHE | A23010300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-01-03 | 4980 | keep | 0 | Jan | 2023 | 0.0033919 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-03 09:02 | 2023-01-03 12:23 | 46 | 3:21 | P | DESGANCHE | 2 X 80 EN C/L Y SE RALIZO DESGANCHE | S23010300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2023-01-03 | 9246 | keep | 0 | Jan | 2023 | 0.0062974 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
PONCE | 2023-01-03 09:05 | 2023-01-03 12:00 | 22 | 2:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | P23010300021 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 175 | 2023-01-03 | 3850 | keep | 0 | Jan | 2023 | 0.0026222 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2023-01-03 09:23 | 2023-01-03 11:08 | 20 | 1:45 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | M23010300015 | New_Event | Animals | Include | Include | Wildlife | 105 | 2023-01-03 | 2100 | keep | 0 | Jan | 2023 | 0.0014303 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-03 09:30 | 2023-01-03 09:31 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 1709-03 SOLO LLEVANO 50% DE SU CARGA, LLEVA 1709-05 | S2301030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 766 | keep | 0 | Jan | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-01-03 09:30 | 2023-01-03 09:31 | 2364 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE 1709-03 SOLO LLEVANO 50% DE SU CARGA, LLEVA 1709-05 | S2301030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-03 | 2364 | keep | 0 | Jan | 2023 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2023-01-03 09:31 | 2023-01-03 12:22 | 30 | 2:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER @ SU-1 Y 1 X 20 SU-1 HACIA T-9 | S23010300052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2023-01-03 | 5130 | keep | 0 | Jan | 2023 | 0.003494 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-01-03 09:37 | 2023-01-03 12:16 | 45 | 2:39 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23010300021 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-01-03 | 7155 | keep | 0 | Jan | 2023 | 0.0048732 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2023-01-03 09:38 | 2023-01-03 10:40 | 38 | 1:02 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23010300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-01-03 | 2356 | keep | 0 | Jan | 2023 | 0.0016047 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
SAN JUAN | 2023-01-03 09:40 | 2023-01-03 14:00 | 20 | 4:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA | S23010300004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 260 | 2023-01-03 | 5200 | keep | 0 | Jan | 2023 | 0.0035417 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-01-03 09:40 | 2023-01-03 11:45 | 7 | 2:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZA TRANSFORMADOR PM-2 50 KVA A 4.16/2.4 KV DEBIDO A QUE NO REGULA VOLTAJE | A23010300047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 125 | 2023-01-03 | 875 | keep | 0 | Jan | 2023 | 0.00059596 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-01-03 09:53 | 2023-01-03 10:40 | 10 | 0:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23010300007 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2023-01-03 | 470 | keep | 0 | Jan | 2023 | 0.00032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-03 09:53 | 2023-01-03 14:12 | 6 | 4:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | B23010300042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2023-01-03 | 1554 | keep | 0 | Jan | 2023 | 0.0010584 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-01-03 09:58 | 2023-01-03 11:58 | 300 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | M23010300028 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2023-01-03 | 36000 | keep | 0 | Jan | 2023 | 0.024519 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2023-01-03 10:00 | 2023-01-03 15:58 | 60 | 5:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M23010300055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 358 | 2023-01-03 | 21480 | keep | 0 | Jan | 2023 | 0.01463 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-01-03 10:03 | 2023-01-03 11:40 | 7 | 1:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | B23010300046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 97 | 2023-01-03 | 679 | keep | 0 | Jan | 2023 | 0.00046246 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-01-03 10:06 | 2023-01-03 11:38 | 15 | 1:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN CORTE DE LINEA FUERTES VIENTOS | M23010300030 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 92 | 2023-01-03 | 1380 | keep | 0 | Jan | 2023 | 0.00093991 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-03 10:07 | 2023-01-03 12:43 | 154 | 2:36 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23010300022 | New_Event | Primary Wire Break | Include | Include | Equipment | 156 | 2023-01-03 | 24024 | keep | 0 | Jan | 2023 | 0.016363 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
BAYAMON | 2023-01-03 10:21 | 2023-01-04 18:55 | 14 | 32:34 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE A T322 | B23010300005 | New_Event | UG Cable Fault | Include | Include | Equipment | 1954 | 2023-01-03 | 27356 | keep | 0 | Jan | 2023 | 0.018632 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2023-01-03 10:25 | 2023-01-03 12:23 | 3 | 1:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M22122900030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 118 | 2023-01-03 | 354 | keep | 0 | Jan | 2023 | 0.00024111 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-01-03 10:36 | 2023-01-03 14:34 | 179 | 3:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CAJA PRIMARIA DE CORTE DE LINEA PARA FIJAR CAJA PRIMARIA A LA CRUCETA Y SE REPARO NEUTRAL | C23010300033 | New_Event | Cutout Failure | Include | Include | Equipment | 238 | 2023-01-03 | 42602 | keep | 0 | Jan | 2023 | 0.029016 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
BARRANQUITAS | 2023-01-03 10:36 | 2023-01-03 14:00 | 3 | 3:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA | C23010300039 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 204 | 2023-01-03 | 612 | keep | 0 | Jan | 2023 | 0.00041683 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-01-03 11:04 | 2023-01-03 11:19 | 1879 | 0:15 | T | NO SE REPORTO CAUSA | DISPARO DE 3006-02 SE BORRARON BANDERAS SE CERRO POR CONTROL LLEVA EL 3006-05 | C23010300040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2023-01-03 | 28185 | keep | 0 | Jan | 2023 | 0.019197 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-01-03 11:04 | 2023-01-03 11:19 | 3005 | 0:15 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR SE BORRARON BANDERAS SE CERRO POR CONTROL CARGA POR EL 3006-02 | C23010300040 | New_Event | Feeder Load Transferred | Include | Include | Other | 15 | 2023-01-03 | 45075 | keep | 0 | Jan | 2023 | 0.0307 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
CANOVANAS | 2023-01-03 11:39 | 2023-01-03 16:11 | 7 | 4:32 | P | CAUSAS EXTERNAS | SE REPARO Y SE TRANSFIRIO SECUNDARIA A POSTE NUEVO, POSTE SECUNDARIO PARTIDO POR CAMION | R23010300031 | New_Event | Damage From Public | Include | Include | Public | 272 | 2023-01-03 | 1904 | keep | 0 | Jan | 2023 | 0.0012968 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-01-03 11:44 | 2023-01-03 11:46 | 5630 | 0:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE BKR SE CERRO POR CONTROL | C23010300088 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2023-01-03 | 11260 | keep | 0 | Jan | 2023 | 0.0076691 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2023-01-03 11:46 | 2023-01-03 16:32 | 33 | 4:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO DISCO ROTO Y SE CERRO TIERRA DEL POSTE GOI CG-230103-02 | C23010300128 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 286 | 2023-01-03 | 9438 | keep | 0 | Jan | 2023 | 0.0064282 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2023-01-03 12:00 | 2023-01-03 14:07 | 50 | 2:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA FUERTES VIENTOS | M23010300075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 127 | 2023-01-03 | 6350 | keep | 0 | Jan | 2023 | 0.004325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-03 12:03 | 2023-01-03 12:36 | 12 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | C23010300024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-01-03 | 396 | keep | 0 | Jan | 2023 | 0.00026971 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-01-03 12:07 | 2023-01-03 17:03 | 6 | 4:56 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR SECUNDARIA CRUZADA | M23010300058 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 296 | 2023-01-03 | 1776 | keep | 0 | Jan | 2023 | 0.0012096 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-01-03 12:10 | 2023-01-03 12:29 | 1 | 0:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO MONTURA DE TRANSFORMADORES PARA REPARAR BAJANTE ZAFADO DE CAJA A TRANSFORMADOR | M23010300038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 19 | 2023-01-03 | 19 | keep | 0 | Jan | 2023 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-03 12:13 | 2023-01-03 15:43 | 10 | 3:30 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23010300039 | New_Event | Primary Wire Break | Include | Include | Equipment | 210 | 2023-01-03 | 2100 | keep | 0 | Jan | 2023 | 0.0014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-01-03 12:14 | 2023-01-03 16:23 | 10 | 4:09 | P | DESGANCHE | 1 X 50 CL DESGANCHE | C23010300095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2023-01-03 | 2490 | keep | 0 | Jan | 2023 | 0.0016959 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-03 12:15 | 2023-01-03 12:16 | 1531 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 5 % DEL 1336-07 YLLEVA 15% DEL 1204-05 SE CERRO POR SCADA | S2301030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-03 | 1531 | keep | 0 | Jan | 2023 | 0.0010428 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-01-03 12:15 | 2023-01-03 12:16 | 312 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 5 % DEL 1336-07 YLLEVA 15% DEL 1204-05 SE CERRO POR SCADA | S2301030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-03 | 312 | keep | 0 | Jan | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-01-03 12:15 | 2023-01-03 12:16 | 5290 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVA 5 % DEL 1336-07 YLLEVA 15% DEL 1204-05 SE CERRO POR SCADA | S2301030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 5290 | keep | 0 | Jan | 2023 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
VEGA BAJA | 2023-01-03 12:25 | 2023-01-03 13:46 | 60 | 1:21 | P | ANIMAL | 1 X 65 EN CL CRUCE DE FASE PRIMARIA POR AVE | A23010300079 | New_Event | Animals | Include | Include | Wildlife | 81 | 2023-01-03 | 4860 | keep | 0 | Jan | 2023 | 0.0033101 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-01-03 12:35 | 2023-01-03 14:48 | 18 | 2:13 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L SE RETIRO GLOBO METALICO | B23010300069 | New_Event | Damage From Public | Include | Include | Public | 133 | 2023-01-03 | 2394 | keep | 0 | Jan | 2023 | 0.0016305 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2023-01-03 13:00 | 2023-01-03 15:28 | 3 | 2:28 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 10 KVA A 37.5 KVA | B23010300105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 148 | 2023-01-03 | 444 | keep | 0 | Jan | 2023 | 0.00030241 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-01-03 13:02 | 2023-01-03 14:04 | 1 | 1:02 | P | DESGANCHE | 1 X 25 EN RISER DESPEJE DE LINEA | S23010300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-01-03 | 62 | keep | 0 | Jan | 2023 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-03 13:07 | 2023-01-03 15:15 | 1000 | 2:08 | P | ERROR HUMANO | 2 X 100 EN CORTE DE LINEA PERSONAL DE XPERTS CORTANDO RAMA CRUZO FASES | M23010300070 | New_Event | Human Error | Include | Include | Other | 128 | 2023-01-03 | 128000 | keep | 0 | Jan | 2023 | 0.08718 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
YAUCO | 2023-01-03 13:25 | 2023-01-03 14:55 | 4 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REEMPLAZO DE LINEA SECUNDARIA | P23010300043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-01-03 | 360 | keep | 0 | Jan | 2023 | 0.00024519 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-01-03 13:30 | 2023-01-03 21:06 | 150 | 7:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23010300139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 456 | 2023-01-03 | 68400 | keep | 0 | Jan | 2023 | 0.046587 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-01-03 13:50 | 2023-01-03 17:10 | 46 | 3:20 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO | A23010300091 | New_Event | Primary Pole Failure | Include | Include | Equipment | 200 | 2023-01-03 | 9200 | keep | 0 | Jan | 2023 | 0.0062661 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
VEGA BAJA | 2023-01-03 14:01 | 2023-01-03 17:55 | 100 | 3:54 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE | A23010300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2023-01-03 | 23400 | keep | 0 | Jan | 2023 | 0.015938 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-01-03 14:02 | 2023-01-03 15:30 | 2163 | 1:28 | S | LINEA DE TRANSMISION 38KV | AISLACION ROTA Y SE PEGO A ESTRUCTURA | P23010300006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2023-01-03 | 190344 | keep | 0 | Jan | 2023 | 0.12964 | 0.0014732 | Sustained | FALSE | FALSE | Not_TMED_Event | 2163
PONCE | 2023-01-03 14:02 | 2023-01-03 15:30 | 1340 | 1:28 | S | LINEA DE TRANSMISION 38KV | AISLACION ROTA Y SE PEGO A ESTRUCTURA | P23010300006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2023-01-03 | 117920 | keep | 0 | Jan | 2023 | 0.080315 | 0.00091267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1340
PONCE | 2023-01-03 14:02 | 2023-01-03 15:30 | 2039 | 1:28 | S | LINEA DE TRANSMISION 38KV | AISLACION ROTA Y SE PEGO A ESTRUCTURA | P23010300006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2023-01-03 | 179432 | keep | 0 | Jan | 2023 | 0.12221 | 0.0013888 | Sustained | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2023-01-03 14:02 | 2023-01-03 17:17 | 485 | 3:15 | S | LINEA DE TRANSMISION 38KV | AISLACION ROTA SE PEGO A ESTRUCTURA | P23010300082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 195 | 2023-01-03 | 94575 | keep | 0 | Jan | 2023 | 0.064415 | 0.00033033 | Sustained | FALSE | FALSE | Not_TMED_Event | 485
PONCE | 2023-01-03 14:02 | 2023-01-03 17:17 | 732 | 3:15 | S | LINEA DE TRANSMISION 38KV | AISLACION ROTA SE PEGO A ESTRUCTURA | P23010300082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 195 | 2023-01-03 | 142740 | keep | 0 | Jan | 2023 | 0.09722 | 0.00049856 | Sustained | FALSE | FALSE | Not_TMED_Event | 732
CANOVANAS | 2023-01-03 14:16 | 2023-01-03 17:31 | 1 | 3:15 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R23010300044 | New_Event | Animals | Include | Include | Wildlife | 195 | 2023-01-03 | 195 | keep | 0 | Jan | 2023 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-03 14:27 | 2023-01-03 16:03 | 60 | 1:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C23010300121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-01-03 | 5760 | keep | 0 | Jan | 2023 | 0.0039231 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-01-03 14:27 | 2023-01-03 16:10 | 34 | 1:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C23010300120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-01-03 | 3502 | keep | 0 | Jan | 2023 | 0.0023852 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
YAUCO | 2023-01-03 14:28 | 2023-01-03 14:29 | 508 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | P23010300115 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-01-03 | 508 | keep | 0 | Jan | 2023 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-01-03 14:29 | 2023-01-03 16:59 | 27 | 2:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P23010300124 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 150 | 2023-01-03 | 4050 | keep | 0 | Jan | 2023 | 0.0027584 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2023-01-03 14:37 | 2023-01-03 15:03 | 1 | 0:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | S23010300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2023-01-03 | 26 | keep | 0 | Jan | 2023 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-01-03 14:47 | 2023-01-03 14:48 | 1902 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2301030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 1902 | keep | 0 | Jan | 2023 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
SAN JUAN | 2023-01-03 14:52 | 2023-01-03 22:04 | 17 | 7:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5 POR 37.5 KVA SE REMPLAZO 2 CAJAS Y 2 X 25 EN TRANSFORMADOR | S23010300068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 432 | 2023-01-03 | 7344 | keep | 0 | Jan | 2023 | 0.005002 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2023-01-03 14:55 | 2023-01-03 16:02 | 70 | 1:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C23010300129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2023-01-03 | 4690 | keep | 0 | Jan | 2023 | 0.0031943 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-01-03 15:00 | 2023-01-03 19:23 | 10 | 4:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M23010300149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2023-01-03 | 2630 | keep | 0 | Jan | 2023 | 0.0017913 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-01-03 15:04 | 2023-01-03 17:08 | 10 | 2:04 | P | DESGANCHE | 1 X 30 C/L DESGANCHE | C23010300142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-01-03 | 1240 | keep | 0 | Jan | 2023 | 0.00084456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-01-03 15:18 | 2023-01-03 16:07 | 1 | 0:49 | P | OTRAS CAUSAS | 1 X 100 EN CORTE DE LINEA SE ENCONTRO FUSIBLE PODRIDO | M23010300116 | New_Event | Other Causes | Include | Include | Other | 49 | 2023-01-03 | 49 | keep | 0 | Jan | 2023 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-03 15:21 | 2023-01-03 17:10 | 25 | 1:49 | P | TRANSFORMADOR AVERIADO | SE ABRIO C/L TOTAL Y SE REPARO BUSHING PRIMARIO EN XMR TRASPATIO | B23010300096 | New_Event | Service Transformer Failure | Include | Include | Equipment | 109 | 2023-01-03 | 2725 | keep | 0 | Jan | 2023 | 0.001856 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-01-03 15:24 | 2023-01-03 17:37 | 4 | 2:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REPARARO BAJANTES SECUNDARIOS DE TRANSFORMADOR | P23010300172 | New_Event | Secondary Wire Break | Include | Include | Equipment | 133 | 2023-01-03 | 532 | keep | 0 | Jan | 2023 | 0.00036234 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-01-03 15:26 | 2023-01-03 18:45 | 24 | 3:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23010300133 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 199 | 2023-01-03 | 4776 | keep | 0 | Jan | 2023 | 0.0032529 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-01-03 15:29 | 2023-01-03 17:17 | 40 | 1:48 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE DE LINEA | B23010300097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-01-03 | 4320 | keep | 0 | Jan | 2023 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-01-03 16:02 | 2023-01-03 16:27 | 1879 | 0:25 | T | NO SE REPORTO CAUSA | SE BORRARON BANDERAS Y SE CERRO POR CONTROL LLEVA EL 3006-05 | C23010300147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2023-01-03 | 46975 | keep | 0 | Jan | 2023 | 0.031994 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-01-03 16:02 | 2023-01-03 16:27 | 3005 | 0:25 | T | ALIMENTADOR AMARRADO | SE BORRARON BANDERAS Y SE CERRO POR CONTROL CARGA X 3006-02 | C23010300147 | New_Event | Feeder Load Transferred | Include | Include | Other | 25 | 2023-01-03 | 75125 | keep | 0 | Jan | 2023 | 0.051167 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
CANOVANAS | 2023-01-03 16:23 | 2023-01-03 16:59 | 7 | 0:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R23010300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2023-01-03 | 252 | keep | 0 | Jan | 2023 | 0.00017164 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-01-03 16:25 | 2023-01-03 16:26 | 125 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE BKR CERRADO POR CONTROL | C2301030000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-01-03 | 125 | keep | 0 | Jan | 2023 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-01-03 16:26 | 2023-01-03 18:49 | 28 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23010300220 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2023-01-03 | 4004 | keep | 0 | Jan | 2023 | 0.0027271 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
CAGUAS | 2023-01-03 16:27 | 2023-01-03 19:37 | 70 | 3:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C23010300129 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-01-03 | 13300 | keep | 0 | Jan | 2023 | 0.0090586 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-01-03 16:34 | 2023-01-03 17:11 | 10 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO CONEXIONES SECUNDARIAS Y SE REGULO VOLTAJE | B23010300107 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-01-03 | 370 | keep | 0 | Jan | 2023 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-03 16:50 | 2023-01-03 19:41 | 7 | 2:51 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | R23010300062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-01-03 | 1197 | keep | 0 | Jan | 2023 | 0.00081527 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-01-03 16:56 | 2023-01-03 18:40 | 120 | 1:44 | P | DESGANCHE | DESGANCHE 1 X 100 EN CONVERTIDOR | P23010300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-01-03 | 12480 | keep | 0 | Jan | 2023 | 0.0085001 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2023-01-03 17:35 | 2023-01-03 19:07 | 7 | 1:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZA TRANSFORMADOR DE 37.5 KVA A 4.16/7.2 KV AVERIADO | A23010300085 | New_Event | Service Transformer Failure | Include | Include | Equipment | 92 | 2023-01-03 | 644 | keep | 0 | Jan | 2023 | 0.00043863 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-01-03 17:36 | 2023-01-03 18:38 | 62 | 1:02 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23010300066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-01-03 | 3844 | keep | 0 | Jan | 2023 | 0.0026181 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
ARECIBO | 2023-01-03 18:07 | 2023-01-03 18:08 | 2228 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIAZA DOS OPERACIONES Y QUEDA EN SERVICIO | A23010300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 2228 | keep | 0 | Jan | 2023 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2023-01-03 18:07 | 2023-01-03 18:08 | 438 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR REALIAZA DOS OPERACIONES Y QUEDA EN SERVICIO | A23010300122 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-03 | 438 | keep | 0 | Jan | 2023 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2023-01-03 18:10 | 2023-01-03 19:49 | 150 | 1:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CL FUERTE LLUVIA | A23010300124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 99 | 2023-01-03 | 14850 | keep | 0 | Jan | 2023 | 0.010114 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-01-03 18:18 | 2023-01-03 20:20 | 50 | 2:02 | P | ANIMAL | 1 X 40 EN CL CRUCE DE FASE POR AVE | A23010300126 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-01-03 | 6100 | keep | 0 | Jan | 2023 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-01-03 18:22 | 2023-01-04 12:34 | 5 | 18:12 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA CRUZADA | M23010300137 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 1092 | 2023-01-03 | 5460 | keep | 0 | Jan | 2023 | 0.0037188 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-01-03 18:22 | 2023-01-04 11:41 | 10 | 17:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | M23010300140 | New_Event | Cutout Failure | Include | Include | Equipment | 1039 | 2023-01-03 | 10390 | keep | 0 | Jan | 2023 | 0.0070766 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-01-03 18:25 | 2023-01-03 20:10 | 125 | 1:45 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | A23010300131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-01-03 | 13125 | keep | 0 | Jan | 2023 | 0.0089394 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
YAUCO | 2023-01-03 18:35 | 2023-01-03 19:47 | 22 | 1:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23010300219 | New_Event | Secondary Wire Break | Include | Include | Equipment | 72 | 2023-01-03 | 1584 | keep | 0 | Jan | 2023 | 0.0010789 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CANOVANAS | 2023-01-03 19:10 | 2023-01-03 20:14 | 10 | 1:04 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | R23010300074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-01-03 | 640 | keep | 0 | Jan | 2023 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-03 19:16 | 2023-01-04 01:29 | 92 | 6:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23010300100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2023-01-03 | 34316 | keep | 0 | Jan | 2023 | 0.023372 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
SAN JUAN | 2023-01-03 19:18 | 2023-01-03 19:19 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR 1206-01 LLEVA 1206-02 | S2301030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 338 | keep | 0 | Jan | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2023-01-03 19:18 | 2023-01-03 19:19 | 733 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1206-01 LLEVA 1206-02 | S2301030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-03 | 733 | keep | 0 | Jan | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
CANOVANAS | 2023-01-03 19:19 | 2023-01-03 20:50 | 176 | 1:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L FUERTES LLUVIAS | R23010300079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 91 | 2023-01-03 | 16016 | keep | 0 | Jan | 2023 | 0.010908 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
CAGUAS | 2023-01-03 19:26 | 2023-01-04 00:29 | 391 | 5:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23010300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2023-01-03 | 118473 | keep | 0 | Jan | 2023 | 0.080691 | 0.00026631 | Sustained | FALSE | FALSE | Not_TMED_Event | 391
SAN JUAN | 2023-01-03 19:30 | 2023-01-04 06:04 | 6 | 10:34 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S23010300105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 634 | 2023-01-03 | 3804 | keep | 0 | Jan | 2023 | 0.0025909 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-01-03 19:31 | 2023-01-03 19:32 | 1403 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR CONTROL | C2301030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 1403 | keep | 0 | Jan | 2023 | 0.00095558 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
HUMACAO | 2023-01-03 20:00 | 2023-01-04 12:34 | 16 | 16:34 | P | DESGANCHE | 1 X 25 C/L DESGANCHE | C23010300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 994 | 2023-01-03 | 15904 | keep | 0 | Jan | 2023 | 0.010832 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
VEGA BAJA | 2023-01-03 20:08 | 2023-01-03 20:09 | 3654 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE REALIZA PRUEBA Y QUEDA EN SERVICIO | A23010300161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 3654 | keep | 0 | Jan | 2023 | 0.0024887 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
CAGUAS | 2023-01-03 20:13 | 2023-01-04 06:33 | 40 | 10:20 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23010300257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 620 | 2023-01-03 | 24800 | keep | 0 | Jan | 2023 | 0.016891 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-01-03 20:21 | 2023-01-04 09:52 | 140 | 13:31 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C23010300259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 811 | 2023-01-03 | 113540 | keep | 0 | Jan | 2023 | 0.077332 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CANOVANAS | 2023-01-03 20:22 | 2023-01-03 21:15 | 12 | 0:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA DE XMR AVERIADA Y REPARO TOMA NO FUNDIO | R23010300091 | New_Event | Cutout Failure | Include | Include | Equipment | 53 | 2023-01-03 | 636 | keep | 0 | Jan | 2023 | 0.00043318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-01-03 20:22 | 2023-01-04 01:48 | 52 | 5:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REEMPLAZO DE CAJA PRIMARIA | C23010300262 | New_Event | Cutout Failure | Include | Include | Equipment | 326 | 2023-01-03 | 16952 | keep | 0 | Jan | 2023 | 0.011546 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
GUAYAMA | 2023-01-03 20:37 | 2023-01-03 21:19 | 60 | 0:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA VIENTOS | P23010300226 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 42 | 2023-01-03 | 2520 | keep | 0 | Jan | 2023 | 0.0017164 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-01-03 20:37 | 2023-01-04 10:10 | 35 | 13:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23010300164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 813 | 2023-01-03 | 28455 | keep | 0 | Jan | 2023 | 0.019381 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-01-03 20:39 | 2023-01-03 20:40 | 760 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO X CONTROL | S23010300115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 760 | keep | 0 | Jan | 2023 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
YAUCO | 2023-01-03 20:45 | 2023-01-04 08:55 | 8 | 12:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23010400223 | New_Event | Secondary Wire Break | Include | Include | Equipment | 730 | 2023-01-03 | 5840 | keep | 0 | Jan | 2023 | 0.0039776 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-03 20:47 | 2023-01-03 20:48 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23010300156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 108 | keep | 0 | Jan | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
UTUADO | 2023-01-03 20:50 | 2023-01-04 08:20 | 60 | 11:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | A23010300165 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 690 | 2023-01-03 | 41400 | keep | 0 | Jan | 2023 | 0.028197 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 2231 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA MANATI SECT | A23010300176 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-01-03 | 2231 | keep | 0 | Jan | 2023 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 1923 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA MANATI SECT | A23010300176 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-01-03 | 1923 | keep | 0 | Jan | 2023 | 0.0013097 | 0.0013097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1923
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 1066 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA MANATI SECT | A23010300176 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-01-03 | 1066 | keep | 0 | Jan | 2023 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 141 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA MANATI SECT | A23010300176 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-01-03 | 141 | keep | 0 | Jan | 2023 | 9.6034e-05 | 9.6034e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 141
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 2107 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 14700 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 2107 | keep | 0 | Jan | 2023 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 308 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 14700 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 308 | keep | 0 | Jan | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 2697 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 14700 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 2697 | keep | 0 | Jan | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 67 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 14700 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 67 | keep | 0 | Jan | 2023 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 1879 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 1879 | keep | 0 | Jan | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 2777 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 2777 | keep | 0 | Jan | 2023 | 0.0018914 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 2 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 2 | keep | 0 | Jan | 2023 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 2839 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300180 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 2839 | keep | 0 | Jan | 2023 | 0.0019336 | 0.0019336 | Momentary | FALSE | FALSE | Not_TMED_Event | 2839
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 1160 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300180 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 1160 | keep | 0 | Jan | 2023 | 0.00079007 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
VEGA BAJA | 2023-01-03 20:51 | 2023-01-03 20:52 | 1860 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300180 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 1860 | keep | 0 | Jan | 2023 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
VEGA BAJA | 2023-01-03 20:52 | 2023-01-03 23:28 | 1 | 2:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN RISER | A22122100050 | New_Event | Cutout Failure | Include | Include | Equipment | 156 | 2023-01-03 | 156 | keep | 0 | Jan | 2023 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-03 20:54 | 2023-01-04 09:10 | 10 | 12:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23010300172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 736 | 2023-01-03 | 7360 | keep | 0 | Jan | 2023 | 0.0050129 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-03 21:01 | 2023-01-04 04:01 | 116 | 7:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN RISER MAL TIEMPO LLUVIA | S23010300121 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 420 | 2023-01-03 | 48720 | keep | 0 | Jan | 2023 | 0.033183 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
ARECIBO | 2023-01-03 21:18 | 2023-01-03 23:35 | 150 | 2:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A23010300188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-01-03 | 20550 | keep | 0 | Jan | 2023 | 0.013997 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-01-03 21:21 | 2023-01-03 21:22 | 1834 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2301030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 1834 | keep | 0 | Jan | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
VEGA BAJA | 2023-01-03 21:23 | 2023-01-03 23:28 | 20 | 2:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 20 EN RISER / SE RETIRO ENREDADERA DE LAS LINEA | A23010300191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-01-03 | 2500 | keep | 0 | Jan | 2023 | 0.0017027 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-03 21:26 | 2023-01-03 21:29 | 73 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO X CONTROL | S2301030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-03 | 219 | keep | 0 | Jan | 2023 | 0.00014916 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2023-01-03 21:26 | 2023-01-03 21:28 | 1191 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO X CONTROL | S23010300119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-03 | 2382 | keep | 0 | Jan | 2023 | 0.0016224 | 0.00081118 | Momentary | FALSE | FALSE | Not_TMED_Event | 1191
SAN JUAN | 2023-01-03 21:26 | 2023-01-03 21:30 | 60 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO X CONTROL LLEVA EL 10% DEL 1420-03 | S23010300120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-01-03 | 240 | keep | 0 | Jan | 2023 | 0.00016346 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-03 21:26 | 2023-01-03 21:30 | 54 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1420-02 CERRADO X CONTROL 10% DE LA CARGA X 1420-02 | S23010300120 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-01-03 | 216 | keep | 0 | Jan | 2023 | 0.00014712 | 3.6779e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 54
CAGUAS | 2023-01-03 21:30 | 2023-01-04 07:10 | 20 | 9:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CAJA A XMR | C23010300299 | New_Event | Primary Wire Break | Include | Include | Equipment | 580 | 2023-01-03 | 11600 | keep | 0 | Jan | 2023 | 0.0079007 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-03 21:46 | 2023-01-03 22:14 | 8 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REMPLAZAR BAJANTE Y CONECTORES SECUNDARIOS | B23010300117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-01-03 | 224 | keep | 0 | Jan | 2023 | 0.00015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-01-03 22:33 | 2023-01-04 09:03 | 1 | 10:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE DE CAJA A TRANSFORMADOR | M23010300158 | New_Event | Secondary Wire Break | Include | Include | Equipment | 630 | 2023-01-03 | 630 | keep | 0 | Jan | 2023 | 0.00042909 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-03 23:28 | 2023-01-03 23:30 | 2466 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | B23010300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-03 | 4932 | keep | 0 | Jan | 2023 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 2231 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 2231 | keep | 0 | Jan | 2023 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 1923 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 1923 | keep | 0 | Jan | 2023 | 0.0013097 | 0.0013097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1923
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 1066 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 1066 | keep | 0 | Jan | 2023 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 141 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 141 | keep | 0 | Jan | 2023 | 9.6034e-05 | 9.6034e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 141
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:57 | 2107 | 0:29 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300242 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2023-01-03 | 61103 | keep | 0 | Jan | 2023 | 0.041617 | 0.0014351 | Sustained | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:57 | 308 | 0:29 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300242 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2023-01-03 | 8932 | keep | 0 | Jan | 2023 | 0.0060835 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:57 | 2697 | 0:29 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300242 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2023-01-03 | 78213 | keep | 0 | Jan | 2023 | 0.053271 | 0.0018369 | Sustained | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:57 | 67 | 0:29 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300242 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2023-01-03 | 1943 | keep | 0 | Jan | 2023 | 0.0013234 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 1879 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300243 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 1879 | keep | 0 | Jan | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 2777 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300243 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 2777 | keep | 0 | Jan | 2023 | 0.0018914 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 2 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300243 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 2 | keep | 0 | Jan | 2023 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 2839 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300244 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 2839 | keep | 0 | Jan | 2023 | 0.0019336 | 0.0019336 | Momentary | FALSE | FALSE | Not_TMED_Event | 2839
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 1160 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300244 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 1160 | keep | 0 | Jan | 2023 | 0.00079007 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
VEGA BAJA | 2023-01-03 23:28 | 2023-01-03 23:29 | 1860 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 PUENTE QUEMADO EN LINEA 14700 OCASIONA DISPARO DE BARRA Y LINEAS | A23010300244 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-03 | 1860 | keep | 0 | Jan | 2023 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
VEGA BAJA | 2023-01-03 23:29 | 2023-01-09 14:22 | 1 | 134:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN RISER ESCUELA ESTUIVO FUERA DESDE EL 12/21/22 | A22122100050 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 8093 | 2023-01-03 | 8093 | keep | 0 | Jan | 2023 | 0.0055121 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-03 23:47 | 2023-01-03 23:48 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23010300133 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-03 | 2466 | keep | 0 | Jan | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
VEGA BAJA | 2023-01-03 23:57 | 2023-01-04 08:05 | 20 | 8:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 20 EN RISER / SE RETIRO ENREDADERA DE LAS LINEA | A23010300191 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 488 | 2023-01-03 | 9760 | keep | 0 | Jan | 2023 | 0.0066475 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-04 00:04 | 2023-01-04 08:07 | 20 | 8:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L Y 1 X 40 EN CL | C23010400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 483 | 2023-01-04 | 9660 | keep | 0 | Jan | 2023 | 0.0065794 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-01-04 00:23 | 2023-01-04 00:24 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23010400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 108 | keep | 0 | Jan | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
HUMACAO | 2023-01-04 01:10 | 2023-01-04 07:50 | 45 | 6:40 | P | DESGANCHE | 1 X 50 C/L DEESGANCHE | C23010400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2023-01-04 | 18000 | keep | 0 | Jan | 2023 | 0.01226 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2023-01-04 01:34 | 2023-01-04 09:29 | 40 | 7:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO PARTIDO Y 1 X 50 EN C/L | B23010400001 | New_Event | Primary Wire Break | Include | Include | Equipment | 475 | 2023-01-04 | 19000 | keep | 0 | Jan | 2023 | 0.012941 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-01-04 02:44 | 2023-01-04 12:42 | 10 | 9:58 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | A23010400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 598 | 2023-01-04 | 5980 | keep | 0 | Jan | 2023 | 0.004073 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-04 03:03 | 2023-01-04 03:04 | 1681 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-04 | S23010400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 1681 | keep | 0 | Jan | 2023 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-01-04 03:03 | 2023-01-04 03:04 | 1598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-04 | S23010400000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-04 | 1598 | keep | 0 | Jan | 2023 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BARRANQUITAS | 2023-01-04 03:08 | 2023-01-04 13:41 | 268 | 10:33 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | C23010400007 | New_Event | Primary Wire Break | Include | Include | Equipment | 633 | 2023-01-04 | 169644 | keep | 0 | Jan | 2023 | 0.11554 | 0.00018253 | Sustained | FALSE | FALSE | Not_TMED_Event | 268
VEGA BAJA | 2023-01-04 03:21 | 2023-01-04 08:00 | 15 | 4:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA / SE RETIRO ENREDADERA DE LAS LINEAS | A23010400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2023-01-04 | 4185 | keep | 0 | Jan | 2023 | 0.0028504 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-01-04 03:52 | 2023-01-04 03:53 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23010400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 3431 | keep | 0 | Jan | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CANOVANAS | 2023-01-04 04:21 | 2023-01-04 11:17 | 30 | 6:56 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23010400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2023-01-04 | 12480 | keep | 0 | Jan | 2023 | 0.0085001 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-04 04:32 | 2023-01-04 08:20 | 204 | 3:48 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE DESGANCHO PALMA | R23010400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-01-04 | 46512 | keep | 0 | Jan | 2023 | 0.031679 | 0.00013894 | Sustained | FALSE | FALSE | Not_TMED_Event | 204
SAN JUAN | 2023-01-04 04:40 | 2023-01-05 13:28 | 10 | 32:48 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER Y 1 X 40 EN SU | S23010400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1968 | 2023-01-04 | 19680 | keep | 0 | Jan | 2023 | 0.013404 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-04 05:45 | 2023-01-04 05:46 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23010400012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 2126 | keep | 0 | Jan | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
YAUCO | 2023-01-04 06:06 | 2023-01-04 09:44 | 50 | 3:38 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23010400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2023-01-04 | 10900 | keep | 0 | Jan | 2023 | 0.0074239 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-04 06:45 | 2023-01-04 10:12 | 10 | 3:27 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | C23010400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-01-04 | 2070 | keep | 0 | Jan | 2023 | 0.0014099 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-04 06:51 | 2023-01-04 19:37 | 26 | 12:46 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO Y TRANSFORMADOR | B23010400047 | New_Event | Primary Pole Failure | Include | Include | Equipment | 766 | 2023-01-04 | 19916 | keep | 0 | Jan | 2023 | 0.013565 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
VEGA BAJA | 2023-01-04 07:00 | 2023-01-04 10:30 | 107 | 3:30 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESPEJE DE LINEA | B23010400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-01-04 | 22470 | keep | 0 | Jan | 2023 | 0.015304 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
GUAYAMA | 2023-01-04 07:29 | 2023-01-04 09:19 | 20 | 1:50 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN C/L | P23010400016 | New_Event | Primary Wire Break | Include | Include | Equipment | 110 | 2023-01-04 | 2200 | keep | 0 | Jan | 2023 | 0.0014984 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2023-01-04 07:34 | 2023-01-04 07:48 | 13 | 0:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | R23010400019 | New_Event | Cutout Failure | Include | Include | Equipment | 14 | 2023-01-04 | 182 | keep | 0 | Jan | 2023 | 0.00012396 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-01-04 07:37 | 2023-01-04 15:22 | 122 | 7:45 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE Y SE REMPLAZO AISLADORES | C23010400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2023-01-04 | 56730 | keep | 0 | Jan | 2023 | 0.038639 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
SAN JUAN | 2023-01-04 07:46 | 2023-01-04 07:47 | 1483 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 5% 1336-07 Y LLEVA 15% 1204-05 | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-04 | 1483 | keep | 0 | Jan | 2023 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-01-04 07:46 | 2023-01-04 07:47 | 1531 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 5% 1336-07 Y LLEVA 15% 1204-05 | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-04 | 1531 | keep | 0 | Jan | 2023 | 0.0010428 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-01-04 07:46 | 2023-01-04 07:47 | 312 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 5% 1336-07 Y LLEVA 15% 1204-05 | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-04 | 312 | keep | 0 | Jan | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-01-04 07:46 | 2023-01-04 07:47 | 5290 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 5% 1336-07 Y LLEVA 15% 1204-05 | S2301040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 5290 | keep | 0 | Jan | 2023 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
PONCE | 2023-01-04 08:30 | 2023-01-04 10:04 | 4009 | 1:34 | T | NO SE REPORTO CAUSA | SE CERRO BRAKER MANUAL NO CAUSA | P23010400023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2023-01-04 | 376846 | keep | 0 | Jan | 2023 | 0.25667 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
BAYAMON | 2023-01-04 08:59 | 2023-01-04 10:33 | 13 | 1:34 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B23010400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2023-01-04 | 1222 | keep | 0 | Jan | 2023 | 0.0008323 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2023-01-04 09:35 | 2023-01-04 14:00 | 1 | 4:25 | P | DESGANCHE | ABRIR PUENTES PARA REALIZAR DESGANCHE MASIVO | A23010400036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2023-01-04 | 265 | keep | 0 | Jan | 2023 | 0.00018049 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-04 09:36 | 2023-01-04 13:06 | 19 | 3:30 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S23010400035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-01-04 | 3990 | keep | 0 | Jan | 2023 | 0.0027176 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-01-04 09:40 | 2023-01-04 11:42 | 50 | 2:02 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | S23010400038 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-01-04 | 6100 | keep | 0 | Jan | 2023 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-01-04 09:45 | 2023-01-04 10:46 | 4 | 1:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR EN MALAS CONDICIONES | M23010400021 | New_Event | Cutout Failure | Include | Include | Equipment | 61 | 2023-01-04 | 244 | keep | 0 | Jan | 2023 | 0.00016619 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-01-04 09:46 | 2023-01-04 11:47 | 12 | 2:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE TRANSFORMADOR | M23010400023 | New_Event | Cutout Failure | Include | Include | Equipment | 121 | 2023-01-04 | 1452 | keep | 0 | Jan | 2023 | 0.00098895 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-01-04 09:52 | 2023-01-04 11:41 | 80 | 1:49 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO | M23010400024 | New_Event | Primary Wire Break | Include | Include | Equipment | 109 | 2023-01-04 | 8720 | keep | 0 | Jan | 2023 | 0.0059392 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-01-04 09:56 | 2023-01-04 11:37 | 55 | 1:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIA | C23010400050 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 101 | 2023-01-04 | 5555 | keep | 0 | Jan | 2023 | 0.0037835 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CANOVANAS | 2023-01-04 10:00 | 2023-01-04 12:49 | 30 | 2:49 | P | DESGANCHE | 2 X 50 Y 1 X 30 EN CORTE DE LINEA DESGANCHE | R23010400041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-01-04 | 5070 | keep | 0 | Jan | 2023 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-04 10:10 | 2023-01-04 15:30 | 5 | 5:20 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | S23010400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2023-01-04 | 1600 | keep | 0 | Jan | 2023 | 0.0010898 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-01-04 10:20 | 2023-01-04 11:55 | 11 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23010400039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2023-01-04 | 1045 | keep | 0 | Jan | 2023 | 0.00071174 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2023-01-04 10:25 | 2023-01-04 15:30 | 12 | 5:05 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23010400043 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 305 | 2023-01-04 | 3660 | keep | 0 | Jan | 2023 | 0.0024928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-01-04 10:30 | 2023-01-04 11:10 | 6 | 0:40 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR REPARACION SECUNDARIA Y REALIZAR DESGANCHE SECUNDARIO | B23010300106 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 40 | 2023-01-04 | 240 | keep | 0 | Jan | 2023 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-01-04 10:42 | 2023-01-04 11:24 | 100 | 0:42 | P | ANIMAL | 2 X 80 EN C/L AVE CRUZO LINEAS | P23010400122 | New_Event | Animals | Include | Include | Wildlife | 42 | 2023-01-04 | 4200 | keep | 0 | Jan | 2023 | 0.0028606 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-01-04 10:59 | 2023-01-04 13:30 | 7 | 2:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA AVERIADA | C23010400070 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2023-01-04 | 1057 | keep | 0 | Jan | 2023 | 0.00071992 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-01-04 10:59 | 2023-01-04 12:32 | 12 | 1:33 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA IGUANA CRUZO FASES | M23010400047 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-01-04 | 1116 | keep | 0 | Jan | 2023 | 0.0007601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-01-04 11:04 | 2023-01-04 13:16 | 100 | 2:12 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L RAYOS | C23010400074 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 132 | 2023-01-04 | 13200 | keep | 0 | Jan | 2023 | 0.0089905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-04 11:06 | 2023-01-04 11:26 | 1 | 0:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO 37.5 KVA X 37.5KVA | S23010400014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 20 | 2023-01-04 | 20 | keep | 0 | Jan | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-04 11:07 | 2023-01-04 14:20 | 1 | 3:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X30 EN C/L MAL TIEMPO LLUVIA | C23010400076 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 193 | 2023-01-04 | 193 | keep | 0 | Jan | 2023 | 0.00013145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-04 11:09 | 2023-01-04 16:00 | 623 | 4:51 | P | DESGANCHE | CG-230104-02 SE REMOVIO BAMBUA Y SE LEVANTO CONDUCTOR | C23010400077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2023-01-04 | 181293 | keep | 0 | Jan | 2023 | 0.12348 | 0.00042432 | Sustained | FALSE | FALSE | Not_TMED_Event | 623
CANOVANAS | 2023-01-04 11:10 | 2023-01-04 12:42 | 163 | 1:32 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE FIJO LINEA A AISLADOR | R23010400047 | New_Event | Primary Wire Break | Include | Include | Equipment | 92 | 2023-01-04 | 14996 | keep | 0 | Jan | 2023 | 0.010214 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
CAGUAS | 2023-01-04 11:10 | 2023-01-04 11:11 | 4634 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 4634 | keep | 0 | Jan | 2023 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
BAYAMON | 2023-01-04 11:12 | 2023-01-04 15:00 | 7 | 3:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN XMR | B23010400040 | New_Event | Cutout Failure | Include | Include | Equipment | 228 | 2023-01-04 | 1596 | keep | 0 | Jan | 2023 | 0.001087 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-01-04 11:19 | 2023-01-04 11:23 | 73 | 0:04 | T | DESCONECTIVO DEFECTUOSO | DISPARO HACIENDO OPERACIONES AL CERRAR BARRA DE INSPECCION 1420-01 | S2301040000X | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2023-01-04 | 292 | keep | 0 | Jan | 2023 | 0.00019888 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2023-01-04 11:19 | 2023-01-04 11:23 | 1191 | 0:04 | T | DESCONECTIVO DEFECTUOSO | DISPARO HACIENDO OPERACIONES AL CERRAR BARRA DE INSPECCION 1420-01 | S23010400057 | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2023-01-04 | 4764 | keep | 0 | Jan | 2023 | 0.0032447 | 0.00081118 | Momentary | FALSE | FALSE | Not_TMED_Event | 1191
AGUADILLA | 2023-01-04 11:23 | 2023-01-04 18:20 | 25 | 6:57 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | M23010400051 | New_Event | Primary Wire Break | Include | Include | Equipment | 417 | 2023-01-04 | 10425 | keep | 0 | Jan | 2023 | 0.0071004 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-04 11:24 | 2023-01-04 13:18 | 60 | 1:54 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR 1420-02 QUE LLEVA 10% DEL 1420-03 Y SE SECCIONALIZO BARRA DE INSPECCION MEDIANTE SJ-230104-02 PARA REEMPLAZO DE MACHETE DE BARRA DE INSPECCION | S23010400059 | New_Event | Switch Failure | Include | Include | Equipment | 114 | 2023-01-04 | 6840 | keep | 0 | Jan | 2023 | 0.0046587 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-04 11:24 | 2023-01-04 13:18 | 54 | 1:54 | P | ALIMENTADOR AMARRADO | SEABRIO BKR 1420-02 QUE LLEVA 10% DEL 1420-03 Y SE SECCIONALIZO BARRA DE INSPECCION MEDIANTE SJ-230104-02 PARA REEMPLAZO DE MACHETE DE BARRA DE INSPECCION | S23010400059 | New_Event | Feeder Load Transferred | Include | Include | Other | 114 | 2023-01-04 | 6156 | keep | 0 | Jan | 2023 | 0.0041928 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
CAGUAS | 2023-01-04 11:32 | 2023-01-04 13:04 | 11 | 1:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO Y SE REPARO CONECTORES | C23010400093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2023-01-04 | 1012 | keep | 0 | Jan | 2023 | 0.00068927 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2023-01-04 11:33 | 2023-01-04 11:34 | 3630 | 0:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M23010400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2023-01-04 | 3630 | keep | 0 | Jan | 2023 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2023-01-04 11:34 | 2023-01-04 15:40 | 10 | 4:06 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA SE CERRO SU-1 AL SU-2 | M23010400066 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 246 | 2023-01-04 | 2460 | keep | 0 | Jan | 2023 | 0.0016755 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-04 11:38 | 2023-01-04 12:15 | 8 | 0:37 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO PARARRAYO AVERIADO Y CAJA PRIMARIA | B23010400050 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 37 | 2023-01-04 | 296 | keep | 0 | Jan | 2023 | 0.0002016 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-01-04 11:40 | 2023-01-04 14:00 | 7 | 2:20 | P | TRANSFORMADOR AVERIADO | REMPLAZO T - 1 DE 50 KVA X 50 KVA CON DERRAME | C23010400097 | New_Event | Service Transformer Failure | Include | Include | Equipment | 140 | 2023-01-04 | 980 | keep | 0 | Jan | 2023 | 0.00066747 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-01-04 11:50 | 2023-01-04 13:10 | 7 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMAOR PARA REPARAR TOMA CON NEUTRAL COMUN | R23010400057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-01-04 | 560 | keep | 0 | Jan | 2023 | 0.00038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-01-04 11:55 | 2023-01-04 12:49 | 4 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23010400025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2023-01-04 | 216 | keep | 0 | Jan | 2023 | 0.00014712 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-01-04 11:57 | 2023-01-04 12:57 | 1 | 1:00 | P | MAL TIEMPO/RAYOS | 2 X 15 EN XMR RAYOS | C23010400104 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 60 | 2023-01-04 | 60 | keep | 0 | Jan | 2023 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-04 11:58 | 2023-01-04 12:01 | 1483 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 5% DEL 1336-07 LLEVA 30% DEL 1204-04 Y LLEVA 15% DEL 1204-05 | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-04 | 4449 | keep | 0 | Jan | 2023 | 0.0030302 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-01-04 11:58 | 2023-01-04 12:01 | 1531 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 5% DEL 1336-07 LLEVA 30% DEL 1204-04 Y LLEVA 15% DEL 1204-05 | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-04 | 4593 | keep | 0 | Jan | 2023 | 0.0031283 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-01-04 11:58 | 2023-01-04 12:01 | 312 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 5% DEL 1336-07 LLEVA 30% DEL 1204-04 Y LLEVA 15% DEL 1204-05 | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-04 | 936 | keep | 0 | Jan | 2023 | 0.00063751 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-01-04 11:58 | 2023-01-04 12:01 | 5290 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 5% DEL 1336-07 LLEVA 30% DEL 1204-04 Y LLEVA 15% DEL 1204-05 | S2301040000X | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-01-04 | 15870 | keep | 0 | Jan | 2023 | 0.010809 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2023-01-04 12:01 | 2023-01-04 16:02 | 115 | 4:01 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO SJ-230104-03 | S23010400076 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 241 | 2023-01-04 | 27715 | keep | 0 | Jan | 2023 | 0.018877 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
CANOVANAS | 2023-01-04 12:01 | 2023-01-04 12:02 | 2090 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE CARGA X 2403-02 | R23010400062 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-04 | 2090 | keep | 0 | Jan | 2023 | 0.0014235 | 0.0014235 | Momentary | FALSE | FALSE | Not_TMED_Event | 2090
CANOVANAS | 2023-01-04 12:01 | 2023-01-04 12:02 | 500 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA DEL 2403-01 | R23010400062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 500 | keep | 0 | Jan | 2023 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
UTUADO | 2023-01-04 12:06 | 2023-01-04 17:20 | 150 | 5:14 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR RAMA SOBRE LINEA | A23010400080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2023-01-04 | 47100 | keep | 0 | Jan | 2023 | 0.03208 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-01-04 12:06 | 2023-01-04 12:11 | 10 | 0:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B23010400051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-01-04 | 50 | keep | 0 | Jan | 2023 | 3.4055e-05 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-04 12:17 | 2023-01-05 10:24 | 20 | 22:07 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | B23010400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1327 | 2023-01-04 | 26540 | keep | 0 | Jan | 2023 | 0.018076 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-01-04 12:24 | 2023-01-04 13:21 | 20 | 0:57 | P | ANIMAL | 1 X 20 EN C/L CRUCE DE AVE | C23010400110 | New_Event | Animals | Include | Include | Wildlife | 57 | 2023-01-04 | 1140 | keep | 0 | Jan | 2023 | 0.00077645 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-04 12:31 | 2023-01-04 13:33 | 7 | 1:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23010400056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 62 | 2023-01-04 | 434 | keep | 0 | Jan | 2023 | 0.0002956 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2023-01-04 12:40 | 2023-01-04 12:45 | 30 | 0:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO VIENTOS | P23010400136 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2023-01-04 | 150 | keep | 0 | Jan | 2023 | 0.00010216 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-01-04 12:40 | 2023-01-04 13:00 | 120 | 0:20 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA | M23010400017 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 20 | 2023-01-04 | 2400 | keep | 0 | Jan | 2023 | 0.0016346 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2023-01-04 12:50 | 2023-01-04 15:15 | 25 | 2:25 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEAS CRUZADAS | M23010400074 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 145 | 2023-01-04 | 3625 | keep | 0 | Jan | 2023 | 0.002469 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-04 13:16 | 2023-01-04 13:17 | 1061 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2301040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 1061 | keep | 0 | Jan | 2023 | 0.00072264 | 0.00072264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1061
PONCE | 2023-01-04 13:16 | 2023-01-04 13:17 | 860 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010400107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 860 | keep | 0 | Jan | 2023 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
VEGA BAJA | 2023-01-04 13:21 | 2023-01-04 13:55 | 7 | 0:34 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO PARARRAYO AVERIADO | B23010400064 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 34 | 2023-01-04 | 238 | keep | 0 | Jan | 2023 | 0.0001621 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-01-04 13:30 | 2023-01-04 17:19 | 67 | 3:49 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L RAYOS | C23010400133 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 229 | 2023-01-04 | 15343 | keep | 0 | Jan | 2023 | 0.01045 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-01-04 13:32 | 2023-01-04 13:33 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-01 LLEVANDO 1206-02 | S2301040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 338 | keep | 0 | Jan | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2023-01-04 13:32 | 2023-01-04 13:33 | 733 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1206-01 LLEVANDO 1206-02 | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-04 | 733 | keep | 0 | Jan | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
CANOVANAS | 2023-01-04 13:35 | 2023-01-04 16:17 | 194 | 2:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE RETIRO CORNER BRACKET 3 X 80 Y 1 X 100 EN C/L | R23010400075 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 162 | 2023-01-04 | 31428 | keep | 0 | Jan | 2023 | 0.021405 | 0.00013213 | Sustained | FALSE | FALSE | Not_TMED_Event | 194
CANOVANAS | 2023-01-04 13:44 | 2023-01-04 13:45 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23010400080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 7621 | keep | 0 | Jan | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
FAJARDO | 2023-01-04 13:48 | 2023-01-04 17:03 | 1 | 3:15 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE XMR 25KVA X 25KVA | R23010400084 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2023-01-04 | 195 | keep | 0 | Jan | 2023 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-04 13:49 | 2023-01-04 15:16 | 1 | 1:27 | P | NO SE REPORTO CAUSA | 1 NX DE 15A EN EL TS - 1 | C23010400145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-01-04 | 87 | keep | 0 | Jan | 2023 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-04 14:10 | 2023-01-04 21:05 | 79 | 6:55 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | C23010400152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2023-01-04 | 32785 | keep | 0 | Jan | 2023 | 0.02233 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
FAJARDO | 2023-01-04 14:15 | 2023-01-04 14:19 | 1234 | 0:04 | T | ARBOL SOBRE LINEA | DISPARO DE BKR SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | R2201040000X | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 4 | 2023-01-04 | 4936 | keep | 0 | Jan | 2023 | 0.0033619 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2023-01-04 14:19 | 2023-01-04 15:45 | 12 | 1:26 | P | ARBOL SOBRE LINEA | 1 X 30 EN C/L SE RETIRO ARBOL SOBRE LINEA | R23010400095 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 86 | 2023-01-04 | 1032 | keep | 0 | Jan | 2023 | 0.00070289 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-01-04 14:27 | 2023-01-04 15:20 | 7 | 0:53 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR PARARRAYO AVERIADO | B23010400076 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 53 | 2023-01-04 | 371 | keep | 0 | Jan | 2023 | 0.00025269 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-01-04 14:35 | 2023-01-04 20:53 | 100 | 6:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | P23010400164 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 378 | 2023-01-04 | 37800 | keep | 0 | Jan | 2023 | 0.025745 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-01-04 14:36 | 2023-01-04 14:51 | 1109 | 0:15 | T | MAL TIEMPO/LLUVIA O VIENTO | SE CERRO BRAKER DISPARO POR MAL TIEMPO VIENTOS | P23010400169 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 15 | 2023-01-04 | 16635 | keep | 0 | Jan | 2023 | 0.01133 | 0.00075533 | Sustained | FALSE | FALSE | Not_TMED_Event | 1109
PONCE | 2023-01-04 14:38 | 2023-01-04 14:51 | 1078 | 0:13 | T | MAL TIEMPO/LLUVIA O VIENTO | SE CERRO BREAKER DISPARO POR MAL TIEMPO VIENTOS | P23010400185 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 13 | 2023-01-04 | 14014 | keep | 0 | Jan | 2023 | 0.0095449 | 0.00073422 | Sustained | FALSE | FALSE | Not_TMED_Event | 1078
FAJARDO | 2023-01-04 14:40 | 2023-01-04 16:52 | 25 | 2:12 | P | ANIMAL | 1 X 30 EN C/L 1 X 10 EN XMR CRUCE X AVE | R23010400106 | New_Event | Animals | Include | Include | Wildlife | 132 | 2023-01-04 | 3300 | keep | 0 | Jan | 2023 | 0.0022476 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-01-04 14:40 | 2023-01-04 17:52 | 50 | 3:12 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23010400172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2023-01-04 | 9600 | keep | 0 | Jan | 2023 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-04 14:43 | 2023-01-04 17:12 | 74 | 2:29 | P | DESGANCHE | DESGANCHE Y 1 X 50 EN C/L | B23010400080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-01-04 | 11026 | keep | 0 | Jan | 2023 | 0.0075098 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2023-01-04 14:43 | 2023-01-04 18:03 | 20 | 3:20 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | B23010400079 | New_Event | Animals | Include | Include | Wildlife | 200 | 2023-01-04 | 4000 | keep | 0 | Jan | 2023 | 0.0027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-01-04 14:44 | 2023-01-04 17:18 | 1000 | 2:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 140 EN C/L MAL TIEMPO VIENTOS | P23010400187 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 154 | 2023-01-04 | 154000 | keep | 0 | Jan | 2023 | 0.10489 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
PONCE | 2023-01-04 14:44 | 2023-01-04 21:27 | 100 | 6:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA FUERTE BRISA | P23010400186 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 403 | 2023-01-04 | 40300 | keep | 0 | Jan | 2023 | 0.027448 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-01-04 14:45 | 2023-01-04 21:46 | 120 | 7:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | P23010400189 | New_Event | Cutout Failure | Include | Include | Equipment | 421 | 2023-01-04 | 50520 | keep | 0 | Jan | 2023 | 0.034409 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2023-01-04 14:47 | 2023-01-04 20:00 | 100 | 5:13 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | P23010400193 | New_Event | Primary Wire Break | Include | Include | Equipment | 313 | 2023-01-04 | 31300 | keep | 0 | Jan | 2023 | 0.021318 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-01-04 14:48 | 2023-01-04 20:10 | 75 | 5:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO VIENTOS | P23010400194 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 322 | 2023-01-04 | 24150 | keep | 0 | Jan | 2023 | 0.016448 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2023-01-04 14:57 | 2023-01-04 19:12 | 500 | 4:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 Y 1 X 140 MAL TIEMPO VIENTOS | P23010400168 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 255 | 2023-01-04 | 127500 | keep | 0 | Jan | 2023 | 0.08684 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2023-01-04 15:00 | 2023-01-05 07:40 | 101 | 16:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23010400219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1000 | 2023-01-04 | 101000 | keep | 0 | Jan | 2023 | 0.068791 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
AGUADILLA | 2023-01-04 15:00 | 2023-01-04 16:55 | 30 | 1:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A23010400121 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 115 | 2023-01-04 | 3450 | keep | 0 | Jan | 2023 | 0.0023498 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-01-04 15:01 | 2023-01-04 18:00 | 30 | 2:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO VIENTOS | P23010400220 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 179 | 2023-01-04 | 5370 | keep | 0 | Jan | 2023 | 0.0036575 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-04 15:05 | 2023-01-04 17:08 | 10 | 2:03 | P | MAL TIEMPO/RAYOS | 2 X 10 EN XMR MAL TIEMPO RAYOS | R23010400115 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2023-01-04 | 1230 | keep | 0 | Jan | 2023 | 0.00083775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-04 15:07 | 2023-01-04 21:26 | 37 | 6:19 | P | CONDUCTOR ROTO O ABIERTO | 2 X 30 EN C/L Y 1 X 65 EN C/L SE LEVANTO CONDUCTOR PRIMARIO Y SECUNDARIO | R23010400117 | New_Event | Primary Wire Break | Include | Include | Equipment | 379 | 2023-01-04 | 14023 | keep | 0 | Jan | 2023 | 0.009551 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
PONCE | 2023-01-04 15:07 | 2023-01-04 19:45 | 50 | 4:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO VIENTOS | P23010400228 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 278 | 2023-01-04 | 13900 | keep | 0 | Jan | 2023 | 0.0094672 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-01-04 15:09 | 2023-01-04 20:29 | 30 | 5:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO VIENTOS | P23010400229 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 320 | 2023-01-04 | 9600 | keep | 0 | Jan | 2023 | 0.0065385 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-04 15:09 | 2023-01-04 15:40 | 7 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA SECUNDARIA EN PEDESTAL | B23010400085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2023-01-04 | 217 | keep | 0 | Jan | 2023 | 0.0001478 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-01-04 15:10 | 2023-01-04 15:20 | 80 | 0:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L REMPLAZO AISLADOR | C23010400077 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 10 | 2023-01-04 | 800 | keep | 0 | Jan | 2023 | 0.00054488 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2023-01-04 15:14 | 2023-01-04 18:49 | 150 | 3:35 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | P23010400236 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2023-01-04 | 32250 | keep | 0 | Jan | 2023 | 0.021965 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-01-04 15:20 | 2023-01-04 16:23 | 40 | 1:03 | P | CONDUCTOR ROTO O ABIERTO | CONECTO BAJANTE DE LINEA A CAJA NO FUNDIO | C23010400077 | New_Event | Primary Wire Break | Include | Include | Equipment | 63 | 2023-01-04 | 2520 | keep | 0 | Jan | 2023 | 0.0017164 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-01-04 15:21 | 2023-01-04 17:08 | 70 | 1:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO VIENTOS | P23010400246 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 107 | 2023-01-04 | 7490 | keep | 0 | Jan | 2023 | 0.0051014 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-01-04 15:23 | 2023-01-04 16:45 | 12 | 1:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23010400103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2023-01-04 | 984 | keep | 0 | Jan | 2023 | 0.0006702 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-01-04 15:40 | 2023-01-04 19:29 | 8 | 3:49 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | C23010400179 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 229 | 2023-01-04 | 1832 | keep | 0 | Jan | 2023 | 0.0012478 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-01-04 15:40 | 2023-01-04 22:45 | 120 | 7:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 2 X 65 EN CORTE DE LINEA POR VIENTOS | M23010400110 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 425 | 2023-01-04 | 51000 | keep | 0 | Jan | 2023 | 0.034736 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
YAUCO | 2023-01-04 15:49 | 2023-01-04 19:22 | 150 | 3:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L MAL TIEMPO VIENTOS | P23010400278 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 213 | 2023-01-04 | 31950 | keep | 0 | Jan | 2023 | 0.021761 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-01-04 15:55 | 2023-01-04 19:59 | 8 | 4:04 | P | DESGANCHE | 1X40 Y 1X30 EN C/L SE DESGANCHO PALMA | R23010400137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2023-01-04 | 1952 | keep | 0 | Jan | 2023 | 0.0013295 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-04 15:56 | 2023-01-04 18:00 | 200 | 2:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23010400118 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 124 | 2023-01-04 | 24800 | keep | 0 | Jan | 2023 | 0.016891 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2023-01-04 16:00 | 2023-01-05 12:43 | 10 | 20:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES DE BAJANTE SECUNDARIO | C23010400183 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1243 | 2023-01-04 | 12430 | keep | 0 | Jan | 2023 | 0.008466 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-01-04 16:02 | 2023-01-04 16:47 | 25 | 0:45 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23010400286 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2023-01-04 | 1125 | keep | 0 | Jan | 2023 | 0.00076623 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-01-04 16:10 | 2023-01-04 16:32 | 19 | 0:22 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE DE PALMA | R23010400139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-01-04 | 418 | keep | 0 | Jan | 2023 | 0.0002847 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2023-01-04 16:24 | 2023-01-04 19:54 | 300 | 3:30 | P | MAL TIEMPO/RAYOS | 2 X 65 Y 1 X 80 EN C/L MAL TIEMPO RAYOS | C23010400190 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 210 | 2023-01-04 | 63000 | keep | 0 | Jan | 2023 | 0.042909 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-01-04 16:26 | 2023-01-04 16:28 | 74 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1529-11 CERRADO X CONTROL | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-04 | 148 | keep | 0 | Jan | 2023 | 0.0001008 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2023-01-04 16:26 | 2023-01-04 16:28 | 1368 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO X CONTROL LLEVA 1521-02 | S2301040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-04 | 2736 | keep | 0 | Jan | 2023 | 0.0018635 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
CANOVANAS | 2023-01-04 16:43 | 2023-01-04 18:27 | 150 | 1:44 | P | NO SE REPORTO CAUSA | 1X80 EN LSU 2A | R23010400145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-01-04 | 15600 | keep | 0 | Jan | 2023 | 0.010625 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-01-04 16:47 | 2023-01-04 18:47 | 52 | 2:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y PARRRAYO. 1 X 50 EN C/L | B23010400092 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 120 | 2023-01-04 | 6240 | keep | 0 | Jan | 2023 | 0.00425 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CANOVANAS | 2023-01-04 17:00 | 2023-01-04 17:31 | 1 | 0:31 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYOS | R23010400148 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 31 | 2023-01-04 | 31 | keep | 0 | Jan | 2023 | 2.1114e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-04 17:10 | 2023-01-04 18:52 | 62 | 1:42 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYOS | C23010400203 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 102 | 2023-01-04 | 6324 | keep | 0 | Jan | 2023 | 0.0043072 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
SAN JUAN | 2023-01-04 17:17 | 2023-01-04 19:45 | 50 | 2:28 | P | DESGANCHE | 2 X 40 EN C/L Y DESGANCHE | S23010400323 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-01-04 | 7400 | keep | 0 | Jan | 2023 | 0.0050401 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-04 17:24 | 2023-01-05 10:31 | 22 | 17:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S23010400326 | New_Event | Cutout Failure | Include | Include | Equipment | 1027 | 2023-01-04 | 22594 | keep | 0 | Jan | 2023 | 0.015389 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-01-04 17:25 | 2023-01-04 18:27 | 9 | 1:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S23010400324 | New_Event | Secondary Wire Break | Include | Include | Equipment | 62 | 2023-01-04 | 558 | keep | 0 | Jan | 2023 | 0.00038005 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
GUAYAMA | 2023-01-04 17:30 | 2023-01-04 19:15 | 15 | 1:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 20 EN XMR MAL TIEMPO VIENTOS | P23010400349 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 105 | 2023-01-04 | 1575 | keep | 0 | Jan | 2023 | 0.0010727 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-04 17:33 | 2023-01-04 17:40 | 26 | 0:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SEC AVERIADA | B23010400094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 7 | 2023-01-04 | 182 | keep | 0 | Jan | 2023 | 0.00012396 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
MAYAGÃœEZ | 2023-01-04 17:36 | 2023-01-05 11:15 | 30 | 17:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23010400142 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1059 | 2023-01-04 | 31770 | keep | 0 | Jan | 2023 | 0.021638 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-01-04 17:55 | 2023-01-04 17:56 | 1089 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | C23010400225 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-01-04 | 1089 | keep | 0 | Jan | 2023 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2023-01-04 17:56 | 2023-01-04 20:58 | 198 | 3:02 | P | MAL TIEMPO/RAYOS | 2 X 80 EN C/L RAYOS | C23010400230 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 182 | 2023-01-04 | 36036 | keep | 0 | Jan | 2023 | 0.024544 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
AGUADILLA | 2023-01-04 18:08 | 2023-01-05 10:01 | 25 | 15:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23010400149 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 953 | 2023-01-04 | 23825 | keep | 0 | Jan | 2023 | 0.016227 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-01-04 18:11 | 2023-01-04 20:38 | 150 | 2:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L MAL TIEMPO VIENTOS | P23010400373 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 147 | 2023-01-04 | 22050 | keep | 0 | Jan | 2023 | 0.015018 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2023-01-04 18:29 | 2023-01-04 23:30 | 78 | 5:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23010400383 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2023-01-04 | 23478 | keep | 0 | Jan | 2023 | 0.015991 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
PONCE | 2023-01-04 18:29 | 2023-01-04 22:26 | 52 | 3:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA VIENTOS | P23010400386 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 237 | 2023-01-04 | 12324 | keep | 0 | Jan | 2023 | 0.0083938 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2023-01-04 18:47 | 2023-01-05 02:02 | 2 | 7:15 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR Y SE RETIRO ENREDADERA EN PRIMARIA | S23010400336 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2023-01-04 | 870 | keep | 0 | Jan | 2023 | 0.00059255 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-01-04 18:47 | 2023-01-04 21:39 | 93 | 2:52 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L Y 1 X 40 EN C/L MAL TIEMPO RAYOS | C23010400245 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 172 | 2023-01-04 | 15996 | keep | 0 | Jan | 2023 | 0.010895 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
CAGUAS | 2023-01-04 18:55 | 2023-01-04 20:48 | 77 | 1:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO AISLADOR | C23010400248 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 113 | 2023-01-04 | 8701 | keep | 0 | Jan | 2023 | 0.0059262 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
GUAYAMA | 2023-01-04 19:20 | 2023-01-04 20:41 | 10 | 1:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR FUERTE BRISA | P23010400419 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 81 | 2023-01-04 | 810 | keep | 0 | Jan | 2023 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-01-04 19:28 | 2023-01-05 09:26 | 4 | 13:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23010400162 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 838 | 2023-01-04 | 3352 | keep | 0 | Jan | 2023 | 0.002283 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-01-04 19:34 | 2023-01-04 22:16 | 15 | 2:42 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | R23010400164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-01-04 | 2430 | keep | 0 | Jan | 2023 | 0.0016551 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-04 19:39 | 2023-01-04 19:40 | 2861 | 0:01 | T | CAUSAS EXTERNAS | RECIERE DE BKR | B23010400104 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-01-04 | 2861 | keep | 0 | Jan | 2023 | 0.0019486 | 0.0019486 | Momentary | FALSE | FALSE | Not_TMED_Event | 2861
YAUCO | 2023-01-04 19:40 | 2023-01-05 08:46 | 20 | 13:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23010400425 | New_Event | Vegetation Contact | Include | Include | Vegetation | 786 | 2023-01-04 | 15720 | keep | 0 | Jan | 2023 | 0.010707 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-04 19:40 | 2023-01-04 22:50 | 105 | 3:10 | P | CAUSAS EXTERNAS | CAMION CRUZO CABLE COMUNICACIONES Y SE RETESO LINEA 1 X 65 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | B23010400106 | 1st_after_momentary | Damage From Public | Include | Include | Public | 190 | 2023-01-04 | 19950 | keep | 0 | Jan | 2023 | 0.013588 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
SAN JUAN | 2023-01-04 19:45 | 2023-01-04 19:46 | 1573 | 0:01 | T | DESGANCHE | RECIERRE DE BKR | S2301040000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-04 | 1573 | keep | 0 | Jan | 2023 | 0.0010714 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-04 19:46 | 2023-01-04 21:30 | 50 | 1:44 | P | DESGANCHE | 2 X 40 EN C/L Y DESGANCHE | S23010400323 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-01-04 | 5200 | keep | 0 | Jan | 2023 | 0.0035417 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-01-04 20:21 | 2023-01-05 06:00 | 54 | 9:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23010400439 | New_Event | Vegetation Contact | Include | Include | Vegetation | 579 | 2023-01-04 | 31266 | keep | 0 | Jan | 2023 | 0.021295 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
VEGA BAJA | 2023-01-04 20:29 | 2023-01-05 07:35 | 30 | 11:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A23010400160 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 666 | 2023-01-04 | 19980 | keep | 0 | Jan | 2023 | 0.013608 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-04 20:33 | 2023-01-05 10:39 | 11 | 14:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S23010400347 | New_Event | Cutout Failure | Include | Include | Equipment | 846 | 2023-01-04 | 9306 | keep | 0 | Jan | 2023 | 0.0063383 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2023-01-04 20:33 | 2023-01-04 21:31 | 90 | 0:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA POR MASETILLA QUEMADA | A23010400161 | New_Event | Cutout Failure | Include | Include | Equipment | 58 | 2023-01-04 | 5220 | keep | 0 | Jan | 2023 | 0.0035553 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2023-01-04 20:46 | 2023-01-05 07:46 | 15 | 11:00 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN XMR TOMA SECUNDARIA CRUZADA, SE DEJO CLIENTE FUERA | B23010400112 | New_Event | Customer-Related Interruption | Include | Include | Public | 660 | 2023-01-04 | 9900 | keep | 0 | Jan | 2023 | 0.0067428 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-01-04 21:33 | 2023-01-04 21:34 | 2192 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23010400268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-04 | 2192 | keep | 0 | Jan | 2023 | 0.001493 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
AGUADILLA | 2023-01-04 21:38 | 2023-01-05 00:54 | 250 | 3:16 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y SE CERRO CORTE DE LINEA | M23010400182 | New_Event | Primary Wire Break | Include | Include | Equipment | 196 | 2023-01-04 | 49000 | keep | 0 | Jan | 2023 | 0.033374 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
HUMACAO | 2023-01-04 21:46 | 2023-01-04 22:58 | 16 | 1:12 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L Y 1 X 10 EN XMR RAYOS | C23010400270 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 72 | 2023-01-04 | 1152 | keep | 0 | Jan | 2023 | 0.00078462 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2023-01-04 22:02 | 2023-01-05 12:35 | 18 | 14:33 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR DE 75 KVA A 2.4 KV AVERIADO | P23010400456 | New_Event | Service Transformer Failure | Include | Include | Equipment | 873 | 2023-01-04 | 15714 | keep | 0 | Jan | 2023 | 0.010703 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-01-04 22:18 | 2023-01-05 01:21 | 80 | 3:03 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23010400272 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2023-01-04 | 14640 | keep | 0 | Jan | 2023 | 0.0099712 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2023-01-04 22:23 | 2023-01-05 07:13 | 25 | 8:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23010400187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 530 | 2023-01-04 | 13250 | keep | 0 | Jan | 2023 | 0.0090245 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-01-04 22:23 | 2023-01-04 23:33 | 14 | 1:10 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA DESGANCHE SECUNDARIO Y REPARAR NEUTRAL SECUNDARIO | B23010400098 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 70 | 2023-01-04 | 980 | keep | 0 | Jan | 2023 | 0.00066747 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-01-04 22:49 | 2023-01-05 01:40 | 2179 | 2:51 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DEL BKR 0050 POR MALA OPERACION DEL BKR 1619-03 EL CUAL ESTA DEFECTUOSO. | R23010500171 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 171 | 2023-01-04 | 372609 | keep | 0 | Jan | 2023 | 0.25378 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2023-01-04 22:49 | 2023-01-05 05:12 | 2025 | 6:23 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE LA ALTA BKR 0050 POR MALA OPERACION DEL BKR 1619-03 SE DEJO FUERA Y DESACOPLADO EL BKR 1619-03.60% DE LA CARGA POR EL 1336-06. SE TRANSFIRIO LA CARGA AL 1619-01 SE ENERGIZO EL 30% | R23010500171 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 383 | 2023-01-04 | 775575 | keep | 0 | Jan | 2023 | 0.52824 | 0.0013792 | Sustained | FALSE | FALSE | Not_TMED_Event | 2025
BAYAMON | 2023-01-04 23:00 | 2023-01-04 23:36 | 1 | 0:36 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B23010400121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2023-01-04 | 36 | keep | 0 | Jan | 2023 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-04 23:39 | 2023-01-05 00:26 | 75 | 0:47 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE PUENTE PARA RETIRAR PELIGRO DE LINEA PRIMARIA PARTIDA | A23010400181 | New_Event | Primary Wire Break | Include | Include | Equipment | 47 | 2023-01-04 | 3525 | keep | 0 | Jan | 2023 | 0.0024009 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-01-05 00:26 | 2023-01-05 09:59 | 1 | 9:33 | P | MAL TIEMPO/RAYOS | 1 X 50 Y 1 X 40 EN C/LS RAYOS | C23010500002 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 573 | 2023-01-05 | 573 | keep | 0 | Jan | 2023 | 0.00039027 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-05 00:26 | 2023-01-05 03:40 | 150 | 3:14 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE PUENTE PARA RETIRAR PELIGRO DE LINEA PRIMARIA PARTIDA Y SE CIERRA CORTE DE LINEA | A23010500001 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 194 | 2023-01-05 | 29100 | keep | 0 | Jan | 2023 | 0.01982 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-01-05 03:40 | 2023-01-05 20:29 | 75 | 16:49 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO | A23010500114 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1009 | 2023-01-05 | 75675 | keep | 0 | Jan | 2023 | 0.051542 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-05 03:55 | 2023-01-05 03:56 | 863 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1119-04 | S2301050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-05 | 863 | keep | 0 | Jan | 2023 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2023-01-05 03:55 | 2023-01-05 03:56 | 2720 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1115-01 | S23010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 2720 | keep | 0 | Jan | 2023 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2023-01-05 04:56 | 2023-01-05 06:18 | 15 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 20 EN PROVISIONAL | B23010500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2023-01-05 | 1230 | keep | 0 | Jan | 2023 | 0.00083775 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-01-05 05:12 | 2023-01-05 05:28 | 1418 | 0:16 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | SE CERRO N/O CONTRA EL 1619-01 PERO SE TUVO QUE ABRIR EL AMARRE NUEVAMENTE POR TRAMO SOTERRADO AVERIADO | R23010500171 | Partial_restoration | Feeder Breaker Failure | Include | Include | Equipment | 16 | 2023-01-05 | 22688 | keep | 0 | Jan | 2023 | 0.015453 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-05 05:17 | 2023-01-05 08:22 | 10 | 3:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A23010500008 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2023-01-05 | 1850 | keep | 0 | Jan | 2023 | 0.00126 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-05 05:28 | 2023-01-05 05:38 | 2025 | 0:10 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE CERRO N/O CONTRA EL 1336-06 100% EN SERVICIO | R23010500171 | Additional_clients | Feeder Breaker Failure | Include | Include | Equipment | 10 | 2023-01-05 | 20250 | keep | 0 | Jan | 2023 | 0.013792 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-05 06:32 | 2023-01-05 10:24 | 67 | 3:52 | P | CABLE SOTERRADO AVERIADO | AVERIA T-114 @ T-115 1 X 40 EN PROVISIONAL SE QUEDA FUERA T-115 | B23010500006 | New_Event | UG Cable Fault | Include | Include | Equipment | 232 | 2023-01-05 | 15544 | keep | 0 | Jan | 2023 | 0.010587 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
CANOVANAS | 2023-01-05 06:34 | 2023-01-05 13:29 | 178 | 6:55 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | R23010500111 | New_Event | Primary Wire Break | Include | Include | Equipment | 415 | 2023-01-05 | 73870 | keep | 0 | Jan | 2023 | 0.050313 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
HUMACAO | 2023-01-05 06:34 | 2023-01-05 13:29 | 6 | 6:55 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYO | C23010500002 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 415 | 2023-01-05 | 2490 | keep | 0 | Jan | 2023 | 0.0016959 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-01-05 06:47 | 2023-01-05 18:30 | 88 | 11:43 | P | DESGANCHE | SE ABRIO C/L PARA DESGANCHE | C23010500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 703 | 2023-01-05 | 61864 | keep | 0 | Jan | 2023 | 0.042135 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
HUMACAO | 2023-01-05 06:55 | 2023-01-05 08:55 | 2450 | 2:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 12600 | C23010500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2023-01-05 | 294000 | keep | 0 | Jan | 2023 | 0.20024 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-01-05 06:55 | 2023-01-05 08:55 | 640 | 2:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 12600 | C23010500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2023-01-05 | 76800 | keep | 0 | Jan | 2023 | 0.052308 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
VEGA BAJA | 2023-01-05 07:02 | 2023-01-05 17:57 | 15 | 10:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23010500008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 655 | 2023-01-05 | 9825 | keep | 0 | Jan | 2023 | 0.0066918 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-05 07:11 | 2023-01-05 10:53 | 99 | 3:42 | P | DESGANCHE | 1 X 80 EN C/L | B23010500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-01-05 | 21978 | keep | 0 | Jan | 2023 | 0.014969 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
CAGUAS | 2023-01-05 07:56 | 2023-01-05 11:29 | 6 | 3:33 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C23010500012 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 213 | 2023-01-05 | 1278 | keep | 0 | Jan | 2023 | 0.00087044 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-01-05 07:56 | 2023-01-05 10:45 | 10 | 2:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23010500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-01-05 | 1690 | keep | 0 | Jan | 2023 | 0.0011511 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-05 07:58 | 2023-01-05 09:38 | 10 | 1:40 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23010500013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2023-01-05 | 1000 | keep | 0 | Jan | 2023 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-05 07:59 | 2023-01-05 09:20 | 1 | 1:21 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO BAJANTE ZAFADO EN RISER | P23010500031 | New_Event | Primary Wire Break | Include | Include | Equipment | 81 | 2023-01-05 | 81 | keep | 0 | Jan | 2023 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-05 08:10 | 2023-01-05 09:10 | 10 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23010500013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-01-05 | 600 | keep | 0 | Jan | 2023 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-05 08:23 | 2023-01-05 10:14 | 10 | 1:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23010500017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 111 | 2023-01-05 | 1110 | keep | 0 | Jan | 2023 | 0.00075602 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-01-05 09:00 | 2023-01-05 13:40 | 10 | 4:40 | P | DESGANCHE | ABRIO XMR PARA DESGANCHE PRIMARIO Y REMPLAZO BAJANTES PRIMARIO Y SECUNDARIO Y PARARRAYO | C23010500025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2023-01-05 | 2800 | keep | 0 | Jan | 2023 | 0.0019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-05 09:12 | 2023-01-05 09:13 | 3597 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23010500018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 3597 | keep | 0 | Jan | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
PONCE | 2023-01-05 09:12 | 2023-01-05 10:56 | 2 | 1:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P23010500041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-01-05 | 208 | keep | 0 | Jan | 2023 | 0.00014167 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-01-05 09:20 | 2023-01-05 12:48 | 10 | 3:28 | P | MAL TIEMPO/RAYOS | 2 X 10 EN XMR SE REMPLAZO XMR 35.5KV AVERIADO POR RAYO | C23010500030 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 208 | 2023-01-05 | 2080 | keep | 0 | Jan | 2023 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-01-05 09:20 | 2023-01-06 09:40 | 11 | 24:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23010500072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1460 | 2023-01-05 | 16060 | keep | 0 | Jan | 2023 | 0.010938 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-01-05 09:25 | 2023-01-05 11:27 | 81 | 2:02 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23010500033 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-01-05 | 9882 | keep | 0 | Jan | 2023 | 0.0067306 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2023-01-05 09:30 | 2023-01-05 09:31 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23010500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 2605 | keep | 0 | Jan | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
MAYAGÃœEZ | 2023-01-05 09:30 | 2023-01-05 13:35 | 8 | 4:05 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE EN MALAS CONDICIONES | M23010500027 | New_Event | Primary Pole Failure | Include | Include | Equipment | 245 | 2023-01-05 | 1960 | keep | 0 | Jan | 2023 | 0.0013349 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-01-05 09:36 | 2023-01-05 10:51 | 1 | 1:15 | P | NO SE REPORTO CAUSA | 2 X 25 EN BANCO DE TRANSFORMADOR | R23010500133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2023-01-05 | 75 | keep | 0 | Jan | 2023 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-01-05 09:38 | 2023-01-05 12:09 | 4 | 2:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23010500026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 151 | 2023-01-05 | 604 | keep | 0 | Jan | 2023 | 0.00041138 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-01-05 09:52 | 2023-01-05 11:15 | 18 | 1:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO CONECTORES DE BAJANTE, SE RETEZO TOMA DE SERVICIO Y RETIRO POSTE | B23010500027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 83 | 2023-01-05 | 1494 | keep | 0 | Jan | 2023 | 0.0010176 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2023-01-05 09:53 | 2023-01-05 11:50 | 12 | 1:57 | P | ANIMAL | 1 X 10 EN XMR SE RETIRO CULEBRA | B23010500028 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-01-05 | 1404 | keep | 0 | Jan | 2023 | 0.00095626 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-01-05 09:56 | 2023-01-05 12:55 | 80 | 2:59 | P | NO SE REPORTO CAUSA | 2 X 80 EN RISER | C23010500042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2023-01-05 | 14320 | keep | 0 | Jan | 2023 | 0.0097533 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-01-05 09:56 | 2023-01-05 16:32 | 1 | 6:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN BANCO DE XMR SE REEMPLAZO CAJA | C23010500041 | New_Event | Cutout Failure | Include | Include | Equipment | 396 | 2023-01-05 | 396 | keep | 0 | Jan | 2023 | 0.00026971 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-01-05 09:57 | 2023-01-05 14:45 | 4 | 4:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23010500029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 288 | 2023-01-05 | 1152 | keep | 0 | Jan | 2023 | 0.00078462 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-01-05 10:00 | 2023-01-05 12:02 | 5 | 2:02 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR PARA REPARAR PEDESTAL AVERIADO | M23010400130 | New_Event |  |  |  |  | 122 | 2023-01-05 | 610 | keep | 0 | Jan | 2023 | 0.00041547 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-01-05 10:05 | 2023-01-05 12:04 | 20 | 1:59 | P | DESGANCHE | 3 X 100 C/L DESGANCHE | C23010500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-01-05 | 2380 | keep | 0 | Jan | 2023 | 0.001621 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-01-05 10:13 | 2023-01-05 17:15 | 50 | 7:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M23010500034 | New_Event | Primary Wire Break | Include | Include | Equipment | 422 | 2023-01-05 | 21100 | keep | 0 | Jan | 2023 | 0.014371 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-01-05 10:14 | 2023-01-05 14:55 | 150 | 4:41 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23010500034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2023-01-05 | 42150 | keep | 0 | Jan | 2023 | 0.028708 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2023-01-05 10:21 | 2023-01-05 15:03 | 12 | 4:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23010500063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 282 | 2023-01-05 | 3384 | keep | 0 | Jan | 2023 | 0.0023048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-01-05 10:22 | 2023-01-05 11:20 | 50 | 0:58 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR PAJARO CRUZO FASE | P23010500065 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-01-05 | 2900 | keep | 0 | Jan | 2023 | 0.0019752 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-05 10:24 | 2023-01-05 10:30 | 356 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO DE UNIDAD 5 SAN JUAN BKR 1328-01 LLEVA 1342-01 Y LLEVA 1342-03 | S2301050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-01-05 | 2136 | keep | 0 | Jan | 2023 | 0.0014548 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
SAN JUAN | 2023-01-05 10:24 | 2023-01-05 10:30 | 29 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO DE UNIDAD 5 SAN JUAN BKR 1328-01 LLEVA 1342-01 Y LLEVA 1342-03 | S2301050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-01-05 | 174 | keep | 0 | Jan | 2023 | 0.00011851 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2023-01-05 10:30 | 2023-01-05 12:19 | 67 | 1:49 | P | CABLE SOTERRADO AVERIADO | AVERIA T-114 @ T-115 1 X 40 EN PROVISIONAL SE QUEDA FUERA T-115 | B23010500006 | New_Event | UG Cable Fault | Include | Include | Equipment | 109 | 2023-01-05 | 7303 | keep | 0 | Jan | 2023 | 0.004974 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2023-01-05 10:30 | 2023-01-05 18:25 | 20 | 7:55 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | B23010400054 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 475 | 2023-01-05 | 9500 | keep | 0 | Jan | 2023 | 0.0064704 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-05 10:31 | 2023-01-05 10:32 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1206-01 LLEVANDO 1206-02 | S2301050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 338 | keep | 0 | Jan | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2023-01-05 10:31 | 2023-01-05 10:32 | 733 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE 1206-01 LLEVANDO 1206-02 | S2301050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-05 | 733 | keep | 0 | Jan | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2023-01-05 10:32 | 2023-01-05 12:42 | 22 | 2:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S23010400326 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 130 | 2023-01-05 | 2860 | keep | 0 | Jan | 2023 | 0.0019479 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-01-05 10:33 | 2023-01-05 16:18 | 4 | 5:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE RELOCALIZO TRANSFORMADOR A POSTE NUEVO Y LINEA | C23010500072 | New_Event | Primary Pole Failure | Include | Include | Equipment | 345 | 2023-01-05 | 1380 | keep | 0 | Jan | 2023 | 0.00093991 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-01-05 10:47 | 2023-01-05 12:28 | 138 | 1:41 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23010500056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-01-05 | 13938 | keep | 0 | Jan | 2023 | 0.0094931 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-01-05 10:48 | 2023-01-05 12:42 | 1483 | 1:54 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 5% DEL 1336-07 LLEVA 30% DEL 1204-04 Y LLEVA 15% DEL 1204-05 | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 114 | 2023-01-05 | 169062 | keep | 0 | Jan | 2023 | 0.11515 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-01-05 10:48 | 2023-01-05 12:42 | 1531 | 1:54 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 5% DEL 1336-07 LLEVA 30% DEL 1204-04 Y LLEVA 15% DEL 1204-05 | S2301040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 114 | 2023-01-05 | 174534 | keep | 0 | Jan | 2023 | 0.11887 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-01-05 10:48 | 2023-01-05 12:42 | 312 | 1:54 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA. EN SERVICIO 5% 1336-07 Y 10 % 1336-08. FUERA 30% 1204-04 Y 15% 1204-05 | S23010500073 | New_Event | Feeder Load Transferred | Include | Include | Other | 114 | 2023-01-05 | 35568 | keep | 0 | Jan | 2023 | 0.024225 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-01-05 10:48 | 2023-01-05 12:42 | 5290 | 1:54 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA. EN SERVICIO 5% 1336-07 Y 10 % 1336-08. FUERA 30% 1204-04 Y 15% 1204-05 | S23010500073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-01-05 | 603060 | keep | 0 | Jan | 2023 | 0.41074 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
PONCE | 2023-01-05 10:48 | 2023-01-05 12:05 | 1 | 1:17 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN CORTE DE LINEA LINEA CRUZADA | P23010500070 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 77 | 2023-01-05 | 77 | keep | 0 | Jan | 2023 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-05 10:51 | 2023-01-05 14:22 | 1 | 3:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER 3 X 25 EN TRANSCLOSURE | B23010500060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2023-01-05 | 211 | keep | 0 | Jan | 2023 | 0.00014371 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-05 10:55 | 2023-01-05 13:08 | 10 | 2:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23010300092 | New_Event | Secondary Wire Break | Include | Include | Equipment | 133 | 2023-01-05 | 1330 | keep | 0 | Jan | 2023 | 0.00090586 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-05 11:02 | 2023-01-05 18:27 | 100 | 7:25 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P23010500076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 445 | 2023-01-05 | 44500 | keep | 0 | Jan | 2023 | 0.030309 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-01-05 11:05 | 2023-01-05 13:47 | 150 | 2:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M23010500048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-01-05 | 24300 | keep | 0 | Jan | 2023 | 0.016551 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2023-01-05 11:21 | 2023-01-05 11:22 | 1173 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010500079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 1173 | keep | 0 | Jan | 2023 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
YAUCO | 2023-01-05 11:22 | 2023-01-05 15:00 | 60 | 3:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23010500051 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 218 | 2023-01-05 | 13080 | keep | 0 | Jan | 2023 | 0.0089087 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-01-05 11:23 | 2023-01-05 15:30 | 47 | 4:07 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CAJA A LINEA NO FUNDIO | C23010500103 | New_Event | Primary Wire Break | Include | Include | Equipment | 247 | 2023-01-05 | 11609 | keep | 0 | Jan | 2023 | 0.0079068 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2023-01-05 11:28 | 2023-01-05 16:30 | 16 | 5:02 | P | DESGANCHE | 1 X 65 EN C/L Y SE REALIZO DESGANCHE DE BAMBUA | C23010500106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2023-01-05 | 4832 | keep | 0 | Jan | 2023 | 0.0032911 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2023-01-05 11:44 | 2023-01-05 11:45 | 860 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010500088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 860 | keep | 0 | Jan | 2023 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
AGUADILLA | 2023-01-05 11:54 | 2023-01-05 14:10 | 1 | 2:16 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO CAUSA | M23010500064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2023-01-05 | 136 | keep | 0 | Jan | 2023 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-01-05 12:01 | 2023-01-05 15:00 | 9 | 2:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR MAL TIEMPO VIENTOS | P23010500091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 179 | 2023-01-05 | 1611 | keep | 0 | Jan | 2023 | 0.0010972 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2023-01-05 12:10 | 2023-01-05 12:11 | 860 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010500092 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 860 | keep | 0 | Jan | 2023 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
CAGUAS | 2023-01-05 12:14 | 2023-01-05 15:18 | 5 | 3:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REEMPLAZO PORTAFUSIBLE | C23010500116 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2023-01-05 | 920 | keep | 0 | Jan | 2023 | 0.00062661 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-05 12:19 | 2023-01-05 22:58 | 12 | 10:39 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL DE EXISTENTE A T-115 | B23010500006 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 639 | 2023-01-05 | 7668 | keep | 0 | Jan | 2023 | 0.0052226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-01-05 12:19 | 2023-01-05 15:01 | 12 | 2:42 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L SE DESPEGO LINEA CRUZADA POR IMPACTO DE CAMION DE COMPAÃ‘IA DE LIBERTY | C23010500117 | New_Event | Damage From Public | Include | Include | Public | 162 | 2023-01-05 | 1944 | keep | 0 | Jan | 2023 | 0.001324 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-01-05 12:23 | 2023-01-05 14:41 | 5 | 2:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23010500066 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 138 | 2023-01-05 | 690 | keep | 0 | Jan | 2023 | 0.00046996 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-05 12:42 | 2023-01-05 13:21 | 1483 | 0:39 | P | ALIMENTADOR AMARRADO | SE CERRO INTERRUPTOR DE POSTE ENTRO EN SERVICIO 50% 1336-08 Y 30% 1204-04. FUERA 15%1204-05 | S23010500073 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 39 | 2023-01-05 | 57837 | keep | 0 | Jan | 2023 | 0.039393 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-05 12:42 | 2023-01-05 12:47 | 338 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DEL 1206-01 LLEVA 1206-02 SE CERRO POR SCADA | S23010500380 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-01-05 | 1690 | keep | 0 | Jan | 2023 | 0.0011511 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2023-01-05 12:42 | 2023-01-05 12:47 | 733 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1206-01 LLEVA 1206-02 SE CERRO POR SCADA | S23010500380 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 5 | 2023-01-05 | 3665 | keep | 0 | Jan | 2023 | 0.0024962 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2023-01-05 12:42 | 2023-01-05 13:21 | 4761 | 0:39 | P | DESGANCHE | SE CERRO INTERRUPTOR DE POSTE ENTRO EN SERVICIO 50% 1336-08 Y 30% 1204-04 | S23010500073 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 39 | 2023-01-05 | 185679 | keep | 0 | Jan | 2023 | 0.12647 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-01-05 12:46 | 2023-01-05 20:46 | 140 | 8:00 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 EN C/L SE REPARO ALAMBRES PRIMARIOS PARTIDOS | P23010500098 | New_Event | Primary Wire Break | Include | Include | Equipment | 480 | 2023-01-05 | 67200 | keep | 0 | Jan | 2023 | 0.04577 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
SAN JUAN | 2023-01-05 12:47 | 2023-01-05 13:43 | 22 | 0:56 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN PROVICIONAL NUEVO POR AVERIA DE RISER A T 7. SE REEMPLAZO CAJA PRIMARIA | S23010400326 | New_Event | UG Cable Fault | Include | Include | Equipment | 56 | 2023-01-05 | 1232 | keep | 0 | Jan | 2023 | 0.00083911 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-01-05 12:47 | 2023-01-05 16:30 | 17 | 3:43 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE DESGANCHO SECUNDARIO | B23010500087 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 223 | 2023-01-05 | 3791 | keep | 0 | Jan | 2023 | 0.002582 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-01-05 12:48 | 2023-01-05 14:15 | 40 | 1:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23010500075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 87 | 2023-01-05 | 3480 | keep | 0 | Jan | 2023 | 0.0023702 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-01-05 12:54 | 2023-01-05 15:11 | 7 | 2:17 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYOS | R23010500203 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 137 | 2023-01-05 | 959 | keep | 0 | Jan | 2023 | 0.00065317 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-01-05 12:55 | 2023-01-05 12:56 | 1879 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 3006-05 | C2301050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 1879 | keep | 0 | Jan | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-01-05 12:55 | 2023-01-05 12:56 | 3005 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL CARGA X 3006-02 | C2301050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-05 | 3005 | keep | 0 | Jan | 2023 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
BAYAMON | 2023-01-05 13:05 | 2023-01-05 13:40 | 10 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23010500090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-01-05 | 350 | keep | 0 | Jan | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-05 13:14 | 2023-01-05 13:16 | 2466 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S2301050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-05 | 4932 | keep | 0 | Jan | 2023 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
VEGA BAJA | 2023-01-05 13:18 | 2023-01-05 16:24 | 3 | 3:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA PARTIDA | A23010500074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 186 | 2023-01-05 | 558 | keep | 0 | Jan | 2023 | 0.00038005 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-01-05 13:21 | 2023-01-05 14:44 | 1532 | 1:23 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR PARA REEMPLAZAR AISLADORES PARTIDOS. 70% 1336-08 Y 15% 1204-05 EN SERVICIO | S23010500073 | New_Event | Feeder Load Transferred | Include | Include | Other | 83 | 2023-01-05 | 127156 | keep | 0 | Jan | 2023 | 0.086605 | 0.0010434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1532
SAN JUAN | 2023-01-05 13:21 | 2023-01-05 14:44 | 2645 | 1:23 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR PARA REEMPLAZAR AISLADORES PARTIDOS. 70% 1336-08 Y 15% 1204-05 EN SERVICIO | S23010500073 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-01-05 | 219535 | keep | 0 | Jan | 2023 | 0.14952 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-05 13:28 | 2023-01-05 16:01 | 52 | 2:33 | P | DESGANCHE | DESGANCHE Y 2 X 65 EN C/L | S23010500596 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-01-05 | 7956 | keep | 0 | Jan | 2023 | 0.0054188 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
HUMACAO | 2023-01-05 13:39 | 2023-01-05 15:15 | 12 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZO DE BAJANTE SECUNDARIO | C23010500134 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2023-01-05 | 1152 | keep | 0 | Jan | 2023 | 0.00078462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-01-05 13:44 | 2023-01-05 15:00 | 80 | 1:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23010500085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-01-05 | 6080 | keep | 0 | Jan | 2023 | 0.0041411 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-05 13:46 | 2023-01-05 13:47 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1118-10 LLEVA 20% 1111-01 | S2301050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-05 | 513 | keep | 0 | Jan | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-01-05 13:46 | 2023-01-05 13:47 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1118-10 LLEVA 20% 1111-01 | S2301050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 2782 | keep | 0 | Jan | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2023-01-05 13:46 | 2023-01-05 18:09 | 90 | 4:23 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23010500496 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2023-01-05 | 23670 | keep | 0 | Jan | 2023 | 0.016122 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2023-01-05 13:51 | 2023-01-05 15:14 | 20 | 1:23 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23010500135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-01-05 | 1660 | keep | 0 | Jan | 2023 | 0.0011306 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-01-05 13:55 | 2023-01-05 14:40 | 40 | 0:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTE 1 X 40 EN CORTE DE LINEA | R23010500211 | New_Event | Primary Pole Failure | Include | Include | Equipment | 45 | 2023-01-05 | 1800 | keep | 0 | Jan | 2023 | 0.001226 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-01-05 13:56 | 2023-01-05 13:57 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2301050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 3464 | keep | 0 | Jan | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
PONCE | 2023-01-05 14:06 | 2023-01-05 15:12 | 20 | 1:06 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO | P23010500099 | New_Event | Primary Wire Break | Include | Include | Equipment | 66 | 2023-01-05 | 1320 | keep | 0 | Jan | 2023 | 0.00089905 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-05 14:11 | 2023-01-05 17:51 | 30 | 3:40 | P | DESGANCHE | 1 X 30 EN C/L Y SE REALIZO DESGANCHE | B23010500098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-01-05 | 6600 | keep | 0 | Jan | 2023 | 0.0044952 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-01-05 14:14 | 2023-01-05 18:20 | 100 | 4:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23010500083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2023-01-05 | 24600 | keep | 0 | Jan | 2023 | 0.016755 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-01-05 14:19 | 2023-01-05 18:10 | 50 | 3:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23010500099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2023-01-05 | 11550 | keep | 0 | Jan | 2023 | 0.0078667 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-05 14:20 | 2023-01-05 15:27 | 89 | 1:07 | P | DESGANCHE | SE DESGANCHO Y 1 X 200 EN CL | S23010500559 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2023-01-05 | 5963 | keep | 0 | Jan | 2023 | 0.0040614 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
ARECIBO | 2023-01-05 14:35 | 2023-01-05 18:40 | 70 | 4:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23010500088 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 245 | 2023-01-05 | 17150 | keep | 0 | Jan | 2023 | 0.011681 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-01-05 14:36 | 2023-01-05 17:00 | 10 | 2:24 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEAS CRUZADAS | M23010500104 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 144 | 2023-01-05 | 1440 | keep | 0 | Jan | 2023 | 0.00098078 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-05 14:40 | 2023-01-05 19:30 | 15 | 4:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE XMR Y POSTE DE 45 PIES | R23010500211 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 290 | 2023-01-05 | 4350 | keep | 0 | Jan | 2023 | 0.0029628 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-05 14:44 | 2023-01-05 15:47 | 1587 | 1:03 | P | DESGANCHE | SE REEMPLAZARON AISLADORES Y SE CERRO MACHETES SECCIONALIZANDO ALIMENTADOR PARA DESGANCHE. 75% 1336-08 EN SERVICIO | S23010500073 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-01-05 | 99981 | keep | 0 | Jan | 2023 | 0.068097 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-05 14:44 | 2023-01-05 17:16 | 17 | 2:32 | P | ANIMAL | 1 X 20 EN C/L CRUCE X AVE | C23010500145 | New_Event | Animals | Include | Include | Wildlife | 152 | 2023-01-05 | 2584 | keep | 0 | Jan | 2023 | 0.00176 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-01-05 14:49 | 2023-01-05 16:52 | 60 | 2:03 | P | NO SE REPORTO CAUSA | 2 X100 EN C/L NO CAUSA | S23010500558 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2023-01-05 | 7380 | keep | 0 | Jan | 2023 | 0.0050265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-01-05 15:22 | 2023-01-05 17:20 | 28 | 1:58 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE AVERIADO | C23010500158 | New_Event | Primary Wire Break | Include | Include | Equipment | 118 | 2023-01-05 | 3304 | keep | 0 | Jan | 2023 | 0.0022503 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
ARECIBO | 2023-01-05 15:30 | 2023-01-05 16:00 | 7 | 0:30 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO | A23010500003 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 30 | 2023-01-05 | 210 | keep | 0 | Jan | 2023 | 0.00014303 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-01-05 15:39 | 2023-01-05 15:40 | 40 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE BKR SOLO LLEVA 10% DE SU CARGA 90% POR 1620-01 | S2301050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 40 | keep | 0 | Jan | 2023 | 2.7244e-05 | 2.7244e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-05 15:47 | 2023-01-05 16:50 | 1322 | 1:03 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO CON VARETA Y SE CERRO MACHETES | S23010500073 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-01-05 | 83286 | keep | 0 | Jan | 2023 | 0.056726 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-01-05 15:54 | 2023-01-05 18:03 | 30 | 2:09 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23010500160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-01-05 | 3870 | keep | 0 | Jan | 2023 | 0.0026358 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-05 16:28 | 2023-01-05 16:48 | 10 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23010500116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-01-05 | 200 | keep | 0 | Jan | 2023 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-01-05 16:37 | 2023-01-05 20:13 | 25 | 3:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23010500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2023-01-05 | 5400 | keep | 0 | Jan | 2023 | 0.0036779 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-05 16:40 | 2023-01-06 11:30 | 25 | 18:50 | P | SECUNDARIA/DESGANCHE | 1 X 30 EN XMR SE REALIZO DESGANCHE SECUNDARIO | S23010500726 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1130 | 2023-01-05 | 28250 | keep | 0 | Jan | 2023 | 0.019241 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-01-05 16:41 | 2023-01-05 17:41 | 15 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23010500119 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-01-05 | 900 | keep | 0 | Jan | 2023 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-01-05 16:46 | 2023-01-05 19:05 | 100 | 2:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLACION | M23010500147 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 139 | 2023-01-05 | 13900 | keep | 0 | Jan | 2023 | 0.0094672 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-01-05 16:55 | 2023-01-05 20:45 | 19 | 3:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5 X 37.5 KVA 2 X 10 EN TRANSFORMADOR | R23010500232 | New_Event | Service Transformer Failure | Include | Include | Equipment | 230 | 2023-01-05 | 4370 | keep | 0 | Jan | 2023 | 0.0029764 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-01-05 17:02 | 2023-01-05 18:20 | 200 | 1:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA 1 X 80 EN C/L | S23010500745 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2023-01-05 | 15600 | keep | 0 | Jan | 2023 | 0.010625 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-01-05 17:04 | 2023-01-05 18:42 | 41 | 1:38 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23010500175 | New_Event | Animals | Include | Include | Wildlife | 98 | 2023-01-05 | 4018 | keep | 0 | Jan | 2023 | 0.0027366 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CAGUAS | 2023-01-05 17:10 | 2023-01-05 19:06 | 214 | 1:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23010500176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2023-01-05 | 24824 | keep | 0 | Jan | 2023 | 0.016908 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
SAN JUAN | 2023-01-05 17:24 | 2023-01-05 19:24 | 11 | 2:00 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN PROVICIONAL NUEVO POR AVERIA DE RISER A T 7. | S23010400326 | New_Event | UG Cable Fault | Include | Include | Equipment | 120 | 2023-01-05 | 1320 | keep | 0 | Jan | 2023 | 0.00089905 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2023-01-05 17:24 | 2023-01-05 22:29 | 24 | 5:05 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE LEVANTO CONDUCTOR PRIMARIO Y NEUTRAL | C23010500180 | New_Event | Primary Wire Break | Include | Include | Equipment | 305 | 2023-01-05 | 7320 | keep | 0 | Jan | 2023 | 0.0049856 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
AGUADILLA | 2023-01-05 18:08 | 2023-01-05 18:50 | 100 | 0:42 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23010500166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 42 | 2023-01-05 | 4200 | keep | 0 | Jan | 2023 | 0.0028606 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-01-05 18:29 | 2023-01-05 18:30 | 1879 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 3006-02 QUE LLEVA 3006-05 SE CERRO POR CONTROL | C23010500198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 1879 | keep | 0 | Jan | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-01-05 18:29 | 2023-01-05 18:30 | 3005 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE 3006-02 QUE LLEVA 3006-05 SE CERRO POR CONTROL | C23010500198 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-05 | 3005 | keep | 0 | Jan | 2023 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CANOVANAS | 2023-01-05 18:33 | 2023-01-05 18:34 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23010500236 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 2039 | keep | 0 | Jan | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
GUAYAMA | 2023-01-05 18:53 | 2023-01-05 21:30 | 37 | 2:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO VIENTOS | P23010500163 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 157 | 2023-01-05 | 5809 | keep | 0 | Jan | 2023 | 0.0039565 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-01-05 19:02 | 2023-01-06 00:37 | 74 | 5:35 | T | ALIMENTADOR AMARRADO | SE REPARO PUENTE PRIMARIO DE LINEA A MACHETE 1529-11 | S23010500765 | New_Event | Feeder Load Transferred | Include | Include | Other | 335 | 2023-01-05 | 24790 | keep | 0 | Jan | 2023 | 0.016884 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2023-01-05 19:02 | 2023-01-05 21:59 | 1368 | 2:57 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALAMBRE ABIERTO DE LINEA A MACHETE CONTINUA FUERA 1521-02 | S23010500765 | New_Event | Primary Wire Break | Include | Include | Equipment | 177 | 2023-01-05 | 242136 | keep | 0 | Jan | 2023 | 0.16492 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
BAYAMON | 2023-01-05 19:02 | 2023-01-05 19:03 | 723 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 1711-05 LLEVA 10% 1711-04 | B2301050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 723 | keep | 0 | Jan | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-01-05 19:02 | 2023-01-05 19:03 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1711-02 Y SE CERRO POR CONTROL 10% X 1711-02 | B2301050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-05 | 198 | keep | 0 | Jan | 2023 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-01-05 19:02 | 2023-01-05 19:03 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1711-02 Y SE CERRO POR CONTROL LLEVA 1711-05 LLEVA 10% 1711-04 | B2301050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-05 | 1976 | keep | 0 | Jan | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
SAN JUAN | 2023-01-05 19:12 | 2023-01-05 19:25 | 12 | 0:13 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE ABRIO PUENTE SECUNDARIO POR ARBOL EN LA LINEA | S23010500769 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 13 | 2023-01-05 | 156 | keep | 0 | Jan | 2023 | 0.00010625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-05 19:24 | 2023-01-05 19:36 | 338 | 0:12 | T | ALIMENTADOR AMARRADO | PERSONAL EN EL CAMPO HACIENDO OPERACIONES DISPARARON EL 1206-02 | S23010500813 | New_Event | Feeder Load Transferred | Include | Include | Other | 12 | 2023-01-05 | 4056 | keep | 0 | Jan | 2023 | 0.0027625 | 0.00023021 | Sustained | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2023-01-05 19:24 | 2023-01-05 19:36 | 338 | 0:12 | T | CABLE SOTERRADO AVERIADO | PERSONAL EN EL CAMPO REALIZO PRUEBAS Y DISPARO EL BKR 1206-02 | S23010500813 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 12 | 2023-01-05 | 4056 | keep | 0 | Jan | 2023 | 0.0027625 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-05 19:36 | 2023-01-05 21:36 | 11 | 2:00 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN PROVICIONAL NUEVO POR AVERIA DE RISER A T 7. | S23010400326 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 120 | 2023-01-05 | 1320 | keep | 0 | Jan | 2023 | 0.00089905 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-05 19:40 | 2023-01-05 20:47 | 10 | 1:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | R23010500240 | New_Event | Cutout Failure | Include | Include | Equipment | 67 | 2023-01-05 | 670 | keep | 0 | Jan | 2023 | 0.00045633 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-05 20:10 | 2023-01-05 20:11 | 4634 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C23010500219 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-01-05 | 4634 | keep | 0 | Jan | 2023 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2023-01-05 20:11 | 2023-01-05 20:13 | 1544 | 0:02 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES QUEMADOS Y SE TRANSFIRIO LA CARGA AL 2603-08 | C23010500290 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 2 | 2023-01-05 | 3088 | keep | 0 | Jan | 2023 | 0.0021032 | 0.0010516 | Momentary | FALSE | FALSE | Not_TMED_Event | 1544
CAGUAS | 2023-01-05 20:13 | 2023-01-05 20:14 | 4634 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C23010500224 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-01-05 | 4634 | keep | 0 | Jan | 2023 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2023-01-05 20:14 | 2023-01-05 22:20 | 1854 | 2:06 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO EN LOS MACHETES QUEMADOS Y SE CERRO EL BYPASS 3205-7B SE TRANSFIRIO 40% DE LA CARGA AL 2603-08 | C23010500290 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 126 | 2023-01-05 | 233604 | keep | 0 | Jan | 2023 | 0.15911 | 0.0012628 | Sustained | FALSE | FALSE | Not_TMED_Event | 1854
CAGUAS | 2023-01-05 20:33 | 2023-01-05 20:34 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECEIRRE | C2301050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 2302 | keep | 0 | Jan | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
GUAYAMA | 2023-01-05 20:33 | 2023-01-05 22:35 | 7 | 2:02 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR RATON CRUZO FASE | P23010500171 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-01-05 | 854 | keep | 0 | Jan | 2023 | 0.00058166 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-01-05 20:36 | 2023-01-05 21:04 | 11 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | B23010500129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-01-05 | 308 | keep | 0 | Jan | 2023 | 0.00020978 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-01-05 20:39 | 2023-01-05 21:13 | 5 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S23010500877 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-01-05 | 170 | keep | 0 | Jan | 2023 | 0.00011579 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-01-05 21:03 | 2023-01-06 08:20 | 5 | 11:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PROTAFUSIBLES EN TRANSFORMADOR | M23010500184 | New_Event | Cutout Failure | Include | Include | Equipment | 677 | 2023-01-05 | 3385 | keep | 0 | Jan | 2023 | 0.0023055 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-01-05 21:26 | 2023-01-05 23:25 | 125 | 1:59 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | A23010500139 | New_Event | Primary Wire Break | Include | Include | Equipment | 119 | 2023-01-05 | 14875 | keep | 0 | Jan | 2023 | 0.010131 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-01-05 21:59 | 2023-01-05 22:16 | 1340 | 0:17 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALAMBRE ABIERTO DE LINEA A MACHETE 10% EN SERVICIO CONTINUA FUERA 1521-02 | S23010500765 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 17 | 2023-01-05 | 22780 | keep | 0 | Jan | 2023 | 0.015515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-05 22:06 | 2023-01-05 22:07 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-05 | 2605 | keep | 0 | Jan | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-01-05 22:16 | 2023-01-06 00:37 | 1368 | 2:21 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO DE LINEA A MACHETE | S23010500765 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 141 | 2023-01-05 | 192888 | keep | 0 | Jan | 2023 | 0.13138 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-05 22:20 | 2023-01-05 22:25 | 4634 | 0:05 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR A PETICION DE JULIO MENDEZ PARA ABRIR MACHETES QUEMADOS E INCOMODOS | C23010500290 | Additional_clients | Switch Failure | Include | Include | Equipment | 5 | 2023-01-05 | 23170 | keep | 0 | Jan | 2023 | 0.015781 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-05 22:25 | 2023-01-05 22:48 | 1854 | 0:23 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO EN LOS MACHETES QUEMADOS Y SE CERRO EL BYPASS 3205-7B SE TRANSFIRIO 40% DE LA CARGA AL 2603-08 | C23010500290 | Partial_restoration | Switch Failure | Include | Include | Equipment | 23 | 2023-01-05 | 42642 | keep | 0 | Jan | 2023 | 0.029043 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-05 23:02 | 2023-01-06 00:37 | 2368 | 1:35 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 SE RETIRO ARBOL SOBRE LINEA 38KV | B23010500178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 95 | 2023-01-05 | 224960 | keep | 0 | Jan | 2023 | 0.15322 | 0.0016128 | Sustained | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2023-01-05 23:02 | 2023-01-06 00:37 | 538 | 1:35 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 SE RETIRO ARBOL SOBRE LINEA 38KV | B23010500178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 95 | 2023-01-05 | 51110 | keep | 0 | Jan | 2023 | 0.034811 | 0.00036643 | Sustained | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2023-01-05 23:02 | 2023-01-06 00:37 | 1284 | 1:35 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 SE RETIRO ARBOL SOBRE LINEA 38KV | B23010500178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 95 | 2023-01-05 | 121980 | keep | 0 | Jan | 2023 | 0.08308 | 0.00087453 | Sustained | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2023-01-05 23:02 | 2023-01-05 23:05 | 1310 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B23010500164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-01-05 | 3930 | keep | 0 | Jan | 2023 | 0.0026767 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2023-01-05 23:02 | 2023-01-05 23:05 | 215 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B23010500164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-01-05 | 645 | keep | 0 | Jan | 2023 | 0.00043931 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-01-05 23:02 | 2023-01-05 23:05 | 1 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B23010500164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-01-05 | 3 | keep | 0 | Jan | 2023 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-05 23:22 | 2023-01-06 07:07 | 110 | 7:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 40 EN C/L SE REEMPLAZO CAJA PRIMARIA | B23010500199 | New_Event | Cutout Failure | Include | Include | Equipment | 465 | 2023-01-05 | 51150 | keep | 0 | Jan | 2023 | 0.034838 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2023-01-06 00:18 | 2023-01-06 07:53 | 114 | 7:35 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | C23010600003 | New_Event | Primary Wire Break | Include | Include | Equipment | 455 | 2023-01-06 | 51870 | keep | 0 | Jan | 2023 | 0.035328 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
BAYAMON | 2023-01-06 00:22 | 2023-01-06 05:03 | 532 | 4:41 | P | CAUSAS EXTERNAS | 1 X 200 EN RISER CAMION IMPACTO POSTE Y CRUZARON FASES | B23010600016 | New_Event | Damage From Public | Include | Include | Public | 281 | 2023-01-06 | 149492 | keep | 0 | Jan | 2023 | 0.10182 | 0.00036234 | Sustained | FALSE | FALSE | Not_TMED_Event | 532
HUMACAO | 2023-01-06 00:55 | 2023-01-06 09:53 | 40 | 8:58 | P | DESGANCHE | 1 X 30 Y 1 X 25 EN C/L SE DESGANCHO | C23010600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 538 | 2023-01-06 | 21520 | keep | 0 | Jan | 2023 | 0.014657 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-06 01:00 | 2023-01-06 01:01 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23010600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-06 | 5252 | keep | 0 | Jan | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
VEGA BAJA | 2023-01-06 03:07 | 2023-01-06 03:08 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | B23010600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-06 | 652 | keep | 0 | Jan | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
MAYAGÃœEZ | 2023-01-06 03:56 | 2023-01-06 09:29 | 1 | 5:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISE Y 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23010600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2023-01-06 | 333 | keep | 0 | Jan | 2023 | 0.0002268 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-06 04:44 | 2023-01-06 06:17 | 1825 | 1:33 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | INTERRUPTOR DEFECTUOSO NO OPERA POR SCADA Y SE PASO LA CARGA AL 1118-09 EN SERVICIO | S23010600009 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 93 | 2023-01-06 | 169725 | keep | 0 | Jan | 2023 | 0.1156 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-01-06 04:54 | 2023-01-06 04:56 | 1483 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 30% POR 1336-08 | S23010600067 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-06 | 2966 | keep | 0 | Jan | 2023 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-01-06 04:54 | 2023-01-06 04:56 | 1531 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 15% POR 1336-08 | S23010600067 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-06 | 3062 | keep | 0 | Jan | 2023 | 0.0020855 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-01-06 04:54 | 2023-01-06 04:56 | 312 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 5% POR 1336-08 | S23010600067 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-06 | 624 | keep | 0 | Jan | 2023 | 0.000425 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-01-06 04:54 | 2023-01-06 04:56 | 5290 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 15% DEL 1204-05 LLEVA 30% DEL 1204-04 Y LLEVA 5% DEL 1336-07 | S23010600067 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-01-06 | 10580 | keep | 0 | Jan | 2023 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2023-01-06 04:56 | 2023-01-06 07:22 | 494 | 2:26 | P | ALIMENTADOR AMARRADO | CONDUCTOR PRIMARIO EN EL SUELO A LA SALIDA DEL ALIMENTADOR SU CARGA ESTA POR 1336-08 | S23010600062 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 146 | 2023-01-06 | 72124 | keep | 0 | Jan | 2023 | 0.049123 | 0.00033646 | Sustained | FALSE | FALSE | Not_TMED_Event | 494
SAN JUAN | 2023-01-06 04:56 | 2023-01-06 07:22 | 510 | 2:26 | P | ALIMENTADOR AMARRADO | CONDUCTOR PRIMARIO EN EL SUELO A LA SALIDA DEL ALIMENTADOR SU CARGA ESTA POR 1336-08 | S23010600062 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 146 | 2023-01-06 | 74460 | keep | 0 | Jan | 2023 | 0.050714 | 0.00034736 | Sustained | FALSE | FALSE | Not_TMED_Event | 510
SAN JUAN | 2023-01-06 04:56 | 2023-01-06 07:22 | 104 | 2:26 | P | ALIMENTADOR AMARRADO | CONDUCTOR PRIMARIO EN EL SUELO A LA SALIDA DEL ALIMENTADOR SU CARGA ESTA POR 1336-08 | S23010600062 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 146 | 2023-01-06 | 15184 | keep | 0 | Jan | 2023 | 0.010342 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
SAN JUAN | 2023-01-06 04:56 | 2023-01-06 07:22 | 1763 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO EN EL SUELO A LA SALIDA DEL ALIMENTADOR 1336-08 LLEVA 30% 1204-04 LLEVA 5% 1336-07 Y LLEVA 15% DEL 1204-05 | S23010600062 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 146 | 2023-01-06 | 257398 | keep | 0 | Jan | 2023 | 0.17531 | 0.0012008 | Sustained | FALSE | FALSE | Not_TMED_Event | 1763
CANOVANAS | 2023-01-06 05:01 | 2023-01-06 14:18 | 1 | 9:17 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23010600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 557 | 2023-01-06 | 557 | keep | 0 | Jan | 2023 | 0.00037937 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-01-06 06:19 | 2023-01-06 08:00 | 1 | 1:41 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23010600008 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-01-06 | 101 | keep | 0 | Jan | 2023 | 6.8791e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-06 06:38 | 2023-01-06 11:47 | 29 | 5:09 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL T-6 @ T-7 1 X 25 EN SU SE CERRO N/O EN EL T-11 @ T-7 | R23010600003 | New_Event | UG Cable Fault | Include | Include | Equipment | 309 | 2023-01-06 | 8961 | keep | 0 | Jan | 2023 | 0.0061033 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
FAJARDO | 2023-01-06 07:09 | 2023-01-06 08:26 | 16 | 1:17 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE X AVE | R23010600005 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-01-06 | 1232 | keep | 0 | Jan | 2023 | 0.00083911 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-01-06 07:15 | 2023-01-06 08:55 | 1 | 1:40 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN TRANSFORMADOR SE ABRIO TOMA PRIVADA | R23010600006 | New_Event | Customer-Related Interruption | Include | Include | Public | 100 | 2023-01-06 | 100 | keep | 0 | Jan | 2023 | 6.811e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-06 07:22 | 2023-01-06 07:34 | 1483 | 0:12 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 5% 1336-07 Y LLEVA 15% 1204-05 CONDUCTOR PRIMARIO EN EL SUELO A LA SALIDA DEL ALIMENTADOR SE PASO CARGA AL 1336-09 | S23010600062 | Additional_clients | Feeder Load Transferred | Include | Include | Other | 12 | 2023-01-06 | 17796 | keep | 0 | Jan | 2023 | 0.012121 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-06 07:22 | 2023-01-06 07:34 | 1531 | 0:12 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 5% 1336-07 Y LLEVA 15% 1204-05 CONDUCTOR PRIMARIO EN EL SUELO A LA SALIDA DEL ALIMENTADOR SE PASO CARGA AL 1336-09 | S23010600062 | Additional_clients | Feeder Load Transferred | Include | Include | Other | 12 | 2023-01-06 | 18372 | keep | 0 | Jan | 2023 | 0.012513 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-06 07:22 | 2023-01-06 07:34 | 312 | 0:12 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 5% 1336-07 Y LLEVA 15% 1204-05 CONDUCTOR PRIMARIO EN EL SUELO A LA SALIDA DEL ALIMENTADOR SE PASO CARGA AL 1336-09 | S23010600062 | Additional_clients | Feeder Load Transferred | Include | Include | Other | 12 | 2023-01-06 | 3744 | keep | 0 | Jan | 2023 | 0.00255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-06 07:22 | 2023-01-06 07:34 | 5290 | 0:12 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 5% 1336-07 Y LLEVA 15% 1204-05 CONDUCTOR PRIMARIO EN EL SUELO A LA SALIDA DEL ALIMENTADOR SE PASO CARGA AL 1336-09 | S23010600062 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 12 | 2023-01-06 | 63480 | keep | 0 | Jan | 2023 | 0.043236 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-01-06 07:52 | 2023-01-06 07:53 | 2201 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A23010600002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-06 | 2201 | keep | 0 | Jan | 2023 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-01-06 07:52 | 2023-01-06 07:53 | 1986 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A23010600002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-06 | 1986 | keep | 0 | Jan | 2023 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2023-01-06 07:52 | 2023-01-06 07:53 | 199 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A23010600002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-06 | 199 | keep | 0 | Jan | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-01-06 07:52 | 2023-01-06 07:53 | 24 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A23010600002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-06 | 24 | keep | 0 | Jan | 2023 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-01-06 07:56 | 2023-01-06 11:33 | 1 | 3:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B23010600031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2023-01-06 | 217 | keep | 0 | Jan | 2023 | 0.0001478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-06 08:00 | 2023-01-06 09:15 | 40 | 1:15 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23010600006 | New_Event | Animals | Include | Include | Wildlife | 75 | 2023-01-06 | 3000 | keep | 0 | Jan | 2023 | 0.0020433 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-01-06 08:13 | 2023-01-06 13:32 | 169 | 5:19 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO RAYOS | C23010600015 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 319 | 2023-01-06 | 53911 | keep | 0 | Jan | 2023 | 0.036719 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
MAYAGÃœEZ | 2023-01-06 08:18 | 2023-01-06 10:02 | 60 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23010600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-01-06 | 6240 | keep | 0 | Jan | 2023 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-01-06 08:20 | 2023-01-06 08:33 | 1 | 0:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23010600013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 13 | 2023-01-06 | 13 | keep | 0 | Jan | 2023 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-06 08:39 | 2023-01-06 10:46 | 8 | 2:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA ABIERTA | C23010600027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 127 | 2023-01-06 | 1016 | keep | 0 | Jan | 2023 | 0.00069199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-01-06 08:43 | 2023-01-06 09:43 | 1 | 1:00 | P | ANIMAL | 1 X 80 Y 1 X 100 EN C/L CRUCE X AVE | R23010600015 | New_Event | Animals | Include | Include | Wildlife | 60 | 2023-01-06 | 60 | keep | 0 | Jan | 2023 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-06 08:46 | 2023-01-06 09:35 | 516 | 0:49 | P | ARBOL SOBRE LINEA | SE ABRIO C/L Y SE ABRIO PUENTES PRIMARIOS PARA RETIRAR ARBOL SOBRE LINEAS | S23010600020 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 49 | 2023-01-06 | 25284 | keep | 0 | Jan | 2023 | 0.017221 | 0.00035145 | Sustained | FALSE | FALSE | Not_TMED_Event | 516
PONCE | 2023-01-06 09:01 | 2023-01-06 10:17 | 1 | 1:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23010600013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 76 | 2023-01-06 | 76 | keep | 0 | Jan | 2023 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-06 09:06 | 2023-01-06 13:41 | 190 | 4:35 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | C23010600042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 275 | 2023-01-06 | 52250 | keep | 0 | Jan | 2023 | 0.035587 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
ARECIBO | 2023-01-06 09:34 | 2023-01-06 12:00 | 70 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA ZAFADA DE AISLADOR | A23010600003 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2023-01-06 | 10220 | keep | 0 | Jan | 2023 | 0.0069608 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-01-06 09:35 | 2023-01-06 18:03 | 48 | 8:28 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEAS PRIMARIAS | S23010600020 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 508 | 2023-01-06 | 24384 | keep | 0 | Jan | 2023 | 0.016608 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-06 09:58 | 2023-01-06 11:08 | 20 | 1:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L CAJA PRIMARIA | B23010600035 | New_Event | Cutout Failure | Include | Include | Equipment | 70 | 2023-01-06 | 1400 | keep | 0 | Jan | 2023 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-01-06 10:14 | 2023-01-06 16:51 | 7 | 6:37 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE DETERIORADO. | C23010600063 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 397 | 2023-01-06 | 2779 | keep | 0 | Jan | 2023 | 0.0018928 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-01-06 10:15 | 2023-01-06 12:08 | 80 | 1:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R23010600018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-01-06 | 9040 | keep | 0 | Jan | 2023 | 0.0061571 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-01-06 10:15 | 2023-01-06 12:45 | 68 | 2:30 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA | C23010600064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-01-06 | 10200 | keep | 0 | Jan | 2023 | 0.0069472 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
VEGA BAJA | 2023-01-06 10:25 | 2023-01-06 12:36 | 257 | 2:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23010600037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2023-01-06 | 33667 | keep | 0 | Jan | 2023 | 0.02293 | 0.00017504 | Sustained | FALSE | FALSE | Not_TMED_Event | 257
BAYAMON | 2023-01-06 10:33 | 2023-01-06 15:50 | 8 | 5:17 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN XMR SE REEMPLAZO XMR | B23010600038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 317 | 2023-01-06 | 2536 | keep | 0 | Jan | 2023 | 0.0017273 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-01-06 10:37 | 2023-01-06 12:01 | 4 | 1:24 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | R23010600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2023-01-06 | 336 | keep | 0 | Jan | 2023 | 0.00022885 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-01-06 10:39 | 2023-01-06 13:25 | 15 | 2:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23010600017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 166 | 2023-01-06 | 2490 | keep | 0 | Jan | 2023 | 0.0016959 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-06 10:40 | 2023-01-06 12:26 | 95 | 1:46 | P | OTRAS CAUSAS | SE RETIRO GLOBO 3 X 30 EN C/L | B23010600043 | New_Event | Other Causes | Include | Include | Other | 106 | 2023-01-06 | 10070 | keep | 0 | Jan | 2023 | 0.0068586 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
UTUADO | 2023-01-06 11:05 | 2023-01-06 20:30 | 5 | 9:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23010600024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 565 | 2023-01-06 | 2825 | keep | 0 | Jan | 2023 | 0.0019241 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-01-06 11:10 | 2023-01-06 12:34 | 1666 | 1:24 | T | DESGANCHE | SE VERIFICO INTERRUPTROR ABIERTO EN LA SUBESTACION YA QUE EL MISMO NO TIENE COMUNICACION POR SCADA SE RETIRO RAMA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR EN LA SUBESTACION | M23010600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-01-06 | 139944 | keep | 0 | Jan | 2023 | 0.095315 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
YAUCO | 2023-01-06 11:35 | 2023-01-06 11:48 | 12 | 0:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22123100038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 13 | 2023-01-06 | 156 | keep | 0 | Jan | 2023 | 0.00010625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-06 12:14 | 2023-01-06 14:15 | 30 | 2:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO XMR Y SE REPARO BAJANTE SECUNDARIO | S23010600221 | New_Event | Secondary Wire Break | Include | Include | Equipment | 121 | 2023-01-06 | 3630 | keep | 0 | Jan | 2023 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-06 12:35 | 2023-01-06 15:02 | 100 | 2:27 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | B23010600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-01-06 | 14700 | keep | 0 | Jan | 2023 | 0.010012 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-01-06 12:46 | 2023-01-06 14:10 | 90 | 1:24 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | M23010600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-01-06 | 7560 | keep | 0 | Jan | 2023 | 0.0051491 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2023-01-06 12:47 | 2023-01-06 14:44 | 80 | 1:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA | P23010600023 | New_Event | Cutout Failure | Include | Include | Equipment | 117 | 2023-01-06 | 9360 | keep | 0 | Jan | 2023 | 0.0063751 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-01-06 12:49 | 2023-01-06 13:11 | 50 | 0:22 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CORTE POR AVE. | R23010600027 | New_Event | Animals | Include | Include | Wildlife | 22 | 2023-01-06 | 1100 | keep | 0 | Jan | 2023 | 0.0007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-06 13:00 | 2023-01-06 15:13 | 70 | 2:13 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L CORTE DE LINEA Y SE REPARO PUENTE PRIMARIO Y SE REPARO BAJANTE SECUNDARIO EN XMR | S23010600023 | New_Event | Primary Wire Break | Include | Include | Equipment | 133 | 2023-01-06 | 9310 | keep | 0 | Jan | 2023 | 0.006341 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-01-06 13:00 | 2023-01-06 13:53 | 5 | 0:53 | P | CONDUCTOR ROTO O ABIERTO | 1 X 10 EN TRANSFORMADOR SE DESPEGO TIERRA DE POSTE SUELTA PEGANDO CON LA CAJA DEL TRANSFORMADOR | M23010600048 | New_Event | Primary Wire Break | Include | Include | Equipment | 53 | 2023-01-06 | 265 | keep | 0 | Jan | 2023 | 0.00018049 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-01-06 13:06 | 2023-01-06 16:43 | 70 | 3:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23010600098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2023-01-06 | 15190 | keep | 0 | Jan | 2023 | 0.010346 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-01-06 13:09 | 2023-01-06 13:10 | 860 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO SE REPORTO CAUSA | P23010600029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-06 | 860 | keep | 0 | Jan | 2023 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
ARECIBO | 2023-01-06 13:10 | 2023-01-06 17:11 | 1227 | 4:01 | T | CONDUCTOR ARRIADO O CRUZADO | SE INSTALO AISLACION A BAJANTE CRUZANDO PRIMARIA | A23010600022 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 241 | 2023-01-06 | 295707 | keep | 0 | Jan | 2023 | 0.2014 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-01-06 13:15 | 2023-01-06 13:45 | 35 | 0:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A23010600025 | New_Event | Cutout Failure | Include | Include | Equipment | 30 | 2023-01-06 | 1050 | keep | 0 | Jan | 2023 | 0.00071515 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-01-06 13:25 | 2023-01-06 13:26 | 1180 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23010600051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-06 | 1180 | keep | 0 | Jan | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2023-01-06 13:40 | 2023-01-06 15:49 | 16 | 2:09 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN PROVISIONAL AVERIA NUEVA DEL T-1 @ T-2 Y AVERIA VIEJA DEL T-2 @ SU-3A. SIGUE FUERA EL T-2 POR AVERRIA SOTERRADA | B23010600052 | New_Event | UG Cable Fault | Include | Include | Equipment | 129 | 2023-01-06 | 2064 | keep | 0 | Jan | 2023 | 0.0014058 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-01-06 13:45 | 2023-01-06 14:12 | 10 | 0:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR SE REALIZO DESGANCHE SE RETEZO LINEA Y SE REMPLAZO CONEXIONES EN LINEA SECUNDARIA | M23010600030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2023-01-06 | 270 | keep | 0 | Jan | 2023 | 0.0001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-06 13:50 | 2023-01-06 14:40 | 79 | 0:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23010600241 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2023-01-06 | 3950 | keep | 0 | Jan | 2023 | 0.0026903 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
FAJARDO | 2023-01-06 14:00 | 2023-01-06 15:11 | 4 | 1:11 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA | R23010600030 | New_Event | Primary Wire Break | Include | Include | Equipment | 71 | 2023-01-06 | 284 | keep | 0 | Jan | 2023 | 0.00019343 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-01-06 14:15 | 2023-01-06 18:20 | 200 | 4:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | M23010600050 | New_Event | Primary Wire Break | Include | Include | Equipment | 245 | 2023-01-06 | 49000 | keep | 0 | Jan | 2023 | 0.033374 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2023-01-06 14:35 | 2023-01-06 14:50 | 8 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL | A23010400063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-01-06 | 120 | keep | 0 | Jan | 2023 | 8.1731e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-01-06 14:43 | 2023-01-06 16:15 | 100 | 1:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA LLUVIA Y VIENTO | M23010600053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 92 | 2023-01-06 | 9200 | keep | 0 | Jan | 2023 | 0.0062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-06 14:48 | 2023-01-06 15:31 | 8 | 0:43 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23010600056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 43 | 2023-01-06 | 344 | keep | 0 | Jan | 2023 | 0.0002343 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-06 15:42 | 2023-01-06 18:51 | 20 | 3:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 75KVA X 75KVA | C23010600106 | New_Event | Service Transformer Failure | Include | Include | Equipment | 189 | 2023-01-06 | 3780 | keep | 0 | Jan | 2023 | 0.0025745 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-01-06 15:48 | 2023-01-07 11:07 | 36 | 19:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO CAJA PARTIDA | C23010600116 | New_Event | Cutout Failure | Include | Include | Equipment | 1159 | 2023-01-06 | 41724 | keep | 0 | Jan | 2023 | 0.028418 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2023-01-06 15:50 | 2023-01-06 15:51 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 3015-05 | C23010600111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-06 | 2302 | keep | 0 | Jan | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
YAUCO | 2023-01-06 15:54 | 2023-01-06 19:43 | 15 | 3:49 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | M23010600056 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 229 | 2023-01-06 | 3435 | keep | 0 | Jan | 2023 | 0.0023396 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-06 15:57 | 2023-01-06 17:57 | 356 | 2:00 | P | CRUCETA DEFECTUOSA O AVERIADA | SE SECCIONALIZO Y SE REMPLAZO CRUCETA PARTIDA EN TRONCAL | S23010600245 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 120 | 2023-01-06 | 42720 | keep | 0 | Jan | 2023 | 0.029096 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
SAN JUAN | 2023-01-06 16:31 | 2023-01-06 16:32 | 1825 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-06 | 1825 | keep | 0 | Jan | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2023-01-06 17:01 | 2023-01-06 18:58 | 14 | 1:57 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR IGUANA CRUZO FASE A TIERRA | M23010600057 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-01-06 | 1638 | keep | 0 | Jan | 2023 | 0.0011156 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-01-06 17:22 | 2023-01-06 19:26 | 5 | 2:04 | P | SOBRECARGA | 1 X 80 EN C/L SOBRECARGA | B23010600065 | New_Event | Trip Due To Overload | Include | Include | Other | 124 | 2023-01-06 | 620 | keep | 0 | Jan | 2023 | 0.00042228 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-06 17:43 | 2023-01-07 11:44 | 12 | 18:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM T-21 AVERIADO | B23010600066 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1081 | 2023-01-06 | 12972 | keep | 0 | Jan | 2023 | 0.0088352 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-01-06 17:47 | 2023-01-07 08:45 | 10 | 14:58 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C23010600121 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 898 | 2023-01-06 | 8980 | keep | 0 | Jan | 2023 | 0.0061162 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-06 18:03 | 2023-01-06 18:46 | 516 | 0:43 | P | ARBOL SOBRE LINEA | SE ABRIO C/L TOTAL PARA CERRAR PUENTES PRIMARIOS QUE SECCIONALIZABAN ARBOL SOBRE LINEAS | S23010600020 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 43 | 2023-01-06 | 22188 | keep | 0 | Jan | 2023 | 0.015112 | 0.00035145 | Sustained | FALSE | FALSE | Not_TMED_Event | 516
MAYAGÃœEZ | 2023-01-06 18:09 | 2023-01-07 08:51 | 20 | 14:42 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23010600065 | New_Event | Animals | Include | Include | Wildlife | 882 | 2023-01-06 | 17640 | keep | 0 | Jan | 2023 | 0.012015 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-06 18:18 | 2023-01-06 20:02 | 30 | 1:44 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23010600311 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-01-06 | 3120 | keep | 0 | Jan | 2023 | 0.002125 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-01-06 18:43 | 2023-01-07 09:25 | 14 | 14:42 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA IGUANA CRUZO FASE A TIERRA | M23010600069 | New_Event | Animals | Include | Include | Wildlife | 882 | 2023-01-06 | 12348 | keep | 0 | Jan | 2023 | 0.0084102 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-01-06 18:53 | 2023-01-07 05:39 | 35 | 10:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | S23010600314 | New_Event | Cutout Failure | Include | Include | Equipment | 646 | 2023-01-06 | 22610 | keep | 0 | Jan | 2023 | 0.0154 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-01-06 18:57 | 2023-01-07 09:40 | 8 | 14:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR Y SE REPARO SECUNDARIA | C23010600123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 883 | 2023-01-06 | 7064 | keep | 0 | Jan | 2023 | 0.0048113 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-06 19:01 | 2023-01-06 19:02 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO BKR | B2201060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-06 | 2605 | keep | 0 | Jan | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
SAN JUAN | 2023-01-06 19:39 | 2023-01-07 07:05 | 26 | 11:26 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | S23010600321 | New_Event | Vegetation Contact | Include | Include | Vegetation | 686 | 2023-01-06 | 17836 | keep | 0 | Jan | 2023 | 0.012148 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
VEGA BAJA | 2023-01-06 19:43 | 2023-01-07 07:25 | 2 | 11:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL FUERTE LLUVIA | A23010600053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 702 | 2023-01-06 | 1404 | keep | 0 | Jan | 2023 | 0.00095626 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-01-06 19:59 | 2023-01-07 09:00 | 12 | 13:01 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | P23010600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 781 | 2023-01-06 | 9372 | keep | 0 | Jan | 2023 | 0.0063832 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-01-06 20:35 | 2023-01-06 23:35 | 50 | 3:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO DE CAJA PRIMARIA | A23010600055 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2023-01-06 | 9000 | keep | 0 | Jan | 2023 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-06 20:39 | 2023-01-07 01:31 | 63 | 4:52 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN C/L Y 1 X 80 EN C/L AVERIADO EL T-4 | S23010600329 | New_Event | Service Transformer Failure | Include | Include | Equipment | 292 | 2023-01-06 | 18396 | keep | 0 | Jan | 2023 | 0.012529 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
SAN JUAN | 2023-01-06 20:39 | 2023-01-07 16:46 | 5 | 20:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR PM-T4 DE 100KVA | S23010600329 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1207 | 2023-01-06 | 6035 | keep | 0 | Jan | 2023 | 0.0041104 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-01-06 21:12 | 2023-01-07 00:09 | 35 | 2:57 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R23010600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2023-01-06 | 6195 | keep | 0 | Jan | 2023 | 0.0042194 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-01-06 22:05 | 2023-01-07 03:23 | 20 | 5:18 | P | CONDUCTOR ROTO O ABIERTO | SE CERO PUENTE DE LINEA A CAJA DE RISER | S23010600339 | New_Event | Primary Wire Break | Include | Include | Equipment | 318 | 2023-01-06 | 6360 | keep | 0 | Jan | 2023 | 0.0043318 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-01-06 23:36 | 2023-01-06 23:37 | 1271 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C23010600129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-06 | 1271 | keep | 0 | Jan | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
BAYAMON | 2023-01-07 00:16 | 2023-01-07 00:17 | 603 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B23010700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-01-07 | 603 | keep | 0 | Jan | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-01-07 00:17 | 2023-01-07 03:44 | 80 | 3:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO LA CAJA PRIMARIA | B23010700002 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 207 | 2023-01-07 | 16560 | keep | 0 | Jan | 2023 | 0.011279 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-07 00:57 | 2023-01-07 00:58 | 7 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23010700010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 7 | keep | 0 | Jan | 2023 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-01-07 01:31 | 2023-01-07 03:31 | 100 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | B23010700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2023-01-07 | 12000 | keep | 0 | Jan | 2023 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-07 02:32 | 2023-01-07 02:33 | 4702 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 4702 | keep | 0 | Jan | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
BAYAMON | 2023-01-07 03:41 | 2023-01-07 03:42 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 2605 | keep | 0 | Jan | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-01-07 03:44 | 2023-01-07 03:45 | 603 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B23010700030 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2023-01-07 | 603 | keep | 0 | Jan | 2023 | 0.0004107 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-07 03:45 | 2023-01-07 05:39 | 80 | 1:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO LA CAJA PRIMARIA | B23010700002 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 114 | 2023-01-07 | 9120 | keep | 0 | Jan | 2023 | 0.0062116 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-07 03:46 | 2023-01-07 03:47 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23010700031 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 2605 | keep | 0 | Jan | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
VEGA BAJA | 2023-01-07 03:47 | 2023-01-07 03:48 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23010700032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 3000 | keep | 0 | Jan | 2023 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2023-01-07 03:50 | 2023-01-07 03:51 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23010700033 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 2605 | keep | 0 | Jan | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
SAN JUAN | 2023-01-07 04:27 | 2023-01-07 11:18 | 65 | 6:51 | P | ANIMAL | 1 X 65 EN C/L AVE | S23010700004 | New_Event | Animals | Include | Include | Wildlife | 411 | 2023-01-07 | 26715 | keep | 0 | Jan | 2023 | 0.018195 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2023-01-07 07:16 | 2023-01-07 10:14 | 1 | 2:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CL SE REMPLAZO PORTA FUSIBLE | A23010700003 | New_Event | Cutout Failure | Include | Include | Equipment | 178 | 2023-01-07 | 178 | keep | 0 | Jan | 2023 | 0.00012123 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-07 07:25 | 2023-01-07 09:35 | 2605 | 2:10 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR Y ENTRO Y 10 % EN SERVICIO | B23010700040 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 130 | 2023-01-07 | 338650 | keep | 0 | Jan | 2023 | 0.23065 | 0.0017743 | Sustained | FALSE | FALSE | Not_TMED_Event | 2605
PONCE | 2023-01-07 07:35 | 2023-01-07 09:19 | 16 | 1:44 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEAS | P23010700003 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-01-07 | 1664 | keep | 0 | Jan | 2023 | 0.0011333 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-01-07 07:58 | 2023-01-07 11:47 | 211 | 3:49 | P | TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO TERMINACION QUEMADA EN EL SU - 5 Y SE CERRO N/O EN EL SU - 1H | R23010700006 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 229 | 2023-01-07 | 48319 | keep | 0 | Jan | 2023 | 0.03291 | 0.00014371 | Sustained | FALSE | FALSE | Not_TMED_Event | 211
SAN JUAN | 2023-01-07 08:00 | 2023-01-07 20:46 | 26 | 12:46 | P | DESGANCHE | SE ABRIO C/L TOTAL PARA RELAIZAR DESGANCHE MASIVO CON COMPAÃ‘IA PRIVADA | S23010700010 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 766 | 2023-01-07 | 19916 | keep | 0 | Jan | 2023 | 0.013565 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-07 08:13 | 2023-01-07 13:48 | 1483 | 5:35 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-09 QUE LLEVA 30% 1204-04 LLEVA 5% 1336-07 LLEVA 15% 1204-05 Y LLEVA 1336-08 SE REEMPLAZO AISLADOR PARTIDO Y SE CERRO POR SCADA | S2301070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 335 | 2023-01-07 | 496805 | keep | 0 | Jan | 2023 | 0.33837 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-01-07 08:13 | 2023-01-07 13:48 | 1531 | 5:35 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-09 QUE LLEVA 30% 1204-04 LLEVA 5% 1336-07 LLEVA 15% 1204-05 Y LLEVA 1336-08 SE REEMPLAZO AISLADOR PARTIDO Y SE CERRO POR SCADA | S2301070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 335 | 2023-01-07 | 512885 | keep | 0 | Jan | 2023 | 0.34932 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-01-07 08:13 | 2023-01-07 13:48 | 312 | 5:35 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-09 QUE LLEVA 30% 1204-04 LLEVA 5% 1336-07 LLEVA 15% 1204-05 Y LLEVA 1336-08 SE REEMPLAZO AISLADOR PARTIDO Y SE CERRO POR SCADA | S2301070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 335 | 2023-01-07 | 104520 | keep | 0 | Jan | 2023 | 0.071188 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-01-07 08:13 | 2023-01-07 13:48 | 5290 | 5:35 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-09 QUE LLEVA 30% 1204-04 LLEVA 5% 1336-07 LLEVA 15% 1204-05 Y LLEVA 1336-08 SE REEMPLAZO AISLADOR PARTIDO Y SE CERRO POR SCADA | S2301070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 335 | 2023-01-07 | 1772150 | keep | 0 | Jan | 2023 | 1.207 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2023-01-07 08:13 | 2023-01-07 13:48 | 207 | 5:35 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1336-09 QUE LLEVA 30% 1204-04 LLEVA 5% 1336-07 LLEVA 15% 1204-05 Y LLEVA 1336-08 SE REEMPLAZO AISLADOR PARTIDO Y SE CERRO POR SCADA | S2301070000X | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 335 | 2023-01-07 | 69345 | keep | 0 | Jan | 2023 | 0.047231 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
CANOVANAS | 2023-01-07 08:27 | 2023-01-07 08:28 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23010700052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 3046 | keep | 0 | Jan | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
AGUADILLA | 2023-01-07 08:38 | 2023-01-07 08:39 | 1047 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23010700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 1047 | keep | 0 | Jan | 2023 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
VEGA BAJA | 2023-01-07 08:48 | 2023-01-07 09:30 | 10 | 0:42 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE XMR 50KVA X 50KVA | B23010700055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 42 | 2023-01-07 | 420 | keep | 0 | Jan | 2023 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-07 08:53 | 2023-01-07 10:41 | 176 | 1:48 | P | ANIMAL | 1 X 10 EN XMR CRUCE X REPTIL | C23010700005 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-01-07 | 19008 | keep | 0 | Jan | 2023 | 0.012946 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
BAYAMON | 2023-01-07 09:04 | 2023-01-07 10:00 | 11 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23010700060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2023-01-07 | 616 | keep | 0 | Jan | 2023 | 0.00041955 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-01-07 09:05 | 2023-01-07 12:38 | 16 | 3:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR LINEAS SECUNDARIAS | A23010700008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 213 | 2023-01-07 | 3408 | keep | 0 | Jan | 2023 | 0.0023212 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-01-07 09:09 | 2023-01-07 11:54 | 1 | 2:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | TRABAJOS DE REMPLAZO DE POSTE PRIMARIO PARTIDO | M23010700010 | New_Event | Primary Pole Failure | Include | Include | Equipment | 165 | 2023-01-07 | 165 | keep | 0 | Jan | 2023 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-07 09:15 | 2023-01-07 11:25 | 742 | 2:10 | T | PARARRAYOS DEFECTUOSO | SE SECCIONALIZO TRAMO Y SE CERRO BKR 10% EN SERVICIO SWF SJ 230107-02 | S23010700355 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 130 | 2023-01-07 | 96460 | keep | 0 | Jan | 2023 | 0.065698 | 0.00050537 | Sustained | FALSE | FALSE | Not_TMED_Event | 742
BARRANQUITAS | 2023-01-07 09:18 | 2023-01-07 10:58 | 30 | 1:40 | P | DESGANCHE | 1 X 30 EN C/L | C23010700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-01-07 | 3000 | keep | 0 | Jan | 2023 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-01-07 09:25 | 2023-01-07 12:04 | 15 | 2:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM T-17 DEBIDO A QUE NO REGULA | A23010700010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 159 | 2023-01-07 | 2385 | keep | 0 | Jan | 2023 | 0.0016244 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-07 09:35 | 2023-01-07 09:45 | 2344 | 0:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE ALIMENTADOR HACIENDO OPERACIONES | B23010700040 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 10 | 2023-01-07 | 23440 | keep | 0 | Jan | 2023 | 0.015965 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-07 09:40 | 2023-01-07 16:10 | 13 | 6:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23010600072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 390 | 2023-01-07 | 5070 | keep | 0 | Jan | 2023 | 0.0034532 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-01-07 09:45 | 2023-01-07 11:09 | 2605 | 1:24 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON AISLADORES 100% EN SERVICIO | B23010700040 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 84 | 2023-01-07 | 218820 | keep | 0 | Jan | 2023 | 0.14904 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-07 09:53 | 2023-01-07 13:27 | 40 | 3:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA QUEMADA NO FUNDIO | C23010700014 | New_Event | Cutout Failure | Include | Include | Equipment | 214 | 2023-01-07 | 8560 | keep | 0 | Jan | 2023 | 0.0058302 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-01-07 09:59 | 2023-01-07 12:09 | 1 | 2:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23010700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2023-01-07 | 130 | keep | 0 | Jan | 2023 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-07 10:02 | 2023-01-07 15:25 | 50 | 5:23 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23010700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2023-01-07 | 16150 | keep | 0 | Jan | 2023 | 0.011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-01-07 10:15 | 2023-01-07 10:45 | 12 | 0:30 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR DE 50KVA X 50KVA | B23010700078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 30 | 2023-01-07 | 360 | keep | 0 | Jan | 2023 | 0.00024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-07 10:16 | 2023-01-07 15:33 | 49 | 5:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZARON AISLADORES | S23010700429 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 317 | 2023-01-07 | 15533 | keep | 0 | Jan | 2023 | 0.010579 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
CAGUAS | 2023-01-07 10:20 | 2023-01-07 16:21 | 45 | 6:01 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO | C23010700020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2023-01-07 | 16245 | keep | 0 | Jan | 2023 | 0.011064 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-01-07 10:23 | 2023-01-07 11:27 | 100 | 1:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA Y SE REPARO LINEA ZAFADA DE AISLADOR | M23010700013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 64 | 2023-01-07 | 6400 | keep | 0 | Jan | 2023 | 0.004359 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-01-07 10:30 | 2023-01-07 10:55 | 15 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23010700014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-07 | 375 | keep | 0 | Jan | 2023 | 0.00025541 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-01-07 10:35 | 2023-01-07 13:04 | 100 | 2:29 | P | CAUSAS EXTERNAS | 2 X 50 EN CORTE DE LINEA CAMION CRUZO LINEAS | A23010700015 | New_Event | Damage From Public | Include | Include | Public | 149 | 2023-01-07 | 14900 | keep | 0 | Jan | 2023 | 0.010148 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-01-07 10:39 | 2023-01-07 13:58 | 11 | 3:19 | P | TRANSFORMADOR AVERIADO | SE INSTALO XMR DE 37.5 KVA Y SE DIVIDIO LAS CARGAS | C23010700021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 199 | 2023-01-07 | 2189 | keep | 0 | Jan | 2023 | 0.0014909 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-01-07 11:05 | 2023-01-07 11:06 | 327 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE INTERRUPTOR CARGA POR EL 2604-01 | C2301070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-07 | 327 | keep | 0 | Jan | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-07 11:05 | 2023-01-07 11:06 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 2604-01 LLEVA EL 2603-07 | C2301070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 2354 | keep | 0 | Jan | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
CAGUAS | 2023-01-07 11:21 | 2023-01-07 15:51 | 6 | 4:30 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR PARA RELOCALIZAR SECUNDARIA | C23010700025 | New_Event | Primary Wire Break | Include | Include | Equipment | 270 | 2023-01-07 | 1620 | keep | 0 | Jan | 2023 | 0.0011034 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-07 11:25 | 2023-01-07 11:40 | 667 | 0:15 | P | PARARRAYOS DEFECTUOSO | SE REALIZARON OPERACIONES 20% EN SERVICIO SWF SJ 230107-02 | S23010700355 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 15 | 2023-01-07 | 10005 | keep | 0 | Jan | 2023 | 0.0068144 | 0.00045429 | Sustained | FALSE | FALSE | Not_TMED_Event | 667
HUMACAO | 2023-01-07 11:29 | 2023-01-07 11:30 | 3902 | 0:01 | T | ANIMAL | RECIERRE | C23010700028 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-07 | 3902 | keep | 0 | Jan | 2023 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2023-01-07 11:30 | 2023-01-07 13:14 | 94 | 1:44 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23010700030 | 1st_after_momentary | Animals | Include | Include | Wildlife | 104 | 2023-01-07 | 9776 | keep | 0 | Jan | 2023 | 0.0066584 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
ARECIBO | 2023-01-07 11:33 | 2023-01-07 13:52 | 50 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23010700023 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-01-07 | 6950 | keep | 0 | Jan | 2023 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-07 11:40 | 2023-01-07 12:13 | 534 | 0:33 | P | PARARRAYOS DEFECTUOSO | SE REALIZARON OPERACIONES DISPARO DEL 1301-02 SWF SJ 230107-02 | S23010700355 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 33 | 2023-01-07 | 17622 | keep | 0 | Jan | 2023 | 0.012002 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-07 11:47 | 2023-01-07 13:01 | 12 | 1:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN C/L MAL TIEMPO LLUVIA | R23010700263 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 74 | 2023-01-07 | 888 | keep | 0 | Jan | 2023 | 0.00060481 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-01-07 11:53 | 2023-01-07 14:00 | 25 | 2:07 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R23010700264 | New_Event | Animals | Include | Include | Wildlife | 127 | 2023-01-07 | 3175 | keep | 0 | Jan | 2023 | 0.0021625 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-07 11:59 | 2023-01-07 15:19 | 56 | 3:20 | P | DESGANCHE | 1 X 65 CL DESGANCHE | S23010700655 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-01-07 | 11200 | keep | 0 | Jan | 2023 | 0.0076283 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
SAN JUAN | 2023-01-07 12:00 | 2023-01-07 12:40 | 2 | 0:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S23010700659 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2023-01-07 | 80 | keep | 0 | Jan | 2023 | 5.4488e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-01-07 12:13 | 2023-01-07 12:17 | 742 | 0:04 | T | PARARRAYOS DEFECTUOSO | SE REALIZARON OPERACIONES 20% EN SERVICIO SWF SJ 230107-02 | S23010700355 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 4 | 2023-01-07 | 2968 | keep | 0 | Jan | 2023 | 0.0020215 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-07 12:17 | 2023-01-07 12:25 | 593 | 0:08 | P | PARARRAYOS DEFECTUOSO | SE REALIZARON OPERACIONES 25% EN SERVICIO SWF SJ 230107-02 | S23010700355 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 8 | 2023-01-07 | 4744 | keep | 0 | Jan | 2023 | 0.0032311 | 0.00040389 | Sustained | FALSE | FALSE | Not_TMED_Event | 593
SAN JUAN | 2023-01-07 12:25 | 2023-01-07 13:30 | 444 | 1:05 | P | PARARRAYOS DEFECTUOSO | SE REALIZARON OPERACIONES 50% EN SERVICIO SWF SJ 230107-02 | S23010700355 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 65 | 2023-01-07 | 28860 | keep | 0 | Jan | 2023 | 0.019656 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-07 12:29 | 2023-01-07 15:05 | 100 | 2:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23010700031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-01-07 | 15600 | keep | 0 | Jan | 2023 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-01-07 12:53 | 2023-01-07 14:15 | 50 | 1:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23010700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2023-01-07 | 4100 | keep | 0 | Jan | 2023 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-01-07 13:00 | 2023-01-07 14:30 | 60 | 1:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23010700024 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 90 | 2023-01-07 | 5400 | keep | 0 | Jan | 2023 | 0.0036779 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-01-07 13:04 | 2023-01-07 13:07 | 766 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1909-07 LLEVA 50% 1709-03 | B2301070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-07 | 2298 | keep | 0 | Jan | 2023 | 0.0015652 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-01-07 13:04 | 2023-01-07 13:07 | 1139 | 0:03 | T | DESGANCHE | DISPARO INTERRUPTOR 1909-07 LLEVA 50% 1709-03 | B2301070000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-01-07 | 3417 | keep | 0 | Jan | 2023 | 0.0023273 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
SAN JUAN | 2023-01-07 13:05 | 2023-01-07 18:00 | 522 | 4:55 | P | ANIMAL | 1 X 80 CL 2 X 80 EN RISER 1 X 80 SU 2 CURCE POR ANIMAL | S23010700786 | New_Event | Animals | Include | Include | Wildlife | 295 | 2023-01-07 | 153990 | keep | 0 | Jan | 2023 | 0.10488 | 0.00035553 | Sustained | FALSE | FALSE | Not_TMED_Event | 522
BAYAMON | 2023-01-07 13:07 | 2023-01-07 15:57 | 25 | 2:50 | P | DESGANCHE | SE REGULO VOLTAGE Y 1 X 80 EN C/L Y 1 X 15 EN C/L DESGANCHE PRIMARIO | S23010700793 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-01-07 | 4250 | keep | 0 | Jan | 2023 | 0.0028947 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-01-07 13:07 | 2023-01-07 17:40 | 6 | 4:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR REPARAR NEUTRAL | M23010700025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 273 | 2023-01-07 | 1638 | keep | 0 | Jan | 2023 | 0.0011156 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-01-07 13:14 | 2023-01-07 13:15 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | A23010700041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 3431 | keep | 0 | Jan | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2023-01-07 13:18 | 2023-01-07 13:58 | 26 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23010700106 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-01-07 | 1040 | keep | 0 | Jan | 2023 | 0.00070834 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2023-01-07 13:30 | 2023-01-07 14:25 | 222 | 0:55 | P | PARARRAYOS DEFECTUOSO | SE REALIZARON OPERACIONES DISPARO DEL 1301-02 SWF SJ 230107-02 | S23010700355 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 55 | 2023-01-07 | 12210 | keep | 0 | Jan | 2023 | 0.0083162 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-07 13:30 | 2023-01-07 14:55 | 8 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA Y REGULO VOLTAGE | B23010700108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2023-01-07 | 680 | keep | 0 | Jan | 2023 | 0.00046314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-01-07 13:41 | 2023-01-07 16:40 | 1 | 2:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZA TRANSFORMADOR QUEMADO DE 25 KVA A 4.16KV | A23010700048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 179 | 2023-01-07 | 179 | keep | 0 | Jan | 2023 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-07 13:45 | 2023-01-07 14:58 | 19 | 1:13 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | R23010700274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-01-07 | 1387 | keep | 0 | Jan | 2023 | 0.00094468 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2023-01-07 14:04 | 2023-01-07 14:05 | 3464 | 0:01 | T | ANIMAL | RECIERRO INTERRUPTOR CARGA POR EL 2404-08 | R23010700276 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-07 | 3464 | keep | 0 | Jan | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2023-01-07 14:04 | 2023-01-07 14:05 | 2675 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE LLEVA EL 2404-05 | R23010700276 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-07 | 2675 | keep | 0 | Jan | 2023 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2023-01-07 14:05 | 2023-01-07 16:32 | 698 | 2:27 | P | ANIMAL | 3 X 200 EN CORTES DE LINEA CRUCE X AVE | R23010700030 | 1st_after_momentary | Animals | Include | Include | Wildlife | 147 | 2023-01-07 | 102606 | keep | 0 | Jan | 2023 | 0.069884 | 0.0004754 | Sustained | FALSE | FALSE | Not_TMED_Event | 698
CAGUAS | 2023-01-07 14:11 | 2023-01-07 17:07 | 30 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIAS | C23010700053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2023-01-07 | 5280 | keep | 0 | Jan | 2023 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-01-07 14:18 | 2023-01-07 15:37 | 5 | 1:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO Y REEMPLAZO TRAMO SECUNDARIO CRUZADO | C23010700055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 79 | 2023-01-07 | 395 | keep | 0 | Jan | 2023 | 0.00026903 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-01-07 14:19 | 2023-01-07 16:00 | 50 | 1:41 | P | ANIMAL | 1 X 80 EN C/L AVE CRUZO LINEAS | P23010700033 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-01-07 | 5050 | keep | 0 | Jan | 2023 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-01-07 14:24 | 2023-01-07 15:13 | 1210 | 0:49 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA ROTA SE ABRIO INTERRUPTOR PARA ABRIR MACHETES Y SECCIONALIZAR | M23010700034 | New_Event | Primary Wire Break | Include | Include | Equipment | 49 | 2023-01-07 | 59290 | keep | 0 | Jan | 2023 | 0.040382 | 0.00082413 | Sustained | FALSE | FALSE | Not_TMED_Event | 1210
SAN JUAN | 2023-01-07 14:25 | 2023-01-07 14:26 | 742 | 0:01 | T | PARARRAYOS DEFECTUOSO | SE REALIZARON OPERACIONES EN SERVICIO EL 50% SWF SJ 230107-02 | S23010700355 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-01-07 | 742 | keep | 0 | Jan | 2023 | 0.00050537 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-07 14:26 | 2023-01-07 15:30 | 371 | 1:04 | P | PARARRAYOS DEFECTUOSO | SE REALIZARON OPERACIONES 90% EN SERVICIO SE AMARRO PARTE CONTRA 1334-01 SWF SJ 230107-02 | S23010700355 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 64 | 2023-01-07 | 23744 | keep | 0 | Jan | 2023 | 0.016172 | 0.00025269 | Sustained | FALSE | FALSE | Not_TMED_Event | 371
UTUADO | 2023-01-07 14:35 | 2023-01-07 18:12 | 45 | 3:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CL FUERTES LLUVIA | A23010700053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 217 | 2023-01-07 | 9765 | keep | 0 | Jan | 2023 | 0.0066509 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-01-07 14:44 | 2023-01-07 16:30 | 50 | 1:46 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS CRUZADAS | M23010700045 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 106 | 2023-01-07 | 5300 | keep | 0 | Jan | 2023 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-07 14:50 | 2023-01-07 16:40 | 7 | 1:50 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA DESGANCHE | B23010700107 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 110 | 2023-01-07 | 770 | keep | 0 | Jan | 2023 | 0.00052444 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-01-07 15:00 | 2023-01-07 15:23 | 1 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23010700002 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-01-07 | 23 | keep | 0 | Jan | 2023 | 1.5665e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-07 15:04 | 2023-01-07 15:05 | 2090 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 2090 CLIENTES POR EL 2403-02 | R23010700302 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-07 | 2090 | keep | 0 | Jan | 2023 | 0.0014235 | 0.0014235 | Momentary | FALSE | FALSE | Not_TMED_Event | 2090
CANOVANAS | 2023-01-07 15:04 | 2023-01-07 15:05 | 500 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRO INTERRUPTOR LLEVA 2090 CLIENTES DEL 2403-01 | R23010700302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 500 | keep | 0 | Jan | 2023 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2023-01-07 15:10 | 2023-01-07 15:11 | 2090 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 2090 CLIENTES POR EL 2403-02 | R23010700306 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-07 | 2090 | keep | 0 | Jan | 2023 | 0.0014235 | 0.0014235 | Momentary | FALSE | FALSE | Not_TMED_Event | 2090
CANOVANAS | 2023-01-07 15:10 | 2023-01-07 15:11 | 500 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR LLEVA 2090 CLIENTES DEL 2403-01 | R23010700306 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 500 | keep | 0 | Jan | 2023 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
YAUCO | 2023-01-07 15:11 | 2023-01-07 15:23 | 1268 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 SE TRANSFORIO A LA LINEA 1200 | M23010700101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-01-07 | 15216 | keep | 0 | Jan | 2023 | 0.010364 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
YAUCO | 2023-01-07 15:11 | 2023-01-07 15:23 | 2064 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 SE TRANSFORIO A LA LINEA 1200 | M23010700101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-01-07 | 24768 | keep | 0 | Jan | 2023 | 0.016869 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
YAUCO | 2023-01-07 15:11 | 2023-01-07 15:23 | 3036 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 SE TRANSFORIO A LA LINEA 1200 | M23010700101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-01-07 | 36432 | keep | 0 | Jan | 2023 | 0.024814 | 0.0020678 | Sustained | FALSE | FALSE | Not_TMED_Event | 3036
YAUCO | 2023-01-07 15:11 | 2023-01-07 15:23 | 2952 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 SE TRANSFORIO A LA LINEA 1200 | M23010700101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-01-07 | 35424 | keep | 0 | Jan | 2023 | 0.024127 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
VEGA BAJA | 2023-01-07 15:11 | 2023-01-07 17:10 | 5 | 1:59 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE | A23010700059 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-01-07 | 595 | keep | 0 | Jan | 2023 | 0.00040525 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-01-07 15:13 | 2023-01-07 15:15 | 3630 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA ABRIR MACHETES | M23010700035 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 2 | 2023-01-07 | 7260 | keep | 0 | Jan | 2023 | 0.0049448 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-01-07 15:15 | 2023-01-07 17:59 | 3530 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO MACHETES | M23010700048 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 164 | 2023-01-07 | 578920 | keep | 0 | Jan | 2023 | 0.3943 | 0.0024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 3530
MAYAGÃœEZ | 2023-01-07 15:26 | 2023-01-07 17:00 | 50 | 1:34 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA LINEA PRIMARIA ARRIADA | M23010700119 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 94 | 2023-01-07 | 4700 | keep | 0 | Jan | 2023 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-01-07 15:26 | 2023-01-07 16:19 | 30 | 0:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23010700064 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 53 | 2023-01-07 | 1590 | keep | 0 | Jan | 2023 | 0.0010829 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-07 15:30 | 2023-01-07 19:28 | 37 | 3:58 | P | PARARRAYOS DEFECTUOSO | SE REALIZARON OPERACIONES DISPARO DEL 1301-02 SWF SJ 230107-02 | S23010700355 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 238 | 2023-01-07 | 8806 | keep | 0 | Jan | 2023 | 0.0059977 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-01-07 15:35 | 2023-01-08 19:00 | 50 | 27:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A23010700065 | New_Event | Cutout Failure | Include | Include | Equipment | 1645 | 2023-01-07 | 82250 | keep | 0 | Jan | 2023 | 0.05602 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-01-07 15:36 | 2023-01-07 16:27 | 79 | 0:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23010700316 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2023-01-07 | 4029 | keep | 0 | Jan | 2023 | 0.0027441 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
PONCE | 2023-01-07 15:52 | 2023-01-07 16:38 | 40 | 0:46 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23010700044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2023-01-07 | 1840 | keep | 0 | Jan | 2023 | 0.0012532 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-01-07 15:54 | 2023-01-07 17:49 | 20 | 1:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23010700320 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 115 | 2023-01-07 | 2300 | keep | 0 | Jan | 2023 | 0.0015665 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-01-07 16:04 | 2023-01-07 18:50 | 61 | 2:46 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23010700173 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 166 | 2023-01-07 | 10126 | keep | 0 | Jan | 2023 | 0.0068968 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
HUMACAO | 2023-01-07 16:14 | 2023-01-07 17:25 | 60 | 1:11 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA NO FUNDIO | C23010700060 | New_Event | Primary Wire Break | Include | Include | Equipment | 71 | 2023-01-07 | 4260 | keep | 0 | Jan | 2023 | 0.0029015 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-01-07 16:14 | 2023-01-07 19:16 | 40 | 3:02 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L MAL TIEMPO RAYOS | P23010700047 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 182 | 2023-01-07 | 7280 | keep | 0 | Jan | 2023 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-01-07 16:40 | 2023-01-07 16:42 | 3420 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C2301070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-07 | 6840 | keep | 0 | Jan | 2023 | 0.0046587 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
CANOVANAS | 2023-01-07 16:47 | 2023-01-07 17:00 | 28 | 0:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN RISER MAL TIEMPO LLUVIA | R23010700012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 13 | 2023-01-07 | 364 | keep | 0 | Jan | 2023 | 0.00024792 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2023-01-07 16:52 | 2023-01-07 19:40 | 23 | 2:48 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23010700116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-01-07 | 3864 | keep | 0 | Jan | 2023 | 0.0026318 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CANOVANAS | 2023-01-07 16:57 | 2023-01-07 16:58 | 2090 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 2090 DE LA CARGA POR 2403-02 | R23010700335 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-07 | 2090 | keep | 0 | Jan | 2023 | 0.0014235 | 0.0014235 | Momentary | FALSE | FALSE | Not_TMED_Event | 2090
CANOVANAS | 2023-01-07 16:57 | 2023-01-07 16:58 | 500 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRO INTERRUPTOR LLEVA 2090 CLIENTES DEL 2403-01 | R23010700335 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 500 | keep | 0 | Jan | 2023 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2023-01-07 17:20 | 2023-01-07 20:29 | 50 | 3:09 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L REEMPLAZO PARARRAYO | C23010700071 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 189 | 2023-01-07 | 9450 | keep | 0 | Jan | 2023 | 0.0064364 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-07 17:31 | 2023-01-08 10:06 | 33 | 16:35 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | S23010700931 | New_Event | Primary Wire Break | Include | Include | Equipment | 995 | 2023-01-07 | 32835 | keep | 0 | Jan | 2023 | 0.022364 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2023-01-07 18:17 | 2023-01-07 22:48 | 5 | 4:31 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA 1 X 15 EN XMR | B23010700126 | New_Event | Primary Wire Break | Include | Include | Equipment | 271 | 2023-01-07 | 1355 | keep | 0 | Jan | 2023 | 0.00092288 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-01-07 18:42 | 2023-01-07 22:26 | 80 | 3:44 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 100 EN CORTE DE LINEA LINEAS ENREDADAS | P23010700069 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 224 | 2023-01-07 | 17920 | keep | 0 | Jan | 2023 | 0.012205 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-01-07 18:48 | 2023-01-07 18:51 | 4702 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | B23010700128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-07 | 14106 | keep | 0 | Jan | 2023 | 0.0096075 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-01-07 18:48 | 2023-01-07 18:49 | 2704 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2301070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 2704 | keep | 0 | Jan | 2023 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
YAUCO | 2023-01-07 18:50 | 2023-01-08 13:21 | 8 | 18:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | M23010700173 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1111 | 2023-01-07 | 8888 | keep | 0 | Jan | 2023 | 0.0060536 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-01-07 18:55 | 2023-01-07 18:56 | 2704 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2301070000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 2704 | keep | 0 | Jan | 2023 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
MAYAGÃœEZ | 2023-01-07 19:07 | 2023-01-08 17:05 | 12 | 21:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA POR LA MISMA CAPACIDAD | M23010700248 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1318 | 2023-01-07 | 15816 | keep | 0 | Jan | 2023 | 0.010772 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-01-07 19:22 | 2023-01-08 09:20 | 10 | 13:58 | P | MAL TIEMPO/RAYOS | 1 X 20 EN XMR MAL TIEMPO RAYOS | P23010700072 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 838 | 2023-01-07 | 8380 | keep | 0 | Jan | 2023 | 0.0057076 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-07 19:28 | 2023-01-07 19:29 | 519 | 0:01 | P | PARARRAYOS DEFECTUOSO | SE CERRO BKR 1301-02 SE REALIZARON OPERACIONES ENTRO EN SERVICIO 90% 30 % X 1334-01 SWF SJ 230107-02 | S23010700355 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-01-07 | 519 | keep | 0 | Jan | 2023 | 0.00035349 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-07 19:29 | 2023-01-07 21:11 | 51 | 1:42 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARAYO CRUZADO ENCIMA DE CRUCETA Y SE CERRO MACHETE SWF SJ-230107-02 100% EN SERVICIO | S23010700355 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 102 | 2023-01-07 | 5202 | keep | 0 | Jan | 2023 | 0.0035431 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
ARECIBO | 2023-01-07 19:55 | 2023-01-07 19:56 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA TRES OPERACIONES Y QUEDA EN SERVICIO | A23010700076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 1227 | keep | 0 | Jan | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-01-07 20:09 | 2023-01-07 22:56 | 40 | 2:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A23010700078 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 167 | 2023-01-07 | 6680 | keep | 0 | Jan | 2023 | 0.0045497 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-01-07 20:43 | 2023-01-08 08:55 | 5 | 12:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REMPLAZO CAJA PRIMARIA EN RISER | A23010700083 | New_Event | Cutout Failure | Include | Include | Equipment | 732 | 2023-01-07 | 3660 | keep | 0 | Jan | 2023 | 0.0024928 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-07 20:58 | 2023-01-08 13:46 | 10 | 16:48 | P | NO SE REPORTO CAUSA | 1 X 125 EN SU Y 1 X 80 EN AEE Y EN CALLE CONDADO 1 X 100 EN C/L | S23010700977 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1008 | 2023-01-07 | 10080 | keep | 0 | Jan | 2023 | 0.0068654 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-07 21:54 | 2023-01-07 21:55 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010700095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 2113 | keep | 0 | Jan | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
CANOVANAS | 2023-01-07 22:06 | 2023-01-08 07:46 | 1 | 9:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN RISER MAL TIEMPO LLUVIA | R23010700344 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 580 | 2023-01-07 | 580 | keep | 0 | Jan | 2023 | 0.00039504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-07 22:45 | 2023-01-08 02:53 | 24 | 4:08 | P | DESGANCHE | 2 X 80 EN C/L Y DESGANCHE | S23010700982 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-01-07 | 5952 | keep | 0 | Jan | 2023 | 0.0040539 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
HUMACAO | 2023-01-07 23:01 | 2023-01-08 01:19 | 2126 | 2:18 | T | ANIMAL | DISPARO INTERRUPTOR SE PATRULLO ALIMENTADOR Y NO SE ENCONTRO NADA SE REALIZO PRUEBA POR CONTROL Y PROBO BUENO. CG-230107-01 | C23010700085 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-01-07 | 293388 | keep | 0 | Jan | 2023 | 0.19983 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2023-01-07 23:10 | 2023-01-08 09:16 | 60 | 10:06 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23010700256 | New_Event | Animals | Include | Include | Wildlife | 606 | 2023-01-07 | 36360 | keep | 0 | Jan | 2023 | 0.024765 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-01-07 23:45 | 2023-01-07 23:46 | 4702 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2301070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-07 | 4702 | keep | 0 | Jan | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
PONCE | 2023-01-08 00:53 | 2023-01-08 03:52 | 200 | 2:59 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P23010800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-01-08 | 35800 | keep | 0 | Jan | 2023 | 0.024383 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-01-08 01:19 | 2023-01-08 11:03 | 1089 | 9:44 | P | ANIMAL | SE ENCONTRO RANA CRUZANDO LINEA PRIMARIA Y SE CERRO PUENTE PRIMARIO | C23010800002 | Partial_restoration | Animals | Include | Include | Wildlife | 584 | 2023-01-08 | 635976 | keep | 0 | Jan | 2023 | 0.43316 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-01-08 01:56 | 2023-01-08 08:30 | 40 | 6:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23010800003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 394 | 2023-01-08 | 15760 | keep | 0 | Jan | 2023 | 0.010734 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-01-08 02:12 | 2023-01-08 02:13 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23010800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 5630 | keep | 0 | Jan | 2023 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
SAN JUAN | 2023-01-08 02:26 | 2023-01-08 02:27 | 143 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 80% DEL 1404-07 | S2301080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 143 | keep | 0 | Jan | 2023 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-01-08 02:26 | 2023-01-08 02:27 | 1085 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 80% DE SU CARGA POR EL 1404-06 | S2301080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-08 | 1085 | keep | 0 | Jan | 2023 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
VEGA BAJA | 2023-01-08 03:01 | 2023-01-08 20:55 | 30 | 17:54 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B23010800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1074 | 2023-01-08 | 32220 | keep | 0 | Jan | 2023 | 0.021945 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-01-08 03:23 | 2023-01-08 03:24 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 2113 | keep | 0 | Jan | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
CANOVANAS | 2023-01-08 04:44 | 2023-01-08 09:04 | 69 | 4:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23010800002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 260 | 2023-01-08 | 17940 | keep | 0 | Jan | 2023 | 0.012219 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
SAN JUAN | 2023-01-08 05:14 | 2023-01-08 05:15 | 1420 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1530-06 | S2301080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-08 | 1420 | keep | 0 | Jan | 2023 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
SAN JUAN | 2023-01-08 05:14 | 2023-01-08 05:15 | 437 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1526-02 | S2301080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 437 | keep | 0 | Jan | 2023 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2023-01-08 05:17 | 2023-01-08 05:18 | 1420 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1530-06 | S2301080000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-08 | 1420 | keep | 0 | Jan | 2023 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
SAN JUAN | 2023-01-08 05:17 | 2023-01-08 05:18 | 437 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1526-02 | S2301080000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 437 | keep | 0 | Jan | 2023 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2023-01-08 05:48 | 2023-01-08 05:49 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTO | S2301080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 2203 | keep | 0 | Jan | 2023 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2023-01-08 05:49 | 2023-01-08 12:35 | 40 | 6:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23010800056 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 406 | 2023-01-08 | 16240 | keep | 0 | Jan | 2023 | 0.011061 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-01-08 06:01 | 2023-01-08 08:37 | 96 | 2:36 | P | NO SE REPORTO CAUSA | SE REPUSO 1 X 80 EN C/L | C23010800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2023-01-08 | 14976 | keep | 0 | Jan | 2023 | 0.0102 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
VEGA BAJA | 2023-01-08 07:03 | 2023-01-08 10:26 | 60 | 3:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REMPLAZO AISLADO | B23010800004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 203 | 2023-01-08 | 12180 | keep | 0 | Jan | 2023 | 0.0082957 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-01-08 07:05 | 2023-01-08 10:45 | 200 | 3:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 Y 1 X 200 EN DISTINTOS CORTES DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23010800005 | New_Event | Cutout Failure | Include | Include | Equipment | 220 | 2023-01-08 | 44000 | keep | 0 | Jan | 2023 | 0.029968 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-01-08 07:31 | 2023-01-08 09:19 | 40 | 1:48 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO BAMBUAS | S23010800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-01-08 | 4320 | keep | 0 | Jan | 2023 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-01-08 08:00 | 2023-01-08 09:11 | 16 | 1:11 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETIRO GUY WIRE EN DESHUSO PEGANDO AL BAJANTE PRIMARIO DE XMR | C23010800007 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 71 | 2023-01-08 | 1136 | keep | 0 | Jan | 2023 | 0.00077372 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
FAJARDO | 2023-01-08 08:09 | 2023-01-08 09:43 | 520 | 1:34 | P | ANIMAL | 1 X 25 EN RISER 1 X 80 Y 1 X 100 EN CORTE DE LINEA CRUCE X AVE | R23010800003 | New_Event | Animals | Include | Include | Wildlife | 94 | 2023-01-08 | 48880 | keep | 0 | Jan | 2023 | 0.033292 | 0.00035417 | Sustained | FALSE | FALSE | Not_TMED_Event | 520
MAYAGÃœEZ | 2023-01-08 08:11 | 2023-01-08 11:16 | 65 | 3:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M23010800018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 185 | 2023-01-08 | 12025 | keep | 0 | Jan | 2023 | 0.0081902 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2023-01-08 08:18 | 2023-01-08 10:43 | 1 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU | C23010800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-01-08 | 145 | keep | 0 | Jan | 2023 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-08 08:30 | 2023-01-08 11:55 | 1 | 3:25 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE X AVE | R23010800009 | New_Event | Animals | Include | Include | Wildlife | 205 | 2023-01-08 | 205 | keep | 0 | Jan | 2023 | 0.00013962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-08 08:30 | 2023-01-08 12:19 | 250 | 3:49 | P | ANIMAL | 1 X 50 1 X 65 1 X 100 1 X 80 CRUCE X AVE | C23010800042 | New_Event | Animals | Include | Include | Wildlife | 229 | 2023-01-08 | 57250 | keep | 0 | Jan | 2023 | 0.038993 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2023-01-08 08:30 | 2023-01-08 09:57 | 150 | 1:27 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23010800010 | New_Event | Animals | Include | Include | Wildlife | 87 | 2023-01-08 | 13050 | keep | 0 | Jan | 2023 | 0.0088883 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-01-08 09:00 | 2023-01-08 12:20 | 76 | 3:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23010800015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2023-01-08 | 15200 | keep | 0 | Jan | 2023 | 0.010353 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
VEGA BAJA | 2023-01-08 09:00 | 2023-01-08 09:20 | 10 | 0:20 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO PARARAYO | B23010800010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 20 | 2023-01-08 | 200 | keep | 0 | Jan | 2023 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-01-08 09:04 | 2023-01-08 13:00 | 10 | 3:56 | P | MAL TIEMPO/RAYOS | 1 X 20 EN C/L MAL TIEMPO RAYOS | P23010800021 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 236 | 2023-01-08 | 2360 | keep | 0 | Jan | 2023 | 0.0016074 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-08 09:37 | 2023-01-08 13:50 | 100 | 4:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C23010800020 | New_Event | Cutout Failure | Include | Include | Equipment | 253 | 2023-01-08 | 25300 | keep | 0 | Jan | 2023 | 0.017232 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-08 10:00 | 2023-01-08 10:45 | 8 | 0:45 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO PARARAYO | B23010800014 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 45 | 2023-01-08 | 360 | keep | 0 | Jan | 2023 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-08 10:06 | 2023-01-08 11:00 | 737 | 0:54 | P | NO SE REPORTO CAUSA | SE ENCONTRO BKR 1346-02 ABIERTO SE CERRO EN EL CAMPO, SOLO LLEVA 40% DE SU CARGA | S23010800022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2023-01-08 | 39798 | keep | 0 | Jan | 2023 | 0.027106 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
HUMACAO | 2023-01-08 10:36 | 2023-01-08 14:18 | 150 | 3:42 | P | DESGANCHE | 2 X 65 EN C/L | C23010800041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-01-08 | 33300 | keep | 0 | Jan | 2023 | 0.02268 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-01-08 10:59 | 2023-01-08 12:47 | 35 | 1:48 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA / AVE CRUZO FASE A TIERRA | M23010800037 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-01-08 | 3780 | keep | 0 | Jan | 2023 | 0.0025745 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-01-08 11:16 | 2023-01-08 11:17 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2301080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 5809 | keep | 0 | Jan | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
CAGUAS | 2023-01-08 11:18 | 2023-01-08 14:51 | 40 | 3:33 | P | CONDUCTOR ROTO O ABIERTO | REPARO BAJANTE DE LINEA A CAJA | C23010800053 | New_Event | Primary Wire Break | Include | Include | Equipment | 213 | 2023-01-08 | 8520 | keep | 0 | Jan | 2023 | 0.0058029 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-01-08 11:37 | 2023-01-08 11:54 | 518 | 0:17 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23010800055 | New_Event | Animals | Include | Include | Wildlife | 17 | 2023-01-08 | 8806 | keep | 0 | Jan | 2023 | 0.0059977 | 0.00035281 | Sustained | FALSE | FALSE | Not_TMED_Event | 518
BAYAMON | 2023-01-08 11:44 | 2023-01-08 13:18 | 10 | 1:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23010800021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 94 | 2023-01-08 | 940 | keep | 0 | Jan | 2023 | 0.00064023 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-08 11:48 | 2023-01-08 13:30 | 12 | 1:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23010800030 | New_Event | Primary Wire Break | Include | Include | Equipment | 102 | 2023-01-08 | 1224 | keep | 0 | Jan | 2023 | 0.00083366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-01-08 12:10 | 2023-01-08 15:37 | 57 | 3:27 | P | DESGANCHE | 1 X 30 EN C/L | C23010800059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-01-08 | 11799 | keep | 0 | Jan | 2023 | 0.0080362 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2023-01-08 12:13 | 2023-01-08 15:35 | 51 | 3:22 | P | TERMINACION SOTERRADA AVERIADA | 2 X 50 EN RISER 2 X 40 EN SUB. DE EDIFICIO SE REPARO TERMINACION | S23010800061 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 202 | 2023-01-08 | 10302 | keep | 0 | Jan | 2023 | 0.0070166 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
SAN JUAN | 2023-01-08 12:17 | 2023-01-08 17:17 | 59 | 5:00 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23010800131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-01-08 | 17700 | keep | 0 | Jan | 2023 | 0.012055 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BAYAMON | 2023-01-08 12:17 | 2023-01-08 17:46 | 93 | 5:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B23010800024 | New_Event | Cutout Failure | Include | Include | Equipment | 329 | 2023-01-08 | 30597 | keep | 0 | Jan | 2023 | 0.020839 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
BAYAMON | 2023-01-08 12:21 | 2023-01-08 12:22 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO X CONTROL | S2301080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 2466 | keep | 0 | Jan | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
YAUCO | 2023-01-08 12:24 | 2023-01-08 14:30 | 15 | 2:06 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO CONEXIONES PRIMARIAS EN EL TRANSFORMADOR | M23010800055 | New_Event | Primary Wire Break | Include | Include | Equipment | 126 | 2023-01-08 | 1890 | keep | 0 | Jan | 2023 | 0.0012873 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-08 12:38 | 2023-01-08 15:59 | 112 | 3:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y C/L SE REMPLAZO PORTAFUSIBLE 2 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | S23010800077 | New_Event | Cutout Failure | Include | Include | Equipment | 201 | 2023-01-08 | 22512 | keep | 0 | Jan | 2023 | 0.015333 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
BAYAMON | 2023-01-08 12:38 | 2023-01-08 16:27 | 43 | 3:49 | P | DESGANCHE | 1 X 50 C/L DESGANCHE | B23010800025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-01-08 | 9847 | keep | 0 | Jan | 2023 | 0.0067067 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
ARECIBO | 2023-01-08 12:38 | 2023-01-08 20:17 | 75 | 7:39 | P | CRUCETA DEFECTUOSA O AVERIADA | 3 X 40 EN CORTE DE LINEA 1 X 50 EN CORTE DE LINEA SE ABRIO PUENTES SECCIONALIZAR CRUCETAS PARA SER REMPLAZADAS | A23010800101 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 459 | 2023-01-08 | 34425 | keep | 0 | Jan | 2023 | 0.023447 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-01-08 12:38 | 2023-01-08 19:25 | 40 | 6:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23010800025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2023-01-08 | 16280 | keep | 0 | Jan | 2023 | 0.011088 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-01-08 13:02 | 2023-01-08 14:52 | 1 | 1:50 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | M23010800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-01-08 | 110 | keep | 0 | Jan | 2023 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-08 13:10 | 2023-01-08 14:50 | 6 | 1:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A23010800027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2023-01-08 | 600 | keep | 0 | Jan | 2023 | 0.00040866 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-01-08 13:13 | 2023-01-08 19:45 | 70 | 6:32 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PRIMARIO PARTIDO POR CAMION | C23010800064 | New_Event | Damage From Public | Include | Include | Public | 392 | 2023-01-08 | 27440 | keep | 0 | Jan | 2023 | 0.018689 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-01-08 13:18 | 2023-01-08 15:42 | 7 | 2:24 | P | ANIMAL | 1 X 10 EN XMR IGUANA | B23010800031 | New_Event | Animals | Include | Include | Wildlife | 144 | 2023-01-08 | 1008 | keep | 0 | Jan | 2023 | 0.00068654 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-01-08 13:40 | 2023-01-08 15:32 | 444 | 1:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO 2 CAJAS PRIMARIAS | B23010800041 | New_Event | Cutout Failure | Include | Include | Equipment | 112 | 2023-01-08 | 49728 | keep | 0 | Jan | 2023 | 0.03387 | 0.00030241 | Sustained | FALSE | FALSE | Not_TMED_Event | 444
MAYAGÃœEZ | 2023-01-08 13:48 | 2023-01-08 14:08 | 8 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23010800053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-01-08 | 160 | keep | 0 | Jan | 2023 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-01-08 14:00 | 2023-01-08 21:43 | 100 | 7:43 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | A23010800032 | New_Event | Primary Wire Break | Include | Include | Equipment | 463 | 2023-01-08 | 46300 | keep | 0 | Jan | 2023 | 0.031535 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-08 14:07 | 2023-01-08 17:56 | 1420 | 3:49 | T | ALIMENTADOR AMARRADO | DISPARO BKR 1526-02 QUE LLEVA 1530-06 SE REALIZO DESGANCHE DESDE EL PISO A VARETA EN EL BKR 1530-06 | S23010800095 | New_Event | Feeder Load Transferred | Include | Include | Other | 229 | 2023-01-08 | 325180 | keep | 0 | Jan | 2023 | 0.22148 | 0.00096716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1420
SAN JUAN | 2023-01-08 14:07 | 2023-01-08 17:56 | 437 | 3:49 | T | DESGANCHE | DISPARO BKR 1526-02 QUE LLEVA 1530-06 SE REALIZO DESGANCHE DESDE EL PISO A VARETA EN EL BKR 1530-06 | S23010800095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-01-08 | 100073 | keep | 0 | Jan | 2023 | 0.068159 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2023-01-08 14:09 | 2023-01-08 16:25 | 66 | 2:16 | P | DESGANCHE | 1 X 40 EN RISER DESGANCHE | S23010800092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-01-08 | 8976 | keep | 0 | Jan | 2023 | 0.0061135 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
AGUADILLA | 2023-01-08 14:12 | 2023-01-08 15:20 | 40 | 1:08 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23010800060 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 68 | 2023-01-08 | 2720 | keep | 0 | Jan | 2023 | 0.0018526 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-08 14:15 | 2023-01-08 14:16 | 61 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR | B2301080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 61 | keep | 0 | Jan | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
GUAYAMA | 2023-01-08 14:22 | 2023-01-08 16:31 | 12 | 2:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REMPLAZO CAJA EN XMR | P23010800039 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2023-01-08 | 1548 | keep | 0 | Jan | 2023 | 0.0010543 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-01-08 14:23 | 2023-01-08 15:55 | 100 | 1:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23010800063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 92 | 2023-01-08 | 9200 | keep | 0 | Jan | 2023 | 0.0062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-01-08 14:27 | 2023-01-08 17:00 | 8 | 2:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REMPLAZO CAJA EN C/L | P23010800040 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2023-01-08 | 1224 | keep | 0 | Jan | 2023 | 0.00083366 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-01-08 14:38 | 2023-01-08 16:29 | 20 | 1:51 | P | CONDUCTOR ARRIADO O CRUZADO | ABRIO C/L PARA RETEZAR LINEAS | C23010800069 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 111 | 2023-01-08 | 2220 | keep | 0 | Jan | 2023 | 0.001512 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-01-08 14:44 | 2023-01-08 16:42 | 2000 | 1:58 | P | INTERRUPTOR DE POSTE DEFECTUOSO O AVERIADO | LINEA SAFADA Y AISLADORES ABRIR INTERRUPTOR A PETICION DEL FOREMAN PARA CERRAR BY-PASS DEL INTELIRRUPTER | A23010800038 | New_Event | Pole Breaker Failure | Include | Include | Equipment | 118 | 2023-01-08 | 236000 | keep | 0 | Jan | 2023 | 0.16074 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
VEGA BAJA | 2023-01-08 14:53 | 2023-01-08 22:34 | 30 | 7:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | A23010800044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 461 | 2023-01-08 | 13830 | keep | 0 | Jan | 2023 | 0.0094196 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-08 14:54 | 2023-01-08 20:14 | 12 | 5:20 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S23010800121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 320 | 2023-01-08 | 3840 | keep | 0 | Jan | 2023 | 0.0026154 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-01-08 14:54 | 2023-01-08 15:47 | 1718 | 0:53 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE ABREN MACHETES EN CARR 110 KM 11.4 PARA SECCIONALIZAR AVERIA DE LINEA PRIMARIA PARTIDA Y SE COLOCA INTERRUPTOR EN SERVICIO POR BAMBUS SOBRE LINEA. | M23010800071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2023-01-08 | 91054 | keep | 0 | Jan | 2023 | 0.062016 | 0.0011701 | Sustained | FALSE | FALSE | Not_TMED_Event | 1718
VEGA BAJA | 2023-01-08 14:55 | 2023-01-08 22:35 | 6 | 7:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23010800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 460 | 2023-01-08 | 2760 | keep | 0 | Jan | 2023 | 0.0018798 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-01-08 15:04 | 2023-01-08 20:00 | 100 | 4:56 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23010800079 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 296 | 2023-01-08 | 29600 | keep | 0 | Jan | 2023 | 0.02016 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-08 15:18 | 2023-01-08 18:06 | 1284 | 2:48 | T | ARBOL SOBRE LINEA | DISPARO DE BKR SE SECCIONALIZO ARBOL SOBRE LINEA BY-230108-01 ENTRO UN 80% EN SERVICIO | B23010800050 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 168 | 2023-01-08 | 215712 | keep | 0 | Jan | 2023 | 0.14692 | 0.00087453 | Sustained | FALSE | FALSE | Not_TMED_Event | 1284
AGUADILLA | 2023-01-08 15:22 | 2023-01-08 15:23 | 1827 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23010800089 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-08 | 1827 | keep | 0 | Jan | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2023-01-08 15:23 | 2023-01-08 20:00 | 50 | 4:37 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M23010800130 | 1st_after_momentary | Animals | Include | Include | Wildlife | 277 | 2023-01-08 | 13850 | keep | 0 | Jan | 2023 | 0.0094332 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-01-08 15:25 | 2023-01-08 20:25 | 20 | 5:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23010800070 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 300 | 2023-01-08 | 6000 | keep | 0 | Jan | 2023 | 0.0040866 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-08 15:40 | 2023-01-08 18:19 | 14 | 2:39 | P | ANIMAL | 1 X 20 EN XMR SE RETIRO AVE | S23010800140 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-01-08 | 2226 | keep | 0 | Jan | 2023 | 0.0015161 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-01-08 15:41 | 2023-01-08 19:00 | 100 | 3:19 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CL SE CERRO PUENTE PRIMARIO | M23010800097 | New_Event | Primary Wire Break | Include | Include | Equipment | 199 | 2023-01-08 | 19900 | keep | 0 | Jan | 2023 | 0.013554 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-01-08 15:47 | 2023-01-08 18:18 | 1200 | 2:31 | P | DESGANCHE | SE REPARO LINEA PRIMARIA Y SE CERRO MACHETES BAMBUS SOBRE LINEA | M23010800100 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-01-08 | 181200 | keep | 0 | Jan | 2023 | 0.12341 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-08 15:55 | 2023-01-08 16:47 | 15 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA 1 X 10 XMR | B23010800077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-01-08 | 780 | keep | 0 | Jan | 2023 | 0.00053125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-01-08 16:27 | 2023-01-08 19:32 | 22 | 3:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN RISER MAL TIEMPO LLUVIAS | C23010800076 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 185 | 2023-01-08 | 4070 | keep | 0 | Jan | 2023 | 0.0027721 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
ARECIBO | 2023-01-08 16:28 | 2023-01-08 17:05 | 4 | 0:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23010800088 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 37 | 2023-01-08 | 148 | keep | 0 | Jan | 2023 | 0.0001008 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-01-08 16:34 | 2023-01-08 18:33 | 60 | 1:59 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CL DESCARGAS ELECTRICAS | M23010800115 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 119 | 2023-01-08 | 7140 | keep | 0 | Jan | 2023 | 0.004863 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-01-08 16:38 | 2023-01-08 16:39 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRO INTERRUPTOR LLEVA LA CARGA DEL 3602-03 | C2301080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 6197 | keep | 0 | Jan | 2023 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2023-01-08 16:38 | 2023-01-08 16:39 | 548 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRO INTERRUPTOR CARGA POR EL 3007-03 | C2301080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-08 | 548 | keep | 0 | Jan | 2023 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
ARECIBO | 2023-01-08 16:42 | 2023-01-08 16:46 | 5042 | 0:04 | T | INTERRUPTOR DE POSTE DEFECTUOSO O AVERIADO | SE ABRIO INTERRUPTOR A PETICION FOREMAN JOSE RALAT PARA CERRAR INTELLIRUPTER | A23010800091 | Additional_clients | Pole Breaker Failure | Include | Include | Equipment | 4 | 2023-01-08 | 20168 | keep | 0 | Jan | 2023 | 0.013736 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-08 16:43 | 2023-01-08 16:45 | 125 | 0:02 | T | DESGANCHE | DISPARO CERRADO X CONTROL | C23010800081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-01-08 | 250 | keep | 0 | Jan | 2023 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-01-08 16:45 | 2023-01-08 18:01 | 50 | 1:16 | P | DESGANCHE | 1 X 65 EN C/L | C23010800096 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-01-08 | 3800 | keep | 0 | Jan | 2023 | 0.0025882 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-01-08 16:46 | 2023-01-08 18:42 | 2000 | 1:56 | P | INTERRUPTOR DE POSTE DEFECTUOSO O AVERIADO | SE REMPLAZO AISLADORES Y SE REPARO LINEA ZAFADA CRUZADA SE CERRO BY-PASS INTELLIRUPTER EL CUAL SE AVERIO | A23010800038 | 1st_after_momentary | Pole Breaker Failure | Include | Include | Equipment | 116 | 2023-01-08 | 232000 | keep | 0 | Jan | 2023 | 0.15801 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
AGUADILLA | 2023-01-08 16:48 | 2023-01-08 20:30 | 12 | 3:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M23010800119 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 222 | 2023-01-08 | 2664 | keep | 0 | Jan | 2023 | 0.0018144 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-08 17:04 | 2023-01-08 19:38 | 112 | 2:34 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23010800167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-01-08 | 17248 | keep | 0 | Jan | 2023 | 0.011748 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
BAYAMON | 2023-01-08 17:27 | 2023-01-08 20:47 | 12 | 3:20 | P | SECUNDARIA/OTROS | ABRIR XMR PARA REPARAR PEDESTAL | B23010800093 | New_Event |  |  |  |  | 200 | 2023-01-08 | 2400 | keep | 0 | Jan | 2023 | 0.0016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-01-08 17:58 | 2023-01-08 19:00 | 2 | 1:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23010800054 | New_Event | Primary Wire Break | Include | Include | Equipment | 62 | 2023-01-08 | 124 | keep | 0 | Jan | 2023 | 8.4456e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-01-08 18:06 | 2023-01-08 18:25 | 256 | 0:19 | P | ARBOL SOBRE LINEA | DISPARO DE BKR SE SECCIONALIZO ARBOL SOBRE LINEA BY-230108-01 ENTRO EL 20% QUE FALTABA EN SERVICIO 100% | B23010800050 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 19 | 2023-01-08 | 4864 | keep | 0 | Jan | 2023 | 0.0033128 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-08 18:10 | 2023-01-08 18:45 | 10 | 0:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 XMR SE REMPLAZO PORTAFUSIBLES | R23010800092 | New_Event | Cutout Failure | Include | Include | Equipment | 35 | 2023-01-08 | 350 | keep | 0 | Jan | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-08 18:17 | 2023-01-08 19:34 | 67 | 1:17 | P | NO SE REPORTO CAUSA | 1 SMU DE 40 EN SU-70 | R23010800093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2023-01-08 | 5159 | keep | 0 | Jan | 2023 | 0.0035138 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2023-01-08 18:31 | 2023-01-08 20:50 | 50 | 2:19 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23010800153 | New_Event | Animals | Include | Include | Wildlife | 139 | 2023-01-08 | 6950 | keep | 0 | Jan | 2023 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-08 19:12 | 2023-01-09 11:34 | 225 | 16:22 | T | PARARRAYOS DEFECTUOSO | SJ-230109-02 DISPARO SE CORRIGIO CONDICIONES DE PARARRAYOS EN EL 1303-04 QUE ESTA ATRAVES DEL 1303-05 | S2301090000X | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 982 | 2023-01-08 | 220950 | keep | 0 | Jan | 2023 | 0.15049 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
ARECIBO | 2023-01-08 19:53 | 2023-01-09 09:30 | 25 | 13:37 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A23010800122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 817 | 2023-01-08 | 20425 | keep | 0 | Jan | 2023 | 0.013911 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-01-08 20:16 | 2023-01-08 21:20 | 10 | 1:04 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | P23010800063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2023-01-08 | 640 | keep | 0 | Jan | 2023 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-01-08 20:17 | 2023-01-09 14:56 | 10 | 18:39 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETA Y SE CERRARON PUENTES PRIMARIOS | A23010800005 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 1119 | 2023-01-08 | 11190 | keep | 0 | Jan | 2023 | 0.0076215 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-01-08 21:44 | 2023-01-09 14:30 | 200 | 16:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M23010800173 | New_Event | Primary Wire Break | Include | Include | Equipment | 1006 | 2023-01-08 | 201200 | keep | 0 | Jan | 2023 | 0.13704 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-01-08 21:56 | 2023-01-08 23:16 | 9 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23010800110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-01-08 | 720 | keep | 0 | Jan | 2023 | 0.00049039 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-01-08 22:12 | 2023-01-08 22:13 | 4702 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2301090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 4702 | keep | 0 | Jan | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
BAYAMON | 2023-01-08 23:44 | 2023-01-08 23:45 | 1834 | 0:01 | T | NO SE REPORTO CAUSA | RECIERE DE INTERRUPTOR | B2301080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-08 | 1834 | keep | 0 | Jan | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
HUMACAO | 2023-01-09 00:11 | 2023-01-09 00:12 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23010900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-09 | 2126 | keep | 0 | Jan | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
VEGA BAJA | 2023-01-09 02:01 | 2023-01-09 10:23 | 18 | 8:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA BAJANTE PRIMARIO | A23010900002 | New_Event | Primary Wire Break | Include | Include | Equipment | 502 | 2023-01-09 | 9036 | keep | 0 | Jan | 2023 | 0.0061544 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2023-01-09 02:17 | 2023-01-09 06:32 | 50 | 4:15 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L SE LEVANTO CONDUCTOR | B23010900002 | New_Event | Primary Wire Break | Include | Include | Equipment | 255 | 2023-01-09 | 12750 | keep | 0 | Jan | 2023 | 0.008684 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-01-09 02:28 | 2023-01-09 02:29 | 1457 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23010900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-09 | 1457 | keep | 0 | Jan | 2023 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
FAJARDO | 2023-01-09 02:30 | 2023-01-09 08:10 | 222 | 5:40 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R23010900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 340 | 2023-01-09 | 75480 | keep | 0 | Jan | 2023 | 0.051409 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
CANOVANAS | 2023-01-09 05:58 | 2023-01-09 08:59 | 1 | 3:01 | P | PROBLEMA DEL CLIENTE | 1 X 40 EN BANCO DE TRANSFORMADORES PROA | R23010900013 | New_Event | Customer-Related Interruption | Include | Include | Public | 181 | 2023-01-09 | 181 | keep | 0 | Jan | 2023 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-09 06:04 | 2023-01-09 12:46 | 20 | 6:42 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23010900024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 402 | 2023-01-09 | 8040 | keep | 0 | Jan | 2023 | 0.005476 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-09 06:04 | 2023-01-09 12:20 | 1 | 6:16 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN C/L SE CERRO PUENTE | B23010900011 | New_Event | Primary Wire Break | Include | Include | Equipment | 376 | 2023-01-09 | 376 | keep | 0 | Jan | 2023 | 0.00025609 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-09 06:49 | 2023-01-09 08:53 | 103 | 2:04 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23010900009 | New_Event | Animals | Include | Include | Wildlife | 124 | 2023-01-09 | 12772 | keep | 0 | Jan | 2023 | 0.008699 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
HUMACAO | 2023-01-09 07:03 | 2023-01-09 07:04 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C23010900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-09 | 551 | keep | 0 | Jan | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
VEGA BAJA | 2023-01-09 07:26 | 2023-01-09 12:45 | 8 | 5:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | A23010900013 | New_Event | Cutout Failure | Include | Include | Equipment | 319 | 2023-01-09 | 2552 | keep | 0 | Jan | 2023 | 0.0017382 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-01-09 07:28 | 2023-01-09 11:01 | 25 | 3:33 | P | DESGANCHE | 1 X 50 EN C/L | C23010900013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-01-09 | 5325 | keep | 0 | Jan | 2023 | 0.0036268 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-09 07:51 | 2023-01-09 07:52 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | HACIENDO OPERACIONES DE V/L D20232422 DISPARO BKR 1206-03 LLEVA 85% DEL 1204-05 CERRADO X CONTROL | S2301090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-09 | 8679 | keep | 0 | Jan | 2023 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-01-09 07:51 | 2023-01-09 07:52 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | HACIENDO OPERACIONES DE V/L D20232422 DISPARO BKR LLEVA 85% DEL 1204-05 CERRADO X CONTROL | S2301090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-09 | 4133 | keep | 0 | Jan | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
CANOVANAS | 2023-01-09 07:51 | 2023-01-09 07:52 | 1615 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | D2023-2422 DISPARO EN MEDIO DE OPERACIONES DE VIA LIBRE Y SE CERRO POR SCADA | S2301090000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-09 | 1615 | keep | 0 | Jan | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
BARRANQUITAS | 2023-01-09 07:51 | 2023-01-09 11:55 | 1 | 4:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE TRANSFORMADORES | C23010900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2023-01-09 | 244 | keep | 0 | Jan | 2023 | 0.00016619 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-09 07:52 | 2023-01-09 11:25 | 100 | 3:33 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A MACHETE | R23010900050 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 213 | 2023-01-09 | 21300 | keep | 0 | Jan | 2023 | 0.014507 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-09 07:54 | 2023-01-09 09:32 | 1681 | 1:38 | T | DESGANCHE | DISPARO 1303-04 QUE LLEVA 1346-06 Y 1303-01. | S23010900027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-01-09 | 164738 | keep | 0 | Jan | 2023 | 0.1122 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-01-09 07:54 | 2023-01-09 09:32 | 1598 | 1:38 | T | ALIMENTADOR AMARRADO | DISPARO 1303-04 QUE LLEVA 1346-06 Y 1303-01. | S23010900027 | New_Event | Feeder Load Transferred | Include | Include | Other | 98 | 2023-01-09 | 156604 | keep | 0 | Jan | 2023 | 0.10666 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
CANOVANAS | 2023-01-09 08:09 | 2023-01-09 08:29 | 6 | 0:20 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R23010900029 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 20 | 2023-01-09 | 120 | keep | 0 | Jan | 2023 | 8.1731e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-09 08:10 | 2023-01-09 08:11 | 414 | 0:01 | P | ERROR HUMANO | DISPARO DE BKR 1204-01 QUE LLEVA 30% DEL 1204-03 HACIENDO OPERACIONES DE VIA LIBRE SE VERIFICO PERSONAL SE CERRO POR SCADA. PERSONAL EN EL CAMPO NO VERIFICO FASEO | S2301090000X | New_Event | Human Error | Include | Include | Other | 1 | 2023-01-09 | 414 | keep | 0 | Jan | 2023 | 0.00028197 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
SAN JUAN | 2023-01-09 08:11 | 2023-01-09 08:12 | 338 | 0:01 | T | OTRAS CAUSAS | SE ABRE INTERRUPTOR 1206-01 QUE LLEVA 1206-02 POR ERROR EN VIA LIBRE D2023-2422 AMARRE NO FASEABA CON PORTATIL | S23010900052 | New_Event | Other Causes | Include | Include | Other | 1 | 2023-01-09 | 338 | keep | 0 | Jan | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2023-01-09 08:11 | 2023-01-09 08:12 | 733 | 0:01 | T | OTRAS CAUSAS | SE ABRE INTERRUPTOR 1206-01 QUE LLEVA 1206-02 POR ERROR EN VIA LIBRE D2023-2422 AMARRE NO FASEA CON PORTATIL. | S2301090000X | New_Event | Other Causes | Include | Include | Other | 1 | 2023-01-09 | 733 | keep | 0 | Jan | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
ARECIBO | 2023-01-09 08:14 | 2023-01-09 10:21 | 1 | 2:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN TRANSFORMADOR POR MAL TIEMPO | A23010900016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 127 | 2023-01-09 | 127 | keep | 0 | Jan | 2023 | 8.6499e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-09 08:29 | 2023-01-09 08:30 | 4154 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R23010900037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-09 | 4154 | keep | 0 | Jan | 2023 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2023-01-09 08:30 | 2023-01-09 10:12 | 6 | 1:42 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R23010900029 | Partial_restoration | Secondary Vegetation | Include | Include | Vegetation | 102 | 2023-01-09 | 612 | keep | 0 | Jan | 2023 | 0.00041683 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-01-09 08:35 | 2023-01-09 08:37 | 3744 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23010900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-09 | 7488 | keep | 0 | Jan | 2023 | 0.0051 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
CANOVANAS | 2023-01-09 08:42 | 2023-01-09 11:25 | 100 | 2:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R23010900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2023-01-09 | 16300 | keep | 0 | Jan | 2023 | 0.011102 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-01-09 08:42 | 2023-01-09 10:06 | 25 | 1:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS QUEMADAS | R23010900042 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2023-01-09 | 2100 | keep | 0 | Jan | 2023 | 0.0014303 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-01-09 08:43 | 2023-01-09 09:20 | 10 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA | B23010900019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-01-09 | 370 | keep | 0 | Jan | 2023 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-01-09 09:06 | 2023-01-09 09:51 | 5 | 0:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA 1 X 80 EN CORTE DE LINEA | P23010900076 | New_Event | Cutout Failure | Include | Include | Equipment | 45 | 2023-01-09 | 225 | keep | 0 | Jan | 2023 | 0.00015325 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-01-09 09:06 | 2023-01-09 15:00 | 8 | 5:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA RELACIONADO A EVENTO M23010900038 | M23010900078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 354 | 2023-01-09 | 2832 | keep | 0 | Jan | 2023 | 0.0019289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-09 09:12 | 2023-01-09 10:32 | 870 | 1:20 | T | ALIMENTADOR AMARRADO | SJ-230109-02 SE CORRIGIO CONDICIONES DE PARARRAYOS EN EL 1303-04 QUE ESTA ATRAVES DEL 1303-05 | S2301090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 80 | 2023-01-09 | 69600 | keep | 0 | Jan | 2023 | 0.047404 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-01-09 09:23 | 2023-01-09 09:26 | 1483 | 0:03 | P | DESGANCHE | SE ABRIO BKR 1303-02 QUE LLEVA 30% DEL 1204-04 PARA RETIRAR BAMBUAS ENCIMA DE LA LINEA | S2301090000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-01-09 | 4449 | keep | 0 | Jan | 2023 | 0.0030302 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-01-09 09:23 | 2023-01-09 09:26 | 2435 | 0:03 | T | DESGANCHE | SE ABRIO BKR 1303-02 QUE LLEVA 30% DEL 1204-04 PARA RETIRAR BAMBUAS ENCIMA DE LA LINEA | S2301090000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-01-09 | 7305 | keep | 0 | Jan | 2023 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
PONCE | 2023-01-09 09:28 | 2023-01-09 11:57 | 4009 | 2:29 | T | DESGANCHE | DISPARO INTERRUPTOR SE CONFIRMO EN EL AREA SE HIZO DESGANCHE MASIVO | P23010900068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-01-09 | 597341 | keep | 0 | Jan | 2023 | 0.40685 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
SAN JUAN | 2023-01-09 09:32 | 2023-01-09 09:36 | 1513 | 0:04 | P | DESGANCHE | DISPARO 1303-04 QUE LLEVA 1346-06 Y 1303-01. SE RETIRARON BAMBUAS EN LA LINEA. | S23010900027 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4 | 2023-01-09 | 6052 | keep | 0 | Jan | 2023 | 0.004122 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-09 09:33 | 2023-01-09 11:56 | 437 | 2:23 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L Y 2 X 50 | S23010900303 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2023-01-09 | 62491 | keep | 0 | Jan | 2023 | 0.042562 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2023-01-09 09:37 | 2023-01-09 09:39 | 2391 | 0:02 | T | DESGANCHE | DISPARO SE CERRO POR CONTROL | S2301090000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-01-09 | 4782 | keep | 0 | Jan | 2023 | 0.003257 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
SAN JUAN | 2023-01-09 09:37 | 2023-01-09 09:39 | 300 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1343-05 QUE LLEVA CONVERTIDOR 1908-03 SE CERRO POR CONTROL | S2301090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-09 | 600 | keep | 0 | Jan | 2023 | 0.00040866 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-01-09 09:39 | 2023-01-09 14:09 | 51 | 4:30 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S23010900361 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 270 | 2023-01-09 | 13770 | keep | 0 | Jan | 2023 | 0.0093787 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
YAUCO | 2023-01-09 09:40 | 2023-01-09 17:00 | 10 | 7:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23010900079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 440 | 2023-01-09 | 4400 | keep | 0 | Jan | 2023 | 0.0029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-09 09:50 | 2023-01-09 11:20 | 14 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRA EN PEDESTAL | B23010900026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-01-09 | 1260 | keep | 0 | Jan | 2023 | 0.00085818 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-01-09 09:50 | 2023-01-09 11:20 | 1 | 1:30 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL DE LA LINEA Y SE CERRO C/L | B23010900336 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 90 | 2023-01-09 | 90 | keep | 0 | Jan | 2023 | 6.1299e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-01-09 09:53 | 2023-01-09 11:36 | 250 | 1:43 | P | DESGANCHE | OPERA INTELIRRUPTER POR ENREDADERAS EN PARARRAYOS | A23010900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-01-09 | 25750 | keep | 0 | Jan | 2023 | 0.017538 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BARRANQUITAS | 2023-01-09 09:54 | 2023-01-09 16:53 | 1 | 6:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CERRO CAJA QUE NO ESTABA BIEN CERRADA | C23010900039 | New_Event | Cutout Failure | Include | Include | Equipment | 419 | 2023-01-09 | 419 | keep | 0 | Jan | 2023 | 0.00028538 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-09 09:58 | 2023-01-09 09:59 | 2725 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C23010900042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 2725 | keep | 0 | Jan | 2023 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2023-01-09 09:58 | 2023-01-09 09:59 | 1834 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C23010900042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 1834 | keep | 0 | Jan | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2023-01-09 09:58 | 2023-01-09 09:59 | 1437 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C23010900042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 1437 | keep | 0 | Jan | 2023 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2023-01-09 09:58 | 2023-01-09 09:59 | 2565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C23010900043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 2565 | keep | 0 | Jan | 2023 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2023-01-09 09:58 | 2023-01-09 09:59 | 3565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | C23010900043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 3565 | keep | 0 | Jan | 2023 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
GUAYAMA | 2023-01-09 09:58 | 2023-01-09 09:59 | 2751 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23010900123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 2751 | keep | 0 | Jan | 2023 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
GUAYAMA | 2023-01-09 09:58 | 2023-01-09 09:59 | 576 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23010900123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 576 | keep | 0 | Jan | 2023 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
GUAYAMA | 2023-01-09 09:58 | 2023-01-09 09:59 | 2584 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23010900123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 2584 | keep | 0 | Jan | 2023 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
GUAYAMA | 2023-01-09 09:58 | 2023-01-09 09:59 | 1606 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23010900123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 1606 | keep | 0 | Jan | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
GUAYAMA | 2023-01-09 09:58 | 2023-01-09 09:59 | 29 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23010900123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 29 | keep | 0 | Jan | 2023 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
GUAYAMA | 2023-01-09 09:58 | 2023-01-09 09:59 | 4035 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23010900123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 4035 | keep | 0 | Jan | 2023 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
GUAYAMA | 2023-01-09 09:58 | 2023-01-09 09:59 | 3718 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23010900123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-09 | 3718 | keep | 0 | Jan | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CAGUAS | 2023-01-09 10:15 | 2023-01-09 12:33 | 9 | 2:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BARRAS DE PEDESTAL | C23010900044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 138 | 2023-01-09 | 1242 | keep | 0 | Jan | 2023 | 0.00084592 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-01-09 10:17 | 2023-01-09 12:26 | 5 | 2:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R23010900067 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2023-01-09 | 645 | keep | 0 | Jan | 2023 | 0.00043931 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-01-09 10:17 | 2023-01-09 12:47 | 7 | 2:30 | P | ANIMAL | 1 X 8 EN XMR CRUCE X SERPIENTE | R23010900066 | New_Event | Animals | Include | Include | Wildlife | 150 | 2023-01-09 | 1050 | keep | 0 | Jan | 2023 | 0.00071515 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-01-09 10:22 | 2023-01-09 11:02 | 1 | 0:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN C/L LLUVIA | B23010900049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 40 | 2023-01-09 | 40 | keep | 0 | Jan | 2023 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-09 10:31 | 2023-01-09 21:09 | 20 | 10:38 | P | NO SE REPORTO CAUSA | SE CERRO FUSIBLE, SE DEJO EN SERVICIO | B23010900037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 638 | 2023-01-09 | 12760 | keep | 0 | Jan | 2023 | 0.0086908 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-01-09 10:52 | 2023-01-09 12:23 | 40 | 1:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P23010900135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-01-09 | 3640 | keep | 0 | Jan | 2023 | 0.0024792 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-09 11:00 | 2023-01-09 17:57 | 291 | 6:57 | P | EXCAVACIONES | SE SECCIONALIZO TRAMO SOTERRADO DE SU-6 @ SU-7 AVERIADO POR AAA. SE TRABAJO CON BY-230109-01 | B23010900043 | New_Event | Excavation | Include | Include | Public | 417 | 2023-01-09 | 121347 | keep | 0 | Jan | 2023 | 0.082649 | 0.0001982 | Sustained | FALSE | FALSE | Not_TMED_Event | 291
PONCE | 2023-01-09 11:10 | 2023-01-09 13:26 | 1109 | 2:16 | T | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE PRIMARIO Y SE CERRO INTERRUPTOR | P23010900145 | New_Event | Primary Wire Break | Include | Include | Equipment | 136 | 2023-01-09 | 150824 | keep | 0 | Jan | 2023 | 0.10273 | 0.00075533 | Sustained | FALSE | FALSE | Not_TMED_Event | 1109
CANOVANAS | 2023-01-09 11:15 | 2023-01-09 11:35 | 14 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23010900011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-01-09 | 280 | keep | 0 | Jan | 2023 | 0.00019071 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-01-09 11:25 | 2023-01-09 14:40 | 250 | 3:15 | P | ARBOL SOBRE LINEA | 1 X 100 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | M23010900069 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 195 | 2023-01-09 | 48750 | keep | 0 | Jan | 2023 | 0.033203 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-01-09 11:25 | 2023-01-09 13:05 | 1 | 1:40 | P | ANIMAL | 1 X 10 EN XMR RATON | B23010900047 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-01-09 | 100 | keep | 0 | Jan | 2023 | 6.811e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-09 11:30 | 2023-01-09 13:40 | 1 | 2:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23010900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2023-01-09 | 130 | keep | 0 | Jan | 2023 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-09 11:34 | 2023-01-09 12:38 | 23 | 1:04 | P | PARARRAYOS DEFECTUOSO | SJ-230109-02 DISPARO SE CORRIGIO CONDICIONES DE PARARRAYOS EN EL 1303-04 QUE ESTA ATRAVES DEL 1303-05 90 % EN SERVICIO | S2301090000X | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 64 | 2023-01-09 | 1472 | keep | 0 | Jan | 2023 | 0.0010026 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-09 11:34 | 2023-01-09 12:38 | 87 | 1:04 | P | PARARRAYOS DEFECTUOSO | SJ-230109-02 DISPARO SE CORRIGIO CONDICIONES DE PARARRAYOS EN EL 1303-04 QUE ESTA ATRAVES DEL 1303-05 90 % EN SERVICIO | S2301090000X | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 64 | 2023-01-09 | 5568 | keep | 0 | Jan | 2023 | 0.0037923 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
HUMACAO | 2023-01-09 11:51 | 2023-01-09 16:28 | 6 | 4:37 | P | CAUSAS EXTERNAS | SE REEMPLAZO PEDESTAL AVERIADO POR EXCAVADORA | C23010900062 | New_Event | Damage From Public | Include | Include | Public | 277 | 2023-01-09 | 1662 | keep | 0 | Jan | 2023 | 0.001132 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-01-09 11:57 | 2023-01-09 15:00 | 5 | 3:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE CAJAS EN TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS | A23010900078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 183 | 2023-01-09 | 915 | keep | 0 | Jan | 2023 | 0.0006232 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-09 12:03 | 2023-01-10 04:58 | 50 | 16:55 | P | ANIMAL | 1 X 20 EN RISER CRUCE X AVE | B23010900059 | New_Event | Animals | Include | Include | Wildlife | 1015 | 2023-01-09 | 50750 | keep | 0 | Jan | 2023 | 0.034566 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-09 12:05 | 2023-01-09 12:30 | 5 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEPARO SECUNDARIA | C23010900064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-09 | 125 | keep | 0 | Jan | 2023 | 8.5137e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-09 12:12 | 2023-01-09 12:50 | 1 | 0:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S23010900521 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2023-01-09 | 38 | keep | 0 | Jan | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-09 12:12 | 2023-01-09 12:13 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2301090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-09 | 4533 | keep | 0 | Jan | 2023 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
CANOVANAS | 2023-01-09 12:13 | 2023-01-09 13:30 | 69 | 1:17 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R23010900082 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-01-09 | 5313 | keep | 0 | Jan | 2023 | 0.0036187 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2023-01-09 12:21 | 2023-01-09 17:44 | 1 | 5:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIR MONTURA PARA REPARAR SECUNDARIA | B23010900063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 323 | 2023-01-09 | 323 | keep | 0 | Jan | 2023 | 0.00021999 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-09 12:30 | 2023-01-09 12:31 | 2417 | 0:01 | T | ANIMAL | RECIERRE | C23010900067 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-09 | 2417 | keep | 0 | Jan | 2023 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
CAGUAS | 2023-01-09 12:31 | 2023-01-09 15:17 | 194 | 2:46 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | C23010900080 | 1st_after_momentary | Animals | Include | Include | Wildlife | 166 | 2023-01-09 | 32204 | keep | 0 | Jan | 2023 | 0.021934 | 0.00013213 | Sustained | FALSE | FALSE | Not_TMED_Event | 194
VEGA BAJA | 2023-01-09 12:32 | 2023-01-09 17:36 | 10 | 5:04 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR AVE | A23010900084 | New_Event | Animals | Include | Include | Wildlife | 304 | 2023-01-09 | 3040 | keep | 0 | Jan | 2023 | 0.0020705 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-09 12:43 | 2023-01-09 16:13 | 5 | 3:30 | P | TRANSFORMADOR AVERIADO | 2 X 20 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR AVERIADO 25 KVA X 25 KVA | R23010900087 | New_Event | Service Transformer Failure | Include | Include | Equipment | 210 | 2023-01-09 | 1050 | keep | 0 | Jan | 2023 | 0.00071515 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-09 12:50 | 2023-01-09 12:53 | 362 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO 1620-01 QUE LLEVA 90% DEL 1336-10, SE CERRO POR SCADA | S2301090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-09 | 1086 | keep | 0 | Jan | 2023 | 0.00073967 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-01-09 12:50 | 2023-01-09 15:30 | 6 | 2:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIAS | S23010900536 | New_Event | Secondary Wire Break | Include | Include | Equipment | 160 | 2023-01-09 | 960 | keep | 0 | Jan | 2023 | 0.00065385 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-09 12:50 | 2023-01-09 12:53 | 36 | 0:03 | T | DESGANCHE | DISPARO 1620-01 QUE LLEVA 90% DEL 1336-10, SE CERRO POR SCADA | S2301090000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-01-09 | 108 | keep | 0 | Jan | 2023 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-01-09 12:54 | 2023-01-09 15:30 | 23 | 2:36 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | S23010900538 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-01-09 | 3588 | keep | 0 | Jan | 2023 | 0.0024438 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-01-09 12:55 | 2023-01-09 20:15 | 15 | 7:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA | B23010900068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 440 | 2023-01-09 | 6600 | keep | 0 | Jan | 2023 | 0.0044952 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-09 13:00 | 2023-01-09 14:00 | 1 | 1:00 | P | OTRAS CAUSAS | SE ABRIO XMR PARA CONECTAR CLIENTES RESIDENCIALES NUEVOS NUEVOS | B23010900029 | New_Event | Other Causes | Include | Include | Other | 60 | 2023-01-09 | 60 | keep | 0 | Jan | 2023 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-09 13:08 | 2023-01-09 16:25 | 12 | 3:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | B23010900069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 197 | 2023-01-09 | 2364 | keep | 0 | Jan | 2023 | 0.0016101 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-01-09 13:12 | 2023-01-09 13:14 | 2106 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R2301090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-09 | 4212 | keep | 0 | Jan | 2023 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
SAN JUAN | 2023-01-09 13:27 | 2023-01-09 16:45 | 34 | 3:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L Y 1 X 40 EN RISER SE REMPLAZARON CAJAS PRIMARIAS EN AMBOS PUNTOS | S23010900554 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2023-01-09 | 6732 | keep | 0 | Jan | 2023 | 0.0045851 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2023-01-09 13:28 | 2023-01-09 16:17 | 109 | 2:49 | P | DESGANCHE | 1 X 50 EN C/L Y SE REALIZO DESGANCHE | S23010900555 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-01-09 | 18421 | keep | 0 | Jan | 2023 | 0.012546 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
VEGA BAJA | 2023-01-09 13:31 | 2023-01-09 16:42 | 30 | 3:11 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | A23010900096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-01-09 | 5730 | keep | 0 | Jan | 2023 | 0.0039027 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-01-09 14:01 | 2023-01-09 17:56 | 7 | 3:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO CAJA | B23010900082 | New_Event | Cutout Failure | Include | Include | Equipment | 235 | 2023-01-09 | 1645 | keep | 0 | Jan | 2023 | 0.0011204 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-01-09 14:07 | 2023-01-10 18:00 | 1 | 27:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23010900101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1673 | 2023-01-09 | 1673 | keep | 0 | Jan | 2023 | 0.0011395 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-09 14:08 | 2023-01-09 15:07 | 3 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23010900084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2023-01-09 | 177 | keep | 0 | Jan | 2023 | 0.00012055 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-01-09 14:16 | 2023-01-09 14:55 | 1 | 0:39 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | C23010900090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2023-01-09 | 39 | keep | 0 | Jan | 2023 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-09 14:29 | 2023-01-10 10:06 | 30 | 19:37 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | B23010900090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1177 | 2023-01-09 | 35310 | keep | 0 | Jan | 2023 | 0.024049 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-01-09 14:47 | 2023-01-09 15:14 | 24 | 0:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23010900099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2023-01-09 | 648 | keep | 0 | Jan | 2023 | 0.00044135 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
AGUADILLA | 2023-01-09 14:58 | 2023-01-09 17:52 | 15 | 2:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | M23010900135 | New_Event | Cutout Failure | Include | Include | Equipment | 174 | 2023-01-09 | 2610 | keep | 0 | Jan | 2023 | 0.0017777 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-09 15:18 | 2023-01-09 16:25 | 19 | 1:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA | S23010900595 | New_Event | Secondary Wire Break | Include | Include | Equipment | 67 | 2023-01-09 | 1273 | keep | 0 | Jan | 2023 | 0.00086703 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-01-09 15:18 | 2023-01-09 18:03 | 79 | 2:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S23010900594 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2023-01-09 | 13035 | keep | 0 | Jan | 2023 | 0.0088781 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
HUMACAO | 2023-01-09 15:30 | 2023-01-09 17:08 | 258 | 1:38 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23010900104 | New_Event | Animals | Include | Include | Wildlife | 98 | 2023-01-09 | 25284 | keep | 0 | Jan | 2023 | 0.017221 | 0.00017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 258
CAGUAS | 2023-01-09 15:31 | 2023-01-09 15:50 | 1 | 0:19 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | C23010900103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-01-09 | 19 | keep | 0 | Jan | 2023 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-09 15:36 | 2023-01-09 15:44 | 11 | 0:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA EN PEDESTAL | C23010900105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 8 | 2023-01-09 | 88 | keep | 0 | Jan | 2023 | 5.9936e-05 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-01-09 15:55 | 2023-01-09 18:00 | 100 | 2:05 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23010900147 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 125 | 2023-01-09 | 12500 | keep | 0 | Jan | 2023 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-01-09 16:02 | 2023-01-09 17:00 | 80 | 0:58 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P23010900192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-01-09 | 4640 | keep | 0 | Jan | 2023 | 0.0031603 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-09 16:06 | 2023-01-09 18:38 | 2 | 2:32 | P | PARARRAYOS DEFECTUOSO | 2 X 100 EN C/L SE REEMPLAZARON 2 PARARRAYOS Y BAJANTE DE LINEA A CAJA | S23010900602 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 152 | 2023-01-09 | 304 | keep | 0 | Jan | 2023 | 0.00020705 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-01-09 16:19 | 2023-01-09 18:49 | 50 | 2:30 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO EN CAJA DE C/L | P23010900196 | New_Event | Primary Wire Break | Include | Include | Equipment | 150 | 2023-01-09 | 7500 | keep | 0 | Jan | 2023 | 0.0051082 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-01-09 16:30 | 2023-01-09 18:10 | 15 | 1:40 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A23010900136 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 100 | 2023-01-09 | 1500 | keep | 0 | Jan | 2023 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-09 16:45 | 2023-01-09 16:55 | 4133 | 0:10 | T | ALIMENTADOR AMARRADO | HACIENDO PRUEBA EN RISER CAJA PRIMARIA SE PARTIO AL CERRAR, SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA. 1620-02 LLEVANDO 1206-03 POR V/L D20232422 | S2301090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 10 | 2023-01-09 | 41330 | keep | 0 | Jan | 2023 | 0.02815 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2023-01-09 16:45 | 2023-01-09 16:55 | 3718 | 0:10 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | HACIENDO PRUEBA EN RISER CAJA PRIMARIA SE PARTIO AL CERRAR, SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA. 1620-02 LLEVANDO 1206-03 POR V/L D20232422 | S2301090000X | Additional_clients | Cutout Failure | Include | Include | Equipment | 10 | 2023-01-09 | 37180 | keep | 0 | Jan | 2023 | 0.025323 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-09 16:55 | 2023-01-09 19:13 | 34 | 2:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L Y 1 X 40 EN RISER SE REMPLAZARON CAJAS PRIMARIAS EN AMBOS PUNTOS | S23010900554 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 138 | 2023-01-09 | 4692 | keep | 0 | Jan | 2023 | 0.0031957 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-09 17:57 | 2023-01-09 18:01 | 141 | 0:04 | P | EXCAVACIONES | SE SECCIONALIZO TRAMO SOTERRADO DE SU-6 @ SU-7 AVERIADO POR AAA. SE TRABAJO CON BY-230109-01 | B23010900043 | Partial_restoration | Excavation | Include | Include | Public | 4 | 2023-01-09 | 564 | keep | 0 | Jan | 2023 | 0.00038414 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-09 18:01 | 2023-01-10 18:53 | 31 | 24:52 | P | EXCAVACIONES | SE REPARO TRAMO SOTERRADO DE SU-6 @ SU-7 AVERIADO POR AAA. SE TRABAJO CON SF BY-230109-01 | B23010900043 | 1st_after_momentary | Excavation | Include | Include | Public | 1492 | 2023-01-09 | 46252 | keep | 0 | Jan | 2023 | 0.031502 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
ARECIBO | 2023-01-09 18:21 | 2023-01-09 18:22 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23010900152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-09 | 1227 | keep | 0 | Jan | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
AGUADILLA | 2023-01-09 18:38 | 2023-01-09 20:56 | 10 | 2:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA | M23010900147 | New_Event | Service Transformer Failure | Include | Include | Equipment | 138 | 2023-01-09 | 1380 | keep | 0 | Jan | 2023 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-09 18:47 | 2023-01-09 18:48 | 1696 | 0:01 | P | ERROR HUMANO | SE ABREN MACHETES PARA NORMALIZAR VIA LIBRE NO FASEA CON PORTATIL. 1206-04 LLEVA 40% DEL 1204-04 | S2301090000X | New_Event | Human Error | Include | Include | Other | 1 | 2023-01-09 | 1696 | keep | 0 | Jan | 2023 | 0.0011551 | 0.0011551 | Momentary | FALSE | FALSE | Not_TMED_Event | 1696
PONCE | 2023-01-09 18:57 | 2023-01-09 20:31 | 1212 | 1:34 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO Y SE REMPLAZO AISLADOR | P23010900216 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 94 | 2023-01-09 | 113928 | keep | 0 | Jan | 2023 | 0.077596 | 0.00082549 | Sustained | FALSE | FALSE | Not_TMED_Event | 1212
VEGA BAJA | 2023-01-09 19:10 | 2023-01-09 19:18 | 10 | 0:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA ES TRANSFORMADOR PARA REMPLAZAR CONECTOR QUEMADO | A23010900147 | New_Event | Secondary Wire Break | Include | Include | Equipment | 8 | 2023-01-09 | 80 | keep | 0 | Jan | 2023 | 5.4488e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-09 19:16 | 2023-01-09 20:55 | 40 | 1:39 | P | NO SE REPORTO CAUSA | 2 X 80 SMU EN SU-2 | S23010900705 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2023-01-09 | 3960 | keep | 0 | Jan | 2023 | 0.0026971 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-09 19:22 | 2023-01-10 06:09 | 10 | 10:47 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L NO CAUSA | B23010900127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 647 | 2023-01-09 | 6470 | keep | 0 | Jan | 2023 | 0.0044067 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-09 19:24 | 2023-01-10 10:58 | 58 | 15:34 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23010900707 | New_Event | Vegetation Contact | Include | Include | Vegetation | 934 | 2023-01-09 | 54172 | keep | 0 | Jan | 2023 | 0.036896 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
ARECIBO | 2023-01-09 19:24 | 2023-01-09 20:10 | 20 | 0:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CL SE REMPLAZA CAJA PRIMARIA EN CL | A23010900159 | New_Event | Cutout Failure | Include | Include | Equipment | 46 | 2023-01-09 | 920 | keep | 0 | Jan | 2023 | 0.00062661 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-09 19:40 | 2023-01-09 19:41 | 207 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | S2301090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-09 | 207 | keep | 0 | Jan | 2023 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
CANOVANAS | 2023-01-09 19:43 | 2023-01-09 21:43 | 9 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R23010900115 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2023-01-09 | 1080 | keep | 0 | Jan | 2023 | 0.00073558 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-01-09 20:04 | 2023-01-09 22:30 | 3896 | 2:26 | T | DESGANCHE | RECERRO INTERRUPTOR QUEDO FUERA SE RETIRO RAMA DE LA LINEA CON VARETA CERRADO POR CONTROL | C23010900131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-01-09 | 568816 | keep | 0 | Jan | 2023 | 0.38742 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
SAN JUAN | 2023-01-09 20:30 | 2023-01-09 21:52 | 60 | 1:22 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23010900724 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2023-01-09 | 4920 | keep | 0 | Jan | 2023 | 0.003351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-09 21:44 | 2023-01-09 23:13 | 207 | 1:29 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23010900748 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 89 | 2023-01-09 | 18423 | keep | 0 | Jan | 2023 | 0.012548 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2023-01-09 23:13 | 2023-01-09 23:45 | 50 | 0:32 | P | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23010900748 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 32 | 2023-01-09 | 1600 | keep | 0 | Jan | 2023 | 0.0010898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-09 23:45 | 2023-01-09 23:50 | 207 | 0:05 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE DISPARO ALIMENTADOR AL RELIZAR OPERACIONES EN EL CAMPO Y SE SECCIONALIZO AVERIA SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S23010900748 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 5 | 2023-01-09 | 1035 | keep | 0 | Jan | 2023 | 0.00070493 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-09 23:50 | 2023-01-10 01:31 | 80 | 1:41 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO AVERIADO | S23010900748 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 101 | 2023-01-09 | 8080 | keep | 0 | Jan | 2023 | 0.0055033 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-10 00:35 | 2023-01-10 10:29 | 25 | 9:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23011000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 594 | 2023-01-10 | 14850 | keep | 0 | Jan | 2023 | 0.010114 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-01-10 04:50 | 2023-01-10 04:51 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23011000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-10 | 2126 | keep | 0 | Jan | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2023-01-10 05:28 | 2023-01-10 09:30 | 2126 | 4:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE BKR SE REALIZARON OPERACIONES Y SE TRANSFIRIO 80% DE LA CARGA AL 2603-06 | C23011000006 | New_Event | Switch Failure | Include | Include | Equipment | 242 | 2023-01-10 | 514492 | keep | 0 | Jan | 2023 | 0.35042 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2023-01-10 05:52 | 2023-01-10 09:45 | 75 | 3:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23011000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2023-01-10 | 17475 | keep | 0 | Jan | 2023 | 0.011902 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-01-10 06:09 | 2023-01-10 06:10 | 2735 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-10 | 2735 | keep | 0 | Jan | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2023-01-10 06:10 | 2023-01-10 09:11 | 10 | 3:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L NO CAUSA | B23011000127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 181 | 2023-01-10 | 1810 | keep | 0 | Jan | 2023 | 0.0012328 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-01-10 06:12 | 2023-01-10 20:51 | 15 | 14:39 | P | ARBOL SOBRE LINEA | 3 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | A23011000086 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 879 | 2023-01-10 | 13185 | keep | 0 | Jan | 2023 | 0.0089802 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-01-10 06:47 | 2023-01-10 09:28 | 1417 | 2:41 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR RTU DOWN SE CERRO MANUAL ELECTRICO | M23011000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2023-01-10 | 228137 | keep | 0 | Jan | 2023 | 0.15538 | 0.00096511 | Sustained | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2023-01-10 06:55 | 2023-01-10 06:56 | 990 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23011000009 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-10 | 990 | keep | 0 | Jan | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2023-01-10 06:56 | 2023-01-10 17:40 | 15 | 10:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ROTO | M23011000012 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 644 | 2023-01-10 | 9660 | keep | 0 | Jan | 2023 | 0.0065794 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-10 07:20 | 2023-01-10 10:55 | 8 | 3:35 | P | ANIMAL | 1 X 15 EN XMR AVE CRUZO LINEAS | B23011000003 | New_Event | Animals | Include | Include | Wildlife | 215 | 2023-01-10 | 1720 | keep | 0 | Jan | 2023 | 0.0011715 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-01-10 07:20 | 2023-01-10 09:44 | 1 | 2:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 15 EN TRANSFORMADOR SE FIJARON BAJANTES SUELTOS | P23011000007 | New_Event | Secondary Wire Break | Include | Include | Equipment | 144 | 2023-01-10 | 144 | keep | 0 | Jan | 2023 | 9.8078e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-10 07:31 | 2023-01-10 08:42 | 3 | 1:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO PORTAFUSIBLE | C23011000014 | New_Event | Cutout Failure | Include | Include | Equipment | 71 | 2023-01-10 | 213 | keep | 0 | Jan | 2023 | 0.00014507 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2023-01-10 08:10 | 2023-01-10 08:56 | 10 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA EN TRANSFORMADOR PARA REMPLAZO DE CONECTORES EN BAJANTES SECUNDARIOS | M23010400068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2023-01-10 | 460 | keep | 0 | Jan | 2023 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-10 08:17 | 2023-01-10 12:19 | 8 | 4:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23011000016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 242 | 2023-01-10 | 1936 | keep | 0 | Jan | 2023 | 0.0013186 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-10 08:23 | 2023-01-10 12:27 | 447 | 4:04 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA 2 X 40 EN RISER COND. PARK BOULEVARD | S23011000020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2023-01-10 | 109068 | keep | 0 | Jan | 2023 | 0.074286 | 0.00030445 | Sustained | FALSE | FALSE | Not_TMED_Event | 447
HUMACAO | 2023-01-10 08:39 | 2023-01-10 13:04 | 10 | 4:25 | P | ANIMAL | 1 X 25 EN C/L CRUCE X REPTIL | C23011000025 | New_Event | Animals | Include | Include | Wildlife | 265 | 2023-01-10 | 2650 | keep | 0 | Jan | 2023 | 0.0018049 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-10 08:58 | 2023-01-10 13:11 | 60 | 4:13 | P | DESGANCHE | DESGANCHE 2 X 50 EN CORTE DE LINEA | S23011000034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2023-01-10 | 15180 | keep | 0 | Jan | 2023 | 0.010339 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-01-10 09:06 | 2023-01-10 10:22 | 127 | 1:16 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | R23011000011 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-01-10 | 9652 | keep | 0 | Jan | 2023 | 0.0065739 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
BAYAMON | 2023-01-10 09:12 | 2023-01-10 13:21 | 1 | 4:09 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B23011000014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2023-01-10 | 249 | keep | 0 | Jan | 2023 | 0.00016959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-10 09:29 | 2023-01-10 09:32 | 329 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | C2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-10 | 987 | keep | 0 | Jan | 2023 | 0.00067224 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
HUMACAO | 2023-01-10 09:30 | 2023-01-10 09:39 | 425 | 0:09 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETES QUEMADOS CG-230110-01 | C23011000006 | Partial_restoration | Switch Failure | Include | Include | Equipment | 9 | 2023-01-10 | 3825 | keep | 0 | Jan | 2023 | 0.0026052 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-10 09:33 | 2023-01-10 09:34 | 3420 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-10 | 3420 | keep | 0 | Jan | 2023 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2023-01-10 09:34 | 2023-01-10 11:37 | 2 | 2:03 | P | ANIMAL | 1 X 50 CL Y CRUCE X AVE | C23011000047 | New_Event | Animals | Include | Include | Wildlife | 123 | 2023-01-10 | 246 | keep | 0 | Jan | 2023 | 0.00016755 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-01-10 09:39 | 2023-01-10 09:41 | 2126 | 0:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE BKR 2603-06 QUE LLEVA LA CARGA DEL 2603-09 Y SE CERRO CONTROL | C23011000006 | Additional_clients | Switch Failure | Include | Include | Equipment | 2 | 2023-01-10 | 4252 | keep | 0 | Jan | 2023 | 0.002896 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-10 09:41 | 2023-01-10 09:46 | 425 | 0:05 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETES QUEMADOS | C23011000006 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 5 | 2023-01-10 | 2125 | keep | 0 | Jan | 2023 | 0.0014473 | 0.00028947 | Momentary | FALSE | FALSE | Not_TMED_Event | 425
VEGA BAJA | 2023-01-10 09:42 | 2023-01-10 10:00 | 4 | 0:18 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR PARARRRAYO DEFECTUOSO | B23011100001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 18 | 2023-01-10 | 72 | keep | 0 | Jan | 2023 | 4.9039e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-01-10 09:46 | 2023-01-10 10:24 | 2126 | 0:38 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE BKR SE SECCIONALIZO TRAMO Y SE CERRO POR CONTROL 40% EN SERVICIO CG-230110-01 | C23011000006 | Additional_clients | Switch Failure | Include | Include | Equipment | 38 | 2023-01-10 | 80788 | keep | 0 | Jan | 2023 | 0.055024 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-10 09:47 | 2023-01-10 10:23 | 1 | 0:36 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 SMU 20 DE 40A CONTAMINACION | R23011000014 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 36 | 2023-01-10 | 36 | keep | 0 | Jan | 2023 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-10 09:54 | 2023-01-10 13:14 | 3896 | 3:20 | T | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA SE CERRO INTERRUPTOR POR CONTROL | C23011000049 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 200 | 2023-01-10 | 779200 | keep | 0 | Jan | 2023 | 0.53071 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
VEGA BAJA | 2023-01-10 10:00 | 2023-01-10 15:35 | 1 | 5:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO SE REPORTO CAUSA | A23011000065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2023-01-10 | 335 | keep | 0 | Jan | 2023 | 0.00022817 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-10 10:03 | 2023-01-10 11:30 | 5 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y REEMPLAZO DE TRAMO SECUNDARIO | C23011000056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2023-01-10 | 435 | keep | 0 | Jan | 2023 | 0.00029628 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-01-10 10:05 | 2023-01-10 12:00 | 13 | 1:55 | P | SECUNDARIA/OTROS | REEMPLAZO DE PEDESTAL Y BARRAS SECUNDARIAS | P23011000032 | New_Event |  |  |  |  | 115 | 2023-01-10 | 1495 | keep | 0 | Jan | 2023 | 0.0010182 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-01-10 10:10 | 2023-01-10 13:24 | 40 | 3:14 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23011000022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-01-10 | 7760 | keep | 0 | Jan | 2023 | 0.0052853 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-10 10:20 | 2023-01-10 10:42 | 1 | 0:22 | P | NO SE REPORTO CAUSA | 1 X 20 EN SUBESTACION DE ESCUELA NO CAUSA | B23011000025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2023-01-10 | 22 | keep | 0 | Jan | 2023 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-01-10 10:20 | 2023-01-10 11:41 | 6 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REEMPLAZAR BARRAS DE PEDESTAL | R23011000016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2023-01-10 | 486 | keep | 0 | Jan | 2023 | 0.00033101 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-01-10 10:24 | 2023-01-10 14:18 | 1275 | 3:54 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE 60% EN SERVICIO CG-230110-01 | C23011000006 | New_Event | Switch Failure | Include | Include | Equipment | 234 | 2023-01-10 | 298350 | keep | 0 | Jan | 2023 | 0.2032 | 0.0008684 | Sustained | FALSE | FALSE | Not_TMED_Event | 1275
BAYAMON | 2023-01-10 10:39 | 2023-01-10 13:00 | 68 | 2:21 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | B23011000032 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-01-10 | 9588 | keep | 0 | Jan | 2023 | 0.0065303 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
MAYAGÃœEZ | 2023-01-10 10:40 | 2023-01-10 11:40 | 8 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23011000017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-01-10 | 480 | keep | 0 | Jan | 2023 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-10 10:44 | 2023-01-10 12:46 | 24 | 2:02 | P | ANIMAL | 1 X 50 CL CRUCE X AVE | B23011000033 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-01-10 | 2928 | keep | 0 | Jan | 2023 | 0.0019942 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
PONCE | 2023-01-10 10:59 | 2023-01-10 17:36 | 1 | 6:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE MONTURA TRIFASICA 1 X 20 | P23011000100 | New_Event | Primary Wire Break | Include | Include | Equipment | 397 | 2023-01-10 | 397 | keep | 0 | Jan | 2023 | 0.00027039 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-10 11:12 | 2023-01-10 11:14 | 3 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-10 | 6 | keep | 0 | Jan | 2023 | 4.0866e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-01-10 11:32 | 2023-01-10 12:22 | 7 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | C23011000081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-01-10 | 350 | keep | 0 | Jan | 2023 | 0.00023838 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-01-10 11:32 | 2023-01-10 12:30 | 10 | 0:58 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR SECUNDARIA | B23011000049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 58 | 2023-01-10 | 580 | keep | 0 | Jan | 2023 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-10 11:55 | 2023-01-10 12:44 | 1 | 0:49 | P | DESGANCHE | 2 X 25 EN CL Y DESGANCHE | B23011000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2023-01-10 | 49 | keep | 0 | Jan | 2023 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-10 12:00 | 2023-01-10 13:33 | 10 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIA | R23011000023 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2023-01-10 | 930 | keep | 0 | Jan | 2023 | 0.00063342 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-10 12:01 | 2023-01-10 12:40 | 8 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | B23011000010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-01-10 | 312 | keep | 0 | Jan | 2023 | 0.0002125 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-01-10 12:02 | 2023-01-10 14:20 | 20 | 2:18 | P | CAUSAS EXTERNAS | MANIOBRAS PARA SECCIONALIZAR AVERIA POR ACCIDENTE DE CAMION DE RECURSOS NATURALES PARTO POSTE SE ABRIO PUENTES Y SE INSTALO TIERRAS Y SE CERRO CORTE DE LINEA SE QUEDARON SIN SERVICIO 10 CLIENTES | P23011000067 | New_Event | Damage From Public | Include | Include | Public | 138 | 2023-01-10 | 2760 | keep | 0 | Jan | 2023 | 0.0018798 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-01-10 12:12 | 2023-01-10 13:41 | 6 | 1:29 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5 A 37.5 KVA | C23011000031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 89 | 2023-01-10 | 534 | keep | 0 | Jan | 2023 | 0.0003637 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-01-10 12:20 | 2023-01-10 12:21 | 614 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | R23011000071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 614 | keep | 0 | Jan | 2023 | 0.00041819 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2023-01-10 12:20 | 2023-01-10 12:21 | 770 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | R23011000071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 770 | keep | 0 | Jan | 2023 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2023-01-10 12:20 | 2023-01-10 12:21 | 1271 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | R23011000071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 1271 | keep | 0 | Jan | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CANOVANAS | 2023-01-10 12:20 | 2023-01-10 12:21 | 247 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | R23011000071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 247 | keep | 0 | Jan | 2023 | 0.00016823 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
CANOVANAS | 2023-01-10 12:21 | 2023-01-10 14:34 | 15 | 2:13 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 40 EN C/L LINEAS ARRIADAS SE LE PUSO AISLACION PARA LUEGO ENDEREZAR POSTE PRIMARIO | R23011000026 | New_Event | Primary Pole Failure | Include | Include | Equipment | 133 | 2023-01-10 | 1995 | keep | 0 | Jan | 2023 | 0.0013588 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-01-10 12:36 | 2023-01-10 17:03 | 7 | 4:27 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO DE TRANSFORMADOR Y CONEXIONES SECUNDARIAS | P23011000059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 267 | 2023-01-10 | 1869 | keep | 0 | Jan | 2023 | 0.001273 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2023-01-10 12:49 | 2023-01-10 16:55 | 150 | 4:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A23011000044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2023-01-10 | 36900 | keep | 0 | Jan | 2023 | 0.025132 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-01-10 12:50 | 2023-01-10 14:25 | 1337 | 1:35 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | M23011000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2023-01-10 | 127015 | keep | 0 | Jan | 2023 | 0.086509 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
BAYAMON | 2023-01-10 12:55 | 2023-01-10 14:49 | 6 | 1:54 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARO SECUNDARIA Y SE DESGANCHO | B23011000059 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 114 | 2023-01-10 | 684 | keep | 0 | Jan | 2023 | 0.00046587 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-01-10 12:57 | 2023-01-10 17:20 | 280 | 4:23 | P | ALIMENTADOR AMARRADO | 1 X 100 EN CORTE DE LINEA SE PATRULLO Y NO SE DETERMINO CAUSA ESTOS CLIENTES ESTAN AHORA TRAVES DEL 6015-01 | M23011000171 | New_Event | Feeder Load Transferred | Include | Include | Other | 263 | 2023-01-10 | 73640 | keep | 0 | Jan | 2023 | 0.050156 | 0.00019071 | Sustained | FALSE | FALSE | Not_TMED_Event | 280
MAYAGÃœEZ | 2023-01-10 12:57 | 2023-01-10 14:40 | 312 | 1:43 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 6015-01 LLEVA PARTE DE LA CARGA DEL 6014-01 LA CUAL SE SECCIONALIZO Y SE CERRO EL INTERRUPTOR SE CONTINUO PATRULLANDO | M23011000075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2023-01-10 | 32136 | keep | 0 | Jan | 2023 | 0.021888 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
BAYAMON | 2023-01-10 13:11 | 2023-01-10 13:12 | 1210 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 BAMBUAS | B23011000060 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 1210 | keep | 0 | Jan | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
BAYAMON | 2023-01-10 13:11 | 2023-01-10 13:12 | 3438 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 BAMBUAS | B23011000060 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 3438 | keep | 0 | Jan | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2023-01-10 13:11 | 2023-01-10 13:12 | 2605 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 BAMBUAS | B23011000060 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 2605 | keep | 0 | Jan | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-01-10 13:11 | 2023-01-10 13:12 | 73 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 BAMBUAS | B23011000060 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 73 | keep | 0 | Jan | 2023 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2023-01-10 13:14 | 2023-01-10 13:15 | 1210 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 BAMBUAS | B23011000060 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 1210 | keep | 0 | Jan | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
BAYAMON | 2023-01-10 13:14 | 2023-01-10 13:15 | 3438 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 BAMBUAS | B23011000060 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 3438 | keep | 0 | Jan | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2023-01-10 13:14 | 2023-01-10 13:15 | 2605 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 BAMBUAS | B23011000060 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 2605 | keep | 0 | Jan | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-01-10 13:14 | 2023-01-10 13:15 | 73 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 BAMBUAS | B23011000060 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 73 | keep | 0 | Jan | 2023 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
CANOVANAS | 2023-01-10 13:16 | 2023-01-10 19:25 | 21 | 6:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REEMPLAZAR BARRAS DE PEDESTAL | R23011000039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 369 | 2023-01-10 | 7749 | keep | 0 | Jan | 2023 | 0.0052778 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2023-01-10 13:22 | 2023-01-10 14:07 | 20 | 0:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5KVA | B23011000061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2023-01-10 | 900 | keep | 0 | Jan | 2023 | 0.00061299 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-01-10 13:40 | 2023-01-10 14:10 | 12 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23011000021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-01-10 | 360 | keep | 0 | Jan | 2023 | 0.00024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-01-10 13:41 | 2023-01-10 18:24 | 10 | 4:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 30 EN CORTE DE LINEA SE REEMPLAZO 3 CAJAS PRIMARIAS | C23011000113 | New_Event | Cutout Failure | Include | Include | Equipment | 283 | 2023-01-10 | 2830 | keep | 0 | Jan | 2023 | 0.0019275 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-10 13:42 | 2023-01-10 13:43 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-10 | 2178 | keep | 0 | Jan | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CAGUAS | 2023-01-10 13:53 | 2023-01-10 15:21 | 6 | 1:28 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | C23011000118 | New_Event | Animals | Include | Include | Wildlife | 88 | 2023-01-10 | 528 | keep | 0 | Jan | 2023 | 0.00035962 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-01-10 13:54 | 2023-01-10 14:53 | 4 | 0:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B23011000066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2023-01-10 | 236 | keep | 0 | Jan | 2023 | 0.00016074 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-01-10 14:02 | 2023-01-10 16:49 | 10 | 2:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CERRO CAJA PRIMARIA NO FUNDIO | C23011000121 | New_Event | Cutout Failure | Include | Include | Equipment | 167 | 2023-01-10 | 1670 | keep | 0 | Jan | 2023 | 0.0011374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-10 14:07 | 2023-01-10 14:15 | 3295 | 0:08 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICA PERSONAL FUERA PARA PROBARLO CERRADO POR SCADA | B2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2023-01-10 | 26360 | keep | 0 | Jan | 2023 | 0.017954 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-01-10 14:08 | 2023-01-10 14:09 | 2858 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4000 | B2301100000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-10 | 2858 | keep | 0 | Jan | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-01-10 14:09 | 2023-01-10 17:02 | 1 | 2:53 | P | LINEA DE TRANSMISION 38KV | 1 X 10 EN XMR DISCO DE LINEA DE 38KVA FUERA DE USO CAYO ENCIMA DE LA CAJA | B23011000113 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 173 | 2023-01-10 | 173 | keep | 0 | Jan | 2023 | 0.00011783 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-10 14:15 | 2023-01-10 18:57 | 20 | 4:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5KVA | B23011000061 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 282 | 2023-01-10 | 5640 | keep | 0 | Jan | 2023 | 0.0038414 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-10 14:18 | 2023-01-10 14:38 | 850 | 0:20 | P | DESCONECTIVO DEFECTUOSO | SE REALIZO COORDINACION DE FUSIBLE 85% EN SERVICIO CG-230110-01 | C23011000006 | Partial_restoration | Switch Failure | Include | Include | Equipment | 20 | 2023-01-10 | 17000 | keep | 0 | Jan | 2023 | 0.011579 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-01-10 14:20 | 2023-01-10 23:52 | 10 | 9:32 | P | CAUSAS EXTERNAS | SE CAMBIARON 3 POSTES PRIMARIOS Y SE CERRARON PUENTES | P23011000067 | Partial_restoration | Damage From Public | Include | Include | Public | 572 | 2023-01-10 | 5720 | keep | 0 | Jan | 2023 | 0.0038959 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-01-10 14:24 | 2023-01-10 18:20 | 11 | 3:56 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23011000127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2023-01-10 | 2596 | keep | 0 | Jan | 2023 | 0.0017681 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-01-10 14:36 | 2023-01-10 16:02 | 8 | 1:26 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23011000083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2023-01-10 | 688 | keep | 0 | Jan | 2023 | 0.00046859 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-10 14:38 | 2023-01-10 16:00 | 319 | 1:22 | P | DESCONECTIVO DEFECTUOSO | SE REALIZO COORDINACION DE FUSIBLE 100% EN SERVICIO CG-230110-01 | C23011000006 | Partial_restoration | Switch Failure | Include | Include | Equipment | 82 | 2023-01-10 | 26158 | keep | 0 | Jan | 2023 | 0.017816 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-10 14:40 | 2023-01-10 14:41 | 5961 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-10 | 5961 | keep | 0 | Jan | 2023 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2023-01-10 14:43 | 2023-01-10 16:24 | 22 | 1:41 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23011000086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-01-10 | 2222 | keep | 0 | Jan | 2023 | 0.0015134 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
GUAYAMA | 2023-01-10 14:47 | 2023-01-10 16:01 | 5 | 1:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON BARRAS PEDESTAL SECUNDARIO | P23011000082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 74 | 2023-01-10 | 370 | keep | 0 | Jan | 2023 | 0.00025201 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-01-10 14:52 | 2023-01-10 16:10 | 6 | 1:18 | P | CAUSAS EXTERNAS | 3 X 65 EN CORTE DE LINEA CAMION IMPACTO LINEAS | M23011000153 | New_Event | Damage From Public | Include | Include | Public | 78 | 2023-01-10 | 468 | keep | 0 | Jan | 2023 | 0.00031875 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-01-10 14:55 | 2023-01-10 14:56 | 766 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1709-03 SOLO LLEVA 50% DE SU CARGA Y LLEVA 1709-05 | S2301100000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-10 | 766 | keep | 0 | Jan | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-01-10 14:55 | 2023-01-10 14:56 | 2364 | 0:01 | T | DESGANCHE | RECIERRE DEL 1709-03 SOLO LLEVA 50% DE SU CARGA Y LLEVA 1709-05 | S2301100000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-10 | 2364 | keep | 0 | Jan | 2023 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2023-01-10 14:56 | 2023-01-10 17:48 | 1 | 2:52 | P | NO SE REPORTO CAUSA | 3 X 80 EN C/L | S23011000116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2023-01-10 | 172 | keep | 0 | Jan | 2023 | 0.00011715 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-10 14:56 | 2023-01-10 19:37 | 21 | 4:41 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | S23011000121 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 281 | 2023-01-10 | 5901 | keep | 0 | Jan | 2023 | 0.0040191 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
PONCE | 2023-01-10 15:01 | 2023-01-10 15:02 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23011000086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-10 | 2379 | keep | 0 | Jan | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
SAN JUAN | 2023-01-10 15:12 | 2023-01-10 17:58 | 6 | 2:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y PUENTE ABIERTO 1 X 80 Y 1X 65 EN C/L | S23011000104 | New_Event | Cutout Failure | Include | Include | Equipment | 166 | 2023-01-10 | 996 | keep | 0 | Jan | 2023 | 0.00067837 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-01-10 15:18 | 2023-01-10 15:19 | 3420 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-10 | 3420 | keep | 0 | Jan | 2023 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
BARRANQUITAS | 2023-01-10 15:19 | 2023-01-10 15:22 | 2192 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-10 | 6576 | keep | 0 | Jan | 2023 | 0.0044789 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
HUMACAO | 2023-01-10 15:21 | 2023-01-10 16:56 | 50 | 1:35 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 65 EN RISER | C23011000143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2023-01-10 | 4750 | keep | 0 | Jan | 2023 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-01-10 15:38 | 2023-01-10 16:04 | 1 | 0:26 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO BAJANTE PRIMARIO A CAJA DE RISER | P23011000092 | New_Event | Primary Wire Break | Include | Include | Equipment | 26 | 2023-01-10 | 26 | keep | 0 | Jan | 2023 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-10 15:49 | 2023-01-10 15:52 | 125 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR SE CERRO POR SCADA | C2301100000X | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-01-10 | 375 | keep | 0 | Jan | 2023 | 0.00025541 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-01-10 15:52 | 2023-01-10 18:22 | 37 | 2:30 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE REPARO CONDUCTOR QUEMADO | C23011000151 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 150 | 2023-01-10 | 5550 | keep | 0 | Jan | 2023 | 0.0037801 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CAGUAS | 2023-01-10 15:59 | 2023-01-10 19:30 | 3 | 3:31 | P | TRANSFORMADOR AVERIADO | SE REPARO XMR AVERIADO PM T-31 | C23011000158 | New_Event | Service Transformer Failure | Include | Include | Equipment | 211 | 2023-01-10 | 633 | keep | 0 | Jan | 2023 | 0.00043113 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-01-10 16:00 | 2023-01-10 18:23 | 30 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIA | C23011000160 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2023-01-10 | 4290 | keep | 0 | Jan | 2023 | 0.0029219 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-10 16:20 | 2023-01-10 18:49 | 18 | 2:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN PROVISIONAL | B23011000118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2023-01-10 | 2682 | keep | 0 | Jan | 2023 | 0.0018267 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2023-01-10 16:39 | 2023-01-10 16:55 | 5 | 0:16 | P | PROBLEMA DEL CLIENTE | SE ABRIO TRANSFORMADOR PARA DESCONECTAR CLIENTE CON PROBLEMA INTERNO | A23011000024 | New_Event | Customer-Related Interruption | Include | Include | Public | 16 | 2023-01-10 | 80 | keep | 0 | Jan | 2023 | 5.4488e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-10 16:43 | 2023-01-10 16:44 | 225 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-05 SE CERRO POR SCADA LLEVA LA CARGA DEL 1303-04 | S2301100000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-10 | 225 | keep | 0 | Jan | 2023 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-01-10 16:43 | 2023-01-10 16:44 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 SE CERRO POR SCADA LLEVA LA CARGA DEL 1303-04 | S2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-10 | 870 | keep | 0 | Jan | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2023-01-10 16:44 | 2023-01-10 18:45 | 50 | 2:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011000175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-01-10 | 6050 | keep | 0 | Jan | 2023 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-10 17:02 | 2023-01-10 18:25 | 1 | 1:23 | P | ANIMAL | 1 X 40 EN SU-1 SE RETIRO RATON | B23011000075 | New_Event | Animals | Include | Include | Wildlife | 83 | 2023-01-10 | 83 | keep | 0 | Jan | 2023 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-10 17:02 | 2023-01-10 17:07 | 2858 | 0:05 | T | LINEA DE TRANSMISION 38KV | SE ABRIO FEEDER POR EMERGENCIA SE RETIRA AISLADOR DEL 38KV CRUZADO A VARETA | B23011000125 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-10 | 14290 | keep | 0 | Jan | 2023 | 0.0097329 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-10 17:07 | 2023-01-10 17:32 | 1 | 0:25 | P | LINEA DE TRANSMISION 38KV | 1 X 10 EN XMR DISCO DE LINEA DE 38KVA FUERA DE USO CAYO ENCIMA DE LA CAJA | B23011000113 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2023-01-10 | 25 | keep | 0 | Jan | 2023 | 1.7027e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-10 17:31 | 2023-01-10 19:42 | 52 | 2:11 | P | DESGANCHE | SE REMPLAZO 1X80 EN CL Y 1X65 EN CL SE REALIZO DESGANCHE | S23011000137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-01-10 | 6812 | keep | 0 | Jan | 2023 | 0.0046396 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2023-01-10 17:48 | 2023-01-10 18:56 | 15 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23011000077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2023-01-10 | 1020 | keep | 0 | Jan | 2023 | 0.00069472 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-10 18:26 | 2023-01-10 20:25 | 6 | 1:59 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA CRUZADA | A23011000088 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 119 | 2023-01-10 | 714 | keep | 0 | Jan | 2023 | 0.0004863 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-01-10 18:27 | 2023-01-10 19:53 | 6 | 1:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | P23011000109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-01-10 | 516 | keep | 0 | Jan | 2023 | 0.00035145 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-01-10 18:35 | 2023-01-10 18:57 | 15 | 0:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23011000057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 22 | 2023-01-10 | 330 | keep | 0 | Jan | 2023 | 0.00022476 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-10 18:43 | 2023-01-10 19:34 | 27 | 0:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S23011000133 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2023-01-10 | 1377 | keep | 0 | Jan | 2023 | 0.00093787 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2023-01-10 18:50 | 2023-01-11 10:10 | 3 | 15:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011000195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 920 | 2023-01-10 | 2760 | keep | 0 | Jan | 2023 | 0.0018798 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-01-10 18:53 | 2023-01-11 09:57 | 35 | 15:04 | P | ERROR HUMANO | SE CERRO FUSIBLE EN SU 5. PERSONAL TRABAJANDO AVERIA SOTERRADA NO CERRO FUSIBLES | B23010900043 | New_Event | Human Error | Include | Include | Other | 904 | 2023-01-10 | 31640 | keep | 0 | Jan | 2023 | 0.02155 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-01-10 18:54 | 2023-01-11 00:15 | 29 | 5:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA TRASPATIO | C23011000201 | New_Event | Cutout Failure | Include | Include | Equipment | 321 | 2023-01-10 | 9309 | keep | 0 | Jan | 2023 | 0.0063403 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
HUMACAO | 2023-01-10 18:55 | 2023-01-10 19:56 | 25 | 1:01 | P | ANIMAL | 1 X 65 EN C/L CRUCE X LAGARTO | C23011000202 | New_Event | Animals | Include | Include | Wildlife | 61 | 2023-01-10 | 1525 | keep | 0 | Jan | 2023 | 0.0010387 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-01-10 19:24 | 2023-01-11 09:50 | 30 | 14:26 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M23011000198 | New_Event | Animals | Include | Include | Wildlife | 866 | 2023-01-10 | 25980 | keep | 0 | Jan | 2023 | 0.017695 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-01-10 19:47 | 2023-01-10 21:05 | 5 | 1:18 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011000199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-01-10 | 390 | keep | 0 | Jan | 2023 | 0.00026563 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-01-10 21:56 | 2023-01-11 08:33 | 12 | 10:37 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | B23011000141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 637 | 2023-01-10 | 7644 | keep | 0 | Jan | 2023 | 0.0052063 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-01-10 22:36 | 2023-01-10 22:37 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23011000123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-10 | 2113 | keep | 0 | Jan | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
VEGA BAJA | 2023-01-11 00:15 | 2023-01-11 09:10 | 40 | 8:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23011100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 535 | 2023-01-11 | 21400 | keep | 0 | Jan | 2023 | 0.014575 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-01-11 03:14 | 2023-01-11 03:15 | 215 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23011100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 215 | keep | 0 | Jan | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
GUAYAMA | 2023-01-11 03:16 | 2023-01-11 05:55 | 25 | 2:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE 100A CON 1 X 80 | P23011100012 | New_Event | Cutout Failure | Include | Include | Equipment | 159 | 2023-01-11 | 3975 | keep | 0 | Jan | 2023 | 0.0027074 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-01-11 05:03 | 2023-01-11 11:13 | 327 | 6:10 | T | ALIMENTADOR AMARRADO | CARGA X 2604-01 SE REMPLAZO 2 DISCOS QUEMADOS, SE DESPEGO PUENTE DE LA CRUCETA Y SE ELIMINO BAJANTE PRIMARIO CRUZADO Y PARARRAYO AVERIADO EN DESUSO, AVERIA ES DEL 2604-01 CG-230111-01 | C23011100003 | New_Event | Feeder Load Transferred | Include | Include | Other | 370 | 2023-01-11 | 120990 | keep | 0 | Jan | 2023 | 0.082406 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-11 05:03 | 2023-01-11 10:47 | 2354 | 5:44 | T | CONDUCTOR ROTO O ABIERTO | ENTRO UN 40% EN SERVICIO SE REEMPLAZO 2 DISCOS QUEMADOS, SE DESPEGO PUENTE DE LA CRUCETA Y SE ELIMINO BAJANTE PRIMARIO CRUZADO Y PARARRAYO AVERIADO EN DESUSO, AVERIA ES DEL 2604-01 LLEVA EL 2603-07 CG-230111-01 | C23011100003 | New_Event | Primary Wire Break | Include | Include | Equipment | 344 | 2023-01-11 | 809776 | keep | 0 | Jan | 2023 | 0.55153 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
CAGUAS | 2023-01-11 05:12 | 2023-01-11 05:13 | 3026 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1608 CLIENTES DEL CONVERTIDOR ESTAN POR 3201-01 EN SERVICIO | C2301110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 3026 | keep | 0 | Jan | 2023 | 0.002061 | 0.002061 | Momentary | FALSE | FALSE | Not_TMED_Event | 3026
BARRANQUITAS | 2023-01-11 05:12 | 2023-01-11 10:24 | 32 | 5:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C23011100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2023-01-11 | 9984 | keep | 0 | Jan | 2023 | 0.0068001 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
GUAYAMA | 2023-01-11 05:42 | 2023-01-11 09:10 | 20 | 3:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA PRIMARIA 1 X 65 EN CORTE DE LINEA | P23011100023 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2023-01-11 | 4160 | keep | 0 | Jan | 2023 | 0.0028334 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-11 07:54 | 2023-01-11 07:55 | 742 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2301110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 742 | keep | 0 | Jan | 2023 | 0.00050537 | 0.00050537 | Momentary | FALSE | FALSE | Not_TMED_Event | 742
VEGA BAJA | 2023-01-11 08:03 | 2023-01-11 13:25 | 10 | 5:22 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | A23011100015 | New_Event | Animals | Include | Include | Wildlife | 322 | 2023-01-11 | 3220 | keep | 0 | Jan | 2023 | 0.0021931 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-11 08:11 | 2023-01-11 23:05 | 43 | 14:54 | P | DESGANCHE | ABRIR C/L -PARA REALIZAR DESGANCHE PRIMARIO | S23011100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 894 | 2023-01-11 | 38442 | keep | 0 | Jan | 2023 | 0.026183 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
PONCE | 2023-01-11 08:13 | 2023-01-11 11:26 | 6 | 3:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CABLE NEUTRAL EN LINEA SECUNDARIA | P23011100029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 193 | 2023-01-11 | 1158 | keep | 0 | Jan | 2023 | 0.00078871 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-01-11 08:39 | 2023-01-11 08:40 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR 1907-03 LLEVA EL 1909-09 | B2301110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 222 | keep | 0 | Jan | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-01-11 08:39 | 2023-01-11 08:40 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1907-03 LLEVA EL 1909-09 | B2301110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-11 | 4456 | keep | 0 | Jan | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
HUMACAO | 2023-01-11 08:41 | 2023-01-11 14:39 | 8 | 5:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 10 EN XMR REPARO SECUNDARIA EVENTO TRANSFERIDO DE PNC A CAGUAS | P23011100033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 358 | 2023-01-11 | 2864 | keep | 0 | Jan | 2023 | 0.0019507 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-11 08:42 | 2023-01-11 10:16 | 527 | 1:34 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZARON LINEAS PARTIDAS Y MACHETE AVERIADO SE CERRO INTERRUPTOR | M23011100019 | New_Event | Primary Wire Break | Include | Include | Equipment | 94 | 2023-01-11 | 49538 | keep | 0 | Jan | 2023 | 0.03374 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
AGUADILLA | 2023-01-11 08:54 | 2023-01-11 08:55 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23011100023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 1827 | keep | 0 | Jan | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2023-01-11 08:55 | 2023-01-11 11:30 | 15 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23011100030 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 155 | 2023-01-11 | 2325 | keep | 0 | Jan | 2023 | 0.0015835 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-01-11 09:00 | 2023-01-11 12:40 | 2 | 3:40 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P23011100090 | New_Event | Animals | Include | Include | Wildlife | 220 | 2023-01-11 | 440 | keep | 0 | Jan | 2023 | 0.00029968 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-01-11 09:00 | 2023-01-11 10:55 | 15 | 1:55 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO SE IDENTIFICO CAUSA | M23011100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2023-01-11 | 1725 | keep | 0 | Jan | 2023 | 0.0011749 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-01-11 09:13 | 2023-01-11 16:18 | 1 | 7:05 | P | DESGANCHE | 1 X 25 EN C/L | C23011100067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2023-01-11 | 425 | keep | 0 | Jan | 2023 | 0.00028947 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-11 09:15 | 2023-01-11 09:35 | 7 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23011100017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-01-11 | 140 | keep | 0 | Jan | 2023 | 9.5353e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-01-11 09:21 | 2023-01-11 12:10 | 60 | 2:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-01-11 | 10140 | keep | 0 | Jan | 2023 | 0.0069063 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-01-11 09:23 | 2023-01-11 09:24 | 4381 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23011100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 4381 | keep | 0 | Jan | 2023 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
SAN JUAN | 2023-01-11 09:25 | 2023-01-11 09:27 | 363 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% DEL 1336-10 | S2301100000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-11 | 726 | keep | 0 | Jan | 2023 | 0.00049448 | 0.00024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 363
SAN JUAN | 2023-01-11 09:25 | 2023-01-11 09:27 | 36 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 90% DEL 1336-10 | S2301100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-11 | 72 | keep | 0 | Jan | 2023 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2023-01-11 09:26 | 2023-01-11 13:15 | 6 | 3:49 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23011100021 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 229 | 2023-01-11 | 1374 | keep | 0 | Jan | 2023 | 0.00093583 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-11 09:48 | 2023-01-11 11:07 | 447 | 1:19 | P | PROBLEMA DEL CLIENTE | 1 X 100 EN CORTE DE LINEA SE DEJO FUERA COND. PARK BOUELEVAR (PROA) | S23011100032 | New_Event | Customer-Related Interruption | Include | Include | Public | 79 | 2023-01-11 | 35313 | keep | 0 | Jan | 2023 | 0.024052 | 0.00030445 | Sustained | FALSE | FALSE | Not_TMED_Event | 447
VEGA BAJA | 2023-01-11 09:53 | 2023-01-11 09:54 | 954 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR A PETICION PERSONAL DE CAMPO PARA ABRIR MACHETES PARA SECCIONALIZAR NEUTRAL PRIMARIO EN EL SUELO. 65% 9201-02 TRANSFERIDO AL 9101-03 | B2301110000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-11 | 954 | keep | 0 | Jan | 2023 | 0.00064977 | 0.00064977 | Momentary | FALSE | FALSE | Not_TMED_Event | 954
VEGA BAJA | 2023-01-11 09:54 | 2023-01-11 11:05 | 540 | 1:11 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO Y SE LEVANTO NEUTRAL PRIMARIO EN TRONCAL. SE NORMALIZO CARGAS | B23011100020 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 71 | 2023-01-11 | 38340 | keep | 0 | Jan | 2023 | 0.026113 | 0.00036779 | Sustained | FALSE | FALSE | Not_TMED_Event | 540
HUMACAO | 2023-01-11 10:00 | 2023-01-11 15:08 | 12 | 5:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REEMPLAZO PIN POLE TOP | C23011100082 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 308 | 2023-01-11 | 3696 | keep | 0 | Jan | 2023 | 0.0025173 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-01-11 10:01 | 2023-01-11 10:57 | 12 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR, REEMPLAZO BARRA EN PEDESTAL | C23011100083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2023-01-11 | 672 | keep | 0 | Jan | 2023 | 0.0004577 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-01-11 10:10 | 2023-01-11 14:05 | 80 | 3:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23011100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2023-01-11 | 18800 | keep | 0 | Jan | 2023 | 0.012805 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-11 10:11 | 2023-01-11 12:32 | 1 | 2:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER HACIA SUBESTACION PRIVADA | B23011100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2023-01-11 | 141 | keep | 0 | Jan | 2023 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-11 10:16 | 2023-01-11 17:18 | 300 | 7:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PARTIDO Y MACHETES QUEMADOS | M23011100047 | New_Event | Primary Wire Break | Include | Include | Equipment | 422 | 2023-01-11 | 126600 | keep | 0 | Jan | 2023 | 0.086227 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2023-01-11 10:43 | 2023-01-11 12:35 | 150 | 1:52 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTES DE LINEA DISTINTOS NO SE IDENTIFICO CAUSA | M23011100050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2023-01-11 | 16800 | keep | 0 | Jan | 2023 | 0.011442 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2023-01-11 10:45 | 2023-01-11 11:10 | 10 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23011100003 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-11 | 250 | keep | 0 | Jan | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-11 10:47 | 2023-01-11 17:05 | 1412 | 6:18 | P | CONDUCTOR ROTO O ABIERTO | ENTRO EL 60% QUE FALTABA 100% EN SERVICIO, SE DESPEGO PUENTE DE LA CRUCETA Y SE ELIMINO BAJANTE PRIMARIO CRUZADO Y PARARRAYO AVERIADO EN DESUSO, SE REEMPLAZO 2 DISCOS QUEMADOS , AVERIA ES DEL 2604-01 LLEVA EL 2603-07 | C23011100003 | New_Event | Primary Wire Break | Include | Include | Equipment | 378 | 2023-01-11 | 533736 | keep | 0 | Jan | 2023 | 0.36353 | 0.00096171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1412
BAYAMON | 2023-01-11 10:53 | 2023-01-11 17:28 | 1 | 6:35 | P | NO SE REPORTO CAUSA | 3 X 15 EN XMR | B23011100033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 395 | 2023-01-11 | 395 | keep | 0 | Jan | 2023 | 0.00026903 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-11 10:55 | 2023-01-11 13:03 | 8 | 2:08 | P | ANIMAL | 1 X 8 XMR CRUCE POR AVE | C23011100088 | New_Event | Animals | Include | Include | Wildlife | 128 | 2023-01-11 | 1024 | keep | 0 | Jan | 2023 | 0.00069744 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-11 11:00 | 2023-01-11 12:15 | 28 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO TOMA DE CLIENTE Y SE CERRO TRANSFORMADOR | S23011100048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-01-11 | 2100 | keep | 0 | Jan | 2023 | 0.0014303 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2023-01-11 11:02 | 2023-01-11 12:47 | 310 | 1:45 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | B23011100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2023-01-11 | 32550 | keep | 0 | Jan | 2023 | 0.02217 | 0.00021114 | Sustained | FALSE | FALSE | Not_TMED_Event | 310
HUMACAO | 2023-01-11 11:45 | 2023-01-11 11:49 | 3420 | 0:04 | T | ANIMAL | DISPARO CERRADO X CONTROL | C2301110000X | New_Event | Animals | Include | Include | Wildlife | 4 | 2023-01-11 | 13680 | keep | 0 | Jan | 2023 | 0.0093174 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
BAYAMON | 2023-01-11 11:59 | 2023-01-11 12:40 | 2 | 0:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONDUCTOR SECUNDARIO | B23011100043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 41 | 2023-01-11 | 82 | keep | 0 | Jan | 2023 | 5.585e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-01-11 12:06 | 2023-01-11 15:21 | 1 | 3:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S23011100061 | New_Event | Primary Wire Break | Include | Include | Equipment | 195 | 2023-01-11 | 195 | keep | 0 | Jan | 2023 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-01-11 12:10 | 2023-01-11 13:25 | 13 | 1:15 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P23011100092 | New_Event | Animals | Include | Include | Wildlife | 75 | 2023-01-11 | 975 | keep | 0 | Jan | 2023 | 0.00066407 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2023-01-11 12:16 | 2023-01-11 13:32 | 2 | 1:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | M23011100082 | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2023-01-11 | 152 | keep | 0 | Jan | 2023 | 0.00010353 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-01-11 12:47 | 2023-01-11 13:09 | 1192 | 0:22 | S | DESCONECTIVO DEFECTUOSO | DISPARO BARRA 38 KV VICTORIA TC SE ENCONTRO #5 DE SUBESTACION 7201 AGUADA QUEMADO | M23011100103 | New_Event | Switch Failure | Include | Include | Equipment | 22 | 2023-01-11 | 26224 | keep | 0 | Jan | 2023 | 0.017861 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2023-01-11 12:47 | 2023-01-11 13:09 | 3041 | 0:22 | S | DESCONECTIVO DEFECTUOSO | DISPARO BARRA 38 KV VICTORIA TC SE ENCONTRO #5 DE SUBESTACION 7201 AGUADA QUEMADO | M23011100103 | New_Event | Switch Failure | Include | Include | Equipment | 22 | 2023-01-11 | 66902 | keep | 0 | Jan | 2023 | 0.045567 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2023-01-11 12:47 | 2023-01-11 13:09 | 390 | 0:22 | S | DESCONECTIVO DEFECTUOSO | DISPARO BARRA 38 KV VICTORIA TC SE ENCONTRO #5 DE SUBESTACION 7201 AGUADA QUEMADO | M23011100103 | New_Event | Switch Failure | Include | Include | Equipment | 22 | 2023-01-11 | 8580 | keep | 0 | Jan | 2023 | 0.0058438 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2023-01-11 12:47 | 2023-01-11 13:09 | 650 | 0:22 | S | DESCONECTIVO DEFECTUOSO | DISPARO BARRA 38 KV VICTORIA TC SE ENCONTRO #5 DE SUBESTACION 7201 AGUADA QUEMADO | M23011100103 | New_Event | Switch Failure | Include | Include | Equipment | 22 | 2023-01-11 | 14300 | keep | 0 | Jan | 2023 | 0.0097397 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
AGUADILLA | 2023-01-11 12:47 | 2023-01-11 17:38 | 154 | 4:51 | S | DESCONECTIVO DEFECTUOSO | DISPARO DE BARRA 38 KV VICTORIA SE RETIRO CARGA A SUBESTACION PARA REMPLAZO DE MACHETE #5 QUEMADO | M23011100103 | New_Event | Switch Failure | Include | Include | Equipment | 291 | 2023-01-11 | 44814 | keep | 0 | Jan | 2023 | 0.030523 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2023-01-11 12:47 | 2023-01-11 17:38 | 1261 | 4:51 | S | DESCONECTIVO DEFECTUOSO | DISPARO DE BARRA 38 KV VICTORIA SE RETIRO CARGA A SUBESTACION PARA REMPLAZO DE MACHETE #5 QUEMADO | M23011100103 | New_Event | Switch Failure | Include | Include | Equipment | 291 | 2023-01-11 | 366951 | keep | 0 | Jan | 2023 | 0.24993 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2023-01-11 12:47 | 2023-01-11 17:38 | 3894 | 4:51 | S | DESCONECTIVO DEFECTUOSO | DISPARO DE BARRA 38 KV VICTORIA SE RETIRO CARGA A SUBESTACION PARA REMPLAZO DE MACHETE #5 QUEMADO | M23011100103 | New_Event | Switch Failure | Include | Include | Equipment | 291 | 2023-01-11 | 1133154 | keep | 0 | Jan | 2023 | 0.77179 | 0.0026522 | Sustained | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2023-01-11 12:47 | 2023-01-11 17:38 | 997 | 4:51 | S | DESCONECTIVO DEFECTUOSO | DISPARO DE BARRA 38 KV VICTORIA SE RETIRO CARGA A SUBESTACION PARA REMPLAZO DE MACHETE #5 QUEMADO | M23011100103 | New_Event | Switch Failure | Include | Include | Equipment | 291 | 2023-01-11 | 290127 | keep | 0 | Jan | 2023 | 0.1976 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2023-01-11 12:47 | 2023-01-11 17:38 | 1497 | 4:51 | S | DESCONECTIVO DEFECTUOSO | DISPARO DE BARRA 38 KV VICTORIA SE RETIRO CARGA A SUBESTACION PARA REMPLAZO DE MACHETE #5 QUEMADO | M23011100103 | New_Event | Switch Failure | Include | Include | Equipment | 291 | 2023-01-11 | 435627 | keep | 0 | Jan | 2023 | 0.2967 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
BAYAMON | 2023-01-11 13:03 | 2023-01-11 14:04 | 100 | 1:01 | P | ANIMAL | 1 X 65 EN C/L AVE | B23011100050 | New_Event | Animals | Include | Include | Wildlife | 61 | 2023-01-11 | 6100 | keep | 0 | Jan | 2023 | 0.0041547 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-01-11 13:09 | 2023-01-11 14:44 | 17 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR CONEXIONES SECUNDARIAS | C23011100139 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2023-01-11 | 1615 | keep | 0 | Jan | 2023 | 0.0011 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-01-11 13:10 | 2023-01-11 17:00 | 12 | 3:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23011100065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 230 | 2023-01-11 | 2760 | keep | 0 | Jan | 2023 | 0.0018798 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-01-11 13:22 | 2023-01-11 14:02 | 27 | 0:40 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO DE SU-2A @ PROVISIONAL AEREO SITUACION DE PELIGRO POSTE EN EL PISO SE RETIRO PELIGRO SE RETEZO PROVICIONAL AEREO Y SE ENERGIZO | R23011100027 | New_Event | Primary Pole Failure | Include | Include | Equipment | 40 | 2023-01-11 | 1080 | keep | 0 | Jan | 2023 | 0.00073558 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2023-01-11 13:27 | 2023-01-11 14:18 | 30 | 0:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23011100177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2023-01-11 | 1530 | keep | 0 | Jan | 2023 | 0.0010421 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-01-11 13:31 | 2023-01-11 15:50 | 6 | 2:19 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR IGUANA CRUZO LINEAS | A23011100072 | New_Event | Animals | Include | Include | Wildlife | 139 | 2023-01-11 | 834 | keep | 0 | Jan | 2023 | 0.00056803 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-01-11 14:00 | 2023-01-11 14:03 | 5630 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23011100156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-11 | 16890 | keep | 0 | Jan | 2023 | 0.011504 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
VEGA BAJA | 2023-01-11 14:00 | 2023-01-11 14:58 | 12 | 0:58 | P | CAUSAS EXTERNAS | SE ABRIO XMR Y SE REPARO SECUNDARIA CABLES AVERIADOS POR CAMION | B23011100056 | New_Event | Damage From Public | Include | Include | Public | 58 | 2023-01-11 | 696 | keep | 0 | Jan | 2023 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-11 14:04 | 2023-01-11 14:53 | 13 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23011000078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-01-11 | 637 | keep | 0 | Jan | 2023 | 0.00043386 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-01-11 14:15 | 2023-01-11 14:30 | 7 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A23011100027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-01-11 | 105 | keep | 0 | Jan | 2023 | 7.1515e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-01-11 15:00 | 2023-01-11 15:45 | 8 | 0:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON PROBLEMAS DE VOLTAJE CLIENTE CON ALTO VOLTAJE EVENTO DEL DIA 10 CANASTO NO LLEGABA LO TABAJARON EL DIA 11 | M23011000185 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2023-01-11 | 360 | keep | 0 | Jan | 2023 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-11 15:03 | 2023-01-11 16:24 | 40 | 1:21 | P | ANIMAL | 1 X 50 EN RISER AVE | B23011100066 | New_Event | Animals | Include | Include | Wildlife | 81 | 2023-01-11 | 3240 | keep | 0 | Jan | 2023 | 0.0022067 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-01-11 15:03 | 2023-01-11 15:04 | 1378 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2301110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 1378 | keep | 0 | Jan | 2023 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
BARRANQUITAS | 2023-01-11 15:17 | 2023-01-11 19:00 | 186 | 3:43 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE CERRO PUENTE CG-230111-02 | C23011100178 | New_Event | Primary Wire Break | Include | Include | Equipment | 223 | 2023-01-11 | 41478 | keep | 0 | Jan | 2023 | 0.02825 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
ARECIBO | 2023-01-11 15:33 | 2023-01-11 15:34 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23011100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 1227 | keep | 0 | Jan | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
FAJARDO | 2023-01-11 15:37 | 2023-01-11 16:31 | 8 | 0:54 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | R23011100037 | New_Event | Animals | Include | Include | Wildlife | 54 | 2023-01-11 | 432 | keep | 0 | Jan | 2023 | 0.00029423 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-11 15:43 | 2023-01-11 17:08 | 4291 | 1:25 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIMENTADOR Y NO SE ENCONTRO CAUSA ENTRO 60% EN SERVICIO | S23011100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2023-01-11 | 364735 | keep | 0 | Jan | 2023 | 0.24842 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
CANOVANAS | 2023-01-11 15:43 | 2023-01-11 15:44 | 3699 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE OPERO EL INTELLIRRUPTER, RETIRAR PELIGRO DE POSTE DE TELEFONICA PARTIDO POR IMPACTO DE CAMION SJ-230111-51 | R23011100038 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-01-11 | 3699 | keep | 0 | Jan | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2023-01-11 15:44 | 2023-01-11 16:43 | 2429 | 0:59 | P | CAUSAS EXTERNAS | SE RETIRO PELIGRO DE POSTE DE TELEFONICA PARTIDO EN CIMA DE LAS LINEAS POR IMPACTO DE CAMION Y SE CERRO EL INTELLIRRUPTER SJ-230111-51 | R23011100041 | 1st_after_momentary | Damage From Public | Include | Include | Public | 59 | 2023-01-11 | 143311 | keep | 0 | Jan | 2023 | 0.097608 | 0.0016544 | Sustained | FALSE | FALSE | Not_TMED_Event | 2429
CANOVANAS | 2023-01-11 15:45 | 2023-01-11 19:17 | 9 | 3:32 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23011100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2023-01-11 | 1908 | keep | 0 | Jan | 2023 | 0.0012995 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2023-01-11 15:45 | 2023-01-11 16:08 | 1 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR CONEXIONES SECUNDARIAS | C23011100187 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-01-11 | 23 | keep | 0 | Jan | 2023 | 1.5665e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-01-11 15:45 | 2023-01-19 14:00 | 1 | 190:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO Y SE REPARO LINEA PRIMARIA SE LEVANTO 2000 FT DE LINEA 1/0. | A23011100094 | New_Event | Primary Wire Break | Include | Include | Equipment | 11415 | 2023-01-11 | 11415 | keep | 0 | Jan | 2023 | 0.0077747 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-11 15:52 | 2023-01-11 16:12 | 1 | 0:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REEMPLAZO PORTA FUSIBLE | B23011100048 | New_Event | Cutout Failure | Include | Include | Equipment | 20 | 2023-01-11 | 20 | keep | 0 | Jan | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-11 15:53 | 2023-01-11 18:45 | 1 | 2:52 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23011100096 | New_Event | Primary Wire Break | Include | Include | Equipment | 172 | 2023-01-11 | 172 | keep | 0 | Jan | 2023 | 0.00011715 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-11 16:00 | 2023-01-11 16:01 | 4085 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE BKR | R23011100052 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-11 | 4085 | keep | 0 | Jan | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-01-11 16:01 | 2023-01-11 17:57 | 99 | 1:56 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L SE REPARO LINEA PRIMARIA Y SECUNDARIA | R23011100076 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 116 | 2023-01-11 | 11484 | keep | 0 | Jan | 2023 | 0.0078217 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
CANOVANAS | 2023-01-11 16:05 | 2023-01-11 20:11 | 4 | 4:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REEMPLAZAR BARRAS DE PEDESTAL | R23011100057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 246 | 2023-01-11 | 984 | keep | 0 | Jan | 2023 | 0.0006702 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2023-01-11 16:23 | 2023-01-11 18:20 | 75 | 1:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23011100100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-01-11 | 8775 | keep | 0 | Jan | 2023 | 0.0059766 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-01-11 16:30 | 2023-01-11 17:05 | 8 | 0:35 | P | EXCAVACIONES | SE ABRIO C/L Y SE REMPLAZO AISLADOR | B23011100075 | New_Event | Excavation | Include | Include | Public | 35 | 2023-01-11 | 280 | keep | 0 | Jan | 2023 | 0.00019071 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-01-11 16:49 | 2023-01-11 22:55 | 169 | 6:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23011100212 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 366 | 2023-01-11 | 61854 | keep | 0 | Jan | 2023 | 0.042128 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BARRANQUITAS | 2023-01-11 16:50 | 2023-01-11 21:40 | 22 | 4:50 | P | DESGANCHE | 1 X 40 EN C/L | C23011100213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2023-01-11 | 6380 | keep | 0 | Jan | 2023 | 0.0043454 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
FAJARDO | 2023-01-11 16:53 | 2023-01-11 17:21 | 30 | 0:28 | P | CAUSAS EXTERNAS | 1 X 100 EN C/L CAMION IMPACTO POSTE DE TELEFONO FUNDIO FUSIBLE | R23011100070 | New_Event | Damage From Public | Include | Include | Public | 28 | 2023-01-11 | 840 | keep | 0 | Jan | 2023 | 0.00057212 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-01-11 17:05 | 2023-01-12 15:50 | 1 | 22:45 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERADO AVERIADO MEDIANTE GOI CG-230112-01 | C23011100003 | New_Event | UG Cable Fault | Include | Include | Equipment | 1365 | 2023-01-11 | 1365 | keep | 0 | Jan | 2023 | 0.0009297 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-11 17:06 | 2023-01-11 18:16 | 12 | 1:10 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR | C23011100219 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 70 | 2023-01-11 | 840 | keep | 0 | Jan | 2023 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-11 17:08 | 2023-01-11 17:37 | 1716 | 0:29 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIMENTADOR Y NO SE ENCONTRO CAUSA ENTRO 70% EN SERVICIO | S23011100094 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 29 | 2023-01-11 | 49764 | keep | 0 | Jan | 2023 | 0.033894 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-01-11 17:11 | 2023-01-11 19:25 | 3630 | 2:14 | T | DESGANCHE | SE RETIRO RAMA CRUZANDO LINEAS | M23011100265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-01-11 | 486420 | keep | 0 | Jan | 2023 | 0.3313 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
HUMACAO | 2023-01-11 17:20 | 2023-01-11 18:40 | 90 | 1:20 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23011100223 | New_Event | Animals | Include | Include | Wildlife | 80 | 2023-01-11 | 7200 | keep | 0 | Jan | 2023 | 0.0049039 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-01-11 17:24 | 2023-01-11 17:25 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1118-10 LLEVA 20% 1111-01 SE CERRO POR SCADA EN SERVICIO | S2301110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-11 | 513 | keep | 0 | Jan | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-01-11 17:24 | 2023-01-11 17:25 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVA 20% 1111-01 SE CERRO POR SCADA EN SERVICIO | S2301110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 2782 | keep | 0 | Jan | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BARRANQUITAS | 2023-01-11 17:26 | 2023-01-11 18:17 | 60 | 0:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23011100227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2023-01-11 | 3060 | keep | 0 | Jan | 2023 | 0.0020842 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-11 17:37 | 2023-01-11 17:53 | 1287 | 0:16 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIMENTADOR Y NO SE ENCONTRO CAUSA ENTRO 100% EN SERVICIO | S23011100094 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-01-11 | 20592 | keep | 0 | Jan | 2023 | 0.014025 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-11 17:40 | 2023-01-11 17:41 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C23011100239 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-11 | 476 | keep | 0 | Jan | 2023 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-01-11 17:40 | 2023-01-11 17:41 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C23011100239 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-11 | 1655 | keep | 0 | Jan | 2023 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-01-11 17:40 | 2023-01-11 17:41 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C23011100239 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-11 | 361 | keep | 0 | Jan | 2023 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-01-11 17:40 | 2023-01-11 17:41 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C23011100239 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-11 | 2842 | keep | 0 | Jan | 2023 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-01-11 17:40 | 2023-01-11 17:41 | 1702 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C23011100240 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-11 | 1702 | keep | 0 | Jan | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-01-11 17:40 | 2023-01-11 17:41 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C23011100240 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-11 | 918 | keep | 0 | Jan | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-01-11 17:40 | 2023-01-11 17:41 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C23011100241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-11 | 1725 | keep | 0 | Jan | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
YAUCO | 2023-01-11 17:40 | 2023-01-11 19:12 | 15 | 1:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO ZAFADO | M23011100217 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2023-01-11 | 1380 | keep | 0 | Jan | 2023 | 0.00093991 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-11 17:46 | 2023-01-11 18:12 | 26 | 0:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011100078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 26 | 2023-01-11 | 676 | keep | 0 | Jan | 2023 | 0.00046042 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
HUMACAO | 2023-01-11 18:04 | 2023-01-11 19:15 | 156 | 1:11 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23011100247 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-01-11 | 11076 | keep | 0 | Jan | 2023 | 0.0075438 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
BAYAMON | 2023-01-11 18:26 | 2023-01-11 21:49 | 60 | 3:23 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B23011100083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2023-01-11 | 12180 | keep | 0 | Jan | 2023 | 0.0082957 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-01-11 18:30 | 2023-01-11 21:47 | 37 | 3:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIA | C23011100259 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 197 | 2023-01-11 | 7289 | keep | 0 | Jan | 2023 | 0.0049645 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
VEGA BAJA | 2023-01-11 19:00 | 2023-01-11 19:29 | 1 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011100085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-01-11 | 29 | keep | 0 | Jan | 2023 | 1.9752e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-01-11 19:10 | 2023-01-12 11:09 | 2 | 15:59 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MONTURA DE TRANSFORMADOR PARA REEMPLAZO DE BAJANTE | A23011100117 | New_Event | Primary Wire Break | Include | Include | Equipment | 959 | 2023-01-11 | 1918 | keep | 0 | Jan | 2023 | 0.0013063 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-01-11 19:11 | 2023-01-12 09:54 | 75 | 14:43 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23011100088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 883 | 2023-01-11 | 66225 | keep | 0 | Jan | 2023 | 0.045106 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-01-11 19:18 | 2023-01-11 20:30 | 15 | 1:12 | P | DESGANCHE | 1 X 40 EN C/L | S23011100179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-01-11 | 1080 | keep | 0 | Jan | 2023 | 0.00073558 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-11 19:19 | 2023-01-11 19:21 | 1715 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1708-03 LLEVA 1708-02 SE CERRO POR CONTROL EN SERVICIO | S2301110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-11 | 3430 | keep | 0 | Jan | 2023 | 0.0023362 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-01-11 19:19 | 2023-01-11 19:21 | 1498 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1708-03 LLEVA 1708-02 SE CERRO POR CONTROL EN SERVICIO | S2301110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-11 | 2996 | keep | 0 | Jan | 2023 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
HUMACAO | 2023-01-11 19:28 | 2023-01-11 21:48 | 8 | 2:20 | P | CAUSAS EXTERNAS | ABRIR XMR PARA LEVANTAR SECUNDARIA AVERIADA POR CAMION | C23011100293 | New_Event | Damage From Public | Include | Include | Public | 140 | 2023-01-11 | 1120 | keep | 0 | Jan | 2023 | 0.00076283 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-01-11 19:34 | 2023-01-12 08:51 | 30 | 13:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRA BAMBUA SOBRE LINEA | A23011100118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 797 | 2023-01-11 | 23910 | keep | 0 | Jan | 2023 | 0.016285 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-01-11 19:47 | 2023-01-11 21:20 | 150 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23011100121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-01-11 | 13950 | keep | 0 | Jan | 2023 | 0.0095013 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-01-11 20:17 | 2023-01-11 21:00 | 25 | 0:43 | P | CONDUCTOR ROTO O ABIERTO | ABRIR CAJAS DE TRANSFORMADOR PARA REPARAR NEUTRAL PRIMARIO | A23011100115 | New_Event | Primary Wire Break | Include | Include | Equipment | 43 | 2023-01-11 | 1075 | keep | 0 | Jan | 2023 | 0.00073218 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-01-11 20:26 | 2023-01-12 09:10 | 12 | 12:44 | P | SECUNDARIA/DESGANCHE | 1X10 EN XMR DESGANCHE | C23011100310 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 764 | 2023-01-11 | 9168 | keep | 0 | Jan | 2023 | 0.0062443 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-11 20:40 | 2023-01-12 10:30 | 22 | 13:50 | P | DESGANCHE | 1 X 20 EN PROVISIONAL SE DESGANCHO | B23011100108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 830 | 2023-01-11 | 18260 | keep | 0 | Jan | 2023 | 0.012437 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-01-11 21:09 | 2023-01-11 23:14 | 60 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIA | B23011100111 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2023-01-11 | 7500 | keep | 0 | Jan | 2023 | 0.0051082 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-01-11 21:24 | 2023-01-11 23:50 | 200 | 2:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23011100155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-01-11 | 29200 | keep | 0 | Jan | 2023 | 0.019888 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-01-11 21:26 | 2023-01-12 07:37 | 10 | 10:11 | P | DESGANCHE | 1X30 EN C/L SE RETIRO ENREDADERA DE LA CAJA | C23011100319 | New_Event | Vegetation Contact | Include | Include | Vegetation | 611 | 2023-01-11 | 6110 | keep | 0 | Jan | 2023 | 0.0041615 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-01-11 21:30 | 2023-01-11 21:55 | 9 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES | M23011100331 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-11 | 225 | keep | 0 | Jan | 2023 | 0.00015325 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-01-11 21:45 | 2023-01-12 07:16 | 273 | 9:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L SE REPORTA MAL TIEMPO | B23011100121 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 571 | 2023-01-11 | 155883 | keep | 0 | Jan | 2023 | 0.10617 | 0.00018594 | Sustained | FALSE | FALSE | Not_TMED_Event | 273
BAYAMON | 2023-01-11 21:49 | 2023-01-12 01:44 | 138 | 3:55 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23011100123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2023-01-11 | 32430 | keep | 0 | Jan | 2023 | 0.022088 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-01-11 22:40 | 2023-01-11 22:41 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2301110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 3718 | keep | 0 | Jan | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
AGUADILLA | 2023-01-11 23:00 | 2023-01-12 09:12 | 8 | 10:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REEMPLAZA MASETILLA | A23011100198 | New_Event | Cutout Failure | Include | Include | Equipment | 612 | 2023-01-11 | 4896 | keep | 0 | Jan | 2023 | 0.0033346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-01-11 23:08 | 2023-01-12 10:25 | 200 | 11:17 | P | CONDUCTOR ROTO O ABIERTO | SE CIERRA PUENTE Y SE CIERRA CORTE DE LINEA | A23011100161 | New_Event | Primary Wire Break | Include | Include | Equipment | 677 | 2023-01-11 | 135400 | keep | 0 | Jan | 2023 | 0.09222 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-01-11 23:53 | 2023-01-11 23:54 | 3464 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR CARGA POR EL 2404-08 EN SERVICIO | R23011100085 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-11 | 3464 | keep | 0 | Jan | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2023-01-11 23:53 | 2023-01-11 23:54 | 2675 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 2404-05 EN SERVICIO | R23011100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-11 | 2675 | keep | 0 | Jan | 2023 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
BAYAMON | 2023-01-12 02:08 | 2023-01-12 02:09 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2301120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 1859 | keep | 0 | Jan | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2023-01-12 02:43 | 2023-01-12 02:44 | 723 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1711-05 LLEVA 10% DEL 1711-04 | B2301120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 723 | keep | 0 | Jan | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-01-12 02:43 | 2023-01-12 02:44 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 10% DE SU CARGA POR EL 1711-02 | B2301120000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-12 | 198 | keep | 0 | Jan | 2023 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-01-12 02:43 | 2023-01-12 02:44 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1711-02 | B2301120000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-12 | 1976 | keep | 0 | Jan | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2023-01-12 02:53 | 2023-01-12 12:36 | 200 | 9:43 | P | CONDUCTOR ROTO O ABIERTO | SE CIERRA PUENTE | A23011200011 | New_Event | Primary Wire Break | Include | Include | Equipment | 583 | 2023-01-12 | 116600 | keep | 0 | Jan | 2023 | 0.079416 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-01-12 02:58 | 2023-01-12 02:59 | 723 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1711-05 LLEVA 10% DEL 1711-04 | B2301120000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 723 | keep | 0 | Jan | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-01-12 02:58 | 2023-01-12 02:59 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 10% DE SU CARGA POR EL 1711-02 | B2301120000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-12 | 198 | keep | 0 | Jan | 2023 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-01-12 02:58 | 2023-01-12 02:59 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1711-02 | B2301120000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-12 | 1976 | keep | 0 | Jan | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
PONCE | 2023-01-12 03:20 | 2023-01-12 07:26 | 45 | 4:06 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23011200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2023-01-12 | 11070 | keep | 0 | Jan | 2023 | 0.0075397 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-01-12 04:33 | 2023-01-12 04:34 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23011200003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 5630 | keep | 0 | Jan | 2023 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BARRANQUITAS | 2023-01-12 05:24 | 2023-01-12 08:33 | 80 | 3:09 | P | DESGANCHE | 1X50 EN C/L | C23011200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2023-01-12 | 15120 | keep | 0 | Jan | 2023 | 0.010298 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-12 06:09 | 2023-01-12 08:48 | 15 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN XMR LLUVIAS | B23011200008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2023-01-12 | 2385 | keep | 0 | Jan | 2023 | 0.0016244 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-12 06:49 | 2023-01-12 08:51 | 12 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR LLUVIA | B23011200014 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2023-01-12 | 1464 | keep | 0 | Jan | 2023 | 0.00099712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-12 07:01 | 2023-01-12 09:41 | 50 | 2:40 | P | DESGANCHE | 1 X 65 EN C/L SE DESPEJO LINEA | B23011200015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-01-12 | 8000 | keep | 0 | Jan | 2023 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-12 07:02 | 2023-01-12 12:08 | 30 | 5:06 | P | DESGANCHE | 1X50 EN C/L | C23011200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2023-01-12 | 9180 | keep | 0 | Jan | 2023 | 0.0062525 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-01-12 07:16 | 2023-01-12 07:17 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23011200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 1192 | keep | 0 | Jan | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
YAUCO | 2023-01-12 07:20 | 2023-01-12 13:00 | 1 | 5:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25 KVA A 4.16 KV QUE ALIMENTA FINCA CON CASA DE VERANEO QUE NO ESTABA HABITADA | P23011200007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 340 | 2023-01-12 | 340 | keep | 0 | Jan | 2023 | 0.00023157 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-12 07:25 | 2023-01-12 10:41 | 15 | 3:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LA SECUNDARIA EN VARIOS PUNTOS | C23011200002 | New_Event | Secondary Wire Break | Include | Include | Equipment | 196 | 2023-01-12 | 2940 | keep | 0 | Jan | 2023 | 0.0020024 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-12 07:29 | 2023-01-12 10:40 | 1 | 3:11 | P | DESGANCHE | 1 X 25 EN C/L SE DESGANCHO | B23011200019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-01-12 | 191 | keep | 0 | Jan | 2023 | 0.00013009 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-01-12 07:36 | 2023-01-12 12:10 | 50 | 4:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 Y 2 X 50 EN CORTES DE LINEA DISTINTOS SE REMPLAZO AISLADOR PARTIDO Y SE REPARARON LINEAS ZAFADAS | M23011200008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 274 | 2023-01-12 | 13700 | keep | 0 | Jan | 2023 | 0.009331 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-12 07:56 | 2023-01-12 07:58 | 641 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 7100 | S23011200016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-12 | 1282 | keep | 0 | Jan | 2023 | 0.00087316 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2023-01-12 07:56 | 2023-01-12 07:58 | 308 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 7100 | S23011200016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-12 | 616 | keep | 0 | Jan | 2023 | 0.00041955 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2023-01-12 07:56 | 2023-01-12 07:58 | 559 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 7100 | S23011200016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-12 | 1118 | keep | 0 | Jan | 2023 | 0.00076146 | 0.00038073 | Momentary | FALSE | FALSE | Not_TMED_Event | 559
SAN JUAN | 2023-01-12 07:56 | 2023-01-12 07:58 | 370 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 7100 | S23011200016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-12 | 740 | keep | 0 | Jan | 2023 | 0.00050401 | 0.00025201 | Momentary | FALSE | FALSE | Not_TMED_Event | 370
SAN JUAN | 2023-01-12 07:56 | 2023-01-12 11:59 | 3709 | 4:03 | S | LINEA DE TRANSMISION 38KV | DISPARO 0050 SE FUE A LOCKOUT TRIP PARARRAYO EN ESTRUCTURA LINEA 7100 | S23011200007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 243 | 2023-01-12 | 901287 | keep | 0 | Jan | 2023 | 0.61386 | 0.0025262 | Sustained | FALSE | FALSE | Not_TMED_Event | 3709
SAN JUAN | 2023-01-12 07:56 | 2023-01-12 11:59 | 24 | 4:03 | S | LINEA DE TRANSMISION 38KV | DISPARO 0050 SE FUE A LOCKOUT TRIP PARARRAYO EN ESTRUCTURA LINEA 7100 | S23011200007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 243 | 2023-01-12 | 5832 | keep | 0 | Jan | 2023 | 0.0039721 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-01-12 07:56 | 2023-01-12 11:59 | 1 | 4:03 | S | LINEA DE TRANSMISION 38KV | DISPARO 0050 SE FUE A LOCKOUT TRIP PARARRAYO EN ESTRUCTURA LINEA 7100 | S23011200007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 243 | 2023-01-12 | 243 | keep | 0 | Jan | 2023 | 0.00016551 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-12 07:58 | 2023-01-12 09:54 | 3 | 1:56 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR PROBO MALO, SE RELOCALIZO LA SECUNDARIA A TRANSFORMADOR CERCANO | C23011200015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 116 | 2023-01-12 | 348 | keep | 0 | Jan | 2023 | 0.00023702 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-01-12 08:21 | 2023-01-12 17:12 | 71 | 8:51 | P | DESGANCHE | 3 X 80 EN C/L DESGANCHE | B23011200024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 531 | 2023-01-12 | 37701 | keep | 0 | Jan | 2023 | 0.025678 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
BAYAMON | 2023-01-12 08:50 | 2023-01-12 11:28 | 7 | 2:38 | P | PROBLEMA DEL CLIENTE | 3 X 80 EN RISER @ SU-1 SE DEJO FUERA SUB. WALGREENS | B23012000032 | New_Event | Customer-Related Interruption | Include | Include | Public | 158 | 2023-01-12 | 1106 | keep | 0 | Jan | 2023 | 0.00075329 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-01-12 09:00 | 2023-01-12 13:12 | 2 | 4:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23011200033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2023-01-12 | 504 | keep | 0 | Jan | 2023 | 0.00034327 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-01-12 09:05 | 2023-01-12 12:58 | 15 | 3:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M23011200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2023-01-12 | 3495 | keep | 0 | Jan | 2023 | 0.0023804 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-12 09:05 | 2023-01-12 09:39 | 10 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR PARA REEMPLAZO DE CONEXIONES SECUNDARIAS | A23011200005 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-01-12 | 340 | keep | 0 | Jan | 2023 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-12 09:15 | 2023-01-12 09:18 | 1879 | 0:03 | T | ANIMAL | DISPARO INTERRUPTOR SE CERRO POR CONTROL LLEVA EL 3006-05 | C23011200038 | New_Event | Animals | Include | Include | Wildlife | 3 | 2023-01-12 | 5637 | keep | 0 | Jan | 2023 | 0.0038393 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-01-12 09:15 | 2023-01-12 09:18 | 3005 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR SE CERRO POR CONTROL CARGA X 3006-02 | C23011200038 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-12 | 9015 | keep | 0 | Jan | 2023 | 0.0061401 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2023-01-12 09:18 | 2023-01-12 11:12 | 20 | 1:54 | P | ANIMAL | 1X80 EN C/L CRUCE POR AVE | C23011200068 | 1st_after_momentary | Animals | Include | Include | Wildlife | 114 | 2023-01-12 | 2280 | keep | 0 | Jan | 2023 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-12 09:31 | 2023-01-12 09:33 | 2617 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO X CONTROL | B23011200038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-12 | 5234 | keep | 0 | Jan | 2023 | 0.0035649 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
CANOVANAS | 2023-01-12 09:44 | 2023-01-12 10:47 | 12 | 1:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R23011200014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2023-01-12 | 756 | keep | 0 | Jan | 2023 | 0.00051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-12 09:52 | 2023-01-12 12:54 | 20 | 3:02 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S23011200118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2023-01-12 | 3640 | keep | 0 | Jan | 2023 | 0.0024792 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-01-12 09:57 | 2023-01-12 13:32 | 2 | 3:35 | P | ANIMAL | 1 X 8 EN XMR AVE CRUZO LINEAS | P23011200032 | New_Event | Animals | Include | Include | Wildlife | 215 | 2023-01-12 | 430 | keep | 0 | Jan | 2023 | 0.00029287 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-01-12 10:02 | 2023-01-12 21:30 | 25 | 11:28 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO POSTE | A23011200082 | New_Event | Primary Pole Failure | Include | Include | Equipment | 688 | 2023-01-12 | 17200 | keep | 0 | Jan | 2023 | 0.011715 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-01-12 10:11 | 2023-01-12 14:34 | 128 | 4:23 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23011200067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2023-01-12 | 33664 | keep | 0 | Jan | 2023 | 0.022928 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
BARRANQUITAS | 2023-01-12 10:36 | 2023-01-12 18:01 | 112 | 7:25 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA TOTAL PARA LEVANTAR CONDUCTOR PRIMARIO DEL SUELO | C23011200071 | New_Event | Primary Wire Break | Include | Include | Equipment | 445 | 2023-01-12 | 49840 | keep | 0 | Jan | 2023 | 0.033946 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
BARRANQUITAS | 2023-01-12 11:00 | 2023-01-12 14:09 | 6 | 3:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23011200081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 189 | 2023-01-12 | 1134 | keep | 0 | Jan | 2023 | 0.00077236 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-01-12 11:05 | 2023-01-12 13:18 | 1 | 2:13 | P | ANIMAL | 1 X 15 EN MONTURA TRIFASICA AVE | P23011200052 | New_Event | Animals | Include | Include | Wildlife | 133 | 2023-01-12 | 133 | keep | 0 | Jan | 2023 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-12 11:31 | 2023-01-12 12:58 | 18 | 1:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO TRANSFORMADOR REEMPLAZO CAJA PRIMARIA Y SE REPARARON CONEXIONES SECUNDARIAS | R23011200029 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2023-01-12 | 1566 | keep | 0 | Jan | 2023 | 0.0010666 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-01-12 11:55 | 2023-01-12 13:50 | 74 | 1:55 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL HACIENDO CONTACTO CON LAS LINEAS | S23011200183 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 115 | 2023-01-12 | 8510 | keep | 0 | Jan | 2023 | 0.0057961 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2023-01-12 11:57 | 2023-01-12 15:02 | 25 | 3:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | S23011200186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-01-12 | 4625 | keep | 0 | Jan | 2023 | 0.0031501 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-01-12 12:14 | 2023-01-12 12:15 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23011200037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 3699 | keep | 0 | Jan | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
GUAYAMA | 2023-01-12 12:14 | 2023-01-12 16:14 | 1 | 4:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | P23011200071 | New_Event | Primary Wire Break | Include | Include | Equipment | 240 | 2023-01-12 | 240 | keep | 0 | Jan | 2023 | 0.00016346 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-12 12:17 | 2023-01-12 14:39 | 25 | 2:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S23011200194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-01-12 | 3550 | keep | 0 | Jan | 2023 | 0.0024179 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-01-12 12:23 | 2023-01-12 13:33 | 80 | 1:10 | P | DESGANCHE | 1 X 65 EN C/L SE RETIRO RAMA DE LA LINEA | C23011200093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-01-12 | 5600 | keep | 0 | Jan | 2023 | 0.0038141 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-12 12:30 | 2023-01-12 13:45 | 10 | 1:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIR TRANSFORMADOR PARA FIJAR AISLADOR A LINEA | S23011200189 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 75 | 2023-01-12 | 750 | keep | 0 | Jan | 2023 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-12 12:31 | 2023-01-12 12:44 | 1 | 0:13 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO CAUSA | R23011200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2023-01-12 | 13 | keep | 0 | Jan | 2023 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-01-12 12:39 | 2023-01-12 16:00 | 1352 | 3:21 | S | PROTECCION DEFECTUOSA | SE REMPLAZO RELAY DE PROTECCION DE AMPERAJE DE LA PORTATIL DISPARABA CUANDO SE ENTRABA CARGA POR MALA COORDINACION ENTRE PROTECCION DEL INTERRUPTOR Y PROTECCION DE PORTATIL | P23011200076 | New_Event | Protection Miscoordination | Include | Include | Other | 201 | 2023-01-12 | 271752 | keep | 0 | Jan | 2023 | 0.18509 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2023-01-12 12:39 | 2023-01-12 16:00 | 3973 | 3:21 | S | PROTECCION DEFECTUOSA | SE REMPLAZO RELAY DE PROTECCION DE AMPERAJE DE LA PORTATIL DISPARABA CUANDO SE ENTRABA CARGA POR MALA COORDINACION ENTRE PROTECCION DEL INTERRUPTOR Y PROTECCION DE PORTATIL | P23011200076 | New_Event | Protection Miscoordination | Include | Include | Other | 201 | 2023-01-12 | 798573 | keep | 0 | Jan | 2023 | 0.5439 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2023-01-12 12:39 | 2023-01-12 16:00 | 2484 | 3:21 | S | PROTECCION DEFECTUOSA | SE REMPLAZO RELAY DE PROTECCION DE AMPERAJE DE LA PORTATIL DISPARABA CUANDO SE ENTRABA CARGA POR MALA COORDINACION ENTRE PROTECCION DEL INTERRUPTOR Y PROTECCION DE PORTATIL | P23011200076 | New_Event | Protection Miscoordination | Include | Include | Other | 201 | 2023-01-12 | 499284 | keep | 0 | Jan | 2023 | 0.34006 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
BAYAMON | 2023-01-12 12:44 | 2023-01-12 12:45 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2301120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 2234 | keep | 0 | Jan | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
VEGA BAJA | 2023-01-12 12:46 | 2023-01-12 13:50 | 50 | 1:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23011200118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-01-12 | 3200 | keep | 0 | Jan | 2023 | 0.0021795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-01-12 13:04 | 2023-01-12 16:25 | 50 | 3:21 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23011200124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2023-01-12 | 10050 | keep | 0 | Jan | 2023 | 0.006845 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-01-12 13:04 | 2023-01-12 18:19 | 9 | 5:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIAS | C23011200103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 315 | 2023-01-12 | 2835 | keep | 0 | Jan | 2023 | 0.0019309 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-01-12 13:11 | 2023-01-12 15:18 | 74 | 2:07 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23011200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-01-12 | 9398 | keep | 0 | Jan | 2023 | 0.0064009 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
MAYAGÃœEZ | 2023-01-12 13:15 | 2023-01-12 15:30 | 12 | 2:15 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR Y SE REMPLAZO CONECTORES Y PEDESTAL | M23011200056 | New_Event |  |  |  |  | 135 | 2023-01-12 | 1620 | keep | 0 | Jan | 2023 | 0.0011034 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-12 13:26 | 2023-01-12 15:14 | 19 | 1:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S23011200218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2023-01-12 | 2052 | keep | 0 | Jan | 2023 | 0.0013976 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2023-01-12 13:51 | 2023-01-12 14:37 | 14 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | C23011200109 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2023-01-12 | 644 | keep | 0 | Jan | 2023 | 0.00043863 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-01-12 14:04 | 2023-01-12 14:44 | 11 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PROVISIONAL AEREO PARA LEVANTAR CONDUCTOR PRIMARIO | S23011200229 | New_Event | Primary Wire Break | Include | Include | Equipment | 40 | 2023-01-12 | 440 | keep | 0 | Jan | 2023 | 0.00029968 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
GUAYAMA | 2023-01-12 14:10 | 2023-01-12 17:38 | 60 | 3:28 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L MAQUINA CRUZO LINEAS | P23011200111 | New_Event | Damage From Public | Include | Include | Public | 208 | 2023-01-12 | 12480 | keep | 0 | Jan | 2023 | 0.0085001 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-01-12 14:29 | 2023-01-12 17:54 | 1 | 3:25 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23011200240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-01-12 | 205 | keep | 0 | Jan | 2023 | 0.00013962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-12 14:34 | 2023-01-13 15:20 | 3 | 24:46 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN C/L SE REEMPLAZO XMR DE 15KVA X 37.5 | C23011200117 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1486 | 2023-01-12 | 4458 | keep | 0 | Jan | 2023 | 0.0030363 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-01-12 14:35 | 2023-01-12 15:10 | 10 | 0:35 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REALIZO DESGANCHE SECUNDARIO | S23011200241 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 35 | 2023-01-12 | 350 | keep | 0 | Jan | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-12 14:36 | 2023-01-12 16:22 | 92 | 1:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23011200074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2023-01-12 | 9752 | keep | 0 | Jan | 2023 | 0.006642 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
PONCE | 2023-01-12 14:37 | 2023-01-12 14:38 | 1078 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P23011200124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 1078 | keep | 0 | Jan | 2023 | 0.00073422 | 0.00073422 | Momentary | FALSE | FALSE | Not_TMED_Event | 1078
MAYAGÃœEZ | 2023-01-12 14:37 | 2023-01-12 17:50 | 8 | 3:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23011200073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2023-01-12 | 1544 | keep | 0 | Jan | 2023 | 0.0010516 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-12 14:41 | 2023-01-12 15:54 | 11 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23011200074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-01-12 | 803 | keep | 0 | Jan | 2023 | 0.00054692 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-01-12 14:58 | 2023-01-12 17:27 | 1 | 2:29 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C23011200122 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-01-12 | 149 | keep | 0 | Jan | 2023 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-01-12 15:01 | 2023-01-12 18:00 | 4 | 2:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CONECTOR EN BAJANTE SECUNDARIO | M23011200076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 179 | 2023-01-12 | 716 | keep | 0 | Jan | 2023 | 0.00048766 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-01-12 15:25 | 2023-01-12 16:16 | 5 | 0:51 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P23011200139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2023-01-12 | 255 | keep | 0 | Jan | 2023 | 0.00017368 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-01-12 15:35 | 2023-01-12 16:40 | 500 | 1:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23011200089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2023-01-12 | 32500 | keep | 0 | Jan | 2023 | 0.022136 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2023-01-12 15:51 | 2023-01-12 17:26 | 137 | 1:35 | P | CONDUCTOR ARRIADO O CRUZADO | SE INSTALO ESPACEADORES 1 X 80 EN CORTE DE LINEA | S23011200254 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 95 | 2023-01-12 | 13015 | keep | 0 | Jan | 2023 | 0.0088645 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
CAGUAS | 2023-01-12 16:08 | 2023-01-12 17:42 | 8 | 1:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA SOTERRADA | C23011200132 | New_Event | Secondary Wire Break | Include | Include | Equipment | 94 | 2023-01-12 | 752 | keep | 0 | Jan | 2023 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-12 16:10 | 2023-01-12 17:58 | 71 | 1:48 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | B23011200085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2023-01-12 | 7668 | keep | 0 | Jan | 2023 | 0.0052226 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
MAYAGÃœEZ | 2023-01-12 16:10 | 2023-01-12 20:26 | 125 | 4:16 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 65 EN CORTE DE LINEA SE SECCIONALIZO DOS POSTES PRIMARIOS PARTIDOS HAY EVENTO POSTERIOR M23011200142 PARA TRABAJAR LA AVERIA | M23011200108 | New_Event | Primary Pole Failure | Include | Include | Equipment | 256 | 2023-01-12 | 32000 | keep | 0 | Jan | 2023 | 0.021795 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-01-12 16:13 | 2023-01-12 19:08 | 152 | 2:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER 1 X 50 EN C/L 1X 40 PROVISIONAL 1 X 30 EN XMR | S23011200264 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2023-01-12 | 26600 | keep | 0 | Jan | 2023 | 0.018117 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
SAN JUAN | 2023-01-12 16:22 | 2023-01-12 21:58 | 13 | 5:36 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | S23011200269 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 336 | 2023-01-12 | 4368 | keep | 0 | Jan | 2023 | 0.002975 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-01-12 16:32 | 2023-01-12 18:10 | 15 | 1:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR REPARAR SECUNDARIA | B23011200089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 98 | 2023-01-12 | 1470 | keep | 0 | Jan | 2023 | 0.0010012 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-01-12 16:40 | 2023-01-12 20:47 | 2 | 4:07 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23011200136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2023-01-12 | 494 | keep | 0 | Jan | 2023 | 0.00033646 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-01-12 16:53 | 2023-01-12 18:50 | 60 | 1:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA LLUVIA Y VIENTO | M23011200127 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 117 | 2023-01-12 | 7020 | keep | 0 | Jan | 2023 | 0.0047813 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-01-12 17:04 | 2023-01-12 17:05 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR EN SERVICIO | C2301120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 918 | keep | 0 | Jan | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-01-12 17:05 | 2023-01-12 18:30 | 100 | 1:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23011200141 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 85 | 2023-01-12 | 8500 | keep | 0 | Jan | 2023 | 0.0057893 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-12 17:35 | 2023-01-12 18:16 | 12 | 0:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR REPARAR SECUNDARIA | B23011200093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 41 | 2023-01-12 | 492 | keep | 0 | Jan | 2023 | 0.0003351 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-01-12 17:40 | 2023-01-12 20:23 | 22 | 2:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23011200146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2023-01-12 | 3586 | keep | 0 | Jan | 2023 | 0.0024424 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-01-12 18:01 | 2023-01-12 19:05 | 15 | 1:04 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA REPARAR Y LEVANTAR CONDUCTOR PRIMARIO | S23011200313 | New_Event | Primary Wire Break | Include | Include | Equipment | 64 | 2023-01-12 | 960 | keep | 0 | Jan | 2023 | 0.00065385 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-12 18:40 | 2023-01-12 20:07 | 94 | 1:27 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | S23011200307 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2023-01-12 | 8178 | keep | 0 | Jan | 2023 | 0.00557 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
YAUCO | 2023-01-12 18:44 | 2023-01-12 18:45 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23011200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-12 | 179 | keep | 0 | Jan | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
GUAYAMA | 2023-01-12 18:49 | 2023-01-12 20:25 | 40 | 1:36 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23011200212 | New_Event | Animals | Include | Include | Wildlife | 96 | 2023-01-12 | 3840 | keep | 0 | Jan | 2023 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-12 18:52 | 2023-01-12 20:24 | 10 | 1:32 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23011200102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2023-01-12 | 920 | keep | 0 | Jan | 2023 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-12 18:53 | 2023-01-12 19:57 | 261 | 1:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L MAL TIEMPO LLUVIA | B23011200103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 64 | 2023-01-12 | 16704 | keep | 0 | Jan | 2023 | 0.011377 | 0.00017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 261
BAYAMON | 2023-01-12 18:54 | 2023-01-12 23:06 | 2 | 4:12 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B23011200104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2023-01-12 | 504 | keep | 0 | Jan | 2023 | 0.00034327 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-01-12 19:01 | 2023-01-12 20:08 | 50 | 1:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S23011200312 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2023-01-12 | 3350 | keep | 0 | Jan | 2023 | 0.0022817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-01-12 19:01 | 2023-01-13 06:58 | 12 | 11:57 | P | ANIMAL | 1X15 EN XMR CRUCE POR AVE | C23011200161 | New_Event | Animals | Include | Include | Wildlife | 717 | 2023-01-12 | 8604 | keep | 0 | Jan | 2023 | 0.0058601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-01-12 19:08 | 2023-01-13 07:03 | 6 | 11:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P23011200213 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 715 | 2023-01-12 | 4290 | keep | 0 | Jan | 2023 | 0.0029219 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-01-12 19:16 | 2023-01-13 02:23 | 20 | 7:07 | P | DESGANCHE | 2 X 50 EN C/ SE DESGANCHO | B23011200117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 427 | 2023-01-12 | 8540 | keep | 0 | Jan | 2023 | 0.0058166 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-12 19:25 | 2023-01-12 19:27 | 761 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR LLEVA EL 1421-01 SE CERRO POR CONTROL | S23011200316 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-12 | 1522 | keep | 0 | Jan | 2023 | 0.0010366 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2023-01-12 19:25 | 2023-01-12 19:27 | 1498 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1310-04 LLEVA EL 1421-01 SE CERRO POR CONTROL | S23011200316 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-12 | 2996 | keep | 0 | Jan | 2023 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
VEGA BAJA | 2023-01-12 19:26 | 2023-01-12 19:27 | 3387 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE CERRO POR CONTROL | B2301120000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-12 | 3387 | keep | 0 | Jan | 2023 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2023-01-12 19:27 | 2023-01-12 19:37 | 1117 | 0:10 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO BY-230112-01 | B23011200130 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 10 | 2023-01-12 | 11170 | keep | 0 | Jan | 2023 | 0.0076078 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
FAJARDO | 2023-01-12 19:32 | 2023-01-12 20:00 | 1 | 0:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO LA CAJA NO FUNDIO | R23011200074 | New_Event | Cutout Failure | Include | Include | Equipment | 28 | 2023-01-12 | 28 | keep | 0 | Jan | 2023 | 1.9071e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-12 19:37 | 2023-01-12 19:38 | 3387 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE CERRO POR CONTROL | B2301120000X | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-12 | 3387 | keep | 0 | Jan | 2023 | 0.0023069 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-12 19:38 | 2023-01-12 21:38 | 1117 | 2:00 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO BY-230112-01 | B23011200130 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 120 | 2023-01-12 | 134040 | keep | 0 | Jan | 2023 | 0.091294 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
SAN JUAN | 2023-01-12 20:06 | 2023-01-12 21:20 | 333 | 1:14 | T | CABLE SOTERRADO AVERIADO | DISPARO DE BKR CABLE SOTERRADO DEL RISER DE SALIDA AVERIADO SE TRANSFIRIO LA CARGA AL 1105-02 CON SJ-230112-02 | S23011200319 | New_Event | UG Cable Fault | Include | Include | Equipment | 74 | 2023-01-12 | 24642 | keep | 0 | Jan | 2023 | 0.016784 | 0.0002268 | Sustained | FALSE | FALSE | Not_TMED_Event | 333
CANOVANAS | 2023-01-12 20:27 | 2023-01-12 21:28 | 70 | 1:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | R23011200076 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 61 | 2023-01-12 | 4270 | keep | 0 | Jan | 2023 | 0.0029083 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-01-12 20:33 | 2023-01-13 17:30 | 100 | 20:57 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 65 EN CORTE DE LINEA REMPLAZO DE POSTE PRIMARIO | M23011200142 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1257 | 2023-01-12 | 125700 | keep | 0 | Jan | 2023 | 0.085614 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-12 20:37 | 2023-01-13 01:49 | 5 | 5:12 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | B23011200207 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 312 | 2023-01-12 | 1560 | keep | 0 | Jan | 2023 | 0.0010625 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-12 20:42 | 2023-01-12 21:51 | 9 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR REPARAR SECUNDARIA | B23011200211 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2023-01-12 | 621 | keep | 0 | Jan | 2023 | 0.00042296 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2023-01-12 21:19 | 2023-01-12 22:55 | 40 | 1:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23011200186 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2023-01-12 | 3840 | keep | 0 | Jan | 2023 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-01-12 21:35 | 2023-01-12 23:40 | 8 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23011200188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2023-01-12 | 1000 | keep | 0 | Jan | 2023 | 0.0006811 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-01-12 21:38 | 2023-01-12 22:11 | 3387 | 0:33 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO CERCA DE LA SALIDA DEL ALIMENTADOR BY-230112-01 | B23011200130 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 33 | 2023-01-12 | 111771 | keep | 0 | Jan | 2023 | 0.076127 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-12 22:04 | 2023-01-13 09:55 | 50 | 11:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L SE REMPLAZO CAJA PRIMARIA | R23011200080 | New_Event | Cutout Failure | Include | Include | Equipment | 711 | 2023-01-12 | 35550 | keep | 0 | Jan | 2023 | 0.024213 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-01-12 22:16 | 2023-01-13 01:02 | 50 | 2:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23011200147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 166 | 2023-01-12 | 8300 | keep | 0 | Jan | 2023 | 0.0056531 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-01-12 22:29 | 2023-01-13 11:15 | 1 | 12:46 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | R23011200084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 766 | 2023-01-12 | 766 | keep | 0 | Jan | 2023 | 0.00052172 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-01-13 00:24 | 2023-01-13 00:25 | 1902 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE PALMER TC A FAJARDO TC VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 1902 | keep | 0 | Jan | 2023 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2023-01-13 00:24 | 2023-01-13 00:25 | 970 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE PALMER TC A FAJARDO TC VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 970 | keep | 0 | Jan | 2023 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2023-01-13 00:24 | 2023-01-13 00:25 | 3003 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE PALMER TC A FAJARDO TC VEHICULO IMPACTO Y PARTIO POSTE | R23011300005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 3003 | keep | 0 | Jan | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2023-01-13 00:24 | 2023-01-13 00:25 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE PALMER TC A FAJARDO TC VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 2343 | keep | 0 | Jan | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2023-01-13 00:24 | 2023-01-13 00:25 | 1830 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE PALMER TC A FAJARDO TC VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 1830 | keep | 0 | Jan | 2023 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-01-13 00:24 | 2023-01-13 00:25 | 710 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE PALMER TC A FAJARDO TC VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 710 | keep | 0 | Jan | 2023 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-01-13 00:24 | 2023-01-13 00:25 | 1197 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE PALMER TC A FAJARDO TC VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 1197 | keep | 0 | Jan | 2023 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
CANOVANAS | 2023-01-13 00:24 | 2023-01-13 00:26 | 3012 | 0:02 | T | LINEA DE TRANSMISION 38KV | DISPARO INTERRUPTOR EN OPERACION DE LA LINEA 3100 DE PALMER TC A FAJARDO TC VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R2301130000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-13 | 6024 | keep | 0 | Jan | 2023 | 0.0041029 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
FAJARDO | 2023-01-13 00:46 | 2023-01-13 02:14 | 1902 | 1:28 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO SE SECCIONALIZO STOP POLE IMPACTADO POR VEHICULO VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300011 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2023-01-13 | 167376 | keep | 0 | Jan | 2023 | 0.114 | 0.0012954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2023-01-13 00:46 | 2023-01-13 02:14 | 970 | 1:28 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO SE SECCIONALIZO STOP POLE IMPACTADO POR VEHICULO VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300011 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2023-01-13 | 85360 | keep | 0 | Jan | 2023 | 0.058138 | 0.00066066 | Sustained | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2023-01-13 00:46 | 2023-01-13 02:14 | 3003 | 1:28 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO SE SECCIONALIZO STOP POLE IMPACTADO POR VEHICULO VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300011 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2023-01-13 | 264264 | keep | 0 | Jan | 2023 | 0.17999 | 0.0020453 | Sustained | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2023-01-13 00:46 | 2023-01-13 02:16 | 2343 | 1:30 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO SE SECCIONALIZO STOP POLE IMPACTADO POR VEHICULO VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300010 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2023-01-13 | 210870 | keep | 0 | Jan | 2023 | 0.14362 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2023-01-13 00:46 | 2023-01-13 02:16 | 1830 | 1:30 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO SE SECCIONALIZO STOP POLE IMPACTADO POR VEHICULO VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300010 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2023-01-13 | 164700 | keep | 0 | Jan | 2023 | 0.11218 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-01-13 00:46 | 2023-01-13 02:16 | 710 | 1:30 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO SE SECCIONALIZO STOP POLE IMPACTADO POR VEHICULO VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300010 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2023-01-13 | 63900 | keep | 0 | Jan | 2023 | 0.043522 | 0.00048358 | Sustained | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-01-13 00:46 | 2023-01-13 02:16 | 1197 | 1:30 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO SE SECCIONALIZO STOP POLE IMPACTADO POR VEHICULO VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300010 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2023-01-13 | 107730 | keep | 0 | Jan | 2023 | 0.073374 | 0.00081527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1197
BAYAMON | 2023-01-13 03:21 | 2023-01-13 03:22 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B23011300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-13 | 1859 | keep | 0 | Jan | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
CANOVANAS | 2023-01-13 03:38 | 2023-01-13 09:36 | 90 | 5:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X40 EN C/L SE REMPLAZO DISCO PRIMARIO | R23011300042 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 358 | 2023-01-13 | 32220 | keep | 0 | Jan | 2023 | 0.021945 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2023-01-13 03:50 | 2023-01-13 03:51 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | C.C.E. ABRIO INTERRUPTOR PARA NORMALIZAR LINEA 3100 VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 2343 | keep | 0 | Jan | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2023-01-13 03:50 | 2023-01-13 03:51 | 1830 | 0:01 | S | LINEA DE TRANSMISION 38KV | C.C.E. ABRIO INTERRUPTOR PARA NORMALIZAR LINEA 3100 VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 1830 | keep | 0 | Jan | 2023 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-01-13 03:50 | 2023-01-13 03:51 | 710 | 0:01 | S | LINEA DE TRANSMISION 38KV | C.C.E. ABRIO INTERRUPTOR PARA NORMALIZAR LINEA 3100 VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 710 | keep | 0 | Jan | 2023 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-01-13 03:50 | 2023-01-13 03:51 | 1197 | 0:01 | S | LINEA DE TRANSMISION 38KV | C.C.E. ABRIO INTERRUPTOR PARA NORMALIZAR LINEA 3100 VEHÃCULO IMPACTO Y PARTIÃ“ POSTE | R23011300043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-13 | 1197 | keep | 0 | Jan | 2023 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
VEGA BAJA | 2023-01-13 04:26 | 2023-01-13 08:34 | 76 | 4:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23011300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 248 | 2023-01-13 | 18848 | keep | 0 | Jan | 2023 | 0.012837 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
MAYAGÃœEZ | 2023-01-13 05:59 | 2023-01-13 09:36 | 1 | 3:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA 1 X 50 EN RISER GRABERA POR LLUVIAS | M23011300003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 217 | 2023-01-13 | 217 | keep | 0 | Jan | 2023 | 0.0001478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-13 06:25 | 2023-01-13 06:26 | 386 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S2301130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-13 | 386 | keep | 0 | Jan | 2023 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
CANOVANAS | 2023-01-13 06:29 | 2023-01-13 09:51 | 6 | 3:22 | P | ANIMAL | 1X65 EN C/L, 1X50 EN C/L Y 1X40 EN OTRO C/L CRUCE DE AVE | R23011300046 | New_Event | Animals | Include | Include | Wildlife | 202 | 2023-01-13 | 1212 | keep | 0 | Jan | 2023 | 0.00082549 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-01-13 07:08 | 2023-01-13 09:59 | 10 | 2:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X8 EN XMR PORTAFUSIBLE QUEMADO | R23011300049 | New_Event | Cutout Failure | Include | Include | Equipment | 171 | 2023-01-13 | 1710 | keep | 0 | Jan | 2023 | 0.0011647 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-13 08:05 | 2023-01-13 09:35 | 8 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REGULO VOLTAJE Y REEMPLAZO DE CONECCIONES SECUNDARIAS | P23011300021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-01-13 | 720 | keep | 0 | Jan | 2023 | 0.00049039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-01-13 08:11 | 2023-01-13 10:54 | 60 | 2:43 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23011300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-01-13 | 9780 | keep | 0 | Jan | 2023 | 0.0066611 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-01-13 08:23 | 2023-01-13 10:36 | 1 | 2:13 | P | NO SE REPORTO CAUSA | 2 X 50 EN MONTURA TRIFASICA NO SE ENCONTRO CAUSA | P23011300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2023-01-13 | 133 | keep | 0 | Jan | 2023 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-13 08:26 | 2023-01-13 11:44 | 12 | 3:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 10 EN TRANSFORMADOR SE REPARO CONEXIONES SECUNDARIAS | A23011300005 | New_Event | Secondary Wire Break | Include | Include | Equipment | 198 | 2023-01-13 | 2376 | keep | 0 | Jan | 2023 | 0.0016183 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-01-13 08:27 | 2023-01-13 09:00 | 90 | 0:33 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C23011300012 | New_Event | Animals | Include | Include | Wildlife | 33 | 2023-01-13 | 2970 | keep | 0 | Jan | 2023 | 0.0020229 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2023-01-13 08:30 | 2023-01-13 10:16 | 2 | 1:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C23011300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2023-01-13 | 212 | keep | 0 | Jan | 2023 | 0.00014439 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-01-13 08:38 | 2023-01-13 12:00 | 100 | 3:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIAS | M23011300013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 202 | 2023-01-13 | 20200 | keep | 0 | Jan | 2023 | 0.013758 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-01-13 08:51 | 2023-01-13 10:31 | 80 | 1:40 | P | ANIMAL | 1 X 100 Y 1 X 80 EN C/L CRUCE POR AVE | R23011300057 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-01-13 | 8000 | keep | 0 | Jan | 2023 | 0.0054488 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-13 08:52 | 2023-01-13 09:36 | 12 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011300021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-01-13 | 528 | keep | 0 | Jan | 2023 | 0.00035962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-13 09:13 | 2023-01-13 10:20 | 50 | 1:07 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S23011300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2023-01-13 | 3350 | keep | 0 | Jan | 2023 | 0.0022817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-01-13 09:14 | 2023-01-13 11:23 | 9 | 2:09 | P | PROBLEMA DEL CLIENTE | 1 X 8 EN TRANSFORMADOR POR BASE CONTADOR AVERIADA | M23011300023 | New_Event | Customer-Related Interruption | Include | Include | Public | 129 | 2023-01-13 | 1161 | keep | 0 | Jan | 2023 | 0.00079075 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-01-13 09:37 | 2023-01-13 12:36 | 12 | 2:59 | P | ANIMAL | 1X20 EN C/L CRUCE DE AVE | C23011300031 | New_Event | Animals | Include | Include | Wildlife | 179 | 2023-01-13 | 2148 | keep | 0 | Jan | 2023 | 0.001463 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-01-13 09:37 | 2023-01-13 13:30 | 18 | 3:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | M23011300028 | New_Event | Cutout Failure | Include | Include | Equipment | 233 | 2023-01-13 | 4194 | keep | 0 | Jan | 2023 | 0.0028565 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-01-13 09:45 | 2023-01-13 10:15 | 2 | 0:30 | P | CAUSAS EXTERNAS | SE ABRE MONTURA DE TRANSFORMADOR PARA REMOVER CONTADOR AVERIADO | M23011200137 | New_Event | Damage From Public | Include | Include | Public | 30 | 2023-01-13 | 60 | keep | 0 | Jan | 2023 | 4.0866e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-01-13 09:45 | 2023-01-13 15:10 | 100 | 5:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2023-01-13 | 32500 | keep | 0 | Jan | 2023 | 0.022136 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-13 09:51 | 2023-01-13 11:17 | 1 | 1:26 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S23011300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2023-01-13 | 86 | keep | 0 | Jan | 2023 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-13 09:54 | 2023-01-14 12:14 | 15 | 26:20 | P | PROBLEMA DEL CLIENTE | 1 X 40 EN RISER 1 X 25 EN SUBEST. PRIVADA PARARRAYO DE CLIENTE AVERIADO | S23011300109 | New_Event | Customer-Related Interruption | Include | Include | Public | 1580 | 2023-01-13 | 23700 | keep | 0 | Jan | 2023 | 0.016142 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-01-13 09:55 | 2023-01-13 11:18 | 1 | 1:23 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMA | A23011300016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-01-13 | 83 | keep | 0 | Jan | 2023 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-01-13 10:09 | 2023-01-13 12:24 | 72 | 2:15 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P23011300033 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-01-13 | 9720 | keep | 0 | Jan | 2023 | 0.0066202 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2023-01-13 10:15 | 2023-01-13 10:45 | 6 | 0:30 | P | SECUNDARIA/OTROS | SE REEMPLAZO PEDESTAL REDONDO CON TODO Y BARRAS | B23011300031 | New_Event |  |  |  |  | 30 | 2023-01-13 | 180 | keep | 0 | Jan | 2023 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-01-13 10:19 | 2023-01-13 10:20 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C2301130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-13 | 1702 | keep | 0 | Jan | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CANOVANAS | 2023-01-13 10:31 | 2023-01-13 10:32 | 4188 | 0:01 | T | ANIMAL | RECERRO | R23011300067 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-13 | 4188 | keep | 0 | Jan | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2023-01-13 10:32 | 2023-01-13 14:11 | 80 | 3:39 | P | ANIMAL | 1 X 100 Y 1 X 80 EN C/L CRUCE POR AVE | R23011300057 | 1st_after_momentary | Animals | Include | Include | Wildlife | 219 | 2023-01-13 | 17520 | keep | 0 | Jan | 2023 | 0.011933 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-01-13 10:37 | 2023-01-13 11:28 | 15 | 0:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BARRA EN PEDESTAL | C23011300044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2023-01-13 | 765 | keep | 0 | Jan | 2023 | 0.00052104 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-01-13 10:42 | 2023-01-13 14:05 | 18 | 3:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO DE CAJA PRIMARIA EN CORTE DE LINEA | P23011300037 | New_Event | Cutout Failure | Include | Include | Equipment | 203 | 2023-01-13 | 3654 | keep | 0 | Jan | 2023 | 0.0024887 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2023-01-13 11:13 | 2023-01-13 11:14 | 766 | 0:01 | P | DESGANCHE | RECIERRE 50% DE SU CARGA POR 1909-07 | S2301130000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-13 | 766 | keep | 0 | Jan | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-01-13 11:13 | 2023-01-13 11:14 | 2364 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | S2301130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-13 | 2364 | keep | 0 | Jan | 2023 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2023-01-13 11:14 | 2023-01-13 19:40 | 1 | 8:26 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23011300046 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 506 | 2023-01-13 | 506 | keep | 0 | Jan | 2023 | 0.00034463 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-13 11:14 | 2023-01-13 15:17 | 900 | 4:03 | P | DESGANCHE | 1 X 100 EN C/L SE REPORTA DESGANCHE | S23011300045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-01-13 | 218700 | keep | 0 | Jan | 2023 | 0.14896 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
MAYAGÃœEZ | 2023-01-13 11:24 | 2023-01-13 17:15 | 100 | 5:51 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | M23011300052 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 351 | 2023-01-13 | 35100 | keep | 0 | Jan | 2023 | 0.023906 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-01-13 11:24 | 2023-01-13 14:20 | 50 | 2:56 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23011300036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-01-13 | 8800 | keep | 0 | Jan | 2023 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-01-13 11:32 | 2023-01-13 15:55 | 8 | 4:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BARRAS EN PEDESTAL | B23011300047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 263 | 2023-01-13 | 2104 | keep | 0 | Jan | 2023 | 0.001433 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-13 11:34 | 2023-01-13 13:20 | 10 | 1:46 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | C23011300055 | New_Event | Animals | Include | Include | Wildlife | 106 | 2023-01-13 | 1060 | keep | 0 | Jan | 2023 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-13 11:35 | 2023-01-13 14:36 | 10 | 3:01 | P | NO SE REPORTO CAUSA | 2 X 100 EN RISER Y EN SU-1 2 X 80 | S23011300041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2023-01-13 | 1810 | keep | 0 | Jan | 2023 | 0.0012328 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-13 11:40 | 2023-01-13 12:06 | 16 | 0:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO BARRA DE PEDESTAL | C23011300057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 26 | 2023-01-13 | 416 | keep | 0 | Jan | 2023 | 0.00028334 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
YAUCO | 2023-01-13 11:53 | 2023-01-13 17:28 | 70 | 5:35 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23011300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2023-01-13 | 23450 | keep | 0 | Jan | 2023 | 0.015972 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-01-13 11:57 | 2023-01-13 12:04 | 15 | 0:07 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B23011300053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-01-13 | 105 | keep | 0 | Jan | 2023 | 7.1515e-05 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-13 12:12 | 2023-01-13 12:13 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2301130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-13 | 5809 | keep | 0 | Jan | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
CANOVANAS | 2023-01-13 12:16 | 2023-01-13 12:17 | 4085 | 0:01 | T | DESGANCHE | RECERRO | R23011300076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-13 | 4085 | keep | 0 | Jan | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-01-13 12:17 | 2023-01-14 19:16 | 40 | 30:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S23011300052 | New_Event | Cutout Failure | Include | Include | Equipment | 1859 | 2023-01-13 | 74360 | keep | 0 | Jan | 2023 | 0.050646 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-01-13 12:17 | 2023-01-13 14:36 | 30 | 2:19 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23011300087 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-01-13 | 4170 | keep | 0 | Jan | 2023 | 0.0028402 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-01-13 12:41 | 2023-01-13 15:18 | 10 | 2:37 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE PRIMARIO EN XMR | P23011300063 | New_Event | Primary Wire Break | Include | Include | Equipment | 157 | 2023-01-13 | 1570 | keep | 0 | Jan | 2023 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-13 12:47 | 2023-01-13 14:15 | 1 | 1:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU-6 | B23011300053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2023-01-13 | 88 | keep | 0 | Jan | 2023 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-13 12:56 | 2023-01-13 15:00 | 1 | 2:04 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011300076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-01-13 | 124 | keep | 0 | Jan | 2023 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-01-13 12:57 | 2023-01-13 15:00 | 40 | 2:03 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS | M23011300079 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 123 | 2023-01-13 | 4920 | keep | 0 | Jan | 2023 | 0.003351 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-01-13 12:59 | 2023-01-13 16:15 | 15 | 3:16 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE ELIMINO PARARRAYOS AVERIADO | A23011300056 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 196 | 2023-01-13 | 2940 | keep | 0 | Jan | 2023 | 0.0020024 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-01-13 13:02 | 2023-01-13 13:27 | 1054 | 0:25 | T | DESGANCHE | SE RETIRO RAMAS DE ARBOL SOBRE LINEA | A23011300059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2023-01-13 | 26350 | keep | 0 | Jan | 2023 | 0.017947 | 0.00071787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1054
HUMACAO | 2023-01-13 13:10 | 2023-01-13 14:25 | 123 | 1:15 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23011300073 | New_Event | Animals | Include | Include | Wildlife | 75 | 2023-01-13 | 9225 | keep | 0 | Jan | 2023 | 0.0062831 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
SAN JUAN | 2023-01-13 13:20 | 2023-01-13 14:35 | 10 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S23011300036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-01-13 | 750 | keep | 0 | Jan | 2023 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-13 13:33 | 2023-01-13 14:30 | 100 | 0:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23011300077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2023-01-13 | 5700 | keep | 0 | Jan | 2023 | 0.0038822 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-13 13:48 | 2023-01-13 13:49 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2301130000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-13 | 5809 | keep | 0 | Jan | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
CAGUAS | 2023-01-13 13:58 | 2023-01-13 14:01 | 329 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA EN SERVICIO | C2301130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-13 | 987 | keep | 0 | Jan | 2023 | 0.00067224 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
GUAYAMA | 2023-01-13 14:30 | 2023-01-13 18:23 | 10 | 3:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PRIMARIO PARTIDO Y PUENTE ABIERTO | P23011300078 | New_Event | Primary Wire Break | Include | Include | Equipment | 233 | 2023-01-13 | 2330 | keep | 0 | Jan | 2023 | 0.001587 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-13 14:39 | 2023-01-13 16:52 | 90 | 2:13 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23011300076 | New_Event | Animals | Include | Include | Wildlife | 133 | 2023-01-13 | 11970 | keep | 0 | Jan | 2023 | 0.0081527 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-01-13 14:43 | 2023-01-13 17:28 | 10 | 2:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO Y SE SUBIO SECUNDARIA DEL SUELO | S23011300080 | New_Event | Secondary Wire Break | Include | Include | Equipment | 165 | 2023-01-13 | 1650 | keep | 0 | Jan | 2023 | 0.0011238 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-13 14:43 | 2023-01-13 18:00 | 17 | 3:17 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y REALIZO DESGANCHE SECUNDARIO | S23011300078 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 197 | 2023-01-13 | 3349 | keep | 0 | Jan | 2023 | 0.002281 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-01-13 14:43 | 2023-01-13 18:00 | 40 | 3:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23011300100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-01-13 | 7880 | keep | 0 | Jan | 2023 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-13 14:45 | 2023-01-13 16:13 | 15 | 1:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23011300083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 88 | 2023-01-13 | 1320 | keep | 0 | Jan | 2023 | 0.00089905 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-13 14:58 | 2023-01-13 17:27 | 4 | 2:29 | P | ANIMAL | 1X15 EN XMR CRUCE DE AVE | B23011300072 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-01-13 | 596 | keep | 0 | Jan | 2023 | 0.00040593 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-01-13 15:16 | 2023-01-13 16:13 | 8 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011300075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-01-13 | 456 | keep | 0 | Jan | 2023 | 0.00031058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-13 15:20 | 2023-01-13 16:30 | 1 | 1:10 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23011300087 | New_Event | Animals | Include | Include | Wildlife | 70 | 2023-01-13 | 70 | keep | 0 | Jan | 2023 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-13 15:32 | 2023-01-13 16:43 | 50 | 1:11 | P | ANIMAL | 1 X 50 Y 1 X 80 EN C/L CRUCE X AVE | C23011300086 | New_Event | Animals | Include | Include | Wildlife | 71 | 2023-01-13 | 3550 | keep | 0 | Jan | 2023 | 0.0024179 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-01-13 15:37 | 2023-01-13 15:38 | 3431 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | A23011300090 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-13 | 3431 | keep | 0 | Jan | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2023-01-13 15:38 | 2023-01-13 16:14 | 15 | 0:36 | P | ANIMAL | 2 X 10 EN XMR CRUCE POR AVE | B23011300063 | New_Event | Animals | Include | Include | Wildlife | 36 | 2023-01-13 | 540 | keep | 0 | Jan | 2023 | 0.00036779 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-01-13 15:38 | 2023-01-13 17:05 | 100 | 1:27 | P | ANIMAL | 2 X 100, 1 X 80 EN CORTE DE LINEA DISTINTOS Y 1 X 10 EN TRANSFORMADOR IGUANA CRUZO FASES A TIERRA | A23011300089 | 1st_after_momentary | Animals | Include | Include | Wildlife | 87 | 2023-01-13 | 8700 | keep | 0 | Jan | 2023 | 0.0059255 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-01-13 16:13 | 2023-01-13 18:45 | 60 | 2:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23011300104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-01-13 | 9120 | keep | 0 | Jan | 2023 | 0.0062116 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-01-13 17:00 | 2023-01-13 18:04 | 10 | 1:04 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23011300115 | New_Event | Animals | Include | Include | Wildlife | 64 | 2023-01-13 | 640 | keep | 0 | Jan | 2023 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-13 17:10 | 2023-01-13 18:21 | 8 | 1:11 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | C23011300116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-01-13 | 568 | keep | 0 | Jan | 2023 | 0.00038686 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-13 17:23 | 2023-01-13 19:00 | 5 | 1:37 | P | OTRAS CAUSAS | 1 X 1O EN XMR FUSIBLE SULFATADO | C23011300119 | New_Event | Other Causes | Include | Include | Other | 97 | 2023-01-13 | 485 | keep | 0 | Jan | 2023 | 0.00033033 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-13 17:37 | 2023-01-15 11:00 | 12 | 41:23 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON (3) MACHETES PRIMARIOS (RADIAL) NO FUNDIO | S23011300095 | New_Event | Switch Failure | Include | Include | Equipment | 2483 | 2023-01-13 | 29796 | keep | 0 | Jan | 2023 | 0.020294 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-13 17:53 | 2023-01-13 18:32 | 6 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23011300090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-01-13 | 234 | keep | 0 | Jan | 2023 | 0.00015938 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-01-13 18:28 | 2023-01-13 20:05 | 15 | 1:37 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23011300113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2023-01-13 | 1455 | keep | 0 | Jan | 2023 | 0.00099099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-13 18:42 | 2023-01-13 19:26 | 10 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REEMPLAZO BARA EN PEDESTAL | B23011300087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-01-13 | 440 | keep | 0 | Jan | 2023 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-01-13 18:45 | 2023-01-13 22:15 | 7 | 3:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS PARTIDAS | A23011300084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 210 | 2023-01-13 | 1470 | keep | 0 | Jan | 2023 | 0.0010012 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2023-01-13 19:06 | 2023-01-14 08:30 | 9 | 13:24 | P | CAUSAS EXTERNAS | MAQUINA IMPACTO POSTE Y CRUZO LINEAS | P23011300100 | New_Event | Damage From Public | Include | Include | Public | 804 | 2023-01-13 | 7236 | keep | 0 | Jan | 2023 | 0.0049284 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-01-13 19:48 | 2023-01-13 20:55 | 15 | 1:07 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | R23011300104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2023-01-13 | 1005 | keep | 0 | Jan | 2023 | 0.0006845 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-01-13 21:30 | 2023-01-13 21:31 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23011300107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-13 | 4085 | keep | 0 | Jan | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-01-13 21:38 | 2023-01-13 22:28 | 300 | 0:50 | P | DESGANCHE | 2 X 140 EN C/L DESGANCHE | R23011300108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2023-01-13 | 15000 | keep | 0 | Jan | 2023 | 0.010216 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2023-01-13 22:03 | 2023-01-14 10:55 | 7 | 12:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRASFORMADOR SE REEMPLAZO DE CAJA PRIMARIA QUEMADA | M23011300140 | New_Event | Cutout Failure | Include | Include | Equipment | 772 | 2023-01-13 | 5404 | keep | 0 | Jan | 2023 | 0.0036806 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-01-13 22:44 | 2023-01-13 22:46 | 1902 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23011300118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-13 | 3804 | keep | 0 | Jan | 2023 | 0.0025909 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2023-01-13 22:44 | 2023-01-13 22:46 | 970 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23011300118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-13 | 1940 | keep | 0 | Jan | 2023 | 0.0013213 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2023-01-13 22:44 | 2023-01-13 22:46 | 3003 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23011300118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-13 | 6006 | keep | 0 | Jan | 2023 | 0.0040907 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2023-01-13 22:44 | 2023-01-13 22:46 | 2343 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23011300119 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-13 | 4686 | keep | 0 | Jan | 2023 | 0.0031916 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2023-01-13 22:44 | 2023-01-13 22:46 | 1830 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23011300119 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-13 | 3660 | keep | 0 | Jan | 2023 | 0.0024928 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-01-13 22:44 | 2023-01-13 22:46 | 710 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23011300119 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-13 | 1420 | keep | 0 | Jan | 2023 | 0.00096716 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-01-13 22:44 | 2023-01-13 22:46 | 1197 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23011300119 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-13 | 2394 | keep | 0 | Jan | 2023 | 0.0016305 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
ARECIBO | 2023-01-13 23:33 | 2023-01-14 08:50 | 6 | 9:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | A23011300125 | New_Event | Cutout Failure | Include | Include | Equipment | 557 | 2023-01-13 | 3342 | keep | 0 | Jan | 2023 | 0.0022762 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-14 00:58 | 2023-01-14 00:59 | 386 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | S2301140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-14 | 386 | keep | 0 | Jan | 2023 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
BAYAMON | 2023-01-14 04:47 | 2023-01-14 04:48 | 4622 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B23011400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-14 | 4622 | keep | 0 | Jan | 2023 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
SAN JUAN | 2023-01-14 05:48 | 2023-01-14 16:21 | 30 | 10:33 | P | CABLE SOTERRADO AVERIADO | 1 X 50 Y 1 X 40 EN C/L SE REPARO PROVISIONAL AEREO Y SE ENCONTRO TRAMO SOTERRADO AVERIADO T-6 @ T-7 | S23011400004 | New_Event | UG Cable Fault | Include | Include | Equipment | 633 | 2023-01-14 | 18990 | keep | 0 | Jan | 2023 | 0.012934 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-14 06:44 | 2023-01-14 10:11 | 50 | 3:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X25 EN RISER SE REMPLAZO CAJA PRIMARIA | S23011400005 | New_Event | Cutout Failure | Include | Include | Equipment | 207 | 2023-01-14 | 10350 | keep | 0 | Jan | 2023 | 0.0070493 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-14 07:46 | 2023-01-14 07:47 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23011400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-14 | 5630 | keep | 0 | Jan | 2023 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2023-01-14 08:14 | 2023-01-14 12:30 | 57 | 4:16 | P | ANIMAL | 1 X 50 EN RISER CRUCE POR AVE | C23011400008 | New_Event | Animals | Include | Include | Wildlife | 256 | 2023-01-14 | 14592 | keep | 0 | Jan | 2023 | 0.0099385 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
HUMACAO | 2023-01-14 08:15 | 2023-01-14 11:17 | 10 | 3:02 | P | ANIMAL | 1 X 80 C/L CRUCE X AVE | C23011400009 | New_Event | Animals | Include | Include | Wildlife | 182 | 2023-01-14 | 1820 | keep | 0 | Jan | 2023 | 0.0012396 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-14 08:21 | 2023-01-14 13:12 | 40 | 4:51 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23011400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2023-01-14 | 11640 | keep | 0 | Jan | 2023 | 0.007928 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-01-14 08:23 | 2023-01-14 09:42 | 3420 | 1:19 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR EN LA SUBESTACION | C23011400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2023-01-14 | 270180 | keep | 0 | Jan | 2023 | 0.18402 | 0.0023293 | Sustained | FALSE | FALSE | Not_TMED_Event | 3420
YAUCO | 2023-01-14 08:25 | 2023-01-14 10:24 | 50 | 1:59 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23011400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-01-14 | 5950 | keep | 0 | Jan | 2023 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-01-14 08:41 | 2023-01-14 08:42 | 4369 | 0:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 0800 20% X 3604-06 | C23011400026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-14 | 4369 | keep | 0 | Jan | 2023 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
BARRANQUITAS | 2023-01-14 08:41 | 2023-01-14 08:42 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 0800 | C23011400024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-14 | 1565 | keep | 0 | Jan | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-01-14 08:41 | 2023-01-14 08:42 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 0800 | C23011400024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-14 | 976 | keep | 0 | Jan | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-01-14 08:41 | 2023-01-14 08:42 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 0800 | C23011400025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-14 | 315 | keep | 0 | Jan | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-01-14 08:41 | 2023-01-14 08:42 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 0800 | C23011400025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-14 | 870 | keep | 0 | Jan | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-01-14 08:41 | 2023-01-14 08:42 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 0800 LLEVA 20% DEL 3010-01 | C23011400026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-14 | 2906 | keep | 0 | Jan | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-01-14 08:41 | 2023-01-14 08:42 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 0800 | C23011400026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-14 | 2343 | keep | 0 | Jan | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
HUMACAO | 2023-01-14 08:47 | 2023-01-14 09:16 | 9 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | C23011400030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-01-14 | 261 | keep | 0 | Jan | 2023 | 0.00017777 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
GUAYAMA | 2023-01-14 08:47 | 2023-01-14 11:31 | 4 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23011400014 | New_Event | Primary Wire Break | Include | Include | Equipment | 164 | 2023-01-14 | 656 | keep | 0 | Jan | 2023 | 0.0004468 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-01-14 08:52 | 2023-01-14 10:24 | 5 | 1:32 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFOMAR POR FUSIBLE SULFATADO | M23011400008 | New_Event | Other Causes | Include | Include | Other | 92 | 2023-01-14 | 460 | keep | 0 | Jan | 2023 | 0.0003133 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-14 09:48 | 2023-01-14 15:28 | 10 | 5:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA EN PEDESTAL | S23011400020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 340 | 2023-01-14 | 3400 | keep | 0 | Jan | 2023 | 0.0023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-14 09:52 | 2023-01-14 13:36 | 1977 | 3:44 | P | ALIMENTADOR AMARRADO | 40% DE SU CARGA POR 1206-04 SE REPARO PARARRAYOS EN LA ALTA DEL TRANSFORMADOR DE LA 1206-00 (ENCANTADA) MEDIANTE G.O.I. SJ-230114-01 | S23011400022 | New_Event | Feeder Load Transferred | Include | Include | Other | 224 | 2023-01-14 | 442848 | keep | 0 | Jan | 2023 | 0.30162 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2023-01-14 09:52 | 2023-01-14 14:41 | 338 | 4:49 | S | LINEA DE TRANSMISION 115KV | SE REALIZO LIMPIEZA Y SE REPARO AISLACION EN AUXILIAR A DEL 0060. TAMBIEN SE REPARO PARARRAYOS EN LA ALTA DEL TRANSFORMADOR MEDIANTE G.O.I. SJ-230114-01 | S23011400022 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 289 | 2023-01-14 | 97682 | keep | 0 | Jan | 2023 | 0.066531 | 0.00023021 | Sustained | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2023-01-14 09:52 | 2023-01-14 14:41 | 733 | 4:49 | S | LINEA DE TRANSMISION 115KV | SE REALIZO LIMPIEZA Y SE REPARO AISLACION EN AUXILIAR A DEL 0060. TAMBIEN SE REPARO PARARRAYOS EN LA ALTA DEL TRANSFORMADOR MEDIANTE G.O.I. SJ-230114-01 | S23011400022 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 289 | 2023-01-14 | 211837 | keep | 0 | Jan | 2023 | 0.14428 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2023-01-14 09:52 | 2023-01-14 12:16 | 4133 | 2:24 | S | LINEA DE TRANSMISION 115KV | SE REALIZO LIMPIEZA Y SE REPARO AISLACION EN AUXILIAR A DEL 0060. TAMBIEN SE REPARO PARARRAYOS EN LA ALTA DEL TRANSFORMADOR MEDIANTE G.O.I. SJ-230114-01 - EN SERVICIO 50% DE SU CARGA | S23011400022 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 144 | 2023-01-14 | 595152 | keep | 0 | Jan | 2023 | 0.40536 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2023-01-14 09:52 | 2023-01-14 13:36 | 1799 | 3:44 | S | LINEA DE TRANSMISION 115KV | SE REALIZO LIMPIEZA Y SE REPARO AISLACION EN AUXILIAR A DEL 0060. TAMBIEN SE REPARO PARARRAYOS EN LA ALTA DEL TRANSFORMADOR MEDIANTE G.O.I. SJ-230114-01 - LLEVA 40% DEL 1204-04 | S23011400022 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 224 | 2023-01-14 | 402976 | keep | 0 | Jan | 2023 | 0.27447 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2023-01-14 09:55 | 2023-01-15 09:16 | 20 | 23:21 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S23011400023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1401 | 2023-01-14 | 28020 | keep | 0 | Jan | 2023 | 0.019084 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-01-14 10:03 | 2023-01-14 15:15 | 70 | 5:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23011400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2023-01-14 | 21840 | keep | 0 | Jan | 2023 | 0.014875 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2023-01-14 10:25 | 2023-01-14 18:30 | 1 | 8:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 25 KVA 2400 VOLT | P23011400027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 485 | 2023-01-14 | 485 | keep | 0 | Jan | 2023 | 0.00033033 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-01-14 11:05 | 2023-01-14 12:24 | 10 | 1:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REEMPLAZAN CONEXIONES | M23011400006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 79 | 2023-01-14 | 790 | keep | 0 | Jan | 2023 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-01-14 11:14 | 2023-01-14 14:58 | 50 | 3:44 | P | DESGANCHE | 2 X 50 EN C/L | C23011400072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-01-14 | 11200 | keep | 0 | Jan | 2023 | 0.0076283 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-14 11:16 | 2023-01-14 15:35 | 66 | 4:19 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN C/L SE LEVANTO LINEA PRIMARIA | B23011400026 | New_Event | Primary Wire Break | Include | Include | Equipment | 259 | 2023-01-14 | 17094 | keep | 0 | Jan | 2023 | 0.011643 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
CANOVANAS | 2023-01-14 11:20 | 2023-01-14 11:43 | 8 | 0:23 | P | PROBLEMA DEL CLIENTE | SE ABRIO TRANSFORMADOR SE DEJO TOMA DE CLIENTE FUERA | R23011400004 | New_Event | Customer-Related Interruption | Include | Include | Public | 23 | 2023-01-14 | 184 | keep | 0 | Jan | 2023 | 0.00012532 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-01-14 11:30 | 2023-01-14 13:00 | 6 | 1:30 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO SECUNDARIA | A23011400039 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 90 | 2023-01-14 | 540 | keep | 0 | Jan | 2023 | 0.00036779 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-01-14 11:33 | 2023-01-14 12:21 | 6 | 0:48 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R23011400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2023-01-14 | 288 | keep | 0 | Jan | 2023 | 0.00019616 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-01-14 11:33 | 2023-01-14 13:25 | 1 | 1:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO DE TRANSFORMADORES PARA REPARAR SECUNDARIA | C23011400036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 112 | 2023-01-14 | 112 | keep | 0 | Jan | 2023 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-14 11:35 | 2023-01-14 12:59 | 26 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011400030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2023-01-14 | 2184 | keep | 0 | Jan | 2023 | 0.0014875 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
PONCE | 2023-01-14 11:37 | 2023-01-14 13:55 | 60 | 2:18 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P23011400033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-01-14 | 8280 | keep | 0 | Jan | 2023 | 0.0056395 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-01-14 11:40 | 2023-01-14 13:45 | 7 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011400031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2023-01-14 | 875 | keep | 0 | Jan | 2023 | 0.00059596 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-01-14 11:46 | 2023-01-14 14:20 | 16 | 2:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23011400072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2023-01-14 | 2464 | keep | 0 | Jan | 2023 | 0.0016782 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-01-14 11:58 | 2023-01-14 12:07 | 8679 | 0:09 | P | ALIMENTADOR AMARRADO | 85% DE SU CARGA POR 1206-03, OPERACIONES PROVOCARON DISPARO DEL 1620-02 MIENTRAS EL 1204-05 ESTUVO TEMPORERAMENTE TRANSFERIDO AL 1620-02 PARA TRABAJAR EN PARARRAYOS DE LA ALTA DEL XMR DE LA 1206-00 | S23011400214 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-01-14 | 78111 | keep | 0 | Jan | 2023 | 0.053201 | 0.0059112 | Sustained | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-01-14 11:58 | 2023-01-14 12:07 | 3718 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO MIENTRAS SE REALIZABAN TRANSFERENCIAS REPARANDO PARARRAYOS EN LA ALTA DEL XMR DE LA 1206-00 LLEVA 85% DE LA CARGA DEL 1204-05 | S23011400214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-01-14 | 33462 | keep | 0 | Jan | 2023 | 0.022791 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
CAGUAS | 2023-01-14 12:05 | 2023-01-14 12:06 | 1307 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR | C2301140000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-14 | 1307 | keep | 0 | Jan | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2023-01-14 12:06 | 2023-01-14 14:40 | 207 | 2:34 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23011400080 | 1st_after_momentary | Animals | Include | Include | Wildlife | 154 | 2023-01-14 | 31878 | keep | 0 | Jan | 2023 | 0.021712 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2023-01-14 12:16 | 2023-01-14 17:00 | 2066 | 4:44 | P | LINEA DE TRANSMISION 115KV | SE REPARO PARARRAYOS EN LA ALTA DEL TRANSFORMADOR, TAMBIEN SE SECCIONALIZO PARA REPARAR PUENTE ABIERTO EN EL TRONCAL MEDIANTE G.O.I. SJ-230114-01 - EN SERVICIO 60% DE SU CARGA TOTAL Y EL 85% QUE LLEVA DEL 1204-05 | S23011400022 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 284 | 2023-01-14 | 586744 | keep | 0 | Jan | 2023 | 0.39963 | 0.0014071 | Sustained | FALSE | FALSE | Not_TMED_Event | 2066
GUAYAMA | 2023-01-14 12:19 | 2023-01-14 13:44 | 50 | 1:25 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23011400042 | New_Event | Animals | Include | Include | Wildlife | 85 | 2023-01-14 | 4250 | keep | 0 | Jan | 2023 | 0.0028947 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-14 12:45 | 2023-01-14 12:50 | 8679 | 0:05 | P | ALIMENTADOR AMARRADO | 85% DE SU CARGA POR 1206-03, OPERACIONES PROVOCARON DISPARO DEL 1620-02 MIENTRAS EL 1204-05 ESTUVO TEMPORERAMENTE TRANSFERIDO AL 1620-02 PARA TRABAJAR EN PARARRAYOS DE LA ALTA DEL XMR DE LA 1206-00 | S23011400273 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 5 | 2023-01-14 | 43395 | keep | 0 | Jan | 2023 | 0.029556 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-14 12:45 | 2023-01-14 12:50 | 3718 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO MIENTRAS SE REALIZABAN TRANSFERENCIAS REPARANDO PARARRAYOS EN LA ALTA DEL XMR DE LA 1206-00 LLEVA 85% DE LA CARGA DEL 1204-05 | S23011400273 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-01-14 | 18590 | keep | 0 | Jan | 2023 | 0.012662 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-14 12:47 | 2023-01-14 16:51 | 40 | 4:04 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23011400039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2023-01-14 | 9760 | keep | 0 | Jan | 2023 | 0.0066475 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-01-14 13:18 | 2023-01-14 15:42 | 15 | 2:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23011400048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 144 | 2023-01-14 | 2160 | keep | 0 | Jan | 2023 | 0.0014712 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-14 13:31 | 2023-01-14 14:56 | 81 | 1:25 | T | CAUSAS EXTERNAS | SE ESTABLECIO GOI BY-230114-01 PARA TRABAJOS DE RETIRAR CANASTO PRIVADO SOBRE LA LINEA | B23011400042 | New_Event | Damage From Public | Include | Include | Public | 85 | 2023-01-14 | 6885 | keep | 0 | Jan | 2023 | 0.0046893 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
GUAYAMA | 2023-01-14 13:56 | 2023-01-14 15:03 | 40 | 1:07 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23011400052 | New_Event | Animals | Include | Include | Wildlife | 67 | 2023-01-14 | 2680 | keep | 0 | Jan | 2023 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-01-14 14:00 | 2023-01-14 14:40 | 10 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO MONTURA DE TRANSFORMADORES PARA REPARAR LINEA SECUNDARIA | M23011400020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-01-14 | 400 | keep | 0 | Jan | 2023 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-14 14:04 | 2023-01-14 16:57 | 776 | 2:53 | T | CAUSAS EXTERNAS | SE ESTABLECIO GOI BY-230114-01 PARA TRABAJOS DE RETIRAR CANASTO PRIVADO SOBRE LA LINEA | B23011400042 | New_Event | Damage From Public | Include | Include | Public | 173 | 2023-01-14 | 134248 | keep | 0 | Jan | 2023 | 0.091436 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
SAN JUAN | 2023-01-14 14:15 | 2023-01-14 21:31 | 40 | 7:16 | P | DESGANCHE | 2 X 65 EN C/L | S23011400360 | New_Event | Vegetation Contact | Include | Include | Vegetation | 436 | 2023-01-14 | 17440 | keep | 0 | Jan | 2023 | 0.011878 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-14 14:23 | 2023-01-14 15:45 | 12 | 1:22 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REPARO BUSHING SECUNDARIO | B23011400048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 82 | 2023-01-14 | 984 | keep | 0 | Jan | 2023 | 0.0006702 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-01-14 14:56 | 2023-01-14 18:36 | 500 | 3:40 | P | DESGANCHE | 2 X 200 Y 1 X 140 EN CORTES DE LINEA DISTINTOS SE REALIZO DESGANCHE | M23011400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-01-14 | 110000 | keep | 0 | Jan | 2023 | 0.07492 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2023-01-14 14:58 | 2023-01-14 16:48 | 30 | 1:50 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23011400056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-01-14 | 3300 | keep | 0 | Jan | 2023 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-01-14 15:00 | 2023-01-14 18:00 | 55 | 3:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A23011400055 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 180 | 2023-01-14 | 9900 | keep | 0 | Jan | 2023 | 0.0067428 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CANOVANAS | 2023-01-14 15:28 | 2023-01-14 17:33 | 40 | 2:05 | P | DESGANCHE | 1 X 40 EN C/L | R23011400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-01-14 | 5000 | keep | 0 | Jan | 2023 | 0.0034055 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-01-14 15:28 | 2023-01-14 17:30 | 75 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTE VIENTO | M23011400044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2023-01-14 | 9150 | keep | 0 | Jan | 2023 | 0.006232 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-01-14 15:30 | 2023-01-14 16:31 | 62 | 1:01 | P | ERROR HUMANO | PERSONAL DE DESGANCHE DEJO CAER ARBOL SOBRE LA LINEA | S23011400445 | New_Event | Human Error | Include | Include | Other | 61 | 2023-01-14 | 3782 | keep | 0 | Jan | 2023 | 0.0025759 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
HUMACAO | 2023-01-14 15:45 | 2023-01-14 20:25 | 310 | 4:40 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PARTIDO IMPACTADO POR CAMION | C23011400103 | New_Event | Damage From Public | Include | Include | Public | 280 | 2023-01-14 | 86800 | keep | 0 | Jan | 2023 | 0.059119 | 0.00021114 | Sustained | FALSE | FALSE | Not_TMED_Event | 310
BAYAMON | 2023-01-14 15:53 | 2023-01-14 18:36 | 60 | 2:43 | P | NO SE REPORTO CAUSA | 1 X 50 SU Y 1 X 15 EN C/L | B23011400057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2023-01-14 | 9780 | keep | 0 | Jan | 2023 | 0.0066611 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-01-14 16:10 | 2023-01-14 17:52 | 16 | 1:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L Y 1 X 15 EN XMR | R23011400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2023-01-14 | 1632 | keep | 0 | Jan | 2023 | 0.0011115 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2023-01-14 16:15 | 2023-01-14 17:00 | 5 | 0:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CAJA A BUSHING PRIMARIO DE TRANSFORMADOR | A23011400042 | New_Event | Primary Wire Break | Include | Include | Equipment | 45 | 2023-01-14 | 225 | keep | 0 | Jan | 2023 | 0.00015325 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-14 16:21 | 2023-01-15 15:09 | 9 | 22:48 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DEL T-6 @ T-7 MEDIANTE G.O.I. SJ-221115-01 | S23011400004 | New_Event | UG Cable Fault | Include | Include | Equipment | 1368 | 2023-01-14 | 12312 | keep | 0 | Jan | 2023 | 0.0083856 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2023-01-14 16:41 | 2023-01-14 17:33 | 16 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M23011400059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-01-14 | 832 | keep | 0 | Jan | 2023 | 0.00056667 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-01-14 16:46 | 2023-01-14 16:47 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-14 | 1307 | keep | 0 | Jan | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2023-01-14 16:47 | 2023-01-14 18:44 | 100 | 1:57 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 100 EN C/L | C23011400116 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 117 | 2023-01-14 | 11700 | keep | 0 | Jan | 2023 | 0.0079688 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-14 17:00 | 2023-01-14 19:04 | 1653 | 2:04 | P | LINEA DE TRANSMISION 115KV | SE REALIZO LIMPIEZA Y SE REPARO AISLACION EN AUXILIAR A DEL 0060. TAMBIEN SE REPARO PARARRAYOS EN LA ALTA DEL TRANSFORMADOR, SE REPARO PUENTE ABIERTO EN EL TRONCAL MEDIANTE G.O.I. SJ-230114-01 - EN SERVICIO EL 40% QUE FALTABA POR ENTRAR | S23011400022 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 124 | 2023-01-14 | 204972 | keep | 0 | Jan | 2023 | 0.13961 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-14 17:50 | 2023-01-14 17:51 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23011400581 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-14 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-01-14 18:11 | 2023-01-15 12:23 | 10 | 18:12 | P | NO SE REPORTO CAUSA | 1X30 EN BANCO DE XMRS | S23011400598 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1092 | 2023-01-14 | 10920 | keep | 0 | Jan | 2023 | 0.0074376 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-14 18:14 | 2023-01-15 00:27 | 59 | 6:13 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L SE CERRO PUENTE ABIERTO | S23011400603 | New_Event | Primary Wire Break | Include | Include | Equipment | 373 | 2023-01-14 | 22007 | keep | 0 | Jan | 2023 | 0.014989 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BAYAMON | 2023-01-14 18:18 | 2023-01-14 18:43 | 3 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23011400602 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-14 | 75 | keep | 0 | Jan | 2023 | 5.1082e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-01-14 18:29 | 2023-01-14 22:06 | 60 | 3:37 | P | ANIMAL | 1 X 100 EN C/L AVE | C23011400142 | New_Event | Animals | Include | Include | Wildlife | 217 | 2023-01-14 | 13020 | keep | 0 | Jan | 2023 | 0.0088679 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-01-14 18:45 | 2023-01-14 18:50 | 8 | 0:05 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR PARAR REPARAR BAJANTE PRIMARIO DE CAJA A BUSHING PRIMARIO | A23011400061 | New_Event | Primary Wire Break | Include | Include | Equipment | 5 | 2023-01-14 | 40 | keep | 0 | Jan | 2023 | 2.7244e-05 | 5.4488e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-14 18:58 | 2023-01-14 20:39 | 50 | 1:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B23011400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2023-01-14 | 5050 | keep | 0 | Jan | 2023 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-01-14 20:42 | 2023-01-14 22:05 | 60 | 1:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23011400071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2023-01-14 | 4980 | keep | 0 | Jan | 2023 | 0.0033919 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-01-14 20:51 | 2023-01-14 23:10 | 14 | 2:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | R23011400025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 139 | 2023-01-14 | 1946 | keep | 0 | Jan | 2023 | 0.0013254 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
GUAYAMA | 2023-01-14 21:01 | 2023-01-15 08:48 | 1 | 11:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN RISER Y SE CAMBIO CAJA PRIMARIA | P23011400075 | New_Event | Cutout Failure | Include | Include | Equipment | 707 | 2023-01-14 | 707 | keep | 0 | Jan | 2023 | 0.00048153 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-01-14 21:12 | 2023-01-15 03:37 | 140 | 6:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR RAMA SOBRE LINEA | M23011400081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2023-01-14 | 53900 | keep | 0 | Jan | 2023 | 0.036711 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
SAN JUAN | 2023-01-14 21:54 | 2023-01-15 11:21 | 100 | 13:27 | P | NO SE REPORTO CAUSA | 1X65 EN AEREO PROVISIONAL | S23011400765 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 807 | 2023-01-14 | 80700 | keep | 0 | Jan | 2023 | 0.054964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-14 22:00 | 2023-01-15 00:15 | 77 | 2:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23011400086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2023-01-14 | 10395 | keep | 0 | Jan | 2023 | 0.00708 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
SAN JUAN | 2023-01-14 22:03 | 2023-01-15 13:37 | 15 | 15:34 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23011400766 | New_Event | Vegetation Contact | Include | Include | Vegetation | 934 | 2023-01-14 | 14010 | keep | 0 | Jan | 2023 | 0.0095421 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-14 22:12 | 2023-01-15 00:26 | 96 | 2:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO PORTAFUSIBLES | B23011400087 | New_Event | Cutout Failure | Include | Include | Equipment | 134 | 2023-01-14 | 12864 | keep | 0 | Jan | 2023 | 0.0087616 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
CANOVANAS | 2023-01-14 23:10 | 2023-01-14 23:11 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2301140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-14 | 1026 | keep | 0 | Jan | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
MAYAGÃœEZ | 2023-01-14 23:12 | 2023-01-15 09:20 | 40 | 10:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23011400093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 608 | 2023-01-14 | 24320 | keep | 0 | Jan | 2023 | 0.016564 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-01-14 23:15 | 2023-01-14 23:16 | 16 | 0:01 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | R23011400023 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-14 | 16 | keep | 0 | Jan | 2023 | 1.0898e-05 | 1.0898e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-01-15 01:32 | 2023-01-15 11:38 | 52 | 10:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C23011500001 | New_Event | Cutout Failure | Include | Include | Equipment | 606 | 2023-01-15 | 31512 | keep | 0 | Jan | 2023 | 0.021463 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
MAYAGÃœEZ | 2023-01-15 02:01 | 2023-01-15 08:55 | 30 | 6:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 414 | 2023-01-15 | 12420 | keep | 0 | Jan | 2023 | 0.0084592 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-15 02:19 | 2023-01-15 02:20 | 1834 | 0:01 | T | DESGANCHE | RECIERRE | B2301150000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-15 | 1834 | keep | 0 | Jan | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2023-01-15 02:20 | 2023-01-15 15:54 | 40 | 13:34 | P | DESGANCHE | 2 X 40 DESGANCHE | B23011500019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 814 | 2023-01-15 | 32560 | keep | 0 | Jan | 2023 | 0.022176 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-01-15 07:06 | 2023-01-15 07:07 | 584 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE. LINEA DISPARA EN EVENTO PT AVERIADO BARRA 1 38KV JOBOS TC. | P23011500011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 584 | keep | 0 | Jan | 2023 | 0.00039776 | 0.00039776 | Momentary | FALSE | FALSE | Not_TMED_Event | 584
GUAYAMA | 2023-01-15 07:06 | 2023-01-15 07:07 | 1658 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE. LINEA DISPARA EN EVENTO PT AVERIADO BARRA 1 38KV JOBOS TC. | P23011500011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 1658 | keep | 0 | Jan | 2023 | 0.0011293 | 0.0011293 | Momentary | FALSE | FALSE | Not_TMED_Event | 1658
GUAYAMA | 2023-01-15 07:06 | 2023-01-15 07:07 | 630 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE. LINEA DISPARA EN EVENTO PT AVERIADO BARRA 1 38KV JOBOS TC. | P23011500011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 630 | keep | 0 | Jan | 2023 | 0.00042909 | 0.00042909 | Momentary | FALSE | FALSE | Not_TMED_Event | 630
GUAYAMA | 2023-01-15 07:06 | 2023-01-15 07:07 | 978 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE. LINEA DISPARA EN EVENTO PT AVERIADO BARRA 1 38KV JOBOS TC. | P23011500011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 978 | keep | 0 | Jan | 2023 | 0.00066611 | 0.00066611 | Momentary | FALSE | FALSE | Not_TMED_Event | 978
GUAYAMA | 2023-01-15 07:06 | 2023-01-15 07:07 | 1730 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE. LINEA DISPARA EN EVENTO PT AVERIADO BARRA 1 38KV JOBOS TC. | P23011500011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 1730 | keep | 0 | Jan | 2023 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
CANOVANAS | 2023-01-15 07:30 | 2023-01-15 08:30 | 10 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23011500003 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-01-15 | 600 | keep | 0 | Jan | 2023 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-15 07:36 | 2023-01-15 12:41 | 90 | 5:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L SE REMPLAZO CAJA PRIMARIA | S23011500016 | New_Event | Cutout Failure | Include | Include | Equipment | 305 | 2023-01-15 | 27450 | keep | 0 | Jan | 2023 | 0.018696 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2023-01-15 07:41 | 2023-01-15 07:42 | 874 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA 20% DE LA CARGA POR EL 3604-07 | C23011500007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 874 | keep | 0 | Jan | 2023 | 0.00059528 | 0.00059528 | Momentary | FALSE | FALSE | Not_TMED_Event | 874
BARRANQUITAS | 2023-01-15 07:41 | 2023-01-15 07:42 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 1565 | keep | 0 | Jan | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-01-15 07:41 | 2023-01-15 07:42 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 976 | keep | 0 | Jan | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-01-15 07:41 | 2023-01-15 07:42 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 315 | keep | 0 | Jan | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-01-15 07:41 | 2023-01-15 07:42 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 870 | keep | 0 | Jan | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-01-15 07:41 | 2023-01-15 07:42 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 2906 | keep | 0 | Jan | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-01-15 07:41 | 2023-01-15 07:42 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA LLEVA 20% DEL 3010-01 | C23011500007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 2343 | keep | 0 | Jan | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
CANOVANAS | 2023-01-15 07:55 | 2023-01-15 11:20 | 16 | 3:25 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR DE 75KVA X 75KVA AVERIADO | R23011500002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 205 | 2023-01-15 | 3280 | keep | 0 | Jan | 2023 | 0.002234 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-01-15 07:55 | 2023-01-15 09:10 | 690 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE CERRO PUENTE DE LINEA A LINEA | C23011500188 | New_Event | Primary Wire Break | Include | Include | Equipment | 75 | 2023-01-15 | 51750 | keep | 0 | Jan | 2023 | 0.035247 | 0.00046996 | Sustained | FALSE | FALSE | Not_TMED_Event | 690
CAGUAS | 2023-01-15 08:15 | 2023-01-15 08:16 | 874 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA 20% DE LA CARGA POR EL 3604-07 | C23011500012 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 874 | keep | 0 | Jan | 2023 | 0.00059528 | 0.00059528 | Momentary | FALSE | FALSE | Not_TMED_Event | 874
BARRANQUITAS | 2023-01-15 08:15 | 2023-01-15 08:16 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500010 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 1565 | keep | 0 | Jan | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-01-15 08:15 | 2023-01-15 08:16 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500010 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 976 | keep | 0 | Jan | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-01-15 08:15 | 2023-01-15 08:16 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500011 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 315 | keep | 0 | Jan | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-01-15 08:15 | 2023-01-15 08:16 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500011 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 870 | keep | 0 | Jan | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-01-15 08:15 | 2023-01-15 08:16 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23011500012 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 2906 | keep | 0 | Jan | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-01-15 08:15 | 2023-01-15 08:16 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA LLEVA 20% DE LA CARGA DEL 3010-01 | C23011500012 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-15 | 2343 | keep | 0 | Jan | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
HUMACAO | 2023-01-15 08:25 | 2023-01-15 11:55 | 8 | 3:30 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO BAMBUA DE CAJA PRIMARIA DEL TRANSFORMADDOR | C23011500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-01-15 | 1680 | keep | 0 | Jan | 2023 | 0.0011442 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-01-15 08:25 | 2023-01-15 09:37 | 154 | 1:12 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C23011500015 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-01-15 | 11088 | keep | 0 | Jan | 2023 | 0.007552 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
HUMACAO | 2023-01-15 08:35 | 2023-01-15 10:04 | 186 | 1:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C23011500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-01-15 | 16554 | keep | 0 | Jan | 2023 | 0.011275 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
YAUCO | 2023-01-15 08:37 | 2023-01-15 08:50 | 8 | 0:13 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR POR IGUANA | P23011500016 | New_Event | Animals | Include | Include | Wildlife | 13 | 2023-01-15 | 104 | keep | 0 | Jan | 2023 | 7.0834e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-01-15 09:37 | 2023-01-15 09:38 | 1307 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C2301150000X | Additional_clients | Animals | Include | Include | Wildlife | 1 | 2023-01-15 | 1307 | keep | 0 | Jan | 2023 | 0.00089019 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-15 09:38 | 2023-01-15 10:22 | 108 | 0:44 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR CHANGO | C23011500039 | 1st_after_momentary | Animals | Include | Include | Wildlife | 44 | 2023-01-15 | 4752 | keep | 0 | Jan | 2023 | 0.0032366 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
CAGUAS | 2023-01-15 09:38 | 2023-01-15 10:06 | 154 | 0:28 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C23011500015 | New_Event | Animals | Include | Include | Wildlife | 28 | 2023-01-15 | 4312 | keep | 0 | Jan | 2023 | 0.0029369 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
CANOVANAS | 2023-01-15 09:39 | 2023-01-15 12:33 | 6 | 2:54 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 25 KVA X 25 KVA | R23011500009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 174 | 2023-01-15 | 1044 | keep | 0 | Jan | 2023 | 0.00071106 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-01-15 10:00 | 2023-01-15 10:50 | 9 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR REPARAR SECUNDARIA | B23011500007 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-01-15 | 450 | keep | 0 | Jan | 2023 | 0.00030649 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-01-15 10:34 | 2023-01-15 11:38 | 45 | 1:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C23011500046 | New_Event | Cutout Failure | Include | Include | Equipment | 64 | 2023-01-15 | 2880 | keep | 0 | Jan | 2023 | 0.0019616 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-01-15 10:47 | 2023-01-15 10:48 | 1681 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE ESTA TRANSFERIDO AL 1303-05, PERO EL LLEVA LA CARGA DEL 1303-01 Y DEL 1346-06 SE CERRO POR CONTROL | S23011500043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 1681 | keep | 0 | Jan | 2023 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-01-15 10:47 | 2023-01-15 10:48 | 1598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-04 QUE ESTA TRANSFERIDO AL 1303-05, PERO EL LLEVA LA CARGA DEL 1303-01 Y DEL 1346-06 SE CERRO POR CONTROL | S23011500043 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-15 | 1598 | keep | 0 | Jan | 2023 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2023-01-15 11:32 | 2023-01-16 19:20 | 1 | 31:48 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO Y SE CERRO LOS PUENTES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A23011500041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1908 | 2023-01-15 | 1908 | keep | 0 | Jan | 2023 | 0.0012995 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-15 11:44 | 2023-01-15 11:45 | 325 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 325 | keep | 0 | Jan | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CAGUAS | 2023-01-15 12:10 | 2023-01-15 13:47 | 110 | 1:37 | P | ANIMAL | 1 X 100 Y 1 X 65 EN CORTE DE LINEA SE RETIRO IGUANA DE LA LINEA | C23011500057 | New_Event | Animals | Include | Include | Wildlife | 97 | 2023-01-15 | 10670 | keep | 0 | Jan | 2023 | 0.0072673 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
BARRANQUITAS | 2023-01-15 12:10 | 2023-01-15 13:08 | 13 | 0:58 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO AVERIADO | C23011500050 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 58 | 2023-01-15 | 754 | keep | 0 | Jan | 2023 | 0.00051355 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2023-01-15 12:26 | 2023-01-15 15:50 | 31 | 3:24 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23011500059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-01-15 | 6324 | keep | 0 | Jan | 2023 | 0.0043072 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
GUAYAMA | 2023-01-15 12:36 | 2023-01-15 15:50 | 25 | 3:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO AISLACION DE PRIMARIA 1 X 80 | P23011500025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 194 | 2023-01-15 | 4850 | keep | 0 | Jan | 2023 | 0.0033033 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-01-15 12:52 | 2023-01-15 16:30 | 40 | 3:38 | P | ANIMAL | 1 X 40 EN RISER LAGARTO CRUZO FASES | M23011500023 | New_Event | Animals | Include | Include | Wildlife | 218 | 2023-01-15 | 8720 | keep | 0 | Jan | 2023 | 0.0059392 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-15 13:03 | 2023-01-15 14:18 | 10 | 1:15 | P | ARBOL SOBRE LINEA | 2 X 15 EN XMR SE RETIRO ARBOL DE LA LINEA | S23011500059 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 75 | 2023-01-15 | 750 | keep | 0 | Jan | 2023 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-01-15 13:06 | 2023-01-15 13:24 | 30 | 0:18 | P | CONDUCTOR ROTO O ABIERTO | SE LLEVO BAJANTE PRMARIO A CAJA DE CORTE DE LINEA | P23011500027 | New_Event | Primary Wire Break | Include | Include | Equipment | 18 | 2023-01-15 | 540 | keep | 0 | Jan | 2023 | 0.00036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-01-15 13:09 | 2023-01-15 14:42 | 30 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23011500062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-01-15 | 2790 | keep | 0 | Jan | 2023 | 0.0019003 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-15 13:18 | 2023-01-15 14:46 | 26 | 1:28 | P | DESGANCHE | SE ABRIO C/L SE DESGANCHO | S23011500062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-01-15 | 2288 | keep | 0 | Jan | 2023 | 0.0015583 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
ARECIBO | 2023-01-15 13:25 | 2023-01-15 19:20 | 60 | 5:55 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE SECCIONALIZO AREA QUE NECESITA DESGANCHE MASIVO | A23011500029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2023-01-15 | 21300 | keep | 0 | Jan | 2023 | 0.014507 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-01-15 13:44 | 2023-01-15 14:28 | 50 | 0:44 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | R23011500024 | New_Event | Animals | Include | Include | Wildlife | 44 | 2023-01-15 | 2200 | keep | 0 | Jan | 2023 | 0.0014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-01-15 14:11 | 2023-01-15 17:50 | 80 | 3:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 2 X 40 EN CORTES DE LINEAS DISTINTOS MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23011500033 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 219 | 2023-01-15 | 17520 | keep | 0 | Jan | 2023 | 0.011933 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-01-15 14:12 | 2023-01-15 16:20 | 40 | 2:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23011500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2023-01-15 | 5120 | keep | 0 | Jan | 2023 | 0.0034872 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-01-15 14:13 | 2023-01-15 22:05 | 224 | 7:52 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO Y CERRO PUENTE | C23011500072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 472 | 2023-01-15 | 105728 | keep | 0 | Jan | 2023 | 0.072011 | 0.00015257 | Sustained | FALSE | FALSE | Not_TMED_Event | 224
YAUCO | 2023-01-15 14:20 | 2023-01-15 16:39 | 14 | 2:19 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN TRANSFORMADOR ALAMBRE SECUNDARIO PEGADO A ESTRUCTURA | P23011500030 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 139 | 2023-01-15 | 1946 | keep | 0 | Jan | 2023 | 0.0013254 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
FAJARDO | 2023-01-15 14:29 | 2023-01-15 16:07 | 4 | 1:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER PORTAFUSIBLE QUEMADO | R23011500025 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2023-01-15 | 392 | keep | 0 | Jan | 2023 | 0.00026699 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-01-15 14:35 | 2023-01-15 15:48 | 5 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO BAJANTE SECUNDARIO (NO FUNDIO) | S23011500068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-01-15 | 365 | keep | 0 | Jan | 2023 | 0.0002486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-15 14:46 | 2023-01-15 14:47 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA CARGA 1720-08 | S2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 2402 | keep | 0 | Jan | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2023-01-15 14:46 | 2023-01-15 14:47 | 1 | 0:01 | T | ALIMENTADOR AMARRADO | BKR 1709-02 RECERRO LLEVA 1720-08 | S2301150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-15 | 1 | keep | 0 | Jan | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-15 14:46 | 2023-01-15 16:46 | 20 | 2:00 | P | ANIMAL | 1 X 8 EN XMR CRUCE POR AVE | R23011500026 | New_Event | Animals | Include | Include | Wildlife | 120 | 2023-01-15 | 2400 | keep | 0 | Jan | 2023 | 0.0016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2023-01-15 15:00 | 2023-01-15 15:18 | 30 | 0:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO C/L EN AERIO PROVISIONAL PARA REPARAR BARRA SECUNDARIA EN EL T-18 | R23011500027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 18 | 2023-01-15 | 540 | keep | 0 | Jan | 2023 | 0.00036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-01-15 15:00 | 2023-01-15 16:44 | 103 | 1:44 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L 1 X 50 EN C/L 1X 10 EN XMR MAL TIEMPO RAYOS | C23011500081 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 104 | 2023-01-15 | 10712 | keep | 0 | Jan | 2023 | 0.0072959 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
CANOVANAS | 2023-01-15 15:09 | 2023-01-15 16:23 | 3 | 1:14 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | R23011500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2023-01-15 | 222 | keep | 0 | Jan | 2023 | 0.0001512 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-01-15 15:57 | 2023-01-15 15:58 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 2234 | keep | 0 | Jan | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-01-15 16:05 | 2023-01-15 22:00 | 48 | 5:55 | P | TERMINACION SOTERRADA AVERIADA | 1 X 100 EN SU-2 | B23011500027 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 355 | 2023-01-15 | 17040 | keep | 0 | Jan | 2023 | 0.011606 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
VEGA BAJA | 2023-01-15 16:19 | 2023-01-15 18:00 | 130 | 1:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | A23011500022 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 101 | 2023-01-15 | 13130 | keep | 0 | Jan | 2023 | 0.0089428 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
GUAYAMA | 2023-01-15 16:27 | 2023-01-15 19:42 | 250 | 3:15 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO EN TRONCAL | P23011500036 | New_Event | Primary Wire Break | Include | Include | Equipment | 195 | 2023-01-15 | 48750 | keep | 0 | Jan | 2023 | 0.033203 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-01-15 16:35 | 2023-01-16 08:37 | 26 | 16:02 | P | NO SE REPORTO CAUSA | 2X40 EN RISER | S23011500079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 962 | 2023-01-15 | 25012 | keep | 0 | Jan | 2023 | 0.017036 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
VEGA BAJA | 2023-01-15 16:36 | 2023-01-15 16:44 | 4702 | 0:08 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO X CONTROL | B23011500035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2023-01-15 | 37616 | keep | 0 | Jan | 2023 | 0.02562 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-01-15 16:37 | 2023-01-15 16:38 | 2468 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B23011500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 2468 | keep | 0 | Jan | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2023-01-15 16:38 | 2023-01-15 21:00 | 25 | 4:22 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | B23011500067 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 262 | 2023-01-15 | 6550 | keep | 0 | Jan | 2023 | 0.0044612 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-15 16:43 | 2023-01-15 16:44 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-01-15 16:44 | 2023-01-15 16:47 | 533 | 0:03 | T | DESGANCHE | DISPARO DE BKR SE CERRO X CONTROL | S2301150000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-01-15 | 1599 | keep | 0 | Jan | 2023 | 0.0010891 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
BAYAMON | 2023-01-15 16:46 | 2023-01-15 16:48 | 1785 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 1801-02 Y SE CERRO POR CONTROL LLEVA 90% 1711-04 LLEVA 10% 1717-01 | B2301150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-15 | 3570 | keep | 0 | Jan | 2023 | 0.0024315 | 0.0012158 | Momentary | FALSE | FALSE | Not_TMED_Event | 1785
BAYAMON | 2023-01-15 16:46 | 2023-01-15 16:48 | 453 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 1801-02 Y SE CERRO POR CONTROL LLEVA 90% 1711-04 LLEVA 10% 1717-01 | B2301150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-15 | 906 | keep | 0 | Jan | 2023 | 0.00061707 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-01-15 16:46 | 2023-01-15 16:48 | 186 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 90% 1711-04 LLEVA 10% 1717-01 | B2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-15 | 372 | keep | 0 | Jan | 2023 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
SAN JUAN | 2023-01-15 16:48 | 2023-01-15 18:59 | 533 | 2:11 | T | DESGANCHE | SE ABRIO MACHETE PARA SECCIONALIZAR AVERIA POR DESGANCHE MEDIANTE SWITCHING-FORM SJ-230112-02 - 60% EN SERVICIO | S23011500087 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-01-15 | 69823 | keep | 0 | Jan | 2023 | 0.047556 | 0.00036302 | Sustained | FALSE | FALSE | Not_TMED_Event | 533
CAGUAS | 2023-01-15 16:51 | 2023-01-15 19:21 | 25 | 2:30 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23011500108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-01-15 | 3750 | keep | 0 | Jan | 2023 | 0.0025541 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-01-15 16:52 | 2023-01-15 20:00 | 50 | 3:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A23011500023 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 188 | 2023-01-15 | 9400 | keep | 0 | Jan | 2023 | 0.0064023 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-15 16:58 | 2023-01-16 01:58 | 80 | 9:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L SE REPORTA LLUVIA Y VIENTO | B23011500055 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 540 | 2023-01-15 | 43200 | keep | 0 | Jan | 2023 | 0.029423 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-15 17:00 | 2023-01-15 18:29 | 112 | 1:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | B23011500056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2023-01-15 | 9968 | keep | 0 | Jan | 2023 | 0.0067892 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
SAN JUAN | 2023-01-15 17:02 | 2023-01-15 17:07 | 427 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO X CONTROL | S23011500098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-01-15 | 2135 | keep | 0 | Jan | 2023 | 0.0014541 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
CAGUAS | 2023-01-15 17:03 | 2023-01-15 17:12 | 32 | 0:09 | P | CRUCETA DEFECTUOSA O AVERIADA | 1 X 50 EN C/L SE RETIRO SOPORTE DE CRUZETA PODRIDO QUE HABIA CAIDO ENCIMA DE LAS LINEAS | C23011500110 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 9 | 2023-01-15 | 288 | keep | 0 | Jan | 2023 | 0.00019616 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
VEGA BAJA | 2023-01-15 17:10 | 2023-01-15 19:20 | 70 | 2:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS DE LAS LINEAS | A23011500027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-01-15 | 9100 | keep | 0 | Jan | 2023 | 0.006198 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2023-01-15 17:26 | 2023-01-15 17:55 | 23 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | C23011500114 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-01-15 | 667 | keep | 0 | Jan | 2023 | 0.00045429 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CANOVANAS | 2023-01-15 17:40 | 2023-01-15 20:17 | 25 | 2:37 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | R23011500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-01-15 | 3925 | keep | 0 | Jan | 2023 | 0.0026733 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-01-15 17:42 | 2023-01-15 20:30 | 54 | 2:48 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23011500119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-01-15 | 9072 | keep | 0 | Jan | 2023 | 0.0061789 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BAYAMON | 2023-01-15 18:12 | 2023-01-16 05:16 | 26 | 11:04 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER Y 1 X 40 SMU-20 EN SU-D | B23011500064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 664 | 2023-01-15 | 17264 | keep | 0 | Jan | 2023 | 0.011758 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CANOVANAS | 2023-01-15 18:15 | 2023-01-15 18:16 | 539 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 539 | keep | 0 | Jan | 2023 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
BARRANQUITAS | 2023-01-15 18:20 | 2023-01-16 14:30 | 39 | 20:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN RISER Y 1 X 40 RISER MAL TIEMPO | C23011500129 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1210 | 2023-01-15 | 47190 | keep | 0 | Jan | 2023 | 0.032141 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2023-01-15 18:20 | 2023-01-15 20:15 | 10 | 1:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR Y SE REPARO SECUNDARIA | B23011500082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 115 | 2023-01-15 | 1150 | keep | 0 | Jan | 2023 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-15 18:23 | 2023-01-15 22:51 | 75 | 4:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B23011500065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 268 | 2023-01-15 | 20100 | keep | 0 | Jan | 2023 | 0.01369 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-01-15 18:36 | 2023-01-15 20:54 | 25 | 2:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S23011500137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2023-01-15 | 3450 | keep | 0 | Jan | 2023 | 0.0023498 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-01-15 18:40 | 2023-01-16 07:30 | 45 | 12:50 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C23011500139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 770 | 2023-01-15 | 34650 | keep | 0 | Jan | 2023 | 0.0236 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-01-15 18:46 | 2023-01-15 21:23 | 8 | 2:37 | P | DESGANCHE | 1 X 20 C/L DESGANCHE | C23011500140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-01-15 | 1256 | keep | 0 | Jan | 2023 | 0.00085546 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-01-15 18:57 | 2023-01-15 21:18 | 11 | 2:21 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23011500046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-01-15 | 1551 | keep | 0 | Jan | 2023 | 0.0010564 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-01-15 18:59 | 2023-01-15 19:55 | 213 | 0:56 | P | DESGANCHE | SE REALIZO DESGANCHE A VARETA DESDE EL SUELO MEDIANTE SWITCHING-FORM SJ-2301-15-02 - EN SERVICIO EL 40% QUE FALTABA POR ENTRAR | S23011500087 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-01-15 | 11928 | keep | 0 | Jan | 2023 | 0.0081241 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-15 19:05 | 2023-01-16 00:37 | 19 | 5:32 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23011500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 332 | 2023-01-15 | 6308 | keep | 0 | Jan | 2023 | 0.0042964 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2023-01-15 19:22 | 2023-01-15 20:05 | 3766 | 0:43 | S | OTRAS CAUSAS | SE TRANFIRIO CARGA DE LA PORTATIL #20 AL 2305-04 POR DISPARO DE ALTA DE LA PORTATIL SE ENCONTRARON FUSIBLES FUNDIDOS HACIA MEDICION REMOTA Y PT'S AVERIADOS | R23011500050 | New_Event | Other Causes | Include | Include | Other | 43 | 2023-01-15 | 161938 | keep | 0 | Jan | 2023 | 0.1103 | 0.002565 | Sustained | FALSE | FALSE | Not_TMED_Event | 3766
CANOVANAS | 2023-01-15 19:22 | 2023-01-15 20:05 | 1380 | 0:43 | S | OTRAS CAUSAS | SE TRANFIRIO CARGA DE LA PORTATIL #20 AL 2305-04 POR DISPARO DE ALTA DE LA PORTATIL SE ENCONTRARON FUSIBLES FUNDIDOS HACIA MEDICION REMOTA Y PT'S AVERIADOS | R23011500050 | New_Event | Other Causes | Include | Include | Other | 43 | 2023-01-15 | 59340 | keep | 0 | Jan | 2023 | 0.040416 | 0.00093991 | Sustained | FALSE | FALSE | Not_TMED_Event | 1380
GUAYAMA | 2023-01-15 19:42 | 2023-01-15 20:19 | 907 | 0:37 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO EN TRONCAL | P23011500056 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 37 | 2023-01-15 | 33559 | keep | 0 | Jan | 2023 | 0.022857 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-01-15 19:52 | 2023-01-15 21:30 | 4009 | 1:38 | S | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SUBESTACION PORTATIL 14 BREAKER SECUNDARIO NO SE ENCONTRO NADA | P23011500059 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 98 | 2023-01-15 | 392882 | keep | 0 | Jan | 2023 | 0.26759 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
ARECIBO | 2023-01-15 20:07 | 2023-01-15 21:42 | 80 | 1:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA LLUVIA Y VIENTO | A23011500043 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 95 | 2023-01-15 | 7600 | keep | 0 | Jan | 2023 | 0.0051763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-01-15 20:10 | 2023-01-15 20:11 | 970 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 970 | keep | 0 | Jan | 2023 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
MAYAGÃœEZ | 2023-01-15 20:12 | 2023-01-16 01:21 | 75 | 5:09 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PARTIDA | M23011500053 | New_Event | Primary Wire Break | Include | Include | Equipment | 309 | 2023-01-15 | 23175 | keep | 0 | Jan | 2023 | 0.015784 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-01-15 20:18 | 2023-01-15 21:15 | 2124 | 0:57 | T | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR CARGA POR EL 1657-04 SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA DEL 1118-07 | R23011500172 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 57 | 2023-01-15 | 121068 | keep | 0 | Jan | 2023 | 0.082459 | 0.0014466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2124
CANOVANAS | 2023-01-15 20:18 | 2023-01-15 21:15 | 14 | 0:57 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR LLEVA EL 1118-07 SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA DEL 1118-07 | R23011500172 | New_Event | Feeder Load Transferred | Include | Include | Other | 57 | 2023-01-15 | 798 | keep | 0 | Jan | 2023 | 0.00054351 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-01-15 20:21 | 2023-01-15 22:26 | 30 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A23011500048 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2023-01-15 | 3750 | keep | 0 | Jan | 2023 | 0.0025541 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-15 20:29 | 2023-01-15 20:31 | 837 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1420-04 CERRADO X CONTROL LLEVA 1401-06 LLEVA 1401-07 LLEVA 30% 1404-09 | S23011500162 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-15 | 1674 | keep | 0 | Jan | 2023 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-01-15 20:29 | 2023-01-15 20:31 | 908 | 0:02 | T | TRANSFORMADOR AVERIADO | DISPARO DE INTERRUPTOR 1420-04 CERRADO X CONTROL LLEVA 1401-06 LLEVA 1401-07 LLEVA 30% 1404-09 | S23011500162 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2 | 2023-01-15 | 1816 | keep | 0 | Jan | 2023 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2023-01-15 20:29 | 2023-01-15 20:31 | 146 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1420-04 CERRADO X CONTROL LLEVA 1401-06 LLEVA 1401-07 LLEVA 30% 1404-09 | S23011500162 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-15 | 292 | keep | 0 | Jan | 2023 | 0.00019888 | 9.944e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 146
SAN JUAN | 2023-01-15 20:29 | 2023-01-15 20:31 | 449 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CERRADO X CONTROL LLEVA 1401-06 LLEVA 1401-07 LLEVA 30% 1404-09 | S23011500162 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-15 | 898 | keep | 0 | Jan | 2023 | 0.00061162 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
SAN JUAN | 2023-01-15 20:31 | 2023-01-16 15:19 | 10 | 18:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 75KVA X 75KVA - FASE @ FASE | S23011500163 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 1128 | 2023-01-15 | 11280 | keep | 0 | Jan | 2023 | 0.0076828 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-15 20:44 | 2023-01-15 22:20 | 40 | 1:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | C23011500157 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2023-01-15 | 3840 | keep | 0 | Jan | 2023 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-15 20:54 | 2023-01-15 20:55 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1206-03 LLEVA 85% 1204-05 | S2301150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-15 | 8679 | keep | 0 | Jan | 2023 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-01-15 20:54 | 2023-01-15 20:55 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR 1206-03 LLEVA 85% 1204-05 | S2301150000X | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 4133 | keep | 0 | Jan | 2023 | 0.002815 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-15 20:55 | 2023-01-16 08:50 | 25 | 11:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S23011500137 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 715 | 2023-01-15 | 17875 | keep | 0 | Jan | 2023 | 0.012175 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-01-15 21:06 | 2023-01-16 11:30 | 50 | 14:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L SE REMPLAZO AISLADOR | C23011500160 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 864 | 2023-01-15 | 43200 | keep | 0 | Jan | 2023 | 0.029423 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-01-15 21:09 | 2023-01-16 14:24 | 1 | 17:15 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHIN DE XMR SE REEMPLAZO BAJANTE 1 X 65 EN C/L | C23011500163 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1035 | 2023-01-15 | 1035 | keep | 0 | Jan | 2023 | 0.00070493 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-15 21:11 | 2023-01-16 08:05 | 50 | 10:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BEJUCOS | A23011500062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 654 | 2023-01-15 | 32700 | keep | 0 | Jan | 2023 | 0.022272 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-15 21:12 | 2023-01-16 11:14 | 36 | 14:02 | P | CABLE SOTERRADO AVERIADO | 1X20 EN RISER | S23011500168 | New_Event | UG Cable Fault | Include | Include | Equipment | 842 | 2023-01-15 | 30312 | keep | 0 | Jan | 2023 | 0.020645 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CANOVANAS | 2023-01-15 21:15 | 2023-01-16 00:09 | 425 | 2:54 | P | TERMINACION SOTERRADA AVERIADA | 2 X 100 Y 1 X 65 EN C/LS DESGANCHO CERRO PUENTE Y REMPLAZO TERMINACION EN RISER | R23011500172 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 174 | 2023-01-15 | 73950 | keep | 0 | Jan | 2023 | 0.050367 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-15 21:25 | 2023-01-15 23:36 | 175 | 2:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CONVERTIDOR | B23011500085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2023-01-15 | 22925 | keep | 0 | Jan | 2023 | 0.015614 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
SAN JUAN | 2023-01-15 21:39 | 2023-01-16 11:57 | 40 | 14:18 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | S23011500175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 858 | 2023-01-15 | 34320 | keep | 0 | Jan | 2023 | 0.023375 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-15 21:41 | 2023-01-16 01:46 | 33 | 4:05 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23011500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2023-01-15 | 8085 | keep | 0 | Jan | 2023 | 0.0055067 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
VEGA BAJA | 2023-01-15 21:52 | 2023-01-16 03:35 | 2697 | 5:43 | T | CONDUCTOR ROTO O ABIERTO | SE REPARA LINEA PRIMARIA PARTIDA EN TRONCAL DE INTERRUPTOR | A23011500065 | New_Event | Primary Wire Break | Include | Include | Equipment | 343 | 2023-01-15 | 925071 | keep | 0 | Jan | 2023 | 0.63006 | 0.0018369 | Sustained | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2023-01-15 21:53 | 2023-01-15 21:54 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23011500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 1227 | keep | 0 | Jan | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
CAGUAS | 2023-01-15 21:55 | 2023-01-16 00:35 | 40 | 2:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | C23011500175 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 160 | 2023-01-15 | 6400 | keep | 0 | Jan | 2023 | 0.004359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-15 22:00 | 2023-01-16 12:38 | 38 | 14:38 | P | TERMINACION SOTERRADA AVERIADA | SE REMPLAZO TERMINACION EN SU-3 | B23011500027 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 878 | 2023-01-15 | 33364 | keep | 0 | Jan | 2023 | 0.022724 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-15 22:05 | 2023-01-15 22:06 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 652 | keep | 0 | Jan | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
PONCE | 2023-01-15 22:08 | 2023-01-15 22:09 | 5063 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECERRO SE REALIZO PRUEBA Y QUEDO EN SERVICIO | P23011500231 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 5063 | keep | 0 | Jan | 2023 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
CANOVANAS | 2023-01-15 22:47 | 2023-01-16 09:21 | 6 | 10:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R23011500301 | New_Event | Primary Wire Break | Include | Include | Equipment | 634 | 2023-01-15 | 3804 | keep | 0 | Jan | 2023 | 0.0025909 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-15 22:50 | 2023-01-15 22:53 | 4291 | 0:03 | T | NO SE REPORTO CAUSA | RECERRO Y QUEDO FUERA SE PROBO Y QUEDO EN SERVICIO | S2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-15 | 12873 | keep | 0 | Jan | 2023 | 0.0087677 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-01-15 23:35 | 2023-01-16 13:49 | 12 | 14:14 | P | DESGANCHE | 1X30 EN XMR DESGANCHE | S23011500202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 854 | 2023-01-15 | 10248 | keep | 0 | Jan | 2023 | 0.0069799 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-15 23:49 | 2023-01-15 23:50 | 732 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 732 | keep | 0 | Jan | 2023 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2023-01-15 23:49 | 2023-01-15 23:50 | 1699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-15 | 1699 | keep | 0 | Jan | 2023 | 0.0011572 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2023-01-15 23:49 | 2023-01-16 02:47 | 514 | 2:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S23011600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 178 | 2023-01-15 | 91492 | keep | 0 | Jan | 2023 | 0.062315 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2023-01-15 23:49 | 2023-01-16 02:47 | 681 | 2:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S23011600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 178 | 2023-01-15 | 121218 | keep | 0 | Jan | 2023 | 0.082561 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2023-01-15 23:49 | 2023-01-16 02:47 | 752 | 2:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S23011600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 178 | 2023-01-15 | 133856 | keep | 0 | Jan | 2023 | 0.091169 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2023-01-15 23:49 | 2023-01-16 02:47 | 68 | 2:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S23011600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 178 | 2023-01-15 | 12104 | keep | 0 | Jan | 2023 | 0.008244 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
HUMACAO | 2023-01-15 23:55 | 2023-01-16 07:55 | 144 | 8:00 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SE ABRE CORTE DE LINEA TOTAL PARA REPARAR | C23011500188 | New_Event | Primary Wire Break | Include | Include | Equipment | 480 | 2023-01-15 | 69120 | keep | 0 | Jan | 2023 | 0.047077 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
CANOVANAS | 2023-01-16 00:07 | 2023-01-16 04:10 | 86 | 4:03 | P | DESGANCHE | 1 X 50 EN C/L | R23011600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-01-16 | 20898 | keep | 0 | Jan | 2023 | 0.014234 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
VEGA BAJA | 2023-01-16 00:19 | 2023-01-16 05:27 | 50 | 5:08 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | A23011600001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 308 | 2023-01-16 | 15400 | keep | 0 | Jan | 2023 | 0.010489 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-01-16 00:25 | 2023-01-16 06:45 | 86 | 6:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23011600002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 380 | 2023-01-16 | 32680 | keep | 0 | Jan | 2023 | 0.022258 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
FAJARDO | 2023-01-16 00:42 | 2023-01-16 08:47 | 100 | 8:05 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23011600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 485 | 2023-01-16 | 48500 | keep | 0 | Jan | 2023 | 0.033033 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-16 00:47 | 2023-01-16 00:48 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-01-16 00:57 | 2023-01-16 00:59 | 207 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-16 | 414 | keep | 0 | Jan | 2023 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
CANOVANAS | 2023-01-16 01:16 | 2023-01-16 15:05 | 42 | 13:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA Y REPARO SECUNDARIA NO FUNDIO | R23011600006 | New_Event | Cutout Failure | Include | Include | Equipment | 829 | 2023-01-16 | 34818 | keep | 0 | Jan | 2023 | 0.023714 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2023-01-16 01:20 | 2023-01-16 01:21 | 1825 | 0:01 | T | DESGANCHE | RECIERRE | S2301160000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-16 | 1825 | keep | 0 | Jan | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
YAUCO | 2023-01-16 01:24 | 2023-01-16 08:35 | 100 | 7:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | P23011600011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 431 | 2023-01-16 | 43100 | keep | 0 | Jan | 2023 | 0.029355 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-16 01:32 | 2023-01-16 14:46 | 26 | 13:14 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23011600041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 794 | 2023-01-16 | 20644 | keep | 0 | Jan | 2023 | 0.014061 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2023-01-16 01:39 | 2023-01-16 01:40 | 867 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 867 | keep | 0 | Jan | 2023 | 0.00059051 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2023-01-16 01:40 | 2023-01-16 01:41 | 1356 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 1356 | keep | 0 | Jan | 2023 | 0.00092357 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
GUAYAMA | 2023-01-16 01:44 | 2023-01-16 01:45 | 75 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 4402-02 EL CUAL LLEVA LA CARGA DEL 4402-01 | P23011600028 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-16 | 75 | keep | 0 | Jan | 2023 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
GUAYAMA | 2023-01-16 01:44 | 2023-01-16 01:45 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO TIENE LA CARGA DEL 4402-01 | P23011600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 449 | keep | 0 | Jan | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
ARECIBO | 2023-01-16 01:45 | 2023-01-16 08:55 | 50 | 7:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23011600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 430 | 2023-01-16 | 21500 | keep | 0 | Jan | 2023 | 0.014644 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-01-16 01:56 | 2023-01-16 09:10 | 35 | 7:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR RAMA SOBRE LINEA | P23011600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2023-01-16 | 15190 | keep | 0 | Jan | 2023 | 0.010346 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-01-16 02:12 | 2023-01-16 02:13 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 5252 | keep | 0 | Jan | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2023-01-16 02:18 | 2023-01-16 10:30 | 36 | 8:12 | P | TERMINACION SOTERRADA AVERIADA | 1 X 40 EN C/L TERMINACION AVERIADA EN PPROVISIONAL AEREO @ T-53 | B23011600003 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 492 | 2023-01-16 | 17712 | keep | 0 | Jan | 2023 | 0.012064 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2023-01-16 02:30 | 2023-01-16 10:00 | 80 | 7:30 | P | DESGANCHE | 1 X 80 1 X 40 SE DESGANCHO | B23011600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 450 | 2023-01-16 | 36000 | keep | 0 | Jan | 2023 | 0.024519 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-16 02:31 | 2023-01-16 02:32 | 1825 | 0:01 | T | DESGANCHE | RECIERRE | S2301160000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-16 | 1825 | keep | 0 | Jan | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BARRANQUITAS | 2023-01-16 02:31 | 2023-01-16 02:32 | 2635 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 2635 | keep | 0 | Jan | 2023 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
SAN JUAN | 2023-01-16 02:32 | 2023-01-16 10:12 | 31 | 7:40 | P | DESGANCHE | 1X65 EN C/L Y 1X20 EN XMR DESGANCHE | S23011600056 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 460 | 2023-01-16 | 14260 | keep | 0 | Jan | 2023 | 0.0097124 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-01-16 03:01 | 2023-01-16 04:36 | 80 | 1:35 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23011600064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-01-16 | 7600 | keep | 0 | Jan | 2023 | 0.0051763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-01-16 03:03 | 2023-01-16 14:09 | 40 | 11:06 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE REPARO PRIMARIA | B23011600006 | New_Event | Primary Wire Break | Include | Include | Equipment | 666 | 2023-01-16 | 26640 | keep | 0 | Jan | 2023 | 0.018144 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-01-16 03:17 | 2023-01-16 18:52 | 150 | 15:35 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA EN EL PISO | P23011600023 | New_Event | Primary Wire Break | Include | Include | Equipment | 935 | 2023-01-16 | 140250 | keep | 0 | Jan | 2023 | 0.095524 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-01-16 03:46 | 2023-01-16 11:07 | 50 | 7:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO | R23011600012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 441 | 2023-01-16 | 22050 | keep | 0 | Jan | 2023 | 0.015018 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-16 03:54 | 2023-01-16 03:55 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 4981 | keep | 0 | Jan | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
SAN JUAN | 2023-01-16 04:03 | 2023-01-16 14:56 | 203 | 10:53 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETE | S23011600068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2023-01-16 | 132559 | keep | 0 | Jan | 2023 | 0.090285 | 0.00013826 | Sustained | FALSE | FALSE | Not_TMED_Event | 203
FAJARDO | 2023-01-16 04:07 | 2023-01-16 08:39 | 167 | 4:32 | P | CAUSAS EXTERNAS | CAMION HALO CABLEADO SECUNDARIO 1 X 50 EN C/L | R23011600015 | New_Event | Damage From Public | Include | Include | Public | 272 | 2023-01-16 | 45424 | keep | 0 | Jan | 2023 | 0.030938 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
PONCE | 2023-01-16 04:19 | 2023-01-16 07:01 | 1650 | 2:42 | T | DESGANCHE | DISPARO INTERRUPTOR SE SACO BAMBUA SOBRE LINEA Y SE CARGO SPRING Y SE PUDO CERRAR INTERRUPTOR POR SCADA. SE SECCIONALIZA EN CORTE DE LINEA FID 1000079011 | P23011600027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-01-16 | 267300 | keep | 0 | Jan | 2023 | 0.18206 | 0.0011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 1650
CANOVANAS | 2023-01-16 04:26 | 2023-01-16 04:29 | 2179 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-16 | 6537 | keep | 0 | Jan | 2023 | 0.0044523 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
PONCE | 2023-01-16 04:31 | 2023-01-16 20:40 | 76 | 16:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23011600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 969 | 2023-01-16 | 73644 | keep | 0 | Jan | 2023 | 0.050159 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
CANOVANAS | 2023-01-16 04:45 | 2023-01-16 09:52 | 100 | 5:07 | P | DESGANCHE | 1 X 80 EN C/L | R23011600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2023-01-16 | 30700 | keep | 0 | Jan | 2023 | 0.02091 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-01-16 05:50 | 2023-01-16 08:15 | 242 | 2:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO | R23011600024 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 145 | 2023-01-16 | 35090 | keep | 0 | Jan | 2023 | 0.0239 | 0.00016483 | Sustained | FALSE | FALSE | Not_TMED_Event | 242
BAYAMON | 2023-01-16 06:09 | 2023-01-16 06:10 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 50% DE SU CARGA TRANSFERIDA AL 1909-07 LLEVA LA CARGA DEL 1709-05 | S23011600091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 766 | keep | 0 | Jan | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-01-16 06:09 | 2023-01-16 06:10 | 2364 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1709-03 50% DE SU CARGA TRANSFERIDA AL 1909-07 LLEVA LA CARGA DEL 1709-05 | S23011600091 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-16 | 2364 | keep | 0 | Jan | 2023 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BARRANQUITAS | 2023-01-16 06:09 | 2023-01-16 10:56 | 130 | 4:47 | P | ARBOL SOBRE LINEA | 1X50 EN C/L SE RETIRO ARBOL DE LA PRIMARIA | C23011600010 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 287 | 2023-01-16 | 37310 | keep | 0 | Jan | 2023 | 0.025412 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2023-01-16 06:14 | 2023-01-16 15:57 | 99 | 9:43 | P | NO SE REPORTO CAUSA | 1X65 DE RISER @ SU-D | S23011600092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 583 | 2023-01-16 | 57717 | keep | 0 | Jan | 2023 | 0.039311 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
SAN JUAN | 2023-01-16 06:17 | 2023-01-16 06:18 | 451 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23011600093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 451 | keep | 0 | Jan | 2023 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
MAYAGÃœEZ | 2023-01-16 06:46 | 2023-01-16 11:00 | 100 | 4:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23011600022 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 254 | 2023-01-16 | 25400 | keep | 0 | Jan | 2023 | 0.0173 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-01-16 06:46 | 2023-01-16 08:40 | 60 | 1:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23011600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2023-01-16 | 6840 | keep | 0 | Jan | 2023 | 0.0046587 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-01-16 06:53 | 2023-01-16 16:30 | 50 | 9:37 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REPARO LINEA PRIMARIA ROTA | A23011600012 | New_Event | Primary Wire Break | Include | Include | Equipment | 577 | 2023-01-16 | 28850 | keep | 0 | Jan | 2023 | 0.01965 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-01-16 06:54 | 2023-01-16 06:55 | 1364 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 1364 | keep | 0 | Jan | 2023 | 0.00092901 | 0.00092901 | Momentary | FALSE | FALSE | Not_TMED_Event | 1364
CAGUAS | 2023-01-16 06:55 | 2023-01-16 07:45 | 86 | 0:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23011600013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2023-01-16 | 4300 | keep | 0 | Jan | 2023 | 0.0029287 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
AGUADILLA | 2023-01-16 07:00 | 2023-01-16 11:25 | 2825 | 4:25 | T | DESGANCHE | SE RETIRO BAMBUS Y RAMAS SOBRE LAS LINEAS Y SE CERRO INTERRUPTOR MANUAL ELECTRICO. RTU DOWN | M23011600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2023-01-16 | 748625 | keep | 0 | Jan | 2023 | 0.50989 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
PONCE | 2023-01-16 07:01 | 2023-01-16 07:33 | 147 | 0:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINE RAFAGAS DE VIENTO | P23011600027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 32 | 2023-01-16 | 4704 | keep | 0 | Jan | 2023 | 0.0032039 | 0.00010012 | Sustained | FALSE | FALSE | Not_TMED_Event | 147
YAUCO | 2023-01-16 07:09 | 2023-01-16 11:30 | 100 | 4:21 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011600037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2023-01-16 | 26100 | keep | 0 | Jan | 2023 | 0.017777 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-16 07:19 | 2023-01-16 11:23 | 1 | 4:04 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN MONTURA 2 X 20 Y 2 X 30 EN C/L | B23011600014 | New_Event | Primary Wire Break | Include | Include | Equipment | 244 | 2023-01-16 | 244 | keep | 0 | Jan | 2023 | 0.00016619 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-16 07:21 | 2023-01-16 11:12 | 10 | 3:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 SMU20 MAL TIEMPO LLUVIA | S23011600040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 231 | 2023-01-16 | 2310 | keep | 0 | Jan | 2023 | 0.0015733 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-16 07:30 | 2023-01-16 13:07 | 27 | 5:37 | P | DESGANCHE | DESGANCHE 2 X 65 EN C/L | S23011600125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2023-01-16 | 9099 | keep | 0 | Jan | 2023 | 0.0061973 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2023-01-16 07:30 | 2023-01-16 10:37 | 29 | 3:07 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | R23011600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2023-01-16 | 5423 | keep | 0 | Jan | 2023 | 0.0036936 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CAGUAS | 2023-01-16 07:42 | 2023-01-16 10:45 | 473 | 3:03 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE DE LINEA A MACHETE | C23011600033 | New_Event | Primary Wire Break | Include | Include | Equipment | 183 | 2023-01-16 | 86559 | keep | 0 | Jan | 2023 | 0.058955 | 0.00032216 | Sustained | FALSE | FALSE | Not_TMED_Event | 473
BARRANQUITAS | 2023-01-16 07:47 | 2023-01-16 08:43 | 139 | 0:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE DE BAMBUA | C23011600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-01-16 | 7784 | keep | 0 | Jan | 2023 | 0.0053016 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
YAUCO | 2023-01-16 07:47 | 2023-01-16 12:20 | 30 | 4:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | P23011600062 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 273 | 2023-01-16 | 8190 | keep | 0 | Jan | 2023 | 0.0055782 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-01-16 07:50 | 2023-01-16 08:37 | 2888 | 0:47 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE MACHETES POR AVERIA DE AISLADORES Y SE CIERRA INTERRUPTOR | A23011600019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 47 | 2023-01-16 | 135736 | keep | 0 | Jan | 2023 | 0.092449 | 0.001967 | Sustained | FALSE | FALSE | Not_TMED_Event | 2888
BARRANQUITAS | 2023-01-16 07:54 | 2023-01-16 12:10 | 338 | 4:16 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LA LINEA | C23011600038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2023-01-16 | 86528 | keep | 0 | Jan | 2023 | 0.058934 | 0.00023021 | Sustained | FALSE | FALSE | Not_TMED_Event | 338
PONCE | 2023-01-16 07:54 | 2023-01-16 15:30 | 125 | 7:36 | P | DESGANCHE | 2 X 80 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23011600066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 456 | 2023-01-16 | 57000 | keep | 0 | Jan | 2023 | 0.038822 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2023-01-16 08:00 | 2023-01-16 18:20 | 45 | 10:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL FUERTES VIENTOS | M23011600061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 620 | 2023-01-16 | 27900 | keep | 0 | Jan | 2023 | 0.019003 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-01-16 08:05 | 2023-01-16 08:19 | 15 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARA NEUTRAL | A23011600009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2023-01-16 | 210 | keep | 0 | Jan | 2023 | 0.00014303 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-16 08:06 | 2023-01-16 15:22 | 30 | 7:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 Y 1 X 50 C/L EN C/L SE LEVANTO PRIMARIA | B23011600022 | New_Event | Primary Wire Break | Include | Include | Equipment | 436 | 2023-01-16 | 13080 | keep | 0 | Jan | 2023 | 0.0089087 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-01-16 08:06 | 2023-01-16 08:07 | 1364 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | C2301160000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 1364 | keep | 0 | Jan | 2023 | 0.00092901 | 0.00092901 | Momentary | FALSE | FALSE | Not_TMED_Event | 1364
PONCE | 2023-01-16 08:08 | 2023-01-16 09:47 | 1650 | 1:39 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE AMARRA CON INTERRUPTOR 2 PARA QUE SUBESTACIONES TRABAJE MECANISMO DE CARGA DE INTERRUPTOR | P23011600081 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 99 | 2023-01-16 | 163350 | keep | 0 | Jan | 2023 | 0.11126 | 0.0011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 1650
ARECIBO | 2023-01-16 08:08 | 2023-01-16 19:50 | 40 | 11:42 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23011600033 | New_Event | Primary Wire Break | Include | Include | Equipment | 702 | 2023-01-16 | 28080 | keep | 0 | Jan | 2023 | 0.019125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-16 08:09 | 2023-01-16 08:10 | 5809 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B2301160000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-01-16 | 5809 | keep | 0 | Jan | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2023-01-16 08:10 | 2023-01-16 16:11 | 71 | 8:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L REMPLAZO CAJA | B23011600095 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 481 | 2023-01-16 | 34151 | keep | 0 | Jan | 2023 | 0.02326 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
CAGUAS | 2023-01-16 08:12 | 2023-01-16 15:04 | 302 | 6:52 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | C23011600044 | New_Event | Animals | Include | Include | Wildlife | 412 | 2023-01-16 | 124424 | keep | 0 | Jan | 2023 | 0.084745 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
CANOVANAS | 2023-01-16 08:13 | 2023-01-16 12:13 | 21 | 4:00 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | R23011600060 | New_Event | Animals | Include | Include | Wildlife | 240 | 2023-01-16 | 5040 | keep | 0 | Jan | 2023 | 0.0034327 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2023-01-16 08:14 | 2023-01-16 11:00 | 12 | 2:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23011600027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2023-01-16 | 1992 | keep | 0 | Jan | 2023 | 0.0013567 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-01-16 08:18 | 2023-01-16 09:56 | 20 | 1:38 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23011600065 | New_Event | Animals | Include | Include | Wildlife | 98 | 2023-01-16 | 1960 | keep | 0 | Jan | 2023 | 0.0013349 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-01-16 08:20 | 2023-01-16 09:21 | 50 | 1:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | P23011600086 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 61 | 2023-01-16 | 3050 | keep | 0 | Jan | 2023 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-16 08:23 | 2023-01-16 11:14 | 1 | 2:51 | P | CONDUCTOR ROTO O ABIERTO | 1 X 10 EN TRANSFORMADOR SE CERRO PUENTE DE LINEA A CAJA | C23011600051 | New_Event | Primary Wire Break | Include | Include | Equipment | 171 | 2023-01-16 | 171 | keep | 0 | Jan | 2023 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-01-16 08:24 | 2023-01-16 08:54 | 50 | 0:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | P23011600089 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 30 | 2023-01-16 | 1500 | keep | 0 | Jan | 2023 | 0.0010216 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-16 08:27 | 2023-01-16 08:28 | 1089 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 DE JUNCOS A RIO BLANCO | C23011600056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-16 | 1089 | keep | 0 | Jan | 2023 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2023-01-16 08:27 | 2023-01-16 08:28 | 3896 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 DE JUNCOS A RIO BLANCO | C23011600056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-16 | 3896 | keep | 0 | Jan | 2023 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2023-01-16 08:27 | 2023-01-16 08:28 | 1467 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 DE JUNCOS A RIO BLANCO | C23011600056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-16 | 1467 | keep | 0 | Jan | 2023 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BAYAMON | 2023-01-16 08:33 | 2023-01-16 14:00 | 1 | 5:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REMPLAZO AISLACION | B23011600038 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 327 | 2023-01-16 | 327 | keep | 0 | Jan | 2023 | 0.00022272 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-16 08:33 | 2023-01-16 13:01 | 15 | 4:28 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE CON VARETA | C23011600062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2023-01-16 | 4020 | keep | 0 | Jan | 2023 | 0.002738 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-01-16 08:34 | 2023-01-16 20:20 | 85 | 11:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23011600101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 706 | 2023-01-16 | 60010 | keep | 0 | Jan | 2023 | 0.040873 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2023-01-16 08:37 | 2023-01-16 11:17 | 400 | 2:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES Y SE REPARA AISLADORES PARTIDOS | A23011600069 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 160 | 2023-01-16 | 64000 | keep | 0 | Jan | 2023 | 0.04359 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-16 08:38 | 2023-01-16 13:30 | 77 | 4:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23011600064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2023-01-16 | 22484 | keep | 0 | Jan | 2023 | 0.015314 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
FAJARDO | 2023-01-16 08:40 | 2023-01-16 09:06 | 4 | 0:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23011600076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 26 | 2023-01-16 | 104 | keep | 0 | Jan | 2023 | 7.0834e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-01-16 08:42 | 2023-01-16 14:52 | 60 | 6:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CL FUERTE VIENTOS | M23011600090 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 370 | 2023-01-16 | 22200 | keep | 0 | Jan | 2023 | 0.01512 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2023-01-16 08:43 | 2023-01-16 10:28 | 20 | 1:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23011600110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-01-16 | 2100 | keep | 0 | Jan | 2023 | 0.0014303 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-01-16 08:45 | 2023-01-16 11:10 | 350 | 2:25 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C23011600069 | New_Event | Animals | Include | Include | Wildlife | 145 | 2023-01-16 | 50750 | keep | 0 | Jan | 2023 | 0.034566 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
ARECIBO | 2023-01-16 08:48 | 2023-01-16 12:37 | 1222 | 3:49 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION POR FUSIBLES EN LA ALTA FUNDIDOS | A23011600118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2023-01-16 | 279838 | keep | 0 | Jan | 2023 | 0.1906 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2023-01-16 08:48 | 2023-01-16 12:37 | 2756 | 3:49 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION POR FUSIBLES EN LA ALTA FUNDIDOS | A23011600118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2023-01-16 | 631124 | keep | 0 | Jan | 2023 | 0.42986 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2023-01-16 08:48 | 2023-01-16 12:37 | 2833 | 3:49 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION POR FUSIBLES EN LA ALTA FUNDIDOS | A23011600118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2023-01-16 | 648757 | keep | 0 | Jan | 2023 | 0.44187 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
FAJARDO | 2023-01-16 08:49 | 2023-01-16 11:01 | 6 | 2:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO Y SECUNDARIA | R23011600084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 132 | 2023-01-16 | 792 | keep | 0 | Jan | 2023 | 0.00053943 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-01-16 08:58 | 2023-01-16 11:54 | 80 | 2:56 | P | DESGANCHE | DESGANCHE 3 X 100 Y 1 X 80 EN DIFERENTES CORTES DE LINEA | P23011600121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-01-16 | 14080 | keep | 0 | Jan | 2023 | 0.0095898 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-16 08:59 | 2023-01-16 17:30 | 100 | 8:31 | P | DESGANCHE | 1 X 100 EN C/L SE REFIRIO PARA DESGANCHE | S23011600210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 511 | 2023-01-16 | 51100 | keep | 0 | Jan | 2023 | 0.034804 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-01-16 09:11 | 2023-01-17 19:45 | 104 | 34:34 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO Y SE NORMALIZARON RECLOSER | M23011600115 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2074 | 2023-01-16 | 215696 | keep | 0 | Jan | 2023 | 0.14691 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
PONCE | 2023-01-16 09:16 | 2023-01-16 14:48 | 253 | 5:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA Y DOS PARARRAYOS | P23011600129 | New_Event | Cutout Failure | Include | Include | Equipment | 332 | 2023-01-16 | 83996 | keep | 0 | Jan | 2023 | 0.057209 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
BAYAMON | 2023-01-16 09:23 | 2023-01-16 16:44 | 11 | 7:21 | P | SECUNDARIA/DESGANCHE | SE DESGANCHO Y SE REMPLAZO 1 X 10 EN XMR | S23011600230 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 441 | 2023-01-16 | 4851 | keep | 0 | Jan | 2023 | 0.003304 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-01-16 09:38 | 2023-01-16 12:46 | 1 | 3:08 | P | NO SE REPORTO CAUSA | 1X30 EN C/L NO CAUSA | S23011600246 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2023-01-16 | 188 | keep | 0 | Jan | 2023 | 0.00012805 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-16 09:43 | 2023-01-16 17:26 | 10 | 7:43 | P | NO SE REPORTO CAUSA | 2X80 EN C/L NO CAUSA | S23011600249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 463 | 2023-01-16 | 4630 | keep | 0 | Jan | 2023 | 0.0031535 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-01-16 09:43 | 2023-01-16 11:02 | 77 | 1:19 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | R23011600113 | New_Event | Animals | Include | Include | Wildlife | 79 | 2023-01-16 | 6083 | keep | 0 | Jan | 2023 | 0.0041431 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
PONCE | 2023-01-16 09:50 | 2023-01-16 12:45 | 38 | 2:55 | P | DESGANCHE | SE HIZO DESGANCHE Y SE LEVANTO ALAMBRE PRIMARIO | P23011600212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-01-16 | 6650 | keep | 0 | Jan | 2023 | 0.0045293 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CANOVANAS | 2023-01-16 09:52 | 2023-01-16 11:33 | 3 | 1:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIA | R23011600117 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 101 | 2023-01-16 | 303 | keep | 0 | Jan | 2023 | 0.00020637 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-01-16 09:55 | 2023-01-16 12:30 | 22 | 2:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO Y SE SUBIO TAP DEL 1 AL 2, SE DEJO 124/248 VOLTIOS | C23011600108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 155 | 2023-01-16 | 3410 | keep | 0 | Jan | 2023 | 0.0023225 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2023-01-16 09:59 | 2023-01-16 12:15 | 127 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS | C23011600111 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2023-01-16 | 17272 | keep | 0 | Jan | 2023 | 0.011764 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
GUAYAMA | 2023-01-16 10:00 | 2023-01-16 16:50 | 17 | 6:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE PARTIDO Y LINEA SECUNDARIA | P23011600135 | New_Event | Primary Pole Failure | Include | Include | Equipment | 410 | 2023-01-16 | 6970 | keep | 0 | Jan | 2023 | 0.0047472 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
GUAYAMA | 2023-01-16 10:07 | 2023-01-16 11:57 | 30 | 1:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR VIENTOS | P23011600161 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 110 | 2023-01-16 | 3300 | keep | 0 | Jan | 2023 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-01-16 10:11 | 2023-01-16 11:59 | 60 | 1:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P23011600164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-01-16 | 6480 | keep | 0 | Jan | 2023 | 0.0044135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-01-16 10:16 | 2023-01-16 13:53 | 35 | 3:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P23011600165 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 217 | 2023-01-16 | 7595 | keep | 0 | Jan | 2023 | 0.0051729 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2023-01-16 10:21 | 2023-01-16 12:30 | 404 | 2:09 | P | ANIMAL | 1 X 140 EN C/L CRUCE POR AVE | C23011600122 | New_Event | Animals | Include | Include | Wildlife | 129 | 2023-01-16 | 52116 | keep | 0 | Jan | 2023 | 0.035496 | 0.00027516 | Sustained | FALSE | FALSE | Not_TMED_Event | 404
SAN JUAN | 2023-01-16 10:25 | 2023-01-16 13:48 | 20 | 3:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO SECUNDARIA NO FUNDIO | S23011600279 | New_Event | Secondary Wire Break | Include | Include | Equipment | 203 | 2023-01-16 | 4060 | keep | 0 | Jan | 2023 | 0.0027652 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-16 10:30 | 2023-01-16 13:30 | 12 | 3:00 | P | TERMINACION SOTERRADA AVERIADA | 1 X 15 EN PROVISIONAL SE REMPLAZO TERMINACION EN PROVISIONAL AEREO | B23011600003 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 180 | 2023-01-16 | 2160 | keep | 0 | Jan | 2023 | 0.0014712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-01-16 10:31 | 2023-01-16 18:50 | 60 | 8:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011600169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 499 | 2023-01-16 | 29940 | keep | 0 | Jan | 2023 | 0.020392 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-01-16 10:50 | 2023-01-16 22:40 | 100 | 11:50 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | P23011600180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 710 | 2023-01-16 | 71000 | keep | 0 | Jan | 2023 | 0.048358 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-16 11:00 | 2023-01-16 11:15 | 1 | 0:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN C/L | B23011600084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2023-01-16 | 15 | keep | 0 | Jan | 2023 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-16 11:14 | 2023-01-16 16:20 | 48 | 5:06 | P | CABLE SOTERRADO AVERIADO | SE REPARO CONDUCTOR SOTERRADO AVERIADO DE T-2 @ T-3 | S23011500168 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 306 | 2023-01-16 | 14688 | keep | 0 | Jan | 2023 | 0.010004 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-16 11:22 | 2023-01-16 11:58 | 1494 | 0:36 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR NO OPERA POR SCADA NI EN EL CAMPO SE PASO CARGA AL 8404-01 | A23011600163 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 36 | 2023-01-16 | 53784 | keep | 0 | Jan | 2023 | 0.036632 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
BAYAMON | 2023-01-16 11:28 | 2023-01-17 07:58 | 1 | 20:30 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23011600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1230 | 2023-01-16 | 1230 | keep | 0 | Jan | 2023 | 0.00083775 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-01-16 11:29 | 2023-01-16 13:30 | 60 | 2:01 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA BAJANTE ZAFADO | M23011600200 | New_Event | Primary Wire Break | Include | Include | Equipment | 121 | 2023-01-16 | 7260 | keep | 0 | Jan | 2023 | 0.0049448 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-01-16 11:36 | 2023-01-16 12:45 | 60 | 1:09 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 100 EN CORTE DE LINEA LINEAS CRUZADAS | M23011600204 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 69 | 2023-01-16 | 4140 | keep | 0 | Jan | 2023 | 0.0028197 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-01-16 11:43 | 2023-01-16 11:44 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 3 | keep | 0 | Jan | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-01-16 11:45 | 2023-01-16 13:15 | 3 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23011600330 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-01-16 | 270 | keep | 0 | Jan | 2023 | 0.0001839 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2023-01-16 11:49 | 2023-01-16 12:43 | 80 | 0:54 | P | DESGANCHE | DESGANCHE 1 X 80 EN CORTE DE LINEA | P23011600215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2023-01-16 | 4320 | keep | 0 | Jan | 2023 | 0.0029423 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-01-16 11:53 | 2023-01-16 13:41 | 9 | 1:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER Y 1 X 40 EN SU-8 | R23011600152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2023-01-16 | 972 | keep | 0 | Jan | 2023 | 0.00066202 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-01-16 11:54 | 2023-01-16 11:55 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23011600165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 5630 | keep | 0 | Jan | 2023 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BARRANQUITAS | 2023-01-16 11:54 | 2023-01-16 15:48 | 22 | 3:54 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYOS | C23011600164 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 234 | 2023-01-16 | 5148 | keep | 0 | Jan | 2023 | 0.0035063 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
PONCE | 2023-01-16 11:58 | 2023-01-17 07:05 | 2 | 19:07 | P | DESGANCHE | DESGANCHE 1 X 40 EN CORTE DE LINEA | P23011600218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1147 | 2023-01-16 | 2294 | keep | 0 | Jan | 2023 | 0.0015624 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-01-16 12:01 | 2023-01-16 13:41 | 10 | 1:40 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO/RELOCALIZO SECUNDARIA PARA SEPARARLA DE LA PRIMARIA | S23011600337 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 100 | 2023-01-16 | 1000 | keep | 0 | Jan | 2023 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-16 12:02 | 2023-01-16 12:50 | 4 | 0:48 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | C23011600168 | New_Event | Animals | Include | Include | Wildlife | 48 | 2023-01-16 | 192 | keep | 0 | Jan | 2023 | 0.00013077 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-01-16 12:30 | 2023-01-16 16:35 | 50 | 4:05 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CL SE RETEZO NEUTRAL PRIMARIO | M23011600217 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 245 | 2023-01-16 | 12250 | keep | 0 | Jan | 2023 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-16 12:46 | 2023-01-16 17:05 | 140 | 4:19 | P | DESGANCHE | 1 X 200 EN C/L SE DESGANCHO | C23011600177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-01-16 | 36260 | keep | 0 | Jan | 2023 | 0.024697 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
PONCE | 2023-01-16 12:51 | 2023-01-16 19:40 | 48 | 6:49 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | P23011600237 | New_Event | Animals | Include | Include | Wildlife | 409 | 2023-01-16 | 19632 | keep | 0 | Jan | 2023 | 0.013371 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BARRANQUITAS | 2023-01-16 12:52 | 2023-01-16 16:48 | 130 | 3:56 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L DE EMERGENCIA POSTE PODRIDO EN LA PERILLA SE INSTALO RIGIDO | C23011600179 | New_Event | Primary Pole Failure | Include | Include | Equipment | 236 | 2023-01-16 | 30680 | keep | 0 | Jan | 2023 | 0.020896 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
ARECIBO | 2023-01-16 12:54 | 2023-01-16 14:05 | 30 | 1:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23011600201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2023-01-16 | 2130 | keep | 0 | Jan | 2023 | 0.0014507 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-01-16 12:57 | 2023-01-16 19:09 | 532 | 6:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE 4 CAJAS 3 X 80 EN C/L Y EN OTROC/L 1 X 100 | C23011600182 | New_Event | Cutout Failure | Include | Include | Equipment | 372 | 2023-01-16 | 197904 | keep | 0 | Jan | 2023 | 0.13479 | 0.00036234 | Sustained | FALSE | FALSE | Not_TMED_Event | 532
YAUCO | 2023-01-16 13:04 | 2023-01-16 16:20 | 125 | 3:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CL SE CERRO PUENTE PRIMARIO | M23011600228 | New_Event | Primary Wire Break | Include | Include | Equipment | 196 | 2023-01-16 | 24500 | keep | 0 | Jan | 2023 | 0.016687 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
HUMACAO | 2023-01-16 13:29 | 2023-01-16 16:10 | 21 | 2:41 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23011600192 | New_Event | Animals | Include | Include | Wildlife | 161 | 2023-01-16 | 3381 | keep | 0 | Jan | 2023 | 0.0023028 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2023-01-16 13:36 | 2023-01-16 15:50 | 10 | 2:14 | P | DESGANCHE | 1 X 65 EN CL BAMBU SOBRE LINEA PRIMARIA | M23011600244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-01-16 | 1340 | keep | 0 | Jan | 2023 | 0.00091267 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-16 13:41 | 2023-01-16 15:11 | 164 | 1:30 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23011600202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-01-16 | 14760 | keep | 0 | Jan | 2023 | 0.010053 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
CANOVANAS | 2023-01-16 13:42 | 2023-01-16 15:33 | 123 | 1:51 | P | DESGANCHE | 2 X 50 EN C/L | R23011600162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-01-16 | 13653 | keep | 0 | Jan | 2023 | 0.009299 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
CAGUAS | 2023-01-16 13:42 | 2023-01-16 19:02 | 127 | 5:20 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | C23011600204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2023-01-16 | 40640 | keep | 0 | Jan | 2023 | 0.02768 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
BAYAMON | 2023-01-16 13:44 | 2023-01-16 15:36 | 1300 | 1:52 | T | ERROR HUMANO | PERSONAL DE SUBESTACIONES REMPLAZANDO RELE CAUSA DISPARO | B23011600136 | New_Event | Human Error | Include | Include | Other | 112 | 2023-01-16 | 145600 | keep | 0 | Jan | 2023 | 0.099167 | 0.00088542 | Sustained | FALSE | FALSE | Not_TMED_Event | 1300
HUMACAO | 2023-01-16 13:48 | 2023-01-16 18:24 | 1 | 4:36 | P | DESGANCHE | 3 X 65 EN RISER Y 2 SMU20 DE 80 AMP SE DESGANCHO PALMA EN RISER | C23011600207 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2023-01-16 | 276 | keep | 0 | Jan | 2023 | 0.00018798 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-16 14:04 | 2023-01-16 16:56 | 40 | 2:52 | P | NO SE REPORTO CAUSA | 1 X 65 1 X 80 EN C/L NO CAUSA | B23011600142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2023-01-16 | 6880 | keep | 0 | Jan | 2023 | 0.0046859 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2023-01-16 14:06 | 2023-01-16 16:20 | 60 | 2:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A23011600218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-01-16 | 8040 | keep | 0 | Jan | 2023 | 0.005476 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-01-16 14:13 | 2023-01-16 14:14 | 1467 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23011600213 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 1467 | keep | 0 | Jan | 2023 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
VEGA BAJA | 2023-01-16 14:18 | 2023-01-16 15:53 | 30 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | B23011600151 | New_Event | Primary Wire Break | Include | Include | Equipment | 95 | 2023-01-16 | 2850 | keep | 0 | Jan | 2023 | 0.0019411 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-01-16 14:22 | 2023-01-16 15:56 | 9 | 1:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REEMPLAZAR BARRA DE NEUTRAL EN PEDESTAL | C23011600216 | New_Event | Secondary Wire Break | Include | Include | Equipment | 94 | 2023-01-16 | 846 | keep | 0 | Jan | 2023 | 0.00057621 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
GUAYAMA | 2023-01-16 14:23 | 2023-01-16 17:26 | 65 | 3:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | P23011600273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-01-16 | 11895 | keep | 0 | Jan | 2023 | 0.0081016 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2023-01-16 14:25 | 2023-01-16 15:18 | 2 | 0:53 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | R23011600163 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 53 | 2023-01-16 | 106 | keep | 0 | Jan | 2023 | 7.2196e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-01-16 14:36 | 2023-01-16 18:17 | 4 | 3:41 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR Y DESGANCHE | C23011600224 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 221 | 2023-01-16 | 884 | keep | 0 | Jan | 2023 | 0.00060209 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-01-16 14:47 | 2023-01-16 14:48 | 2308 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE LLEVA CARGA DE 5901-03 | P23011600286 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-01-16 | 2308 | keep | 0 | Jan | 2023 | 0.001572 | 0.001572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2308
PONCE | 2023-01-16 14:47 | 2023-01-16 14:48 | 1650 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE INTERRUPTOR 5901-02 CON CARGA 5901-03 | P23011600286 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-16 | 1650 | keep | 0 | Jan | 2023 | 0.0011238 | 0.0011238 | Momentary | FALSE | FALSE | Not_TMED_Event | 1650
PONCE | 2023-01-16 14:48 | 2023-01-16 18:10 | 253 | 3:22 | P | PARARRAYOS DEFECTUOSO | 2 X 100 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA Y DOS PARARRAYOS | P23011600129 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 202 | 2023-01-16 | 51106 | keep | 0 | Jan | 2023 | 0.034808 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
SAN JUAN | 2023-01-16 14:55 | 2023-01-16 14:56 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S23011600427 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2023-01-16 14:59 | 2023-01-16 17:30 | 100 | 2:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS DE LAS LINEAS | A23011600225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-01-16 | 15100 | keep | 0 | Jan | 2023 | 0.010285 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-16 15:24 | 2023-01-16 17:40 | 100 | 2:16 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR NO FUNDIO | S23011600429 | New_Event | Primary Wire Break | Include | Include | Equipment | 136 | 2023-01-16 | 13600 | keep | 0 | Jan | 2023 | 0.0092629 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-01-16 15:25 | 2023-01-16 18:30 | 1352 | 3:05 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR NO DIO INDICACION DE OPEN EN SCADA SE CERRO MANUALMENTE | P23011600399 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2023-01-16 | 250120 | keep | 0 | Jan | 2023 | 0.17036 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
AGUADILLA | 2023-01-16 15:39 | 2023-01-16 18:30 | 80 | 2:51 | P | DESGANCHE | 1 X 50 EN CL SE RETIRO RAMA SOBRE LINEA PRIMARIA | M23011600288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-01-16 | 13680 | keep | 0 | Jan | 2023 | 0.0093174 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-16 15:47 | 2023-01-16 17:10 | 40 | 1:23 | P | NO SE REPORTO CAUSA | 1X65 EN RISER NO CAUSA | B23011600176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2023-01-16 | 3320 | keep | 0 | Jan | 2023 | 0.0022612 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-01-16 16:04 | 2023-01-16 18:55 | 1 | 2:51 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A23011600234 | New_Event | Primary Wire Break | Include | Include | Equipment | 171 | 2023-01-16 | 171 | keep | 0 | Jan | 2023 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-01-16 16:05 | 2023-01-16 16:06 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23011600332 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-16 | 2113 | keep | 0 | Jan | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
FAJARDO | 2023-01-16 16:16 | 2023-01-16 18:00 | 40 | 1:44 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L CAMION SACUDIO LAS LINEAS AL IMPACTAR POSTE DE LA TELEFONICA | R23011600170 | New_Event | Damage From Public | Include | Include | Public | 104 | 2023-01-16 | 4160 | keep | 0 | Jan | 2023 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-01-16 16:23 | 2023-01-16 16:29 | 30 | 0:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CL FUERTES VIENTOS | M23011600298 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 6 | 2023-01-16 | 180 | keep | 0 | Jan | 2023 | 0.0001226 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-01-16 16:23 | 2023-01-16 17:38 | 50 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | M23011600260 | New_Event | Primary Wire Break | Include | Include | Equipment | 75 | 2023-01-16 | 3750 | keep | 0 | Jan | 2023 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-01-16 16:40 | 2023-01-17 13:45 | 10 | 21:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | M23011700035 | New_Event | Cutout Failure | Include | Include | Equipment | 1265 | 2023-01-16 | 12650 | keep | 0 | Jan | 2023 | 0.0086159 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-01-16 17:03 | 2023-01-16 20:02 | 6 | 2:59 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHAR Y REPARAR LINEA SECUNDARIA | C23011600270 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 179 | 2023-01-16 | 1074 | keep | 0 | Jan | 2023 | 0.0007315 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-01-16 17:07 | 2023-01-16 19:05 | 65 | 1:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 65 EN CL FUERTES VIENTOS | M23011600307 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2023-01-16 | 7670 | keep | 0 | Jan | 2023 | 0.005224 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-01-16 17:17 | 2023-01-16 18:59 | 3 | 1:42 | P | DESGANCHE | 1X20 EN XMR DESGANCHE | S23011600441 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-01-16 | 306 | keep | 0 | Jan | 2023 | 0.00020842 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-01-16 17:19 | 2023-01-16 19:08 | 9 | 1:49 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R23011600174 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 109 | 2023-01-16 | 981 | keep | 0 | Jan | 2023 | 0.00066815 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-01-16 17:23 | 2023-01-17 11:04 | 7 | 17:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR BAJANTES Y SE REEMPLAZO TOMA | C23011600277 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1061 | 2023-01-16 | 7427 | keep | 0 | Jan | 2023 | 0.0050585 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-01-16 17:36 | 2023-01-16 19:37 | 50 | 2:01 | P | NO SE REPORTO CAUSA | 3 X 100 EN C/L NO CAUSA | S23011600446 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2023-01-16 | 6050 | keep | 0 | Jan | 2023 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-01-16 18:20 | 2023-01-16 19:50 | 75 | 1:30 | P | DESGANCHE | 2 X 50 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P23011600392 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-01-16 | 6750 | keep | 0 | Jan | 2023 | 0.0045974 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-01-16 18:25 | 2023-01-16 20:46 | 200 | 2:21 | P | NO SE REPORTO CAUSA | SE REMPLAZO SMU20 20 AMP NO CAUSA | S23011600452 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2023-01-16 | 28200 | keep | 0 | Jan | 2023 | 0.019207 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-01-16 19:02 | 2023-01-17 07:30 | 40 | 12:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | C23011600204 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 748 | 2023-01-16 | 29920 | keep | 0 | Jan | 2023 | 0.020378 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-16 19:09 | 2023-01-16 19:46 | 4027 | 0:37 | T | ARBOL SOBRE LINEA | SE SECCIONALIZO ALIMENTADOR 60% EN SERVICIO | B23011600217 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 37 | 2023-01-16 | 148999 | keep | 0 | Jan | 2023 | 0.10148 | 0.0027428 | Sustained | FALSE | FALSE | Not_TMED_Event | 4027
BAYAMON | 2023-01-16 19:13 | 2023-01-16 21:15 | 40 | 2:02 | P | NO SE REPORTO CAUSA | 2 X 30 EN RISER 1 X 65 EN C/L NO CAUSA | S23011600457 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2023-01-16 | 4880 | keep | 0 | Jan | 2023 | 0.0033237 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-01-16 19:42 | 2023-01-16 21:18 | 7 | 1:36 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR Y DESGANCHE | C23011600293 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 96 | 2023-01-16 | 672 | keep | 0 | Jan | 2023 | 0.0004577 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-01-16 19:46 | 2023-01-16 20:07 | 805 | 0:21 | P | ARBOL SOBRE LINEA | SE SECCIONALIZO ALIMENTADOR 20% ADICIONAL A PARA UN 80 % EN SERVICIO | B23011600217 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 21 | 2023-01-16 | 16905 | keep | 0 | Jan | 2023 | 0.011514 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-16 20:07 | 2023-01-16 21:21 | 800 | 1:14 | P | ARBOL SOBRE LINEA | SE LEVANTO LINEA PRIMARIA PARTIDA POR ARBOL Y SE CERRO LOS MACHETES 100%EN SERVICIO BY-230116-02 | B23011600217 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 74 | 2023-01-16 | 59200 | keep | 0 | Jan | 2023 | 0.040321 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-16 20:10 | 2023-01-16 22:39 | 145 | 2:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REMPLAZO AISLADOR | B23011600232 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 149 | 2023-01-16 | 21605 | keep | 0 | Jan | 2023 | 0.014715 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
BARRANQUITAS | 2023-01-16 20:17 | 2023-01-17 07:15 | 58 | 10:58 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23011600300 | New_Event | Vegetation Contact | Include | Include | Vegetation | 658 | 2023-01-16 | 38164 | keep | 0 | Jan | 2023 | 0.025993 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
HUMACAO | 2023-01-16 20:51 | 2023-01-17 00:13 | 165 | 3:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L REMPLAZO CAJA QUEMADA | C23011600306 | New_Event | Cutout Failure | Include | Include | Equipment | 202 | 2023-01-16 | 33330 | keep | 0 | Jan | 2023 | 0.022701 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
PONCE | 2023-01-16 21:11 | 2023-01-16 21:12 | 1650 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | P23011600415 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-01-16 | 1650 | keep | 0 | Jan | 2023 | 0.0011238 | 0.0011238 | Momentary | FALSE | FALSE | Not_TMED_Event | 1650
PONCE | 2023-01-16 21:12 | 2023-01-16 23:44 | 100 | 2:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CL FUERTES VIENTOS | P23011600417 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 152 | 2023-01-16 | 15200 | keep | 0 | Jan | 2023 | 0.010353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-16 22:30 | 2023-01-17 08:01 | 15 | 9:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23011600242 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 571 | 2023-01-16 | 8565 | keep | 0 | Jan | 2023 | 0.0058336 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-01-16 22:31 | 2023-01-17 05:02 | 31 | 6:31 | P | DESGANCHE | 1 X 50 EN C/L | R23011600188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 391 | 2023-01-16 | 12121 | keep | 0 | Jan | 2023 | 0.0082556 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-01-16 22:54 | 2023-01-16 23:05 | 3709 | 0:11 | T | CONDUCTOR ROTO O ABIERTO | SJ-230116-01 SE ABRE INTERRUPTOR POR CONDUCTOR VIVO EN EL SUELO SE SECCIONALIZA Y SE CIERRA POR SCADA 75% EN SERVICIO | S23011600495 | New_Event | Primary Wire Break | Include | Include | Equipment | 11 | 2023-01-16 | 40799 | keep | 0 | Jan | 2023 | 0.027788 | 0.0025262 | Sustained | FALSE | FALSE | Not_TMED_Event | 3709
AGUADILLA | 2023-01-16 23:01 | 2023-01-17 00:54 | 50 | 1:53 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23011600267 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-01-16 | 5650 | keep | 0 | Jan | 2023 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-16 23:05 | 2023-01-17 00:32 | 927 | 1:27 | P | CONDUCTOR ROTO O ABIERTO | SJ-230116-01 SE SUBIO PRIMARIA Y SE NORMALIZO GOI | S23011600495 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 87 | 2023-01-16 | 80649 | keep | 0 | Jan | 2023 | 0.05493 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-16 23:22 | 2023-01-17 07:15 | 40 | 7:53 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23011600337 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 473 | 2023-01-16 | 18920 | keep | 0 | Jan | 2023 | 0.012886 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-17 00:42 | 2023-01-17 06:04 | 6 | 5:22 | P | PARARRAYOS DEFECTUOSO | SE ELIMINO PARRARAYO Y 1 X 50 EN C/L | B23011700003 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 322 | 2023-01-17 | 1932 | keep | 0 | Jan | 2023 | 0.0013159 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-01-17 00:51 | 2023-01-17 03:27 | 131 | 2:36 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 EN EL SU - 4CA SU - 4CA REQUIERE MANTENIMIENTO | R23011700001 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 156 | 2023-01-17 | 20436 | keep | 0 | Jan | 2023 | 0.013919 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
FAJARDO | 2023-01-17 03:02 | 2023-01-17 03:03 | 3003 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2301170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-17 | 3003 | keep | 0 | Jan | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
VEGA BAJA | 2023-01-17 04:14 | 2023-01-17 04:15 | 4702 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | B2301170000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-17 | 4702 | keep | 0 | Jan | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-01-17 04:15 | 2023-01-17 12:42 | 8 | 8:27 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA A CAJA | B23011700005 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 507 | 2023-01-17 | 4056 | keep | 0 | Jan | 2023 | 0.0027625 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-01-17 04:33 | 2023-01-17 10:33 | 20 | 6:00 | P | DESGANCHE | DESGANCHE MASIVO 1 X 80 EN CORTE DE LINEA | P23011700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2023-01-17 | 7200 | keep | 0 | Jan | 2023 | 0.0049039 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-01-17 04:54 | 2023-01-17 08:00 | 30 | 3:06 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23011700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-01-17 | 5580 | keep | 0 | Jan | 2023 | 0.0038005 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-17 05:11 | 2023-01-17 10:00 | 2 | 4:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y 1 X 20 EN RISER SE REEMPLAZO PORTAFUSIBLE | R23011700008 | New_Event | Cutout Failure | Include | Include | Equipment | 289 | 2023-01-17 | 578 | keep | 0 | Jan | 2023 | 0.00039367 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-01-17 05:20 | 2023-01-17 09:30 | 50 | 4:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO CAJA PRIMARIA | R23011700009 | New_Event | Cutout Failure | Include | Include | Equipment | 250 | 2023-01-17 | 12500 | keep | 0 | Jan | 2023 | 0.0085137 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-01-17 05:28 | 2023-01-17 05:30 | 2179 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO CERRADO X CONTROL | R2301170000X | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-01-17 | 4358 | keep | 0 | Jan | 2023 | 0.0029682 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2023-01-17 05:30 | 2023-01-17 06:40 | 727 | 1:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO Y AISLADOR LASTIMADO EN RISER DE SALIDA | R23011700010 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 70 | 2023-01-17 | 50890 | keep | 0 | Jan | 2023 | 0.034661 | 0.00049516 | Sustained | FALSE | FALSE | Not_TMED_Event | 727
SAN JUAN | 2023-01-17 05:53 | 2023-01-17 11:06 | 25 | 5:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESPEJE LINEA | S23011700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2023-01-17 | 7825 | keep | 0 | Jan | 2023 | 0.0053296 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-01-17 06:12 | 2023-01-17 10:00 | 75 | 3:48 | P | DESGANCHE | DESGANCHE 2 X 50 EN CORTE DE LINEA | P23011700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-01-17 | 17100 | keep | 0 | Jan | 2023 | 0.011647 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-01-17 06:37 | 2023-01-17 08:36 | 6 | 1:59 | P | ANIMAL | 2 X 40 2 X 50 Y 1 X 65 EN C/L CRUCE X AVE | R23011700033 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-01-17 | 714 | keep | 0 | Jan | 2023 | 0.0004863 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-01-17 06:43 | 2023-01-17 10:00 | 15 | 3:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | A23011700002 | New_Event | Cutout Failure | Include | Include | Equipment | 197 | 2023-01-17 | 2955 | keep | 0 | Jan | 2023 | 0.0020126 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-01-17 07:04 | 2023-01-17 07:26 | 2 | 0:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P23011700015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 22 | 2023-01-17 | 44 | keep | 0 | Jan | 2023 | 2.9968e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-01-17 07:07 | 2023-01-17 20:13 | 4 | 13:06 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHANDO | C23011700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 786 | 2023-01-17 | 3144 | keep | 0 | Jan | 2023 | 0.0021414 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-01-17 07:20 | 2023-01-17 10:30 | 12 | 3:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P23011700018 | New_Event | Primary Wire Break | Include | Include | Equipment | 190 | 2023-01-17 | 2280 | keep | 0 | Jan | 2023 | 0.0015529 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-01-17 07:35 | 2023-01-17 15:30 | 8 | 7:55 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR REMPLAZO DE DOS POSTES SECUNDARIOS PARTIDOS | A23011700005 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 475 | 2023-01-17 | 3800 | keep | 0 | Jan | 2023 | 0.0025882 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-01-17 08:08 | 2023-01-17 09:26 | 20 | 1:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR VIENTOS | P23011700020 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 78 | 2023-01-17 | 1560 | keep | 0 | Jan | 2023 | 0.0010625 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-17 08:14 | 2023-01-17 10:24 | 10 | 2:10 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | S23011700016 | New_Event | Animals | Include | Include | Wildlife | 130 | 2023-01-17 | 1300 | keep | 0 | Jan | 2023 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-01-17 08:40 | 2023-01-17 11:25 | 30 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P23011700031 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-01-17 | 4950 | keep | 0 | Jan | 2023 | 0.0033714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-01-17 08:42 | 2023-01-17 13:32 | 55 | 4:50 | P | ANIMAL | 2 X 40 EN C/L CRUCE POR AVE | C23011700020 | New_Event | Animals | Include | Include | Wildlife | 290 | 2023-01-17 | 15950 | keep | 0 | Jan | 2023 | 0.010863 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
AGUADILLA | 2023-01-17 08:49 | 2023-01-17 14:05 | 7 | 5:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR QUEMADO DE 50KVA X MISMA CAPACIDAD | M23011700013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 316 | 2023-01-17 | 2212 | keep | 0 | Jan | 2023 | 0.0015066 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-01-17 08:50 | 2023-01-17 18:15 | 125 | 9:25 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO Y DESGANCHE | M23011700014 | New_Event | Primary Pole Failure | Include | Include | Equipment | 565 | 2023-01-17 | 70625 | keep | 0 | Jan | 2023 | 0.048102 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
VEGA BAJA | 2023-01-17 08:50 | 2023-01-17 10:51 | 130 | 2:01 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA Y 1 X 100 EN C/L | B23011700022 | New_Event | Primary Pole Failure | Include | Include | Equipment | 121 | 2023-01-17 | 15730 | keep | 0 | Jan | 2023 | 0.010714 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
MAYAGÃœEZ | 2023-01-17 08:51 | 2023-01-17 13:51 | 20 | 5:00 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M23011700016 | New_Event | Primary Wire Break | Include | Include | Equipment | 300 | 2023-01-17 | 6000 | keep | 0 | Jan | 2023 | 0.0040866 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-01-17 09:02 | 2023-01-17 09:03 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23011700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-17 | 990 | keep | 0 | Jan | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
ARECIBO | 2023-01-17 09:08 | 2023-01-17 10:14 | 5 | 1:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | A23011700024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2023-01-17 | 330 | keep | 0 | Jan | 2023 | 0.00022476 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-01-17 09:15 | 2023-01-17 17:28 | 79 | 8:13 | P | DESGANCHE | SE ABRIO C/L SE REALIZO DESGANCHE Y SE CERRO C/L | C23011700033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2023-01-17 | 38947 | keep | 0 | Jan | 2023 | 0.026527 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BARRANQUITAS | 2023-01-17 09:21 | 2023-01-17 13:00 | 7 | 3:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50KVA POR UNO 50 KVA | C23011700034 | New_Event | Service Transformer Failure | Include | Include | Equipment | 219 | 2023-01-17 | 1533 | keep | 0 | Jan | 2023 | 0.0010441 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-01-17 09:24 | 2023-01-17 11:52 | 431 | 2:28 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23011700036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-01-17 | 63788 | keep | 0 | Jan | 2023 | 0.043446 | 0.00029355 | Sustained | FALSE | FALSE | Not_TMED_Event | 431
MAYAGÃœEZ | 2023-01-17 09:28 | 2023-01-17 13:00 | 5 | 3:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 5 EN TRANSFORMADOR SE REPARO SECUNADRIA PARTIDA | M23011700023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 212 | 2023-01-17 | 1060 | keep | 0 | Jan | 2023 | 0.00072196 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-01-17 09:35 | 2023-01-17 10:38 | 3718 | 1:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR. INDICA HECTOR MACHADO QUE SE SAFA BAJANTE DE CAJA PRIMARIA DE CORTE DE LINEA Y CRUZA CON CRUCETA DISPARANDO EL INTERRUPTOR | P23011700054 | New_Event | Primary Wire Break | Include | Include | Equipment | 63 | 2023-01-17 | 234234 | keep | 0 | Jan | 2023 | 0.15954 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
VEGA BAJA | 2023-01-17 09:45 | 2023-01-17 14:23 | 6 | 4:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO | B23011700038 | New_Event | Primary Pole Failure | Include | Include | Equipment | 278 | 2023-01-17 | 1668 | keep | 0 | Jan | 2023 | 0.0011361 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-01-17 09:45 | 2023-01-17 14:23 | 2 | 4:38 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REPARO CRUCETA PARTIDA | B23011700025 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 278 | 2023-01-17 | 556 | keep | 0 | Jan | 2023 | 0.00037869 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-01-17 09:57 | 2023-01-17 11:00 | 2 | 1:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23011700034 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 63 | 2023-01-17 | 126 | keep | 0 | Jan | 2023 | 8.5818e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-01-17 10:09 | 2023-01-17 12:16 | 65 | 2:07 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | S23011700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-01-17 | 8255 | keep | 0 | Jan | 2023 | 0.0056224 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2023-01-17 10:17 | 2023-01-17 17:34 | 5 | 7:17 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L Y SE REMPLAZO POSTE SECUNDARIO | C23011700059 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 437 | 2023-01-17 | 2185 | keep | 0 | Jan | 2023 | 0.0014882 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-01-17 10:21 | 2023-01-17 12:35 | 17 | 2:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 75 KVA X 75 KVA | R23011700051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 134 | 2023-01-17 | 2278 | keep | 0 | Jan | 2023 | 0.0015515 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-01-17 10:30 | 2023-01-17 11:30 | 8 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTORES SECUNDARIO | S22011600387 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-01-17 | 480 | keep | 0 | Jan | 2023 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-17 10:31 | 2023-01-17 17:04 | 5 | 6:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 65 EN CORTE DE LINEA Y SE ABRIO XMR PARA REPARAR SECUNDARIA QUEMADA | S23011700037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 393 | 2023-01-17 | 1965 | keep | 0 | Jan | 2023 | 0.0013384 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-17 10:35 | 2023-01-17 13:24 | 1 | 2:49 | P | NO SE REPORTO CAUSA | 1 X 200 EN RISER | S23011700039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2023-01-17 | 169 | keep | 0 | Jan | 2023 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-17 10:40 | 2023-01-17 13:20 | 50 | 2:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23011700045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-01-17 | 8000 | keep | 0 | Jan | 2023 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-01-17 10:46 | 2023-01-17 10:47 | 934 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36400 | A23011700055 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-17 | 934 | keep | 0 | Jan | 2023 | 0.00063614 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2023-01-17 10:46 | 2023-01-17 10:47 | 4 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36400 | A23011700055 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-17 | 4 | keep | 0 | Jan | 2023 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-01-17 10:46 | 2023-01-17 10:47 | 1479 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36400 | A23011700055 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-17 | 1479 | keep | 0 | Jan | 2023 | 0.0010073 | 0.0010073 | Momentary | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2023-01-17 10:46 | 2023-01-17 10:47 | 1841 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36400 | A23011700056 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-17 | 1841 | keep | 0 | Jan | 2023 | 0.0012539 | 0.0012539 | Momentary | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2023-01-17 10:46 | 2023-01-17 10:47 | 1950 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36400 | A23011700056 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-17 | 1950 | keep | 0 | Jan | 2023 | 0.0013281 | 0.0013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 1950
UTUADO | 2023-01-17 10:51 | 2023-01-17 14:20 | 40 | 3:29 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23011700050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-01-17 | 8360 | keep | 0 | Jan | 2023 | 0.005694 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-01-17 11:07 | 2023-01-17 11:08 | 3076 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23011700055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-17 | 3076 | keep | 0 | Jan | 2023 | 0.002095 | 0.002095 | Momentary | FALSE | FALSE | Not_TMED_Event | 3076
AGUADILLA | 2023-01-17 11:15 | 2023-01-17 15:50 | 10 | 4:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A23011700043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 275 | 2023-01-17 | 2750 | keep | 0 | Jan | 2023 | 0.001873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-17 11:18 | 2023-01-17 11:19 | 3597 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | B2301170000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-17 | 3597 | keep | 0 | Jan | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-01-17 11:19 | 2023-01-17 13:20 | 650 | 2:01 | P | ANIMAL | 1 X 100 EN C/L Y 1 X 50 EN C/L CRUCE X AVE | B23011700062 | 1st_after_momentary | Animals | Include | Include | Wildlife | 121 | 2023-01-17 | 78650 | keep | 0 | Jan | 2023 | 0.053568 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
SAN JUAN | 2023-01-17 11:31 | 2023-01-17 13:16 | 8 | 1:45 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S23011700051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2023-01-17 | 840 | keep | 0 | Jan | 2023 | 0.00057212 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-17 11:32 | 2023-01-17 12:42 | 25 | 1:10 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23011700063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-01-17 | 1750 | keep | 0 | Jan | 2023 | 0.0011919 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-01-17 11:36 | 2023-01-17 13:42 | 1 | 2:06 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | C23011700083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-01-17 | 126 | keep | 0 | Jan | 2023 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-17 11:40 | 2023-01-17 14:41 | 116 | 3:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CONVERTIDOR Y SE REEMPLAZO CAJA PRIMARIA | R23011700059 | New_Event | Cutout Failure | Include | Include | Equipment | 181 | 2023-01-17 | 20996 | keep | 0 | Jan | 2023 | 0.0143 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
YAUCO | 2023-01-17 11:47 | 2023-01-17 15:15 | 75 | 3:28 | P | CAUSAS EXTERNAS | 1 X 80 EN CORE DE LINEA CAMION IMPACTO POSTE Y CRUZARON FASES | P23011700084 | New_Event | Damage From Public | Include | Include | Public | 208 | 2023-01-17 | 15600 | keep | 0 | Jan | 2023 | 0.010625 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-01-17 11:53 | 2023-01-17 15:00 | 2 | 3:07 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | M23011700038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2023-01-17 | 374 | keep | 0 | Jan | 2023 | 0.00025473 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-01-17 11:58 | 2023-01-17 14:30 | 20 | 2:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE DESPEJO LINEA | S23011700054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-01-17 | 3040 | keep | 0 | Jan | 2023 | 0.0020705 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-17 12:05 | 2023-01-17 14:03 | 28 | 1:58 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L Y 1 X 80 EN C/L | B23011700076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2023-01-17 | 3304 | keep | 0 | Jan | 2023 | 0.0022503 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2023-01-17 12:23 | 2023-01-17 12:24 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2301170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-17 | 3070 | keep | 0 | Jan | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-01-17 12:46 | 2023-01-17 14:51 | 15 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO BAJANTE SECUNDARIO | S23011700058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2023-01-17 | 1875 | keep | 0 | Jan | 2023 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-01-17 12:50 | 2023-01-17 15:15 | 4 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA Y BAJANTE SECUNDARIO | R23011700072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-01-17 | 580 | keep | 0 | Jan | 2023 | 0.00039504 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2023-01-17 12:51 | 2023-01-17 13:46 | 25 | 0:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR VIENTOS | P23011700094 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 55 | 2023-01-17 | 1375 | keep | 0 | Jan | 2023 | 0.00093651 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-01-17 12:59 | 2023-01-17 19:05 | 3 | 6:06 | P | TRANSFORMADOR AVERIADO | XMR PROBO MALO. SE PASO LA CARGA A OTRO XMR | C23011700093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 366 | 2023-01-17 | 1098 | keep | 0 | Jan | 2023 | 0.00074784 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-01-17 13:44 | 2023-01-17 14:14 | 4 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARO SECUNDARIO | C23011700101 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-01-17 | 120 | keep | 0 | Jan | 2023 | 8.1731e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-01-17 13:47 | 2023-01-17 16:38 | 5 | 2:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON BAJANTES SECUNDARIOS EN TRANSFORMADOR | P23011600236 | New_Event | Secondary Wire Break | Include | Include | Equipment | 171 | 2023-01-17 | 855 | keep | 0 | Jan | 2023 | 0.00058234 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-01-17 13:54 | 2023-01-18 08:03 | 29 | 18:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C23011700103 | New_Event | Cutout Failure | Include | Include | Equipment | 1089 | 2023-01-17 | 31581 | keep | 0 | Jan | 2023 | 0.02151 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
YAUCO | 2023-01-17 14:40 | 2023-01-17 17:08 | 35 | 2:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P23011700110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-01-17 | 5180 | keep | 0 | Jan | 2023 | 0.0035281 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2023-01-17 14:41 | 2023-01-17 16:08 | 80 | 1:27 | P | DESGANCHE | 1 X 50 CL DESGANCHE | M23011700070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2023-01-17 | 6960 | keep | 0 | Jan | 2023 | 0.0047404 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-01-17 15:09 | 2023-01-17 17:50 | 10 | 2:41 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 2 X 5 EN TRANSFORMADOR SE RETIRA TOMA SECUNDARIA CRUZADA EN CONDULETO DE CASA ABANDONADA | M23011700074 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 161 | 2023-01-17 | 1610 | keep | 0 | Jan | 2023 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-17 15:25 | 2023-01-17 15:50 | 11 | 0:25 | P | PROBLEMA DEL CLIENTE | SE ABRE TRANSFORMADOR PARA CONECTAR LINEA SECUNDARIA SOTERRADA | P23011700116 | New_Event | Customer-Related Interruption | Include | Include | Public | 25 | 2023-01-17 | 275 | keep | 0 | Jan | 2023 | 0.0001873 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2023-01-17 15:38 | 2023-01-17 17:48 | 30 | 2:10 | P | DESGANCHE | 1 X 50 CL DESGANCHE | M23011700083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-01-17 | 3900 | keep | 0 | Jan | 2023 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-01-17 15:44 | 2023-01-17 17:48 | 10 | 2:04 | P | DESGANCHE | 1 X 5 EN TRANSFORMADOR SE HIZO DESGANCHE | P23011700119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-01-17 | 1240 | keep | 0 | Jan | 2023 | 0.00084456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-17 15:59 | 2023-01-17 16:30 | 1 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO DE XMR Y SE REPARO CONECTORES DE BAJANTE SECUNDARIO | B23011700100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2023-01-17 | 31 | keep | 0 | Jan | 2023 | 2.1114e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-17 16:10 | 2023-01-17 17:44 | 12 | 1:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA | B23011700110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 94 | 2023-01-17 | 1128 | keep | 0 | Jan | 2023 | 0.00076828 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-01-17 16:18 | 2023-01-17 20:35 | 75 | 4:17 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE SECCIONALIZO POSTE Y CRUCETAS PARTIDAS SE REPARO LINEA PRIMARIA PARTIDA | A23011700109 | New_Event | Primary Pole Failure | Include | Include | Equipment | 257 | 2023-01-17 | 19275 | keep | 0 | Jan | 2023 | 0.013128 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-01-17 16:20 | 2023-01-17 19:23 | 20 | 3:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011700111 | New_Event | Secondary Wire Break | Include | Include | Equipment | 183 | 2023-01-17 | 3660 | keep | 0 | Jan | 2023 | 0.0024928 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-01-17 16:25 | 2023-01-17 16:29 | 1572 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1658-14 LLEVA 70% 1658-13 | R2301170000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-01-17 | 6288 | keep | 0 | Jan | 2023 | 0.0042827 | 0.0010707 | Momentary | FALSE | FALSE | Not_TMED_Event | 1572
CANOVANAS | 2023-01-17 16:25 | 2023-01-17 16:29 | 1 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE BKR LLEVA 70% 1658-13 | R2301170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-01-17 | 4 | keep | 0 | Jan | 2023 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-17 16:36 | 2023-01-17 16:37 | 1352 | 0:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23011700094 | New_Event | Other Causes | Include | Include | Other | 1 | 2023-01-17 | 1352 | keep | 0 | Jan | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-01-17 16:37 | 2023-01-17 16:38 | 871 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23011700094 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-17 | 871 | keep | 0 | Jan | 2023 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2023-01-17 16:40 | 2023-01-17 18:25 | 20 | 1:45 | P | NO SE REPORTO CAUSA | 1 X 10 TRANSFORMADOR NO SE ENCONTRO CAUSA | M23011700096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2023-01-17 | 2100 | keep | 0 | Jan | 2023 | 0.0014303 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-17 16:40 | 2023-01-17 18:20 | 12 | 1:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A23011700114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-01-17 | 1200 | keep | 0 | Jan | 2023 | 0.00081731 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-01-17 16:41 | 2023-01-17 18:06 | 51 | 1:25 | P | NO SE REPORTO CAUSA | 2 X 140 EN C/L | R23011700096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2023-01-17 | 4335 | keep | 0 | Jan | 2023 | 0.0029525 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
BAYAMON | 2023-01-17 17:12 | 2023-01-17 17:49 | 17 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REGULO DEL 4 AL 3 121V POR FASE SE REPARARON CONECTORES DE BAJANTE SECUNDARIO | B23011700121 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-01-17 | 629 | keep | 0 | Jan | 2023 | 0.00042841 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-01-17 17:20 | 2023-01-17 18:06 | 4 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO BAJANTE SECUNDARIO Y CONECTORES QUEMADOS | S23011700094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2023-01-17 | 184 | keep | 0 | Jan | 2023 | 0.00012532 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-01-17 17:29 | 2023-01-17 17:32 | 635 | 0:03 | T | ALIMENTADOR AMARRADO | SE ABRIO BKR 2305-04 QUE LLEVABA LAS CARGAS DE LA 2306-00 PARA NORMLAIZAR LAS CARGAS DE LA PORTATIL #20 DEBIDO A QUE NO FASEABAN. SE REEMPLAZARON PT'S EN PORTATIL #20 Y SE REEMPLAZO MACHETE QUEMADO EN EL 2306-01. | R23011700108 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-17 | 1905 | keep | 0 | Jan | 2023 | 0.0012975 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2023-01-17 17:29 | 2023-01-17 17:32 | 3766 | 0:03 | T | PROTECCION DEFECTUOSA | SE ABRIO BKR 2305-04 QUE LLEVABA LAS CARGAS DE LA 2306-00 PARA NORMLAIZAR LAS CARGAS DE LA PORTATIL #20 DEBIDO A QUE NO FASEABAN. SE REEMPLAZARON PT'S EN PORTATIL #20 Y SE REEMPLAZO MACHETE QUEMADO EN EL 2306-01. | R23011700108 | New_Event | Protection Miscoordination | Include | Include | Other | 3 | 2023-01-17 | 11298 | keep | 0 | Jan | 2023 | 0.007695 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
CANOVANAS | 2023-01-17 17:29 | 2023-01-17 17:32 | 1380 | 0:03 | T | PROTECCION DEFECTUOSA | SE ABRIO BKR 2305-04 QUE LLEVABA LAS CARGAS DE LA 2306-00 PARA NORMLAIZAR LAS CARGAS DE LA PORTATIL #20 DEBIDO A QUE NO FASEABAN. SE REEMPLAZARON PT'S EN PORTATIL #20 Y SE REEMPLAZO MACHETE QUEMADO EN EL 2306-01. | R23011700108 | New_Event | Protection Miscoordination | Include | Include | Other | 3 | 2023-01-17 | 4140 | keep | 0 | Jan | 2023 | 0.0028197 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
VEGA BAJA | 2023-01-17 17:35 | 2023-01-17 18:50 | 7 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23010800014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-01-17 | 525 | keep | 0 | Jan | 2023 | 0.00035758 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-01-17 17:43 | 2023-01-17 18:39 | 10 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011700124 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2023-01-17 | 560 | keep | 0 | Jan | 2023 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-17 18:07 | 2023-01-17 20:00 | 75 | 1:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23011700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-01-17 | 8475 | keep | 0 | Jan | 2023 | 0.0057723 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2023-01-17 18:21 | 2023-01-18 11:30 | 11 | 17:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO 2 CAJAS PRIMARIAS EN CORTES DE LINEA | C23011700134 | New_Event | Cutout Failure | Include | Include | Equipment | 1029 | 2023-01-17 | 11319 | keep | 0 | Jan | 2023 | 0.0077093 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-01-17 18:26 | 2023-01-17 19:09 | 10 | 0:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTORES DE BAJANTE SECUNDARIO | B23011700127 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2023-01-17 | 430 | keep | 0 | Jan | 2023 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-17 18:37 | 2023-01-17 18:38 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2301170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-17 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-01-17 18:46 | 2023-01-17 20:50 | 100 | 2:04 | P | DESGANCHE | 1 X 100 EN CL SE REALIZO DESGANCHE | M23011700109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-01-17 | 12400 | keep | 0 | Jan | 2023 | 0.0084456 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-17 18:53 | 2023-01-17 23:00 | 25 | 4:07 | P | NO SE REPORTO CAUSA | 1 X 20 TIPO NX EN SU SHOPPING | B23011700128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2023-01-17 | 6175 | keep | 0 | Jan | 2023 | 0.0042058 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-17 18:55 | 2023-01-17 21:49 | 10 | 2:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | PORTAFUSIBLE 1 X 20 TRANSFORMADOR | S23011700103 | New_Event | Cutout Failure | Include | Include | Equipment | 174 | 2023-01-17 | 1740 | keep | 0 | Jan | 2023 | 0.0011851 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-17 19:21 | 2023-01-17 19:46 | 10 | 0:25 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE PRIMARIO | R23011700116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2023-01-17 | 250 | keep | 0 | Jan | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-17 19:22 | 2023-01-17 19:23 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R23011700117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-17 | 4188 | keep | 0 | Jan | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
PONCE | 2023-01-17 20:31 | 2023-01-18 18:30 | 70 | 21:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | P23011700141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1319 | 2023-01-17 | 92330 | keep | 0 | Jan | 2023 | 0.062886 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-01-17 20:35 | 2023-01-17 23:16 | 25 | 2:41 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE Y CRUCETAS PARTIDAS SE REPARO PUENTES PRIMARIOS | A23011700109 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 161 | 2023-01-17 | 4025 | keep | 0 | Jan | 2023 | 0.0027414 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-01-17 21:02 | 2023-01-17 23:40 | 20 | 2:38 | P | DESCONECTIVO DEFECTUOSO | SE CIERRAN MACHETES DE AMARRE N/O 4101-01 & 4101-04 Y SE ABREN MACHETES QUEMADO QUEDANDO TODOS LOS CLIENTES EN SERVICIO | P23011700146 | New_Event | Switch Failure | Include | Include | Equipment | 158 | 2023-01-17 | 3160 | keep | 0 | Jan | 2023 | 0.0021523 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-01-17 21:23 | 2023-01-17 22:32 | 250 | 1:09 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA ENERGIZADA EN EL SUELO SE ABRE INTERRUPTOR GOI PC-230117-01A | P23011700153 | New_Event | Primary Wire Break | Include | Include | Equipment | 69 | 2023-01-17 | 17250 | keep | 0 | Jan | 2023 | 0.011749 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
PONCE | 2023-01-17 22:32 | 2023-01-17 22:50 | 5063 | 0:18 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA SECCIONALIZAR AVERIA Y SE COLOCO INTERRUPTOR EN SERVICIO GOI PC-230117-01A | P23011700153 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 18 | 2023-01-17 | 91134 | keep | 0 | Jan | 2023 | 0.062071 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-01-17 22:50 | 2023-01-17 23:38 | 1842 | 0:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA LINEA PRIMARIA Y SE CIERRA MACHETES GOI PC-230117-01A | P23011700153 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 48 | 2023-01-17 | 88416 | keep | 0 | Jan | 2023 | 0.06022 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-01-18 00:11 | 2023-01-18 01:36 | 29 | 1:25 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO OPERO POR SCADA SE CERRO MANUAL ELECTRICAMENTE | P23011800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2023-01-18 | 2465 | keep | 0 | Jan | 2023 | 0.0016789 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CAGUAS | 2023-01-18 02:10 | 2023-01-18 02:11 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23011800002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 476 | keep | 0 | Jan | 2023 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-01-18 02:10 | 2023-01-18 02:11 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23011800002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 1655 | keep | 0 | Jan | 2023 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-01-18 02:10 | 2023-01-18 02:11 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23011800002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 361 | keep | 0 | Jan | 2023 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-01-18 02:10 | 2023-01-18 02:11 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23011800002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 2842 | keep | 0 | Jan | 2023 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-01-18 02:10 | 2023-01-18 02:11 | 1702 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23011800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 1702 | keep | 0 | Jan | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-01-18 02:10 | 2023-01-18 02:11 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23011800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 918 | keep | 0 | Jan | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-01-18 02:10 | 2023-01-18 02:11 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23011800004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 1725 | keep | 0 | Jan | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
BAYAMON | 2023-01-18 02:30 | 2023-01-18 03:08 | 5 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIAS | B23011700133 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2023-01-18 | 190 | keep | 0 | Jan | 2023 | 0.00012941 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-01-18 03:20 | 2023-01-18 03:21 | 1478 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23011800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-18 | 1478 | keep | 0 | Jan | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
BAYAMON | 2023-01-18 03:47 | 2023-01-18 06:28 | 78 | 2:41 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23011800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-01-18 | 12558 | keep | 0 | Jan | 2023 | 0.0085532 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
CAGUAS | 2023-01-18 04:50 | 2023-01-18 06:45 | 20 | 1:55 | P | ALIMENTADOR AMARRADO | 1 X 50 EN CORTE DE LINEA | C23011800005 | New_Event | Feeder Load Transferred | Include | Include | Other | 115 | 2023-01-18 | 2300 | keep | 0 | Jan | 2023 | 0.0015665 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-01-18 05:00 | 2023-01-18 05:01 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23011800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-18 | 1648 | keep | 0 | Jan | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-01-18 05:01 | 2023-01-18 10:38 | 12 | 5:37 | P | NO SE REPORTO CAUSA | 1 X50 EN C/L | R23011800005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 337 | 2023-01-18 | 4044 | keep | 0 | Jan | 2023 | 0.0027543 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-01-18 05:10 | 2023-01-18 08:26 | 70 | 3:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23011800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2023-01-18 | 13720 | keep | 0 | Jan | 2023 | 0.0093446 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2023-01-18 05:31 | 2023-01-18 09:25 | 107 | 3:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE Y ENDERZO CAJA PRIMARIA | C23011800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2023-01-18 | 25038 | keep | 0 | Jan | 2023 | 0.017053 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
PONCE | 2023-01-18 07:06 | 2023-01-18 09:11 | 1979 | 2:05 | S | DISPARO DE BARRA DE TRANSMISION | SE PUSO EN SERVICIO RING BOX Y SE DEVOLVIERON LAS CARGAS. APARENTA HABER SIDO CAUSADO POR MALA OPERACION DE LAS PROTECCIONES DE CEMEX | P23011800026 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 125 | 2023-01-18 | 247375 | keep | 0 | Jan | 2023 | 0.16849 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2023-01-18 07:06 | 2023-01-18 09:11 | 3114 | 2:05 | S | DISPARO DE BARRA DE TRANSMISION | SE PUSO EN SERVICIO RING BOX Y SE DEVOLVIERON LAS CARGAS. APARENTA HABER SIDO CAUSADO POR MALA OPERACION DE LAS PROTECCIONES DE CEMEX | P23011800026 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 125 | 2023-01-18 | 389250 | keep | 0 | Jan | 2023 | 0.26512 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2023-01-18 07:06 | 2023-01-18 09:11 | 5069 | 2:05 | S | DISPARO DE BARRA DE TRANSMISION | SE PUSO EN SERVICIO RING BOX Y SE DEVOLVIERON LAS CARGAS. APARENTA HABER SIDO CAUSADO POR MALA OPERACION DE LAS PROTECCIONES DE CEMEX | P23011800026 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 125 | 2023-01-18 | 633625 | keep | 0 | Jan | 2023 | 0.43156 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2023-01-18 07:06 | 2023-01-18 09:11 | 2696 | 2:05 | S | DISPARO DE BARRA DE TRANSMISION | SE PUSO EN SERVICIO RING BOX Y SE DEVOLVIERON LAS CARGAS. APARENTA HABER SIDO CAUSADO POR MALA OPERACION DE LAS PROTECCIONES DE CEMEX | P23011800026 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 125 | 2023-01-18 | 337000 | keep | 0 | Jan | 2023 | 0.22953 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2023-01-18 07:06 | 2023-01-18 09:11 | 5063 | 2:05 | S | DISPARO DE BARRA DE TRANSMISION | SE PUSO EN SERVICIO RING BOX Y SE DEVOLVIERON LAS CARGAS. APARENTA HABER SIDO CAUSADO POR MALA OPERACION DE LAS PROTECCIONES DE CEMEX | P23011800026 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 125 | 2023-01-18 | 632875 | keep | 0 | Jan | 2023 | 0.43105 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
YAUCO | 2023-01-18 07:20 | 2023-01-18 13:57 | 4 | 6:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y SE REPARO LINEA SECUNDARIA | P23011800031 | New_Event | Cutout Failure | Include | Include | Equipment | 397 | 2023-01-18 | 1588 | keep | 0 | Jan | 2023 | 0.0010816 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-01-18 07:28 | 2023-01-18 11:00 | 15 | 3:32 | P | ANIMAL | 1 X 20 EN RISER CRUCE POR AVE | S23011800004 | New_Event | Animals | Include | Include | Wildlife | 212 | 2023-01-18 | 3180 | keep | 0 | Jan | 2023 | 0.0021659 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 1222 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 1222 | keep | 0 | Jan | 2023 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 2756 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 2756 | keep | 0 | Jan | 2023 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 2833 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 2833 | keep | 0 | Jan | 2023 | 0.0019295 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 1218 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 1218 | keep | 0 | Jan | 2023 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 1345 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 1345 | keep | 0 | Jan | 2023 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 1265 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 1265 | keep | 0 | Jan | 2023 | 0.00086159 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 2071 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 2071 | keep | 0 | Jan | 2023 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 760 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 760 | keep | 0 | Jan | 2023 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 509 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 509 | keep | 0 | Jan | 2023 | 0.00034668 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 2620 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 2620 | keep | 0 | Jan | 2023 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2023-01-18 07:28 | 2023-01-18 07:29 | 1916 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23011800010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-18 | 1916 | keep | 0 | Jan | 2023 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
SAN JUAN | 2023-01-18 07:37 | 2023-01-18 07:39 | 1106 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE PROBO POR CONTROL QUEDO EN SERVICIO | S23011800007 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-18 | 2212 | keep | 0 | Jan | 2023 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-01-18 07:37 | 2023-01-18 07:39 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE PROBO POR CONTROL QUEDO EN SERVICIO | S23011800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-18 | 3604 | keep | 0 | Jan | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
FAJARDO | 2023-01-18 07:39 | 2023-01-18 08:05 | 10 | 0:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO PORTAFUSIBLE Y 1 X 10 EN XMR | R23011800006 | New_Event | Cutout Failure | Include | Include | Equipment | 26 | 2023-01-18 | 260 | keep | 0 | Jan | 2023 | 0.00017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-18 08:11 | 2023-01-18 09:40 | 1 | 1:29 | P | ANIMAL | 2 X 10 EN MONTURA DE XMR CRUCE POR AVE | B23011800010 | New_Event | Animals | Include | Include | Wildlife | 89 | 2023-01-18 | 89 | keep | 0 | Jan | 2023 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-18 08:23 | 2023-01-18 09:53 | 11 | 1:30 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23011800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-01-18 | 990 | keep | 0 | Jan | 2023 | 0.00067428 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-01-18 08:37 | 2023-01-18 13:36 | 12 | 4:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN XMR Y SE REEMPLAZO PORTAFUSIBLE | S23011800019 | New_Event | Cutout Failure | Include | Include | Equipment | 299 | 2023-01-18 | 3588 | keep | 0 | Jan | 2023 | 0.0024438 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-01-18 08:41 | 2023-01-18 08:42 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23011800068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-18 | 4279 | keep | 0 | Jan | 2023 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
AGUADILLA | 2023-01-18 08:55 | 2023-01-18 15:46 | 2 | 6:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE | A23011800044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 411 | 2023-01-18 | 822 | keep | 0 | Jan | 2023 | 0.00055986 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-01-18 09:11 | 2023-01-18 11:04 | 4 | 1:53 | P | SECUNDARIA/OTROS | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR AISLACION SECUNDARIA | M23011800011 | New_Event |  |  |  |  | 113 | 2023-01-18 | 452 | keep | 0 | Jan | 2023 | 0.00030786 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-01-18 09:35 | 2023-01-18 10:30 | 12 | 0:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50 KVA X 50 KVA | R23011800014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 55 | 2023-01-18 | 660 | keep | 0 | Jan | 2023 | 0.00044952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-01-18 09:36 | 2023-01-18 10:39 | 20 | 1:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23011800103 | New_Event | Primary Wire Break | Include | Include | Equipment | 63 | 2023-01-18 | 1260 | keep | 0 | Jan | 2023 | 0.00085818 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-01-18 09:56 | 2023-01-18 13:53 | 1 | 3:57 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | R23011800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2023-01-18 | 237 | keep | 0 | Jan | 2023 | 0.00016142 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-01-18 09:56 | 2023-01-18 11:39 | 8 | 1:43 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA POR AVE | P23011800115 | New_Event | Animals | Include | Include | Wildlife | 103 | 2023-01-18 | 824 | keep | 0 | Jan | 2023 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-18 10:03 | 2023-01-18 17:15 | 15 | 7:12 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y RELOCALIZO SECUNDARIA Y SE HIZO DESGANCHE | S23011800027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 432 | 2023-01-18 | 6480 | keep | 0 | Jan | 2023 | 0.0044135 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-01-18 10:03 | 2023-01-18 18:35 | 104 | 8:32 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE RECLOSER PARA CAMBIO DE POSTE PARTIDO CONTINUACIOPN DEL DIA 16 | M23011800033 | New_Event | Primary Pole Failure | Include | Include | Equipment | 512 | 2023-01-18 | 53248 | keep | 0 | Jan | 2023 | 0.036267 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
ARECIBO | 2023-01-18 10:20 | 2023-01-18 12:52 | 1222 | 2:32 | S | NO SE REPORTO CAUSA | SE REMPLAZO FUSIBLE FUNDIDO 38KV FASE B | A23011800090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2023-01-18 | 185744 | keep | 0 | Jan | 2023 | 0.12651 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2023-01-18 10:20 | 2023-01-18 12:52 | 2756 | 2:32 | S | NO SE REPORTO CAUSA | SE REMPLAZO FUSIBLE FUNDIDO 38KV FASE B | A23011800090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2023-01-18 | 418912 | keep | 0 | Jan | 2023 | 0.28532 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2023-01-18 10:20 | 2023-01-18 12:52 | 2833 | 2:32 | S | LINEA DE TRANSMISION 38KV | SE REMPLAZO FUSIBLE FUNDIDO 38KV FASE B | A23011800090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2023-01-18 | 430616 | keep | 0 | Jan | 2023 | 0.29329 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
SAN JUAN | 2023-01-18 10:31 | 2023-01-18 10:32 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2301180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-18 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-01-18 10:36 | 2023-01-18 19:40 | 20 | 9:04 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO POSTE PRIMARIO | B23011800037 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 544 | 2023-01-18 | 10880 | keep | 0 | Jan | 2023 | 0.0074103 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-01-18 10:59 | 2023-01-18 13:15 | 164 | 2:16 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P23011800138 | New_Event | Animals | Include | Include | Wildlife | 136 | 2023-01-18 | 22304 | keep | 0 | Jan | 2023 | 0.015191 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2023-01-18 11:16 | 2023-01-18 14:30 | 20 | 3:14 | P | DESGANCHE | 1 X 65 EN C/L SE RETIRO RAMA DE LA LINEA | S23011800039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-01-18 | 3880 | keep | 0 | Jan | 2023 | 0.0026427 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-18 11:16 | 2023-01-18 13:04 | 56 | 1:48 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23011800046 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-01-18 | 6048 | keep | 0 | Jan | 2023 | 0.0041193 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
GUAYAMA | 2023-01-18 11:33 | 2023-01-18 14:27 | 60 | 2:54 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P23011800149 | New_Event | Animals | Include | Include | Wildlife | 174 | 2023-01-18 | 10440 | keep | 0 | Jan | 2023 | 0.0071106 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-18 11:37 | 2023-01-18 11:39 | 60 | 0:02 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR PARA ABRIR AMARRE CON EL 10% DEL 1420-03 PARA SECCIONALIZAR Y REMPLAZAR MACHETE Y PARARRAYO DEL 1420-03 | S2301130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-18 | 120 | keep | 0 | Jan | 2023 | 8.1731e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-18 11:37 | 2023-01-18 12:23 | 55 | 0:46 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 1420-02 PARA ROMPER AMARRE CONTRA 10% 1420-03 Y ESTA CARGA SE PASO AL 1420-04 POR MACHETES QUEMADOS EN ALIMENTADOR 1420-03 | S2301180000X | New_Event | Switch Failure | Include | Include | Equipment | 46 | 2023-01-18 | 2530 | keep | 0 | Jan | 2023 | 0.0017232 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
VEGA BAJA | 2023-01-18 11:45 | 2023-01-18 12:23 | 16 | 0:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO | B23011800032 | New_Event | Primary Pole Failure | Include | Include | Equipment | 38 | 2023-01-18 | 608 | keep | 0 | Jan | 2023 | 0.00041411 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2023-01-18 11:50 | 2023-01-18 17:08 | 13 | 5:18 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE DE CIVIL | C23011800061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2023-01-18 | 4134 | keep | 0 | Jan | 2023 | 0.0028156 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-01-18 12:15 | 2023-01-18 12:43 | 8 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE ZAFADO DE CAJA A TRANSFORMADOR | A23011800111 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-01-18 | 224 | keep | 0 | Jan | 2023 | 0.00015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-18 12:20 | 2023-01-18 16:29 | 6 | 4:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO Y REPARAR LINEA SECUNDARIA | C23011801010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 249 | 2023-01-18 | 1494 | keep | 0 | Jan | 2023 | 0.0010176 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-01-18 12:26 | 2023-01-18 13:19 | 13 | 0:53 | P | CAUSAS EXTERNAS | SE RETIRO TENSO SOBRE BUSHING SECUNDARIO DEL XMR | C23011800069 | New_Event | Damage From Public | Include | Include | Public | 53 | 2023-01-18 | 689 | keep | 0 | Jan | 2023 | 0.00046927 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2023-01-18 12:49 | 2023-01-18 13:21 | 3296 | 0:32 | T | PARARRAYOS DEFECTUOSO | DISPARO SE DESPEGO BAJANTE DE PARARRAYO AVERIADO CON VARETA, SE CERRO POR CONTOL | C23011800075 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 32 | 2023-01-18 | 105472 | keep | 0 | Jan | 2023 | 0.071836 | 0.0022449 | Sustained | FALSE | FALSE | Not_TMED_Event | 3296
VEGA BAJA | 2023-01-18 13:05 | 2023-01-18 14:27 | 1 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A23011800041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-01-18 | 82 | keep | 0 | Jan | 2023 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-18 13:08 | 2023-01-18 15:15 | 8 | 2:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REEMPLAZARON BARRAS EN PEDESTAL Y SE REPARARON TOMAS | C23011800036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 127 | 2023-01-18 | 1016 | keep | 0 | Jan | 2023 | 0.00069199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-18 13:11 | 2023-01-18 15:15 | 1 | 2:04 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | S23011800055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-01-18 | 124 | keep | 0 | Jan | 2023 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-01-18 13:19 | 2023-01-18 15:35 | 60 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN CORTE DE LINEA FUERTES VIENTOS | A23011800133 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2023-01-18 | 8160 | keep | 0 | Jan | 2023 | 0.0055577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-01-18 13:20 | 2023-01-18 16:15 | 60 | 2:55 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23011800090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-01-18 | 10500 | keep | 0 | Jan | 2023 | 0.0071515 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-01-18 13:21 | 2023-01-18 15:11 | 18 | 1:50 | P | PARARRAYOS DEFECTUOSO | 2 X 10 EN XMR REMPLAZO 2 PARARRAYOS AVERIADOS | C23011800075 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 110 | 2023-01-18 | 1980 | keep | 0 | Jan | 2023 | 0.0013486 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-01-18 13:24 | 2023-01-18 17:20 | 11 | 3:56 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | P23011800172 | New_Event | Primary Wire Break | Include | Include | Equipment | 236 | 2023-01-18 | 2596 | keep | 0 | Jan | 2023 | 0.0017681 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-01-18 13:37 | 2023-01-18 15:11 | 8 | 1:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REPARO SECUNDARIO Y REGULO XMR | C2301180009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 94 | 2023-01-18 | 752 | keep | 0 | Jan | 2023 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-18 13:51 | 2023-01-18 15:35 | 20 | 1:44 | P | DESGANCHE | 2 X 15 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23011800088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-01-18 | 2080 | keep | 0 | Jan | 2023 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-18 14:07 | 2023-01-18 15:32 | 13 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR Y REPARO SECUNDARIA | B23011800070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2023-01-18 | 1105 | keep | 0 | Jan | 2023 | 0.00075261 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-01-18 14:10 | 2023-01-18 16:57 | 125 | 2:47 | P | DESCONECTIVO DEFECTUOSO | SE CERRO PUENTE PRIMARIO TRAS PATIO Y SE REMPLAZO MACHETE | S23011800060 | New_Event | Switch Failure | Include | Include | Equipment | 167 | 2023-01-18 | 20875 | keep | 0 | Jan | 2023 | 0.014218 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
FAJARDO | 2023-01-18 14:19 | 2023-01-18 15:54 | 5 | 1:35 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | R23011800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-01-18 | 475 | keep | 0 | Jan | 2023 | 0.00032352 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-01-18 14:40 | 2023-01-18 17:03 | 7 | 2:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23011800109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2023-01-18 | 1001 | keep | 0 | Jan | 2023 | 0.00068178 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2023-01-18 14:41 | 2023-01-18 18:00 | 50 | 3:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P23011800194 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2023-01-18 | 9950 | keep | 0 | Jan | 2023 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-01-18 14:42 | 2023-01-18 19:56 | 12 | 5:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23011800139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 314 | 2023-01-18 | 3768 | keep | 0 | Jan | 2023 | 0.0025664 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-01-18 14:49 | 2023-01-18 18:50 | 100 | 4:01 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO NEUTRAL PRIMARIO | M23011800099 | New_Event | Primary Wire Break | Include | Include | Equipment | 241 | 2023-01-18 | 24100 | keep | 0 | Jan | 2023 | 0.016414 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-01-18 14:55 | 2023-01-18 17:05 | 40 | 2:10 | P | PARARRAYOS DEFECTUOSO | 1 X 50 Y 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M23011800103 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 130 | 2023-01-18 | 5200 | keep | 0 | Jan | 2023 | 0.0035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-18 15:10 | 2023-01-18 16:17 | 6 | 1:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23011800076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 67 | 2023-01-18 | 402 | keep | 0 | Jan | 2023 | 0.0002738 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-01-18 15:19 | 2023-01-18 18:00 | 100 | 2:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M23011800108 | New_Event | Cutout Failure | Include | Include | Equipment | 161 | 2023-01-18 | 16100 | keep | 0 | Jan | 2023 | 0.010966 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-01-18 15:26 | 2023-01-18 20:30 | 163 | 5:04 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P23011800202 | New_Event | Animals | Include | Include | Wildlife | 304 | 2023-01-18 | 49552 | keep | 0 | Jan | 2023 | 0.03375 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
FAJARDO | 2023-01-18 15:28 | 2023-01-18 17:14 | 43 | 1:46 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO PARTIDO Y SE SUBIO CONDUCTOR PRIMARIO | R23011800050 | New_Event | Primary Pole Failure | Include | Include | Equipment | 106 | 2023-01-18 | 4558 | keep | 0 | Jan | 2023 | 0.0031044 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
GUAYAMA | 2023-01-18 15:28 | 2023-01-18 18:20 | 10 | 2:52 | P | CONDUCTOR ROTO O ABIERTO | SE ABREN PUENTES PARA ELIMINAR DOS LINEAS EN EL PISO SE INSTALO JUMPER 1 X 40 EN CORTE DE LINEA | P23011800203 | New_Event | Primary Wire Break | Include | Include | Equipment | 172 | 2023-01-18 | 1720 | keep | 0 | Jan | 2023 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-18 15:40 | 2023-01-18 17:03 | 6 | 1:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | C23011800116 | New_Event | Cutout Failure | Include | Include | Equipment | 83 | 2023-01-18 | 498 | keep | 0 | Jan | 2023 | 0.00033919 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-01-18 15:40 | 2023-01-19 16:10 | 6 | 24:30 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MONTURA DE TRASFORMADOR Y SE REPARA BAJANTE PRIMARIO | M23011800041 | New_Event | Primary Wire Break | Include | Include | Equipment | 1470 | 2023-01-18 | 8820 | keep | 0 | Jan | 2023 | 0.0060073 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-01-18 15:40 | 2023-01-18 17:04 | 13 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011800085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2023-01-18 | 1092 | keep | 0 | Jan | 2023 | 0.00074376 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2023-01-18 15:45 | 2023-01-18 16:15 | 1 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO | C23011800114 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-01-18 | 30 | keep | 0 | Jan | 2023 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-18 15:54 | 2023-01-18 16:10 | 1 | 0:16 | P | TRANSFORMADOR AVERIADO | 2 X 25 EN CORTE DE LINEA SE HIZO REFERIDO PARA REMPLAZO DE BUSHING DE TRANSFORMADOR EN MALAS CONDICIONES | A23011800149 | New_Event | Service Transformer Failure | Include | Include | Equipment | 16 | 2023-01-18 | 16 | keep | 0 | Jan | 2023 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-18 16:24 | 2023-01-18 17:33 | 15 | 1:09 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA SECCIONALIZAR PEDESTAL QUEMADO | R23011800015 | New_Event |  |  |  |  | 69 | 2023-01-18 | 1035 | keep | 0 | Jan | 2023 | 0.00070493 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-01-18 16:25 | 2023-01-18 18:15 | 3 | 1:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23010500030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 110 | 2023-01-18 | 330 | keep | 0 | Jan | 2023 | 0.00022476 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-01-18 16:37 | 2023-01-18 22:23 | 6 | 5:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011800093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 346 | 2023-01-18 | 2076 | keep | 0 | Jan | 2023 | 0.001414 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-01-18 16:51 | 2023-01-18 16:52 | 4132 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23011800068 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-18 | 4132 | keep | 0 | Jan | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
SAN JUAN | 2023-01-18 17:19 | 2023-01-18 18:19 | 60 | 1:00 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE DE INSPECCION SJ-221121-02 | S23011800095 | New_Event | Switch Failure | Include | Include | Equipment | 60 | 2023-01-18 | 3600 | keep | 0 | Jan | 2023 | 0.0024519 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-18 17:55 | 2023-01-18 18:15 | 6 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE LEVANTO SECUNDARIA | S23011800096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-01-18 | 120 | keep | 0 | Jan | 2023 | 8.1731e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-18 18:20 | 2023-01-18 18:36 | 54 | 0:16 | P | DESCONECTIVO DEFECTUOSO | SE RETIRO PUENTE QUE ESTAN POR 1420-04 Y SE REMPLAZO Y SE PASO 10% POR 1420-02 POR BARRA INSPECCION | S2301180000X | New_Event | Switch Failure | Include | Include | Equipment | 16 | 2023-01-18 | 864 | keep | 0 | Jan | 2023 | 0.00058847 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BAYAMON | 2023-01-18 18:31 | 2023-01-18 21:08 | 5 | 2:37 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | B23011800103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2023-01-18 | 785 | keep | 0 | Jan | 2023 | 0.00053466 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-01-18 18:31 | 2023-01-18 19:50 | 85 | 1:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L DESGANCHO Y REMPLAZO CAJA QUEMADA | C23011800134 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2023-01-18 | 6715 | keep | 0 | Jan | 2023 | 0.0045736 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2023-01-18 19:10 | 2023-01-18 19:36 | 5 | 0:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23011800146 | New_Event | Secondary Wire Break | Include | Include | Equipment | 26 | 2023-01-18 | 130 | keep | 0 | Jan | 2023 | 8.8542e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-01-18 19:21 | 2023-01-18 20:08 | 25 | 0:47 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23011800057 | New_Event | Animals | Include | Include | Wildlife | 47 | 2023-01-18 | 1175 | keep | 0 | Jan | 2023 | 0.00080029 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-18 19:33 | 2023-01-18 21:49 | 137 | 2:16 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 100 EN CORTE DE LINEA, ANTERIOR SE DEJO TAG POSTE PARTIDO SE QUEDO FUERA 114 CLIENTES | S23011800116 | New_Event | Primary Pole Failure | Include | Include | Equipment | 136 | 2023-01-18 | 18632 | keep | 0 | Jan | 2023 | 0.01269 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
BAYAMON | 2023-01-18 19:36 | 2023-01-18 19:55 | 3 | 0:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | B23011800105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-01-18 | 57 | keep | 0 | Jan | 2023 | 3.8822e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-01-18 20:25 | 2023-01-19 10:48 | 20 | 14:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23011800170 | New_Event | Primary Wire Break | Include | Include | Equipment | 863 | 2023-01-18 | 17260 | keep | 0 | Jan | 2023 | 0.011756 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-18 21:49 | 2023-01-19 18:21 | 114 | 20:32 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZO DE POSTE PRIMARIO PARTIDO | S23011800129 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1232 | 2023-01-18 | 140448 | keep | 0 | Jan | 2023 | 0.095658 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-01-18 21:57 | 2023-01-19 13:39 | 385 | 15:42 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | INTERRUPTOR DE PORTATIL # 13 NO ABRIO EN AVERIA DE ARBOL SOBRE LINEAS BOBINA DE TRIP AVERIADA. GOI AR230119-01A | A23011800175 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 942 | 2023-01-18 | 362670 | keep | 0 | Jan | 2023 | 0.24701 | 0.00026222 | Sustained | FALSE | FALSE | Not_TMED_Event | 385
ARECIBO | 2023-01-18 21:57 | 2023-01-19 13:39 | 264 | 15:42 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | INTERRUPTOR DE PORTATIL # 13 NO ABRIO EN AVERIA DE ARBOL SOBRE LINEAS BOBINA DE TRIP AVERIADA. GOI AR230119-01A | A23011800175 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 942 | 2023-01-18 | 248688 | keep | 0 | Jan | 2023 | 0.16938 | 0.00017981 | Sustained | FALSE | FALSE | Not_TMED_Event | 264
YAUCO | 2023-01-18 22:22 | 2023-01-19 10:12 | 5 | 11:50 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23011800160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 710 | 2023-01-18 | 3550 | keep | 0 | Jan | 2023 | 0.0024179 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-01-18 22:55 | 2023-01-18 23:55 | 10 | 1:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | A23011800185 | New_Event | Cutout Failure | Include | Include | Equipment | 60 | 2023-01-18 | 600 | keep | 0 | Jan | 2023 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-18 23:53 | 2023-01-18 23:54 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23011800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-18 | 4188 | keep | 0 | Jan | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2023-01-19 00:50 | 2023-01-19 07:15 | 132 | 6:25 | P | DESGANCHE | 1 X 80 EN SU-4 SE RETIRO RAMA DE AEREO PROVISIONAL | R23011900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2023-01-19 | 50820 | keep | 0 | Jan | 2023 | 0.034613 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
ARECIBO | 2023-01-19 01:46 | 2023-01-19 01:50 | 2523 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A23011900001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-19 | 10092 | keep | 0 | Jan | 2023 | 0.0068736 | 0.0017184 | Momentary | FALSE | FALSE | Not_TMED_Event | 2523
ARECIBO | 2023-01-19 01:46 | 2023-01-19 01:50 | 1607 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A23011900001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-19 | 6428 | keep | 0 | Jan | 2023 | 0.0043781 | 0.0010945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1607
ARECIBO | 2023-01-19 01:46 | 2023-01-19 01:50 | 1722 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A23011900001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-19 | 6888 | keep | 0 | Jan | 2023 | 0.0046914 | 0.0011728 | Momentary | FALSE | FALSE | Not_TMED_Event | 1722
ARECIBO | 2023-01-19 01:46 | 2023-01-19 01:50 | 619 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A23011900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-19 | 2476 | keep | 0 | Jan | 2023 | 0.0016864 | 0.0004216 | Momentary | FALSE | FALSE | Not_TMED_Event | 619
ARECIBO | 2023-01-19 01:46 | 2023-01-19 01:50 | 243 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A23011900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-19 | 972 | keep | 0 | Jan | 2023 | 0.00066202 | 0.00016551 | Momentary | FALSE | FALSE | Not_TMED_Event | 243
ARECIBO | 2023-01-19 01:46 | 2023-01-19 01:50 | 2703 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A23011900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-01-19 | 10812 | keep | 0 | Jan | 2023 | 0.007364 | 0.001841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2703
CANOVANAS | 2023-01-19 02:36 | 2023-01-19 02:37 | 500 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23011900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-19 | 500 | keep | 0 | Jan | 2023 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2023-01-19 05:23 | 2023-01-19 08:39 | 70 | 3:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23011900007 | New_Event | Cutout Failure | Include | Include | Equipment | 196 | 2023-01-19 | 13720 | keep | 0 | Jan | 2023 | 0.0093446 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-01-19 06:45 | 2023-01-19 08:30 | 60 | 1:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23011900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-01-19 | 6300 | keep | 0 | Jan | 2023 | 0.0042909 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-01-19 06:53 | 2023-01-19 10:34 | 9 | 3:41 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR IGUANA | M23011900002 | New_Event | Animals | Include | Include | Wildlife | 221 | 2023-01-19 | 1989 | keep | 0 | Jan | 2023 | 0.0013547 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-01-19 07:39 | 2023-01-19 09:49 | 4 | 2:10 | P | DESGANCHE | 1 X 40 E C/L DESGANCHE | B23011900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-01-19 | 520 | keep | 0 | Jan | 2023 | 0.00035417 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-01-19 08:01 | 2023-01-19 08:03 | 3709 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2301190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-19 | 7418 | keep | 0 | Jan | 2023 | 0.0050524 | 0.0025262 | Momentary | FALSE | FALSE | Not_TMED_Event | 3709
CANOVANAS | 2023-01-19 08:41 | 2023-01-19 12:05 | 2 | 3:24 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | R23011900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-01-19 | 408 | keep | 0 | Jan | 2023 | 0.00027789 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-01-19 09:00 | 2023-01-19 15:00 | 30 | 6:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | M23011900067 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 360 | 2023-01-19 | 10800 | keep | 0 | Jan | 2023 | 0.0073558 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-01-19 09:01 | 2023-01-19 11:00 | 2 | 1:59 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R23011900025 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-01-19 | 238 | keep | 0 | Jan | 2023 | 0.0001621 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-01-19 09:15 | 2023-01-19 09:45 | 2 | 0:30 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE EN TRANSFORMADOR | M23011900004 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 30 | 2023-01-19 | 60 | keep | 0 | Jan | 2023 | 4.0866e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-01-19 09:32 | 2023-01-19 12:29 | 184 | 2:57 | P | NO SE REPORTO CAUSA | 1 X 65 1 X 80 Y 1 X 100 EN C/L DIFERENTES | S23011900031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2023-01-19 | 32568 | keep | 0 | Jan | 2023 | 0.022182 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
CANOVANAS | 2023-01-19 09:37 | 2023-01-19 13:28 | 41 | 3:51 | P | DESGANCHE | 1 X 40 EN AEREO PROVISIONAL SE DESGANCHO PALMA | R23011900030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2023-01-19 | 9471 | keep | 0 | Jan | 2023 | 0.0064507 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CAGUAS | 2023-01-19 09:57 | 2023-01-19 09:58 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-19 | 1307 | keep | 0 | Jan | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
UTUADO | 2023-01-19 10:00 | 2023-01-19 10:50 | 7 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON LINEAS SECUNDARIAS | A23011800175 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-01-19 | 350 | keep | 0 | Jan | 2023 | 0.00023838 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-01-19 10:10 | 2023-01-19 13:23 | 30 | 3:13 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE PRIMARIO Y 1 X 50 EN C/L | C23011900032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2023-01-19 | 5790 | keep | 0 | Jan | 2023 | 0.0039435 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-01-19 10:35 | 2023-01-19 12:30 | 4 | 1:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BARRAS EN PEDESTAL | C23011900021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 115 | 2023-01-19 | 460 | keep | 0 | Jan | 2023 | 0.0003133 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-01-19 10:38 | 2023-01-19 12:00 | 75 | 1:22 | P | ANIMAL | 1 X 80 EN C/L AVE CRUZO LINEAS | P23011900043 | New_Event | Animals | Include | Include | Wildlife | 82 | 2023-01-19 | 6150 | keep | 0 | Jan | 2023 | 0.0041887 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
YAUCO | 2023-01-19 10:47 | 2023-01-19 19:10 | 1 | 8:23 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO CAUSA | P23011900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 503 | 2023-01-19 | 503 | keep | 0 | Jan | 2023 | 0.00034259 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-19 11:01 | 2023-01-19 15:20 | 100 | 4:19 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C23011900049 | New_Event | Primary Wire Break | Include | Include | Equipment | 259 | 2023-01-19 | 25900 | keep | 0 | Jan | 2023 | 0.01764 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-01-19 11:35 | 2023-01-19 14:50 | 10 | 3:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR, SE REPARO NEUTRAL SOTERADO | M22121500004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 195 | 2023-01-19 | 1950 | keep | 0 | Jan | 2023 | 0.0013281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-19 11:40 | 2023-01-19 12:14 | 5 | 0:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5 X 37.5 | B23011900026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 34 | 2023-01-19 | 170 | keep | 0 | Jan | 2023 | 0.00011579 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2023-01-19 12:18 | 2023-01-19 12:48 | 69 | 0:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO C/L PARA RETEZAR LNIEA PIRMARIA MONOFASICA Y SE REEMPLAZO ASILADOR PARTIDO | C23011900065 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 30 | 2023-01-19 | 2070 | keep | 0 | Jan | 2023 | 0.0014099 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
CAGUAS | 2023-01-19 12:20 | 2023-01-19 14:37 | 486 | 2:17 | P | CABLE SOTERRADO AVERIADO | SE CERRARON PUENTES CON CG-230103-01 PARA MOVER N/O Y SE NORMALIZARON LAS CARGAS DEL 3005-02 YA QUE NO SE PUDO CORREGIR AVERIA SOTERADA DEL SU-D AL SU-E | C23011900078 | New_Event | UG Cable Fault | Include | Include | Equipment | 137 | 2023-01-19 | 66582 | keep | 0 | Jan | 2023 | 0.045349 | 0.00033101 | Sustained | FALSE | FALSE | Not_TMED_Event | 486
BAYAMON | 2023-01-19 12:22 | 2023-01-19 12:48 | 8 | 0:26 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR Y SE DESCONECTO CLIENTE POR AVERIA INTERNA PROA | B23011900007 | New_Event | Customer-Related Interruption | Include | Include | Public | 26 | 2023-01-19 | 208 | keep | 0 | Jan | 2023 | 0.00014167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-19 12:33 | 2023-01-19 13:16 | 23 | 0:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23011900035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2023-01-19 | 989 | keep | 0 | Jan | 2023 | 0.0006736 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2023-01-19 12:36 | 2023-01-19 14:43 | 15 | 2:07 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR YSE REEMPLAZO BAJANTE DE XMR Y SE RETEZO SEC | S23011900070 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 127 | 2023-01-19 | 1905 | keep | 0 | Jan | 2023 | 0.0012975 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-01-19 12:42 | 2023-01-19 14:26 | 2 | 1:44 | P | TRANSFORMADOR AVERIADO | 2 X 10 EN TRANSFORMADOR SE DEJO DELTA ABIERTA Y SE ELIMINO UNO QUEDO TODO EN SERVICIO | R23011900053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 104 | 2023-01-19 | 208 | keep | 0 | Jan | 2023 | 0.00014167 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-01-19 12:50 | 2023-01-19 12:53 | 718 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1330-01 LLEVA 90% 1901-05 SE CERRO POR SCADA | S23011900072 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-01-19 | 2154 | keep | 0 | Jan | 2023 | 0.0014671 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
BAYAMON | 2023-01-19 12:50 | 2023-01-19 12:53 | 558 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1330-01 LLEVA 90% 1901-05 SE CERRO POR SCADA | S23011900072 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-19 | 1674 | keep | 0 | Jan | 2023 | 0.0011402 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
SAN JUAN | 2023-01-19 12:53 | 2023-01-19 15:30 | 263 | 2:37 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L NO CAUSA | S23011900073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2023-01-19 | 41291 | keep | 0 | Jan | 2023 | 0.028123 | 0.00017913 | Sustained | FALSE | FALSE | Not_TMED_Event | 263
SAN JUAN | 2023-01-19 12:53 | 2023-01-19 19:19 | 60 | 6:26 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO PARTIDO | S23011900139 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 386 | 2023-01-19 | 23160 | keep | 0 | Jan | 2023 | 0.015774 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-01-19 13:03 | 2023-01-19 18:11 | 30 | 5:08 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA POR LINEA ARRIADA | M23011900064 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 308 | 2023-01-19 | 9240 | keep | 0 | Jan | 2023 | 0.0062933 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-19 13:21 | 2023-01-19 13:24 | 143 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-06 LLEVA 80% 1404-07 SE CERRO POR SCADA | S23011900083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-19 | 429 | keep | 0 | Jan | 2023 | 0.00029219 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-01-19 13:21 | 2023-01-19 13:24 | 1085 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1404-06 LLEVA 80% 1404-07 SE CERRO POR SCADA | S23011900083 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-19 | 3255 | keep | 0 | Jan | 2023 | 0.002217 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
MAYAGÃœEZ | 2023-01-19 13:24 | 2023-01-19 13:25 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23011900069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-19 | 1352 | keep | 0 | Jan | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-01-19 13:24 | 2023-01-19 13:25 | 871 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE 6012-05 LLEVA LA CARGA DEL 6014-03 | M23011900069 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-19 | 871 | keep | 0 | Jan | 2023 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
VEGA BAJA | 2023-01-19 13:28 | 2023-01-19 14:02 | 8 | 0:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 50KVA X 50KVA | B23011900042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 34 | 2023-01-19 | 272 | keep | 0 | Jan | 2023 | 0.00018526 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-01-19 13:31 | 2023-01-19 17:45 | 9 | 4:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA 1 X 10 EN TRANSFORMADOR | P23011900072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 254 | 2023-01-19 | 2286 | keep | 0 | Jan | 2023 | 0.001557 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-01-19 13:36 | 2023-01-19 16:20 | 7 | 2:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23011900064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-01-19 | 1148 | keep | 0 | Jan | 2023 | 0.0007819 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-01-19 13:39 | 2023-01-19 16:20 | 75 | 2:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN MACHETES | A23011900029 | New_Event | Primary Wire Break | Include | Include | Equipment | 161 | 2023-01-19 | 12075 | keep | 0 | Jan | 2023 | 0.0082242 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-01-19 13:45 | 2023-01-19 14:38 | 10 | 0:53 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR Y SE REPARO PUENTE PRIMARIO DE LINEA A CAJA EN XMR | S23011900090 | New_Event | Primary Wire Break | Include | Include | Equipment | 53 | 2023-01-19 | 530 | keep | 0 | Jan | 2023 | 0.00036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-19 13:47 | 2023-01-20 10:39 | 8 | 20:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO | C23011900090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1252 | 2023-01-19 | 10016 | keep | 0 | Jan | 2023 | 0.0068219 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-19 14:50 | 2023-01-19 15:30 | 20 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR PARA REEMPLAZO DE BAJANTE SECUNDARIO | M23011700092 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-01-19 | 800 | keep | 0 | Jan | 2023 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-01-19 15:00 | 2023-01-19 15:15 | 19 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR SECUNDARIA | R23011900069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-01-19 | 285 | keep | 0 | Jan | 2023 | 0.00019411 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-01-19 15:06 | 2023-01-19 19:12 | 1 | 4:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA DE RISER AVERIADA | S23011900102 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2023-01-19 | 246 | keep | 0 | Jan | 2023 | 0.00016755 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-19 15:20 | 2023-01-19 18:32 | 5 | 3:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REPARARON CONEXIONES SECUNDARIAS | C23011900105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 192 | 2023-01-19 | 960 | keep | 0 | Jan | 2023 | 0.00065385 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-19 15:24 | 2023-01-19 15:25 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2301190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-19 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-01-19 15:44 | 2023-01-19 16:04 | 1 | 0:20 | P | NO SE REPORTO CAUSA | 2 X 20 EN BANCO DE XMR | B23011900056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2023-01-19 | 20 | keep | 0 | Jan | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-19 15:50 | 2023-01-19 16:46 | 61 | 0:56 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTE PARA SECCIONALIZAR POSTE PARTIDO BY-230119-01 | B23011900064 | New_Event | Primary Pole Failure | Include | Include | Equipment | 56 | 2023-01-19 | 3416 | keep | 0 | Jan | 2023 | 0.0023266 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2023-01-19 16:07 | 2023-01-19 17:11 | 10 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REGULAR VOLTAGE SE BAJO TAP DEL 4 AL 2 122V POR FASE | S23011900114 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2023-01-19 | 640 | keep | 0 | Jan | 2023 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-19 16:08 | 2023-01-19 20:36 | 24 | 4:28 | P | NO SE REPORTO CAUSA | 2 X 30 SMU EN SU-04 | B23011900060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 268 | 2023-01-19 | 6432 | keep | 0 | Jan | 2023 | 0.0043808 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
AGUADILLA | 2023-01-19 16:45 | 2023-01-19 17:30 | 10 | 0:45 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR ESCAPE DE ACEITE DE 50 KVA POR 25 KVA | A23011900088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2023-01-19 | 450 | keep | 0 | Jan | 2023 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-19 16:46 | 2023-01-20 17:32 | 2 | 24:46 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE PRIMARIO PARTIDO | B23011900069 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1486 | 2023-01-19 | 2972 | keep | 0 | Jan | 2023 | 0.0020242 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-19 16:47 | 2023-01-19 19:10 | 18 | 2:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR LINEAS SECUNDARIAS | C23011900117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 143 | 2023-01-19 | 2574 | keep | 0 | Jan | 2023 | 0.0017531 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-01-19 16:53 | 2023-01-19 19:32 | 25 | 2:39 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23011900118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2023-01-19 | 3975 | keep | 0 | Jan | 2023 | 0.0027074 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-01-19 17:42 | 2023-01-19 19:40 | 17 | 1:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REGULO VOLTAGE 122V POR FASE | B23011900067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 118 | 2023-01-19 | 2006 | keep | 0 | Jan | 2023 | 0.0013663 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-01-19 17:44 | 2023-01-19 17:45 | 320 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2301190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-19 | 320 | keep | 0 | Jan | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
VEGA BAJA | 2023-01-19 18:00 | 2023-01-19 18:45 | 5 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPLAZARON BAJANTES SECUNDARIO TRANSFORMADOR | A23011400051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-01-19 | 225 | keep | 0 | Jan | 2023 | 0.00015325 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-01-19 18:27 | 2023-01-19 19:50 | 100 | 1:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIO | R23011900078 | New_Event | Cutout Failure | Include | Include | Equipment | 83 | 2023-01-19 | 8300 | keep | 0 | Jan | 2023 | 0.0056531 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-01-19 18:44 | 2023-01-20 21:54 | 25 | 27:10 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23011900091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1630 | 2023-01-19 | 40750 | keep | 0 | Jan | 2023 | 0.027755 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-01-19 18:55 | 2023-01-19 20:00 | 24 | 1:05 | P | NO SE REPORTO CAUSA | 1 X 15 XMR | C23011900126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2023-01-19 | 1560 | keep | 0 | Jan | 2023 | 0.0010625 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-01-19 19:19 | 2023-01-19 21:08 | 180 | 1:49 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MACHETES PARA LEVANTAR CONDUCTOR PRIMARIO PARTIDO SJ-230119-01 | S23011900139 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 109 | 2023-01-19 | 19620 | keep | 0 | Jan | 2023 | 0.013363 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-19 19:24 | 2023-01-19 19:25 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R23011900083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-19 | 2039 | keep | 0 | Jan | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
ARECIBO | 2023-01-19 19:25 | 2023-01-20 09:40 | 10 | 14:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23011900104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 855 | 2023-01-19 | 8550 | keep | 0 | Jan | 2023 | 0.0058234 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-01-19 19:42 | 2023-01-20 09:02 | 15 | 13:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23011900106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 800 | 2023-01-19 | 12000 | keep | 0 | Jan | 2023 | 0.0081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-19 19:51 | 2023-01-19 21:08 | 7 | 1:17 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR PARA TRABAJAR CONDICION DE ALAMBRE PRIMARIO EN EL SUELO S230119-01 | S23011900141 | New_Event | Primary Wire Break | Include | Include | Equipment | 77 | 2023-01-19 | 539 | keep | 0 | Jan | 2023 | 0.00036711 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-01-19 19:51 | 2023-01-20 06:27 | 12 | 10:36 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | C23011900131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 636 | 2023-01-19 | 7632 | keep | 0 | Jan | 2023 | 0.0051981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-19 19:58 | 2023-01-19 20:41 | 15 | 0:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REAPARO BAJANTE SECUNDARIO | B23011900074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2023-01-19 | 645 | keep | 0 | Jan | 2023 | 0.00043931 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-19 20:04 | 2023-01-19 21:44 | 135 | 1:40 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23011900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-01-19 | 13500 | keep | 0 | Jan | 2023 | 0.0091948 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
HUMACAO | 2023-01-19 20:24 | 2023-01-19 22:26 | 60 | 2:02 | P | ANIMAL | 1X40 EN C/L CRUCE POR AVE | C23011900132 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-01-19 | 7320 | keep | 0 | Jan | 2023 | 0.0049856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-01-19 20:34 | 2023-01-20 11:24 | 1 | 14:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | R23011900093 | New_Event | Cutout Failure | Include | Include | Equipment | 890 | 2023-01-19 | 890 | keep | 0 | Jan | 2023 | 0.00060617 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-19 20:47 | 2023-01-20 08:12 | 5 | 11:25 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZAR BUSHING SECUNDARIO QUEMADO EN TRANSFORMADOR | M23011900106 | New_Event | Service Transformer Failure | Include | Include | Equipment | 685 | 2023-01-19 | 3425 | keep | 0 | Jan | 2023 | 0.0023328 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-01-19 20:51 | 2023-01-20 09:15 | 8 | 12:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 POR 37.5 | C23011900133 | New_Event | Service Transformer Failure | Include | Include | Equipment | 744 | 2023-01-19 | 5952 | keep | 0 | Jan | 2023 | 0.0040539 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-19 21:43 | 2023-01-20 09:05 | 3 | 11:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23011900099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 682 | 2023-01-19 | 2046 | keep | 0 | Jan | 2023 | 0.0013935 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2023-01-19 21:54 | 2023-01-20 09:23 | 8 | 11:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CONECTORES SECUNDARIOS | A23011900113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 689 | 2023-01-19 | 5512 | keep | 0 | Jan | 2023 | 0.0037542 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-19 22:26 | 2023-01-20 03:42 | 327 | 5:16 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DEL 0040 LOCKOUT SE ENCONTRO 2603-07 INTERRUPTOR QUEMADO Y DISCO EN TRONCAL QUEMADO Y ROTO | C23011900146 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 316 | 2023-01-19 | 103332 | keep | 0 | Jan | 2023 | 0.070379 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-19 22:26 | 2023-01-20 03:42 | 5630 | 5:16 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DEL 0040 LOCKOUT SE ENCONTRO 2603-07 INTERRUPTOR QUEMADO Y DISCO EN TRONCAL QUEMADO Y ROTO | C23011900146 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 316 | 2023-01-19 | 1779080 | keep | 0 | Jan | 2023 | 1.2117 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2023-01-19 22:26 | 2023-01-20 03:42 | 2126 | 5:16 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DEL 0040 LOCKOUT SE ENCONTRO 2603-07 INTERRUPTOR QUEMADO Y DISCO EN TRONCAL QUEMADO Y ROTO | C23011900146 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 316 | 2023-01-19 | 671816 | keep | 0 | Jan | 2023 | 0.45757 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2023-01-19 22:26 | 2023-01-20 01:32 | 551 | 3:06 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DEL 0040 LOCKOUT SE ENCONTRO 2603-07 INTERRUPTOR QUEMADO Y DISCO EN TRONCAL QUEMADO Y ROTO | C23011900146 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 186 | 2023-01-19 | 102486 | keep | 0 | Jan | 2023 | 0.069803 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2023-01-19 22:26 | 2023-01-19 22:27 | 2354 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE POR CAUSA DE AVERIA DEL 2603-07 - NO ESTAN AMARRADOS, OPERARON SIMULTANEAMENTE | C2301190000X | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-19 | 2354 | keep | 0 | Jan | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-01-19 22:26 | 2023-01-19 22:27 | 1891 | 0:01 | S | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE LA LINEA 3700 POR CAUSA DE AVERIA DEL 2603-07 | C2301190000X | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-19 | 1891 | keep | 0 | Jan | 2023 | 0.001288 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2023-01-19 22:26 | 2023-01-19 22:27 | 1250 | 0:01 | S | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE LA LINEA 3700 POR CAUSA DE AVERIA DEL 2603-07 | C2301190000X | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-19 | 1250 | keep | 0 | Jan | 2023 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2023-01-19 22:26 | 2023-01-19 22:27 | 2141 | 0:01 | S | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE LA LINEA 3700 POR CAUSA DE AVERIA DEL 2603-07 | C2301190000X | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-19 | 2141 | keep | 0 | Jan | 2023 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2023-01-19 22:26 | 2023-01-19 22:27 | 1827 | 0:01 | S | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE LA LINEA 3700 POR CAUSA DE AVERIA DEL 2603-07 | C2301190000X | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-19 | 1827 | keep | 0 | Jan | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CAGUAS | 2023-01-19 22:26 | 2023-01-20 08:01 | 52 | 9:35 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | C23011900138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 575 | 2023-01-19 | 29900 | keep | 0 | Jan | 2023 | 0.020365 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2023-01-19 23:44 | 2023-01-20 10:00 | 13 | 10:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA A XMR | S23011900145 | New_Event | Primary Wire Break | Include | Include | Equipment | 616 | 2023-01-19 | 8008 | keep | 0 | Jan | 2023 | 0.0054542 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2023-01-19 23:48 | 2023-01-19 23:49 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23011900087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-19 | 4085 | keep | 0 | Jan | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
HUMACAO | 2023-01-20 00:33 | 2023-01-20 00:34 | 327 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL 2604-01 DISCO QUEMADO Y ROTO EN EL ALIMENTADOR CARGA POR EL 2604-01 | C231220000X | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-20 | 327 | keep | 0 | Jan | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-20 00:33 | 2023-01-20 00:34 | 2354 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE LLEVANDO LA CARGA DE 2603-07 AVERIA DE DISCO ROTO EN ALIMENTADOR 2603-07 | C231220000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-20 | 2354 | keep | 0 | Jan | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-01-20 00:42 | 2023-01-20 00:43 | 327 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL 2604-01 DISCO QUEMADO Y ROTO EN EL ALIMENTADOR CARGA POR EL 2604-01 | C231220000X | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-20 | 327 | keep | 0 | Jan | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-20 00:42 | 2023-01-20 00:43 | 2354 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE LLEVANDO LA CARGA DE 2603-07 AVERIA DE DISCO ROTO EN ALIMENTADOR 2603-07 | C231220000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-20 | 2354 | keep | 0 | Jan | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-01-20 01:53 | 2023-01-20 03:00 | 327 | 1:07 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DEL 2604-01 AVERIA DE DISCO ROTO SE DESAMARRARON CARGAS ENTRE 2604-01 Y 2603-07 CARGA POR EL 2603-06 | C231220000X | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 67 | 2023-01-20 | 21909 | keep | 0 | Jan | 2023 | 0.014922 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-20 01:53 | 2023-01-20 02:13 | 2354 | 0:20 | T | ALIMENTADOR AMARRADO | DISPARO LLEVANDO LA CARGA DE 2603-07 AVERIA DE DISCO ROTO EN ALIMENTADOR 2603-07 SE DESAMARRARON CARGAS ENTRE 2604-01 Y 2603-07 | C231220000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 20 | 2023-01-20 | 47080 | keep | 0 | Jan | 2023 | 0.032066 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2023-01-20 02:09 | 2023-01-20 12:15 | 50 | 10:06 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M23012000001 | New_Event | Primary Wire Break | Include | Include | Equipment | 606 | 2023-01-20 | 30300 | keep | 0 | Jan | 2023 | 0.020637 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-01-20 02:11 | 2023-01-20 09:53 | 20 | 7:42 | P | DESGANCHE | DESGANCHE 1 X 100 EN CORTE DE LINEA | R23012000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 462 | 2023-01-20 | 9240 | keep | 0 | Jan | 2023 | 0.0062933 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-01-20 03:42 | 2023-01-20 07:22 | 60 | 3:40 | P | ANIMAL | 1X40 EN C/L CRUCE POR AVE | C23011900132 | New_Event | Animals | Include | Include | Wildlife | 220 | 2023-01-20 | 13200 | keep | 0 | Jan | 2023 | 0.0089905 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-01-20 03:46 | 2023-01-20 03:47 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-20 | 1648 | keep | 0 | Jan | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
HUMACAO | 2023-01-20 03:49 | 2023-01-20 08:58 | 80 | 5:09 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | C23012000019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 309 | 2023-01-20 | 24720 | keep | 0 | Jan | 2023 | 0.016837 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-20 04:13 | 2023-01-20 04:14 | 271 | 0:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | S2301200000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-20 | 271 | keep | 0 | Jan | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2023-01-20 04:14 | 2023-01-20 06:00 | 15 | 1:46 | P | DESGANCHE | SE ABRIO XMR PARA DESGANCHAR Y ELIMINAR PARARRAYO | S23012000009 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-01-20 | 1590 | keep | 0 | Jan | 2023 | 0.0010829 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-20 04:29 | 2023-01-20 04:30 | 3709 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTOL | S2301200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-20 | 3709 | keep | 0 | Jan | 2023 | 0.0025262 | 0.0025262 | Momentary | FALSE | FALSE | Not_TMED_Event | 3709
AGUADILLA | 2023-01-20 04:48 | 2023-01-20 04:49 | 1 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23012000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-20 | 1 | keep | 0 | Jan | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-20 05:30 | 2023-01-20 11:30 | 1 | 6:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23012000020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 360 | 2023-01-20 | 360 | keep | 0 | Jan | 2023 | 0.00024519 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-20 05:35 | 2023-01-20 05:36 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2301200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-20 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-01-20 06:16 | 2023-01-20 09:38 | 30 | 3:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23012000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-01-20 | 6060 | keep | 0 | Jan | 2023 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-20 06:19 | 2023-01-20 06:21 | 1984 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23012000015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-20 | 3968 | keep | 0 | Jan | 2023 | 0.0027026 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
CAGUAS | 2023-01-20 07:29 | 2023-01-20 09:41 | 30 | 2:12 | P | DESGANCHE | 1X50 EN C/L Y 1X10 EN XMR | C23012000037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-01-20 | 3960 | keep | 0 | Jan | 2023 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-20 07:52 | 2023-01-20 10:39 | 25 | 2:47 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23012000006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-01-20 | 4175 | keep | 0 | Jan | 2023 | 0.0028436 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-01-20 07:54 | 2023-01-20 10:42 | 100 | 2:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23012000013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2023-01-20 | 16800 | keep | 0 | Jan | 2023 | 0.011442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-01-20 08:19 | 2023-01-20 12:21 | 10 | 4:02 | P | ANIMAL | 1X10 EN XMR SE RETIRO SERPIENTE | C23012000041 | New_Event | Animals | Include | Include | Wildlife | 242 | 2023-01-20 | 2420 | keep | 0 | Jan | 2023 | 0.0016483 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-01-20 08:37 | 2023-01-20 11:00 | 200 | 2:23 | P | DESGANCHE | 2 X 140 EN C/L DESGANCHE | C23012000045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-01-20 | 28600 | keep | 0 | Jan | 2023 | 0.019479 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2023-01-20 08:46 | 2023-01-20 10:52 | 60 | 2:06 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | R23012000010 | New_Event | Animals | Include | Include | Wildlife | 126 | 2023-01-20 | 7560 | keep | 0 | Jan | 2023 | 0.0051491 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-20 09:08 | 2023-01-20 09:10 | 242 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-09 LLEVANDO 1420-05 Y 20% DE SU CARGA POR 1401-07 Y 30% POR 1420-04 | S23012000075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-20 | 484 | keep | 0 | Jan | 2023 | 0.00032965 | 0.00016483 | Momentary | FALSE | FALSE | Not_TMED_Event | 242
SAN JUAN | 2023-01-20 09:08 | 2023-01-20 09:10 | 4 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1404-09 LLEVANDO 1420-05 Y 20% DE SU CARGA POR 1401-07 Y 30% POR 1420-04 | S23012000075 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-20 | 8 | keep | 0 | Jan | 2023 | 5.4488e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-01-20 09:30 | 2023-01-20 13:15 | 8 | 3:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23012000026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 225 | 2023-01-20 | 1800 | keep | 0 | Jan | 2023 | 0.001226 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-20 09:33 | 2023-01-20 14:15 | 56 | 4:42 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | B23012000020 | New_Event | Animals | Include | Include | Wildlife | 282 | 2023-01-20 | 15792 | keep | 0 | Jan | 2023 | 0.010756 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BARRANQUITAS | 2023-01-20 09:45 | 2023-01-20 13:14 | 12 | 3:29 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE RETEZO/RELOCALIZO SECUNDARIA A NUEVO POSTE | C23012000065 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 209 | 2023-01-20 | 2508 | keep | 0 | Jan | 2023 | 0.0017082 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-20 10:00 | 2023-01-20 10:25 | 16 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | B23012000023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-20 | 400 | keep | 0 | Jan | 2023 | 0.00027244 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-01-20 10:24 | 2023-01-20 14:00 | 12 | 3:36 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L CAMION CON TUMBA TOCO LA LINEA | C23012000084 | New_Event | Damage From Public | Include | Include | Public | 216 | 2023-01-20 | 2592 | keep | 0 | Jan | 2023 | 0.0017654 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-20 10:29 | 2023-01-20 10:59 | 2 | 0:30 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | S23012000043 | New_Event | Animals | Include | Include | Wildlife | 30 | 2023-01-20 | 60 | keep | 0 | Jan | 2023 | 4.0866e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-01-20 10:30 | 2023-01-20 12:51 | 64 | 2:21 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA POSTE IMPACTADO POR CAMION | R23012000025 | New_Event | Damage From Public | Include | Include | Public | 141 | 2023-01-20 | 9024 | keep | 0 | Jan | 2023 | 0.0061462 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
CANOVANAS | 2023-01-20 10:33 | 2023-01-20 13:37 | 50 | 3:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 1 X 100 EN CORTE DE LINEA | R23012000028 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2023-01-20 | 9200 | keep | 0 | Jan | 2023 | 0.0062661 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-20 10:35 | 2023-01-20 15:29 | 71 | 4:54 | P | SOBRECARGA | 1 X 100 EN C/L SE INFORMA SOBRECARGA | B23012000030 | New_Event | Trip Due To Overload | Include | Include | Other | 294 | 2023-01-20 | 20874 | keep | 0 | Jan | 2023 | 0.014217 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
SAN JUAN | 2023-01-20 10:49 | 2023-01-20 13:00 | 25 | 2:11 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA RELOCALIZAR SECUNDARIAS A POSTE SECUNDARIO NUEVO | S23012000108 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 131 | 2023-01-20 | 3275 | keep | 0 | Jan | 2023 | 0.0022306 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-01-20 10:51 | 2023-01-20 13:08 | 5 | 2:17 | P | PARARRAYOS DEFECTUOSO | 2 X 15 EN XMR SE ELIMINO PARARRAYO | S23012000109 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 137 | 2023-01-20 | 685 | keep | 0 | Jan | 2023 | 0.00046655 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-01-20 10:51 | 2023-01-20 11:00 | 8 | 0:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTOR SECUNDARIO SAFADO DE BUSHING | R23012000032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 9 | 2023-01-20 | 72 | keep | 0 | Jan | 2023 | 4.9039e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-01-20 11:00 | 2023-01-20 13:10 | 1 | 2:10 | P | OTRAS CAUSAS | SE REPARO EQUIPO MEDICION | R23012000038 | New_Event | Other Causes | Include | Include | Other | 130 | 2023-01-20 | 130 | keep | 0 | Jan | 2023 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-20 11:11 | 2023-01-20 12:27 | 6 | 1:16 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO BEJUCO | R23012000037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-01-20 | 456 | keep | 0 | Jan | 2023 | 0.00031058 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-01-20 11:15 | 2023-01-20 14:38 | 37 | 3:23 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230120-50 SE REMPLAZO POSTE PRIMARIO | R23012000013 | New_Event | Primary Pole Failure | Include | Include | Equipment | 203 | 2023-01-20 | 7511 | keep | 0 | Jan | 2023 | 0.0051157 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BARRANQUITAS | 2023-01-20 11:18 | 2023-01-20 14:10 | 9 | 2:52 | P | ANIMAL | SE REPARO BAJANTE SECUNDARIO CRUCE POR AVE | C23012000098 | New_Event | Animals | Include | Include | Wildlife | 172 | 2023-01-20 | 1548 | keep | 0 | Jan | 2023 | 0.0010543 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-01-20 11:40 | 2023-01-20 13:07 | 1 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL PARTIDO | A23011900116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2023-01-20 | 87 | keep | 0 | Jan | 2023 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-20 11:46 | 2023-01-20 11:59 | 2999 | 0:13 | T | ERROR HUMANO | DISPARO DE INTERRUPTORN CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR HABIA PERSONAL CON HO TRABAJANDO EN ALIMENTADOR | M23012000076 | New_Event | Human Error | Include | Include | Other | 13 | 2023-01-20 | 38987 | keep | 0 | Jan | 2023 | 0.026554 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
SAN JUAN | 2023-01-20 11:53 | 2023-01-20 11:58 | 3 | 0:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 37800 | S23012000132 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-20 | 15 | keep | 0 | Jan | 2023 | 1.0216e-05 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-01-20 11:53 | 2023-01-20 11:58 | 3957 | 0:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 37800 | S23012000132 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-20 | 19785 | keep | 0 | Jan | 2023 | 0.013475 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2023-01-20 11:53 | 2023-01-20 11:58 | 58 | 0:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 37800 | S23012000132 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-20 | 290 | keep | 0 | Jan | 2023 | 0.00019752 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2023-01-20 11:53 | 2023-01-20 11:58 | 386 | 0:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 37800 | S23012000132 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-20 | 1930 | keep | 0 | Jan | 2023 | 0.0013145 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
HUMACAO | 2023-01-20 11:54 | 2023-01-20 12:59 | 1 | 1:05 | P | NO SE REPORTO CAUSA | 2X10 EN BANCO DE XMRS | C23012000110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2023-01-20 | 65 | keep | 0 | Jan | 2023 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-20 12:08 | 2023-01-20 15:06 | 6 | 2:58 | P | ANIMAL | 1X20 EN XMR CRUCE POR AVE | C23012000113 | New_Event | Animals | Include | Include | Wildlife | 178 | 2023-01-20 | 1068 | keep | 0 | Jan | 2023 | 0.00072741 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-20 12:50 | 2023-01-20 14:40 | 10 | 1:50 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REALIZO DESGANCHE SECUNDARIO Y SE RETEZO LINEA SECUNDARIA | S23012000148 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 110 | 2023-01-20 | 1100 | keep | 0 | Jan | 2023 | 0.0007492 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-01-20 12:57 | 2023-01-20 15:14 | 1 | 2:17 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23012000088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2023-01-20 | 137 | keep | 0 | Jan | 2023 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-20 13:19 | 2023-01-20 14:28 | 6 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES SECUNDARIOS @ LA SALIDA DEL XMR | B23012000048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2023-01-20 | 414 | keep | 0 | Jan | 2023 | 0.00028197 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-01-20 13:55 | 2023-01-20 15:51 | 100 | 1:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZA CAJA PRIMARIA 2 X 80 ENCORTE DE LINEA 1 X 65 EN CORTE DE LINEA | R23012000056 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2023-01-20 | 11600 | keep | 0 | Jan | 2023 | 0.0079007 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-20 14:40 | 2023-01-20 18:36 | 140 | 3:56 | P | ANIMAL | 1 X 50 EN SU-6 1 X 40 EN RISER 1 X 30 EN C/L CRUCE X AVE | B23012000057 | New_Event | Animals | Include | Include | Wildlife | 236 | 2023-01-20 | 33040 | keep | 0 | Jan | 2023 | 0.022503 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
SAN JUAN | 2023-01-20 15:17 | 2023-01-20 18:43 | 345 | 3:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | S23012000189 | New_Event | Primary Wire Break | Include | Include | Equipment | 206 | 2023-01-20 | 71070 | keep | 0 | Jan | 2023 | 0.048405 | 0.00023498 | Sustained | FALSE | FALSE | Not_TMED_Event | 345
BAYAMON | 2023-01-20 15:17 | 2023-01-20 16:55 | 12 | 1:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | S23012000186 | New_Event | Secondary Wire Break | Include | Include | Equipment | 98 | 2023-01-20 | 1176 | keep | 0 | Jan | 2023 | 0.00080097 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-20 15:22 | 2023-01-20 16:01 | 10 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIAS | S23012000188 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-01-20 | 390 | keep | 0 | Jan | 2023 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-20 15:31 | 2023-01-20 15:32 | 435 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1345-03 CARGA X 1345-03 | S2301200000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-20 | 435 | keep | 0 | Jan | 2023 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-01-20 15:31 | 2023-01-20 15:32 | 259 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1345-03 LLEVA CARGA 1345-02 | S2301200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-20 | 259 | keep | 0 | Jan | 2023 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
MAYAGÃœEZ | 2023-01-20 15:52 | 2023-01-20 18:30 | 80 | 2:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | M23012000099 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2023-01-20 | 12640 | keep | 0 | Jan | 2023 | 0.008609 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-20 16:01 | 2023-01-20 17:40 | 100 | 1:39 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEA | S23012000212 | New_Event | Animals | Include | Include | Wildlife | 99 | 2023-01-20 | 9900 | keep | 0 | Jan | 2023 | 0.0067428 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-20 16:01 | 2023-01-20 18:45 | 10 | 2:44 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE PARTIDO | B23012000042 | New_Event | Primary Pole Failure | Include | Include | Equipment | 164 | 2023-01-20 | 1640 | keep | 0 | Jan | 2023 | 0.001117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-20 16:09 | 2023-01-20 18:34 | 10 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE IINSTALO PROVISIONAL AEREO SECUNDARIO | R23011900073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-01-20 | 1450 | keep | 0 | Jan | 2023 | 0.00098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-20 17:01 | 2023-01-20 17:02 | 1478 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE AL CERRAR RISER AVERIADO | P23012000093 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-20 | 1478 | keep | 0 | Jan | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
CANOVANAS | 2023-01-20 17:04 | 2023-01-20 17:58 | 10 | 0:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y SE REEMPLAZO PORTAFUSIBLE | R23012000077 | New_Event | Cutout Failure | Include | Include | Equipment | 54 | 2023-01-20 | 540 | keep | 0 | Jan | 2023 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-01-20 17:12 | 2023-01-20 18:10 | 8 | 0:58 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | P23012000094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2023-01-20 | 464 | keep | 0 | Jan | 2023 | 0.00031603 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-20 17:17 | 2023-01-20 18:53 | 20 | 1:36 | P | NO SE REPORTO CAUSA | 1 X 30 EN AEREO PROVISIONAL | S23012000240 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2023-01-20 | 1920 | keep | 0 | Jan | 2023 | 0.0013077 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-20 17:28 | 2023-01-20 17:55 | 20 | 0:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARA SECUNDARIA | B23012000080 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2023-01-20 | 540 | keep | 0 | Jan | 2023 | 0.00036779 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-20 18:11 | 2023-01-20 21:40 | 12 | 3:29 | P | NO SE REPORTO CAUSA | 2 X 125 EN SU 1 | S23012000257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2023-01-20 | 2508 | keep | 0 | Jan | 2023 | 0.0017082 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-20 18:20 | 2023-01-20 21:00 | 30 | 2:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REEMPLAZO CAJA PRIMARIA | S23012000250 | New_Event | Cutout Failure | Include | Include | Equipment | 160 | 2023-01-20 | 4800 | keep | 0 | Jan | 2023 | 0.0032693 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-01-20 18:50 | 2023-01-21 09:47 | 15 | 14:57 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA POR CONTAMINACION (FRENTE PLAYA) | A23012000093 | New_Event | Damage From Public | Include | Include | Public | 897 | 2023-01-20 | 13455 | keep | 0 | Jan | 2023 | 0.0091641 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-01-20 19:02 | 2023-01-20 19:03 | 817 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23012000087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-20 | 817 | keep | 0 | Jan | 2023 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CANOVANAS | 2023-01-20 19:24 | 2023-01-20 21:28 | 100 | 2:04 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE PARA SECCIONALIZAR Y PASAR CARGA AL 1620-5 ALAMBRE SAFADO DE HOT CLAMP Y CAYO AL PISO TRAS PATIO | R23012000097 | New_Event | Primary Wire Break | Include | Include | Equipment | 124 | 2023-01-20 | 12400 | keep | 0 | Jan | 2023 | 0.0084456 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-20 19:52 | 2023-01-21 01:34 | 191 | 5:42 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN C/L SE SECCIONALIZO TRAMO, PARA CONTINUAR TRABAJOS LUEGO | B23012000091 | New_Event | UG Cable Fault | Include | Include | Equipment | 342 | 2023-01-20 | 65322 | keep | 0 | Jan | 2023 | 0.044491 | 0.00013009 | Sustained | FALSE | FALSE | Not_TMED_Event | 191
CAGUAS | 2023-01-20 20:37 | 2023-01-21 09:36 | 4 | 12:59 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | C23012000146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 779 | 2023-01-20 | 3116 | keep | 0 | Jan | 2023 | 0.0021223 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2023-01-20 20:43 | 2023-01-20 22:17 | 1 | 1:34 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R23012000123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-01-20 | 94 | keep | 0 | Jan | 2023 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-20 20:49 | 2023-01-20 20:50 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C23012000148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-20 | 1702 | keep | 0 | Jan | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CANOVANAS | 2023-01-20 21:28 | 2023-01-20 21:38 | 500 | 0:10 | P | CONDUCTOR ROTO O ABIERTO | SE PASO CLIENTES DEL 1646-01 AL 1620-5 ALAMBRE EN EL PISO SE SAFO DE HOT CLAMP TRAMO TRAS PATIO | R23012000097 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 10 | 2023-01-20 | 5000 | keep | 0 | Jan | 2023 | 0.0034055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-20 21:38 | 2023-01-20 22:08 | 20 | 0:30 | P | CONDUCTOR ROTO O ABIERTO | SE PASO CLIENTES DEL 1646-01 AL 1620-5 ALAMBRE EN EL PISO SE SAFO DE HOT CLAMP TRAMO TRAS PATIO SE SECCIONALIZO CONDUCTOR EN EL SUELO | R23012000097 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 30 | 2023-01-20 | 600 | keep | 0 | Jan | 2023 | 0.00040866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-20 22:52 | 2023-01-21 08:31 | 4 | 9:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S23012000267 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 579 | 2023-01-20 | 2316 | keep | 0 | Jan | 2023 | 0.0015774 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-01-20 22:52 | 2023-01-21 | 20 | 1:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C23012000149 | New_Event | Cutout Failure | Include | Include | Equipment | 68 | 2023-01-20 | 1360 | keep | 0 | Jan | 2023 | 0.00092629 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-21 01:34 | 2023-01-21 19:55 | 10 | 18:21 | P | CABLE SOTERRADO AVERIADO | MEDIANTE GOI BY-230121-02 SE REPARO TRAMO DEL T-151 @ T-150 | B23012000091 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1101 | 2023-01-21 | 11010 | keep | 0 | Jan | 2023 | 0.0074989 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-01-21 02:20 | 2023-01-21 08:53 | 50 | 6:33 | P | DESGANCHE | 2 X 40 EN CL SE REMOVIO RAMA DE PINO | M23012100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2023-01-21 | 19650 | keep | 0 | Jan | 2023 | 0.013384 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-01-21 03:18 | 2023-01-21 03:19 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2301210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-21 | 3000 | keep | 0 | Jan | 2023 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2023-01-21 03:50 | 2023-01-21 12:55 | 50 | 9:05 | P | ANIMAL | 1 SMU X 25 Y 2 X 50 EN RISER Y 1 X 1OO EN C/L CRUCE X RATON | B23012100002 | New_Event | Animals | Include | Include | Wildlife | 545 | 2023-01-21 | 27250 | keep | 0 | Jan | 2023 | 0.01856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-01-21 05:10 | 2023-01-21 07:24 | 1066 | 2:14 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO RAMA CRUZANDO CAJA PRIMARIA Y NEUTRAL PRIMARIO | A23012100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-01-21 | 142844 | keep | 0 | Jan | 2023 | 0.09729 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
PONCE | 2023-01-21 07:27 | 2023-01-21 07:28 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23012100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-21 | 2379 | keep | 0 | Jan | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
CANOVANAS | 2023-01-21 07:42 | 2023-01-21 08:29 | 4 | 0:47 | P | PARARRAYOS DEFECTUOSO | SE RETIRO PARARRAYO QUEMADO/SE REMPLAZO BAJANTE PRIMARIO | R23012100006 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 47 | 2023-01-21 | 188 | keep | 0 | Jan | 2023 | 0.00012805 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-01-21 07:45 | 2023-01-21 13:05 | 8 | 5:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR POSTE SECUNDARIO | S23012100009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 320 | 2023-01-21 | 2560 | keep | 0 | Jan | 2023 | 0.0017436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-21 08:05 | 2023-01-21 11:14 | 12 | 3:09 | P | ANIMAL | 1X10 EN XMR CRUCE POR AVE | C23012100004 | New_Event | Animals | Include | Include | Wildlife | 189 | 2023-01-21 | 2268 | keep | 0 | Jan | 2023 | 0.0015447 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-01-21 08:16 | 2023-01-21 09:27 | 40 | 1:11 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASES | M23012100006 | New_Event | Animals | Include | Include | Wildlife | 71 | 2023-01-21 | 2840 | keep | 0 | Jan | 2023 | 0.0019343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2023-01-21 08:19 | 2023-01-21 10:33 | 40 | 2:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23012100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-01-21 | 5360 | keep | 0 | Jan | 2023 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-01-21 08:20 | 2023-01-21 11:39 | 19 | 3:19 | P | DESGANCHE | 1X40 EN C/L | C23012100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2023-01-21 | 3781 | keep | 0 | Jan | 2023 | 0.0025752 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
AGUADILLA | 2023-01-21 08:20 | 2023-01-21 12:15 | 8 | 3:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23012100011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 235 | 2023-01-21 | 1880 | keep | 0 | Jan | 2023 | 0.0012805 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-21 08:55 | 2023-01-21 09:16 | 4 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | M23011600016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2023-01-21 | 84 | keep | 0 | Jan | 2023 | 5.7212e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-01-21 09:14 | 2023-01-21 16:03 | 8 | 6:49 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE RELOCALIZO XMR A NUEVO POSTE | C23012100016 | New_Event | Primary Pole Failure | Include | Include | Equipment | 409 | 2023-01-21 | 3272 | keep | 0 | Jan | 2023 | 0.0022285 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-01-21 09:15 | 2023-01-21 11:40 | 3 | 2:25 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 25KVA X 37.5KVA | A23012100017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 145 | 2023-01-21 | 435 | keep | 0 | Jan | 2023 | 0.00029628 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-01-21 09:17 | 2023-01-21 18:31 | 12 | 9:14 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO. NO SE REPUSO FUSIBLE | S23012100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 554 | 2023-01-21 | 6648 | keep | 0 | Jan | 2023 | 0.0045279 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-01-21 09:21 | 2023-01-21 13:04 | 232 | 3:43 | P | PARARRAYOS DEFECTUOSO | 3X80 EN C/L SE REMPLAZARON (4) PARARRAYOS | C23012100018 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 223 | 2023-01-21 | 51736 | keep | 0 | Jan | 2023 | 0.035237 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
CANOVANAS | 2023-01-21 09:30 | 2023-01-21 09:31 | 7621 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE INTERRUPTOR AL MISMO TIEMPO QUE EL 2404-7 SE ENCONTRO MACHETE FASE A DEL 2404-7 PUNTO CALIENTE CORREN AMBOS MISMA ESTRUCTURA | R23012100010 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-01-21 | 7621 | keep | 0 | Jan | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2023-01-21 09:30 | 2023-01-21 09:31 | 3699 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE INTERRUPTOR AL MISMO TIEMPO QUE EL 2404-6 SE ENCONTRO MACHETE FASE A DEL 2404-7 PUNTO CALIENTE CORREN AMBOS MISMA ESTRUCTURA | R23012100011 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-01-21 | 3699 | keep | 0 | Jan | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2023-01-21 09:43 | 2023-01-21 12:05 | 11 | 2:22 | P | CONDUCTOR ROTO O ABIERTO | SE INSTALO HOT CLAMP SE HIZO DESGANCHE | R23012100013 | New_Event | Primary Wire Break | Include | Include | Equipment | 142 | 2023-01-21 | 1562 | keep | 0 | Jan | 2023 | 0.0010639 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-01-21 09:46 | 2023-01-21 09:47 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-21 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2023-01-21 09:55 | 2023-01-21 13:43 | 10 | 3:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 25KVA X 37.5KVA | C23012100028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 228 | 2023-01-21 | 2280 | keep | 0 | Jan | 2023 | 0.0015529 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-01-21 10:05 | 2023-01-21 10:15 | 15 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23012100015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-01-21 | 150 | keep | 0 | Jan | 2023 | 0.00010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-21 10:32 | 2023-01-21 10:33 | 5961 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1713-05 LLEVA 95 % DEL 1717-02 SE CERRO POR CONTROL | B2301210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-21 | 5961 | keep | 0 | Jan | 2023 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2023-01-21 10:32 | 2023-01-21 10:33 | 865 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1713-05 LLEVA 95 % DEL 1717-02 SE CERRO POR CONTROL | B2301210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-21 | 865 | keep | 0 | Jan | 2023 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
BARRANQUITAS | 2023-01-21 10:44 | 2023-01-21 16:31 | 30 | 5:47 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | C23012100030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 347 | 2023-01-21 | 10410 | keep | 0 | Jan | 2023 | 0.0070902 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-01-21 10:51 | 2023-01-21 12:52 | 1 | 2:01 | P | ANIMAL | 1X30 EN RISER CRUCE POR AVE | C23012100032 | New_Event | Animals | Include | Include | Wildlife | 121 | 2023-01-21 | 121 | keep | 0 | Jan | 2023 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-21 10:57 | 2023-01-21 11:35 | 12 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B23012100001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2023-01-21 | 456 | keep | 0 | Jan | 2023 | 0.00031058 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-01-21 12:05 | 2023-01-21 15:04 | 1 | 2:59 | P | ANIMAL | 1X40 EN C/L CRUCE POR AVE | C23012100045 | New_Event | Animals | Include | Include | Wildlife | 179 | 2023-01-21 | 179 | keep | 0 | Jan | 2023 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-01-21 12:17 | 2023-01-21 15:14 | 1 | 2:57 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | P23012100024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2023-01-21 | 177 | keep | 0 | Jan | 2023 | 0.00012055 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-21 12:23 | 2023-01-21 15:03 | 6 | 2:40 | P | DESGANCHE | 1X50 EN C/L | C23012100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-01-21 | 960 | keep | 0 | Jan | 2023 | 0.00065385 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-01-21 12:24 | 2023-01-21 12:25 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 50% DE SU CARGA ESTA POR 1909-07 Y LLEVA 1709-05 | S2301210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-21 | 766 | keep | 0 | Jan | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-01-21 12:24 | 2023-01-21 12:25 | 2364 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR 1709-03 50% DE SU CARGA ESTA POR 1909-07 Y LLEVA 1709-05 | S2301210000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-01-21 | 2364 | keep | 0 | Jan | 2023 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2023-01-21 12:25 | 2023-01-21 14:32 | 40 | 2:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA | S23012100036 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 127 | 2023-01-21 | 5080 | keep | 0 | Jan | 2023 | 0.00346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-21 12:38 | 2023-01-21 14:16 | 7 | 1:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR SECUNDARIA | S23012100039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 98 | 2023-01-21 | 686 | keep | 0 | Jan | 2023 | 0.00046723 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-01-21 12:40 | 2023-01-21 18:47 | 12 | 6:07 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S23012100062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 367 | 2023-01-21 | 4404 | keep | 0 | Jan | 2023 | 0.0029995 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-21 12:42 | 2023-01-21 14:14 | 12 | 1:32 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO Y REEMPLAZAR SECUNDARIA | S23012100040 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 92 | 2023-01-21 | 1104 | keep | 0 | Jan | 2023 | 0.00075193 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-01-21 12:54 | 2023-01-21 14:44 | 58 | 1:50 | P | ANIMAL | 1 X 40 EN RISER ANIMAL CRUZO LINEA | R23012100022 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-01-21 | 6380 | keep | 0 | Jan | 2023 | 0.0043454 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
GUAYAMA | 2023-01-21 13:27 | 2023-01-21 17:30 | 12 | 4:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR VIENTOS | P23012100027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 243 | 2023-01-21 | 2916 | keep | 0 | Jan | 2023 | 0.0019861 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-21 13:31 | 2023-01-21 14:55 | 80 | 1:24 | P | DESGANCHE | 1X80 EN C/L 1X65 EN OTRO C/L | B23012100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-01-21 | 6720 | keep | 0 | Jan | 2023 | 0.004577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-01-21 13:40 | 2023-01-21 16:10 | 12 | 2:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS ABIERTAS | A23012100037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 150 | 2023-01-21 | 1800 | keep | 0 | Jan | 2023 | 0.001226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-01-21 14:08 | 2023-01-21 15:11 | 1 | 1:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R23012100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-01-21 | 63 | keep | 0 | Jan | 2023 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-01-21 14:09 | 2023-01-21 17:10 | 2 | 3:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE CAMBIO AISLADOR 2 X 65 EN CORTE DE LINEA | P23012100029 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 181 | 2023-01-21 | 362 | keep | 0 | Jan | 2023 | 0.00024656 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-01-21 14:12 | 2023-01-21 14:13 | 5630 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | C23012100060 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-01-21 | 5630 | keep | 0 | Jan | 2023 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2023-01-21 14:13 | 2023-01-21 15:52 | 12 | 1:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X10 EN XMR SE REMPLAZO CAJA PRIMARIA | C23012100062 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 99 | 2023-01-21 | 1188 | keep | 0 | Jan | 2023 | 0.00080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-01-21 14:37 | 2023-01-21 18:03 | 4 | 3:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X8AMPS. EN XMR SE REMPLAZO PORTAFUSIBLE | C23012100063 | New_Event | Cutout Failure | Include | Include | Equipment | 206 | 2023-01-21 | 824 | keep | 0 | Jan | 2023 | 0.00056122 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-01-21 14:53 | 2023-01-21 16:00 | 50 | 1:07 | P | FUEGO | BOMBEROS APAGARON FUEGO Y SE CERRO C/L | B23012100045 | New_Event | Fire | Include | Include | Public | 67 | 2023-01-21 | 3350 | keep | 0 | Jan | 2023 | 0.0022817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-01-21 15:09 | 2023-01-21 16:21 | 20 | 1:12 | P | DESGANCHE | DESGANCHE 1 X 50 EN CORTE DE LINEA | P23012100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-01-21 | 1440 | keep | 0 | Jan | 2023 | 0.00098078 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-01-21 15:44 | 2023-01-21 16:44 | 13 | 1:00 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA POR CONDUCTOR PEGO A ESTRUCTURA | P23012100036 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 60 | 2023-01-21 | 780 | keep | 0 | Jan | 2023 | 0.00053125 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2023-01-21 15:58 | 2023-01-21 17:24 | 20 | 1:26 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR POR AVE | P23012100037 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-01-21 | 1720 | keep | 0 | Jan | 2023 | 0.0011715 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-21 16:04 | 2023-01-21 16:05 | 137 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 LLEVA 20% DEL 1342-04 | S23012100057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-21 | 137 | keep | 0 | Jan | 2023 | 9.331e-05 | 9.331e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-01-21 16:04 | 2023-01-21 16:05 | 760 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S23012100057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-21 | 760 | keep | 0 | Jan | 2023 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2023-01-21 16:04 | 2023-01-21 16:05 | 4291 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S23012100056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-21 | 4291 | keep | 0 | Jan | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-01-21 16:04 | 2023-01-21 16:05 | 414 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 20% DE LA CARGA X 1204-01 | S23012100056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-21 | 414 | keep | 0 | Jan | 2023 | 0.00028197 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
SAN JUAN | 2023-01-21 16:04 | 2023-01-21 16:05 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-21 | 4133 | keep | 0 | Jan | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2023-01-21 16:04 | 2023-01-21 16:05 | 78 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 20% X 1201-01 | S23012100057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-21 | 78 | keep | 0 | Jan | 2023 | 5.3125e-05 | 5.3125e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 78
UTUADO | 2023-01-21 16:11 | 2023-01-22 09:40 | 35 | 17:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23012100044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1049 | 2023-01-21 | 36715 | keep | 0 | Jan | 2023 | 0.025006 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-01-21 16:34 | 2023-01-21 17:47 | 23 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23012100056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-01-21 | 1679 | keep | 0 | Jan | 2023 | 0.0011436 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
AGUADILLA | 2023-01-21 16:58 | 2023-01-21 18:00 | 20 | 1:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23012100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2023-01-21 | 1240 | keep | 0 | Jan | 2023 | 0.00084456 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-01-21 16:58 | 2023-01-21 20:00 | 5 | 3:02 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23012100047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2023-01-21 | 910 | keep | 0 | Jan | 2023 | 0.0006198 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-01-21 17:11 | 2023-01-22 09:45 | 1 | 16:34 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23012100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 994 | 2023-01-21 | 994 | keep | 0 | Jan | 2023 | 0.00067701 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-21 17:39 | 2023-01-21 17:40 | 946 | 0:01 | T | ALIMENTADOR AMARRADO | SE CERRO POR CONTROL CARGA X 1525-05 | S23012100066 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-21 | 946 | keep | 0 | Jan | 2023 | 0.00064432 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
SAN JUAN | 2023-01-21 17:39 | 2023-01-21 17:40 | 937 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA 1525-02 | S23012100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-21 | 937 | keep | 0 | Jan | 2023 | 0.00063819 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
FAJARDO | 2023-01-21 18:13 | 2023-01-21 20:29 | 20 | 2:16 | P | NO SE REPORTO CAUSA | 1X40 DE RISER @ T-6 Y 1X25 EN EL T-6 | R23012100032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2023-01-21 | 2720 | keep | 0 | Jan | 2023 | 0.0018526 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-01-21 18:14 | 2023-01-21 19:40 | 139 | 1:26 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR ANIMAL | P23012100042 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-01-21 | 11954 | keep | 0 | Jan | 2023 | 0.0081418 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
VEGA BAJA | 2023-01-21 18:15 | 2023-01-21 19:30 | 7 | 1:15 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23012100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2023-01-21 | 525 | keep | 0 | Jan | 2023 | 0.00035758 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-01-21 18:42 | 2023-01-21 18:57 | 5 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO Y SE REPARO BAJANTE SECUNDARIO | R23012100031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-01-21 | 75 | keep | 0 | Jan | 2023 | 5.1082e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-01-21 19:26 | 2023-01-22 08:25 | 12 | 12:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23012100045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 779 | 2023-01-21 | 9348 | keep | 0 | Jan | 2023 | 0.0063669 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-21 19:38 | 2023-01-21 19:39 | 362 | 0:01 | P | ALIMENTADOR AMARRADO | CERRADO POR CONTROL 90% DE LA CARGA X 1620-01 | S2301210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-21 | 362 | keep | 0 | Jan | 2023 | 0.00024656 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-01-21 19:38 | 2023-01-21 19:39 | 36 | 0:01 | T | NO SE REPORTO CAUSA | CERRADO POR CONTROL LLEVA 90% DEL 1336-10 | S2301210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-21 | 36 | keep | 0 | Jan | 2023 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
FAJARDO | 2023-01-21 19:57 | 2023-01-21 19:58 | 1234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23012100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-21 | 1234 | keep | 0 | Jan | 2023 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
AGUADILLA | 2023-01-21 20:13 | 2023-01-22 16:25 | 12 | 20:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZA TRANSFORMADOR 50KVA POR 50 KVA AVERIADO | M23012100054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1212 | 2023-01-21 | 14544 | keep | 0 | Jan | 2023 | 0.0099059 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-01-21 21:01 | 2023-01-22 10:25 | 10 | 13:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23012100047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 804 | 2023-01-21 | 8040 | keep | 0 | Jan | 2023 | 0.005476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-21 22:26 | 2023-01-22 02:03 | 30 | 3:37 | P | DESGANCHE | 1 X 25 EN C/L POR DESGANCHE | B23012100069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2023-01-21 | 6510 | keep | 0 | Jan | 2023 | 0.0044339 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-01-21 22:59 | 2023-01-22 09:12 | 50 | 10:13 | P | NO SE REPORTO CAUSA | 2 X 65 EN CL NO SE ENCONTRO CAUSA | M22012100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 613 | 2023-01-21 | 30650 | keep | 0 | Jan | 2023 | 0.020876 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-01-22 00:09 | 2023-01-22 01:10 | 4009 | 1:01 | T | NO SE REPORTO CAUSA | SE CERRO BREAKER MANUAL NO CAUSA | P23012200021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2023-01-22 | 244549 | keep | 0 | Jan | 2023 | 0.16656 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
BAYAMON | 2023-01-22 03:26 | 2023-01-22 03:27 | 4079 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO | B2301220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-22 | 4079 | keep | 0 | Jan | 2023 | 0.0027782 | 0.0027782 | Momentary | FALSE | FALSE | Not_TMED_Event | 4079
BAYAMON | 2023-01-22 03:27 | 2023-01-22 15:46 | 2 | 12:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B23012200015 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 739 | 2023-01-22 | 1478 | keep | 0 | Jan | 2023 | 0.0010067 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-01-22 04:34 | 2023-01-22 14:00 | 567 | 9:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA | A23012200005 | New_Event | Primary Wire Break | Include | Include | Equipment | 566 | 2023-01-22 | 320922 | keep | 0 | Jan | 2023 | 0.21858 | 0.00038618 | Sustained | FALSE | FALSE | Not_TMED_Event | 567
YAUCO | 2023-01-22 05:12 | 2023-01-22 09:00 | 40 | 3:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P23012200109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-01-22 | 9120 | keep | 0 | Jan | 2023 | 0.0062116 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-01-22 06:21 | 2023-01-22 08:32 | 4 | 2:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23012200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-01-22 | 524 | keep | 0 | Jan | 2023 | 0.00035689 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-01-22 06:46 | 2023-01-22 07:54 | 8679 | 1:08 | P | DESGANCHE | SWF SJ-230122-01 SE SECCIONALIZO AREA DE DESGANCHE 85% POR 1206-03 | S23012200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-01-22 | 590172 | keep | 0 | Jan | 2023 | 0.40196 | 0.0059112 | Sustained | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-01-22 06:46 | 2023-01-22 07:54 | 4133 | 1:08 | T | ALIMENTADOR AMARRADO | SWF SJ-230122-01 SE SECCIONALIZO TRAMO DEL 1204-05 Y SE CERRO POR SCADA 1206-03 QUE LLEVA 85% DEL 1204-05 | S23012200007 | New_Event | Feeder Load Transferred | Include | Include | Other | 68 | 2023-01-22 | 281044 | keep | 0 | Jan | 2023 | 0.19142 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
HUMACAO | 2023-01-22 06:59 | 2023-01-22 07:00 | 989 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA CERRADO X CONTROL | C23012200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-22 | 989 | keep | 0 | Jan | 2023 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
SAN JUAN | 2023-01-22 07:54 | 2023-01-22 08:39 | 6509 | 0:45 | P | DESGANCHE | SWF SJ-230122-01 SE REALIZO DESGANCHE 100% EN SERVICO DEL 1204-05 85% POR 1206-03 | S23012200007 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 45 | 2023-01-22 | 292905 | keep | 0 | Jan | 2023 | 0.1995 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-01-22 08:05 | 2023-01-22 09:45 | 235 | 1:40 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23012200005 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-01-22 | 23500 | keep | 0 | Jan | 2023 | 0.016006 | 0.00016006 | Sustained | FALSE | FALSE | Not_TMED_Event | 235
BAYAMON | 2023-01-22 08:29 | 2023-01-22 11:12 | 12 | 2:43 | P | ARBOL SOBRE LINEA | SE ABRIO XMR SE RETIRO ARBOL ENTERO DE LA SECUNDARIA (NO FUNDIO) | B23012200007 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 163 | 2023-01-22 | 1956 | keep | 0 | Jan | 2023 | 0.0013322 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-01-22 08:30 | 2023-01-22 10:11 | 34 | 1:41 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23012200006 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-01-22 | 3434 | keep | 0 | Jan | 2023 | 0.0023389 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BARRANQUITAS | 2023-01-22 08:59 | 2023-01-22 12:46 | 30 | 3:47 | P | DESGANCHE | 1X50 SE RETIRO ENRREDADERA | C23012200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-01-22 | 6810 | keep | 0 | Jan | 2023 | 0.0046383 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-22 10:03 | 2023-01-22 12:16 | 10 | 2:13 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | S23012200093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-01-22 | 1330 | keep | 0 | Jan | 2023 | 0.00090586 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-01-22 10:10 | 2023-01-22 12:32 | 37 | 2:22 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN RISER PARARRAYO | R23012200009 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 142 | 2023-01-22 | 5254 | keep | 0 | Jan | 2023 | 0.0035785 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
AGUADILLA | 2023-01-22 10:26 | 2023-01-22 11:15 | 2 | 0:49 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTES PARA REMPLAZAR POSTE PRIMARIO | M23012200013 | New_Event | Primary Pole Failure | Include | Include | Equipment | 49 | 2023-01-22 | 98 | keep | 0 | Jan | 2023 | 6.6747e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-01-22 10:28 | 2023-01-22 11:45 | 7 | 1:17 | P | ANIMAL | 1 X 10 EN XMR CRUCE X REPTIL | C23012200016 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-01-22 | 539 | keep | 0 | Jan | 2023 | 0.00036711 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-01-22 10:42 | 2023-01-22 10:43 | 1648 | 0:01 | T | ANIMAL | RECERRO | R23012200010 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-22 | 1648 | keep | 0 | Jan | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-01-22 10:43 | 2023-01-22 12:06 | 175 | 1:23 | P | ANIMAL | 1 X 80 EN C/L Y 1 X 65 EN C/L CRUCE X AVE | R23012200013 | 1st_after_momentary | Animals | Include | Include | Wildlife | 83 | 2023-01-22 | 14525 | keep | 0 | Jan | 2023 | 0.0098929 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
YAUCO | 2023-01-22 10:44 | 2023-01-22 14:09 | 200 | 3:25 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P23012200128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-01-22 | 41000 | keep | 0 | Jan | 2023 | 0.027925 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2023-01-22 10:46 | 2023-01-22 11:38 | 2 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO DE XMR Y SE REPARO BAJANTE Y CONEXIONES SECUNDARIAS | R23012200011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-01-22 | 104 | keep | 0 | Jan | 2023 | 7.0834e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-01-22 10:57 | 2023-01-22 11:46 | 10 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA SUBIR TAP DEL 3 @ 4 Y SE REPARO SECUNDARIA | S23012200096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-01-22 | 490 | keep | 0 | Jan | 2023 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-22 11:01 | 2023-01-22 11:50 | 30 | 0:49 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR ANIMAL | P23012200133 | New_Event | Animals | Include | Include | Wildlife | 49 | 2023-01-22 | 1470 | keep | 0 | Jan | 2023 | 0.0010012 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-01-22 11:59 | 2023-01-22 14:43 | 2747 | 2:44 | T | ARBOL SOBRE LINEA | SE ELIMINO ARBOL SOBRE LINEA | P23012200138 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 164 | 2023-01-22 | 450508 | keep | 0 | Jan | 2023 | 0.30684 | 0.001871 | Sustained | FALSE | FALSE | Not_TMED_Event | 2747
BAYAMON | 2023-01-22 12:00 | 2023-01-22 12:26 | 11 | 0:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARARON CONECCIONES EN SECUNDARIA | B23012200012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 26 | 2023-01-22 | 286 | keep | 0 | Jan | 2023 | 0.00019479 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
GUAYAMA | 2023-01-22 12:05 | 2023-01-22 18:25 | 45 | 6:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | P23012200139 | New_Event | Primary Wire Break | Include | Include | Equipment | 380 | 2023-01-22 | 17100 | keep | 0 | Jan | 2023 | 0.011647 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-01-22 12:08 | 2023-01-22 14:14 | 1 | 2:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON (2) CAJAS PRIMARIAS EN MONTURA DE XMRS Y (1) TOMA DE SERVICIO | S23012200105 | New_Event | Cutout Failure | Include | Include | Equipment | 126 | 2023-01-22 | 126 | keep | 0 | Jan | 2023 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-22 12:08 | 2023-01-22 15:43 | 14 | 3:35 | P | DESGANCHE | 2 X 50 EN C/L | R23012200015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2023-01-22 | 3010 | keep | 0 | Jan | 2023 | 0.0020501 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-01-22 12:13 | 2023-01-22 14:09 | 21 | 1:56 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE PRIMARIO | R23012200017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-01-22 | 2436 | keep | 0 | Jan | 2023 | 0.0016591 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
GUAYAMA | 2023-01-22 12:19 | 2023-01-22 14:57 | 15 | 2:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE TRANSFORMADOR | P23012200142 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2023-01-22 | 2370 | keep | 0 | Jan | 2023 | 0.0016142 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-01-22 12:33 | 2023-01-22 21:10 | 60 | 8:37 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M23012200018 | New_Event | Primary Wire Break | Include | Include | Equipment | 517 | 2023-01-22 | 31020 | keep | 0 | Jan | 2023 | 0.021128 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-01-22 12:45 | 2023-01-22 12:46 | 725 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2301220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-22 | 725 | keep | 0 | Jan | 2023 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
MAYAGÃœEZ | 2023-01-22 12:53 | 2023-01-22 16:45 | 103 | 3:52 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23012200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-01-22 | 23896 | keep | 0 | Jan | 2023 | 0.016275 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
CAGUAS | 2023-01-22 13:01 | 2023-01-22 13:18 | 918 | 0:17 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO BKR PARA REMPLAZAR AISLADOR GOI CG-230122-01 | C23012200036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 17 | 2023-01-22 | 15606 | keep | 0 | Jan | 2023 | 0.010629 | 0.00062525 | Sustained | FALSE | FALSE | Not_TMED_Event | 918
MAYAGÃœEZ | 2023-01-22 13:10 | 2023-01-22 13:40 | 7 | 0:30 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA RETIRAR POSTE SECUNDARIO PARTIDO | M23012200021 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 30 | 2023-01-22 | 210 | keep | 0 | Jan | 2023 | 0.00014303 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-01-22 13:34 | 2023-01-22 16:37 | 50 | 3:03 | P | DESGANCHE | 1 X 50 EN C/L | C23012200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-01-22 | 9150 | keep | 0 | Jan | 2023 | 0.006232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-22 13:45 | 2023-01-22 14:20 | 10 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | C23012200062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-01-22 | 350 | keep | 0 | Jan | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-22 14:07 | 2023-01-22 15:37 | 22 | 1:30 | P | DESGANCHE | 1X100 EN C/L | S23012200109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-01-22 | 1980 | keep | 0 | Jan | 2023 | 0.0013486 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2023-01-22 14:11 | 2023-01-22 16:32 | 1 | 2:21 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A23012200015 | New_Event | Primary Wire Break | Include | Include | Equipment | 141 | 2023-01-22 | 141 | keep | 0 | Jan | 2023 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-01-22 14:14 | 2023-01-22 17:45 | 200 | 3:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23012200030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2023-01-22 | 42200 | keep | 0 | Jan | 2023 | 0.028742 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2023-01-22 14:26 | 2023-01-22 14:27 | 1109 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23012200176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-22 | 1109 | keep | 0 | Jan | 2023 | 0.00075533 | 0.00075533 | Momentary | FALSE | FALSE | Not_TMED_Event | 1109
CANOVANAS | 2023-01-22 14:38 | 2023-01-22 15:41 | 28 | 1:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R23012200038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2023-01-22 | 1764 | keep | 0 | Jan | 2023 | 0.0012015 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2023-01-22 14:44 | 2023-01-22 16:11 | 1 | 1:27 | P | NO SE REPORTO CAUSA | 1X10 EN MONTURA DE XMRS PRIVADA | S23012200113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-01-22 | 87 | keep | 0 | Jan | 2023 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-22 15:08 | 2023-01-22 18:00 | 30 | 2:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23012200036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-01-22 | 5160 | keep | 0 | Jan | 2023 | 0.0035145 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-01-22 15:09 | 2023-01-22 18:22 | 40 | 3:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR VIENTOS | P23012200179 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 193 | 2023-01-22 | 7720 | keep | 0 | Jan | 2023 | 0.0052581 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-01-22 15:23 | 2023-01-22 15:51 | 1666 | 0:28 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR PERSONAL EN EL AREA REALIZANDO TRABAJOS SE VERIFICO PERSONAL FUERA PARA CERRAR INTERRUPTOR | M23012200038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2023-01-22 | 46648 | keep | 0 | Jan | 2023 | 0.031772 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
SAN JUAN | 2023-01-22 15:51 | 2023-01-22 16:00 | 1106 | 0:09 | P | ALIMENTADOR AMARRADO | DISPARO DEL INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE CERRO POR CONTROL | S23012200115 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-01-22 | 9954 | keep | 0 | Jan | 2023 | 0.0067796 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-01-22 15:51 | 2023-01-22 16:00 | 1802 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE CERRO POR CONTROL | S23012200115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-01-22 | 16218 | keep | 0 | Jan | 2023 | 0.011046 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BARRANQUITAS | 2023-01-22 16:02 | 2023-01-22 16:42 | 16 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23012200067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-01-22 | 640 | keep | 0 | Jan | 2023 | 0.0004359 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-01-22 16:05 | 2023-01-22 17:46 | 6 | 1:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR REPARO SECUNDARIA CRUZADA | C23012200068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 101 | 2023-01-22 | 606 | keep | 0 | Jan | 2023 | 0.00041274 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-01-22 16:08 | 2023-01-22 17:00 | 15 | 0:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE CAMBIA CAJA QUEMADA | A23012200018 | New_Event | Cutout Failure | Include | Include | Equipment | 52 | 2023-01-22 | 780 | keep | 0 | Jan | 2023 | 0.00053125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-22 16:08 | 2023-01-22 18:52 | 41 | 2:44 | P | DESGANCHE | 2 X 50 EN C/L SE DESGANCHO | B23012200017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-01-22 | 6724 | keep | 0 | Jan | 2023 | 0.0045797 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CANOVANAS | 2023-01-22 16:09 | 2023-01-22 18:26 | 400 | 2:17 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | R23012200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2023-01-22 | 54800 | keep | 0 | Jan | 2023 | 0.037324 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CANOVANAS | 2023-01-22 16:10 | 2023-01-22 16:11 | 1894 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2301220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-22 | 1894 | keep | 0 | Jan | 2023 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
AGUADILLA | 2023-01-22 16:25 | 2023-01-22 17:30 | 60 | 1:05 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO ENCONTRADO LUEGO DE REMPLAZO DE TRANSFORMADOR | M23012100054 | New_Event | Primary Wire Break | Include | Include | Equipment | 65 | 2023-01-22 | 3900 | keep | 0 | Jan | 2023 | 0.0026563 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-01-22 16:29 | 2023-01-22 19:33 | 5 | 3:04 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESPEJO XMR | C23012200071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 184 | 2023-01-22 | 920 | keep | 0 | Jan | 2023 | 0.00062661 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-01-22 16:30 | 2023-01-22 17:55 | 25 | 1:25 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 25 EN CORTE DE LINEA LINEAS CRUZADAS | M23012200045 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 85 | 2023-01-22 | 2125 | keep | 0 | Jan | 2023 | 0.0014473 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-01-22 16:50 | 2023-01-22 19:14 | 30 | 2:24 | P | CAUSAS EXTERNAS | 1 X 20 Y 1 X 25 EN C/LS AUTO IMPACTO POSTE | C23012200073 | New_Event | Damage From Public | Include | Include | Public | 144 | 2023-01-22 | 4320 | keep | 0 | Jan | 2023 | 0.0029423 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-22 16:51 | 2023-01-22 16:52 | 3766 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2301220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-22 | 3766 | keep | 0 | Jan | 2023 | 0.002565 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
HUMACAO | 2023-01-22 17:38 | 2023-01-22 20:04 | 40 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | C23012200079 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2023-01-22 | 5840 | keep | 0 | Jan | 2023 | 0.0039776 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-22 17:46 | 2023-01-22 18:39 | 1 | 0:53 | P | DESGANCHE | 1X50 EN C/L | S23012200129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2023-01-22 | 53 | keep | 0 | Jan | 2023 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-22 18:22 | 2023-01-22 19:51 | 1 | 1:29 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN XMR ELIMINO PARARRAYO CRUZADO PRIVADO | R23012200050 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 89 | 2023-01-22 | 89 | keep | 0 | Jan | 2023 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-01-22 19:30 | 2023-01-23 08:26 | 20 | 12:56 | P | DESGANCHE | DESGANCHE MASIVO 2 X 100 EN CORTE DE LINEA | P23012200208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 776 | 2023-01-22 | 15520 | keep | 0 | Jan | 2023 | 0.010571 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-01-22 23:59 | 2023-01-23 10:35 | 89 | 10:36 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | C23012200085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 636 | 2023-01-22 | 56604 | keep | 0 | Jan | 2023 | 0.038553 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
CANOVANAS | 2023-01-23 00:36 | 2023-01-23 09:52 | 80 | 9:16 | P | DESGANCHE | 1 X 65 EN C/L | R23012300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 556 | 2023-01-23 | 44480 | keep | 0 | Jan | 2023 | 0.030295 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-23 02:33 | 2023-01-23 02:34 | 1812 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B23012300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 1812 | keep | 0 | Jan | 2023 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
SAN JUAN | 2023-01-23 02:49 | 2023-01-23 02:50 | 726 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 1346-04 | S23012300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 726 | keep | 0 | Jan | 2023 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-01-23 02:49 | 2023-01-23 02:50 | 3932 | 0:01 | T | ALIMENTADOR AMARRADO | CARGA TRANSFERIDA AL 1303-03 DISPARO Y SE CERRO POR CONTROL | S23012300004 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-23 | 3932 | keep | 0 | Jan | 2023 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
FAJARDO | 2023-01-23 03:51 | 2023-01-23 03:52 | 3003 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23012300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 3003 | keep | 0 | Jan | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
BAYAMON | 2023-01-23 04:14 | 2023-01-23 06:19 | 150 | 2:05 | P | PARARRAYOS DEFECTUOSO | 1X100 EN C/L SE DESPEGO PARARRAYO DE CRUCETA (A VARETA) | B23012300007 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 125 | 2023-01-23 | 18750 | keep | 0 | Jan | 2023 | 0.012771 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-01-23 05:05 | 2023-01-23 05:06 | 5668 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23012300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 5668 | keep | 0 | Jan | 2023 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2023-01-23 05:16 | 2023-01-23 07:21 | 837 | 2:05 | T | CABLE SOTERRADO AVERIADO | SWF SJ-230123-01 SE SECCIONALZO TRAMO CARGA X 1401-07 EN SERVICIO 60% DEL 1401-06 | S23012300009 | New_Event | UG Cable Fault | Include | Include | Equipment | 125 | 2023-01-23 | 104625 | keep | 0 | Jan | 2023 | 0.07126 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-01-23 05:16 | 2023-01-23 07:21 | 908 | 2:05 | T | ALIMENTADOR AMARRADO | SWF SJ-230123-01 SE SECCIONALZO TRAMO LLEVA 1401-06 EN SERVICIO 100 % DEL 1401-07 EN SERVICIO 60% DEL 1401-06 | S23012300009 | New_Event | Feeder Load Transferred | Include | Include | Other | 125 | 2023-01-23 | 113500 | keep | 0 | Jan | 2023 | 0.077304 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2023-01-23 05:17 | 2023-01-23 13:41 | 11 | 8:24 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE PARA SECCIONALIZAR PUENTE PRIMARIO ABIERTO MEDIANTE G.O.I. SJ-230123-02 | S23012300008 | New_Event | Primary Wire Break | Include | Include | Equipment | 504 | 2023-01-23 | 5544 | keep | 0 | Jan | 2023 | 0.003776 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-01-23 05:50 | 2023-01-23 05:51 | 989 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23012300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 989 | keep | 0 | Jan | 2023 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
SAN JUAN | 2023-01-23 06:15 | 2023-01-23 06:18 | 362 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL 1620-01 90% POR 1620-01 | S2301230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-23 | 1086 | keep | 0 | Jan | 2023 | 0.00073967 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-01-23 06:15 | 2023-01-23 06:18 | 36 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 90% DEL 1336-10 | S2301230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-23 | 108 | keep | 0 | Jan | 2023 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-01-23 06:21 | 2023-01-23 11:51 | 16 | 5:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L SE REMPLAZO PORTAFUSIBLE | S23012300035 | New_Event | Cutout Failure | Include | Include | Equipment | 330 | 2023-01-23 | 5280 | keep | 0 | Jan | 2023 | 0.0035962 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2023-01-23 06:32 | 2023-01-23 13:44 | 4 | 7:12 | P | CONDUCTOR ROTO O ABIERTO | SE RERPARO BAJANTE DE TRANSFORMADOR | P23012300068 | New_Event | Primary Wire Break | Include | Include | Equipment | 432 | 2023-01-23 | 1728 | keep | 0 | Jan | 2023 | 0.0011769 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-01-23 06:59 | 2023-01-23 09:34 | 41 | 2:35 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | B23012300022 | New_Event | Animals | Include | Include | Wildlife | 155 | 2023-01-23 | 6355 | keep | 0 | Jan | 2023 | 0.0043284 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2023-01-23 06:59 | 2023-01-23 08:28 | 1 | 1:29 | P | DESGANCHE | 1X10 EN XMR | B23012300021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-01-23 | 89 | keep | 0 | Jan | 2023 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-23 07:07 | 2023-01-23 07:10 | 99 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1647-08 | R23012300017 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-23 | 297 | keep | 0 | Jan | 2023 | 0.00020229 | 6.7428e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 99
CANOVANAS | 2023-01-23 07:07 | 2023-01-23 07:10 | 1474 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA LA CARGA DEL 1647-06 CERRADO X CONTROL | R23012300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-23 | 4422 | keep | 0 | Jan | 2023 | 0.0030118 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
CANOVANAS | 2023-01-23 07:10 | 2023-01-23 12:01 | 172 | 4:51 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L REMPLAZO HOT CLAMP QUEMADO | R23012300016 | New_Event | Primary Wire Break | Include | Include | Equipment | 291 | 2023-01-23 | 50052 | keep | 0 | Jan | 2023 | 0.03409 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2023-01-23 07:21 | 2023-01-23 13:15 | 363 | 5:54 | P | CABLE SOTERRADO AVERIADO | SWF SJ-230123-01 SE SECCIONALIZO AVERIA SOTERRADA DE RISER A SU3 Y SE CERRO N/O CONTRA 1401-09 CARGA X 1401-07 EN SERVICIO 100 % DEL 1401-06 | S23012300009 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 354 | 2023-01-23 | 128502 | keep | 0 | Jan | 2023 | 0.087522 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-01-23 07:51 | 2023-01-23 09:55 | 7 | 2:04 | P | ANIMAL | 1 X 15 EN XMR CRUCE X RATA | R23012300019 | New_Event | Animals | Include | Include | Wildlife | 124 | 2023-01-23 | 868 | keep | 0 | Jan | 2023 | 0.00059119 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-01-23 07:53 | 2023-01-23 07:54 | 3147 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA CARGA A TRAVES DEL 6704-01(SPARE) | M23012300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 3147 | keep | 0 | Jan | 2023 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
HUMACAO | 2023-01-23 07:55 | 2023-01-23 09:22 | 54 | 1:27 | P | DESGANCHE | 2 X 40 EN C/L Y DESGANCHE | C23012300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2023-01-23 | 4698 | keep | 0 | Jan | 2023 | 0.0031998 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
GUAYAMA | 2023-01-23 08:14 | 2023-01-23 08:59 | 15 | 0:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA 1 X 50 EN CORTE DE LINEA | P23012300015 | New_Event | Cutout Failure | Include | Include | Equipment | 45 | 2023-01-23 | 675 | keep | 0 | Jan | 2023 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-01-23 08:15 | 2023-01-23 09:30 | 8 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23012200063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-01-23 | 600 | keep | 0 | Jan | 2023 | 0.00040866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-01-23 08:17 | 2023-01-23 09:15 | 22 | 0:58 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA Y SE HIZO DEGANCHE | P23012300016 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 58 | 2023-01-23 | 1276 | keep | 0 | Jan | 2023 | 0.00086908 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
VEGA BAJA | 2023-01-23 08:20 | 2023-01-23 08:21 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23012300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 1310 | keep | 0 | Jan | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CAGUAS | 2023-01-23 08:24 | 2023-01-23 10:32 | 2 | 2:08 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23012300001 | New_Event | Animals | Include | Include | Wildlife | 128 | 2023-01-23 | 256 | keep | 0 | Jan | 2023 | 0.00017436 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-01-23 08:32 | 2023-01-23 11:55 | 50 | 3:23 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23012300019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2023-01-23 | 10150 | keep | 0 | Jan | 2023 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-01-23 08:52 | 2023-01-23 10:55 | 97 | 2:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZA CAJA PRIMARIA AVERIADA | A23012300001 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2023-01-23 | 11931 | keep | 0 | Jan | 2023 | 0.0081261 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
BAYAMON | 2023-01-23 08:55 | 2023-01-23 10:19 | 1 | 1:24 | P | DESGANCHE | 1X30 DE RISER @ BOVEDA Y SE REALIZO DESGANCHE | B23012300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-01-23 | 84 | keep | 0 | Jan | 2023 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-23 08:55 | 2023-01-23 11:18 | 12 | 2:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON LAS (3) BARRAS EN EL PEDESTAL | B23012300033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 143 | 2023-01-23 | 1716 | keep | 0 | Jan | 2023 | 0.0011688 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-23 08:58 | 2023-01-23 17:01 | 12 | 8:03 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR SE REPARO TRAMO SECUNDARIO | S23012300084 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 483 | 2023-01-23 | 5796 | keep | 0 | Jan | 2023 | 0.0039476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-01-23 09:19 | 2023-01-23 11:00 | 80 | 1:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23012300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2023-01-23 | 8080 | keep | 0 | Jan | 2023 | 0.0055033 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-01-23 09:25 | 2023-01-23 12:00 | 100 | 2:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M23012300019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 155 | 2023-01-23 | 15500 | keep | 0 | Jan | 2023 | 0.010557 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-01-23 09:26 | 2023-01-23 13:41 | 40 | 4:15 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23012300027 | New_Event | Animals | Include | Include | Wildlife | 255 | 2023-01-23 | 10200 | keep | 0 | Jan | 2023 | 0.0069472 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-01-23 09:28 | 2023-01-23 13:49 | 1 | 4:21 | P | DESGANCHE | 1 X 50 EN C/L 1 X 40 EN RISER Y 1 SMU 20 DE 20AMP EN EL SU DESGANCHE | R23012300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2023-01-23 | 261 | keep | 0 | Jan | 2023 | 0.00017777 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-01-23 09:40 | 2023-01-23 14:45 | 60 | 5:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23012300019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2023-01-23 | 18300 | keep | 0 | Jan | 2023 | 0.012464 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-01-23 09:43 | 2023-01-23 12:44 | 15 | 3:01 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR Y DESGACNHE DE ENREDARERA | C23012300035 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 181 | 2023-01-23 | 2715 | keep | 0 | Jan | 2023 | 0.0018492 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-01-23 09:46 | 2023-01-23 09:47 | 989 | 0:01 | T | ARBOL SOBRE LINEA | DISPARO DE BKR SE CERRO POR CONTROL | C23012300036 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2023-01-23 | 989 | keep | 0 | Jan | 2023 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2023-01-23 09:50 | 2023-01-23 12:37 | 989 | 2:47 | T | ARBOL SOBRE LINEA | DISPARO DE BKR POR ARBOL SOBRE LINEAS SE HICIERON OPERACIONES CON EL CG-230123-01 | C23012300037 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 167 | 2023-01-23 | 165163 | keep | 0 | Jan | 2023 | 0.11249 | 0.0006736 | Sustained | FALSE | FALSE | Not_TMED_Event | 989
BAYAMON | 2023-01-23 09:57 | 2023-01-23 14:00 | 36 | 4:03 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN RISER SE REPARO AVERIA T-22 @ T-21 | B23012300043 | New_Event | UG Cable Fault | Include | Include | Equipment | 243 | 2023-01-23 | 8748 | keep | 0 | Jan | 2023 | 0.0059582 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
GUAYAMA | 2023-01-23 10:02 | 2023-01-23 12:08 | 70 | 2:06 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P23012300037 | New_Event | Animals | Include | Include | Wildlife | 126 | 2023-01-23 | 8820 | keep | 0 | Jan | 2023 | 0.0060073 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-01-23 10:15 | 2023-01-23 12:20 | 15 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23012300014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2023-01-23 | 1875 | keep | 0 | Jan | 2023 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-01-23 10:44 | 2023-01-23 11:58 | 2 | 1:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA SE REPARAR CONEXIONES EN XMR Y PEDESTAL | R23011200038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 74 | 2023-01-23 | 148 | keep | 0 | Jan | 2023 | 0.0001008 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-01-23 10:58 | 2023-01-23 12:46 | 40 | 1:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CL NO SE REPORTA CAUSA | A23012300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2023-01-23 | 4320 | keep | 0 | Jan | 2023 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-23 11:26 | 2023-01-23 15:09 | 70 | 3:43 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | S23012300129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2023-01-23 | 15610 | keep | 0 | Jan | 2023 | 0.010632 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-01-23 11:47 | 2023-01-23 13:40 | 40 | 1:53 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEA A TIERRA | M23012300051 | New_Event | Animals | Include | Include | Wildlife | 113 | 2023-01-23 | 4520 | keep | 0 | Jan | 2023 | 0.0030786 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-23 11:48 | 2023-01-23 11:50 | 108 | 0:02 | T | NO SE REPORTO CAUSA | CERRADO POR CONTROL | S23012300132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-23 | 216 | keep | 0 | Jan | 2023 | 0.00014712 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2023-01-23 11:54 | 2023-01-23 11:55 | 225 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1303-05 CERRADO POR CONTROL CARGA POR 1303-05 | S2301230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-23 | 225 | keep | 0 | Jan | 2023 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-01-23 11:54 | 2023-01-23 11:55 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA EL 1303-04 | S2301230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 870 | keep | 0 | Jan | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2023-01-23 12:00 | 2023-01-23 12:01 | 1784 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 SE CERRO POR CONTROL | B2301230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-23 | 1784 | keep | 0 | Jan | 2023 | 0.0012151 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2023-01-23 12:00 | 2023-01-23 12:01 | 453 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 SE CERRO POR CONTROL | B2301230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-23 | 453 | keep | 0 | Jan | 2023 | 0.00030854 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-01-23 12:00 | 2023-01-23 12:01 | 186 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 SE CERRO POR CONTROL | B2301230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 186 | keep | 0 | Jan | 2023 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
MAYAGÃœEZ | 2023-01-23 12:00 | 2023-01-23 12:09 | 1444 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR. SE CERRO POR CONTROL SCADA | M23012300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-01-23 | 12996 | keep | 0 | Jan | 2023 | 0.0088515 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2023-01-23 12:04 | 2023-01-23 12:12 | 1666 | 0:08 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS NO SE REPORTO CAUSA | M23012300056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2023-01-23 | 13328 | keep | 0 | Jan | 2023 | 0.0090776 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
BAYAMON | 2023-01-23 12:16 | 2023-01-23 14:30 | 60 | 2:14 | P | ANIMAL | 1 X 80 EN C/L 1 X 50 EN C/L CRUCE CON AVE | B23012300079 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-01-23 | 8040 | keep | 0 | Jan | 2023 | 0.005476 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-01-23 12:20 | 2023-01-23 17:18 | 2 | 4:58 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R23012300045 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 298 | 2023-01-23 | 596 | keep | 0 | Jan | 2023 | 0.00040593 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2023-01-23 12:22 | 2023-01-23 14:30 | 6 | 2:08 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R23012300047 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 128 | 2023-01-23 | 768 | keep | 0 | Jan | 2023 | 0.00052308 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-01-23 12:27 | 2023-01-23 14:47 | 1 | 2:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | R23012300048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2023-01-23 | 140 | keep | 0 | Jan | 2023 | 9.5353e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-23 12:31 | 2023-01-23 13:32 | 46 | 1:01 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | C23012300074 | New_Event | Animals | Include | Include | Wildlife | 61 | 2023-01-23 | 2806 | keep | 0 | Jan | 2023 | 0.0019112 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
CAGUAS | 2023-01-23 12:48 | 2023-01-23 13:48 | 4 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PM PARA REPARAR CONEXIONES EN BARRA DE PEDESTAL | C23012300051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-01-23 | 240 | keep | 0 | Jan | 2023 | 0.00016346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-01-23 12:50 | 2023-01-23 18:50 | 1 | 6:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23012300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2023-01-23 | 360 | keep | 0 | Jan | 2023 | 0.00024519 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-23 13:02 | 2023-01-23 15:02 | 40 | 2:00 | P | DESGANCHE | 1 X 50 EN C/L | R23012300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-01-23 | 4800 | keep | 0 | Jan | 2023 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-23 13:12 | 2023-01-23 13:13 | 276 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE 1345-02 LLEVA 80% DEL 1342-04 | S2301230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-23 | 276 | keep | 0 | Jan | 2023 | 0.00018798 | 0.00018798 | Momentary | FALSE | FALSE | Not_TMED_Event | 276
SAN JUAN | 2023-01-23 13:12 | 2023-01-23 13:13 | 435 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1345-02 LLEVA 80% DEL 1342-04 | S2301230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 435 | keep | 0 | Jan | 2023 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
ARECIBO | 2023-01-23 13:36 | 2023-01-23 15:42 | 437 | 2:06 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES A LA SALIDA DEL ALIMENTADOR | A23012300079 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 126 | 2023-01-23 | 55062 | keep | 0 | Jan | 2023 | 0.037502 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
YAUCO | 2023-01-23 13:38 | 2023-01-23 17:01 | 135 | 3:23 | P | DESGANCHE | 1 X 60 EN CORTE DE LINEA SE RETIRO BAMBUS | M23012300075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2023-01-23 | 27405 | keep | 0 | Jan | 2023 | 0.018665 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2023-01-23 13:41 | 2023-01-23 13:48 | 74 | 0:07 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO EN SU-5 @ RISER PARA TRANSFERIR PARTE DE LA CARGA AL 1908-03 POR PUENTE PRIMARIO ABIERTO MEDIANTE G.O.I. SJ-230123-02 | S23012300008 | New_Event | Primary Wire Break | Include | Include | Equipment | 7 | 2023-01-23 | 518 | keep | 0 | Jan | 2023 | 0.00035281 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2023-01-23 13:42 | 2023-01-23 13:43 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2023-01-23 13:42 | 2023-01-23 14:43 | 6 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA PARTIDA POR CAMION Y SE HIZO DESGANCHE | P23012300076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2023-01-23 | 366 | keep | 0 | Jan | 2023 | 0.00024928 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-23 13:48 | 2023-01-23 16:15 | 102 | 2:27 | P | CONDUCTOR ROTO O ABIERTO | SE TERMINO DE REPARAR PUENTE PRIMARIO ABIERTO MEDIANTE G.O.I. SJ-230123-02 Y SE VOLVIO A ABRIR DEL SU-5 @ RISER - (UNA VEZ, YA REPARADO EL PUENTE) NORMALIZADAS LAS CARGAS QUE SE HABIAN TRANSFERIDO | S23012300008 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 147 | 2023-01-23 | 14994 | keep | 0 | Jan | 2023 | 0.010212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-23 13:52 | 2023-01-23 14:50 | 2107 | 0:58 | T | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO MACHETES SECCIONALIZAR AVERIA | A23012300084 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 58 | 2023-01-23 | 122206 | keep | 0 | Jan | 2023 | 0.083234 | 0.0014351 | Sustained | FALSE | FALSE | Not_TMED_Event | 2107
CAGUAS | 2023-01-23 13:59 | 2023-01-23 16:48 | 59 | 2:49 | P | DESGANCHE | 1 X 40 EN C/L | C23012300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-01-23 | 9971 | keep | 0 | Jan | 2023 | 0.0067912 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BAYAMON | 2023-01-23 14:00 | 2023-01-24 14:16 | 13 | 24:16 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DEL T-121 @ T-122 MEDIANTE G.O.I. BY-221121-01 | B23012300043 | New_Event | UG Cable Fault | Include | Include | Equipment | 1456 | 2023-01-23 | 18928 | keep | 0 | Jan | 2023 | 0.012892 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-01-23 14:04 | 2023-01-23 22:05 | 30 | 8:01 | P | ANIMAL | 1 X 50 EN C/L IGUANA | B23012300096 | New_Event | Animals | Include | Include | Wildlife | 481 | 2023-01-23 | 14430 | keep | 0 | Jan | 2023 | 0.0098282 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-01-23 14:33 | 2023-01-23 16:53 | 8 | 2:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANATE SECUNDARIO | C23012300092 | New_Event | Secondary Wire Break | Include | Include | Equipment | 140 | 2023-01-23 | 1120 | keep | 0 | Jan | 2023 | 0.00076283 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-23 14:38 | 2023-01-23 16:24 | 10 | 1:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23012300094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 106 | 2023-01-23 | 1060 | keep | 0 | Jan | 2023 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-23 14:49 | 2023-01-23 15:17 | 1 | 0:28 | P | ANIMAL | 1 X 20 EN C/L AVE | B23012300104 | New_Event | Animals | Include | Include | Wildlife | 28 | 2023-01-23 | 28 | keep | 0 | Jan | 2023 | 1.9071e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-23 14:50 | 2023-01-23 17:43 | 1000 | 2:53 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETAS Y AISLADORES | A23012300084 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 173 | 2023-01-23 | 173000 | keep | 0 | Jan | 2023 | 0.11783 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-01-23 14:55 | 2023-01-23 15:35 | 6 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR REPARAR BAJANTES SECUNDARIOS WR6261709 EMERGENCIA FASE FUERA/SERVICIO SOLO EL CLIENTE ALIMENTADOR DE BARTOLO/ SAN SEBASTIAN | M23012300087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-01-23 | 240 | keep | 0 | Jan | 2023 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-01-23 14:59 | 2023-01-23 15:01 | 5630 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C2301230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-23 | 11260 | keep | 0 | Jan | 2023 | 0.0076691 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2023-01-23 15:08 | 2023-01-23 16:53 | 283 | 1:45 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN C/L DIFERENTES POR DESGANCHE | B23012300108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-01-23 | 29715 | keep | 0 | Jan | 2023 | 0.020239 | 0.00019275 | Sustained | FALSE | FALSE | Not_TMED_Event | 283
UTUADO | 2023-01-23 15:16 | 2023-01-23 18:00 | 3 | 2:44 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A23012300118 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 164 | 2023-01-23 | 492 | keep | 0 | Jan | 2023 | 0.0003351 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-01-23 15:21 | 2023-01-23 18:29 | 25 | 3:08 | P | DESGANCHE | 1 X10 EN XMR Y SE REPARO BAJANTE PRIMARIO Y DESGANCHE PRIMARIO | C23012300107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-01-23 | 4700 | keep | 0 | Jan | 2023 | 0.0032011 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-01-23 15:42 | 2023-01-23 16:28 | 1 | 0:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23012300096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 46 | 2023-01-23 | 46 | keep | 0 | Jan | 2023 | 3.133e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-23 16:56 | 2023-01-24 09:20 | 1 | 16:24 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A23012300155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 984 | 2023-01-23 | 984 | keep | 0 | Jan | 2023 | 0.0006702 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-23 17:23 | 2023-01-24 10:19 | 30 | 16:56 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA ( NO FUNDIO) | S23012300200 | New_Event | Primary Wire Break | Include | Include | Equipment | 1016 | 2023-01-23 | 30480 | keep | 0 | Jan | 2023 | 0.02076 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-23 17:25 | 2023-01-23 18:25 | 12 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA EN PEDESTAL | B23012300132 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-01-23 | 720 | keep | 0 | Jan | 2023 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-01-23 17:30 | 2023-01-23 19:05 | 1 | 1:35 | P | ANIMAL | 1 X 20 EN XMR Y 1 X 30 EN RISER CRUCE X RANA | R23012300080 | New_Event | Animals | Include | Include | Wildlife | 95 | 2023-01-23 | 95 | keep | 0 | Jan | 2023 | 6.4704e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-23 17:33 | 2023-01-23 18:32 | 25 | 0:59 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR IGUANA | R23012300074 | New_Event | Animals | Include | Include | Wildlife | 59 | 2023-01-23 | 1475 | keep | 0 | Jan | 2023 | 0.0010046 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-01-23 17:41 | 2023-01-23 18:50 | 15 | 1:09 | P | ARBOL SOBRE LINEA | SE ABRE INTERRUPTOR POR ARBOL SOBRE LINEA | M23012300112 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 69 | 2023-01-23 | 1035 | keep | 0 | Jan | 2023 | 0.00070493 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-01-23 18:13 | 2023-01-23 20:37 | 1 | 2:24 | P | SOBRECARGA | 1 X 65 EN RISER POR CARGA | M23012300119 | New_Event | Trip Due To Overload | Include | Include | Other | 144 | 2023-01-23 | 144 | keep | 0 | Jan | 2023 | 9.8078e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-23 18:20 | 2023-01-24 04:56 | 12 | 10:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN XMR | S23012300207 | New_Event | Cutout Failure | Include | Include | Equipment | 636 | 2023-01-23 | 7632 | keep | 0 | Jan | 2023 | 0.0051981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-01-23 18:25 | 2023-01-23 21:05 | 47 | 2:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR | B23012300140 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 160 | 2023-01-23 | 7520 | keep | 0 | Jan | 2023 | 0.0051218 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2023-01-23 18:35 | 2023-01-23 18:36 | 73 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO LLEVA 9207-08 | B2301230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-23 | 73 | keep | 0 | Jan | 2023 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2023-01-23 18:35 | 2023-01-23 18:36 | 1859 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN TRONCAL | B2301230000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-23 | 1859 | keep | 0 | Jan | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2023-01-23 18:36 | 2023-01-23 21:20 | 1859 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | B23012300150 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 164 | 2023-01-23 | 304876 | keep | 0 | Jan | 2023 | 0.20765 | 0.0012662 | Sustained | FALSE | FALSE | Not_TMED_Event | 1859
AGUADILLA | 2023-01-23 18:37 | 2023-01-23 18:45 | 129 | 0:08 | T | ERROR HUMANO | SE ABRE INTERRUPTOR ERRONEO POR NO SER EL DE LA SITUACION PELIGROSA | M23012300122 | New_Event | Human Error | Include | Include | Other | 8 | 2023-01-23 | 1032 | keep | 0 | Jan | 2023 | 0.00070289 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
VEGA BAJA | 2023-01-23 18:40 | 2023-01-23 19:38 | 8 | 0:58 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR AVE | A23012300175 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-01-23 | 464 | keep | 0 | Jan | 2023 | 0.00031603 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-01-23 18:50 | 2023-01-23 20:55 | 99 | 2:05 | T | ARBOL SOBRE LINEA | SE ABRE INTERRUPTOR POR ARBOL SOBRE LINEA | M23012300112 | Additional_clients | Vegetation Uprooted Tree | Include | Include | Vegetation | 125 | 2023-01-23 | 12375 | keep | 0 | Jan | 2023 | 0.0084286 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-01-23 18:51 | 2023-01-23 20:08 | 20 | 1:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA PORTA FUSIBLE | P23012300114 | New_Event | Cutout Failure | Include | Include | Equipment | 77 | 2023-01-23 | 1540 | keep | 0 | Jan | 2023 | 0.0010489 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-01-23 19:11 | 2023-01-23 19:12 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23012300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-23 | 7621 | keep | 0 | Jan | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CAGUAS | 2023-01-23 19:17 | 2023-01-23 22:59 | 260 | 3:42 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C23012300128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-01-23 | 57720 | keep | 0 | Jan | 2023 | 0.039313 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
VEGA BAJA | 2023-01-23 22:39 | 2023-01-23 22:43 | 3387 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B23012300300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-01-23 | 13548 | keep | 0 | Jan | 2023 | 0.0092275 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2023-01-23 22:43 | 2023-01-24 01:36 | 216 | 2:53 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23012300317 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 173 | 2023-01-23 | 37368 | keep | 0 | Jan | 2023 | 0.025451 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
MAYAGÃœEZ | 2023-01-23 23:55 | 2023-01-24 10:47 | 50 | 10:52 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23012300141 | New_Event | Primary Wire Break | Include | Include | Equipment | 652 | 2023-01-23 | 32600 | keep | 0 | Jan | 2023 | 0.022204 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-01-24 00:58 | 2023-01-24 00:59 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23012400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-24 | 308 | keep | 0 | Jan | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
HUMACAO | 2023-01-24 03:28 | 2023-01-24 08:56 | 40 | 5:28 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23012400001 | New_Event | Animals | Include | Include | Wildlife | 328 | 2023-01-24 | 13120 | keep | 0 | Jan | 2023 | 0.008936 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-24 04:06 | 2023-01-24 04:07 | 3295 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B2301240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-24 | 3295 | keep | 0 | Jan | 2023 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
AGUADILLA | 2023-01-24 04:08 | 2023-01-24 11:07 | 100 | 6:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M23012400005 | New_Event | Cutout Failure | Include | Include | Equipment | 419 | 2023-01-24 | 41900 | keep | 0 | Jan | 2023 | 0.028538 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-24 04:24 | 2023-01-24 04:26 | 3709 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S2301240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-24 | 7418 | keep | 0 | Jan | 2023 | 0.0050524 | 0.0025262 | Momentary | FALSE | FALSE | Not_TMED_Event | 3709
CANOVANAS | 2023-01-24 04:33 | 2023-01-24 10:00 | 9 | 5:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR Y SE REPARO SECUNDARIA | R23012400001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 327 | 2023-01-24 | 2943 | keep | 0 | Jan | 2023 | 0.0020045 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-01-24 04:45 | 2023-01-24 09:52 | 40 | 5:07 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23012400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2023-01-24 | 12280 | keep | 0 | Jan | 2023 | 0.0083639 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-01-24 04:53 | 2023-01-24 04:54 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23012400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-24 | 449 | keep | 0 | Jan | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
HUMACAO | 2023-01-24 05:41 | 2023-01-24 05:42 | 327 | 0:01 | T | ANIMAL | DISPARO DE BKR SE CERRO POR CONTROL | C2301240000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-24 | 327 | keep | 0 | Jan | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-24 05:42 | 2023-01-24 13:08 | 1 | 7:26 | P | ANIMAL | 1 X 10 EN XMR CRUCE X RANA | C23012400123 | 1st_after_momentary | Animals | Include | Include | Wildlife | 446 | 2023-01-24 | 446 | keep | 0 | Jan | 2023 | 0.00030377 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-24 05:54 | 2023-01-24 12:03 | 50 | 6:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X40 EN C/L Y 1X15 EN XMR POR LLUVIA | B23012400006 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 369 | 2023-01-24 | 18450 | keep | 0 | Jan | 2023 | 0.012566 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-01-24 06:00 | 2023-01-24 09:14 | 100 | 3:14 | P | DESGANCHE | 1 X 65 EN C/LY 1 X 50 EN C/L Y DESGANCHE | R23012400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-01-24 | 19400 | keep | 0 | Jan | 2023 | 0.013213 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-24 06:13 | 2023-01-24 10:37 | 30 | 4:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23012400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2023-01-24 | 7920 | keep | 0 | Jan | 2023 | 0.0053943 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-01-24 06:26 | 2023-01-24 07:55 | 200 | 1:29 | P | DESGANCHE | 1 X 140 EN C/L | C23012400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-01-24 | 17800 | keep | 0 | Jan | 2023 | 0.012123 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2023-01-24 06:31 | 2023-01-24 09:41 | 80 | 3:10 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23012400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-01-24 | 15200 | keep | 0 | Jan | 2023 | 0.010353 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-24 06:41 | 2023-01-24 11:23 | 30 | 4:42 | P | CONDUCTOR ROTO O ABIERTO | 2X50 EN C/L SE REPARO CONDUCTOR PRIMARIO | B23012400007 | New_Event | Primary Wire Break | Include | Include | Equipment | 282 | 2023-01-24 | 8460 | keep | 0 | Jan | 2023 | 0.0057621 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-24 06:54 | 2023-01-24 06:55 | 603 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR 9206-08 LLEVA LA CARGA DEL 9206-09 | B23012400010 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-01-24 | 603 | keep | 0 | Jan | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-01-24 06:54 | 2023-01-24 06:55 | 6 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-08 LLEVA LA CARGA DEL 9206-09 | B23012400010 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-24 | 6 | keep | 0 | Jan | 2023 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-01-24 06:55 | 2023-01-24 10:28 | 10 | 3:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN XMR SE REMPLAZO CAJA PRIMARIA | B23012400018 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 213 | 2023-01-24 | 2130 | keep | 0 | Jan | 2023 | 0.0014507 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-24 07:35 | 2023-01-24 07:36 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2301240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-24 | 4533 | keep | 0 | Jan | 2023 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
VEGA BAJA | 2023-01-24 07:46 | 2023-01-24 11:36 | 12 | 3:50 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | B23012400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2023-01-24 | 2760 | keep | 0 | Jan | 2023 | 0.0018798 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-01-24 07:49 | 2023-01-24 11:42 | 40 | 3:53 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE RETIRO PARARRAYO CRUZADO | C23012400066 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 233 | 2023-01-24 | 9320 | keep | 0 | Jan | 2023 | 0.0063478 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-01-24 08:17 | 2023-01-24 10:50 | 25 | 2:33 | P | ERROR HUMANO | 1 X 100 Y 1 X 80 EN CORTES DE LINEA PERSONAL COMPAÃ‘IA CENTURION DESGANCHANDO EN EL AREA | A23012400010 | New_Event | Human Error | Include | Include | Other | 153 | 2023-01-24 | 3825 | keep | 0 | Jan | 2023 | 0.0026052 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-01-24 08:24 | 2023-01-24 08:25 | 1227 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23012400011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-24 | 1227 | keep | 0 | Jan | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
CANOVANAS | 2023-01-24 08:37 | 2023-01-24 08:38 | 1937 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | R23012400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-24 | 1937 | keep | 0 | Jan | 2023 | 0.0013193 | 0.0013193 | Momentary | FALSE | FALSE | Not_TMED_Event | 1937
SAN JUAN | 2023-01-24 08:46 | 2023-01-24 12:32 | 30 | 3:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPAZARON 2 CAJAS PRIMARIAS | S23012400014 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2023-01-24 | 6780 | keep | 0 | Jan | 2023 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-24 08:56 | 2023-01-24 10:08 | 208 | 1:12 | P | ANIMAL | 1 X 100 EN C/L Y 1 X 80 EN RISER CRUCE X AVE | R23012400012 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-01-24 | 14976 | keep | 0 | Jan | 2023 | 0.0102 | 0.00014167 | Sustained | FALSE | FALSE | Not_TMED_Event | 208
CANOVANAS | 2023-01-24 08:56 | 2023-01-24 08:57 | 2675 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2301240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-24 | 2675 | keep | 0 | Jan | 2023 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
MAYAGÃœEZ | 2023-01-24 09:10 | 2023-01-24 15:35 | 3 | 6:25 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE CAJAS EN TRANSFORMADOR PARA REMPLAZAR POSTE PRIMARIO | M23012400101 | New_Event | Primary Pole Failure | Include | Include | Equipment | 385 | 2023-01-24 | 1155 | keep | 0 | Jan | 2023 | 0.00078667 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-01-24 09:24 | 2023-01-24 11:04 | 13 | 1:40 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR POSTE SECUNDARIO | C23012400089 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 100 | 2023-01-24 | 1300 | keep | 0 | Jan | 2023 | 0.00088542 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-01-24 10:00 | 2023-01-24 10:14 | 7 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BARRAS EN PEDESTAL AVERIADA | C23012400010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2023-01-24 | 98 | keep | 0 | Jan | 2023 | 6.6747e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-01-24 10:03 | 2023-01-24 13:30 | 150 | 3:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA/ VIENTO | A23012400027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 207 | 2023-01-24 | 31050 | keep | 0 | Jan | 2023 | 0.021148 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-01-24 10:09 | 2023-01-24 11:35 | 30 | 1:26 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23012400099 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-01-24 | 2580 | keep | 0 | Jan | 2023 | 0.0017572 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-24 10:09 | 2023-01-24 10:57 | 6 | 0:48 | P | CONDUCTOR ROTO O ABIERTO | 1X10 EN XMR SE REPARO BAJANTE PRIMARIO | B23012400036 | New_Event | Primary Wire Break | Include | Include | Equipment | 48 | 2023-01-24 | 288 | keep | 0 | Jan | 2023 | 0.00019616 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-01-24 10:15 | 2023-01-24 11:00 | 60 | 0:45 | P | DESGANCHE | 1X50 SE DESGANCHO PROVICIONAL AEREO, 1X20 RISER | R23012400022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2023-01-24 | 2700 | keep | 0 | Jan | 2023 | 0.001839 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-01-24 10:16 | 2023-01-24 12:20 | 20 | 2:04 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23012400032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-01-24 | 2480 | keep | 0 | Jan | 2023 | 0.0016891 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-01-24 10:17 | 2023-01-24 12:33 | 45 | 2:16 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE INSTALO POSTE Y SE CERRO TRANSFORMADOR | P23012400028 | New_Event | Primary Pole Failure | Include | Include | Equipment | 136 | 2023-01-24 | 6120 | keep | 0 | Jan | 2023 | 0.0041683 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-01-24 10:19 | 2023-01-24 11:41 | 1 | 1:22 | P | ANIMAL | 1X20 SU-J @ RISER CRUCE POR AVE | B23012400038 | New_Event | Animals | Include | Include | Wildlife | 82 | 2023-01-24 | 82 | keep | 0 | Jan | 2023 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-24 10:22 | 2023-01-24 11:30 | 5 | 1:08 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR IGUANA CRUZO BUSHING | A23012400035 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-01-24 | 340 | keep | 0 | Jan | 2023 | 0.00023157 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-01-24 10:54 | 2023-01-24 14:36 | 30 | 3:42 | P | ANIMAL | 1 X 30 EN C/L CRUCE X REPTIL | C23012400111 | New_Event | Animals | Include | Include | Wildlife | 222 | 2023-01-24 | 6660 | keep | 0 | Jan | 2023 | 0.0045361 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-01-24 11:05 | 2023-01-24 13:23 | 10 | 2:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRA DE PEDESTAL | C23012400113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 138 | 2023-01-24 | 1380 | keep | 0 | Jan | 2023 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-01-24 11:05 | 2023-01-24 12:46 | 90 | 1:41 | P | DESGANCHE | 2 X 40 Y 1 X 50 EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23012400151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-01-24 | 9090 | keep | 0 | Jan | 2023 | 0.0061912 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-01-24 11:09 | 2023-01-24 14:51 | 3 | 3:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO (NO FUNDIO) | S23012400043 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2023-01-24 | 666 | keep | 0 | Jan | 2023 | 0.00045361 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-01-24 11:13 | 2023-01-24 12:00 | 1 | 0:47 | P | PROBLEMA DEL CLIENTE | 1 SMU 20 DE 25AMP PROA | R23012400026 | New_Event | Customer-Related Interruption | Include | Include | Public | 47 | 2023-01-24 | 47 | keep | 0 | Jan | 2023 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-24 11:16 | 2023-01-24 14:09 | 2 | 2:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTE SECUNDARIO QUEMADO (NO FUNDIO) | B23012400050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 173 | 2023-01-24 | 346 | keep | 0 | Jan | 2023 | 0.00023566 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-01-24 11:17 | 2023-01-24 13:49 | 2 | 2:32 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO EN XMR (NO FUNDIO) | B23012400051 | New_Event | Primary Wire Break | Include | Include | Equipment | 152 | 2023-01-24 | 304 | keep | 0 | Jan | 2023 | 0.00020705 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-01-24 11:36 | 2023-01-24 14:05 | 2999 | 2:29 | T | ERROR HUMANO | PERSONAL COMPAÃ‘IA DE DESGANCHE AVERIA LINEA PRIMARIA Y FIBRA OPTICA SE ABRE MACHETES PARA SECCIONALIZAR Y SE COLOCA INTERRUPTOR EN SERVICIO MANUAL ELECTRICAMENTE | M23012400174 | New_Event | Human Error | Include | Include | Other | 149 | 2023-01-24 | 446851 | keep | 0 | Jan | 2023 | 0.30435 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
CANOVANAS | 2023-01-24 11:46 | 2023-01-24 14:12 | 195 | 2:26 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGANCHE | R23012400030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-01-24 | 28470 | keep | 0 | Jan | 2023 | 0.019391 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
GUAYAMA | 2023-01-24 11:48 | 2023-01-24 14:17 | 1 | 2:29 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA NO FUNDIO FUSIBLE | P23012400040 | New_Event | Primary Wire Break | Include | Include | Equipment | 149 | 2023-01-24 | 149 | keep | 0 | Jan | 2023 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-01-24 12:04 | 2023-01-24 12:18 | 4 | 0:14 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR Y SE DESGANCHO | R23012400033 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 14 | 2023-01-24 | 56 | keep | 0 | Jan | 2023 | 3.8141e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-01-24 12:07 | 2023-01-24 13:22 | 4 | 1:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO 2 CAJAS PRIMARIAS | R23012400034 | New_Event | Cutout Failure | Include | Include | Equipment | 75 | 2023-01-24 | 300 | keep | 0 | Jan | 2023 | 0.00020433 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-01-24 12:08 | 2023-01-24 13:15 | 8 | 1:07 | P | CAUSAS EXTERNAS | 1 X 8 EN TRANSFORMADOR VEHICULO IMPACTO POSTE Y CRUZO LINEAS | M23012400191 | New_Event | Damage From Public | Include | Include | Public | 67 | 2023-01-24 | 536 | keep | 0 | Jan | 2023 | 0.00036507 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-24 12:11 | 2023-01-24 14:42 | 2 | 2:31 | P | PARARRAYOS DEFECTUOSO | 1X80 EN C/L SE ELIMINO PARARRAYOS DEFECTUOSO | B23012400058 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 151 | 2023-01-24 | 302 | keep | 0 | Jan | 2023 | 0.00020569 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2023-01-24 12:18 | 2023-01-24 17:06 | 85 | 4:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A23012400053 | New_Event | Cutout Failure | Include | Include | Equipment | 288 | 2023-01-24 | 24480 | keep | 0 | Jan | 2023 | 0.016673 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2023-01-24 12:40 | 2023-01-24 12:42 | 476 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CHANGO QUEMADO EN AREA PORTAFUSIBLES SUB 3202 JUNCOS PROV | C23012400139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-24 | 952 | keep | 0 | Jan | 2023 | 0.0006484 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-01-24 12:40 | 2023-01-24 12:42 | 1655 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CHANGO QUEMADO EN AREA PORTAFUSIBLES SUB 3202 JUNCOS PROV | C23012400139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-24 | 3310 | keep | 0 | Jan | 2023 | 0.0022544 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-01-24 12:40 | 2023-01-24 12:42 | 361 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CHANGO QUEMADO EN AREA PORTAFUSIBLES SUB 3202 JUNCOS PROV | C23012400139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-24 | 722 | keep | 0 | Jan | 2023 | 0.00049175 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-01-24 12:40 | 2023-01-24 12:42 | 2842 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CHANGO QUEMADO EN AREA PORTAFUSIBLES SUB 3202 JUNCOS PROV | C23012400139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-24 | 5684 | keep | 0 | Jan | 2023 | 0.0038713 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-01-24 12:40 | 2023-01-24 12:42 | 1702 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CHANGO QUEMADO EN AREA PORTAFUSIBLES SUB 3202 JUNCOS PROV | C23012400138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-24 | 3404 | keep | 0 | Jan | 2023 | 0.0023184 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-01-24 12:40 | 2023-01-24 12:42 | 918 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CHANGO QUEMADO EN AREA PORTAFUSIBLES SUB 3202 JUNCOS PROV | C23012400138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-24 | 1836 | keep | 0 | Jan | 2023 | 0.0012505 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-01-24 12:40 | 2023-01-24 12:42 | 1725 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CHANGO QUEMADO EN AREA PORTAFUSIBLES SUB 3202 JUNCOS PROV | C23012400140 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-01-24 | 3450 | keep | 0 | Jan | 2023 | 0.0023498 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
CAGUAS | 2023-01-24 12:55 | 2023-01-24 18:19 | 100 | 5:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA QUEMADA | C23012400142 | New_Event | Cutout Failure | Include | Include | Equipment | 324 | 2023-01-24 | 32400 | keep | 0 | Jan | 2023 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-01-24 13:10 | 2023-01-24 13:41 | 20 | 0:31 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS ARRIADAS | M23012100020 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 31 | 2023-01-24 | 620 | keep | 0 | Jan | 2023 | 0.00042228 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-01-24 13:20 | 2023-01-24 14:00 | 40 | 0:40 | P | NO SE REPORTO CAUSA | 1 X 40 EN CONVERTIDOR NO SE REPORTO CAUSA | A23012400065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2023-01-24 | 1600 | keep | 0 | Jan | 2023 | 0.0010898 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-24 13:25 | 2023-01-24 13:59 | 30 | 0:34 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230124-02 SE SECCIONALIZA POSTE PARTIDO, EMERGENCIA SE AMARRO PARTE DE LA CARGA | S23012400063 | New_Event | Primary Pole Failure | Include | Include | Equipment | 34 | 2023-01-24 | 1020 | keep | 0 | Jan | 2023 | 0.00069472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-24 13:31 | 2023-01-25 00:13 | 11 | 10:42 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 20 EN XMR SE REEMPLAZO POSTE PRIMARIO Y SE REEMPLAZO XMR 50 KVA X 50 KVA | R23012400045 | New_Event | Primary Pole Failure | Include | Include | Equipment | 642 | 2023-01-24 | 7062 | keep | 0 | Jan | 2023 | 0.0048099 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2023-01-24 13:32 | 2023-01-24 15:37 | 10 | 2:05 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 100 EN CORTE DE LINEA CRUCE DE FASES | P23012400057 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 125 | 2023-01-24 | 1250 | keep | 0 | Jan | 2023 | 0.00085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-24 13:36 | 2023-01-24 14:39 | 12 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO/LEVANTO CONDUCTOR SECUNDARIO DEL SUELO | B23012400068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2023-01-24 | 756 | keep | 0 | Jan | 2023 | 0.00051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-01-24 13:48 | 2023-01-24 15:38 | 25 | 1:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE DEL MUNICIPIO | P23012400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-01-24 | 2750 | keep | 0 | Jan | 2023 | 0.001873 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-01-24 13:52 | 2023-01-24 15:54 | 80 | 2:02 | P | ANIMAL | 1 X 140 CRUCE POR AVE | C23012400159 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-01-24 | 9760 | keep | 0 | Jan | 2023 | 0.0066475 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-24 13:59 | 2023-01-24 21:15 | 15 | 7:16 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230124-02 SE ABRE INTERRUPTOR PARA NORMALIZAR PUENTES ABIERTOS LUEGO DE REMPLAZO DE POSTE Y NORMALIZAR CARGA TOTAL | S23012400063 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 436 | 2023-01-24 | 6540 | keep | 0 | Jan | 2023 | 0.0044544 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-24 14:04 | 2023-01-24 16:58 | 35 | 2:54 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23012400164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2023-01-24 | 6090 | keep | 0 | Jan | 2023 | 0.0041479 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-01-24 14:05 | 2023-01-24 15:27 | 381 | 1:22 | P | ERROR HUMANO | SE RETIRA ARBOL Y SE CERRO MACHETES | M23012400258 | Partial_restoration | Human Error | Include | Include | Other | 82 | 2023-01-24 | 31242 | keep | 0 | Jan | 2023 | 0.021279 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-24 14:16 | 2023-01-24 18:21 | 91 | 4:05 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | B23012400073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2023-01-24 | 22295 | keep | 0 | Jan | 2023 | 0.015185 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
HUMACAO | 2023-01-24 14:18 | 2023-01-24 14:45 | 5 | 0:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE | C23012400170 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2023-01-24 | 135 | keep | 0 | Jan | 2023 | 9.1948e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-01-24 14:20 | 2023-01-24 15:56 | 5 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES | M23012300095 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2023-01-24 | 480 | keep | 0 | Jan | 2023 | 0.00032693 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-24 14:23 | 2023-01-24 14:25 | 1483 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 15% 1204-05 LLEVA 5% 1336-07 | S2301240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-24 | 2966 | keep | 0 | Jan | 2023 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-01-24 14:23 | 2023-01-24 14:25 | 1531 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 15% 1204-05 LLEVA 5% 1336-07 | S2301240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-24 | 3062 | keep | 0 | Jan | 2023 | 0.0020855 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-01-24 14:23 | 2023-01-24 14:25 | 312 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 15% 1204-05 LLEVA 5% 1336-07 | S2301240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-24 | 624 | keep | 0 | Jan | 2023 | 0.000425 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-01-24 14:23 | 2023-01-24 14:25 | 5290 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 15% 1204-05 LLEVA 5% 1336-07 | S2301240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-24 | 10580 | keep | 0 | Jan | 2023 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
BARRANQUITAS | 2023-01-24 14:28 | 2023-01-24 16:57 | 35 | 2:29 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23012400178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-01-24 | 5215 | keep | 0 | Jan | 2023 | 0.0035519 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-01-24 14:40 | 2023-01-24 15:46 | 1825 | 1:06 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIMENTADOR POR CONDUCTOR EN SEL SUELO ENTRO 50% EN SERVICIO | S23012400083 | New_Event | Primary Wire Break | Include | Include | Equipment | 66 | 2023-01-24 | 120450 | keep | 0 | Jan | 2023 | 0.082038 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-01-24 14:41 | 2023-01-24 15:44 | 6 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23012400080 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2023-01-24 | 378 | keep | 0 | Jan | 2023 | 0.00025745 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-01-24 14:44 | 2023-01-24 20:40 | 5 | 5:56 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 20 EN C/L Y SE INSTALO POSTE PRIMARIO Y SE REEMPLAZO XMR DE 25 KVA X 37.5 KVA | R23012400059 | New_Event | Primary Pole Failure | Include | Include | Equipment | 356 | 2023-01-24 | 1780 | keep | 0 | Jan | 2023 | 0.0012123 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-01-24 15:00 | 2023-01-24 16:30 | 8 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | M23012400233 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-01-24 | 720 | keep | 0 | Jan | 2023 | 0.00049039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-01-24 15:11 | 2023-01-24 16:27 | 5 | 1:16 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | C23012400188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-01-24 | 380 | keep | 0 | Jan | 2023 | 0.00025882 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-01-24 15:15 | 2023-01-24 18:44 | 9 | 3:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 65 EN C/L Y 1 X 80 EN C/L SE REPARO SECUNDARIA | R23012400065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 209 | 2023-01-24 | 1881 | keep | 0 | Jan | 2023 | 0.0012811 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-01-24 15:17 | 2023-01-24 17:12 | 50 | 1:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A23012400090 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 115 | 2023-01-24 | 5750 | keep | 0 | Jan | 2023 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-24 15:41 | 2023-01-24 17:44 | 65 | 2:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO EL PORTAFUSIBLE | C23012400201 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2023-01-24 | 7995 | keep | 0 | Jan | 2023 | 0.0054454 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-01-24 15:46 | 2023-01-24 16:40 | 912 | 0:54 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIMENTADOR POR CONDUCTOR EN SEL SUELO ENTRO 100% EN SERVICIO | S23012400083 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 54 | 2023-01-24 | 49248 | keep | 0 | Jan | 2023 | 0.033543 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-24 16:11 | 2023-01-24 17:37 | 30 | 1:26 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23012400085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-01-24 | 2580 | keep | 0 | Jan | 2023 | 0.0017572 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-01-24 16:25 | 2023-01-24 19:17 | 12 | 2:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M23012400280 | New_Event | Secondary Wire Break | Include | Include | Equipment | 172 | 2023-01-24 | 2064 | keep | 0 | Jan | 2023 | 0.0014058 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-24 16:33 | 2023-01-24 16:34 | 1085 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | S23012400120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-24 | 1085 | keep | 0 | Jan | 2023 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
YAUCO | 2023-01-24 16:36 | 2023-01-24 19:55 | 2246 | 3:19 | T | CAUSAS EXTERNAS | SE ABRIERON MACHETES FID 1001137814 Y SE ABRIO CORTE DE LINEA DEL ALIMENTADOR PARA SACAR ALAMBRE ENCIMA DE ESTE ALIMENTADOR SE INSTALARON TIERRAS PARA DEJAR AREA DONDE ESTA EL AUTO ACCIDENTADO PARA QUE LO SAQUEN CON SEGURIDAD Y SE CERRO INTERRUPTOR | P23012400096 | New_Event | Damage From Public | Include | Include | Public | 199 | 2023-01-24 | 446954 | keep | 0 | Jan | 2023 | 0.30442 | 0.0015297 | Sustained | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2023-01-24 16:36 | 2023-01-24 16:40 | 1475 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23012400095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-01-24 | 5900 | keep | 0 | Jan | 2023 | 0.0040185 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
BAYAMON | 2023-01-24 16:39 | 2023-01-24 21:22 | 26 | 4:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X40 EN C/L SE REMPLAZO AISLADOR PRIMARIO | B23012400088 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 283 | 2023-01-24 | 7358 | keep | 0 | Jan | 2023 | 0.0050115 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
YAUCO | 2023-01-24 16:42 | 2023-01-24 18:03 | 75 | 1:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23012400097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-01-24 | 6075 | keep | 0 | Jan | 2023 | 0.0041377 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-01-24 16:51 | 2023-01-24 18:44 | 12 | 1:53 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23012400083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-01-24 | 1356 | keep | 0 | Jan | 2023 | 0.00092357 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-24 16:54 | 2023-01-24 16:56 | 5191 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23012400091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-24 | 10382 | keep | 0 | Jan | 2023 | 0.0070711 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
HUMACAO | 2023-01-24 17:09 | 2023-01-24 18:03 | 8 | 0:54 | P | ANIMAL | 1 X 8 EN XMR CRUCE X AVE | C23012400228 | New_Event | Animals | Include | Include | Wildlife | 54 | 2023-01-24 | 432 | keep | 0 | Jan | 2023 | 0.00029423 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-01-24 17:15 | 2023-01-24 18:32 | 19 | 1:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 10 Y 1 X 40 EN C/L | R23012400087 | New_Event | Cutout Failure | Include | Include | Equipment | 77 | 2023-01-24 | 1463 | keep | 0 | Jan | 2023 | 0.00099644 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-01-24 17:18 | 2023-01-24 17:54 | 10 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA | S23012400123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2023-01-24 | 360 | keep | 0 | Jan | 2023 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-01-24 17:35 | 2023-01-24 19:55 | 150 | 2:20 | P | MAL TIEMPO/RAYOS | 2 X 80 EN CORTE DE LINEA POR RAYO | M23012400294 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 140 | 2023-01-24 | 21000 | keep | 0 | Jan | 2023 | 0.014303 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-01-24 17:51 | 2023-01-25 12:30 | 5 | 18:39 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 CL SE CERRO PUENTE ABIERTO | S23012400145 | New_Event | Primary Wire Break | Include | Include | Equipment | 1119 | 2023-01-24 | 5595 | keep | 0 | Jan | 2023 | 0.0038107 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-24 17:52 | 2023-01-24 18:34 | 10 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON (2) BARRAS EN PEDESTAL REDONDO | B23012400098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2023-01-24 | 420 | keep | 0 | Jan | 2023 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-24 18:09 | 2023-01-24 19:04 | 7 | 0:55 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR Y SE CERRO PUENTE DE CAJA A BUSHING DEL TRANSFORMADOR | S23012400126 | New_Event | Primary Wire Break | Include | Include | Equipment | 55 | 2023-01-24 | 385 | keep | 0 | Jan | 2023 | 0.00026222 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-01-24 18:20 | 2023-01-24 20:27 | 14 | 2:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN C/L LLUVIA | R23012400096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 127 | 2023-01-24 | 1778 | keep | 0 | Jan | 2023 | 0.001211 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2023-01-24 18:28 | 2023-01-26 14:46 | 1 | 44:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | A23012600110 | New_Event | Cutout Failure | Include | Include | Equipment | 2658 | 2023-01-24 | 2658 | keep | 0 | Jan | 2023 | 0.0018104 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-24 18:36 | 2023-01-24 19:39 | 12 | 1:03 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASES | A23012400106 | New_Event | Animals | Include | Include | Wildlife | 63 | 2023-01-24 | 756 | keep | 0 | Jan | 2023 | 0.00051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-01-24 18:39 | 2023-01-24 19:44 | 65 | 1:05 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN CORTE DE LINEA SE RETIRO PARARRAYO QUEMADO | M23012400301 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 65 | 2023-01-24 | 4225 | keep | 0 | Jan | 2023 | 0.0028776 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2023-01-24 18:43 | 2023-01-24 20:13 | 80 | 1:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23012400251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2023-01-24 | 7200 | keep | 0 | Jan | 2023 | 0.0049039 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-01-24 18:49 | 2023-01-25 12:29 | 10 | 17:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA | A23012400107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1060 | 2023-01-24 | 10600 | keep | 0 | Jan | 2023 | 0.0072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-24 18:52 | 2023-01-24 19:53 | 40 | 1:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L REMPLAZO CAJA AVERIADA | C23012400254 | New_Event | Cutout Failure | Include | Include | Equipment | 61 | 2023-01-24 | 2440 | keep | 0 | Jan | 2023 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-01-24 18:57 | 2023-01-24 19:16 | 3464 | 0:19 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIMENTADOR PARA REEMPLAZAR AISLADOR PARTIDO ENTRO 40% EN SERVICIO | R23012400158 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 19 | 2023-01-24 | 65816 | keep | 0 | Jan | 2023 | 0.044827 | 0.0023593 | Sustained | FALSE | FALSE | Not_TMED_Event | 3464
BARRANQUITAS | 2023-01-24 19:10 | 2023-01-25 08:18 | 50 | 13:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA CRUCE POR PENCA DE PALMA | C23012400255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 788 | 2023-01-24 | 39400 | keep | 0 | Jan | 2023 | 0.026835 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-01-24 19:16 | 2023-01-24 20:03 | 2078 | 0:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR PARTIDO 100% EN SERVICIO | R23012400158 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 47 | 2023-01-24 | 97666 | keep | 0 | Jan | 2023 | 0.06652 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-24 19:39 | 2023-01-24 21:05 | 1 | 1:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN BANCO DE XMR | S23012400133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2023-01-24 | 86 | keep | 0 | Jan | 2023 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-01-24 19:40 | 2023-01-25 01:45 | 1 | 6:05 | P | CAUSAS EXTERNAS | SE ABRE CORTE DE LINEA PARA RETIRAR NEUTRAL PRIMARIO CRUZADO EN MONTURA AAA DEBIDO A POSTE PARTIDO POR ACCIDENTE DE AUTO | P23012400096 | New_Event | Damage From Public | Include | Include | Public | 365 | 2023-01-24 | 365 | keep | 0 | Jan | 2023 | 0.0002486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-24 19:51 | 2023-01-24 21:43 | 650 | 1:52 | P | ANIMAL | 1X100 EN C/L PRINCIPAL Y 1X65 EN OTRO C/L CRUCE POR AVE | B23012400105 | New_Event | Animals | Include | Include | Wildlife | 112 | 2023-01-24 | 72800 | keep | 0 | Jan | 2023 | 0.049584 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
YAUCO | 2023-01-24 19:55 | 2023-01-25 01:45 | 1978 | 5:50 | P | CAUSAS EXTERNAS | POSTE PARTIDO POR ACCIDENTE DE AUTO | P23012400122 | Partial_restoration | Damage From Public | Include | Include | Public | 350 | 2023-01-24 | 692300 | keep | 0 | Jan | 2023 | 0.47152 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-24 20:04 | 2023-01-24 20:56 | 4 | 0:52 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23012400272 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2023-01-24 | 208 | keep | 0 | Jan | 2023 | 0.00014167 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-01-24 21:05 | 2023-01-24 21:48 | 11 | 0:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23012400138 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2023-01-24 | 473 | keep | 0 | Jan | 2023 | 0.00032216 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-01-24 21:15 | 2023-01-24 22:10 | 30 | 0:55 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230124-02 SE REEMPLAZO POSTE PRIMARIO PARTIDO Y SE CERRO PUENTES PRIMARIOS | S23012400063 | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 55 | 2023-01-24 | 1650 | keep | 0 | Jan | 2023 | 0.0011238 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-01-24 21:29 | 2023-01-25 01:11 | 5 | 3:42 | P | CAUSAS EXTERNAS | 1 X 10 EN TRANSFORMADOR SE REMPLAZO POSTE SECUNDARIO PARTIDO POR IMPACTO DE AUTO | M23012400312 | New_Event | Damage From Public | Include | Include | Public | 222 | 2023-01-24 | 1110 | keep | 0 | Jan | 2023 | 0.00075602 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-24 21:36 | 2023-01-25 02:23 | 3 | 4:47 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | B23012400114 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 287 | 2023-01-24 | 861 | keep | 0 | Jan | 2023 | 0.00058642 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-01-24 23:30 | 2023-01-25 07:41 | 70 | 8:11 | P | MAL TIEMPO/RAYOS | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23012400118 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 491 | 2023-01-24 | 34370 | keep | 0 | Jan | 2023 | 0.023409 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2023-01-25 02:33 | 2023-01-25 02:34 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23012500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-25 | 5630 | keep | 0 | Jan | 2023 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
AGUADILLA | 2023-01-25 03:06 | 2023-01-25 09:10 | 60 | 6:04 | P | NO SE REPORTO CAUSA | 1 X 50 EN CL NO SE ENCONTRO CAUSA | M23012500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 364 | 2023-01-25 | 21840 | keep | 0 | Jan | 2023 | 0.014875 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-01-25 03:14 | 2023-01-25 03:15 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2301250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-25 | 853 | keep | 0 | Jan | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
BAYAMON | 2023-01-25 03:15 | 2023-01-25 03:16 | 1834 | 0:01 | T | DESGANCHE | RECIERRE | B2301250000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-25 | 1834 | keep | 0 | Jan | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2023-01-25 03:16 | 2023-01-25 10:25 | 1 | 7:09 | P | DESGANCHE | 1 X 15 TRANSFORMADOR DESGANCHE PRIMARIO | B23012500001 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 429 | 2023-01-25 | 429 | keep | 0 | Jan | 2023 | 0.00029219 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-25 03:27 | 2023-01-25 03:28 | 1210 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2301250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-25 | 1210 | keep | 0 | Jan | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
CANOVANAS | 2023-01-25 03:50 | 2023-01-25 03:51 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23012500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-25 | 4085 | keep | 0 | Jan | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-01-25 04:22 | 2023-01-25 10:30 | 1 | 6:08 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE | R23012500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2023-01-25 | 368 | keep | 0 | Jan | 2023 | 0.00025064 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-25 04:55 | 2023-01-25 10:09 | 20 | 5:14 | P | ANIMAL | 1 X 40 EN C/L CRUCE X RATA | R23012500003 | New_Event | Animals | Include | Include | Wildlife | 314 | 2023-01-25 | 6280 | keep | 0 | Jan | 2023 | 0.0042773 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-01-25 05:10 | 2023-01-25 11:15 | 30 | 6:05 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23012500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2023-01-25 | 10950 | keep | 0 | Jan | 2023 | 0.007458 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-25 06:25 | 2023-01-25 08:38 | 73 | 2:13 | T | CONDUCTOR ROTO O ABIERTO | SWF SJ-230125-01 SE LEVANTO LINEA DEL SUELO Y SE CERRO POR CONTROL | S23012500002 | New_Event | Primary Wire Break | Include | Include | Equipment | 133 | 2023-01-25 | 9709 | keep | 0 | Jan | 2023 | 0.0066128 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
CANOVANAS | 2023-01-25 07:09 | 2023-01-25 10:05 | 4 | 2:56 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23012500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-01-25 | 704 | keep | 0 | Jan | 2023 | 0.00047949 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-01-25 07:13 | 2023-01-25 10:32 | 9 | 3:19 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 25KVA X UNO DE 25 KVA Y SE ENDEREZO POSTE | C23012500008 | New_Event | Service Transformer Failure | Include | Include | Equipment | 199 | 2023-01-25 | 1791 | keep | 0 | Jan | 2023 | 0.0012198 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-01-25 07:17 | 2023-01-25 13:09 | 6 | 5:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE DE XMR | S23012500008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 352 | 2023-01-25 | 2112 | keep | 0 | Jan | 2023 | 0.0014385 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-01-25 07:30 | 2023-01-25 08:03 | 11 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23012400284 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-01-25 | 363 | keep | 0 | Jan | 2023 | 0.00024724 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2023-01-25 07:43 | 2023-01-25 10:45 | 4 | 3:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REEMPLAZO DE PORTA FUSIBLE | C23012500011 | New_Event | Cutout Failure | Include | Include | Equipment | 182 | 2023-01-25 | 728 | keep | 0 | Jan | 2023 | 0.00049584 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-01-25 07:47 | 2023-01-25 11:32 | 50 | 3:45 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO FASE | S23012500013 | New_Event | Animals | Include | Include | Wildlife | 225 | 2023-01-25 | 11250 | keep | 0 | Jan | 2023 | 0.0076623 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-01-25 07:50 | 2023-01-25 10:35 | 60 | 2:45 | P | CAUSAS EXTERNAS | 1 X 100 EN CORTE DE LINEA ACCIDENTE DE AUTO | P23012500017 | New_Event | Damage From Public | Include | Include | Public | 165 | 2023-01-25 | 9900 | keep | 0 | Jan | 2023 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2023-01-25 07:54 | 2023-01-25 10:32 | 4 | 2:38 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | P23012500018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-01-25 | 632 | keep | 0 | Jan | 2023 | 0.00043045 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-01-25 08:20 | 2023-01-25 11:30 | 30 | 3:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23012500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-01-25 | 5700 | keep | 0 | Jan | 2023 | 0.0038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-01-25 08:22 | 2023-01-25 08:23 | 1227 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23012500010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-01-25 | 1227 | keep | 0 | Jan | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
BAYAMON | 2023-01-25 08:31 | 2023-01-25 08:32 | 3597 | 0:01 | T | ANIMAL | RECIERRE DE BKR | C2301250000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-25 | 3597 | keep | 0 | Jan | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-01-25 08:32 | 2023-01-25 10:03 | 175 | 1:31 | P | ANIMAL | 1 X 100 Y 1 X 40 EN CORTES DE LINEA CRUCE POR AVE | B23012500004 | 1st_after_momentary | Animals | Include | Include | Wildlife | 91 | 2023-01-25 | 15925 | keep | 0 | Jan | 2023 | 0.010846 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
VEGA BAJA | 2023-01-25 08:53 | 2023-01-25 12:30 | 49 | 3:37 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR AVE CRUZO FASES | B23012500012 | New_Event | Animals | Include | Include | Wildlife | 217 | 2023-01-25 | 10633 | keep | 0 | Jan | 2023 | 0.0072421 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
SAN JUAN | 2023-01-25 09:00 | 2023-01-25 13:05 | 4 | 4:05 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR PARA DEJAR TOMA DE CLIENTE FUERA TIENE PROA | S23012500022 | New_Event | Customer-Related Interruption | Include | Include | Public | 245 | 2023-01-25 | 980 | keep | 0 | Jan | 2023 | 0.00066747 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-01-25 09:10 | 2023-01-25 12:45 | 2 | 3:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23012500019 | New_Event | Cutout Failure | Include | Include | Equipment | 215 | 2023-01-25 | 430 | keep | 0 | Jan | 2023 | 0.00029287 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-01-25 09:13 | 2023-01-25 14:05 | 200 | 4:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23012500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2023-01-25 | 58400 | keep | 0 | Jan | 2023 | 0.039776 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-01-25 09:25 | 2023-01-25 13:23 | 2 | 3:58 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | M23012500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-01-25 | 476 | keep | 0 | Jan | 2023 | 0.0003242 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-01-25 09:31 | 2023-01-25 14:52 | 2 | 5:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN BANCO TRANSFORMADOR SE REMPLAZO CAJA | B23012500023 | New_Event | Cutout Failure | Include | Include | Equipment | 321 | 2023-01-25 | 642 | keep | 0 | Jan | 2023 | 0.00043726 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-01-25 09:34 | 2023-01-25 11:32 | 50 | 1:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | B23012500024 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2023-01-25 | 5900 | keep | 0 | Jan | 2023 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-25 09:45 | 2023-01-25 09:46 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B23012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-25 | 4533 | keep | 0 | Jan | 2023 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
MAYAGÃœEZ | 2023-01-25 09:56 | 2023-01-25 12:42 | 25 | 2:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 8 EN TRANSFORMADOR SE REPARO SECUNDARIA AVERIADA | M23012500036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 166 | 2023-01-25 | 4150 | keep | 0 | Jan | 2023 | 0.0028265 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-01-25 10:00 | 2023-01-25 11:05 | 6 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS | M23010200078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-01-25 | 390 | keep | 0 | Jan | 2023 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-01-25 10:11 | 2023-01-25 12:01 | 60 | 1:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23012500037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-01-25 | 6600 | keep | 0 | Jan | 2023 | 0.0044952 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-01-25 10:12 | 2023-01-25 11:40 | 1 | 1:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23012500040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 88 | 2023-01-25 | 88 | keep | 0 | Jan | 2023 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-01-25 10:31 | 2023-01-25 17:15 | 12 | 6:44 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZO DE POSTE | A23012500032 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 404 | 2023-01-25 | 4848 | keep | 0 | Jan | 2023 | 0.003302 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-01-25 10:50 | 2023-01-25 14:55 | 50 | 4:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23012500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2023-01-25 | 12250 | keep | 0 | Jan | 2023 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-01-25 10:54 | 2023-01-25 12:40 | 8 | 1:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO POSTAFUSIBLE QUEMADO | R23012500016 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2023-01-25 | 848 | keep | 0 | Jan | 2023 | 0.00057757 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-25 11:11 | 2023-01-25 14:54 | 111 | 3:43 | P | CAUSAS EXTERNAS | 1 X 100 EN RISER CAMION IMPACTO PM T-37 | S23012500053 | New_Event | Damage From Public | Include | Include | Public | 223 | 2023-01-25 | 24753 | keep | 0 | Jan | 2023 | 0.016859 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
FAJARDO | 2023-01-25 11:11 | 2023-01-25 12:53 | 3 | 1:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR CON DERRAME DE ACEITE 50 KVA X 50 KVA | R23012500017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 102 | 2023-01-25 | 306 | keep | 0 | Jan | 2023 | 0.00020842 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-01-25 11:26 | 2023-01-25 12:49 | 10 | 1:23 | P | DESGANCHE | 1 X 50 EN RISER DESGANCHE | R23012500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-01-25 | 830 | keep | 0 | Jan | 2023 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-25 11:42 | 2023-01-25 14:33 | 7 | 2:51 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR PARA DESCONECTAR TOMA EN PEDESTAL AVERIADA DE CLIENTE. | C23012500046 | New_Event | Customer-Related Interruption | Include | Include | Public | 171 | 2023-01-25 | 1197 | keep | 0 | Jan | 2023 | 0.00081527 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-01-25 11:58 | 2023-01-25 13:16 | 50 | 1:18 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L NO DIGITALIZADO PARA LEVANTAR NEUTRAL PRIMARIO | C23012500051 | New_Event | Primary Wire Break | Include | Include | Equipment | 78 | 2023-01-25 | 3900 | keep | 0 | Jan | 2023 | 0.0026563 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-25 12:00 | 2023-01-25 12:30 | 13 | 0:30 | P | SECUNDARIA/DESGANCHE | PODA Y SE ABRIO XMR PARA REPARAR CONECTORES SECUNDARIOS TRASPATIO | B23012500055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 30 | 2023-01-25 | 390 | keep | 0 | Jan | 2023 | 0.00026563 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2023-01-25 12:18 | 2023-01-25 18:19 | 7 | 6:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23012500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2023-01-25 | 2527 | keep | 0 | Jan | 2023 | 0.0017211 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-01-25 12:22 | 2023-01-25 15:10 | 12 | 2:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REEMPLAZARON DOS AISLADORES Y SE HIZO DESGANCHE | P23012500068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-01-25 | 2016 | keep | 0 | Jan | 2023 | 0.0013731 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-25 12:40 | 2023-01-25 14:35 | 35 | 1:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | B23012500062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-01-25 | 4025 | keep | 0 | Jan | 2023 | 0.0027414 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-01-25 12:50 | 2023-01-25 13:50 | 4 | 1:00 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R23012500025 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 60 | 2023-01-25 | 240 | keep | 0 | Jan | 2023 | 0.00016346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-01-25 12:54 | 2023-01-25 12:55 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23012500027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-25 | 4085 | keep | 0 | Jan | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-01-25 12:56 | 2023-01-25 18:06 | 10 | 5:10 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE Y SE REPARO SECUNDARIA | S23012500083 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 310 | 2023-01-25 | 3100 | keep | 0 | Jan | 2023 | 0.0021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-25 13:00 | 2023-01-25 13:29 | 12 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO Y TOMA | R23012500028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-01-25 | 348 | keep | 0 | Jan | 2023 | 0.00023702 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-01-25 13:17 | 2023-01-25 16:10 | 6 | 2:53 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 100 EN CORTE DE LINEA LINEA ARRIADA | P23012500081 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 173 | 2023-01-25 | 1038 | keep | 0 | Jan | 2023 | 0.00070698 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-01-25 13:32 | 2023-01-25 19:10 | 63 | 5:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER , 1 X 50 EN SU#1 | P23012500084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 338 | 2023-01-25 | 21294 | keep | 0 | Jan | 2023 | 0.014503 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
BAYAMON | 2023-01-25 13:35 | 2023-01-25 13:45 | 2 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA Y TOMA | B23012500061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-01-25 | 20 | keep | 0 | Jan | 2023 | 1.3622e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-01-25 13:40 | 2023-01-25 17:37 | 63 | 3:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y SE LEVANTO LINEA | B23012500071 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 237 | 2023-01-25 | 14931 | keep | 0 | Jan | 2023 | 0.010169 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
SAN JUAN | 2023-01-25 13:42 | 2023-01-25 16:30 | 111 | 2:48 | P | DESGANCHE | 1 X 65 EN C/L Y SE REALIZO DESGANCHE | S23012500093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-01-25 | 18648 | keep | 0 | Jan | 2023 | 0.012701 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
BAYAMON | 2023-01-25 13:42 | 2023-01-26 11:40 | 16 | 21:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 75 KVA | B23012500072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1318 | 2023-01-25 | 21088 | keep | 0 | Jan | 2023 | 0.014363 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
YAUCO | 2023-01-25 13:50 | 2023-01-25 15:18 | 20 | 1:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA CON ESCAPE DE ACEITE | M23012500065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 88 | 2023-01-25 | 1760 | keep | 0 | Jan | 2023 | 0.0011987 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-25 13:59 | 2023-01-25 17:30 | 8 | 3:31 | P | SECUNDARIA/DESGANCHE | DESGANCHE SECUNDARIA 1 X 15 EN TRANSFORMADOR | B23012500076 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 211 | 2023-01-25 | 1688 | keep | 0 | Jan | 2023 | 0.0011497 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-25 14:06 | 2023-01-25 14:07 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-25 | 4291 | keep | 0 | Jan | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
HUMACAO | 2023-01-25 14:10 | 2023-01-25 15:28 | 154 | 1:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C23012500064 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2023-01-25 | 12012 | keep | 0 | Jan | 2023 | 0.0081813 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
BAYAMON | 2023-01-25 14:11 | 2023-01-25 15:10 | 320 | 0:59 | T | DESGANCHE | SE RETIRO GANCHO YAGRUMO CRUZANDO FASE SE PROBO INTERRUPTOR QUEDO EN SERVICIO | B23012500078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-01-25 | 18880 | keep | 0 | Jan | 2023 | 0.012859 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-01-25 14:14 | 2023-01-25 16:59 | 2 | 2:45 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23012500080 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-01-25 | 330 | keep | 0 | Jan | 2023 | 0.00022476 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-01-25 14:50 | 2023-01-25 17:00 | 15 | 2:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M23012400309 | New_Event | Secondary Wire Break | Include | Include | Equipment | 130 | 2023-01-25 | 1950 | keep | 0 | Jan | 2023 | 0.0013281 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-25 14:54 | 2023-01-25 19:22 | 17 | 4:28 | P | CAUSAS EXTERNAS | SE REPARO CONEXIONES SOTERRADA Y DOS PISTOLAS Y SE REACOMODO PM CAMION IMPACTO PM | S23012500097 | Partial_restoration | Damage From Public | Include | Include | Public | 268 | 2023-01-25 | 4556 | keep | 0 | Jan | 2023 | 0.0031031 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-01-25 15:01 | 2023-01-25 15:44 | 89 | 0:43 | P | DESGANCHE | SE REEMPLAZO 1 X 65 EN C/L DESGANCHE | R23012500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2023-01-25 | 3827 | keep | 0 | Jan | 2023 | 0.0026066 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
BAYAMON | 2023-01-25 15:10 | 2023-01-25 15:47 | 320 | 0:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA | B23012500090 | New_Event | Primary Wire Break | Include | Include | Equipment | 37 | 2023-01-25 | 11840 | keep | 0 | Jan | 2023 | 0.0080642 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-01-25 15:21 | 2023-01-25 18:06 | 6 | 2:45 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CULEBRA CRUZO FASE | B23012500089 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-01-25 | 990 | keep | 0 | Jan | 2023 | 0.00067428 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-01-25 15:24 | 2023-01-25 16:50 | 150 | 1:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M23012500079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-01-25 | 12900 | keep | 0 | Jan | 2023 | 0.0087861 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-01-25 15:49 | 2023-01-25 17:25 | 300 | 1:36 | P | DESGANCHE | SE RETIRO RAMA 2 X 80 EN CORTE DE LINEA | B23012500094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-01-25 | 28800 | keep | 0 | Jan | 2023 | 0.019616 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2023-01-25 16:26 | 2023-01-25 17:34 | 9 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | P23012500089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2023-01-25 | 612 | keep | 0 | Jan | 2023 | 0.00041683 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-01-25 16:52 | 2023-01-25 17:42 | 414 | 0:50 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | SE TRANSFIRIO EL 30% DE LA CARGA QUE LLEVABA EL BKR 1204-03 AL 1204-01 POR PROBLEMAS EN BREAKER | S23012500134 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 50 | 2023-01-25 | 20700 | keep | 0 | Jan | 2023 | 0.014099 | 0.00028197 | Sustained | FALSE | FALSE | Not_TMED_Event | 414
UTUADO | 2023-01-25 17:06 | 2023-01-25 20:23 | 80 | 3:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23012500108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-01-25 | 15760 | keep | 0 | Jan | 2023 | 0.010734 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-01-25 17:31 | 2023-01-25 21:36 | 15 | 4:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23012500120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2023-01-25 | 3675 | keep | 0 | Jan | 2023 | 0.002503 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-01-25 17:51 | 2023-01-25 17:52 | 329 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23012500097 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-01-25 | 329 | keep | 0 | Jan | 2023 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2023-01-25 17:52 | 2023-01-25 20:30 | 151 | 2:38 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETE QUEMADO Y SE TRANSFIRIO LA CARGA 100% EN SERVICIO CG-230125-02 | C23012500099 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 158 | 2023-01-25 | 23858 | keep | 0 | Jan | 2023 | 0.01625 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
BAYAMON | 2023-01-25 18:12 | 2023-01-25 21:05 | 180 | 2:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B23012500117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2023-01-25 | 31140 | keep | 0 | Jan | 2023 | 0.021209 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CANOVANAS | 2023-01-25 18:35 | 2023-01-25 21:00 | 93 | 2:25 | P | TERMINACION SOTERRADA AVERIADA | 1 X 50 EN C/L Y 1 X 30 EN EL RISER REMPLAZO TERMINACION QUEMADA | R23012500053 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 145 | 2023-01-25 | 13485 | keep | 0 | Jan | 2023 | 0.0091846 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
BAYAMON | 2023-01-25 18:36 | 2023-01-25 22:05 | 80 | 3:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L AVERIA DE T23 A T22 FUERA 3 XMR | B23012500123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2023-01-25 | 16720 | keep | 0 | Jan | 2023 | 0.011388 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-25 18:44 | 2023-01-26 11:09 | 10 | 16:25 | P | DESGANCHE | 1 X 15 EN XMR Y DESGANCHE | S23012500179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 985 | 2023-01-25 | 9850 | keep | 0 | Jan | 2023 | 0.0067088 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-25 18:46 | 2023-01-25 20:38 | 1 | 1:52 | P | MAL TIEMPO/RAYOS | 1 X 20 EN RISER MAL TIEMPO RAYOS | C23012500103 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 112 | 2023-01-25 | 112 | keep | 0 | Jan | 2023 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-25 19:12 | 2023-01-25 19:13 | 2708 | 0:01 | T | NO SE REPORTO CAUSA | RECIERE | R23012500056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-25 | 2708 | keep | 0 | Jan | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
BAYAMON | 2023-01-25 19:17 | 2023-01-25 22:44 | 60 | 3:27 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | B23012500132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-01-25 | 12420 | keep | 0 | Jan | 2023 | 0.0084592 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-25 20:09 | 2023-01-25 21:40 | 12 | 1:31 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE RETEZO SECUNDARIA | S23012500145 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 91 | 2023-01-25 | 1092 | keep | 0 | Jan | 2023 | 0.00074376 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-01-25 20:21 | 2023-01-26 07:41 | 7 | 11:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23012500117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 680 | 2023-01-25 | 4760 | keep | 0 | Jan | 2023 | 0.003242 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-01-25 21:34 | 2023-01-25 22:47 | 238 | 1:13 | P | DESGANCHE | 2 X 80 EN C/L SE REALIZO DESGANCHE | B23012500145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-01-25 | 17374 | keep | 0 | Jan | 2023 | 0.011833 | 0.0001621 | Sustained | FALSE | FALSE | Not_TMED_Event | 238
SAN JUAN | 2023-01-25 21:57 | 2023-01-26 09:54 | 50 | 11:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S23012500196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 717 | 2023-01-25 | 35850 | keep | 0 | Jan | 2023 | 0.024417 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-25 22:05 | 2023-01-26 22:00 | 45 | 23:55 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO DE PROVISIONAL EXISTENTE A T-22. EN SERVICIO EL T-20, T-21 Y T-22 | B23012500123 | New_Event | UG Cable Fault | Include | Include | Equipment | 1435 | 2023-01-25 | 64575 | keep | 0 | Jan | 2023 | 0.043982 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
GUAYAMA | 2023-01-25 22:10 | 2023-01-26 09:18 | 10 | 11:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA QUEMADA EN C/L | P23012500145 | New_Event | Cutout Failure | Include | Include | Equipment | 668 | 2023-01-25 | 6680 | keep | 0 | Jan | 2023 | 0.0045497 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-25 22:27 | 2023-01-26 09:26 | 169 | 10:59 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | R23012500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 659 | 2023-01-25 | 111371 | keep | 0 | Jan | 2023 | 0.075854 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
VEGA BAJA | 2023-01-25 22:28 | 2023-01-25 22:30 | 2216 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23012500151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-25 | 4432 | keep | 0 | Jan | 2023 | 0.0030186 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
PONCE | 2023-01-25 22:30 | 2023-01-26 06:40 | 12 | 8:10 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN XMR SE REPARO BAJANTE PRIMARIO EN XMR | P23012500147 | New_Event | Primary Wire Break | Include | Include | Equipment | 490 | 2023-01-25 | 5880 | keep | 0 | Jan | 2023 | 0.0040048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-01-25 22:50 | 2023-01-25 22:52 | 723 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA | B2301250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-25 | 1446 | keep | 0 | Jan | 2023 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-01-25 22:50 | 2023-01-25 22:52 | 198 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA | B2301250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-25 | 396 | keep | 0 | Jan | 2023 | 0.00026971 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-01-25 22:50 | 2023-01-25 22:52 | 1976 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA | B2301250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-25 | 3952 | keep | 0 | Jan | 2023 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
SAN JUAN | 2023-01-25 23:19 | 2023-01-26 11:07 | 10 | 11:48 | P | NO SE REPORTO CAUSA | 1 X 40 C/L | S23012500201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 708 | 2023-01-25 | 7080 | keep | 0 | Jan | 2023 | 0.0048222 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-25 23:56 | 2023-01-25 23:58 | 327 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 2603-06 SE CERRO POR CONTROL LLEVA EL 2603-07 | C2301250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-25 | 654 | keep | 0 | Jan | 2023 | 0.00044544 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
BAYAMON | 2023-01-26 00:40 | 2023-01-26 02:08 | 5809 | 1:28 | T | CONDUCTOR ARRIADO O CRUZADO | SE DESENREDO LINEAS PRIMARIAS CON VARETA EN EL MONTE Y SE CERRO POR SCADA | B23012600004 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 88 | 2023-01-26 | 511192 | keep | 0 | Jan | 2023 | 0.34817 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
CANOVANAS | 2023-01-26 00:56 | 2023-01-26 03:24 | 2000 | 2:28 | P | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTELLIRRUPTER 2404-06B SE SECCIONALIZO TRAMO Y SE CERRO PB 2404-06B | R23012600004 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 148 | 2023-01-26 | 296000 | keep | 0 | Jan | 2023 | 0.2016 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
CANOVANAS | 2023-01-26 01:15 | 2023-01-26 08:30 | 93 | 7:15 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23012600030 | New_Event | Animals | Include | Include | Wildlife | 435 | 2023-01-26 | 40455 | keep | 0 | Jan | 2023 | 0.027554 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
HUMACAO | 2023-01-26 01:29 | 2023-01-26 08:13 | 40 | 6:44 | P | ANIMAL | 1 X 200 EN C/L CRUCE X AVE | C23012600003 | New_Event | Animals | Include | Include | Wildlife | 404 | 2023-01-26 | 16160 | keep | 0 | Jan | 2023 | 0.011007 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-26 02:08 | 2023-01-26 04:41 | 3742 | 2:33 | P | CONDUCTOR ARRIADO O CRUZADO | SE CERRO INTELLIRUPTER 1710-01A 100% EN SERVICIO | B23012600068 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 153 | 2023-01-26 | 572526 | keep | 0 | Jan | 2023 | 0.38994 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-01-26 02:13 | 2023-01-26 10:03 | 150 | 7:50 | P | PARARRAYOS DEFECTUOSO | 1 X 100 Y 1 X 80 EN C/LS REMPLAZO PARARRAYO CRUZADO | C23012600005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 470 | 2023-01-26 | 70500 | keep | 0 | Jan | 2023 | 0.048017 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-01-26 02:16 | 2023-01-26 02:17 | 327 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 2603-06 SE CERRO POR CONTROL LLEVA 2603-07 | C2301260000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-26 | 327 | keep | 0 | Jan | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
CANOVANAS | 2023-01-26 02:24 | 2023-01-26 02:27 | 1648 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | R23012600091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-26 | 4944 | keep | 0 | Jan | 2023 | 0.0033673 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-01-26 02:27 | 2023-01-26 09:40 | 10 | 7:13 | P | NO SE REPORTO CAUSA | 1 X 5 EN XMR | R23012600145 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 433 | 2023-01-26 | 4330 | keep | 0 | Jan | 2023 | 0.0029491 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-26 02:35 | 2023-01-26 02:36 | 3597 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23012600059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-26 | 3597 | keep | 0 | Jan | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
PONCE | 2023-01-26 03:12 | 2023-01-26 03:13 | 3744 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23012600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-26 | 3744 | keep | 0 | Jan | 2023 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
CANOVANAS | 2023-01-26 03:24 | 2023-01-26 03:42 | 1177 | 0:18 | P | TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO MACHETES QUEMADOS Y SE PROBO TRAMO | R23012600004 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 18 | 2023-01-26 | 21186 | keep | 0 | Jan | 2023 | 0.01443 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-26 03:42 | 2023-01-26 05:42 | 608 | 2:00 | P | TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO MACHETE QUEMADO. SE SECCIONALIZO TERMINACIONES QUEMADAS EN EL SU-F | R23012600004 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 120 | 2023-01-26 | 72960 | keep | 0 | Jan | 2023 | 0.049693 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-01-26 03:56 | 2023-01-26 08:49 | 140 | 4:53 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23012600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 293 | 2023-01-26 | 41020 | keep | 0 | Jan | 2023 | 0.027939 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BARRANQUITAS | 2023-01-26 05:41 | 2023-01-26 05:42 | 2486 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23012600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-26 | 2486 | keep | 0 | Jan | 2023 | 0.0016932 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
CANOVANAS | 2023-01-26 05:42 | 2023-01-26 06:03 | 387 | 0:21 | P | TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO AVERIA SOTERRADA SE CERRO N/O DEL SU-C @ SU-B 1336-06/2404-06 | R23012600004 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 21 | 2023-01-26 | 8127 | keep | 0 | Jan | 2023 | 0.0055353 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-26 06:03 | 2023-01-26 15:42 | 40 | 9:39 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACIONES QUEMADAS EN EL SU-F | R23012600004 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 579 | 2023-01-26 | 23160 | keep | 0 | Jan | 2023 | 0.015774 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-01-26 06:12 | 2023-01-26 08:25 | 6 | 2:13 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23012600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2023-01-26 | 798 | keep | 0 | Jan | 2023 | 0.00054351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-01-26 06:38 | 2023-01-26 09:46 | 1 | 3:08 | P | ANIMAL | 2 X 40 EN C/L Y 2 X 15 EN BANCO DE XMR CRUCE X AVE | C23012600029 | New_Event | Animals | Include | Include | Wildlife | 188 | 2023-01-26 | 188 | keep | 0 | Jan | 2023 | 0.00012805 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-26 07:54 | 2023-01-26 10:49 | 6 | 2:55 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE - EVENTO TRANSFERIDO DE REGION ARECIBO | A23012600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-01-26 | 1050 | keep | 0 | Jan | 2023 | 0.00071515 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-01-26 08:15 | 2023-01-26 18:02 | 40 | 9:47 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | M23012600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 587 | 2023-01-26 | 23480 | keep | 0 | Jan | 2023 | 0.015992 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-01-26 08:30 | 2023-01-26 08:31 | 2697 | 0:01 | T | ANIMAL | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23012600009 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-26 | 2697 | keep | 0 | Jan | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-01-26 08:31 | 2023-01-26 11:30 | 60 | 2:59 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A23012600010 | 1st_after_momentary | Animals | Include | Include | Wildlife | 179 | 2023-01-26 | 10740 | keep | 0 | Jan | 2023 | 0.007315 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-01-26 08:47 | 2023-01-26 08:48 | 1894 | 0:01 | T | NO SE REPORTO CAUSA | RECERRE | R2301260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-26 | 1894 | keep | 0 | Jan | 2023 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
ARECIBO | 2023-01-26 08:49 | 2023-01-26 11:55 | 5 | 3:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23012600030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2023-01-26 | 930 | keep | 0 | Jan | 2023 | 0.00063342 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-01-26 08:53 | 2023-01-26 11:05 | 1 | 2:12 | P | ANIMAL | 2 X 25 EN RISER CRUCE DE FASE PRIMARIA POR AVE | M23012600046 | New_Event | Animals | Include | Include | Wildlife | 132 | 2023-01-26 | 132 | keep | 0 | Jan | 2023 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-01-26 09:10 | 2023-01-26 19:32 | 35 | 10:22 | P | CABLE SOTERRADO AVERIADO | SE REPARO ALAMBRE SOTERRADO Y SE REMPLAZO 2 XMR | P23012600034 | New_Event | UG Cable Fault | Include | Include | Equipment | 622 | 2023-01-26 | 21770 | keep | 0 | Jan | 2023 | 0.014827 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-01-26 09:12 | 2023-01-26 11:04 | 3012 | 1:52 | T | CAUSAS EXTERNAS | RECERRO 3 VECES QUEDO FUERA SE SECCIONALIZO AVERIA DE CONTRATISTA EN PULLBOX. SE CERRO N/O CON 2005-10 70% EN SERVICIO. VER SJ-230126-51 | R23012600150 | New_Event | Damage From Public | Include | Include | Public | 112 | 2023-01-26 | 337344 | keep | 0 | Jan | 2023 | 0.22976 | 0.0020515 | Sustained | FALSE | FALSE | Not_TMED_Event | 3012
FAJARDO | 2023-01-26 09:14 | 2023-01-26 12:04 | 52 | 2:50 | P | DESGANCHE | 1 X 25 EN C/L 1 X 20 EN C/L DESGANCHE | R23012600151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-01-26 | 8840 | keep | 0 | Jan | 2023 | 0.0060209 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2023-01-26 09:15 | 2023-01-26 12:14 | 1 | 2:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | B23012600124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-01-26 | 179 | keep | 0 | Jan | 2023 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-01-26 09:23 | 2023-01-26 10:37 | 17 | 1:14 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ELIMINO POSTE SECUNDARIO Y SE RELOCALIZO SECUNDARIA A POSTE DE CEMENTO | P23012600037 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 74 | 2023-01-26 | 1258 | keep | 0 | Jan | 2023 | 0.00085682 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-01-26 09:30 | 2023-01-26 15:30 | 5 | 6:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO | B23012600116 | New_Event | Primary Pole Failure | Include | Include | Equipment | 360 | 2023-01-26 | 1800 | keep | 0 | Jan | 2023 | 0.001226 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-01-26 09:44 | 2023-01-26 13:00 | 10 | 3:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN XMR SE REPARO SECUNDARIA | P23012600045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 196 | 2023-01-26 | 1960 | keep | 0 | Jan | 2023 | 0.0013349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-26 10:00 | 2023-01-26 11:50 | 8 | 1:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE RELOCALIZO LINEA Y TRANSFORMADOR | B23012600112 | New_Event | Primary Pole Failure | Include | Include | Equipment | 110 | 2023-01-26 | 880 | keep | 0 | Jan | 2023 | 0.00059936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-26 10:01 | 2023-01-26 10:02 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2301260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-26 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-01-26 10:10 | 2023-01-26 10:35 | 15 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23012600006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-26 | 375 | keep | 0 | Jan | 2023 | 0.00025541 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-01-26 10:27 | 2023-01-26 19:38 | 15 | 9:11 | P | MAL TIEMPO/RAYOS | 1 X 40 Y 1 X 50 EN DIFERENTES CORTES DE LINEA LLUVIA Y FUERTES VIENTOS EVENTO A23012600027 CERRADO DEL SECTOR | A23012600100 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 551 | 2023-01-26 | 8265 | keep | 0 | Jan | 2023 | 0.0056293 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-01-26 10:36 | 2023-01-26 13:40 | 50 | 3:04 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23012600054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2023-01-26 | 9200 | keep | 0 | Jan | 2023 | 0.0062661 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-26 10:50 | 2023-01-26 12:00 | 1 | 1:10 | P | NO SE REPORTO CAUSA | 1 X 40 CL | S23012600047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2023-01-26 | 70 | keep | 0 | Jan | 2023 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-26 10:51 | 2023-01-26 10:52 | 4291 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | S2301260000X | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-01-26 | 4291 | keep | 0 | Jan | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
BAYAMON | 2023-01-26 10:51 | 2023-01-26 14:33 | 12 | 3:42 | P | ANIMAL | 1 X 25 EN RISER AVE CRUZO FASE | B23012600148 | New_Event | Animals | Include | Include | Wildlife | 222 | 2023-01-26 | 2664 | keep | 0 | Jan | 2023 | 0.0018144 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-26 10:52 | 2023-01-26 15:50 | 1 | 4:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRAS EN PEDESTAL | S23012600048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 298 | 2023-01-26 | 298 | keep | 0 | Jan | 2023 | 0.00020297 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-26 10:55 | 2023-01-26 13:03 | 1 | 2:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA AVERIADA | C23012600083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 128 | 2023-01-26 | 128 | keep | 0 | Jan | 2023 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-26 11:00 | 2023-01-26 14:14 | 2 | 3:14 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23012600191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-01-26 | 388 | keep | 0 | Jan | 2023 | 0.00026427 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-01-26 11:04 | 2023-01-26 12:58 | 15 | 1:54 | P | CAUSAS EXTERNAS | RECERRO 3 VECES QUEDO FUERA SE SECCIONALIZO AVERIA DE CONTRATISTA EN PULLBOX. SE CERRO N/O CON 2305-04 100% EN SERVICIO. VER SJ-230126-51 | R23012600150 | New_Event | Damage From Public | Include | Include | Public | 114 | 2023-01-26 | 1710 | keep | 0 | Jan | 2023 | 0.0011647 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-01-26 11:34 | 2023-01-26 19:00 | 2 | 7:26 | P | CRUCETA DEFECTUOSA O AVERIADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CRUCETA PODRIDA | A23012600040 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 446 | 2023-01-26 | 892 | keep | 0 | Jan | 2023 | 0.00060754 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2023-01-26 11:34 | 2023-01-26 11:36 | 1241 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECERRO SE CERRO POR CONTROL SCADA | A23012600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-26 | 2482 | keep | 0 | Jan | 2023 | 0.0016905 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
CANOVANAS | 2023-01-26 11:38 | 2023-01-26 12:18 | 2106 | 0:40 | T | ERROR HUMANO | SE ABRIO EN SU 2 ERRONEAMENTE POR MALA ROTULACION SE VOLVIO A CERRAR EN SU 100% EN SERVICIO. EN OPERACIONES DE SECCIONALIZAR AVERIA EN BKR 2305-02 | R23012600215 | New_Event | Human Error | Include | Include | Other | 40 | 2023-01-26 | 84240 | keep | 0 | Jan | 2023 | 0.057375 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
SAN JUAN | 2023-01-26 11:40 | 2023-01-26 12:00 | 10 | 0:20 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S2301260037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2023-01-26 | 200 | keep | 0 | Jan | 2023 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-26 11:43 | 2023-01-26 15:44 | 3 | 4:01 | P | ANIMAL | 2 X 15 EN XMR CRUCE POR AVE | C23012600095 | New_Event | Animals | Include | Include | Wildlife | 241 | 2023-01-26 | 723 | keep | 0 | Jan | 2023 | 0.00049243 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-01-26 11:46 | 2023-01-26 20:00 | 15 | 8:14 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M23012600082 | New_Event | Primary Wire Break | Include | Include | Equipment | 494 | 2023-01-26 | 7410 | keep | 0 | Jan | 2023 | 0.0050469 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-26 11:48 | 2023-01-26 12:44 | 43 | 0:56 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S23012600071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-01-26 | 2408 | keep | 0 | Jan | 2023 | 0.0016401 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BAYAMON | 2023-01-26 11:54 | 2023-01-26 12:19 | 1 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | TRABAJAR ABRIENDO TRANSFORMADOR PARA PODER RETIRAR BAJANTES Y SECUNDARIA | B23012600151 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-26 | 25 | keep | 0 | Jan | 2023 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-26 12:15 | 2023-01-26 12:17 | 4291 | 0:02 | T | CAUSAS EXTERNAS | DISPARO CERRADO POR CONTROL | S2301250000X | 1st_after_momentary | Damage From Public | Include | Include | Public | 2 | 2023-01-26 | 8582 | keep | 0 | Jan | 2023 | 0.0058452 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
VEGA BAJA | 2023-01-26 12:15 | 2023-01-26 18:19 | 75 | 6:04 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A23012600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 364 | 2023-01-26 | 27300 | keep | 0 | Jan | 2023 | 0.018594 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-01-26 12:22 | 2023-01-26 13:32 | 1 | 1:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA FUERTE | B23012600155 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 70 | 2023-01-26 | 70 | keep | 0 | Jan | 2023 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-26 12:27 | 2023-01-26 15:36 | 20 | 3:09 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHO | C23012600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2023-01-26 | 3780 | keep | 0 | Jan | 2023 | 0.0025745 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-01-26 13:00 | 2023-01-26 13:45 | 14 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS SOTERRADAS | M23012600063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-01-26 | 630 | keep | 0 | Jan | 2023 | 0.00042909 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-01-26 13:10 | 2023-01-26 16:50 | 1 | 3:40 | P | ANIMAL | 1 X 25 EN RISER Y 1 X 50 EN CORTE DE LINEA AVE CRUZO FASES | B23012600166 | New_Event | Animals | Include | Include | Wildlife | 220 | 2023-01-26 | 220 | keep | 0 | Jan | 2023 | 0.00014984 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-26 13:15 | 2023-01-26 14:04 | 5 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BARRA SECUNDARIA | A23012500069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-01-26 | 245 | keep | 0 | Jan | 2023 | 0.00016687 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-26 13:30 | 2023-01-26 13:31 | 4291 | 0:01 | T | CAUSAS EXTERNAS | DISPARO CERRADO POR CONTROL | S2301250000X | 1st_after_momentary | Damage From Public | Include | Include | Public | 1 | 2023-01-26 | 4291 | keep | 0 | Jan | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
CAGUAS | 2023-01-26 13:38 | 2023-01-26 14:42 | 60 | 1:04 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C23012600122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-01-26 | 3840 | keep | 0 | Jan | 2023 | 0.0026154 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-01-26 13:43 | 2023-01-26 15:06 | 17 | 1:23 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRASFORMADOR PARA REALIZAR PODA | B23012600159 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 83 | 2023-01-26 | 1411 | keep | 0 | Jan | 2023 | 0.00096103 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-01-26 13:46 | 2023-01-26 15:03 | 10 | 1:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23012600095 | New_Event | Secondary Wire Break | Include | Include | Equipment | 77 | 2023-01-26 | 770 | keep | 0 | Jan | 2023 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-26 13:58 | 2023-01-26 16:15 | 100 | 2:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B23012600178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-01-26 | 13700 | keep | 0 | Jan | 2023 | 0.009331 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-01-26 13:59 | 2023-01-26 16:22 | 48 | 2:23 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23012600129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-01-26 | 6864 | keep | 0 | Jan | 2023 | 0.004675 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2023-01-26 14:00 | 2023-01-26 15:33 | 10 | 1:33 | P | DESGANCHE | DESGANCHE PRIMARIO 1 X 15 EN TRANSFORMADOR | B23012600180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-01-26 | 930 | keep | 0 | Jan | 2023 | 0.00063342 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-01-26 14:02 | 2023-01-26 14:03 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23012600070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-26 | 3431 | keep | 0 | Jan | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2023-01-26 14:10 | 2023-01-26 15:08 | 32 | 0:58 | P | CAUSAS EXTERNAS | SE ABRIO MACHETE PARA ELEMINAR TENSOR CRUZANDO LINEAS Y SE NORMALIZARON CARGAS 1717-02 Y 1713-05, EL CUAL NO TUVO INTERRUPCION ( LO QUE SE ABRIO FUE UN N/O ) | B23012600176 | New_Event | Damage From Public | Include | Include | Public | 58 | 2023-01-26 | 1856 | keep | 0 | Jan | 2023 | 0.0012641 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
VEGA BAJA | 2023-01-26 14:15 | 2023-01-26 14:46 | 40 | 0:31 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO DEFECTUOSO | A23012600096 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 31 | 2023-01-26 | 1240 | keep | 0 | Jan | 2023 | 0.00084456 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-01-26 14:19 | 2023-01-26 15:03 | 15 | 0:44 | P | CAUSAS EXTERNAS | 1 X 10 EN XMR ACCIDENTE EXCAVADORA | C23012600137 | New_Event | Damage From Public | Include | Include | Public | 44 | 2023-01-26 | 660 | keep | 0 | Jan | 2023 | 0.00044952 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-26 14:29 | 2023-01-26 21:24 | 50 | 6:55 | P | ANIMAL | IGUANA CRUZO FASE 2 X 50 EN CORTE DE LINEA | B23012600187 | New_Event | Animals | Include | Include | Wildlife | 415 | 2023-01-26 | 20750 | keep | 0 | Jan | 2023 | 0.014133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-01-26 14:36 | 2023-01-26 17:18 | 10 | 2:42 | P | DESGANCHE | 2 X 65 EN C/L Y DESGANCHE | R23012600251 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-01-26 | 1620 | keep | 0 | Jan | 2023 | 0.0011034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-01-26 14:40 | 2023-01-26 17:23 | 12 | 2:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REGULO VOLTAJE DEL TAP 3 AL 2 ESTABA 252V Y QUEDO 246V | C23012600134 | New_Event | Secondary Wire Break | Include | Include | Equipment | 163 | 2023-01-26 | 1956 | keep | 0 | Jan | 2023 | 0.0013322 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-26 14:42 | 2023-01-26 14:43 | 4291 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | S2301260000X | 1st_after_momentary | Damage From Public | Include | Include | Public | 1 | 2023-01-26 | 4291 | keep | 0 | Jan | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
AGUADILLA | 2023-01-26 14:45 | 2023-01-26 16:15 | 20 | 1:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA CON PROBLEMA DE ALTO VOLTAJE CLIENTE CON SERVICIO EVENTO DEL DIA 24 | A23012400084 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2023-01-26 | 1800 | keep | 0 | Jan | 2023 | 0.001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-26 14:46 | 2023-01-26 14:47 | 2791 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A23012600080 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-26 | 2791 | keep | 0 | Jan | 2023 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2023-01-26 14:46 | 2023-01-26 14:47 | 1464 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A23012600080 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-26 | 1464 | keep | 0 | Jan | 2023 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
VEGA BAJA | 2023-01-26 14:46 | 2023-01-26 14:47 | 759 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A23012600080 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-26 | 759 | keep | 0 | Jan | 2023 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2023-01-26 14:46 | 2023-01-26 14:47 | 1500 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A23012600080 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-26 | 1500 | keep | 0 | Jan | 2023 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
VEGA BAJA | 2023-01-26 14:47 | 2023-01-26 20:33 | 1 | 5:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | A23012600110 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 346 | 2023-01-26 | 346 | keep | 0 | Jan | 2023 | 0.00023566 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-26 14:47 | 2023-01-26 18:12 | 40 | 3:25 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO DEFECTUOSO | A23012600096 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 205 | 2023-01-26 | 8200 | keep | 0 | Jan | 2023 | 0.005585 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-01-26 14:55 | 2023-01-26 17:00 | 462 | 2:05 | T | EXCAVACIONES | CABLE SOTERRADO DE BREAKER A MH 17 AVERIADO SE TRANSFIRIO CARGA AL 5003-01 COMPANIA PRIVADA HACIENDO DIRECT DRILLING AVERIO CABLE SOTERRADO | P23012600082 | New_Event | Excavation | Include | Include | Public | 125 | 2023-01-26 | 57750 | keep | 0 | Jan | 2023 | 0.039333 | 0.00031467 | Sustained | FALSE | FALSE | Not_TMED_Event | 462
SAN JUAN | 2023-01-26 15:02 | 2023-01-26 17:08 | 4291 | 2:06 | T | CAUSAS EXTERNAS | SE ENCONTRO PERSONAL PRIVADO DESGANCHANDO QUE DEJARON CAER RAMAS EN LAS LINEAS PERSONAL TERMINARON SUS TRABAJOS Y SE CERRO BKR POR SCADA | S23012600112 | 1st_after_momentary | Damage From Public | Include | Include | Public | 126 | 2023-01-26 | 540666 | keep | 0 | Jan | 2023 | 0.36825 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
MAYAGÃœEZ | 2023-01-26 15:03 | 2023-01-26 17:00 | 15 | 1:57 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE | M23012600124 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-01-26 | 1755 | keep | 0 | Jan | 2023 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-01-26 15:24 | 2023-01-26 17:26 | 300 | 2:02 | P | ANIMAL | 3 X 100 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M23012600131 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-01-26 | 36600 | keep | 0 | Jan | 2023 | 0.024928 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-01-26 15:29 | 2023-01-26 16:27 | 2605 | 0:58 | T | DESGANCHE | SE RETIRO BAMBUAS CON VARETA DE PISO Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO | B23012600230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-01-26 | 151090 | keep | 0 | Jan | 2023 | 0.10291 | 0.0017743 | Sustained | FALSE | FALSE | Not_TMED_Event | 2605
MAYAGÃœEZ | 2023-01-26 15:31 | 2023-01-26 17:54 | 5 | 2:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M23012600132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2023-01-26 | 715 | keep | 0 | Jan | 2023 | 0.00048698 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-01-26 15:49 | 2023-01-26 16:45 | 1 | 0:56 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | C23012600160 | New_Event | Animals | Include | Include | Wildlife | 56 | 2023-01-26 | 56 | keep | 0 | Jan | 2023 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-26 16:06 | 2023-01-26 17:10 | 20 | 1:04 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A23012600093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-01-26 | 1280 | keep | 0 | Jan | 2023 | 0.0008718 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-01-26 16:20 | 2023-01-26 18:01 | 3 | 1:41 | P | CAUSAS EXTERNAS | ABRIO XMR PARA DESCONECTAR RISER SECUNDARIO QUEMADO POR CRUCE CON EXCAVADORA | C23012600165 | New_Event | Damage From Public | Include | Include | Public | 101 | 2023-01-26 | 303 | keep | 0 | Jan | 2023 | 0.00020637 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-01-26 16:57 | 2023-01-26 18:40 | 60 | 1:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23012600141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-01-26 | 6180 | keep | 0 | Jan | 2023 | 0.0042092 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-01-26 17:07 | 2023-01-26 19:25 | 15 | 2:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23012600144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-01-26 | 2070 | keep | 0 | Jan | 2023 | 0.0014099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-01-26 17:10 | 2023-01-26 18:19 | 15 | 1:09 | P | ANIMAL | 1 X 65 EN C/L IGUANA CRUZO LINEAS | P23012600127 | New_Event | Animals | Include | Include | Wildlife | 69 | 2023-01-26 | 1035 | keep | 0 | Jan | 2023 | 0.00070493 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-01-26 17:12 | 2023-01-26 17:45 | 18 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR REPARAR BAJANTE SECUNDARIO | M23012600051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-01-26 | 594 | keep | 0 | Jan | 2023 | 0.00040457 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2023-01-26 17:23 | 2023-01-26 20:45 | 50 | 3:22 | P | DESGANCHE | 1 X 40 EN COFRTE DE LINEA DESGANCHE | B23012600262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-01-26 | 10100 | keep | 0 | Jan | 2023 | 0.0068791 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-01-26 17:35 | 2023-01-26 18:00 | 2 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23012600279 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-26 | 50 | keep | 0 | Jan | 2023 | 3.4055e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-01-26 17:36 | 2023-01-26 21:46 | 3 | 4:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | B23012600025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2023-01-26 | 750 | keep | 0 | Jan | 2023 | 0.00051082 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-01-26 17:38 | 2023-01-26 18:05 | 5 | 0:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTORES SECUNDARIA | B23012600172 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2023-01-26 | 135 | keep | 0 | Jan | 2023 | 9.1948e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-01-26 17:50 | 2023-01-26 18:23 | 10 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A23012500120 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-01-26 | 330 | keep | 0 | Jan | 2023 | 0.00022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-01-26 18:13 | 2023-01-26 19:00 | 16 | 0:47 | P | ANIMAL | 1 X 80 EN C/L AVE CRUZO LINEAS | P23012600143 | New_Event | Animals | Include | Include | Wildlife | 47 | 2023-01-26 | 752 | keep | 0 | Jan | 2023 | 0.00051218 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-01-26 19:26 | 2023-01-26 21:45 | 199 | 2:19 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | SE ABRIO BREAKER POR PROBLEMAS MECANICOS PARA TRATAR DE DEJAR EL BKR TOTALMENTE OPERACIONAL Y CARGA NO AMARRA. AUN LOS PROBLEMAS PERSISTEN NO ABRE POR SCADA Y SOLO LLEVA 20% DE SU CARGA. SE TERMINO ENERGIZANDO SJ-230126-02 | S23012600104 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 139 | 2023-01-26 | 27661 | keep | 0 | Jan | 2023 | 0.01884 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2023-01-26 20:08 | 2023-01-26 20:30 | 63 | 0:22 | P | ANIMAL | 1 X 50 EN C/L PALOMA | S23012600238 | New_Event | Animals | Include | Include | Wildlife | 22 | 2023-01-26 | 1386 | keep | 0 | Jan | 2023 | 0.000944 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
MAYAGÃœEZ | 2023-01-26 20:35 | 2023-01-27 10:05 | 45 | 13:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | M23012600160 | New_Event | Cutout Failure | Include | Include | Equipment | 810 | 2023-01-26 | 36450 | keep | 0 | Jan | 2023 | 0.024826 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-01-26 20:35 | 2023-01-26 22:25 | 8 | 1:50 | P | ANIMAL | 1 X 15 EN XMR AVE CRUZO LINEAS | B23012600273 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-01-26 | 880 | keep | 0 | Jan | 2023 | 0.00059936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-01-26 20:38 | 2023-01-26 20:39 | 370 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | RECIERRE 70% DE SU CARGA ESTA POR 2305-02 | R2301260000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-26 | 370 | keep | 0 | Jan | 2023 | 0.00025201 | 0.00025201 | Momentary | FALSE | FALSE | Not_TMED_Event | 370
CANOVANAS | 2023-01-26 20:38 | 2023-01-26 20:39 | 2108 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE 2005-10 70% DE SU CARGA X 2005-10 | R2301260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-26 | 2108 | keep | 0 | Jan | 2023 | 0.0014357 | 0.0014357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2108
FAJARDO | 2023-01-26 20:39 | 2023-01-26 22:55 | 456 | 2:16 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN MACHETE | R23012600291 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 136 | 2023-01-26 | 62016 | keep | 0 | Jan | 2023 | 0.042239 | 0.00031058 | Sustained | FALSE | FALSE | Not_TMED_Event | 456
SAN JUAN | 2023-01-26 21:02 | 2023-01-26 22:14 | 418 | 1:12 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO INTERRUPTOR Y SE CERRO POR SCADA 25% EN SERVICIO | S23012600293 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 72 | 2023-01-26 | 30096 | keep | 0 | Jan | 2023 | 0.020498 | 0.0002847 | Sustained | FALSE | FALSE | Not_TMED_Event | 418
BARRANQUITAS | 2023-01-26 21:07 | 2023-01-27 07:37 | 3 | 10:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23012600189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 630 | 2023-01-26 | 1890 | keep | 0 | Jan | 2023 | 0.0012873 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-01-26 22:14 | 2023-01-26 22:16 | 314 | 0:02 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZO OPERACIONES PARA SECCIONALIZAR AVERIA 35% EN SERVICIO | S23012600293 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2023-01-26 | 628 | keep | 0 | Jan | 2023 | 0.00042773 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-26 22:16 | 2023-01-26 22:17 | 272 | 0:01 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR AL REALIZAR OPERACIONES PARA SECCIONALIZAR AVERIA | S23012600293 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-01-26 | 272 | keep | 0 | Jan | 2023 | 0.00018526 | 0.00018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 272
SAN JUAN | 2023-01-26 22:17 | 2023-01-26 22:18 | 418 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO INTERRUPTOR EN SU 13 HACHIA MH 11 Y SE CERRO INTERRUPTOR 35% EN SERVICIO | S23012600293 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-01-26 | 418 | keep | 0 | Jan | 2023 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
SAN JUAN | 2023-01-26 22:18 | 2023-01-26 22:30 | 272 | 0:12 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO INTERRUPTOR EN SU 13 HACHIA MH 11 Y SE CERRO INTERRUPTOR 45% EN SERVICIO | S23012600293 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 12 | 2023-01-26 | 3264 | keep | 0 | Jan | 2023 | 0.0022231 | 0.00018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 272
SAN JUAN | 2023-01-26 22:30 | 2023-01-26 22:54 | 230 | 0:24 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZARON OPERACIONES PARA LOCALIZAR AVERIA Y SE ENERGIZO 55% | S23012600293 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 24 | 2023-01-26 | 5520 | keep | 0 | Jan | 2023 | 0.0037596 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-26 22:54 | 2023-01-26 23:04 | 188 | 0:10 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA | S23012600293 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 10 | 2023-01-26 | 1880 | keep | 0 | Jan | 2023 | 0.0012805 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-26 23:04 | 2023-01-26 23:06 | 418 | 0:02 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO TRAMO DE MH 16 @ MH 20 POR TERMINACION SOTERRADA AVERIADA Y SE CERRO INTERRUPTOR 55% EN SERVICIO | S23012600293 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2023-01-26 | 836 | keep | 0 | Jan | 2023 | 0.0005694 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-26 23:06 | 2023-01-26 23:09 | 188 | 0:03 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO INTERRUPTOR EN MH 16 HACIA CAJAS SECAS Y SE ENERGIZO 65% | S23012600293 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 3 | 2023-01-26 | 564 | keep | 0 | Jan | 2023 | 0.00038414 | 0.00012805 | Momentary | FALSE | FALSE | Not_TMED_Event | 188
SAN JUAN | 2023-01-26 23:09 | 2023-01-27 00:36 | 146 | 1:27 | P | ALIMENTADOR AMARRADO | SE CERRO N/O CONTRA 1014-16 PARA ENERGIZAR PARTE DEL 1013-13 SECCIONALIZADO 80% EN SERVICIO | S23012600293 | New_Event | Feeder Load Transferred | Include | Include | Other | 87 | 2023-01-26 | 12702 | keep | 0 | Jan | 2023 | 0.0086513 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
SAN JUAN | 2023-01-27 00:06 | 2023-01-27 00:08 | 295 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR AL TRATAR DE TRANSFERIR PARTE DE LA CARGA DEL 1013-13 | S2301270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-27 | 590 | keep | 0 | Jan | 2023 | 0.00040185 | 0.00020092 | Momentary | FALSE | FALSE | Not_TMED_Event | 295
HUMACAO | 2023-01-27 00:25 | 2023-01-27 12:34 | 40 | 12:09 | P | DESGANCHE | 1X 40 EN C/L DESGANCHE | C23012700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 729 | 2023-01-27 | 29160 | keep | 0 | Jan | 2023 | 0.019861 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-27 00:36 | 2023-01-27 00:47 | 83 | 0:11 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO EN MH 22 HACIA CAJAS SECAS 85% EN SERVICIO | S23012600293 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 11 | 2023-01-27 | 913 | keep | 0 | Jan | 2023 | 0.00062184 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
SAN JUAN | 2023-01-27 00:47 | 2023-01-27 01:52 | 62 | 1:05 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO EN MH 22 HACIA SALIDA AEREA 95% EN SERVICIO | S23012600293 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 65 | 2023-01-27 | 4030 | keep | 0 | Jan | 2023 | 0.0027448 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-01-27 00:57 | 2023-01-27 04:50 | 4009 | 3:53 | T | ANIMAL | ALIMENTADOR FUERA DE SERVICIO POR AVE CRUZO SALIDA DEL BREAKER SECUNDARIO DE PORTATIL #14 | P23012700011 | New_Event | Animals | Include | Include | Wildlife | 233 | 2023-01-27 | 934097 | keep | 0 | Jan | 2023 | 0.63621 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
SAN JUAN | 2023-01-27 01:52 | 2023-01-27 03:37 | 272 | 1:45 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR LLEVANDO 65% DE SU CARGA SE SECCIONALIZO Y SE CERRO POR CONTROL 25% DE LA CARGA EN SERVICIO | S23012700005 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 105 | 2023-01-27 | 28560 | keep | 0 | Jan | 2023 | 0.019452 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-27 03:37 | 2023-01-27 03:49 | 204 | 0:12 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZO OPERACIONES PARA SECCIONALIZAR AVERIA 50% DE LA CARGA EN SERVICIO | S23012700005 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 12 | 2023-01-27 | 2448 | keep | 0 | Jan | 2023 | 0.0016673 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-27 03:49 | 2023-01-27 05:15 | 135 | 1:26 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZO OPERACIONES PARA SECCIONALIZAR AVERIA 55% DE LA CARGA EN SERVICIO | S23012700005 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 86 | 2023-01-27 | 11610 | keep | 0 | Jan | 2023 | 0.0079075 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-27 04:14 | 2023-01-27 07:24 | 451 | 3:10 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR | S23012700010 | New_Event | Primary Wire Break | Include | Include | Equipment | 190 | 2023-01-27 | 85690 | keep | 0 | Jan | 2023 | 0.058363 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2023-01-27 04:19 | 2023-01-27 05:58 | 15 | 1:39 | P | DESGANCHE | 1X65 EN C/L SE REALIZO DESGANCHE | S23012700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-01-27 | 1485 | keep | 0 | Jan | 2023 | 0.0010114 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-27 04:26 | 2023-01-27 10:47 | 50 | 6:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | S23012700012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 381 | 2023-01-27 | 19050 | keep | 0 | Jan | 2023 | 0.012975 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-27 04:26 | 2023-01-27 10:55 | 100 | 6:29 | P | TERMINACION SOTERRADA AVERIADA | 1X50 EN AEREO PROVISIONAL SE REPARO TERMINACION AVERIADA EN RISER | B23012700005 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 389 | 2023-01-27 | 38900 | keep | 0 | Jan | 2023 | 0.026495 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-27 04:49 | 2023-01-27 09:11 | 172 | 4:22 | P | TERMINACION SOTERRADA AVERIADA | 1X30 EN PROVISIONAL AEREO SE REMPLAZO TERMINACION QUEMADA EN RISER | B23012700007 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 262 | 2023-01-27 | 45064 | keep | 0 | Jan | 2023 | 0.030693 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
CANOVANAS | 2023-01-27 04:53 | 2023-01-27 09:49 | 80 | 4:56 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | R23012700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2023-01-27 | 23680 | keep | 0 | Jan | 2023 | 0.016128 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-01-27 04:56 | 2023-01-27 09:09 | 30 | 4:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A23012700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2023-01-27 | 7590 | keep | 0 | Jan | 2023 | 0.0051695 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-01-27 05:09 | 2023-01-27 08:42 | 30 | 3:33 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23012700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-01-27 | 6390 | keep | 0 | Jan | 2023 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-27 05:11 | 2023-01-27 05:14 | 4398 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23012700013 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-01-27 | 13194 | keep | 0 | Jan | 2023 | 0.0089864 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2023-01-27 05:14 | 2023-01-27 12:25 | 10 | 7:11 | P | CONDUCTOR ROTO O ABIERTO | DESGANCHE Y SE REPARO BAJANTE DE LINEA A TRANSFORMADOR | S23012700018 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 431 | 2023-01-27 | 4310 | keep | 0 | Jan | 2023 | 0.0029355 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-27 05:15 | 2023-01-27 05:28 | 122 | 0:13 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZO OPERACIONES PARA SECCIONALIZAR AVERIA 65% DE LA CARGA EN SERVICIO | S23012700005 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 13 | 2023-01-27 | 1586 | keep | 0 | Jan | 2023 | 0.0010802 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-27 05:28 | 2023-01-27 05:29 | 95 | 0:01 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR AL REALIZAR OPERACIONES DE MH 14A A MH 16 | S23012700005 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-01-27 | 95 | keep | 0 | Jan | 2023 | 6.4704e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-27 05:29 | 2023-01-27 05:30 | 272 | 0:01 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR CON 65% DE SU CARGA SE SECCIONALIZO Y SE CERRO POR SCADA ENTRO 65% DE LA CARGA | S23012700005 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-01-27 | 272 | keep | 0 | Jan | 2023 | 0.00018526 | 0.00018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 272
SAN JUAN | 2023-01-27 05:30 | 2023-01-27 15:10 | 2 | 9:40 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ELIMINO VS DE MH 16 | S23012600293 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 580 | 2023-01-27 | 1160 | keep | 0 | Jan | 2023 | 0.00079007 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-01-27 05:53 | 2023-01-27 05:55 | 172 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23012700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-27 | 344 | keep | 0 | Jan | 2023 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CANOVANAS | 2023-01-27 06:07 | 2023-01-27 10:30 | 1 | 4:23 | P | ANIMAL | 2 X 25 EN CORTE DE LINEA 2 X 40 EN CORTE DE LINEA CRUCE POR GATO | R23012700012 | New_Event | Animals | Include | Include | Wildlife | 263 | 2023-01-27 | 263 | keep | 0 | Jan | 2023 | 0.00017913 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-27 06:12 | 2023-01-27 09:31 | 10 | 3:19 | P | NO SE REPORTO CAUSA | 1X8 EN T-20 | B23012700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2023-01-27 | 1990 | keep | 0 | Jan | 2023 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-27 06:16 | 2023-01-27 09:49 | 140 | 3:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y SE REEMPLAZO PORTAFUSIBLE | S23012700019 | New_Event | Cutout Failure | Include | Include | Equipment | 213 | 2023-01-27 | 29820 | keep | 0 | Jan | 2023 | 0.02031 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
ARECIBO | 2023-01-27 06:23 | 2023-01-27 09:12 | 30 | 2:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA | A23012700012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 169 | 2023-01-27 | 5070 | keep | 0 | Jan | 2023 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-27 06:27 | 2023-01-27 12:38 | 20 | 6:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L POR LLUVIAS | S23012700020 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 371 | 2023-01-27 | 7420 | keep | 0 | Jan | 2023 | 0.0050537 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-01-27 07:06 | 2023-01-27 08:35 | 2126 | 1:29 | T | ANIMAL | DISPARO DE BKR SE SECCIONALIZO CAJA PRIMARIA QUEMADA A CAUSA DE RANA EN TRONCAL Y SE CERRO POR CONTROL 50% EN SERVICIO | C23012700009 | New_Event | Animals | Include | Include | Wildlife | 89 | 2023-01-27 | 189214 | keep | 0 | Jan | 2023 | 0.12887 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2023-01-27 07:09 | 2023-01-27 09:22 | 340 | 2:13 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23012700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-01-27 | 45220 | keep | 0 | Jan | 2023 | 0.030799 | 0.00023157 | Sustained | FALSE | FALSE | Not_TMED_Event | 340
HUMACAO | 2023-01-27 07:11 | 2023-01-27 07:13 | 327 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C2301270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-27 | 654 | keep | 0 | Jan | 2023 | 0.00044544 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-27 07:17 | 2023-01-27 07:18 | 327 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C2301270000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-27 | 327 | keep | 0 | Jan | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2023-01-27 07:19 | 2023-01-27 09:18 | 4830 | 1:59 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE SECCIONALIZO ALAMBRE DEL SUELO Y SE CERRO POR CONTROL 98% EN SERVICIO | C23012700015 | New_Event | Primary Wire Break | Include | Include | Equipment | 119 | 2023-01-27 | 574770 | keep | 0 | Jan | 2023 | 0.39147 | 0.0032897 | Sustained | FALSE | FALSE | Not_TMED_Event | 4830
SAN JUAN | 2023-01-27 07:24 | 2023-01-27 17:10 | 216 | 9:46 | P | CONDUCTOR ROTO O ABIERTO | MEDIANTE GOI SJ-230127-01 SE LEVANTO CONDUCTOR PRIMARIO | S23012700054 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 586 | 2023-01-27 | 126576 | keep | 0 | Jan | 2023 | 0.08621 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-27 07:42 | 2023-01-27 07:43 | 1494 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | B2301270000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-01-27 | 1494 | keep | 0 | Jan | 2023 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2023-01-27 07:43 | 2023-01-27 08:05 | 498 | 0:22 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN LA SALIDA DE ALIMENTADOR | B2301270000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 22 | 2023-01-27 | 10956 | keep | 0 | Jan | 2023 | 0.0074621 | 0.00033919 | Sustained | FALSE | FALSE | Not_TMED_Event | 498
BARRANQUITAS | 2023-01-27 07:52 | 2023-01-27 10:00 | 10 | 2:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L SE REEMPLAZO AISLADOR PRIMARIO | C23012700018 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 128 | 2023-01-27 | 1280 | keep | 0 | Jan | 2023 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-01-27 08:00 | 2023-01-27 09:03 | 1 | 1:03 | P | OTRAS CAUSAS | 1 X 15 TRANSFORMADOR PT AVERIADO | R23012700039 | New_Event | Other Causes | Include | Include | Other | 63 | 2023-01-27 | 63 | keep | 0 | Jan | 2023 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-27 08:05 | 2023-01-27 10:00 | 40 | 1:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R23012700024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-01-27 | 4600 | keep | 0 | Jan | 2023 | 0.003133 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-01-27 08:05 | 2023-01-27 15:50 | 12 | 7:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE CORTE DE LINEA PARA REMPLAZAR AISLADOR Y RETEZAR LINEA PRIMARIA | P23012700101 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 465 | 2023-01-27 | 5580 | keep | 0 | Jan | 2023 | 0.0038005 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-01-27 08:05 | 2023-01-27 09:28 | 1494 | 1:23 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO FRENTE A LA SALIDA MEDIANTE G.O.I. BY-230127-01 | B23012700024 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 83 | 2023-01-27 | 124002 | keep | 0 | Jan | 2023 | 0.084457 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-27 08:09 | 2023-01-27 09:54 | 30 | 1:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA 1 X 20 EN CORTE DE LINEA (SECUNDARIO) DESGANCHE | R23012700025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-01-27 | 3150 | keep | 0 | Jan | 2023 | 0.0021455 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-27 08:10 | 2023-01-27 08:11 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S2301270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-27 | 2466 | keep | 0 | Jan | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
ARECIBO | 2023-01-27 08:10 | 2023-01-27 09:11 | 5 | 1:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN CORTE DE LINEA POR FUERTES LLUVIA | A23012700023 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 61 | 2023-01-27 | 305 | keep | 0 | Jan | 2023 | 0.00020773 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-01-27 08:12 | 2023-01-27 10:02 | 40 | 1:50 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA 1 X 50 EN CORTE DE LINEA | R23012700027 | New_Event | Primary Wire Break | Include | Include | Equipment | 110 | 2023-01-27 | 4400 | keep | 0 | Jan | 2023 | 0.0029968 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-01-27 08:33 | 2023-01-27 10:25 | 18 | 1:52 | P | OTRAS CAUSAS | 1 X 5 EN TRANSFORMADOR FUSIBLE OXIDADO | M23012700011 | New_Event | Other Causes | Include | Include | Other | 112 | 2023-01-27 | 2016 | keep | 0 | Jan | 2023 | 0.0013731 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2023-01-27 08:33 | 2023-01-27 10:54 | 60 | 2:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23012700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-01-27 | 8460 | keep | 0 | Jan | 2023 | 0.0057621 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-01-27 08:35 | 2023-01-27 09:30 | 1063 | 0:55 | P | ANIMAL | SE REEMPLAZO CAJA PRIMARIA QUEMADA A CAUSA DE RANA EN TRONCAL 100% EN SERVICIO | C23012700009 | Partial_restoration | Animals | Include | Include | Wildlife | 55 | 2023-01-27 | 58465 | keep | 0 | Jan | 2023 | 0.03982 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-01-27 08:35 | 2023-01-27 15:19 | 3 | 6:44 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO | M23012700006 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 404 | 2023-01-27 | 1212 | keep | 0 | Jan | 2023 | 0.00082549 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2023-01-27 08:43 | 2023-01-27 08:44 | 1571 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23012700035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-27 | 1571 | keep | 0 | Jan | 2023 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
BARRANQUITAS | 2023-01-27 08:53 | 2023-01-27 13:10 | 50 | 4:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE SAFAFO DE LA CAJA PRIMARIA | C23012700047 | New_Event | Primary Wire Break | Include | Include | Equipment | 257 | 2023-01-27 | 12850 | keep | 0 | Jan | 2023 | 0.0087521 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-27 08:56 | 2023-01-27 10:00 | 652 | 1:04 | P | ANIMAL | 1X80 EN C/L PRINCIPAL 1X65 EN C/L INTERIOR CRUCE POR AVE | B23012700055 | New_Event | Animals | Include | Include | Wildlife | 64 | 2023-01-27 | 41728 | keep | 0 | Jan | 2023 | 0.028421 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
FAJARDO | 2023-01-27 08:57 | 2023-01-27 12:00 | 40 | 3:03 | P | DESGANCHE | SE RETIRO PALMA 1 X 100 EN CORTE DE LINEA | R23012700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-01-27 | 7320 | keep | 0 | Jan | 2023 | 0.0049856 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-01-27 08:57 | 2023-01-27 10:54 | 1 | 1:57 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A23012700034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-01-27 | 117 | keep | 0 | Jan | 2023 | 7.9688e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-27 09:05 | 2023-01-27 09:14 | 125 | 0:09 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR 1014-16 LLEVA 30% DE 1013-13 HACIENDO OPERACION CON EL ALIMENTADOR CON EL 1013-13 DISPARA | S2301270000X | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 9 | 2023-01-27 | 1125 | keep | 0 | Jan | 2023 | 0.00076623 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-01-27 09:05 | 2023-01-27 09:14 | 295 | 0:09 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1014-16 LLEVA 30% DE 1013-13 HACIENDO OPERACION CON EL ALIMENTADOR 1013-13 DISPARA | S2301270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-01-27 | 2655 | keep | 0 | Jan | 2023 | 0.0018083 | 0.00020092 | Sustained | FALSE | FALSE | Not_TMED_Event | 295
HUMACAO | 2023-01-27 09:08 | 2023-01-27 14:42 | 20 | 5:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C23012700069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2023-01-27 | 6680 | keep | 0 | Jan | 2023 | 0.0045497 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-27 09:14 | 2023-01-27 18:57 | 3 | 9:43 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | REPONER FUSIBLE 1 X 50 EN SU POR AVERIA DEL MH-16 | S23012700122 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 583 | 2023-01-27 | 1749 | keep | 0 | Jan | 2023 | 0.0011912 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-27 09:18 | 2023-01-27 15:40 | 4 | 6:22 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR DEL SUELO CG-230127-02 | C23012700015 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 382 | 2023-01-27 | 1528 | keep | 0 | Jan | 2023 | 0.0010407 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-27 09:35 | 2023-01-27 11:45 | 19 | 2:10 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA @ LINEA NO FUNDIO | B23012700071 | New_Event | Primary Wire Break | Include | Include | Equipment | 130 | 2023-01-27 | 2470 | keep | 0 | Jan | 2023 | 0.0016823 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
YAUCO | 2023-01-27 09:45 | 2023-01-27 11:45 | 10 | 2:00 | P | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZAR CRUCETA | M23012700021 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 120 | 2023-01-27 | 1200 | keep | 0 | Jan | 2023 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-01-27 09:51 | 2023-01-27 11:33 | 1227 | 1:42 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR POR AISLADOR ROTO | A23012700042 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 102 | 2023-01-27 | 125154 | keep | 0 | Jan | 2023 | 0.085242 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-01-27 09:52 | 2023-01-27 10:05 | 40 | 0:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA | A23012700044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 13 | 2023-01-27 | 520 | keep | 0 | Jan | 2023 | 0.00035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-27 09:53 | 2023-01-27 12:26 | 60 | 2:33 | P | DESGANCHE | 1X65 EN C/L | B23012700078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-01-27 | 9180 | keep | 0 | Jan | 2023 | 0.0062525 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-01-27 09:58 | 2023-01-27 11:45 | 20 | 1:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR LLUVIA | A23012700046 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 107 | 2023-01-27 | 2140 | keep | 0 | Jan | 2023 | 0.0014575 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-27 10:00 | 2023-01-27 11:00 | 922 | 1:00 | T | ALIMENTADOR AMARRADO | DISPARO SE CERRO EN EL CAMPO. CARGA POR 1401-08 | S2301270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 60 | 2023-01-27 | 55320 | keep | 0 | Jan | 2023 | 0.037678 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-01-27 10:00 | 2023-01-27 11:00 | 135 | 1:00 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO EN EL CAMPO. LLEVA EL 1346-05 | S2301270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-01-27 | 8100 | keep | 0 | Jan | 2023 | 0.0055169 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2023-01-27 10:04 | 2023-01-27 10:11 | 1 | 0:07 | P | DESGANCHE | 1X15 EN XMR SE REALIZO DESGANCHE PRIMARIO | B23012700085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 7 | 2023-01-27 | 7 | keep | 0 | Jan | 2023 | 4.7677e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-27 10:06 | 2023-01-27 11:27 | 100 | 1:21 | P | DESGANCHE | 2X65 EN C/L SE REALIZO DESGANCHE | B23012700086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-01-27 | 8100 | keep | 0 | Jan | 2023 | 0.0055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-01-27 10:20 | 2023-01-27 10:57 | 12 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR PARA REEMPLAZO DE BAJANTE SECUNDARIO | A23012700020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-01-27 | 444 | keep | 0 | Jan | 2023 | 0.00030241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-01-27 10:21 | 2023-01-27 12:14 | 60 | 1:53 | P | ARBOL SOBRE LINEA | 1X50 EN C/L SE RETIRO ARBOL DE LA LINEA | B23012700092 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 113 | 2023-01-27 | 6780 | keep | 0 | Jan | 2023 | 0.0046178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-01-27 10:24 | 2023-01-28 12:37 | 11 | 26:13 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 25KVA X 75KVA | B23012700164 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1573 | 2023-01-27 | 17303 | keep | 0 | Jan | 2023 | 0.011785 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-01-27 10:25 | 2023-01-27 11:36 | 40 | 1:11 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA DE PROVISIONAL | C23012700043 | New_Event | Primary Wire Break | Include | Include | Equipment | 71 | 2023-01-27 | 2840 | keep | 0 | Jan | 2023 | 0.0019343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-01-27 10:27 | 2023-01-27 15:57 | 8 | 5:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 X 37.5KVA | C23012700076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 330 | 2023-01-27 | 2640 | keep | 0 | Jan | 2023 | 0.0017981 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-27 10:28 | 2023-01-27 15:25 | 50 | 4:57 | P | NO SE REPORTO CAUSA | 2 X 5O EN CORTE DE LINEA Y 2 X 10 EN RISER | M23012700041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2023-01-27 | 14850 | keep | 0 | Jan | 2023 | 0.010114 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-01-27 10:31 | 2023-01-27 12:05 | 50 | 1:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO VIENTOS | P23012700125 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 94 | 2023-01-27 | 4700 | keep | 0 | Jan | 2023 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-01-27 10:38 | 2023-01-27 14:25 | 35 | 3:47 | P | DESGANCHE | SE RETIRO BAMBUA 1 X 80 EN CORTE DE LINEA | P23012700130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-01-27 | 7945 | keep | 0 | Jan | 2023 | 0.0054113 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2023-01-27 10:40 | 2023-01-27 18:53 | 125 | 8:13 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A23012700058 | New_Event | Primary Wire Break | Include | Include | Equipment | 493 | 2023-01-27 | 61625 | keep | 0 | Jan | 2023 | 0.041973 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-01-27 10:43 | 2023-01-27 10:46 | 271 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL EN SERVICIO | S2301270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-27 | 813 | keep | 0 | Jan | 2023 | 0.00055373 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
HUMACAO | 2023-01-27 10:49 | 2023-01-27 10:50 | 3025 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-27 | 3025 | keep | 0 | Jan | 2023 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
CAGUAS | 2023-01-27 10:51 | 2023-01-27 12:50 | 20 | 1:59 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23012700084 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-01-27 | 2380 | keep | 0 | Jan | 2023 | 0.001621 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-27 11:00 | 2023-01-27 12:30 | 17 | 1:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER 1 X 80 EN C/L | S23012700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2023-01-27 | 1530 | keep | 0 | Jan | 2023 | 0.0010421 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2023-01-27 11:00 | 2023-01-27 18:47 | 40 | 7:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A23012700134 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 467 | 2023-01-27 | 18680 | keep | 0 | Jan | 2023 | 0.012723 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-01-27 11:10 | 2023-01-27 11:11 | 2708 | 0:01 | T | DESGANCHE | RECIERRE | R23012700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-27 | 2708 | keep | 0 | Jan | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-01-27 11:11 | 2023-01-27 13:19 | 80 | 2:08 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | R23012700060 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-01-27 | 10240 | keep | 0 | Jan | 2023 | 0.0069744 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-01-27 11:37 | 2023-01-27 14:02 | 30 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-1 NO CAUSA | R23012700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-01-27 | 4350 | keep | 0 | Jan | 2023 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-27 11:38 | 2023-01-27 11:50 | 42 | 0:12 | P | DESGANCHE | SE ABRIO CORTE DE LINEA HIZO DESGANCHE Y SE RETESO LINEA | R23012700061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 12 | 2023-01-27 | 504 | keep | 0 | Jan | 2023 | 0.00034327 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2023-01-27 11:44 | 2023-01-27 11:47 | 362 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% 1336-10 | S2301270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-27 | 1086 | keep | 0 | Jan | 2023 | 0.00073967 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-01-27 11:44 | 2023-01-27 11:47 | 36 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% 1336-10 | S2301270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-27 | 108 | keep | 0 | Jan | 2023 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2023-01-27 11:44 | 2023-01-27 13:35 | 30 | 1:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | A23012700082 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 111 | 2023-01-27 | 3330 | keep | 0 | Jan | 2023 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-01-27 12:03 | 2023-01-27 14:13 | 15 | 2:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON BARRAS DE PEDESTAL SULFATADAS. | C23012700098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 130 | 2023-01-27 | 1950 | keep | 0 | Jan | 2023 | 0.0013281 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-27 12:05 | 2023-01-27 12:54 | 1 | 0:49 | P | ANIMAL | 1X15 EN MONTURA DE XMRS CRUCE POR AVE | B23012700123 | New_Event | Animals | Include | Include | Wildlife | 49 | 2023-01-27 | 49 | keep | 0 | Jan | 2023 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-27 12:07 | 2023-01-27 16:21 | 8 | 4:14 | P | CAUSAS EXTERNAS | SE REPARARON TOMAS SECUNDARIAS DERRIBADAS POR CAMION PRIVADO | C23012700099 | New_Event | Damage From Public | Include | Include | Public | 254 | 2023-01-27 | 2032 | keep | 0 | Jan | 2023 | 0.001384 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-27 12:10 | 2023-01-27 14:10 | 25 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23012700171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2023-01-27 | 3000 | keep | 0 | Jan | 2023 | 0.0020433 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-01-27 12:14 | 2023-01-27 12:35 | 3630 | 0:21 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR LLUVIA Y VIENTO EN EL AREA | M23012700063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 21 | 2023-01-27 | 76230 | keep | 0 | Jan | 2023 | 0.05192 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
CAGUAS | 2023-01-27 12:15 | 2023-01-27 12:19 | 1 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 1608 CLIENTES DEL 3205-07 | C23012700100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-01-27 | 4 | keep | 0 | Jan | 2023 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-27 12:15 | 2023-01-27 12:19 | 1608 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR LLEVA 1608 CLIENTES DEL 3205-07 | C23012700100 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-01-27 | 6432 | keep | 0 | Jan | 2023 | 0.0043808 | 0.0010952 | Momentary | FALSE | FALSE | Not_TMED_Event | 1608
CAGUAS | 2023-01-27 12:15 | 2023-01-27 12:16 | 3026 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1608 CLEINTES TRANSFERIDFOS AL 3201-01 | C2301270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-27 | 3026 | keep | 0 | Jan | 2023 | 0.002061 | 0.002061 | Momentary | FALSE | FALSE | Not_TMED_Event | 3026
CANOVANAS | 2023-01-27 12:26 | 2023-01-27 13:43 | 120 | 1:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23012700076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-01-27 | 9240 | keep | 0 | Jan | 2023 | 0.0062933 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2023-01-27 12:30 | 2023-01-27 15:30 | 6 | 3:00 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA A POSTE NUEVO | R23012700075 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 180 | 2023-01-27 | 1080 | keep | 0 | Jan | 2023 | 0.00073558 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-01-27 12:34 | 2023-01-27 12:35 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23012700178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-27 | 1310 | keep | 0 | Jan | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
MAYAGÃœEZ | 2023-01-27 12:35 | 2023-01-27 14:10 | 200 | 1:35 | P | MAL TIEMPO/LLUVIA O VIENTO | SE RECETEO INTERRUPTER CAUSA | M23012700079 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 95 | 2023-01-27 | 19000 | keep | 0 | Jan | 2023 | 0.012941 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-01-27 12:37 | 2023-01-27 15:34 | 20 | 2:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONNECTORES SULFATADOS. | R23012700078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 177 | 2023-01-27 | 3540 | keep | 0 | Jan | 2023 | 0.0024111 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-01-27 12:51 | 2023-01-27 16:07 | 39 | 3:16 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C23012700108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-01-27 | 7644 | keep | 0 | Jan | 2023 | 0.0052063 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2023-01-27 12:53 | 2023-01-27 17:00 | 30 | 4:07 | P | DESGANCHE | 1X15 EN XMR DESGANCHE PRIMARIO | B23012700131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2023-01-27 | 7410 | keep | 0 | Jan | 2023 | 0.0050469 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-27 12:55 | 2023-01-27 13:56 | 6 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL BAJANTE DE TRANSFORMADOR Y SECUNDARIA | R23012700077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2023-01-27 | 366 | keep | 0 | Jan | 2023 | 0.00024928 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-01-27 13:02 | 2023-01-27 17:05 | 1 | 4:03 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE DETECTO CAUSA | M23012700080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 243 | 2023-01-27 | 243 | keep | 0 | Jan | 2023 | 0.00016551 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-27 13:03 | 2023-01-27 15:23 | 45 | 2:20 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASES | A23012700094 | New_Event | Animals | Include | Include | Wildlife | 140 | 2023-01-27 | 6300 | keep | 0 | Jan | 2023 | 0.0042909 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-01-27 13:11 | 2023-01-27 18:20 | 10 | 5:09 | P | NO SE REPORTO CAUSA | 1 X 8 EN CORTE DE LINEA | C23012700114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 309 | 2023-01-27 | 3090 | keep | 0 | Jan | 2023 | 0.0021046 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-27 13:24 | 2023-01-27 14:36 | 8 | 1:12 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA PARTIDA NO FUNDIO | B23012700136 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 72 | 2023-01-27 | 576 | keep | 0 | Jan | 2023 | 0.00039231 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-27 13:26 | 2023-01-27 13:27 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23012700137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-27 | 2234 | keep | 0 | Jan | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2023-01-27 13:35 | 2023-01-27 14:54 | 10 | 1:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR EN MALAS CONDICIONES SE VERIFICO EN OMS EVENTO SITUACION PELIGROSA, TIENEN SERVICIO | A23010900153 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2023-01-27 | 790 | keep | 0 | Jan | 2023 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-01-27 13:37 | 2023-01-27 14:21 | 136 | 0:44 | P | CAUSAS EXTERNAS | POSTE PARTIDO POR ACCIDENTE AUTO SE CERRO N/O CONTRA 2501-1 Y 2501-2 | R23012700089 | New_Event | Damage From Public | Include | Include | Public | 44 | 2023-01-27 | 5984 | keep | 0 | Jan | 2023 | 0.0040757 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
CANOVANAS | 2023-01-27 13:44 | 2023-01-27 15:04 | 130 | 1:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R23012700093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2023-01-27 | 10400 | keep | 0 | Jan | 2023 | 0.0070834 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CANOVANAS | 2023-01-27 13:50 | 2023-01-27 15:10 | 161 | 1:20 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | R23012700099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2023-01-27 | 12880 | keep | 0 | Jan | 2023 | 0.0087725 | 0.00010966 | Sustained | FALSE | FALSE | Not_TMED_Event | 161
YAUCO | 2023-01-27 13:50 | 2023-01-27 15:22 | 10 | 1:32 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO LINEA SECUNDARIA Y SE REGULO VOLTAJE | P23012700173 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 92 | 2023-01-27 | 920 | keep | 0 | Jan | 2023 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-01-27 13:58 | 2023-01-27 20:15 | 55 | 6:17 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO DE MACHETE QUEMADO 1 X 65 EN CORTE DE LINEA | P23012700178 | New_Event | Switch Failure | Include | Include | Equipment | 377 | 2023-01-27 | 20735 | keep | 0 | Jan | 2023 | 0.014123 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2023-01-27 14:00 | 2023-01-27 15:37 | 1 | 1:37 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER NO SE REPORTO CAUSA ESE ES EL EVENTO QUE DIERON | P23012700180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2023-01-27 | 97 | keep | 0 | Jan | 2023 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-01-27 14:05 | 2023-01-27 16:10 | 7 | 2:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE | P23012700182 | New_Event | Service Transformer Failure | Include | Include | Equipment | 125 | 2023-01-27 | 875 | keep | 0 | Jan | 2023 | 0.00059596 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-01-27 14:13 | 2023-01-27 17:29 | 3 | 3:16 | P | DESGANCHE | 1 X 30 EN RISER A CLIENTE Y 1 X 40 EN CORTE DE LINEA SE HIZO DESGANCHE | R23012700108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-01-27 | 588 | keep | 0 | Jan | 2023 | 0.00040048 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2023-01-27 14:21 | 2023-01-27 20:45 | 86 | 6:24 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIA | R23012700089 | Partial_restoration | Damage From Public | Include | Include | Public | 384 | 2023-01-27 | 33024 | keep | 0 | Jan | 2023 | 0.022492 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-01-27 14:26 | 2023-01-27 17:25 | 78 | 2:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C23012700130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-01-27 | 13962 | keep | 0 | Jan | 2023 | 0.0095095 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
ARECIBO | 2023-01-27 14:30 | 2023-01-27 18:05 | 6 | 3:35 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA IGUANA CRUZO FASES | A23012700116 | New_Event | Animals | Include | Include | Wildlife | 215 | 2023-01-27 | 1290 | keep | 0 | Jan | 2023 | 0.00087861 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-27 14:31 | 2023-01-27 15:55 | 4 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO BARRA EN PEDESTAL | S23012700208 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2023-01-27 | 336 | keep | 0 | Jan | 2023 | 0.00022885 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-01-27 14:37 | 2023-01-27 15:00 | 4 | 0:23 | P | PARARRAYOS DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZAR PARARRAYOS | M23012700096 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 23 | 2023-01-27 | 92 | keep | 0 | Jan | 2023 | 6.2661e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-01-27 14:47 | 2023-01-27 14:48 | 3026 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE PARTE X 3201-01 | C23012700133 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-27 | 3026 | keep | 0 | Jan | 2023 | 0.002061 | 0.002061 | Momentary | FALSE | FALSE | Not_TMED_Event | 3026
HUMACAO | 2023-01-27 14:57 | 2023-01-27 17:13 | 25 | 2:16 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C23012700134 | New_Event | Animals | Include | Include | Wildlife | 136 | 2023-01-27 | 3400 | keep | 0 | Jan | 2023 | 0.0023157 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-01-27 15:00 | 2023-01-27 16:45 | 60 | 1:45 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23012700097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-01-27 | 6300 | keep | 0 | Jan | 2023 | 0.0042909 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-01-27 15:00 | 2023-01-27 16:52 | 30 | 1:52 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A23012700117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-01-27 | 3360 | keep | 0 | Jan | 2023 | 0.0022885 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-01-27 15:24 | 2023-01-27 16:38 | 20 | 1:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C23012700138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-01-27 | 1480 | keep | 0 | Jan | 2023 | 0.001008 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-27 15:40 | 2023-01-27 17:17 | 1 | 1:37 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | S23012700214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2023-01-27 | 97 | keep | 0 | Jan | 2023 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-27 15:43 | 2023-01-27 21:36 | 80 | 5:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M23012700101 | New_Event | Cutout Failure | Include | Include | Equipment | 353 | 2023-01-27 | 28240 | keep | 0 | Jan | 2023 | 0.019234 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-01-27 15:55 | 2023-01-27 17:10 | 60 | 1:15 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE RETESO LINEA | R23012700119 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 75 | 2023-01-27 | 4500 | keep | 0 | Jan | 2023 | 0.0030649 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-01-27 16:10 | 2023-01-27 17:05 | 16 | 0:55 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR DESGANCHE | C23012700146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-01-27 | 880 | keep | 0 | Jan | 2023 | 0.00059936 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2023-01-27 16:10 | 2023-01-27 18:15 | 18 | 2:05 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO HACIA CAJA DE TRANSFORMADOR | C23012700147 | New_Event | Primary Wire Break | Include | Include | Equipment | 125 | 2023-01-27 | 2250 | keep | 0 | Jan | 2023 | 0.0015325 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
YAUCO | 2023-01-27 16:15 | 2023-01-27 16:19 | 3973 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | P23012700130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-01-27 | 15892 | keep | 0 | Jan | 2023 | 0.010824 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
SAN JUAN | 2023-01-27 16:20 | 2023-01-27 17:49 | 100 | 1:29 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | S23012700220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-01-27 | 8900 | keep | 0 | Jan | 2023 | 0.0060617 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-01-27 16:25 | 2023-01-27 19:37 | 69 | 3:12 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | P23012700220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2023-01-27 | 13248 | keep | 0 | Jan | 2023 | 0.0090232 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2023-01-27 17:33 | 2023-01-27 19:31 | 8 | 1:58 | P | DESGANCHE | 1X10 EN XMR DESGANCHE PRIMARIO | B23012700147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-01-27 | 944 | keep | 0 | Jan | 2023 | 0.00064295 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-27 18:08 | 2023-01-27 19:14 | 1 | 1:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | S23012700022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 66 | 2023-01-27 | 66 | keep | 0 | Jan | 2023 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-01-27 18:12 | 2023-01-27 19:00 | 50 | 0:48 | P | CAUSAS EXTERNAS | GLOBO DE HELIO CRUZO FASE SE CERRO PUENTE ABIERTO 2 X 50 EN CORTE DE LINEA | P23012700237 | New_Event | Damage From Public | Include | Include | Public | 48 | 2023-01-27 | 2400 | keep | 0 | Jan | 2023 | 0.0016346 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-01-27 19:05 | 2023-01-27 19:06 | 3973 | 0:01 | T | PROTECCION DEFECTUOSA | RECIERRE | P23012700241 | New_Event | Protection Miscoordination | Include | Include | Other | 1 | 2023-01-27 | 3973 | keep | 0 | Jan | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
HUMACAO | 2023-01-27 20:16 | 2023-01-27 22:30 | 65 | 2:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN C/L | C23012700164 | New_Event | Primary Wire Break | Include | Include | Equipment | 134 | 2023-01-27 | 8710 | keep | 0 | Jan | 2023 | 0.0059323 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2023-01-27 20:44 | 2023-01-27 22:20 | 200 | 1:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REEMPLAZO PORTAFUSIBLE | C23012700169 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2023-01-27 | 19200 | keep | 0 | Jan | 2023 | 0.013077 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-01-27 21:09 | 2023-01-28 12:10 | 200 | 15:01 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE EN MACHETE PRIMARIO | A23012700153 | New_Event | Primary Wire Break | Include | Include | Equipment | 901 | 2023-01-27 | 180200 | keep | 0 | Jan | 2023 | 0.12273 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-01-27 21:38 | 2023-01-28 09:30 | 15 | 11:52 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | P23012700257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 712 | 2023-01-27 | 10680 | keep | 0 | Jan | 2023 | 0.0072741 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-01-27 21:39 | 2023-01-28 10:26 | 4 | 12:47 | P | ANIMAL | 1 X 5 EN TRANSFORMADOR IGUANA SOBRE CAJA PRIMARIA | A23012700160 | New_Event | Animals | Include | Include | Wildlife | 767 | 2023-01-27 | 3068 | keep | 0 | Jan | 2023 | 0.0020896 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-01-27 22:32 | 2023-01-28 11:22 | 12 | 12:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | S23012700236 | New_Event | Secondary Wire Break | Include | Include | Equipment | 770 | 2023-01-27 | 9240 | keep | 0 | Jan | 2023 | 0.0062933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-01-27 22:59 | 2023-01-28 15:47 | 75 | 16:48 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 37.5KVA | C23012700182 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1008 | 2023-01-27 | 75600 | keep | 0 | Jan | 2023 | 0.051491 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2023-01-27 23:02 | 2023-01-28 09:14 | 42 | 10:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23012700185 | New_Event | Cutout Failure | Include | Include | Equipment | 612 | 2023-01-27 | 25704 | keep | 0 | Jan | 2023 | 0.017507 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BAYAMON | 2023-01-27 23:39 | 2023-01-28 01:05 | 3742 | 1:26 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTELLIRUPTER SE SECCIONALIZO ABRIENDO MACHETES Y SE CERRO INTERRUPTOR EN EL CAMPO 30% EN SERVICIO PB EN AVE. STA. JUANITA/FINAL (CAMINO ESTEBAN ORTIZ) | B23012700177 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 86 | 2023-01-27 | 321812 | keep | 0 | Jan | 2023 | 0.21918 | 0.0025487 | Sustained | FALSE | FALSE | Not_TMED_Event | 3742
ARECIBO | 2023-01-28 00:13 | 2023-01-28 10:26 | 400 | 10:13 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRE MACHETES PARA COLOCAR AISLADOR Y CREAR DESPEJE ENTRE LINEAS PRIMARIAS CRUZADAS | A23012800008 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 613 | 2023-01-28 | 245200 | keep | 0 | Jan | 2023 | 0.167 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-01-28 00:18 | 2023-01-28 03:10 | 10 | 2:52 | P | ANIMAL | 1 X 10 EN XMR SE REPORTA CRUCE CON ANIMAL | B23012800021 | New_Event | Animals | Include | Include | Wildlife | 172 | 2023-01-28 | 1720 | keep | 0 | Jan | 2023 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-28 01:05 | 2023-01-28 01:09 | 1077 | 0:04 | P | MAL TIEMPO/LLUVIA O VIENTO | SE CERRO MACHETES SE REPORTA MAL TIEMPO EN LA ZONA | B23012700177 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 4 | 2023-01-28 | 4308 | keep | 0 | Jan | 2023 | 0.0029342 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-01-28 01:11 | 2023-01-28 12:15 | 90 | 11:04 | P | CONDUCTOR ROTO O ABIERTO | BAJANTE PRIMARIO SAFADO EN CAJA EN CL | A23012800040 | New_Event | Primary Wire Break | Include | Include | Equipment | 664 | 2023-01-28 | 59760 | keep | 0 | Jan | 2023 | 0.040702 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2023-01-28 01:20 | 2023-01-28 10:20 | 50 | 9:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ENREDADERA | M23012800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 540 | 2023-01-28 | 27000 | keep | 0 | Jan | 2023 | 0.01839 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-28 01:49 | 2023-01-28 17:05 | 10 | 15:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5 KVA AVERIADO | S23012800002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 916 | 2023-01-28 | 9160 | keep | 0 | Jan | 2023 | 0.0062388 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-28 02:00 | 2023-01-28 02:01 | 3025 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2301280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 3025 | keep | 0 | Jan | 2023 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
BARRANQUITAS | 2023-01-28 02:06 | 2023-01-28 02:07 | 1854 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23012800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 1854 | keep | 0 | Jan | 2023 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
VEGA BAJA | 2023-01-28 02:19 | 2023-01-28 07:30 | 130 | 5:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CL FUERTE LLUVIA | A23012800051 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 311 | 2023-01-28 | 40430 | keep | 0 | Jan | 2023 | 0.027537 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2023-01-28 02:23 | 2023-01-28 02:26 | 651 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | B2301280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-28 | 1953 | keep | 0 | Jan | 2023 | 0.0013302 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
SAN JUAN | 2023-01-28 03:38 | 2023-01-28 03:39 | 1978 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE 1206-04 LLEVANDO 40% 1204-04 | S2101280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-28 | 1978 | keep | 0 | Jan | 2023 | 0.0013472 | 0.0013472 | Momentary | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2023-01-28 03:38 | 2023-01-28 03:39 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1206-04 LLEVANDO 40% 1204-04 | S2101280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 1799 | keep | 0 | Jan | 2023 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2023-01-28 03:48 | 2023-01-28 03:50 | 243 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 1404-09 LLEVANDO 1420-05 Y 50% DE SU CARGA SE CERRO POR SCADA | S2301280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-28 | 486 | keep | 0 | Jan | 2023 | 0.00033101 | 0.00016551 | Momentary | FALSE | FALSE | Not_TMED_Event | 243
SAN JUAN | 2023-01-28 03:48 | 2023-01-28 03:50 | 4 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO 1404-09 LLEVANDO 1420-05 Y 50% DE SU CARGA SE CERRO POR SCADA | S2301280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-28 | 8 | keep | 0 | Jan | 2023 | 5.4488e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-01-28 06:09 | 2023-01-28 06:10 | 681 | 0:01 | T | DESGANCHE | RECERRO | S2301280000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-28 | 681 | keep | 0 | Jan | 2023 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
FAJARDO | 2023-01-28 06:22 | 2023-01-28 08:35 | 40 | 2:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23012800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-01-28 | 5320 | keep | 0 | Jan | 2023 | 0.0036234 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-28 06:24 | 2023-01-28 09:10 | 60 | 2:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIA | B23012800068 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 166 | 2023-01-28 | 9960 | keep | 0 | Jan | 2023 | 0.0067837 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-01-28 06:41 | 2023-01-28 10:08 | 149 | 3:27 | P | DESGANCHE | 2 X 25 EN C/L DESGANCHE | B23012800070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-01-28 | 30843 | keep | 0 | Jan | 2023 | 0.021007 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
YAUCO | 2023-01-28 06:58 | 2023-01-28 10:10 | 50 | 3:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO VIENTOS | P23012800012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 192 | 2023-01-28 | 9600 | keep | 0 | Jan | 2023 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-01-28 07:00 | 2023-01-28 11:33 | 80 | 4:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M23012800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2023-01-28 | 21840 | keep | 0 | Jan | 2023 | 0.014875 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-28 07:08 | 2023-01-28 07:09 | 681 | 0:01 | T | DESGANCHE | RECERRO | S2301280000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-28 | 681 | keep | 0 | Jan | 2023 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2023-01-28 07:10 | 2023-01-28 07:12 | 1483 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-09 LLEVA LA CARGA DEL 1336-08 LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 LLEVA 5% DEL 1336-07 SE CERRO POR CONTROL | S23012800007 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-28 | 2966 | keep | 0 | Jan | 2023 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-01-28 07:10 | 2023-01-28 07:12 | 1531 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-09 LLEVA LA CARGA DEL 1336-08 LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 LLEVA 5% DEL 1336-07 SE CERRO POR CONTROL | S23012800007 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-28 | 3062 | keep | 0 | Jan | 2023 | 0.0020855 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-01-28 07:10 | 2023-01-28 07:12 | 312 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-09 LLEVA LA CARGA DEL 1336-08 LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 LLEVA 5% DEL 1336-07 SE CERRO POR CONTROL | S23012800007 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-28 | 624 | keep | 0 | Jan | 2023 | 0.000425 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-01-28 07:10 | 2023-01-28 07:12 | 5290 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-09 LLEVA LA CARGA DEL 1336-08 LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 LLEVA 5% DEL 1336-07 SE CERRO POR CONTROL | S23012800007 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-28 | 10580 | keep | 0 | Jan | 2023 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2023-01-28 07:10 | 2023-01-28 07:12 | 207 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-09 LLEVA LA CARGA DEL 1336-08 LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 LLEVA 5% DEL 1336-07 SE CERRO POR CONTROL | S23012800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-28 | 414 | keep | 0 | Jan | 2023 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2023-01-28 07:12 | 2023-01-28 08:33 | 681 | 1:21 | T | DESGANCHE | SE ABRIO MACHETE PARA SECCIONALIZAR POR DESGANCHE PRIMARIO G.O.I. SJ-230128-01 - 90% EN SERVICIO | S23012800010 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-01-28 | 55161 | keep | 0 | Jan | 2023 | 0.03757 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
HUMACAO | 2023-01-28 07:14 | 2023-01-28 17:49 | 7 | 10:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C23012800004 | New_Event | Cutout Failure | Include | Include | Equipment | 635 | 2023-01-28 | 4445 | keep | 0 | Jan | 2023 | 0.0030275 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-01-28 07:23 | 2023-01-28 07:24 | 5069 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23012800013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 5069 | keep | 0 | Jan | 2023 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2023-01-28 07:29 | 2023-01-28 11:00 | 45 | 3:31 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23012800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2023-01-28 | 9495 | keep | 0 | Jan | 2023 | 0.006467 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-01-28 07:35 | 2023-01-28 14:45 | 1 | 7:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN CORTE DE LINEA LLUVIA Y VIENTO | A23012800083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 430 | 2023-01-28 | 430 | keep | 0 | Jan | 2023 | 0.00029287 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-28 07:47 | 2023-01-28 13:19 | 150 | 5:32 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L Y SE LEVANTO CONDUCTOR PRIMARIO | B23012800072 | New_Event | Primary Wire Break | Include | Include | Equipment | 332 | 2023-01-28 | 49800 | keep | 0 | Jan | 2023 | 0.033919 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-01-28 08:08 | 2023-01-28 12:18 | 7 | 4:10 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23012800029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2023-01-28 | 1750 | keep | 0 | Jan | 2023 | 0.0011919 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-01-28 08:10 | 2023-01-28 11:02 | 10 | 2:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONEXIONES SECUNDARIA | B23012800076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 172 | 2023-01-28 | 1720 | keep | 0 | Jan | 2023 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-28 08:23 | 2023-01-28 11:58 | 150 | 3:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CL SE REMPLAZO AISLADOR Y SE CERRO PUENTE PRIMARIO | A23012800113 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 215 | 2023-01-28 | 32250 | keep | 0 | Jan | 2023 | 0.021965 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-01-28 08:33 | 2023-01-28 09:14 | 68 | 0:41 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO G.O.I. SJ-230128-01 - EN SERVICIO EL 10% QUE FALTABA | S23012800010 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 41 | 2023-01-28 | 2788 | keep | 0 | Jan | 2023 | 0.0018989 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-01-28 08:33 | 2023-01-28 08:34 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23012800015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 108 | keep | 0 | Jan | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
GUAYAMA | 2023-01-28 08:42 | 2023-01-28 11:45 | 8 | 3:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23012800022 | New_Event | Primary Wire Break | Include | Include | Equipment | 183 | 2023-01-28 | 1464 | keep | 0 | Jan | 2023 | 0.00099712 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-01-28 08:48 | 2023-01-28 09:26 | 8 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23012800034 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2023-01-28 | 304 | keep | 0 | Jan | 2023 | 0.00020705 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-01-28 08:55 | 2023-01-28 15:07 | 20 | 6:12 | P | DESGANCHE | SE ABRIO PUENTE PRIMARIO (RADIAL) Y SE REALIZO DESGANCHE PRIMARIO MASIVO | S23012800032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2023-01-28 | 7440 | keep | 0 | Jan | 2023 | 0.0050674 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-01-28 09:17 | 2023-01-28 12:00 | 15 | 2:43 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23012800042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-01-28 | 2445 | keep | 0 | Jan | 2023 | 0.0016653 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-28 09:23 | 2023-01-28 09:24 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2301280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-01-28 09:32 | 2023-01-28 12:44 | 11 | 3:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | B23012800089 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 192 | 2023-01-28 | 2112 | keep | 0 | Jan | 2023 | 0.0014385 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2023-01-28 09:36 | 2023-01-28 11:46 | 30 | 2:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO VIENTOS | P23012800025 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 130 | 2023-01-28 | 3900 | keep | 0 | Jan | 2023 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-28 09:37 | 2023-01-28 10:34 | 35 | 0:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23012800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2023-01-28 | 1995 | keep | 0 | Jan | 2023 | 0.0013588 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-01-28 09:48 | 2023-01-28 17:09 | 20 | 7:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON BARRAS DE PEDESTAL TIPO MOLE | S23012800035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 441 | 2023-01-28 | 8820 | keep | 0 | Jan | 2023 | 0.0060073 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-28 09:49 | 2023-01-28 09:51 | 320 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL | B23012800095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-28 | 640 | keep | 0 | Jan | 2023 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-01-28 10:00 | 2023-01-28 10:48 | 1 | 0:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 15 EN XMR MAL TIEMPO LLUVIA | B23012800101 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 48 | 2023-01-28 | 48 | keep | 0 | Jan | 2023 | 3.2693e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-28 10:22 | 2023-01-28 13:07 | 26 | 2:45 | P | DESGANCHE | 1 X 40 EN C/L DEGANCHE | B23012800103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-01-28 | 4290 | keep | 0 | Jan | 2023 | 0.0029219 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
ARECIBO | 2023-01-28 10:26 | 2023-01-28 10:27 | 2407 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO AL REALIZAR OPERACION PARA ABRIR MACHETES PARA SECCIONALIZAR AVERIA LOS CUALES NO ABRIERON | A23012800188 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-01-28 | 2407 | keep | 0 | Jan | 2023 | 0.0016394 | 0.0016394 | Momentary | FALSE | FALSE | Not_TMED_Event | 2407
ARECIBO | 2023-01-28 10:27 | 2023-01-28 11:22 | 400 | 0:55 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRE MACHETES PARA COLOCAR AISLADOR Y CREAR DESPEJE ENTRE LINEAS PRIMARIAS CRUZADAS | A23012800008 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 55 | 2023-01-28 | 22000 | keep | 0 | Jan | 2023 | 0.014984 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-01-28 10:29 | 2023-01-28 12:30 | 40 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23012800027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2023-01-28 | 4840 | keep | 0 | Jan | 2023 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-01-28 10:46 | 2023-01-28 10:47 | 2697 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23012800194 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-01-28 | 2697 | keep | 0 | Jan | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-01-28 10:47 | 2023-01-28 12:48 | 150 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CL FUERTE LLUVIA | A23012800206 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2023-01-28 | 18150 | keep | 0 | Jan | 2023 | 0.012362 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-01-28 10:48 | 2023-01-28 14:26 | 100 | 3:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M23012800030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2023-01-28 | 21800 | keep | 0 | Jan | 2023 | 0.014848 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-28 10:56 | 2023-01-28 14:23 | 60 | 3:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIA | B23012800109 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 207 | 2023-01-28 | 12420 | keep | 0 | Jan | 2023 | 0.0084592 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-01-28 11:03 | 2023-01-28 13:10 | 20 | 2:07 | P | DESGANCHE | 1 X 40 EN PROVISIONAL DESGANCHE | R23012800024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-01-28 | 2540 | keep | 0 | Jan | 2023 | 0.00173 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-01-28 11:09 | 2023-01-28 11:25 | 1 | 0:16 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23012800032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-01-28 | 16 | keep | 0 | Jan | 2023 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-28 11:18 | 2023-01-28 11:19 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2301280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-01-28 11:20 | 2023-01-28 15:28 | 12 | 4:08 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE SUBIO/RETEZO SECUNDARIA (NO FUNDIO) | S23012800048 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 248 | 2023-01-28 | 2976 | keep | 0 | Jan | 2023 | 0.0020269 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-01-28 11:22 | 2023-01-28 12:23 | 2407 | 1:01 | T | CONDUCTOR ARRIADO O CRUZADO | SE COLOCA AISLADOR PARA CREAR DESPEJE ENTRE LINEAS PRIMARIAS CRUZADAS Y SE PONE INTERRUPTOR EN SERVICIO | A23012800218 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 61 | 2023-01-28 | 146827 | keep | 0 | Jan | 2023 | 0.1 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-01-28 11:52 | 2023-01-28 13:41 | 80 | 1:49 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE Y SE LEVANTO CONDUCTOR PRIMARIO | C23012800052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2023-01-28 | 8720 | keep | 0 | Jan | 2023 | 0.0059392 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-01-28 12:05 | 2023-01-28 13:19 | 80 | 1:14 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C23012800066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-01-28 | 5920 | keep | 0 | Jan | 2023 | 0.0040321 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-01-28 12:13 | 2023-01-28 15:46 | 40 | 3:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE REPARO LINEA PRIMARIA | P23012800046 | New_Event | Primary Wire Break | Include | Include | Equipment | 213 | 2023-01-28 | 8520 | keep | 0 | Jan | 2023 | 0.0058029 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-01-28 12:13 | 2023-01-28 16:22 | 30 | 4:09 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23012800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2023-01-28 | 7470 | keep | 0 | Jan | 2023 | 0.0050878 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-01-28 12:13 | 2023-01-28 16:00 | 47 | 3:47 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23012800053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-01-28 | 10669 | keep | 0 | Jan | 2023 | 0.0072666 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
GUAYAMA | 2023-01-28 12:17 | 2023-01-28 15:30 | 8 | 3:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 KVA 4160 VOLT | P23012800047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 193 | 2023-01-28 | 1544 | keep | 0 | Jan | 2023 | 0.0010516 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-01-28 12:22 | 2023-01-28 16:25 | 7 | 4:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIAS | C23012800074 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 243 | 2023-01-28 | 1701 | keep | 0 | Jan | 2023 | 0.0011585 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-01-28 12:30 | 2023-01-28 16:19 | 60 | 3:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C23012800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-01-28 | 13740 | keep | 0 | Jan | 2023 | 0.0093583 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-01-28 12:30 | 2023-01-28 14:42 | 40 | 2:12 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M23012800057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-01-28 | 5280 | keep | 0 | Jan | 2023 | 0.0035962 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-28 12:34 | 2023-01-28 15:57 | 200 | 3:23 | P | ARBOL SOBRE LINEA | 1X100 EN C/L SE RETIRO ARBOL DEL 13KV | S23012800059 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 203 | 2023-01-28 | 40600 | keep | 0 | Jan | 2023 | 0.027652 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-01-28 12:34 | 2023-01-28 13:19 | 1681 | 0:45 | T | DESGANCHE | SU CARGA POR 1303-04, SE SECCIONALIZO PARA DESGANCHE G.O.I. SJ-230128-02 - 90% EN SERVICIO | S23012800061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2023-01-28 | 75645 | keep | 0 | Jan | 2023 | 0.051521 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-01-28 12:34 | 2023-01-28 13:19 | 1598 | 0:45 | T | ALIMENTADOR AMARRADO | SU CARGA POR 1303-04 - 100% EN SERVICIO | S23012800061 | New_Event | Feeder Load Transferred | Include | Include | Other | 45 | 2023-01-28 | 71910 | keep | 0 | Jan | 2023 | 0.048978 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
AGUADILLA | 2023-01-28 12:50 | 2023-01-28 13:47 | 25 | 0:57 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA POR DESGANCHE | M23012800048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2023-01-28 | 1425 | keep | 0 | Jan | 2023 | 0.00097056 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-01-28 12:52 | 2023-01-28 13:57 | 50 | 1:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CL FUERTE LLUVIA | A23012800236 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 65 | 2023-01-28 | 3250 | keep | 0 | Jan | 2023 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-01-28 12:57 | 2023-01-28 13:00 | 863 | 0:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR NO RECERRO CERRADO POR SCADA | M23012800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-01-28 | 2589 | keep | 0 | Jan | 2023 | 0.0017634 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
ARECIBO | 2023-01-28 12:59 | 2023-01-28 13:00 | 1 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A23012800238 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-28 | 1 | keep | 0 | Jan | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-28 12:59 | 2023-01-28 13:00 | 2266 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A23012800238 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-28 | 2266 | keep | 0 | Jan | 2023 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2023-01-28 12:59 | 2023-01-28 13:00 | 1399 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A23012800238 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-28 | 1399 | keep | 0 | Jan | 2023 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
MAYAGÃœEZ | 2023-01-28 13:00 | 2023-01-28 17:21 | 20 | 4:21 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M23012800097 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 261 | 2023-01-28 | 5220 | keep | 0 | Jan | 2023 | 0.0035553 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-01-28 13:07 | 2023-01-28 17:00 | 40 | 3:53 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M23012800053 | New_Event | Primary Wire Break | Include | Include | Equipment | 233 | 2023-01-28 | 9320 | keep | 0 | Jan | 2023 | 0.0063478 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-01-28 13:07 | 2023-01-28 14:47 | 1 | 1:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23012800240 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2023-01-28 | 100 | keep | 0 | Jan | 2023 | 6.811e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-28 13:07 | 2023-01-28 14:47 | 2266 | 1:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23012800240 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2023-01-28 | 226600 | keep | 0 | Jan | 2023 | 0.15434 | 0.0015434 | Sustained | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2023-01-28 13:07 | 2023-01-28 14:47 | 1399 | 1:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23012800240 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2023-01-28 | 139900 | keep | 0 | Jan | 2023 | 0.095285 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
YAUCO | 2023-01-28 13:08 | 2023-01-28 13:40 | 1 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23012800051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2023-01-28 | 32 | keep | 0 | Jan | 2023 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-28 13:13 | 2023-01-28 18:09 | 75 | 4:56 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTES DE LINEA 1 X 25 EN RISER SE REALIZO DESGANCHE | C23012800163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2023-01-28 | 22200 | keep | 0 | Jan | 2023 | 0.01512 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-01-28 13:19 | 2023-01-28 13:41 | 168 | 0:22 | P | DESGANCHE | SU CARGA POR 1303-04, SE REALIZO DESGANCHE MEDIANTE G.O.I. SJ-230128-02 | S23012800061 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-01-28 | 3696 | keep | 0 | Jan | 2023 | 0.0025173 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-01-28 13:20 | 2023-01-28 17:17 | 30 | 3:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M23012800088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2023-01-28 | 7110 | keep | 0 | Jan | 2023 | 0.0048426 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-01-28 13:30 | 2023-01-28 15:43 | 80 | 2:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23012800073 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 133 | 2023-01-28 | 10640 | keep | 0 | Jan | 2023 | 0.0072469 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-28 13:59 | 2023-01-28 17:00 | 15 | 3:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23012800147 | New_Event | Secondary Wire Break | Include | Include | Equipment | 181 | 2023-01-28 | 2715 | keep | 0 | Jan | 2023 | 0.0018492 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-28 14:00 | 2023-01-28 15:53 | 74 | 1:53 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23012800149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-01-28 | 8362 | keep | 0 | Jan | 2023 | 0.0056953 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
AGUADILLA | 2023-01-28 14:00 | 2023-01-28 18:16 | 50 | 4:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | M23012800102 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 256 | 2023-01-28 | 12800 | keep | 0 | Jan | 2023 | 0.008718 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-01-28 14:05 | 2023-01-28 14:21 | 5 | 0:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M23012700135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 16 | 2023-01-28 | 80 | keep | 0 | Jan | 2023 | 5.4488e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 849 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 4245 | keep | 0 | Jan | 2023 | 0.0028913 | 0.00057825 | Momentary | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 893 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 4465 | keep | 0 | Jan | 2023 | 0.0030411 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 602 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 3010 | keep | 0 | Jan | 2023 | 0.0020501 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 43 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 215 | keep | 0 | Jan | 2023 | 0.00014644 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 1389 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 6945 | keep | 0 | Jan | 2023 | 0.0047302 | 0.00094604 | Momentary | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 673 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE BALDRICH 38KV | S23012800138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 3365 | keep | 0 | Jan | 2023 | 0.0022919 | 0.00045838 | Momentary | FALSE | FALSE | Not_TMED_Event | 673
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:14 | 372 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-01-28 | 2232 | keep | 0 | Jan | 2023 | 0.0015202 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 732 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 3660 | keep | 0 | Jan | 2023 | 0.0024928 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 637 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 3185 | keep | 0 | Jan | 2023 | 0.0021693 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 721 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 3605 | keep | 0 | Jan | 2023 | 0.0024553 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 325 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 1625 | keep | 0 | Jan | 2023 | 0.0011068 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 600 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 3000 | keep | 0 | Jan | 2023 | 0.0020433 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 267 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 1335 | keep | 0 | Jan | 2023 | 0.00090926 | 0.00018185 | Momentary | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 621 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 3105 | keep | 0 | Jan | 2023 | 0.0021148 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 2203 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 11015 | keep | 0 | Jan | 2023 | 0.0075023 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 246 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 1230 | keep | 0 | Jan | 2023 | 0.00083775 | 0.00016755 | Momentary | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2023-01-28 14:08 | 2023-01-28 14:13 | 9 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-3200 CAUSANDO QE SE APAGARA LA BARRA DE BALDRICH 38KV | S23012800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-01-28 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-01-28 14:17 | 2023-01-28 14:51 | 13 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO SULFATADO | C23012800132 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-01-28 | 442 | keep | 0 | Jan | 2023 | 0.00030104 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-01-28 14:36 | 2023-01-28 17:00 | 25 | 2:24 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | B23012800152 | New_Event | Primary Wire Break | Include | Include | Equipment | 144 | 2023-01-28 | 3600 | keep | 0 | Jan | 2023 | 0.0024519 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-01-28 14:40 | 2023-01-28 15:45 | 15 | 1:05 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA HACER PRUEBAS DE VOLTAJEEN OMS DICE REMPLAZARON 300 PIES DE LINEA SECUNDARIA Y NEUTRALES EN POSTE Y DESGANCHE, LABORES CONTINUAN MANANA. PROBLEMAS DESDE FIONA | M23011800030 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 65 | 2023-01-28 | 975 | keep | 0 | Jan | 2023 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-01-28 14:42 | 2023-01-28 17:01 | 70 | 2:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23012800253 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-01-28 | 9730 | keep | 0 | Jan | 2023 | 0.0066271 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-01-28 14:44 | 2023-01-28 16:38 | 20 | 1:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BARRAS EN PEDESTAL | R23012800031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 114 | 2023-01-28 | 2280 | keep | 0 | Jan | 2023 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-01-28 14:54 | 2023-01-28 18:00 | 50 | 3:06 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | P23012800068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-01-28 | 9300 | keep | 0 | Jan | 2023 | 0.0063342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-01-28 15:00 | 2023-01-28 19:00 | 35 | 4:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 E CORTE DE LINEA FUERTES VIENTOS | M23012800099 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 240 | 2023-01-28 | 8400 | keep | 0 | Jan | 2023 | 0.0057212 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-01-28 15:00 | 2023-01-28 16:30 | 80 | 1:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | M23012800093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 90 | 2023-01-28 | 7200 | keep | 0 | Jan | 2023 | 0.0049039 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-28 15:02 | 2023-01-28 15:04 | 2052 | 0:02 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA POR 1118-10 LLEVA LA CARGA DEL 1115-03 | S23012800149 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-01-28 | 4104 | keep | 0 | Jan | 2023 | 0.0027952 | 0.0013976 | Momentary | FALSE | FALSE | Not_TMED_Event | 2052
SAN JUAN | 2023-01-28 15:02 | 2023-01-28 15:04 | 134 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA POR 1118-10 LLEVA LA CARGA DEL 1115-03 SE CERRO POR CONTROL | S23012800149 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-28 | 268 | keep | 0 | Jan | 2023 | 0.00018253 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
SAN JUAN | 2023-01-28 15:04 | 2023-01-28 19:55 | 128 | 4:51 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. SJ-230128-03 | S23012800157 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 291 | 2023-01-28 | 37248 | keep | 0 | Jan | 2023 | 0.025369 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
BAYAMON | 2023-01-28 15:19 | 2023-01-28 18:02 | 80 | 2:43 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23012800160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-01-28 | 13040 | keep | 0 | Jan | 2023 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-01-28 15:19 | 2023-01-28 19:26 | 60 | 4:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C23012800096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2023-01-28 | 14820 | keep | 0 | Jan | 2023 | 0.010094 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-01-28 15:23 | 2023-01-28 17:18 | 90 | 1:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23012800097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-01-28 | 10350 | keep | 0 | Jan | 2023 | 0.0070493 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
YAUCO | 2023-01-28 15:58 | 2023-01-28 18:00 | 30 | 2:02 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23012800112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-01-28 | 3660 | keep | 0 | Jan | 2023 | 0.0024928 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-01-28 16:00 | 2023-01-28 16:55 | 10 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M23012800075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-01-28 | 550 | keep | 0 | Jan | 2023 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-01-28 16:37 | 2023-01-28 18:03 | 80 | 1:26 | P | DESGANCHE | 1 X 65 Y 1 X 100 EN DIFERENTES CORTES DE LINEA REQUIERE DESGANCHE | M23012800112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-01-28 | 6880 | keep | 0 | Jan | 2023 | 0.0046859 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-28 16:58 | 2023-01-28 20:06 | 10 | 3:08 | P | SECUNDARIA/DESGANCHE | SE REMPLAZARON APROX. 30' DE SECUNDARIA Y SE REALIZO DESGANCHE SECUNDARIO | S23012800184 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 188 | 2023-01-28 | 1880 | keep | 0 | Jan | 2023 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-28 17:06 | 2023-01-28 21:00 | 64 | 3:54 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L SE LEVANTO CONDUCTOR | S23012800185 | New_Event | Primary Wire Break | Include | Include | Equipment | 234 | 2023-01-28 | 14976 | keep | 0 | Jan | 2023 | 0.0102 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
BAYAMON | 2023-01-28 17:34 | 2023-01-28 17:35 | 2735 | 0:01 | T | DESGANCHE | RECERRO | B2301280000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-28 | 2735 | keep | 0 | Jan | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2023-01-28 17:35 | 2023-01-28 18:04 | 1364 | 0:29 | P | DESGANCHE | SE SECCIONALIZO PARA RETIRAR BAMBUA, REALIZAR DESGANCHE Y REPARAR CONDUCTOR PRIMARIO EN EL SUELO EL CUAL DISCURRE POR EL MONTE - QUEDA 60% SIN SERVICIO | B2301280000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 29 | 2023-01-28 | 39556 | keep | 0 | Jan | 2023 | 0.026941 | 0.00092901 | Sustained | FALSE | FALSE | Not_TMED_Event | 1364
BAYAMON | 2023-01-28 18:04 | 2023-01-28 20:12 | 2735 | 2:08 | T | DESGANCHE | DISPARO DE BKR SE SECCIONALIZO PARA RETIRAR BAMBUA, REALIZAR DESGANCHE Y REPARAR CONDUCTOR PRIMARIO EN EL SUELO EL CUAL DISCURRE POR EL MONTE BY-230128-02 | B23012800182 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-01-28 | 350080 | keep | 0 | Jan | 2023 | 0.23844 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-01-28 18:24 | 2023-01-28 19:46 | 18 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR 1 X 30 EN CORTE DE LINEA | C23012800108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2023-01-28 | 1476 | keep | 0 | Jan | 2023 | 0.0010053 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-01-28 18:27 | 2023-01-29 13:05 | 15 | 18:38 | P | TERMINACION SOTERRADA AVERIADA | SE REPARARON TERMINACIONES EN RISER Y 1 X 25 EN RISER | C23012800110 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1118 | 2023-01-28 | 16770 | keep | 0 | Jan | 2023 | 0.011422 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-28 18:29 | 2023-01-28 18:30 | 1588 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B23012800209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 1588 | keep | 0 | Jan | 2023 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
MAYAGÃœEZ | 2023-01-28 18:30 | 2023-01-28 20:40 | 20 | 2:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN RISER LLUVIA Y FUERTES VIENTOS | M23012800122 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 130 | 2023-01-28 | 2600 | keep | 0 | Jan | 2023 | 0.0017708 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-01-28 18:54 | 2023-01-28 21:44 | 20 | 2:50 | P | ANIMAL | 1X100 EN C/L Y 1X20 EN XMR SE RETIRO IGUANA | S23012800196 | New_Event | Animals | Include | Include | Wildlife | 170 | 2023-01-28 | 3400 | keep | 0 | Jan | 2023 | 0.0023157 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-01-28 19:00 | 2023-01-29 09:25 | 50 | 14:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M23012800124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 865 | 2023-01-28 | 43250 | keep | 0 | Jan | 2023 | 0.029457 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-28 19:07 | 2023-01-28 21:43 | 1 | 2:36 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | S23012800197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2023-01-28 | 156 | keep | 0 | Jan | 2023 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-28 19:10 | 2023-01-28 19:28 | 2888 | 0:18 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR POR SEGURIDAD A PETICION DE JUAN CARLOS RESTO POR BAJANTE PRIMARIO ZAFADO Y CRUZANDO CON CRUCETA PRENDIDO EN FUEGO EN EL CORTE DE LINEAS PRICIPAL | A23012800291 | New_Event | Primary Wire Break | Include | Include | Equipment | 18 | 2023-01-28 | 51984 | keep | 0 | Jan | 2023 | 0.035406 | 0.001967 | Sustained | FALSE | FALSE | Not_TMED_Event | 2888
VEGA BAJA | 2023-01-28 19:28 | 2023-01-28 19:49 | 50 | 0:21 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO Y SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | A23012800295 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 21 | 2023-01-28 | 1050 | keep | 0 | Jan | 2023 | 0.00071515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-01-28 20:12 | 2023-01-29 15:01 | 1364 | 18:49 | P | DESGANCHE | SWF BY-230128-02 SE RETIRO BAMBUA, REALIZO DESGANCHE Y LEVANTO CONDUCTOR PRIMARIO EN EL SUELO EL CUAL DISCURRE POR EL MONTE | B23012800182 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1129 | 2023-01-28 | 1539956 | keep | 0 | Jan | 2023 | 1.0489 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-28 20:45 | 2023-01-28 20:46 | 2126 | 0:01 | T | ANIMAL | DISPARO SE CERRO POR CONTROL | C23012800114 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-01-28 | 2126 | keep | 0 | Jan | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
CANOVANAS | 2023-01-28 20:46 | 2023-01-28 20:47 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2301280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 1026 | keep | 0 | Jan | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
HUMACAO | 2023-01-28 20:46 | 2023-01-28 23:48 | 129 | 3:02 | P | ANIMAL | 3X65 EN RISER Y RANA CRUZO LINEAS | C23012800117 | 1st_after_momentary | Animals | Include | Include | Wildlife | 182 | 2023-01-28 | 23478 | keep | 0 | Jan | 2023 | 0.015991 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
BAYAMON | 2023-01-28 20:56 | 2023-01-29 09:54 | 75 | 12:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN EN C/L Y SE REMPLAZO AISLADOR ROTO | B23012800270 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 778 | 2023-01-28 | 58350 | keep | 0 | Jan | 2023 | 0.039742 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-01-28 21:49 | 2023-01-29 01:05 | 200 | 3:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 Y 1 X 80 EN C/L LLUVIAS | B23012800292 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 196 | 2023-01-28 | 39200 | keep | 0 | Jan | 2023 | 0.026699 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-01-28 22:00 | 2023-01-29 00:25 | 75 | 2:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23012800309 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 145 | 2023-01-28 | 10875 | keep | 0 | Jan | 2023 | 0.0074069 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2023-01-28 22:28 | 2023-01-29 09:37 | 100 | 11:09 | P | DESGANCHE | 2 X 80 EN C/L | C23012800121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 669 | 2023-01-28 | 66900 | keep | 0 | Jan | 2023 | 0.045565 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-28 22:47 | 2023-01-29 13:46 | 17 | 14:59 | P | DESGANCHE | 2 X 40 EN CL DESGANCHE | A23012800311 | New_Event | Vegetation Contact | Include | Include | Vegetation | 899 | 2023-01-28 | 15283 | keep | 0 | Jan | 2023 | 0.010409 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-01-28 23:17 | 2023-01-28 23:18 | 767 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 LLEVA 50% DE SU CARGA Y LLEVA 1709-05 | B2301280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-28 | 767 | keep | 0 | Jan | 2023 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2023-01-28 23:17 | 2023-01-28 23:18 | 2364 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1709-03 LLEVA 50% DE SU CARGA Y LLEVA 1709-05 | B2301280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-28 | 2364 | keep | 0 | Jan | 2023 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BARRANQUITAS | 2023-01-28 23:24 | 2023-01-29 11:14 | 16 | 11:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L REEMPLAZO AISLADOR | C23012800135 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 710 | 2023-01-28 | 11360 | keep | 0 | Jan | 2023 | 0.0077372 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-01-28 23:49 | 2023-01-29 08:11 | 1 | 8:22 | P | DESGANCHE | 1 X 65 EN C/L | C23012800138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 502 | 2023-01-28 | 502 | keep | 0 | Jan | 2023 | 0.00034191 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-29 00:01 | 2023-01-29 10:50 | 5 | 10:49 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REALIZO DESGANCHE SECUNDARIO | B23012900002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 649 | 2023-01-29 | 3245 | keep | 0 | Jan | 2023 | 0.0022102 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-01-29 00:36 | 2023-01-29 10:01 | 50 | 9:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA POR LLUVIAS | M23012900002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 565 | 2023-01-29 | 28250 | keep | 0 | Jan | 2023 | 0.019241 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-29 00:50 | 2023-01-29 00:51 | 6136 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23012900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 6136 | keep | 0 | Jan | 2023 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2023-01-29 01:15 | 2023-01-29 01:16 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23012900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 3511 | keep | 0 | Jan | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2023-01-29 01:20 | 2023-01-29 09:49 | 26 | 8:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L Y SE REMPLAZO CAJA PRIMARIA | B23012900008 | New_Event | Cutout Failure | Include | Include | Equipment | 509 | 2023-01-29 | 13234 | keep | 0 | Jan | 2023 | 0.0090136 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
AGUADILLA | 2023-01-29 01:30 | 2023-01-29 09:46 | 30 | 8:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR LLUVIAS | M23012900004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 496 | 2023-01-29 | 14880 | keep | 0 | Jan | 2023 | 0.010135 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-29 01:40 | 2023-01-29 01:43 | 1681 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 LLEVA 1346-06 Y 1303-01. OPERO AL MISMO TIEMPO QUE EL 1303-03. | S2301290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-29 | 5043 | keep | 0 | Jan | 2023 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-01-29 01:40 | 2023-01-29 01:42 | 726 | 0:02 | T | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1303-03 LLEVA 1346-04 | S23012900002 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 2 | 2023-01-29 | 1452 | keep | 0 | Jan | 2023 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-01-29 01:40 | 2023-01-29 01:42 | 3932 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-03 LLEVA 1346-04 | S23012900002 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-29 | 7864 | keep | 0 | Jan | 2023 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2023-01-29 01:40 | 2023-01-29 01:43 | 1598 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-04 LLEVA 1346-06 Y 1303-01. OPERO AL MISMO TIEMPO QUE EL 1303-03. | S2301290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-29 | 4794 | keep | 0 | Jan | 2023 | 0.0032652 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2023-01-29 01:59 | 2023-01-29 02:01 | 726 | 0:02 | T | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1303-03 LLEVA EL 1346-04 | S23012900013 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 2 | 2023-01-29 | 1452 | keep | 0 | Jan | 2023 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-01-29 01:59 | 2023-01-29 02:01 | 3932 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-03 LLEVA EL 1346-04 | S23012900013 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-29 | 7864 | keep | 0 | Jan | 2023 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2023-01-29 02:02 | 2023-01-29 04:34 | 726 | 2:32 | T | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1303-03 LLEVA EL 1346-04. SE ENCONTRARON TERMINACIONES AVERIADAS EN EL RISER DE SALIDA DEL 1303-03. SE TRANSFIRIERON LAS CARGAS AL 1303-04 ATRAVEZ DE LA BARRA DE INSPECCION. SJ-230129-01 | S23012900014 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 152 | 2023-01-29 | 110352 | keep | 0 | Jan | 2023 | 0.07516 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-01-29 02:02 | 2023-01-29 04:34 | 3932 | 2:32 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-03 LLEVA EL 1346-04. SE ENCONTRARON TERMINACIONES AVERIADAS EN EL RISER DE SALIDA DEL 1303-03. SE TRANSFIRIERON LAS CARGAS AL 1303-04 ATRAVEZ DE LA BARRA DE INSPECCION. SJ-230129-01 | S23012900014 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 152 | 2023-01-29 | 597664 | keep | 0 | Jan | 2023 | 0.40707 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
CANOVANAS | 2023-01-29 02:50 | 2023-01-29 08:20 | 85 | 5:30 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23012900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2023-01-29 | 28050 | keep | 0 | Jan | 2023 | 0.019105 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2023-01-29 02:58 | 2023-01-29 09:05 | 30 | 6:07 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23012900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2023-01-29 | 11010 | keep | 0 | Jan | 2023 | 0.0074989 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-01-29 03:13 | 2023-01-29 09:28 | 30 | 6:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA | M23012900012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 375 | 2023-01-29 | 11250 | keep | 0 | Jan | 2023 | 0.0076623 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-01-29 03:40 | 2023-01-29 10:00 | 35 | 6:20 | P | DESGANCHE | 1 X 50 EN C/L | C23012900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2023-01-29 | 13300 | keep | 0 | Jan | 2023 | 0.0090586 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-01-29 04:24 | 2023-01-29 09:09 | 40 | 4:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIA | M23012900013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 285 | 2023-01-29 | 11400 | keep | 0 | Jan | 2023 | 0.0077645 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-29 04:33 | 2023-01-29 09:04 | 10 | 4:31 | P | DESGANCHE | 1 X 15 EN C/L DESGANCHE | B23012900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2023-01-29 | 2710 | keep | 0 | Jan | 2023 | 0.0018458 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-29 06:46 | 2023-01-29 10:40 | 156 | 3:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER REEMPLAZO CAJA QUEMADA | C23012900010 | New_Event | Cutout Failure | Include | Include | Equipment | 234 | 2023-01-29 | 36504 | keep | 0 | Jan | 2023 | 0.024863 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
SAN JUAN | 2023-01-29 06:57 | 2023-01-29 11:00 | 100 | 4:03 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 EN RISER A SU-2 1 X 80 EN RISER A SU-3 Y 1 X 100 EN RISER A SU-1 CONTAMINACION | S23012900089 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 243 | 2023-01-29 | 24300 | keep | 0 | Jan | 2023 | 0.016551 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-29 07:15 | 2023-01-29 07:16 | 215 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23012900053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-01-29 | 215 | keep | 0 | Jan | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-01-29 07:16 | 2023-01-29 08:40 | 80 | 1:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L MAL TIEMPO LLUVIA | B23012900055 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 84 | 2023-01-29 | 6720 | keep | 0 | Jan | 2023 | 0.004577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-29 07:23 | 2023-01-29 07:24 | 1977 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 40% POR 1206-04 | S23012900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-29 | 1977 | keep | 0 | Jan | 2023 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2023-01-29 07:23 | 2023-01-29 07:24 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA 40% DEL 1204-04 | S23012900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 1799 | keep | 0 | Jan | 2023 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
AGUADILLA | 2023-01-29 07:28 | 2023-01-29 11:15 | 50 | 3:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | M23012900016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 227 | 2023-01-29 | 11350 | keep | 0 | Jan | 2023 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-01-29 07:33 | 2023-01-29 10:42 | 1 | 3:09 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA POR ALAMBRE PRIMARIO EN PISO | P23012900009 | New_Event | Primary Wire Break | Include | Include | Equipment | 189 | 2023-01-29 | 189 | keep | 0 | Jan | 2023 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-29 07:34 | 2023-01-29 10:42 | 40 | 3:08 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23012900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-01-29 | 7520 | keep | 0 | Jan | 2023 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-01-29 07:50 | 2023-01-29 07:51 | 1271 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23012900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 1271 | keep | 0 | Jan | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2023-01-29 08:06 | 2023-01-29 08:07 | 473 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | C23012900017 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-01-29 | 473 | keep | 0 | Jan | 2023 | 0.00032216 | 0.00032216 | Momentary | FALSE | FALSE | Not_TMED_Event | 473
CAGUAS | 2023-01-29 08:07 | 2023-01-29 10:09 | 40 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIA | C23012900018 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2023-01-29 | 4880 | keep | 0 | Jan | 2023 | 0.0033237 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-01-29 08:18 | 2023-01-29 09:50 | 150 | 1:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L REEMPLAZO DE CAJA PRIMARIA | R23012900009 | New_Event | Cutout Failure | Include | Include | Equipment | 92 | 2023-01-29 | 13800 | keep | 0 | Jan | 2023 | 0.0093991 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2023-01-29 08:19 | 2023-01-29 13:29 | 40 | 5:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23012900012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2023-01-29 | 12400 | keep | 0 | Jan | 2023 | 0.0084456 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-01-29 08:19 | 2023-01-29 13:45 | 25 | 5:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | M23012900021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2023-01-29 | 8150 | keep | 0 | Jan | 2023 | 0.0055509 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-01-29 08:28 | 2023-01-29 09:12 | 1 | 0:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L FUSIBLE SULFATADO | R23012900010 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2023-01-29 | 44 | keep | 0 | Jan | 2023 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-01-29 08:46 | 2023-01-29 09:35 | 81 | 0:49 | P | ANIMAL | 1 X 25 Y 1 X 50 EN C/LS CRUCE X AVE | C23012900023 | New_Event | Animals | Include | Include | Wildlife | 49 | 2023-01-29 | 3969 | keep | 0 | Jan | 2023 | 0.0027033 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
SAN JUAN | 2023-01-29 09:00 | 2023-01-29 09:01 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23012900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 45 | keep | 0 | Jan | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-01-29 09:11 | 2023-01-29 09:15 | 3500 | 0:04 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE DE SU CARGA POR 1343-05 | S23012900097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-01-29 | 14000 | keep | 0 | Jan | 2023 | 0.0095353 | 0.0023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 3500
BAYAMON | 2023-01-29 09:49 | 2023-01-29 11:28 | 303 | 1:39 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | B23012900131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-01-29 | 29997 | keep | 0 | Jan | 2023 | 0.020431 | 0.00020637 | Sustained | FALSE | FALSE | Not_TMED_Event | 303
ARECIBO | 2023-01-29 09:50 | 2023-01-29 12:52 | 3 | 3:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN XMR SE REMPLAZO DOS CAJAS PRIMARIAS EN TRANSDORMADOR | A23012900010 | New_Event | Cutout Failure | Include | Include | Equipment | 182 | 2023-01-29 | 546 | keep | 0 | Jan | 2023 | 0.00037188 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2023-01-29 10:12 | 2023-01-29 12:38 | 65 | 2:26 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | P23012900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-01-29 | 9490 | keep | 0 | Jan | 2023 | 0.0064636 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-01-29 10:18 | 2023-01-29 14:02 | 50 | 3:44 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23012900117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-01-29 | 11200 | keep | 0 | Jan | 2023 | 0.0076283 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-01-29 10:22 | 2023-01-29 12:59 | 4 | 2:37 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XMR DESGANCHO SECUNDARIA | C23012900036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 157 | 2023-01-29 | 628 | keep | 0 | Jan | 2023 | 0.00042773 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-01-29 10:36 | 2023-01-29 11:31 | 1 | 0:55 | P | ANIMAL | 2 X 65 EN C/L CRUCE X AVE | C23012900033 | New_Event | Animals | Include | Include | Wildlife | 55 | 2023-01-29 | 55 | keep | 0 | Jan | 2023 | 3.746e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-29 10:50 | 2023-01-29 10:51 | 1261 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23012900042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 1261 | keep | 0 | Jan | 2023 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
CAGUAS | 2023-01-29 11:01 | 2023-01-29 12:22 | 4 | 1:21 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23012900043 | New_Event | Animals | Include | Include | Wildlife | 81 | 2023-01-29 | 324 | keep | 0 | Jan | 2023 | 0.00022067 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-01-29 11:15 | 2023-01-29 12:34 | 15 | 1:19 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REALIZO DESGANCHE SECUNDARIO | B23012900157 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 79 | 2023-01-29 | 1185 | keep | 0 | Jan | 2023 | 0.0008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-01-29 11:22 | 2023-01-29 11:26 | 3597 | 0:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23012900158 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2023-01-29 | 14388 | keep | 0 | Jan | 2023 | 0.0097996 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-01-29 11:26 | 2023-01-29 14:06 | 300 | 2:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 Y 3 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | B23012900205 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 160 | 2023-01-29 | 48000 | keep | 0 | Jan | 2023 | 0.032693 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2023-01-29 11:39 | 2023-01-29 12:20 | 8 | 0:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R23012900014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 41 | 2023-01-29 | 328 | keep | 0 | Jan | 2023 | 0.0002234 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-01-29 11:43 | 2023-01-29 17:50 | 50 | 6:07 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN CL SE RETEZO LINEAS PRIMARIAS | A23012900017 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 367 | 2023-01-29 | 18350 | keep | 0 | Jan | 2023 | 0.012498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-01-29 11:58 | 2023-01-29 12:30 | 10 | 0:32 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE | S23012900098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2023-01-29 | 320 | keep | 0 | Jan | 2023 | 0.00021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-29 12:00 | 2023-01-29 15:26 | 300 | 3:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO MEDIANTE G.O.I. SJ-230129-02 | S23012900128 | New_Event | Primary Wire Break | Include | Include | Equipment | 206 | 2023-01-29 | 61800 | keep | 0 | Jan | 2023 | 0.042092 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-01-29 12:26 | 2023-01-29 15:01 | 15 | 2:35 | P | ANIMAL | 1 X 65 EN CL 1X 15 EN XMR CRUCE POR ANIMAL | B23012900022 | New_Event | Animals | Include | Include | Wildlife | 155 | 2023-01-29 | 2325 | keep | 0 | Jan | 2023 | 0.0015835 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-29 12:28 | 2023-01-29 14:04 | 12 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO EN XMR | S23012900131 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2023-01-29 | 1152 | keep | 0 | Jan | 2023 | 0.00078462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-01-29 12:43 | 2023-01-29 18:01 | 60 | 5:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23012900042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2023-01-29 | 19080 | keep | 0 | Jan | 2023 | 0.012995 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-01-29 12:43 | 2023-01-29 15:00 | 10 | 2:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR REPARO SECUNDARIA | C23012900056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 137 | 2023-01-29 | 1370 | keep | 0 | Jan | 2023 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-29 12:53 | 2023-01-29 12:54 | 40 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO SOLO LLEVA 10% DE SU CARGA | S23012900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 40 | keep | 0 | Jan | 2023 | 2.7244e-05 | 2.7244e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-29 12:54 | 2023-01-29 16:31 | 40 | 3:37 | P | NO SE REPORTO CAUSA | 1X80 DE RISER @ SU-1 | S23012900135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2023-01-29 | 8680 | keep | 0 | Jan | 2023 | 0.0059119 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-29 13:05 | 2023-01-29 13:06 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23012900251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 1746 | keep | 0 | Jan | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BARRANQUITAS | 2023-01-29 13:06 | 2023-01-29 14:34 | 3 | 1:28 | P | SECUNDARIA/DESGANCHE | 1 X 5 EN TRANSFORMADOR Y DESGANCHE | C23012900058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 88 | 2023-01-29 | 264 | keep | 0 | Jan | 2023 | 0.00017981 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-01-29 13:34 | 2023-01-29 16:26 | 150 | 2:52 | P | DESGANCHE | 1X80 EN C/L DESGANCHE PRIMARIO | S23012900139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-01-29 | 25800 | keep | 0 | Jan | 2023 | 0.017572 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2023-01-29 13:35 | 2023-01-29 13:36 | 1241 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECERRO SE COLOCO RECIERRE EN OFF Y SE REALIZO PRUEBA QUEDANDO EN SERVICIO | A23012900024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 1241 | keep | 0 | Jan | 2023 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
MAYAGÃœEZ | 2023-01-29 13:57 | 2023-01-29 13:58 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23012900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 4641 | keep | 0 | Jan | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
BAYAMON | 2023-01-29 14:29 | 2023-01-29 18:48 | 10 | 4:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REPARO SECUNDARIA | B23012900290 | New_Event | Secondary Wire Break | Include | Include | Equipment | 259 | 2023-01-29 | 2590 | keep | 0 | Jan | 2023 | 0.001764 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-01-29 14:30 | 2023-01-29 15:05 | 10 | 0:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23012900049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 35 | 2023-01-29 | 350 | keep | 0 | Jan | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-29 14:38 | 2023-01-29 17:29 | 14 | 2:51 | P | DESGANCHE | 1 X 15 EN XMR Y DESGANCHE | B23012900294 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-01-29 | 2394 | keep | 0 | Jan | 2023 | 0.0016305 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-01-29 14:41 | 2023-01-29 17:21 | 10 | 2:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 XMR SECUANDARIA CRUZADA | B23012900296 | New_Event | Secondary Wire Break | Include | Include | Equipment | 160 | 2023-01-29 | 1600 | keep | 0 | Jan | 2023 | 0.0010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-01-29 14:42 | 2023-01-29 14:43 | 1613 | 0:01 | T | DESGANCHE | RECIERRE DE BKR | R2301290000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-01-29 | 1613 | keep | 0 | Jan | 2023 | 0.0010986 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2023-01-29 14:43 | 2023-01-29 17:18 | 100 | 2:35 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | R23012900027 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-01-29 | 15500 | keep | 0 | Jan | 2023 | 0.010557 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-01-29 15:34 | 2023-01-30 02:45 | 70 | 11:11 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO CASOS DE LA MISMA AREA NO ES LO MISMO AL EVENTO 55 | M23012900054 | New_Event | Primary Pole Failure | Include | Include | Equipment | 671 | 2023-01-29 | 46970 | keep | 0 | Jan | 2023 | 0.031991 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-01-29 15:35 | 2023-01-29 15:36 | 614 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO X CONTROL | R2301290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 614 | keep | 0 | Jan | 2023 | 0.00041819 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
AGUADILLA | 2023-01-29 15:41 | 2023-01-30 13:15 | 1 | 21:34 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE PASO TRANSFORMADOR DE POSTE PARTIDO A POSTE NUEVO | M23012900055 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1294 | 2023-01-29 | 1294 | keep | 0 | Jan | 2023 | 0.00088134 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-29 15:50 | 2023-01-29 18:08 | 35 | 2:18 | P | TRANSFORMADOR AVERIADO | SE SECCIONALIZO PARA REMPLAZO DE PM (T-99) MEDIANTE G.O.I. SJ-230129-03 | S23012900151 | New_Event | Service Transformer Failure | Include | Include | Equipment | 138 | 2023-01-29 | 4830 | keep | 0 | Jan | 2023 | 0.0032897 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-01-29 15:59 | 2023-01-29 22:00 | 80 | 6:01 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | B23012900316 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2023-01-29 | 28880 | keep | 0 | Jan | 2023 | 0.01967 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-29 15:59 | 2023-01-29 22:53 | 100 | 6:54 | P | DESGANCHE | 2X100 EN C/L DESGANCHE | S23012900155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 414 | 2023-01-29 | 41400 | keep | 0 | Jan | 2023 | 0.028197 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-29 16:00 | 2023-01-29 16:47 | 71 | 0:47 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23012900156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2023-01-29 | 3337 | keep | 0 | Jan | 2023 | 0.0022728 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
BARRANQUITAS | 2023-01-29 16:05 | 2023-01-30 07:53 | 1 | 15:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REEMPLAZO AISLADOR | C23012900066 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 948 | 2023-01-29 | 948 | keep | 0 | Jan | 2023 | 0.00064568 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-29 16:05 | 2023-01-29 16:50 | 4 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M23012900038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-01-29 | 180 | keep | 0 | Jan | 2023 | 0.0001226 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-01-29 16:42 | 2023-01-29 17:40 | 60 | 0:58 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | R23012900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2023-01-29 | 3480 | keep | 0 | Jan | 2023 | 0.0023702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-01-29 16:55 | 2023-01-29 17:54 | 20 | 0:59 | P | PROBLEMA DEL CLIENTE | 1 X 65 EN CORTE DE LINEA 2 X 40 EN SU HACIA TRANSCLOUSURE DEL CLIENTE BOMBA AAA CONTAMINADA | R23012900034 | New_Event | Customer-Related Interruption | Include | Include | Public | 59 | 2023-01-29 | 1180 | keep | 0 | Jan | 2023 | 0.00080369 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-01-29 17:13 | 2023-01-29 17:14 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23012900068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 5630 | keep | 0 | Jan | 2023 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
AGUADILLA | 2023-01-29 17:20 | 2023-01-29 17:45 | 2 | 0:25 | P | CAUSAS EXTERNAS | ABRIR RISER PARA REPARAR SALIDA DEL RISER IMPACTADA POR UN CAMION | M23012900064 | New_Event | Damage From Public | Include | Include | Public | 25 | 2023-01-29 | 50 | keep | 0 | Jan | 2023 | 3.4055e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2023-01-29 17:39 | 2023-01-29 19:50 | 5 | 2:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CAMBIO BARRA DE PEDESTAL SECUNDARIO | P23012900073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 131 | 2023-01-29 | 655 | keep | 0 | Jan | 2023 | 0.00044612 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-01-29 17:40 | 2023-01-29 17:45 | 3 | 0:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M23012900031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 5 | 2023-01-29 | 15 | keep | 0 | Jan | 2023 | 1.0216e-05 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-01-29 17:53 | 2023-01-29 20:42 | 1 | 2:49 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE DE LINEA A CAJA NO FUNDIO | C23012900070 | New_Event | Primary Wire Break | Include | Include | Equipment | 169 | 2023-01-29 | 169 | keep | 0 | Jan | 2023 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-01-29 17:56 | 2023-01-29 20:17 | 300 | 2:21 | P | DESGANCHE | 2 X 100 EN CL DESGANCHE | A23012900072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-01-29 | 42300 | keep | 0 | Jan | 2023 | 0.02881 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-01-29 18:08 | 2023-01-29 21:38 | 35 | 3:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM AVERIADO (T-99) MEDIANTE G.O.I. SJ-230129-03 | S23012900151 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 210 | 2023-01-29 | 7350 | keep | 0 | Jan | 2023 | 0.0050061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-29 18:29 | 2023-01-30 02:34 | 81 | 8:05 | P | DESGANCHE | 2X50 EN C/L DESGANCHE | S23012900196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 485 | 2023-01-29 | 39285 | keep | 0 | Jan | 2023 | 0.026757 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2023-01-29 18:52 | 2023-01-29 19:04 | 10 | 0:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL SECUNDARIO QUEMADO | B23012900329 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 12 | 2023-01-29 | 120 | keep | 0 | Jan | 2023 | 8.1731e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-01-29 20:06 | 2023-01-30 08:20 | 5 | 12:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA POR LLUVIAS | A23012900104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 734 | 2023-01-29 | 3670 | keep | 0 | Jan | 2023 | 0.0024996 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-01-29 20:36 | 2023-01-29 20:44 | 20 | 0:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | R23012900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 8 | 2023-01-29 | 160 | keep | 0 | Jan | 2023 | 0.00010898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-29 21:05 | 2023-01-29 21:06 | 2324 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2301290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 2324 | keep | 0 | Jan | 2023 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
CAGUAS | 2023-01-29 21:32 | 2023-01-29 21:33 | 4634 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23012900080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 4634 | keep | 0 | Jan | 2023 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
FAJARDO | 2023-01-29 22:01 | 2023-01-30 00:47 | 90 | 2:46 | P | CONDUCTOR ROTO O ABIERTO | SJ-230130-50 SE LEVANTO CONDUCTOR DEL SUELO | R23012900046 | New_Event | Primary Wire Break | Include | Include | Equipment | 166 | 2023-01-29 | 14940 | keep | 0 | Jan | 2023 | 0.010176 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2023-01-29 22:24 | 2023-01-30 13:12 | 150 | 14:48 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23012900106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 888 | 2023-01-29 | 133200 | keep | 0 | Jan | 2023 | 0.090722 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-01-29 22:29 | 2023-01-29 22:30 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R23012900049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 4085 | keep | 0 | Jan | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CAGUAS | 2023-01-29 23:03 | 2023-01-29 23:04 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23012900084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-29 | 853 | keep | 0 | Jan | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
BAYAMON | 2023-01-29 23:49 | 2023-01-30 02:14 | 100 | 2:25 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | B23012900352 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-01-29 | 14500 | keep | 0 | Jan | 2023 | 0.0098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-01-30 00:24 | 2023-01-30 09:13 | 90 | 8:49 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23013000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 529 | 2023-01-30 | 47610 | keep | 0 | Jan | 2023 | 0.032427 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2023-01-30 00:47 | 2023-01-30 00:48 | 1902 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE RIO GRANDE A FAJARDO | R23013000004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-30 | 1902 | keep | 0 | Jan | 2023 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2023-01-30 00:47 | 2023-01-30 00:48 | 970 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE RIO GRANDE A FAJARDO | R23013000004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-30 | 970 | keep | 0 | Jan | 2023 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2023-01-30 00:47 | 2023-01-30 00:48 | 3003 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE RIO GRANDE A FAJARDO | R23013000004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-30 | 3003 | keep | 0 | Jan | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2023-01-30 00:47 | 2023-01-30 00:48 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE RIO GRANDE A FAJARDO | R23013000003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-30 | 2343 | keep | 0 | Jan | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2023-01-30 00:47 | 2023-01-30 00:48 | 1830 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE RIO GRANDE A FAJARDO | R23013000003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-30 | 1830 | keep | 0 | Jan | 2023 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-01-30 00:47 | 2023-01-30 00:48 | 710 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE RIO GRANDE A FAJARDO | R23013000003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-30 | 710 | keep | 0 | Jan | 2023 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-01-30 00:47 | 2023-01-30 00:48 | 1197 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE RIO GRANDE A FAJARDO | R23013000003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-30 | 1197 | keep | 0 | Jan | 2023 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
FAJARDO | 2023-01-30 00:48 | 2023-01-30 10:01 | 90 | 9:13 | P | CONDUCTOR ROTO O ABIERTO | SJ-230130-50 SE LEVANTO CONDUCTOR DEL SUELO | R23012900046 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 553 | 2023-01-30 | 49770 | keep | 0 | Jan | 2023 | 0.033898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-30 00:49 | 2023-01-30 00:51 | 125 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE BKR SE CERRO POR CONTROL | C2301300000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2023-01-30 | 250 | keep | 0 | Jan | 2023 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-01-30 00:51 | 2023-01-30 06:03 | 31 | 5:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | C23013000005 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 312 | 2023-01-30 | 9672 | keep | 0 | Jan | 2023 | 0.0065876 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
HUMACAO | 2023-01-30 01:25 | 2023-01-30 01:26 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-30 | 2354 | keep | 0 | Jan | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
CANOVANAS | 2023-01-30 01:28 | 2023-01-30 08:42 | 11 | 7:14 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR | R23013000006 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 434 | 2023-01-30 | 4774 | keep | 0 | Jan | 2023 | 0.0032515 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-01-30 01:51 | 2023-01-30 01:52 | 1879 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL LLEVA EL 3006-05 | C23013000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-30 | 1879 | keep | 0 | Jan | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-01-30 01:51 | 2023-01-30 01:52 | 3005 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 3006-02 SE CERRO POR CONTROL LLEVA EL 3006-05 | C23013000007 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-30 | 3005 | keep | 0 | Jan | 2023 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
SAN JUAN | 2023-01-30 02:28 | 2023-01-30 02:31 | 225 | 0:03 | T | ALIMENTADOR AMARRADO | CARGA TRANSFERIDA AL 1303-05 SE CERRO POR CONTROL | S2301300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-01-30 | 675 | keep | 0 | Jan | 2023 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-01-30 02:28 | 2023-01-30 02:31 | 870 | 0:03 | T | NO SE REPORTO CAUSA | LLEVA LA CARGA DEL 1303-04 SE CERRO POR CONTROL | S2301300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-01-30 | 2610 | keep | 0 | Jan | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2023-01-30 02:40 | 2023-01-30 05:16 | 12 | 2:36 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | B23013000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2023-01-30 | 1872 | keep | 0 | Jan | 2023 | 0.001275 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-30 02:53 | 2023-01-30 02:55 | 1061 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23013000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-30 | 2122 | keep | 0 | Jan | 2023 | 0.0014453 | 0.00072264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1061
BARRANQUITAS | 2023-01-30 03:20 | 2023-01-30 07:08 | 110 | 3:48 | P | DESGANCHE | 2 X 50 EN C/L | C23013000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-01-30 | 25080 | keep | 0 | Jan | 2023 | 0.017082 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
PONCE | 2023-01-30 04:34 | 2023-01-30 07:24 | 100 | 2:50 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23013000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-01-30 | 17000 | keep | 0 | Jan | 2023 | 0.011579 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-30 05:16 | 2023-01-30 11:10 | 3 | 5:54 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA NO FUNDIO | S23013000007 | New_Event | Primary Wire Break | Include | Include | Equipment | 354 | 2023-01-30 | 1062 | keep | 0 | Jan | 2023 | 0.00072332 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-01-30 05:51 | 2023-01-30 09:54 | 508 | 4:03 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23013000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-01-30 | 123444 | keep | 0 | Jan | 2023 | 0.084077 | 0.000346 | Sustained | FALSE | FALSE | Not_TMED_Event | 508
GUAYAMA | 2023-01-30 06:00 | 2023-01-30 08:15 | 100 | 2:15 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | P23013000016 | New_Event | Switch Failure | Include | Include | Equipment | 135 | 2023-01-30 | 13500 | keep | 0 | Jan | 2023 | 0.0091948 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-30 06:06 | 2023-01-30 12:32 | 75 | 6:26 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23013000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2023-01-30 | 28950 | keep | 0 | Jan | 2023 | 0.019718 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-01-30 06:12 | 2023-01-30 11:52 | 14 | 5:40 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23013000017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2023-01-30 | 4760 | keep | 0 | Jan | 2023 | 0.003242 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-01-30 06:44 | 2023-01-30 11:25 | 133 | 4:41 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO MEDIANTE SJ-230130-02 | S23013000011 | New_Event | Primary Wire Break | Include | Include | Equipment | 281 | 2023-01-30 | 37373 | keep | 0 | Jan | 2023 | 0.025455 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
CANOVANAS | 2023-01-30 06:45 | 2023-01-30 08:40 | 8 | 1:55 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR CRUCE X AVE | R23013000015 | New_Event | Animals | Include | Include | Wildlife | 115 | 2023-01-30 | 920 | keep | 0 | Jan | 2023 | 0.00062661 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-01-30 06:48 | 2023-01-30 11:20 | 80 | 4:32 | P | ANIMAL | 1 X 100 Y 1 X 50 EN CORTES DE LINEA DISTINTOS AVE CRUZO LINEAS | M23013000003 | New_Event | Animals | Include | Include | Wildlife | 272 | 2023-01-30 | 21760 | keep | 0 | Jan | 2023 | 0.014821 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-01-30 07:07 | 2023-01-30 08:05 | 2 | 0:58 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A23013000007 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-01-30 | 116 | keep | 0 | Jan | 2023 | 7.9007e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-01-30 07:17 | 2023-01-30 08:55 | 1 | 1:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN CORTE DE LINEA LLUVIA Y VIENTO | A23013000007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 98 | 2023-01-30 | 98 | keep | 0 | Jan | 2023 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-30 07:36 | 2023-01-30 12:39 | 1 | 5:03 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23013000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2023-01-30 | 303 | keep | 0 | Jan | 2023 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-30 07:49 | 2023-01-30 12:00 | 240 | 4:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C23013000017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2023-01-30 | 60240 | keep | 0 | Jan | 2023 | 0.041029 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
VEGA BAJA | 2023-01-30 07:56 | 2023-01-30 11:10 | 70 | 3:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23013000014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-01-30 | 13580 | keep | 0 | Jan | 2023 | 0.0092493 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2023-01-30 08:00 | 2023-01-30 08:20 | 17 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR NEUTRAL EN BAJANTE SECUNDARIO | C23013000020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-01-30 | 340 | keep | 0 | Jan | 2023 | 0.00023157 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
GUAYAMA | 2023-01-30 08:00 | 2023-01-30 17:32 | 1 | 9:32 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR ANIMA | P23013000034 | New_Event | Animals | Include | Include | Wildlife | 572 | 2023-01-30 | 572 | keep | 0 | Jan | 2023 | 0.00038959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-01-30 08:04 | 2023-01-30 11:00 | 30 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS | P23013000036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2023-01-30 | 5280 | keep | 0 | Jan | 2023 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-01-30 08:47 | 2023-01-30 11:55 | 1 | 3:08 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23013000024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-01-30 | 188 | keep | 0 | Jan | 2023 | 0.00012805 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-30 08:49 | 2023-01-30 12:40 | 35 | 3:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M23013000016 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2023-01-30 | 8085 | keep | 0 | Jan | 2023 | 0.0055067 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-01-30 08:57 | 2023-01-30 23:15 | 30 | 14:18 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 25 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO | M23013000020 | New_Event | Primary Pole Failure | Include | Include | Equipment | 858 | 2023-01-30 | 25740 | keep | 0 | Jan | 2023 | 0.017531 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-30 09:05 | 2023-01-30 11:25 | 1 | 2:20 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN TRANSFORMADOR. BASE DE CONTADOR DE CLIENTE SULFATADA. | R23013000039 | New_Event | Customer-Related Interruption | Include | Include | Public | 140 | 2023-01-30 | 140 | keep | 0 | Jan | 2023 | 9.5353e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-30 09:13 | 2023-01-30 11:02 | 15 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23013000032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2023-01-30 | 1635 | keep | 0 | Jan | 2023 | 0.0011136 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-30 09:15 | 2023-01-30 14:54 | 30 | 5:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIA EVENTO PERTENECE A SJ | C23013000036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 339 | 2023-01-30 | 10170 | keep | 0 | Jan | 2023 | 0.0069267 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-30 09:18 | 2023-01-30 10:15 | 1 | 0:57 | P | ANIMAL | 1 X 40 RN RISER CRUCE X AVE | B23013000047 | New_Event | Animals | Include | Include | Wildlife | 57 | 2023-01-30 | 57 | keep | 0 | Jan | 2023 | 3.8822e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-30 09:22 | 2023-01-30 14:58 | 10 | 5:36 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REALIZO DESGANCHE SECUNDARIO NO FUNDIO | S23013000033 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 336 | 2023-01-30 | 3360 | keep | 0 | Jan | 2023 | 0.0022885 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-01-30 09:38 | 2023-01-30 18:00 | 30 | 8:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CL SE REMPLAZO CAJA PRIMARIA EN CL | M23013000029 | New_Event | Cutout Failure | Include | Include | Equipment | 502 | 2023-01-30 | 15060 | keep | 0 | Jan | 2023 | 0.010257 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-01-30 09:48 | 2023-01-30 14:08 | 20 | 4:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR POR UNO DE 37.5KVA 1 X 10 EN TRANSFORMADOR | R23013000044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 260 | 2023-01-30 | 5200 | keep | 0 | Jan | 2023 | 0.0035417 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2023-01-30 09:57 | 2023-01-30 11:20 | 8 | 1:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO SULFATADO | R23013000021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 83 | 2023-01-30 | 664 | keep | 0 | Jan | 2023 | 0.00045225 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-01-30 10:30 | 2023-01-30 14:00 | 7 | 3:30 | P | DESGANCHE | DESGANCHE 1 X 40 EN C/L | C23013000050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-01-30 | 1470 | keep | 0 | Jan | 2023 | 0.0010012 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-01-30 10:33 | 2023-01-30 13:07 | 8 | 2:34 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CULEBRA CRUZO LINEAS | A23013000065 | New_Event | Animals | Include | Include | Wildlife | 154 | 2023-01-30 | 1232 | keep | 0 | Jan | 2023 | 0.00083911 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-01-30 10:43 | 2023-01-30 13:50 | 50 | 3:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23013000071 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 187 | 2023-01-30 | 9350 | keep | 0 | Jan | 2023 | 0.0063682 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-01-30 10:46 | 2023-01-30 12:08 | 10 | 1:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23013000072 | New_Event | Cutout Failure | Include | Include | Equipment | 82 | 2023-01-30 | 820 | keep | 0 | Jan | 2023 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-01-30 10:48 | 2023-01-30 14:02 | 11 | 3:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE INSTALO CAJA AL XMR SE REEMPLAZO DISCOS Y BAJANTE SECUNDARIO | C23013000053 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2023-01-30 | 2134 | keep | 0 | Jan | 2023 | 0.0014535 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-01-30 10:56 | 2023-01-30 13:12 | 6 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | C23013000056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2023-01-30 | 816 | keep | 0 | Jan | 2023 | 0.00055577 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-01-30 10:56 | 2023-01-30 13:34 | 8 | 2:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23012900073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 158 | 2023-01-30 | 1264 | keep | 0 | Jan | 2023 | 0.0008609 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-01-30 11:20 | 2023-01-30 12:49 | 80 | 1:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 65 EN C/L VIENTOS FUERTES | C23013000060 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 89 | 2023-01-30 | 7120 | keep | 0 | Jan | 2023 | 0.0048494 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-01-30 11:25 | 2023-01-30 14:06 | 1 | 2:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA ABIERTA CRUZADA | B23013000074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 161 | 2023-01-30 | 161 | keep | 0 | Jan | 2023 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-30 11:25 | 2023-01-30 17:25 | 8 | 6:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23013000053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2023-01-30 | 2880 | keep | 0 | Jan | 2023 | 0.0019616 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-01-30 11:47 | 2023-01-30 17:26 | 100 | 5:39 | P | ANIMAL | 1X80 EN C/L CRUCE POR AVE | B23013000077 | New_Event | Animals | Include | Include | Wildlife | 339 | 2023-01-30 | 33900 | keep | 0 | Jan | 2023 | 0.023089 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-01-30 11:49 | 2023-01-30 14:00 | 1 | 2:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23013000057 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 131 | 2023-01-30 | 131 | keep | 0 | Jan | 2023 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-01-30 11:50 | 2023-01-30 13:51 | 100 | 2:01 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23013000065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-01-30 | 12100 | keep | 0 | Jan | 2023 | 0.0082413 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-30 11:58 | 2023-01-30 13:39 | 100 | 1:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | B23013000079 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2023-01-30 | 10100 | keep | 0 | Jan | 2023 | 0.0068791 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-01-30 12:04 | 2023-01-30 15:05 | 60 | 3:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CL FUERTES VIENTOS | M23013000063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 181 | 2023-01-30 | 10860 | keep | 0 | Jan | 2023 | 0.0073967 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2023-01-30 12:07 | 2023-01-30 13:06 | 2571 | 0:59 | S | LINEA DE TRANSMISION 38KV | SE REPARO TERMINACION EN RISER | P23013000159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2023-01-30 | 151689 | keep | 0 | Jan | 2023 | 0.10331 | 0.0017511 | Sustained | FALSE | FALSE | Not_TMED_Event | 2571
GUAYAMA | 2023-01-30 12:07 | 2023-01-30 13:06 | 2235 | 0:59 | S | LINEA DE TRANSMISION 38KV | SE REPARO TERMINACION EN RISER | P23013000159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2023-01-30 | 131865 | keep | 0 | Jan | 2023 | 0.089813 | 0.0015222 | Sustained | FALSE | FALSE | Not_TMED_Event | 2235
GUAYAMA | 2023-01-30 12:07 | 2023-01-30 13:06 | 713 | 0:59 | S | LINEA DE TRANSMISION 38KV | SE REPARO TERMINACION EN RISER | P23013000159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2023-01-30 | 42067 | keep | 0 | Jan | 2023 | 0.028652 | 0.00048562 | Sustained | FALSE | FALSE | Not_TMED_Event | 713
GUAYAMA | 2023-01-30 12:07 | 2023-01-30 13:06 | 1067 | 0:59 | S | LINEA DE TRANSMISION 38KV | SE REPARO TERMINACION EN RISER | P23013000159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2023-01-30 | 62953 | keep | 0 | Jan | 2023 | 0.042877 | 0.00072673 | Sustained | FALSE | FALSE | Not_TMED_Event | 1067
GUAYAMA | 2023-01-30 12:07 | 2023-01-30 13:06 | 1293 | 0:59 | S | LINEA DE TRANSMISION 38KV | SE REPARO TERMINACION EN RISER | P23013000160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2023-01-30 | 76287 | keep | 0 | Jan | 2023 | 0.051959 | 0.00088066 | Sustained | FALSE | FALSE | Not_TMED_Event | 1293
GUAYAMA | 2023-01-30 12:07 | 2023-01-30 13:06 | 426 | 0:59 | S | LINEA DE TRANSMISION 38KV | SE REPARO TERMINACION EN RISER | P23013000160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2023-01-30 | 25134 | keep | 0 | Jan | 2023 | 0.017119 | 0.00029015 | Sustained | FALSE | FALSE | Not_TMED_Event | 426
GUAYAMA | 2023-01-30 12:07 | 2023-01-30 13:06 | 907 | 0:59 | S | LINEA DE TRANSMISION 38KV | SE REPARO TERMINACION EN RISER | P23013000160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2023-01-30 | 53513 | keep | 0 | Jan | 2023 | 0.036447 | 0.00061775 | Sustained | FALSE | FALSE | Not_TMED_Event | 907
CANOVANAS | 2023-01-30 12:11 | 2023-01-30 17:01 | 1 | 4:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA MAL TIEMPO | R23013000053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 290 | 2023-01-30 | 290 | keep | 0 | Jan | 2023 | 0.00019752 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-30 12:11 | 2023-01-30 17:15 | 20 | 5:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REEMPLAZO CAJA | C23013000066 | New_Event | Cutout Failure | Include | Include | Equipment | 304 | 2023-01-30 | 6080 | keep | 0 | Jan | 2023 | 0.0041411 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-01-30 12:16 | 2023-01-30 12:18 | 1501 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL EN SERVICIO | B23013000082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-01-30 | 3002 | keep | 0 | Jan | 2023 | 0.0020446 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
CANOVANAS | 2023-01-30 12:18 | 2023-01-30 14:28 | 5 | 2:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARRA SECUNDARIA AVERIADA | R23013000054 | New_Event | Secondary Wire Break | Include | Include | Equipment | 130 | 2023-01-30 | 650 | keep | 0 | Jan | 2023 | 0.00044271 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-01-30 12:21 | 2023-01-30 14:48 | 7 | 2:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23013000067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 147 | 2023-01-30 | 1029 | keep | 0 | Jan | 2023 | 0.00070085 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-01-30 12:31 | 2023-01-30 17:07 | 70 | 4:36 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23013000070 | New_Event | Animals | Include | Include | Wildlife | 276 | 2023-01-30 | 19320 | keep | 0 | Jan | 2023 | 0.013159 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-01-30 12:47 | 2023-01-30 16:18 | 1 | 3:31 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR ANIMAL | P23013000174 | New_Event | Animals | Include | Include | Wildlife | 211 | 2023-01-30 | 211 | keep | 0 | Jan | 2023 | 0.00014371 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-30 13:02 | 2023-01-30 15:35 | 15 | 2:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M23013000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-01-30 | 2295 | keep | 0 | Jan | 2023 | 0.0015631 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-01-30 13:06 | 2023-01-30 18:45 | 10 | 5:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23013000072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 339 | 2023-01-30 | 3390 | keep | 0 | Jan | 2023 | 0.0023089 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-01-30 13:10 | 2023-01-30 13:44 | 10 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BARRA EN PEDESTAL | P23013000184 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-01-30 | 340 | keep | 0 | Jan | 2023 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-01-30 13:14 | 2023-01-30 14:27 | 33 | 1:13 | P | SECUNDARIA/DESGANCHE | 1 X 20 Y 1 X 25 EN TRANSFORMADORES | R23013000066 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 73 | 2023-01-30 | 2409 | keep | 0 | Jan | 2023 | 0.0016408 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
HUMACAO | 2023-01-30 13:18 | 2023-01-30 15:14 | 1 | 1:56 | P | ANIMAL | 1 X 100 EN RISER Y 1 SMU 20 DE 80A CRUCE X AVE | C23013000084 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-01-30 | 116 | keep | 0 | Jan | 2023 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-30 13:30 | 2023-01-30 15:00 | 68 | 1:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR PRIMARIO | S23013000075 | New_Event | Primary Wire Break | Include | Include | Equipment | 90 | 2023-01-30 | 6120 | keep | 0 | Jan | 2023 | 0.0041683 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
HUMACAO | 2023-01-30 13:32 | 2023-01-30 14:50 | 1 | 1:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C23013000090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-01-30 | 78 | keep | 0 | Jan | 2023 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-01-30 13:33 | 2023-01-30 14:54 | 100 | 1:21 | P | CAUSAS EXTERNAS | 2X50 EN C/L SE RETIRO CARPA PLASTICA DEL 13KV | B23013000097 | New_Event | Damage From Public | Include | Include | Public | 81 | 2023-01-30 | 8100 | keep | 0 | Jan | 2023 | 0.0055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-01-30 13:34 | 2023-01-30 16:40 | 249 | 3:06 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CAJA PRIMARIA PARA CERRAR PUENTE | S23013000078 | New_Event | Primary Wire Break | Include | Include | Equipment | 186 | 2023-01-30 | 46314 | keep | 0 | Jan | 2023 | 0.031544 | 0.00016959 | Sustained | FALSE | FALSE | Not_TMED_Event | 249
CANOVANAS | 2023-01-30 13:51 | 2023-01-30 16:59 | 70 | 3:08 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23013000069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-01-30 | 13160 | keep | 0 | Jan | 2023 | 0.0089632 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-01-30 14:32 | 2023-01-30 16:15 | 150 | 1:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23013000086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-01-30 | 15450 | keep | 0 | Jan | 2023 | 0.010523 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-01-30 14:45 | 2023-01-30 16:37 | 60 | 1:52 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE X AVE | R23013000075 | New_Event | Animals | Include | Include | Wildlife | 112 | 2023-01-30 | 6720 | keep | 0 | Jan | 2023 | 0.004577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-01-30 14:45 | 2023-01-30 14:46 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2301300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-30 | 2234 | keep | 0 | Jan | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
CAGUAS | 2023-01-30 14:53 | 2023-01-30 17:06 | 102 | 2:13 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23013000109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-01-30 | 13566 | keep | 0 | Jan | 2023 | 0.0092397 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
BAYAMON | 2023-01-30 14:59 | 2023-01-30 15:09 | 8 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO TRAMO SECUNDARIO APROX. 100' | B23013000115 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-01-30 | 80 | keep | 0 | Jan | 2023 | 5.4488e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-01-30 15:13 | 2023-01-30 16:55 | 6 | 1:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23013000115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2023-01-30 | 612 | keep | 0 | Jan | 2023 | 0.00041683 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-01-30 15:20 | 2023-01-30 15:31 | 1 | 0:11 | P | NO SE REPORTO CAUSA | SE CERRO CAJA DEL XMR | C23013000121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2023-01-30 | 11 | keep | 0 | Jan | 2023 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-30 15:40 | 2023-01-30 15:45 | 316 | 0:05 | T | CABLE SOTERRADO AVERIADO | DISPARO CERRADO POR CONTROL LLEVA 25% DEL 1119-04 LLEVA 25% DEL 1119-02 | S2301300000X | New_Event | UG Cable Fault | Include | Include | Equipment | 5 | 2023-01-30 | 1580 | keep | 0 | Jan | 2023 | 0.0010761 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
SAN JUAN | 2023-01-30 15:40 | 2023-01-30 15:45 | 215 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1117-09 CERRADO POR CONTROL 25% POR 1117-09 | S2301300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-01-30 | 1075 | keep | 0 | Jan | 2023 | 0.00073218 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-01-30 15:40 | 2023-01-30 15:45 | 680 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO 25% POR 1117-09 | S2301300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-01-30 | 3400 | keep | 0 | Jan | 2023 | 0.0023157 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
BAYAMON | 2023-01-30 16:02 | 2023-01-30 16:39 | 15 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR LAS (2) BARRAS EN PEDESTAL RECTANGULAR | B23013000132 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-01-30 | 555 | keep | 0 | Jan | 2023 | 0.00037801 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-01-30 16:07 | 2023-01-30 18:56 | 22 | 2:49 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | S23013000114 | New_Event | Animals | Include | Include | Wildlife | 169 | 2023-01-30 | 3718 | keep | 0 | Jan | 2023 | 0.0025323 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
PONCE | 2023-01-30 16:16 | 2023-01-30 16:17 | 5063 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23013000220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-30 | 5063 | keep | 0 | Jan | 2023 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
PONCE | 2023-01-30 16:17 | 2023-01-30 18:39 | 30 | 2:22 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA 1 X 20 EN TRANSFORMADOR ANIMAL | P23013000222 | New_Event | Animals | Include | Include | Wildlife | 142 | 2023-01-30 | 4260 | keep | 0 | Jan | 2023 | 0.0029015 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-30 16:20 | 2023-01-30 20:37 | 1 | 4:17 | P | DESGANCHE | 1 X 80 C/L Y DESGANCHE | S23013000116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2023-01-30 | 257 | keep | 0 | Jan | 2023 | 0.00017504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-30 16:40 | 2023-01-30 17:30 | 400 | 0:50 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE CAJA A LINEA | S23013000078 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 50 | 2023-01-30 | 20000 | keep | 0 | Jan | 2023 | 0.013622 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-30 16:40 | 2023-01-30 19:25 | 30 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 1 X 65 EN C/L LLUVIA MAL TIEMPO | C23013000142 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-01-30 | 4950 | keep | 0 | Jan | 2023 | 0.0033714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-01-30 17:01 | 2023-01-30 17:45 | 30 | 0:44 | P | DESGANCHE | 1 X 65 C/L Y DESGANCHE | S23013000126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2023-01-30 | 1320 | keep | 0 | Jan | 2023 | 0.00089905 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-01-30 17:08 | 2023-01-30 18:42 | 50 | 1:34 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | P23013000228 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-01-30 | 4700 | keep | 0 | Jan | 2023 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-01-30 17:13 | 2023-01-30 19:17 | 16 | 2:04 | P | TRANSFORMADOR AVERIADO | 1X10 EN XMR SE REFIERE PARA CAMBIO DE TRANSFORMADOR | B23013000145 | New_Event | Service Transformer Failure | Include | Include | Equipment | 124 | 2023-01-30 | 1984 | keep | 0 | Jan | 2023 | 0.0013513 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-01-30 17:13 | 2023-01-30 20:30 | 25 | 3:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23013000108 | New_Event | Primary Wire Break | Include | Include | Equipment | 197 | 2023-01-30 | 4925 | keep | 0 | Jan | 2023 | 0.0033544 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-01-30 17:35 | 2023-01-30 18:47 | 1 | 1:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA DE RISER | P23013000231 | New_Event | Primary Wire Break | Include | Include | Equipment | 72 | 2023-01-30 | 72 | keep | 0 | Jan | 2023 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-01-30 17:41 | 2023-01-30 19:53 | 6 | 2:12 | P | DESGANCHE | 1 X 30 EN TRANSFORMADOR POR DESGANCHE | P23013000233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-01-30 | 792 | keep | 0 | Jan | 2023 | 0.00053943 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-01-30 17:50 | 2023-01-30 19:31 | 10 | 1:41 | P | DESGANCHE | SE DESGANCHO Y SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO NO FUNDIO | B23013000151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-01-30 | 1010 | keep | 0 | Jan | 2023 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-01-30 17:51 | 2023-01-30 18:32 | 7 | 0:41 | P | ANIMAL | 2 X 8 EN TRANSFORMADOR IGUANA CRUZO LINEAS | A23013000027 | New_Event | Animals | Include | Include | Wildlife | 41 | 2023-01-30 | 287 | keep | 0 | Jan | 2023 | 0.00019547 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-01-30 18:48 | 2023-01-30 21:54 | 14 | 3:06 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | S23013000137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2023-01-30 | 2604 | keep | 0 | Jan | 2023 | 0.0017736 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2023-01-30 18:50 | 2023-01-30 21:20 | 100 | 2:30 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23013000159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-01-30 | 15000 | keep | 0 | Jan | 2023 | 0.010216 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-30 19:17 | 2023-01-31 13:02 | 9 | 17:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50KVA X 50KVA 122/244V | B23013000145 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1065 | 2023-01-30 | 9585 | keep | 0 | Jan | 2023 | 0.0065283 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-30 19:33 | 2023-01-30 19:34 | 316 | 0:01 | T | CABLE SOTERRADO AVERIADO | PROBO MALO DE RISER A MH7 DISPARO CERRADO POR CONTROL LLEVA 25% DEL 1119-04 LLEVA 25% DEL 1119-02 | S23013000107 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1 | 2023-01-30 | 316 | keep | 0 | Jan | 2023 | 0.00021523 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-30 19:33 | 2023-01-30 19:34 | 215 | 0:01 | P | ALIMENTADOR AMARRADO | PROBO MALO DE RISER A MH7 DISPARO DEL 1117-09 CERRADO POR CONTROL 25% POR 1117-09 | S23013000107 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-30 | 215 | keep | 0 | Jan | 2023 | 0.00014644 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-01-30 19:33 | 2023-01-30 19:34 | 680 | 0:01 | P | ALIMENTADOR AMARRADO | PROBO MALO DE RISER A MH7 DISPARO CERRADO POR CONTROL 25% POR 1117-09 | S23013000107 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-30 | 680 | keep | 0 | Jan | 2023 | 0.00046314 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-01-30 20:22 | 2023-01-31 08:10 | 20 | 11:48 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR | C23013000164 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 708 | 2023-01-30 | 14160 | keep | 0 | Jan | 2023 | 0.0096443 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-01-30 20:46 | 2023-01-31 10:50 | 70 | 14:04 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA SE CORRIGIO CONDICION DE TENSOR CRUZANDO CON CAJA PRIMARIA | A23013000138 | New_Event | Damage From Public | Include | Include | Public | 844 | 2023-01-30 | 59080 | keep | 0 | Jan | 2023 | 0.040239 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2023-01-30 21:01 | 2023-01-31 09:53 | 40 | 12:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23013000246 | New_Event | Vegetation Contact | Include | Include | Vegetation | 772 | 2023-01-30 | 30880 | keep | 0 | Jan | 2023 | 0.021032 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-01-30 21:02 | 2023-01-31 00:22 | 12 | 3:20 | P | DESGANCHE | 1 X 25 EN C/L Y DESGANCHE | C23013000165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-01-30 | 2400 | keep | 0 | Jan | 2023 | 0.0016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-01-30 21:10 | 2023-01-31 09:20 | 1 | 12:10 | P | DESGANCHE | 2 X 20 EN RISER DESGANCHE | S23013000148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 730 | 2023-01-30 | 730 | keep | 0 | Jan | 2023 | 0.0004972 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-01-30 21:15 | 2023-01-31 05:17 | 18 | 8:02 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE PRIMARIO DE LINEA A CAJA | C23013000166 | New_Event | Primary Wire Break | Include | Include | Equipment | 482 | 2023-01-30 | 8676 | keep | 0 | Jan | 2023 | 0.0059092 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2023-01-30 21:15 | 2023-01-30 21:16 | 113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23013000250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-30 | 113 | keep | 0 | Jan | 2023 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
BARRANQUITAS | 2023-01-30 21:33 | 2023-01-31 08:14 | 50 | 10:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C23013000168 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 641 | 2023-01-30 | 32050 | keep | 0 | Jan | 2023 | 0.021829 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-01-30 23:21 | 2023-01-30 23:22 | 1725 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-30 | 1725 | keep | 0 | Jan | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
BARRANQUITAS | 2023-01-30 23:35 | 2023-01-31 23:11 | 78 | 23:36 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZARON 2 POSTES PRIMARIOS 3 X 50 EN C/L | C23013000171 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1416 | 2023-01-30 | 110448 | keep | 0 | Jan | 2023 | 0.075226 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
VEGA BAJA | 2023-01-30 23:41 | 2023-01-30 23:42 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2301300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-30 | 3332 | keep | 0 | Jan | 2023 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
UTUADO | 2023-01-30 23:58 | 2023-01-31 09:47 | 8 | 9:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CONVERTIDOR LLUVIA Y VIENTO | A23013000147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 589 | 2023-01-30 | 4712 | keep | 0 | Jan | 2023 | 0.0032093 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-01-31 00:35 | 2023-01-31 10:19 | 40 | 9:44 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEAS PRIMARIAS | A23013100001 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 584 | 2023-01-31 | 23360 | keep | 0 | Jan | 2023 | 0.01591 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-01-31 00:55 | 2023-01-31 03:58 | 110 | 3:03 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C23013100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-01-31 | 20130 | keep | 0 | Jan | 2023 | 0.01371 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
HUMACAO | 2023-01-31 02:49 | 2023-01-31 09:17 | 100 | 6:28 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C23013100009 | New_Event | Animals | Include | Include | Wildlife | 388 | 2023-01-31 | 38800 | keep | 0 | Jan | 2023 | 0.026427 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-01-31 04:06 | 2023-01-31 04:07 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2301310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 1702 | keep | 0 | Jan | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BARRANQUITAS | 2023-01-31 04:31 | 2023-01-31 06:31 | 2 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA | C23013100015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2023-01-31 | 240 | keep | 0 | Jan | 2023 | 0.00016346 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-01-31 05:01 | 2023-01-31 05:02 | 1615 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR LLEVA UN 5% DEL 1646-01 SE CERRO POR CONTROL | S2301310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 1615 | keep | 0 | Jan | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-01-31 05:01 | 2023-01-31 05:02 | 300 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1620-05 QUE LLEVA UN 5% DEL 1646-01 SE CERRO POR CONTROL | S2301310000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-31 | 300 | keep | 0 | Jan | 2023 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-01-31 05:18 | 2023-01-31 05:19 | 73 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 9207-08 | B2301310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 73 | keep | 0 | Jan | 2023 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2023-01-31 05:18 | 2023-01-31 05:19 | 1859 | 0:01 | T | ALIMENTADOR AMARRADO | 1718-04 RECERRO Y LLEVA LA CARGA DEL 9207-08 | B2301310000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-01-31 | 1859 | keep | 0 | Jan | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BARRANQUITAS | 2023-01-31 05:19 | 2023-01-31 10:31 | 222 | 5:12 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C23013100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2023-01-31 | 69264 | keep | 0 | Jan | 2023 | 0.047175 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-01-31 05:20 | 2023-01-31 06:34 | 82 | 1:14 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23013100004 | New_Event | Animals | Include | Include | Wildlife | 74 | 2023-01-31 | 6068 | keep | 0 | Jan | 2023 | 0.0041329 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
BAYAMON | 2023-01-31 05:38 | 2023-01-31 10:54 | 80 | 5:16 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN C/L DESGANCHE | B23013100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2023-01-31 | 25280 | keep | 0 | Jan | 2023 | 0.017218 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-01-31 05:41 | 2023-01-31 10:09 | 9 | 4:28 | P | ANIMAL | 1 X 25 EN XMR CRUCE X RATON | R23013100003 | New_Event | Animals | Include | Include | Wildlife | 268 | 2023-01-31 | 2412 | keep | 0 | Jan | 2023 | 0.0016428 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-01-31 06:03 | 2023-01-31 10:05 | 17 | 4:02 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23013100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2023-01-31 | 4114 | keep | 0 | Jan | 2023 | 0.002802 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
YAUCO | 2023-01-31 06:13 | 2023-01-31 08:50 | 150 | 2:37 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23013100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-01-31 | 23550 | keep | 0 | Jan | 2023 | 0.01604 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-01-31 06:21 | 2023-01-31 06:23 | 598 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL CARGA POR EL 3405-03 | C23013100030 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-01-31 | 1196 | keep | 0 | Jan | 2023 | 0.00081459 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2023-01-31 06:21 | 2023-01-31 06:23 | 1001 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 3403-01 | C23013100030 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-01-31 | 2002 | keep | 0 | Jan | 2023 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
BARRANQUITAS | 2023-01-31 06:23 | 2023-01-31 12:52 | 132 | 6:29 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTARON CONDUCTORES DEL SUELO. | C23013100039 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 389 | 2023-01-31 | 51348 | keep | 0 | Jan | 2023 | 0.034973 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
PONCE | 2023-01-31 06:50 | 2023-01-31 09:00 | 349 | 2:10 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 500 DISPARA BREAKER 0510, SE TRANSFIERA 50% DE SU CARGA A 5010-06 Y 50% DE SU CARGA A 5010-03 | P23013100025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2023-01-31 | 45370 | keep | 0 | Jan | 2023 | 0.030901 | 0.0002377 | Sustained | FALSE | FALSE | Not_TMED_Event | 349
PONCE | 2023-01-31 06:50 | 2023-01-31 09:50 | 653 | 3:00 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 500 DISPARA BREAKER 0510, SE TRANSFIERE 50% DE SU CARGA A 5010-06 Y 50%DE SU CARGA 5002-02 | P23013100025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2023-01-31 | 117540 | keep | 0 | Jan | 2023 | 0.080056 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
PONCE | 2023-01-31 06:50 | 2023-01-31 09:48 | 860 | 2:58 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 500 DISPARA BREAKER 0510 SE TRANSFIERE 100% DE SU CARGA A 5010-06 | P23013100025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 178 | 2023-01-31 | 153080 | keep | 0 | Jan | 2023 | 0.10426 | 0.00058574 | Sustained | FALSE | FALSE | Not_TMED_Event | 860
ARECIBO | 2023-01-31 06:56 | 2023-01-31 06:57 | 1 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23013100003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-31 | 1 | keep | 0 | Jan | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-31 06:56 | 2023-01-31 06:57 | 2266 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23013100003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-31 | 2266 | keep | 0 | Jan | 2023 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2023-01-31 06:56 | 2023-01-31 06:57 | 1399 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23013100003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-31 | 1399 | keep | 0 | Jan | 2023 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BARRANQUITAS | 2023-01-31 07:15 | 2023-01-31 11:32 | 25 | 4:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23013100053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2023-01-31 | 6425 | keep | 0 | Jan | 2023 | 0.004376 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-01-31 07:22 | 2023-01-31 10:20 | 55 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | P23013100031 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-01-31 | 9790 | keep | 0 | Jan | 2023 | 0.0066679 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
MAYAGÃœEZ | 2023-01-31 07:30 | 2023-01-31 10:35 | 20 | 3:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23013100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-01-31 | 3700 | keep | 0 | Jan | 2023 | 0.0025201 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-01-31 07:43 | 2023-01-31 11:47 | 135 | 4:04 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23013100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2023-01-31 | 32940 | keep | 0 | Jan | 2023 | 0.022435 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2023-01-31 07:44 | 2023-01-31 12:10 | 65 | 4:26 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23013100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-01-31 | 17290 | keep | 0 | Jan | 2023 | 0.011776 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BARRANQUITAS | 2023-01-31 08:13 | 2023-01-31 13:28 | 60 | 5:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23013100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2023-01-31 | 18900 | keep | 0 | Jan | 2023 | 0.012873 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-01-31 08:16 | 2023-01-31 09:58 | 50 | 1:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M23013100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-01-31 | 5100 | keep | 0 | Jan | 2023 | 0.0034736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-01-31 08:16 | 2023-01-31 10:55 | 10 | 2:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO CONECTORES AVERIADOS | M23013200016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 159 | 2023-01-31 | 1590 | keep | 0 | Jan | 2023 | 0.0010829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-01-31 08:26 | 2023-01-31 10:00 | 157 | 1:34 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | B23013100016 | New_Event | Animals | Include | Include | Wildlife | 94 | 2023-01-31 | 14758 | keep | 0 | Jan | 2023 | 0.010052 | 0.00010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 157
MAYAGÃœEZ | 2023-01-31 08:33 | 2023-01-31 08:50 | 1 | 0:17 | P | ANIMAL | 1 X 20 EN RISER POR PAJARO | M23013100030 | New_Event | Animals | Include | Include | Wildlife | 17 | 2023-01-31 | 17 | keep | 0 | Jan | 2023 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-01-31 08:53 | 2023-01-31 13:20 | 10 | 4:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23013100019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 267 | 2023-01-31 | 2670 | keep | 0 | Jan | 2023 | 0.0018185 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-01-31 09:02 | 2023-01-31 11:07 | 12 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO CONECTORES SECUNDARIO | S23013100021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2023-01-31 | 1500 | keep | 0 | Jan | 2023 | 0.0010216 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-01-31 09:07 | 2023-01-31 10:39 | 100 | 1:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C23013100099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-01-31 | 9200 | keep | 0 | Jan | 2023 | 0.0062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-01-31 09:07 | 2023-01-31 16:28 | 100 | 7:21 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | B23013100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2023-01-31 | 44100 | keep | 0 | Jan | 2023 | 0.030036 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-01-31 09:34 | 2023-01-31 12:41 | 6 | 3:07 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR SE RETIRO ENREDADERA | R23013100017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 187 | 2023-01-31 | 1122 | keep | 0 | Jan | 2023 | 0.00076419 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-01-31 09:49 | 2023-01-31 10:55 | 100 | 1:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23013100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2023-01-31 | 6600 | keep | 0 | Jan | 2023 | 0.0044952 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-01-31 09:54 | 2023-01-31 09:55 | 1 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23013100030 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-31 | 1 | keep | 0 | Jan | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-31 09:54 | 2023-01-31 09:55 | 2266 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23013100030 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-31 | 2266 | keep | 0 | Jan | 2023 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2023-01-31 09:54 | 2023-01-31 09:55 | 1399 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23013100030 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-31 | 1399 | keep | 0 | Jan | 2023 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
ARECIBO | 2023-01-31 10:03 | 2023-01-31 10:04 | 1 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23013100032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-31 | 1 | keep | 0 | Jan | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-31 10:03 | 2023-01-31 10:04 | 2266 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23013100032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-31 | 2266 | keep | 0 | Jan | 2023 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2023-01-31 10:03 | 2023-01-31 10:04 | 1399 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23013100032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-01-31 | 1399 | keep | 0 | Jan | 2023 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
ARECIBO | 2023-01-31 10:06 | 2023-01-31 11:48 | 1 | 1:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINES 2600 SE SECCIONALIZO LA LINEA 2600 Y SE ENERGIZO LA SUBESTACION | A23013100034 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2023-01-31 | 102 | keep | 0 | Jan | 2023 | 6.9472e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-01-31 10:06 | 2023-01-31 11:48 | 2266 | 1:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINES 2600 SE SECCIONALIZO LA LINEA 2600 Y SE ENERGIZO LA SUBESTACION | A23013100034 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2023-01-31 | 231132 | keep | 0 | Jan | 2023 | 0.15742 | 0.0015434 | Sustained | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2023-01-31 10:06 | 2023-01-31 11:48 | 1399 | 1:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINES 2600 SE SECCIONALIZO LA LINEA 2600 Y SE ENERGIZO LA SUBESTACION | A23013100034 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2023-01-31 | 142698 | keep | 0 | Jan | 2023 | 0.097191 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
HUMACAO | 2023-01-31 10:43 | 2023-01-31 12:28 | 2354 | 1:45 | T | TERMINACION SOTERRADA AVERIADA | DISPARO DE BKR SE HICIERON OPERACIONES CON CG-230131-01. ENTRO UN 5% EN SERVICIO | C23013100148 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 105 | 2023-01-31 | 247170 | keep | 0 | Jan | 2023 | 0.16835 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
CAGUAS | 2023-01-31 10:52 | 2023-01-31 13:21 | 100 | 2:29 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23013100151 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-01-31 | 14900 | keep | 0 | Jan | 2023 | 0.010148 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-01-31 10:57 | 2023-01-31 17:10 | 30 | 6:13 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 100 EN CL SE RETEZO NEUTRAL PRIMARIO | A23013100054 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 373 | 2023-01-31 | 11190 | keep | 0 | Jan | 2023 | 0.0076215 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-01-31 11:11 | 2023-01-31 12:25 | 20 | 1:14 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23013100038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-01-31 | 1480 | keep | 0 | Jan | 2023 | 0.001008 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-01-31 11:30 | 2023-01-31 11:39 | 6 | 0:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A23013100071 | New_Event | Secondary Wire Break | Include | Include | Equipment | 9 | 2023-01-31 | 54 | keep | 0 | Jan | 2023 | 3.6779e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-01-31 11:39 | 2023-01-31 13:15 | 1527 | 1:36 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE PATRULLO SOLO SE REPORTA FUERTE VIENTO EN EL AREA SE CERRO EL INTERRUPTOR | A23013100076 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2023-01-31 | 146592 | keep | 0 | Jan | 2023 | 0.099843 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
CANOVANAS | 2023-01-31 11:44 | 2023-01-31 14:05 | 10 | 2:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO DE CAJA PRIMARIA | R23013100029 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2023-01-31 | 1410 | keep | 0 | Jan | 2023 | 0.00096034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-01-31 11:48 | 2023-01-31 18:22 | 30 | 6:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23013100079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2023-01-31 | 11820 | keep | 0 | Jan | 2023 | 0.0080505 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-01-31 11:53 | 2023-01-31 11:54 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S23013100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 2402 | keep | 0 | Jan | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
CAGUAS | 2023-01-31 11:59 | 2023-01-31 14:30 | 22 | 2:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | C23013100182 | New_Event | Secondary Wire Break | Include | Include | Equipment | 151 | 2023-01-31 | 3322 | keep | 0 | Jan | 2023 | 0.0022626 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
UTUADO | 2023-01-31 12:21 | 2023-01-31 17:50 | 150 | 5:29 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA | A23013100098 | New_Event | Primary Wire Break | Include | Include | Equipment | 329 | 2023-01-31 | 49350 | keep | 0 | Jan | 2023 | 0.033612 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-01-31 12:28 | 2023-01-31 15:33 | 10 | 3:05 | P | DESGANCHE | 1 X 10 EN XMR Y 1 X 25 EN CL Y 1 X 40 EN CL DESGANCHE | R23013100038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-01-31 | 1850 | keep | 0 | Jan | 2023 | 0.00126 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-01-31 12:28 | 2023-01-31 13:02 | 2243 | 0:34 | P | TERMINACION SOTERRADA AVERIADA | ABIERTO EN EL PB-E CON CG-230131-01 ENTRO UN 38% EN SERVICIO | C23013100148 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 34 | 2023-01-31 | 76262 | keep | 0 | Jan | 2023 | 0.051942 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-01-31 12:29 | 2023-01-31 12:37 | 2916 | 0:08 | T | LINEA DE TRANSMISION 38KV | SE ABRIO EL INTERRUPTOR SOLICITADO POR VICTOR LOPEZ PARA SECCIONALIZAR FASE ROTA DE LA LINEA 2200 CAIDA SOBRE EL ALIMENTADOR. POSTE LINEA 2200 IMPACTADO POR AUTOMÃ“VIL | A23013100104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-01-31 | 23328 | keep | 0 | Jan | 2023 | 0.015889 | 0.0019861 | Sustained | FALSE | FALSE | Not_TMED_Event | 2916
VEGA BAJA | 2023-01-31 12:37 | 2023-01-31 21:28 | 1640 | 8:51 | P | LINEA DE TRANSMISION 38KV | SE ABRE MACHETES PARA SECCIONALIZAR AVERIA LINEA TRANSMISION SOBRE CIRCUITO ALIMENTADOR 8602-03 POSTE LINEA 2200 IMPACTADO POR AUTOMÃ“VIL | A23013100110 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 531 | 2023-01-31 | 870840 | keep | 0 | Jan | 2023 | 0.59313 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-01-31 12:41 | 2023-01-31 16:25 | 15 | 3:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CAJA PRIMARIA A BUSHING EN TRANSFORMADOR | A23013100108 | New_Event | Primary Wire Break | Include | Include | Equipment | 224 | 2023-01-31 | 3360 | keep | 0 | Jan | 2023 | 0.0022885 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-01-31 13:02 | 2023-01-31 13:05 | 1469 | 0:03 | P | TERMINACION SOTERRADA AVERIADA | ABIERTO EN EL PB-2 PB-3 CON CG-230131-01 ENTRO UN 62% EN SERVICIO | C23013100148 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 3 | 2023-01-31 | 4407 | keep | 0 | Jan | 2023 | 0.0030016 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-31 13:05 | 2023-01-31 13:18 | 2354 | 0:13 | T | TERMINACION SOTERRADA AVERIADA | DISPARO EN OPERACIONES CON CG-230131-01 SE VERIFICO PERSONAL FUERA ENTRO UN 62% EN SERVICIO | C23013100148 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 13 | 2023-01-31 | 30602 | keep | 0 | Jan | 2023 | 0.020843 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
PONCE | 2023-01-31 13:15 | 2023-01-31 14:47 | 50 | 1:32 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P23013100112 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-01-31 | 4600 | keep | 0 | Jan | 2023 | 0.003133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-01-31 13:15 | 2023-01-31 17:35 | 6 | 4:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A23013100071 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 260 | 2023-01-31 | 1560 | keep | 0 | Jan | 2023 | 0.0010625 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-31 13:18 | 2023-01-31 14:55 | 885 | 1:37 | P | TERMINACION SOTERRADA AVERIADA | PERSONAL LOCALIZANDO AVERIA SOTERRADA. CON CG-230131-01 ENTRO UN 67% EN SERVICIO | C23013100148 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 97 | 2023-01-31 | 85845 | keep | 0 | Jan | 2023 | 0.058469 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-01-31 13:19 | 2023-01-31 14:20 | 10 | 1:01 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M23013100095 | New_Event | Animals | Include | Include | Wildlife | 61 | 2023-01-31 | 610 | keep | 0 | Jan | 2023 | 0.00041547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-01-31 13:22 | 2023-01-31 15:03 | 80 | 1:41 | P | DESGANCHE | 2 X 30 Y 2 X 50 EN C/L DESGANCHE | C23013100204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-01-31 | 8080 | keep | 0 | Jan | 2023 | 0.0055033 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-01-31 13:23 | 2023-01-31 16:48 | 6 | 3:25 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR Y SE REPARO PUNETE DE LINEA A CAJA | S23013100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2023-01-31 | 1230 | keep | 0 | Jan | 2023 | 0.00083775 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-01-31 13:28 | 2023-01-31 14:35 | 20 | 1:07 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARA Y SE CERRO PUENTE | A23013100119 | New_Event | Primary Wire Break | Include | Include | Equipment | 67 | 2023-01-31 | 1340 | keep | 0 | Jan | 2023 | 0.00091267 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-01-31 13:35 | 2023-01-31 15:45 | 4 | 2:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE CAJAS EN TRANSFORMADOR PARA REMPLAZAR BARRAS EN PEDESTAL SECUNDARIO | A23013100063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 130 | 2023-01-31 | 520 | keep | 0 | Jan | 2023 | 0.00035417 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-01-31 13:57 | 2023-01-31 16:07 | 70 | 2:10 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CL SE REPARO NEUTRAL PRIMARIO | A23013100126 | New_Event | Primary Wire Break | Include | Include | Equipment | 130 | 2023-01-31 | 9100 | keep | 0 | Jan | 2023 | 0.006198 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-01-31 14:11 | 2023-01-31 17:52 | 12 | 3:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE REPARO SECUNDARIA | R23013100055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 221 | 2023-01-31 | 2652 | keep | 0 | Jan | 2023 | 0.0018063 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-01-31 14:19 | 2023-01-31 16:15 | 8 | 1:56 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23013100103 | New_Event | Primary Wire Break | Include | Include | Equipment | 116 | 2023-01-31 | 928 | keep | 0 | Jan | 2023 | 0.00063206 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-01-31 14:19 | 2023-01-31 17:15 | 40 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23013100131 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2023-01-31 | 7040 | keep | 0 | Jan | 2023 | 0.0047949 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-01-31 14:20 | 2023-01-31 14:45 | 12 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M23013100015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-01-31 | 300 | keep | 0 | Jan | 2023 | 0.00020433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-01-31 14:29 | 2023-01-31 15:42 | 5 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C23013000077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-01-31 | 365 | keep | 0 | Jan | 2023 | 0.0002486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-01-31 14:36 | 2023-01-31 14:42 | 2052 | 0:06 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA 20% DE SU CARGA POR EL 1118-10 | S23013100071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-01-31 | 12312 | keep | 0 | Jan | 2023 | 0.0083856 | 0.0013976 | Sustained | FALSE | FALSE | Not_TMED_Event | 2052
PONCE | 2023-01-31 14:43 | 2023-01-31 14:44 | 349 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO AL CERRAR MACHETES DE AMARRE | P23013100146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 349 | keep | 0 | Jan | 2023 | 0.0002377 | 0.0002377 | Momentary | FALSE | FALSE | Not_TMED_Event | 349
PONCE | 2023-01-31 14:43 | 2023-01-31 14:44 | 948 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE AL CERRAR MACHETES DE AMARRE | P23013100147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 948 | keep | 0 | Jan | 2023 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
BARRANQUITAS | 2023-01-31 14:44 | 2023-01-31 17:35 | 139 | 2:51 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23013100227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-01-31 | 23769 | keep | 0 | Jan | 2023 | 0.016189 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
PONCE | 2023-01-31 14:45 | 2023-01-31 14:46 | 349 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO AL CERRAR MACHETES DE AMARRE | P23012300148 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 349 | keep | 0 | Jan | 2023 | 0.0002377 | 0.0002377 | Momentary | FALSE | FALSE | Not_TMED_Event | 349
PONCE | 2023-01-31 14:45 | 2023-01-31 14:46 | 948 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE AL CERRAR MACHETES DE AMARRE | P23013100149 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 948 | keep | 0 | Jan | 2023 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
HUMACAO | 2023-01-31 14:55 | 2023-01-31 15:00 | 2354 | 0:05 | T | TERMINACION SOTERRADA AVERIADA | PERSONAL LOCALIZANDO AVERIA SOTERRADA DISPARO. OPERACIONES CON CG-230131-01 | C23013100148 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 5 | 2023-01-31 | 11770 | keep | 0 | Jan | 2023 | 0.0080165 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-31 15:00 | 2023-01-31 16:43 | 774 | 1:43 | P | TERMINACION SOTERRADA AVERIADA | PERSONAL LOCALIZANDO AVERIA SOTERRADA. OPERACIONES CON CG-230131-01. ENTRO UN 90% EN SERVICIO | C23013100148 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 103 | 2023-01-31 | 79722 | keep | 0 | Jan | 2023 | 0.054298 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-01-31 15:31 | 2023-01-31 16:45 | 6 | 1:14 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R23013100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-01-31 | 444 | keep | 0 | Jan | 2023 | 0.00030241 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-01-31 15:34 | 2023-01-31 15:47 | 18 | 0:13 | P | CAUSAS EXTERNAS | 1 X 10 EN XMR CLIENTE DESGANCHANDO | C23013100248 | New_Event | Damage From Public | Include | Include | Public | 13 | 2023-01-31 | 234 | keep | 0 | Jan | 2023 | 0.00015938 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2023-01-31 15:55 | 2023-01-31 21:25 | 60 | 5:30 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | B23013100078 | New_Event | Animals | Include | Include | Wildlife | 330 | 2023-01-31 | 19800 | keep | 0 | Jan | 2023 | 0.013486 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-01-31 16:08 | 2023-01-31 17:37 | 100 | 1:29 | P | DESGANCHE | 1 X 80 C/L SE REALIZO DESGANCHE | R23013100067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-01-31 | 8900 | keep | 0 | Jan | 2023 | 0.0060617 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-01-31 16:13 | 2023-01-31 18:57 | 15 | 2:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23013100117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-01-31 | 2460 | keep | 0 | Jan | 2023 | 0.0016755 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-01-31 16:20 | 2023-01-31 18:25 | 40 | 2:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | A23013100161 | New_Event | Primary Wire Break | Include | Include | Equipment | 125 | 2023-01-31 | 5000 | keep | 0 | Jan | 2023 | 0.0034055 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-01-31 16:20 | 2023-01-31 18:10 | 9 | 1:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23013100162 | New_Event | Secondary Wire Break | Include | Include | Equipment | 110 | 2023-01-31 | 990 | keep | 0 | Jan | 2023 | 0.00067428 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-01-31 16:25 | 2023-01-31 21:10 | 5 | 4:45 | P | TRANSFORMADOR AVERIADO | SE SECCIONALIZO AREA PARA REEMPAZAR PM T-06 | S23013100091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 285 | 2023-01-31 | 1425 | keep | 0 | Jan | 2023 | 0.00097056 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-01-31 16:25 | 2023-01-31 17:56 | 20 | 1:31 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23013100085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-01-31 | 1820 | keep | 0 | Jan | 2023 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-01-31 16:30 | 2023-01-31 19:30 | 40 | 3:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23013100165 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 180 | 2023-01-31 | 7200 | keep | 0 | Jan | 2023 | 0.0049039 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-01-31 16:34 | 2023-01-31 17:37 | 25 | 1:03 | P | DESGANCHE | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO Y DESGANCHE SEC | S23013100094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-01-31 | 1575 | keep | 0 | Jan | 2023 | 0.0010727 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-01-31 16:43 | 2023-01-31 16:47 | 2354 | 0:04 | T | TERMINACION SOTERRADA AVERIADA | PERSONAL LOCALIZANDO AVERIA DISPARO.OPERACIONES CON CG-230131-01 | C23013100148 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 4 | 2023-01-31 | 9416 | keep | 0 | Jan | 2023 | 0.0064132 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-01-31 16:47 | 2023-01-31 18:40 | 215 | 1:53 | P | TERMINACION SOTERRADA AVERIADA | TERMINACION SOTERRADA AVERIADA. SE SECCIONALIZO TERMINACION QUEMADA EN SU-CCD-1A. CG-230131-01 ENTRO EL 10%. QUE FALTABA 100% EN SERVICIO | C23013100148 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 113 | 2023-01-31 | 24295 | keep | 0 | Jan | 2023 | 0.016547 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-01-31 16:53 | 2023-01-31 19:57 | 122 | 3:04 | P | DESGANCHE | 2X100 EN C/L DESGANCHE | B23013100088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2023-01-31 | 22448 | keep | 0 | Jan | 2023 | 0.015289 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
BARRANQUITAS | 2023-01-31 17:20 | 2023-01-31 19:00 | 27 | 1:40 | P | DESGANCHE | 1 X 40 EN C/L | C23013100289 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-01-31 | 2700 | keep | 0 | Jan | 2023 | 0.001839 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
GUAYAMA | 2023-01-31 17:32 | 2023-01-31 18:08 | 52 | 0:36 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P23013100158 | New_Event | Animals | Include | Include | Wildlife | 36 | 2023-01-31 | 1872 | keep | 0 | Jan | 2023 | 0.001275 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2023-01-31 17:33 | 2023-01-31 17:34 | 533 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA. | S2301310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 533 | keep | 0 | Jan | 2023 | 0.00036302 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
UTUADO | 2023-01-31 17:33 | 2023-01-31 18:25 | 1 | 0:52 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A23013100175 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 52 | 2023-01-31 | 52 | keep | 0 | Jan | 2023 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-01-31 17:38 | 2023-01-31 18:57 | 100 | 1:19 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | R23013100077 | New_Event | Animals | Include | Include | Wildlife | 79 | 2023-01-31 | 7900 | keep | 0 | Jan | 2023 | 0.0053807 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-01-31 17:43 | 2023-01-31 18:00 | 4 | 0:17 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23013100180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2023-01-31 | 68 | keep | 0 | Jan | 2023 | 4.6314e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-01-31 17:52 | 2023-01-31 18:45 | 17 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SEECUNDARIA | S23013100106 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-01-31 | 901 | keep | 0 | Jan | 2023 | 0.00061367 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BARRANQUITAS | 2023-01-31 17:52 | 2023-02-01 07:22 | 17 | 13:30 | P | TRANSFORMADOR AVERIADO | XMR 25 KVA QUEMADO, PENDIENTE A REMPLAZO.SE REGARON 150 PIES 3/4, HAY QUE REEMPLAZAR XMR, EN SERVICIO LOS CLIENTES | C23013100296 | New_Event | Service Transformer Failure | Include | Include | Equipment | 810 | 2023-01-31 | 13770 | keep | 0 | Jan | 2023 | 0.0093787 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2023-01-31 18:06 | 2023-01-31 20:18 | 270 | 2:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 1 X 50 1 X 65 Y 1 X 80 EN C/LS MAL TIEMPO LLUVIAS | C23013100302 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 132 | 2023-01-31 | 35640 | keep | 0 | Jan | 2023 | 0.024274 | 0.0001839 | Sustained | FALSE | FALSE | Not_TMED_Event | 270
SAN JUAN | 2023-01-31 18:52 | 2023-02-01 18:27 | 52 | 23:35 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO Y DESGANCHE | S23013100113 | New_Event | Primary Wire Break | Include | Include | Equipment | 1415 | 2023-01-31 | 73580 | keep | 0 | Jan | 2023 | 0.050115 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CANOVANAS | 2023-01-31 18:57 | 2023-01-31 20:27 | 15 | 1:30 | P | DESGANCHE | 1 X 40 C/L Y 1 X 15 C/L DESGANCHE | R23013100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-01-31 | 1350 | keep | 0 | Jan | 2023 | 0.00091948 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-01-31 19:07 | 2023-01-31 20:41 | 497 | 1:34 | P | DESGANCHE | 1 X 200 EN C/L DESGANCHE | C23013100326 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-01-31 | 46718 | keep | 0 | Jan | 2023 | 0.031819 | 0.0003385 | Sustained | FALSE | FALSE | Not_TMED_Event | 497
CAGUAS | 2023-01-31 19:07 | 2023-01-31 22:01 | 133 | 2:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIA | C23013100321 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 174 | 2023-01-31 | 23142 | keep | 0 | Jan | 2023 | 0.015762 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
BARRANQUITAS | 2023-01-31 19:12 | 2023-02-01 08:07 | 24 | 12:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | C23013100322 | New_Event | Cutout Failure | Include | Include | Equipment | 775 | 2023-01-31 | 18600 | keep | 0 | Jan | 2023 | 0.012668 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-01-31 19:13 | 2023-01-31 21:08 | 50 | 1:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO NO FUNDIO | S23013100115 | New_Event | Primary Wire Break | Include | Include | Equipment | 115 | 2023-01-31 | 5750 | keep | 0 | Jan | 2023 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-01-31 19:14 | 2023-01-31 21:06 | 80 | 1:52 | P | DESGANCHE | 2 X 80 EN CL DESGANCHE | A23013100188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-01-31 | 8960 | keep | 0 | Jan | 2023 | 0.0061026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-01-31 19:57 | 2023-02-01 12:11 | 50 | 16:14 | P | DESGANCHE | SE REALIZO DESGANCHE SE LEVANTARON CONDUCTORES Y SE CERRO PUENTES PRIMARIOS | B23013100088 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 974 | 2023-01-31 | 48700 | keep | 0 | Jan | 2023 | 0.033169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-01-31 20:03 | 2023-02-01 06:37 | 45 | 10:34 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA PAJARO CRUZO FASE | P23013100178 | New_Event | Animals | Include | Include | Wildlife | 634 | 2023-01-31 | 28530 | keep | 0 | Jan | 2023 | 0.019432 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2023-01-31 20:27 | 2023-01-31 23:33 | 22 | 3:06 | P | TERMINACION SOTERRADA AVERIADA | 1 X 50 Y 1 X 65 EN CL QUEDARON 20 CLIENTES FUERAS APROX. | C23013100365 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 186 | 2023-01-31 | 4092 | keep | 0 | Jan | 2023 | 0.002787 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-01-31 20:36 | 2023-02-01 02:16 | 85 | 5:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN C/L SE REMPLAZO CAJA | S23013100123 | New_Event | Cutout Failure | Include | Include | Equipment | 340 | 2023-01-31 | 28900 | keep | 0 | Jan | 2023 | 0.019684 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
AGUADILLA | 2023-01-31 20:55 | 2023-02-01 11:05 | 1 | 14:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23013100129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 850 | 2023-01-31 | 850 | keep | 0 | Jan | 2023 | 0.00057893 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-01-31 21:23 | 2023-01-31 23:48 | 150 | 2:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23013100133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2023-01-31 | 21750 | keep | 0 | Jan | 2023 | 0.014814 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-01-31 22:06 | 2023-01-31 22:07 | 3597 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECERRO | B2301310000X | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-01-31 | 3597 | keep | 0 | Jan | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-01-31 22:07 | 2023-01-31 23:31 | 650 | 1:24 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L 2 X 80 EN OTRO C/L SE ELIMINO PARARAYO | B23013100133 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 84 | 2023-01-31 | 54600 | keep | 0 | Jan | 2023 | 0.037188 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
AGUADILLA | 2023-01-31 22:20 | 2023-02-01 12:30 | 12 | 14:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON LINEAS SECUNDARIAS Y SE RELOCALIZARON OTRAS LINEAS SECUNDARIAS | A23013100203 | New_Event | Secondary Wire Break | Include | Include | Equipment | 850 | 2023-01-31 | 10200 | keep | 0 | Jan | 2023 | 0.0069472 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-01-31 22:59 | 2023-02-01 09:37 | 40 | 10:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23013100135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 638 | 2023-01-31 | 25520 | keep | 0 | Jan | 2023 | 0.017382 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-01-31 23:16 | 2023-01-31 23:17 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2301310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-01-31 | 5809 | keep | 0 | Jan | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
AGUADILLA | 2023-01-31 23:31 | 2023-02-01 02:04 | 854 | 2:33 | P | REGULADOR DEFECTUOSO O AVERIADO | SE SECCIONALIZO ALIMENTADOR SE CERRO INTERRUPTOR | M23013100152 | New_Event | Regulator Failure | Include | Include | Equipment | 153 | 2023-01-31 | 130662 | keep | 0 | Jan | 2023 | 0.088993 | 0.00058166 | Sustained | FALSE | FALSE | Not_TMED_Event | 854
AGUADILLA | 2023-01-31 23:31 | 2023-02-01 15:40 | 5 | 16:09 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23013100204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 969 | 2023-01-31 | 4845 | keep | 0 | Jan | 2023 | 0.0032999 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-01-31 23:33 | 2023-02-01 14:00 | 32 | 14:27 | P | TERMINACION SOTERRADA AVERIADA | 1 X 30 EN AEREO PROVISIONAL SE REEMPLAZO PISTOLA EN PM | C23013100365 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 867 | 2023-01-31 | 27744 | keep | 0 | Jan | 2023 | 0.018896 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-01 00:45 | 2023-02-01 05:41 | 543 | 4:56 | P | ANIMAL | 3 X 200 EN CORTE DE LINEA SE REEMPLAZO MACHETE QUEMADO EN RISER A CAUSA DE SAPO | C23020100006 | New_Event | Animals | Include | Include | Wildlife | 296 | 2023-02-01 | 160728 | keep | 0 | Feb | 2023 | 0.10947 | 0.00036983 | Sustained | FALSE | FALSE | Not_TMED_Event | 543
SAN JUAN | 2023-02-01 01:00 | 2023-02-01 01:01 | 1225 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1203-01 QUE LLEVA EL 75% 1203-03 | S2302010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 1225 | keep | 0 | Feb | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-02-01 01:00 | 2023-02-01 01:01 | 462 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1203-01 QUE LLEVA EL 75% 1203-03 | S2302010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-01 | 462 | keep | 0 | Feb | 2023 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
CAGUAS | 2023-02-01 01:11 | 2023-02-01 01:12 | 1772 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C23020100011 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-01 | 1772 | keep | 0 | Feb | 2023 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
CAGUAS | 2023-02-01 01:12 | 2023-02-01 07:47 | 11 | 6:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REPLAZO CAJA QUEMADA | C23020100012 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 395 | 2023-02-01 | 4345 | keep | 0 | Feb | 2023 | 0.0029594 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-02-01 01:28 | 2023-02-01 01:29 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R23020100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 1026 | keep | 0 | Feb | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
AGUADILLA | 2023-02-01 02:04 | 2023-02-01 11:25 | 997 | 9:21 | T | ALIMENTADOR AMARRADO | INTERRUPTOR FUERA AMARRADO CON EL 7201-04 | M23013100152 | New_Event | Feeder Load Transferred | Include | Include | Other | 561 | 2023-02-01 | 559317 | keep | 0 | Feb | 2023 | 0.38095 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
SAN JUAN | 2023-02-01 05:03 | 2023-02-01 05:12 | 2966 | 0:09 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 40% DE SU CARGA X 1206-04 | S23020100035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-02-01 | 26694 | keep | 0 | Feb | 2023 | 0.018181 | 0.0020201 | Sustained | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2023-02-01 05:03 | 2023-02-01 05:12 | 8679 | 0:09 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 85% DEL SU CARGA X EL 1206-03 | S23020100035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-02-01 | 78111 | keep | 0 | Feb | 2023 | 0.053201 | 0.0059112 | Sustained | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-02-01 05:03 | 2023-02-01 05:12 | 338 | 0:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S23020100035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-02-01 | 3042 | keep | 0 | Feb | 2023 | 0.0020719 | 0.00023021 | Sustained | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2023-02-01 05:03 | 2023-02-01 05:12 | 733 | 0:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S23020100035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-02-01 | 6597 | keep | 0 | Feb | 2023 | 0.0044932 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2023-02-01 05:03 | 2023-02-01 05:12 | 4133 | 0:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S23020100035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-02-01 | 37197 | keep | 0 | Feb | 2023 | 0.025335 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2023-02-01 05:03 | 2023-02-01 05:12 | 1799 | 0:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S23020100035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-02-01 | 16191 | keep | 0 | Feb | 2023 | 0.011028 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
HUMACAO | 2023-02-01 05:41 | 2023-02-01 05:45 | 2126 | 0:04 | T | ANIMAL | DISPARO DE BKR SE CERRO POR CONTROL PESONAL REALIZANDO OPERCIONES | C23020100031 | Additional_clients | Animals | Include | Include | Wildlife | 4 | 2023-02-01 | 8504 | keep | 0 | Feb | 2023 | 0.005792 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-01 05:45 | 2023-02-01 15:35 | 1091 | 9:50 | P | ANIMAL | 3 X 200 EN CORTE DE LINEA SE REEMPLAZO MACHETE QUEMADO EN RISER A CAUSA DE SAPO | C23020100006 | 1st_after_momentary | Animals | Include | Include | Wildlife | 590 | 2023-02-01 | 643690 | keep | 0 | Feb | 2023 | 0.43841 | 0.00074308 | Sustained | FALSE | FALSE | Not_TMED_Event | 1091
PONCE | 2023-02-01 05:53 | 2023-02-01 08:40 | 155 | 2:47 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P23020100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-02-01 | 25885 | keep | 0 | Feb | 2023 | 0.01763 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
BAYAMON | 2023-02-01 05:54 | 2023-02-01 10:10 | 50 | 4:16 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B23020100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2023-02-01 | 12800 | keep | 0 | Feb | 2023 | 0.008718 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-01 06:00 | 2023-02-01 06:01 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 3070 | keep | 0 | Feb | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-02-01 06:01 | 2023-02-01 09:07 | 67 | 3:06 | P | DESGANCHE | 2 X 80 EN C/L SE REALIZO DESGANCHE | B23020100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-02-01 | 12462 | keep | 0 | Feb | 2023 | 0.0084878 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
CANOVANAS | 2023-02-01 06:01 | 2023-02-01 08:52 | 80 | 2:51 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE X AVE | R23020100005 | New_Event | Animals | Include | Include | Wildlife | 171 | 2023-02-01 | 13680 | keep | 0 | Feb | 2023 | 0.0093174 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-01 06:07 | 2023-02-01 08:36 | 10 | 2:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 5 EN XMR SE REEMPLAZO BAJANTES SECUNDARIOS Y CAJAS PRIMARIAS | B23020100021 | New_Event | Cutout Failure | Include | Include | Equipment | 149 | 2023-02-01 | 1490 | keep | 0 | Feb | 2023 | 0.0010148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-01 06:22 | 2023-02-01 10:38 | 205 | 4:16 | P | DESGANCHE | SE RETIRO RAMA 1 X 50 EN C/L | B23020100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2023-02-01 | 52480 | keep | 0 | Feb | 2023 | 0.035744 | 0.00013962 | Sustained | FALSE | FALSE | Not_TMED_Event | 205
UTUADO | 2023-02-01 06:44 | 2023-02-01 10:10 | 50 | 3:26 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE NECESITA DESGANCHE | A23020100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-02-01 | 10300 | keep | 0 | Feb | 2023 | 0.0070153 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-02-01 06:46 | 2023-02-01 18:00 | 300 | 11:14 | P | DESGANCHE | 2 X 100 EN CL Y 2 X 80 EN CL, SE REPARO LINEA PRIMARIA BAMBUS SOBRE LINEA | M23020100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 674 | 2023-02-01 | 202200 | keep | 0 | Feb | 2023 | 0.13772 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2023-02-01 06:49 | 2023-02-01 11:00 | 6 | 4:11 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR POR LINEA PRIMARIA CRUZADA | A23020100006 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 251 | 2023-02-01 | 1506 | keep | 0 | Feb | 2023 | 0.0010257 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-02-01 06:53 | 2023-02-01 13:25 | 125 | 6:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 50, 1 X 100 EN CORTE DE LINEA | P23020100036 | New_Event | Cutout Failure | Include | Include | Equipment | 392 | 2023-02-01 | 49000 | keep | 0 | Feb | 2023 | 0.033374 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
FAJARDO | 2023-02-01 07:00 | 2023-02-01 08:55 | 1 | 1:55 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR 1 X 40 EN CORTE DE LINEA DESGANCHE BOMBA AAA | R23020100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-02-01 | 115 | keep | 0 | Feb | 2023 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-01 07:00 | 2023-02-01 10:30 | 1 | 3:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA QUEMADA | R23020100020 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2023-02-01 | 210 | keep | 0 | Feb | 2023 | 0.00014303 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-01 07:01 | 2023-02-01 12:48 | 10 | 5:47 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA Y NEUTRAL 1 X 15 EN CORT DE LINEA | R23020100010 | New_Event | Primary Wire Break | Include | Include | Equipment | 347 | 2023-02-01 | 3470 | keep | 0 | Feb | 2023 | 0.0023634 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-01 07:28 | 2023-02-01 07:30 | 64 | 0:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y AISLADOR QUEMADO. | S23020100129 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2023-02-01 | 128 | keep | 0 | Feb | 2023 | 8.718e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2023-02-01 07:30 | 2023-02-01 12:20 | 250 | 4:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO PARA REMPLAZAR CAJA PRIMARIA QUEMADA. SJ-230201-01 LLEVA 20% DE SU CARGA. | S23020100129 | New_Event | Cutout Failure | Include | Include | Equipment | 290 | 2023-02-01 | 72500 | keep | 0 | Feb | 2023 | 0.049379 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-02-01 07:30 | 2023-02-01 12:20 | 1290 | 4:50 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO PORTATIL #8 SE SECCIONALIZO TRAMO PARA REMPLAZAR CAJA PRIMARIA QUEMADA. SJ-230201-01 | S23020100129 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 290 | 2023-02-01 | 374100 | keep | 0 | Feb | 2023 | 0.2548 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BARRANQUITAS | 2023-02-01 07:30 | 2023-02-01 10:52 | 150 | 3:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 Y 1 X 100 EN C/LS SE REMPLAZO AISLADOR ROTO | C23020100070 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 202 | 2023-02-01 | 30300 | keep | 0 | Feb | 2023 | 0.020637 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-02-01 07:31 | 2023-02-01 10:46 | 85 | 3:15 | P | DESGANCHE | 2 X 50 Y 1 X 65 EN C/LS (EVENTO PASO DE PONCE PARA HUMACAO) | P23020100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-02-01 | 16575 | keep | 0 | Feb | 2023 | 0.011289 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2023-02-01 07:32 | 2023-02-01 12:40 | 8 | 5:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A23020100007 | New_Event | Cutout Failure | Include | Include | Equipment | 308 | 2023-02-01 | 2464 | keep | 0 | Feb | 2023 | 0.0016782 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-02-01 07:34 | 2023-02-01 12:51 | 45 | 5:17 | P | DESGANCHE | 1 X 80 EN C/L | C23020100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2023-02-01 | 14265 | keep | 0 | Feb | 2023 | 0.0097158 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2023-02-01 07:37 | 2023-02-01 13:23 | 20 | 5:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE ALIMENTADOR DE UTUADO | P23020100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 346 | 2023-02-01 | 6920 | keep | 0 | Feb | 2023 | 0.0047132 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 295 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100181 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 590 | keep | 0 | Feb | 2023 | 0.00040185 | 0.00020092 | Momentary | FALSE | FALSE | Not_TMED_Event | 295
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 948 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100181 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 1896 | keep | 0 | Feb | 2023 | 0.0012914 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:41 | 218 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2302010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 218 | keep | 0 | Feb | 2023 | 0.00014848 | 0.00014848 | Momentary | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 08:35 | 72 | 0:55 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO 1 Y 2 DE BARRA DE HATO REY TC. 5% DE SU CARGA POR 1404-07 | S23020100291 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 55 | 2023-02-01 | 3960 | keep | 0 | Feb | 2023 | 0.0026971 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 1058 | 0:02 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 HATO REY TC 20% POR EL 1424-08 | S23020100173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 2116 | keep | 0 | Feb | 2023 | 0.0014412 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 1000 | 0:02 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 HATO REY TC 80% DE SU CARGA POR EL 1424-08 | S23020100173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 2000 | keep | 0 | Feb | 2023 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 278 | 0:02 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 HATO REY TC CARGA POR EL 1424-08 | S23020100173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 556 | keep | 0 | Feb | 2023 | 0.00037869 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 1295 | 0:02 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 HATO REY TC CARGA POR EL 1424-08 | S23020100173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 2590 | keep | 0 | Feb | 2023 | 0.001764 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 08:35 | 143 | 0:55 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO 1 Y 2 DE BARRA DE HATO REY TC. | S23020100291 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 55 | 2023-02-01 | 7865 | keep | 0 | Feb | 2023 | 0.0053568 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 08:35 | 1357 | 0:55 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO 1 Y 2 DE BARRA DE HATO REY TC. | S23020100291 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 55 | 2023-02-01 | 74635 | keep | 0 | Feb | 2023 | 0.050834 | 0.00092425 | Sustained | FALSE | FALSE | Not_TMED_Event | 1357
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 08:35 | 328 | 0:55 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO 1 Y 2 DE BARRA DE HATO REY TC. | S23020100291 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 55 | 2023-02-01 | 18040 | keep | 0 | Feb | 2023 | 0.012287 | 0.0002234 | Sustained | FALSE | FALSE | Not_TMED_Event | 328
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 11:46 | 242 | 4:06 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO 1 Y 2 DE BARRA DE HATO REY TC. 20% POR 1401-07 30% POR 1420-04 | S23020100291 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 246 | 2023-02-01 | 59532 | keep | 0 | Feb | 2023 | 0.040547 | 0.00016483 | Sustained | FALSE | FALSE | Not_TMED_Event | 242
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 10:15 | 23 | 2:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC DE | S23020100186 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 155 | 2023-02-01 | 3565 | keep | 0 | Feb | 2023 | 0.0024281 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 10:15 | 530 | 2:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC DE | S23020100186 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 155 | 2023-02-01 | 82150 | keep | 0 | Feb | 2023 | 0.055952 | 0.00036098 | Sustained | FALSE | FALSE | Not_TMED_Event | 530
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 10:15 | 37 | 2:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC DE | S23020100186 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 155 | 2023-02-01 | 5735 | keep | 0 | Feb | 2023 | 0.0039061 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 10:15 | 929 | 2:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC DE | S23020100186 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 155 | 2023-02-01 | 143995 | keep | 0 | Feb | 2023 | 0.098074 | 0.00063274 | Sustained | FALSE | FALSE | Not_TMED_Event | 929
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 10:15 | 21 | 2:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC DE | S23020100186 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 155 | 2023-02-01 | 3255 | keep | 0 | Feb | 2023 | 0.002217 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 849 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100188 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 1698 | keep | 0 | Feb | 2023 | 0.0011565 | 0.00057825 | Momentary | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 893 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100188 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 1786 | keep | 0 | Feb | 2023 | 0.0012164 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 602 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100188 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 1204 | keep | 0 | Feb | 2023 | 0.00082004 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 43 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100188 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 86 | keep | 0 | Feb | 2023 | 5.8574e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 11:46 | 4 | 4:06 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO 1 Y 2 DE BARRA DE HATO REY TC. | S23020100291 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 246 | 2023-02-01 | 984 | keep | 0 | Feb | 2023 | 0.0006702 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 673 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC | S23020100183 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 1346 | keep | 0 | Feb | 2023 | 0.00091675 | 0.00045838 | Momentary | FALSE | FALSE | Not_TMED_Event | 673
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 257 | 0:02 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC 20% DE SU CARGA POR EL 1338-02 | S23020100183 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 514 | keep | 0 | Feb | 2023 | 0.00035008 | 0.00017504 | Momentary | FALSE | FALSE | Not_TMED_Event | 257
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 732 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC | S23020100183 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 1464 | keep | 0 | Feb | 2023 | 0.00099712 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 721 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 1442 | keep | 0 | Feb | 2023 | 0.00098214 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 325 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 650 | keep | 0 | Feb | 2023 | 0.00044271 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 600 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 1200 | keep | 0 | Feb | 2023 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 267 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 534 | keep | 0 | Feb | 2023 | 0.0003637 | 0.00018185 | Momentary | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 621 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC. | S23020100178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 1242 | keep | 0 | Feb | 2023 | 0.00084592 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 2203 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO Y 2 DE HATO REY TC | S23020100173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 4406 | keep | 0 | Feb | 2023 | 0.0030009 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 246 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO Y 2 DE HATO REY TC | S23020100173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 492 | keep | 0 | Feb | 2023 | 0.0003351 | 0.00016755 | Momentary | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 07:42 | 9 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO Y 2 DE HATO REY TC LLEVA LA CARGA DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 LLEVA EL 1401-10 | S23020100173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-02-01 | 18 | keep | 0 | Feb | 2023 | 1.226e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 12:15 | 514 | 4:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC | S23020100169 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 275 | 2023-02-01 | 141350 | keep | 0 | Feb | 2023 | 0.096273 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 12:15 | 681 | 4:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC | S23020100169 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 275 | 2023-02-01 | 187275 | keep | 0 | Feb | 2023 | 0.12755 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 12:15 | 752 | 4:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC | S23020100169 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 275 | 2023-02-01 | 206800 | keep | 0 | Feb | 2023 | 0.14085 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2023-02-01 07:40 | 2023-02-01 12:15 | 68 | 4:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 1 Y 2 DE HATO REY TC | S23020100169 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 275 | 2023-02-01 | 18700 | keep | 0 | Feb | 2023 | 0.012736 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
VEGA BAJA | 2023-02-01 07:42 | 2023-02-01 16:00 | 8 | 8:18 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR AVE CRUZO LINEAS | A23020100008 | New_Event | Animals | Include | Include | Wildlife | 498 | 2023-02-01 | 3984 | keep | 0 | Feb | 2023 | 0.0027135 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-02-01 07:53 | 2023-02-01 10:21 | 122 | 2:28 | P | DESGANCHE | 2 X 80 EN C/L | C23010200095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-02-01 | 18056 | keep | 0 | Feb | 2023 | 0.012298 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
BAYAMON | 2023-02-01 07:56 | 2023-02-01 07:58 | 911 | 0:02 | T | DESGANCHE | DISPARO SE CERRO POR CONTROL. | B23020100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-02-01 | 1822 | keep | 0 | Feb | 2023 | 0.001241 | 0.00062048 | Momentary | FALSE | FALSE | Not_TMED_Event | 911
BAYAMON | 2023-02-01 07:58 | 2023-02-01 10:17 | 75 | 2:19 | P | DESGANCHE | 2 X 50 EN C/L SE REALIZO DESGANCHE | B23020100052 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-02-01 | 10425 | keep | 0 | Feb | 2023 | 0.0071004 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2023-02-01 08:04 | 2023-02-01 10:48 | 46 | 2:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | C23020100101 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 164 | 2023-02-01 | 7544 | keep | 0 | Feb | 2023 | 0.0051382 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
BAYAMON | 2023-02-01 08:06 | 2023-02-01 08:08 | 5191 | 0:02 | T | DESGANCHE | DISPARO SE CERRO POR SCADA. | B2302010000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-02-01 | 10382 | keep | 0 | Feb | 2023 | 0.0070711 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2023-02-01 08:07 | 2023-02-01 09:36 | 181 | 1:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE LLEVO PUENTE PRIMARIO DE LINEA A CAJA EN C/L | B23020100033 | New_Event | Primary Wire Break | Include | Include | Equipment | 89 | 2023-02-01 | 16109 | keep | 0 | Feb | 2023 | 0.010972 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
BAYAMON | 2023-02-01 08:08 | 2023-02-01 08:46 | 1 | 0:38 | P | DESGANCHE | 1 X 25 EN C/L Y 1 X 15 EN XMR DESGANCHE | B23020100059 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 38 | 2023-02-01 | 38 | keep | 0 | Feb | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-01 08:11 | 2023-02-01 14:30 | 1 | 6:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | B23020100119 | New_Event | Cutout Failure | Include | Include | Equipment | 379 | 2023-02-01 | 379 | keep | 0 | Feb | 2023 | 0.00025814 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-01 08:15 | 2023-02-01 11:52 | 30 | 3:37 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23020100108 | New_Event | Animals | Include | Include | Wildlife | 217 | 2023-02-01 | 6510 | keep | 0 | Feb | 2023 | 0.0044339 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-02-01 08:20 | 2023-02-01 09:02 | 200 | 0:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A23020100015 | New_Event | Primary Wire Break | Include | Include | Equipment | 42 | 2023-02-01 | 8400 | keep | 0 | Feb | 2023 | 0.0057212 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-02-01 08:23 | 2023-02-01 09:55 | 40 | 1:32 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23020100047 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-02-01 | 3680 | keep | 0 | Feb | 2023 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-02-01 08:28 | 2023-02-01 08:59 | 20 | 0:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R23020100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2023-02-01 | 620 | keep | 0 | Feb | 2023 | 0.00042228 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-01 08:39 | 2023-02-01 10:11 | 1 | 1:32 | P | ANIMAL | 1 X 65 EN C/L CRUCE X REPTIL | C23020100122 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-02-01 | 92 | keep | 0 | Feb | 2023 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-02-01 08:44 | 2023-02-01 12:43 | 15 | 3:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL FUERTES VIENTOS | M23020100053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 239 | 2023-02-01 | 3585 | keep | 0 | Feb | 2023 | 0.0024417 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-01 08:56 | 2023-02-01 09:56 | 1 | 1:00 | P | NO SE REPORTO CAUSA | 2 X 40 SMU 20 EN TRANSCLOSURE | B23020100064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-02-01 | 60 | keep | 0 | Feb | 2023 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-01 09:03 | 2023-02-01 11:00 | 1648 | 1:57 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE TRANSFIRIO CARGA DEL 2302-3 AL 2302-2 SE CERRO N/O FTE SUBEST. SE PROBO SIN CARGA CON AUXILIARES ABIERTOS 100% EN SERVICIO | R23020100016 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 117 | 2023-02-01 | 192816 | keep | 0 | Feb | 2023 | 0.13133 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-02-01 09:03 | 2023-02-01 11:00 | 931 | 1:57 | P | ALIMENTADOR AMARRADO | SE TRANSFIRIO CARGA DEL 2302-3 AL 2302-2 SE CERRO N/O FTE SUBEST. SE PROBO SIN CARGA CON AUXILIARES ABIERTOS 100% EN SERVICIO PARTE POR 2302-3 SE ENCONTRO BKR. AVERIADO | R23020100016 | New_Event | Feeder Load Transferred | Include | Include | Other | 117 | 2023-02-01 | 108927 | keep | 0 | Feb | 2023 | 0.07419 | 0.0006341 | Sustained | FALSE | FALSE | Not_TMED_Event | 931
YAUCO | 2023-02-01 09:04 | 2023-02-01 12:20 | 118 | 3:16 | P | DESGANCHE | 1 X 50 Y 1 X 25 EN DIFERENTES CORTES DE LINEA POR DESGANCHE | P23020100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-02-01 | 23128 | keep | 0 | Feb | 2023 | 0.015752 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
GUAYAMA | 2023-02-01 09:10 | 2023-02-01 15:05 | 5 | 5:55 | P | DESGANCHE | D2023-2677 SECCIONALIZAR TRAMO DE LINEA PARA REALIZAR DESGANCHE | P23020100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2023-02-01 | 1775 | keep | 0 | Feb | 2023 | 0.0012089 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-02-01 09:11 | 2023-02-01 13:13 | 125 | 4:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23020100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2023-02-01 | 30250 | keep | 0 | Feb | 2023 | 0.020603 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
PONCE | 2023-02-01 09:14 | 2023-02-01 09:15 | 1478 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23020100081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 1478 | keep | 0 | Feb | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
MAYAGÃœEZ | 2023-02-01 09:17 | 2023-02-01 12:45 | 6 | 3:28 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23020100069 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 208 | 2023-02-01 | 1248 | keep | 0 | Feb | 2023 | 0.00085001 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-01 09:26 | 2023-02-01 09:28 | 1483 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL. 30% SU CARGA A TRAVER POR EL 1336-09. | S2302010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-01 | 2966 | keep | 0 | Feb | 2023 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-02-01 09:26 | 2023-02-01 09:28 | 510 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL. 15% SU CARGA A TRAVER POR EL 1336-09. | S2302010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-01 | 1020 | keep | 0 | Feb | 2023 | 0.00069472 | 0.00034736 | Momentary | FALSE | FALSE | Not_TMED_Event | 510
SAN JUAN | 2023-02-01 09:26 | 2023-02-01 09:28 | 312 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL. 5% SU CARGA A TRAVER POR EL 1336-09. | S2302010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-01 | 624 | keep | 0 | Feb | 2023 | 0.000425 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-02-01 09:26 | 2023-02-01 09:28 | 4232 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL. 80% POR EL 1336-09. | S2302010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-01 | 8464 | keep | 0 | Feb | 2023 | 0.0057648 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
SAN JUAN | 2023-02-01 09:26 | 2023-02-01 09:28 | 207 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL. | S2302010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-01 | 414 | keep | 0 | Feb | 2023 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
CANOVANAS | 2023-02-01 09:27 | 2023-02-01 10:21 | 1937 | 0:54 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZARON MANIOBRAS EN TRAMO SOTERRADO SE ABRIO DE SU-24 A SUU-25 SE ENCONTRO SU 2 AVERIADO 8% EN SERVICIO SJ-230201-51 | R23020100022 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 54 | 2023-02-01 | 104598 | keep | 0 | Feb | 2023 | 0.071241 | 0.0013193 | Sustained | FALSE | FALSE | Not_TMED_Event | 1937
VEGA BAJA | 2023-02-01 09:27 | 2023-02-01 13:24 | 15 | 3:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L LLUVIA FUERTE | B23020100070 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 237 | 2023-02-01 | 3555 | keep | 0 | Feb | 2023 | 0.0024213 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-02-01 09:48 | 2023-02-01 13:35 | 10 | 3:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M23020100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-02-01 | 2270 | keep | 0 | Feb | 2023 | 0.0015461 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-02-01 09:55 | 2023-02-01 10:30 | 1 | 0:35 | P | DESGANCHE | SE HIZO DESGANCHE Y SE REGULO VOLTAJE | P23020100091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2023-02-01 | 35 | keep | 0 | Feb | 2023 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-01 09:55 | 2023-02-01 13:40 | 854 | 3:45 | P | REGULADOR DEFECTUOSO O AVERIADO | SE ABRIO MACHETES SE RETIRO REGULADORES VACANTES AVERIADOS SE CERRO CORTE DE LINEA | M23013100152 | New_Event | Regulator Failure | Include | Include | Equipment | 225 | 2023-02-01 | 192150 | keep | 0 | Feb | 2023 | 0.13087 | 0.00058166 | Sustained | FALSE | FALSE | Not_TMED_Event | 854
VEGA BAJA | 2023-02-01 10:07 | 2023-02-01 11:07 | 1464 | 1:00 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SE CONFIRMO PERSONAL FUERA DE LAS LINEAS SE LE HIZO PRUEBA AL INTERRUPTOR Y QUEDO EN SERVICIO SE INFORMA MAL TIEMPO EN LA ZONA | A23020100053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 60 | 2023-02-01 | 87840 | keep | 0 | Feb | 2023 | 0.059827 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
SAN JUAN | 2023-02-01 10:13 | 2023-02-01 18:10 | 7 | 7:57 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO 2 POSTES PRIMARIOS | S23020100405 | New_Event | Primary Pole Failure | Include | Include | Equipment | 477 | 2023-02-01 | 3339 | keep | 0 | Feb | 2023 | 0.0022742 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-02-01 10:19 | 2023-02-01 13:48 | 100 | 3:29 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23020100171 | New_Event | Animals | Include | Include | Wildlife | 209 | 2023-02-01 | 20900 | keep | 0 | Feb | 2023 | 0.014235 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-02-01 10:20 | 2023-02-01 11:26 | 752 | 1:06 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE ENCONTRO INTERRUPTOR AVERIADO SE TRANSFIERE CARGA A 5018-04 | P23020100120 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 66 | 2023-02-01 | 49632 | keep | 0 | Feb | 2023 | 0.033804 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
CANOVANAS | 2023-02-01 10:21 | 2023-02-01 10:34 | 1782 | 0:13 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO TRAMO SOTERRADO SE ABRIO SU-24 A SU-17 Y SE CERRO SU-24 A SU-17 SE ENCONTRO SU-2 AVERIADO SJ-230201-51 10% EN SERVICIO | R23020100022 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 13 | 2023-02-01 | 23166 | keep | 0 | Feb | 2023 | 0.015778 | 0.0012137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1782
VEGA BAJA | 2023-02-01 10:21 | 2023-02-01 10:22 | 4702 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | B23020100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 4702 | keep | 0 | Feb | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
BAYAMON | 2023-02-01 10:27 | 2023-02-01 12:21 | 108 | 1:54 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE Y SE REEMPLAZO CAJA PRIMARIA | B23020100088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-02-01 | 12312 | keep | 0 | Feb | 2023 | 0.0083856 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
CANOVANAS | 2023-02-01 10:33 | 2023-02-01 11:50 | 30 | 1:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R23020100056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-02-01 | 2310 | keep | 0 | Feb | 2023 | 0.0015733 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-02-01 10:34 | 2023-02-01 10:58 | 1743 | 0:24 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO TRAMO SOTERRADO SE ABRE DE SU-1 A SU-11 Y SE CERRO DE SU-16 A SU-17 SE ENCONTRO SU-2 AVERIADO SU 2 AVERIADO SJ-230201-51 80% EN SERVICIO | R23020100022 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 24 | 2023-02-01 | 41832 | keep | 0 | Feb | 2023 | 0.028492 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-01 10:50 | 2023-02-01 14:45 | 100 | 3:55 | P | DESGANCHE | 1 X 20 Y 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23020100071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2023-02-01 | 23500 | keep | 0 | Feb | 2023 | 0.016006 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-02-01 10:50 | 2023-02-01 17:06 | 1 | 6:16 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | B23020100162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 376 | 2023-02-01 | 376 | keep | 0 | Feb | 2023 | 0.00025609 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-01 10:58 | 2023-02-01 11:57 | 387 | 0:59 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIOZ TRAMO SE ABRE DE SU-3 A SU-2 SE ENCONTRO SU 2 AVERIADO SJ-230201-51 90% EN SERVICIO | R23020100022 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 59 | 2023-02-01 | 22833 | keep | 0 | Feb | 2023 | 0.015551 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-01 10:59 | 2023-02-01 12:07 | 17 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE BAJO TAP DEL 3 AL 2 Y SE REPARARON NEUTRALES EN BAJANTE SECUNDARIO | B23020100100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2023-02-01 | 1156 | keep | 0 | Feb | 2023 | 0.00078735 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-02-01 11:00 | 2023-02-01 11:52 | 150 | 0:52 | P | CAUSAS EXTERNAS | 2 X 50 EN C/L CRUCE CON CAMION | B23020100107 | New_Event | Damage From Public | Include | Include | Public | 52 | 2023-02-01 | 7800 | keep | 0 | Feb | 2023 | 0.0053125 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-02-01 11:03 | 2023-02-01 13:18 | 1 | 2:15 | P | DESGANCHE | 2 X 30 EN C/L | C23020100199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-02-01 | 135 | keep | 0 | Feb | 2023 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-01 11:20 | 2023-02-01 11:21 | 1478 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23020100129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 1478 | keep | 0 | Feb | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
BARRANQUITAS | 2023-02-01 11:36 | 2023-02-01 15:52 | 146 | 4:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTO | C23020100214 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 256 | 2023-02-01 | 37376 | keep | 0 | Feb | 2023 | 0.025457 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
PONCE | 2023-02-01 11:48 | 2023-02-01 12:34 | 55 | 0:46 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P23020100138 | New_Event | Animals | Include | Include | Wildlife | 46 | 2023-02-01 | 2530 | keep | 0 | Feb | 2023 | 0.0017232 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CANOVANAS | 2023-02-01 11:57 | 2023-02-01 12:25 | 194 | 0:28 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO TRAMO DE SU-6 A SU-2 Y SE CERRO TRAMO DE SU-5B A SU-5A SE ENCONTRO SU 2 AVERIADO SJ-230201-51 99% EN SERVICIO | R23020100022 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 28 | 2023-02-01 | 5432 | keep | 0 | Feb | 2023 | 0.0036997 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-01 12:20 | 2023-02-01 13:21 | 64 | 1:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y AISLADOR QUEMADO. | S23020100129 | New_Event | Cutout Failure | Include | Include | Equipment | 61 | 2023-02-01 | 3904 | keep | 0 | Feb | 2023 | 0.002659 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
CANOVANAS | 2023-02-01 12:25 | 2023-02-01 18:40 | 20 | 6:15 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZARON 9 MACHETES EN SU-2 100% EN SERVICIO | R23020100022 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 375 | 2023-02-01 | 7500 | keep | 0 | Feb | 2023 | 0.0051082 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-02-01 12:33 | 2023-02-01 17:15 | 20 | 4:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020100153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2023-02-01 | 5640 | keep | 0 | Feb | 2023 | 0.0038414 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-01 12:35 | 2023-02-01 14:15 | 100 | 1:40 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23020100552 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-02-01 | 10000 | keep | 0 | Feb | 2023 | 0.006811 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-02-01 12:35 | 2023-02-01 15:44 | 7 | 3:09 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23020100539 | New_Event | Primary Wire Break | Include | Include | Equipment | 189 | 2023-02-01 | 1323 | keep | 0 | Feb | 2023 | 0.00090109 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-02-01 13:09 | 2023-02-01 13:30 | 25 | 0:21 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | S23020100559 | New_Event | Vegetation Contact | Include | Include | Vegetation | 21 | 2023-02-01 | 525 | keep | 0 | Feb | 2023 | 0.00035758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-01 13:15 | 2023-02-01 14:51 | 10 | 1:36 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23020100564 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2023-02-01 | 960 | keep | 0 | Feb | 2023 | 0.00065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-01 13:15 | 2023-02-01 14:00 | 8 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23020100130 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-02-01 | 360 | keep | 0 | Feb | 2023 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-02-01 13:16 | 2023-02-01 14:25 | 13 | 1:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | R23020100111 | New_Event | Cutout Failure | Include | Include | Equipment | 69 | 2023-02-01 | 897 | keep | 0 | Feb | 2023 | 0.00061094 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-02-01 13:21 | 2023-02-01 14:17 | 1 | 0:56 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23020100121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-02-01 | 56 | keep | 0 | Feb | 2023 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-01 13:23 | 2023-02-01 19:55 | 10 | 6:32 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C23020100242 | New_Event | Animals | Include | Include | Wildlife | 392 | 2023-02-01 | 3920 | keep | 0 | Feb | 2023 | 0.0026699 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-01 13:25 | 2023-02-01 15:35 | 30 | 2:10 | P | NO SE REPORTO CAUSA | 1 X 150 EN SU | S23020100569 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2023-02-01 | 3900 | keep | 0 | Feb | 2023 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-02-01 14:18 | 2023-02-01 14:35 | 3 | 0:17 | P | DESGANCHE | DESGANCHE 2 X 40 EN CORTE DE LINEA | R23020100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2023-02-01 | 51 | keep | 0 | Feb | 2023 | 3.4736e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-02-01 14:21 | 2023-02-01 14:22 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
FAJARDO | 2023-02-01 14:26 | 2023-02-01 15:15 | 40 | 0:49 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE LINEA CAMION CRUZO CABLE DE COMUNICACIIONES | R23020100125 | New_Event | Damage From Public | Include | Include | Public | 49 | 2023-02-01 | 1960 | keep | 0 | Feb | 2023 | 0.0013349 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-02-01 14:26 | 2023-02-01 14:48 | 1 | 0:22 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | P23020100179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2023-02-01 | 22 | keep | 0 | Feb | 2023 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-01 14:32 | 2023-02-01 14:33 | 1725 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C23020100268 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-01 | 1725 | keep | 0 | Feb | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
MAYAGÃœEZ | 2023-02-01 14:50 | 2023-02-01 17:45 | 10 | 2:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23020100199 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 175 | 2023-02-01 | 1750 | keep | 0 | Feb | 2023 | 0.0011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-01 14:55 | 2023-02-01 16:13 | 294 | 1:18 | P | ANIMAL | 1 X 25 EN C/L 2 X 30 EN C/L 1 X 50 EN C/L Y 1 X 65 EN C/L CRUCE X AVE | B23020100143 | New_Event | Animals | Include | Include | Wildlife | 78 | 2023-02-01 | 22932 | keep | 0 | Feb | 2023 | 0.015619 | 0.00020024 | Sustained | FALSE | FALSE | Not_TMED_Event | 294
BARRANQUITAS | 2023-02-01 15:15 | 2023-02-02 11:37 | 4 | 20:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR | C23020100274 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1222 | 2023-02-01 | 4888 | keep | 0 | Feb | 2023 | 0.0033292 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-02-01 15:25 | 2023-02-01 16:50 | 27 | 1:25 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE LEVANTO NEUTRAL PRIMARIO | C23020100192 | New_Event | Primary Wire Break | Include | Include | Equipment | 85 | 2023-02-01 | 2295 | keep | 0 | Feb | 2023 | 0.0015631 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2023-02-01 15:39 | 2023-02-01 16:56 | 70 | 1:17 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R23020100130 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-02-01 | 5390 | keep | 0 | Feb | 2023 | 0.0036711 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-02-01 15:47 | 2023-02-01 16:24 | 8 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | B23020100152 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-02-01 | 296 | keep | 0 | Feb | 2023 | 0.0002016 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-02-01 15:48 | 2023-02-02 09:13 | 10 | 17:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR MAL TIEMPO LLUVIA | C23020100286 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1045 | 2023-02-01 | 10450 | keep | 0 | Feb | 2023 | 0.0071174 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-01 16:09 | 2023-02-01 16:10 | 1725 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C23020100296 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-01 | 1725 | keep | 0 | Feb | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
ARECIBO | 2023-02-01 16:13 | 2023-02-01 17:10 | 5 | 0:57 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23020100138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2023-02-01 | 285 | keep | 0 | Feb | 2023 | 0.00019411 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-02-01 16:15 | 2023-02-01 16:16 | 1725 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C23020100300 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-01 | 1725 | keep | 0 | Feb | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
CAGUAS | 2023-02-01 16:23 | 2023-02-01 16:24 | 1725 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C2302010000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-01 | 1725 | keep | 0 | Feb | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
CAGUAS | 2023-02-01 16:24 | 2023-02-01 19:40 | 773 | 3:16 | P | DESGANCHE | SE SECCIONALIZO CONDUCTOR EN EL SUELO A CAUSA DE DESGANCHE EN SALIDA CARR. 185 HACIA LA SUBESTACION 3202 Y SE CERRO N/O CON EL 3201-03, SE LE INFORMO AL DESPACHO DE SERVICIO Y SE VA A TRABAJAR MAÃ‘ANA CON EL EVENTO C23020100431 QUEDARON 21 CLIENTES FUERA | C23020100355 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-02-01 | 151508 | keep | 0 | Feb | 2023 | 0.10319 | 0.00052649 | Sustained | FALSE | FALSE | Not_TMED_Event | 773
BARRANQUITAS | 2023-02-01 16:25 | 2023-02-01 17:33 | 11 | 1:08 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR | C23020100304 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 68 | 2023-02-01 | 748 | keep | 0 | Feb | 2023 | 0.00050946 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2023-02-01 16:45 | 2023-02-01 17:20 | 10 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23020100119 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-02-01 | 350 | keep | 0 | Feb | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-02-01 17:00 | 2023-02-01 18:38 | 10 | 1:38 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR | P23020100214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2023-02-01 | 980 | keep | 0 | Feb | 2023 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-01 17:02 | 2023-02-01 17:03 | 151 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 151 CLIENTES POR EL 3015-06 EN SERVICIO | C2302010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-01 | 151 | keep | 0 | Feb | 2023 | 0.00010285 | 0.00010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 151
CAGUAS | 2023-02-01 17:02 | 2023-02-01 17:03 | 1342 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA 151 CLIENTES DEL 3006-01 EN SERVICIO | C2302010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 1342 | keep | 0 | Feb | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
BAYAMON | 2023-02-01 17:10 | 2023-02-01 21:30 | 93 | 4:20 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE REEMPLAZO CAJA PRIMARIA Y SE ELIMINO PRARRAYO | B23020100165 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 260 | 2023-02-01 | 24180 | keep | 0 | Feb | 2023 | 0.016469 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
HUMACAO | 2023-02-01 17:13 | 2023-02-01 19:22 | 35 | 2:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BAJANTES SECUNDARIOS QUEMADOS | C23020100331 | New_Event | Secondary Wire Break | Include | Include | Equipment | 129 | 2023-02-01 | 4515 | keep | 0 | Feb | 2023 | 0.0030751 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2023-02-01 17:31 | 2023-02-01 19:50 | 20 | 2:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | A23020100244 | New_Event | Primary Wire Break | Include | Include | Equipment | 139 | 2023-02-01 | 2780 | keep | 0 | Feb | 2023 | 0.0018934 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-01 17:43 | 2023-02-01 21:17 | 67 | 3:34 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO EN EL SUELO, SE SECCIONALIZO TRAMO, SE QUEDARON 3 CLIENTES FUERA | S23020100667 | New_Event | Primary Wire Break | Include | Include | Equipment | 214 | 2023-02-01 | 14338 | keep | 0 | Feb | 2023 | 0.0097655 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-02-01 17:43 | 2023-02-01 19:13 | 62 | 1:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23020100667 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2023-02-01 | 5580 | keep | 0 | Feb | 2023 | 0.0038005 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
HUMACAO | 2023-02-01 17:49 | 2023-02-01 17:51 | 3420 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C2302010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-01 | 6840 | keep | 0 | Feb | 2023 | 0.0046587 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
CANOVANAS | 2023-02-01 17:50 | 2023-02-01 18:25 | 26 | 0:35 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE HIZO DESGANCHE | R23020100147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2023-02-01 | 910 | keep | 0 | Feb | 2023 | 0.0006198 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
ARECIBO | 2023-02-01 17:55 | 2023-02-01 18:05 | 20 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23020100140 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-02-01 | 200 | keep | 0 | Feb | 2023 | 0.00013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-01 17:58 | 2023-02-01 19:16 | 520 | 1:18 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE DE BAMBUA | C23020100354 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-02-01 | 40560 | keep | 0 | Feb | 2023 | 0.027625 | 0.00035417 | Sustained | FALSE | FALSE | Not_TMED_Event | 520
GUAYAMA | 2023-02-01 18:05 | 2023-02-01 19:00 | 5 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPRAR CONEXIONES SECUNDARIAS | P23020100220 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-02-01 | 275 | keep | 0 | Feb | 2023 | 0.0001873 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-02-01 18:19 | 2023-02-02 07:46 | 12 | 13:27 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M23020100250 | New_Event | Animals | Include | Include | Wildlife | 807 | 2023-02-01 | 9684 | keep | 0 | Feb | 2023 | 0.0065957 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-01 18:30 | 2023-02-01 18:33 | 271 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2302010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-01 | 813 | keep | 0 | Feb | 2023 | 0.00055373 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BARRANQUITAS | 2023-02-01 18:43 | 2023-02-01 18:45 | 1 | 0:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 8 EN BANCO DE TRANSFORMADORES MAL TIEMPO LLUVIA | C23020100399 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2023-02-01 | 2 | keep | 0 | Feb | 2023 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-01 18:45 | 2023-02-01 19:15 | 17 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR CONECTOR SECUNDARIO | R23020100148 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-02-01 | 510 | keep | 0 | Feb | 2023 | 0.00034736 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-02-01 18:47 | 2023-02-01 18:49 | 1444 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL SCADA | M23020100256 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-01 | 2888 | keep | 0 | Feb | 2023 | 0.001967 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
BAYAMON | 2023-02-01 18:53 | 2023-02-02 01:03 | 12 | 6:10 | P | DESGANCHE | 2 X 10 EN XMR DESGANCHE PRIMARIO Y SE REPARO SECUNDARIA | S23020100688 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2023-02-01 | 4440 | keep | 0 | Feb | 2023 | 0.0030241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-02-01 18:53 | 2023-02-02 11:46 | 200 | 16:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M2302010257 | New_Event | Cutout Failure | Include | Include | Equipment | 1013 | 2023-02-01 | 202600 | keep | 0 | Feb | 2023 | 0.13799 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2023-02-01 19:00 | 2023-02-01 20:40 | 250 | 1:40 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P23020100231 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-02-01 | 25000 | keep | 0 | Feb | 2023 | 0.017027 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-02-01 19:07 | 2023-02-01 21:00 | 10 | 1:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L Y SE REMPLAZO CAJA PRIMARIA | S23020100696 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2023-02-01 | 1130 | keep | 0 | Feb | 2023 | 0.00076964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-01 19:16 | 2023-02-01 21:58 | 793 | 2:42 | P | DESGANCHE | ABRIR CORTE DE LINEA TOTAL PARA CERRAR PUENTE DE LINEA A LINEA X DESGANCHE | C23020100432 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-02-01 | 128466 | keep | 0 | Feb | 2023 | 0.087498 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-01 19:31 | 2023-02-01 21:37 | 150 | 2:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIA | S23020100069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 126 | 2023-02-01 | 18900 | keep | 0 | Feb | 2023 | 0.012873 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-02-01 19:40 | 2023-02-02 11:30 | 21 | 15:50 | P | DESGANCHE | SE REALIZO DESGANCHE Y LEVANTO CONDUCTOR GOI CG-230202-01 | C23020100431 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 950 | 2023-02-01 | 19950 | keep | 0 | Feb | 2023 | 0.013588 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-01 21:17 | 2023-02-02 10:21 | 3 | 13:04 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO EN EL SUELO. SE ABRE C/L TOTAL PARA QUE PERSONAL TRABAJE CON SEGURIDAD | S23020100667 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 784 | 2023-02-01 | 2352 | keep | 0 | Feb | 2023 | 0.0016019 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-01 21:30 | 2023-02-01 23:01 | 150 | 1:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | A23020100151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-02-01 | 13650 | keep | 0 | Feb | 2023 | 0.009297 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2023-02-01 21:58 | 2023-02-02 07:45 | 52 | 9:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P23020100252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 587 | 2023-02-01 | 30524 | keep | 0 | Feb | 2023 | 0.02079 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
ARECIBO | 2023-02-01 22:00 | 2023-02-02 09:00 | 30 | 11:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CL | A23020100153 | New_Event | Primary Wire Break | Include | Include | Equipment | 660 | 2023-02-01 | 19800 | keep | 0 | Feb | 2023 | 0.013486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-02-01 22:20 | 2023-02-02 08:48 | 50 | 10:28 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23020100465 | New_Event | Animals | Include | Include | Wildlife | 628 | 2023-02-01 | 31400 | keep | 0 | Feb | 2023 | 0.021386 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-01 22:41 | 2023-02-01 22:42 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23020100154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-01 | 4085 | keep | 0 | Feb | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-02-01 22:55 | 2023-02-01 22:56 | 251 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 LLEVA EL 20% DE SU CARGA | S23020100750 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-01 | 251 | keep | 0 | Feb | 2023 | 0.00017095 | 0.00017095 | Momentary | FALSE | FALSE | Not_TMED_Event | 251
SAN JUAN | 2023-02-01 22:55 | 2023-02-01 22:56 | 1290 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S23020100750 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-01 | 1290 | keep | 0 | Feb | 2023 | 0.00087861 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2023-02-01 22:58 | 2023-02-01 23:07 | 716 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | S2302010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-02-01 | 6444 | keep | 0 | Feb | 2023 | 0.004389 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
SAN JUAN | 2023-02-01 23:31 | 2023-02-02 11:59 | 19 | 12:28 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | S23020100754 | New_Event | Vegetation Contact | Include | Include | Vegetation | 748 | 2023-02-01 | 14212 | keep | 0 | Feb | 2023 | 0.0096797 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-02-02 00:50 | 2023-02-02 05:35 | 30 | 4:45 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23020200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2023-02-02 | 8550 | keep | 0 | Feb | 2023 | 0.0058234 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-02-02 01:12 | 2023-02-02 01:13 | 2286 | 0:01 | T | ANIMAL | RECIERRE | R23020200001 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-02 | 2286 | keep | 0 | Feb | 2023 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2023-02-02 01:13 | 2023-02-02 10:23 | 18 | 9:10 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | R23020200012 | 1st_after_momentary | Animals | Include | Include | Wildlife | 550 | 2023-02-02 | 9900 | keep | 0 | Feb | 2023 | 0.0067428 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2023-02-02 01:16 | 2023-02-02 01:17 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23020200003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-02 | 1192 | keep | 0 | Feb | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CAGUAS | 2023-02-02 01:52 | 2023-02-02 07:19 | 50 | 5:27 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23020200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2023-02-02 | 16350 | keep | 0 | Feb | 2023 | 0.011136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-02 01:53 | 2023-02-02 04:37 | 20 | 2:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | B23020200003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 164 | 2023-02-02 | 3280 | keep | 0 | Feb | 2023 | 0.002234 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-02-02 02:09 | 2023-02-02 09:08 | 4 | 6:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23020200002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 419 | 2023-02-02 | 1676 | keep | 0 | Feb | 2023 | 0.0011415 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-02-02 02:39 | 2023-02-02 09:07 | 50 | 6:28 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | R23020200003 | New_Event | Animals | Include | Include | Wildlife | 388 | 2023-02-02 | 19400 | keep | 0 | Feb | 2023 | 0.013213 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-02-02 04:32 | 2023-02-02 09:15 | 50 | 4:43 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M2302020004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 283 | 2023-02-02 | 14150 | keep | 0 | Feb | 2023 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-02-02 04:37 | 2023-02-02 14:20 | 20 | 9:43 | P | TERMINACION SOTERRADA AVERIADA | 1 X 30 EN AEREO PROVISIONAL SE REEMPLAZO PISTOLA EN T-27 | C23020200002 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 583 | 2023-02-02 | 11660 | keep | 0 | Feb | 2023 | 0.0079416 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-02 04:39 | 2023-02-02 08:10 | 20 | 3:31 | P | DESGANCHE | 1 X 50 EN C/L SE RETEZO LINEA Y SE REALIZO DESGANCHE | B23020200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2023-02-02 | 4220 | keep | 0 | Feb | 2023 | 0.0028742 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-02 04:43 | 2023-02-02 07:25 | 25 | 2:42 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23020200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-02-02 | 4050 | keep | 0 | Feb | 2023 | 0.0027584 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-02 05:16 | 2023-02-02 12:31 | 15 | 7:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S23020200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 435 | 2023-02-02 | 6525 | keep | 0 | Feb | 2023 | 0.0044441 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-02 05:43 | 2023-02-02 18:18 | 10 | 12:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23020200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 755 | 2023-02-02 | 7550 | keep | 0 | Feb | 2023 | 0.0051423 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-02-02 05:55 | 2023-02-02 10:30 | 50 | 4:35 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN SALIDA CONVERTIDOR FASE CRUZADA CON NEUTRAL PRIMARIO | A23020200001 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 275 | 2023-02-02 | 13750 | keep | 0 | Feb | 2023 | 0.0093651 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-02-02 06:11 | 2023-02-02 09:53 | 60 | 3:42 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23020200016 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2023-02-02 | 13320 | keep | 0 | Feb | 2023 | 0.0090722 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-02 06:23 | 2023-02-02 10:10 | 252 | 3:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO VIENTOS | S23020200022 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 227 | 2023-02-02 | 57204 | keep | 0 | Feb | 2023 | 0.038961 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
AGUADILLA | 2023-02-02 06:57 | 2023-02-02 12:33 | 226 | 5:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | A23020200003 | New_Event | Cutout Failure | Include | Include | Equipment | 336 | 2023-02-02 | 75936 | keep | 0 | Feb | 2023 | 0.05172 | 0.00015393 | Sustained | FALSE | FALSE | Not_TMED_Event | 226
BARRANQUITAS | 2023-02-02 07:12 | 2023-02-02 15:53 | 7 | 8:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 75 KVA | C23020200006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 521 | 2023-02-02 | 3647 | keep | 0 | Feb | 2023 | 0.002484 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-02-02 07:29 | 2023-02-02 07:30 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R23020200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-02 | 2722 | keep | 0 | Feb | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
BAYAMON | 2023-02-02 07:36 | 2023-02-02 07:37 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-02 | 4431 | keep | 0 | Feb | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
SAN JUAN | 2023-02-02 07:45 | 2023-02-02 11:56 | 81 | 4:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23020200048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 251 | 2023-02-02 | 20331 | keep | 0 | Feb | 2023 | 0.013847 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
MAYAGÃœEZ | 2023-02-02 07:52 | 2023-02-02 16:15 | 15 | 8:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 503 | 2023-02-02 | 7545 | keep | 0 | Feb | 2023 | 0.0051389 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-02-02 07:55 | 2023-02-02 14:58 | 4 | 7:03 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | A23020200013 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 423 | 2023-02-02 | 1692 | keep | 0 | Feb | 2023 | 0.0011524 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-02-02 08:12 | 2023-02-02 14:25 | 30 | 6:13 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23020200023 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 373 | 2023-02-02 | 11190 | keep | 0 | Feb | 2023 | 0.0076215 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-02-02 08:14 | 2023-02-02 11:15 | 80 | 3:01 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE | A23020200016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-02-02 | 14480 | keep | 0 | Feb | 2023 | 0.0098623 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-02-02 08:17 | 2023-02-02 10:15 | 19 | 1:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN XMR Y SE REPARO CONEXIONES SECUNDARIAS | S23020200059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 118 | 2023-02-02 | 2242 | keep | 0 | Feb | 2023 | 0.001527 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-02-02 08:19 | 2023-02-02 14:00 | 8 | 5:41 | P | DESGANCHE | 1 X 65 EN CL Y DESGANCHE | S23020200060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 341 | 2023-02-02 | 2728 | keep | 0 | Feb | 2023 | 0.001858 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-02-02 08:20 | 2023-02-02 13:11 | 40 | 4:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | C23020200016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 291 | 2023-02-02 | 11640 | keep | 0 | Feb | 2023 | 0.007928 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-02-02 08:29 | 2023-02-02 11:13 | 100 | 2:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA Y 1 X 80 AMP | P23020200029 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2023-02-02 | 16400 | keep | 0 | Feb | 2023 | 0.01117 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-02-02 08:48 | 2023-02-02 11:00 | 35 | 2:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | A23020200019 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2023-02-02 | 4620 | keep | 0 | Feb | 2023 | 0.0031467 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-02-02 09:04 | 2023-02-02 15:36 | 10 | 6:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23020200090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 392 | 2023-02-02 | 3920 | keep | 0 | Feb | 2023 | 0.0026699 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-02 09:11 | 2023-02-02 09:13 | 1879 | 0:02 | T | DESGANCHE | DISPARO LLEVA EL 3006-05 | C23020200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-02-02 | 3758 | keep | 0 | Feb | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-02-02 09:11 | 2023-02-02 09:13 | 3005 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DEL 3006-02 QUE LLEVA EL 3006-05 | C23020200026 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-02 | 6010 | keep | 0 | Feb | 2023 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2023-02-02 09:13 | 2023-02-02 11:31 | 40 | 2:18 | P | DESGANCHE | 1 X 65 EN RISER DESGANCHE | C23020200047 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-02-02 | 5520 | keep | 0 | Feb | 2023 | 0.0037596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-02-02 09:13 | 2023-02-02 15:00 | 15 | 5:47 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO CAJA SECA QUEMADA | M23020200046 | New_Event | UG Cable Fault | Include | Include | Equipment | 347 | 2023-02-02 | 5205 | keep | 0 | Feb | 2023 | 0.0035451 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-02-02 09:14 | 2023-02-02 09:35 | 17 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO BARRA EN PEDESTAL | R23020200018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2023-02-02 | 357 | keep | 0 | Feb | 2023 | 0.00024315 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2023-02-02 09:16 | 2023-02-02 09:17 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23020200028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-02 | 1307 | keep | 0 | Feb | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
SAN JUAN | 2023-02-02 09:31 | 2023-02-02 14:16 | 1 | 4:45 | P | NO SE REPORTO CAUSA | 1 X 40 NX EN GABINETE | S23020200103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2023-02-02 | 285 | keep | 0 | Feb | 2023 | 0.00019411 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-02 10:05 | 2023-02-02 11:10 | 8 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REEMPLAZO DE CONEXIONES EN LINEA SECUNDARIA | P23020200037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-02-02 | 520 | keep | 0 | Feb | 2023 | 0.00035417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-02-02 10:07 | 2023-02-02 11:26 | 10 | 1:19 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO CAUSA | P23020200038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2023-02-02 | 790 | keep | 0 | Feb | 2023 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-02 10:38 | 2023-02-02 14:35 | 716 | 3:57 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | S23020200126 | New_Event | Primary Wire Break | Include | Include | Equipment | 237 | 2023-02-02 | 169692 | keep | 0 | Feb | 2023 | 0.11558 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
SAN JUAN | 2023-02-02 10:39 | 2023-02-02 12:31 | 8 | 1:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23020200123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 112 | 2023-02-02 | 896 | keep | 0 | Feb | 2023 | 0.00061026 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-02 10:50 | 2023-02-02 13:16 | 60 | 2:26 | P | DESGANCHE | 1 X 50, 1 X 65 Y 1 X 80 EN C/L DESGANCHE | S23020200128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-02-02 | 8760 | keep | 0 | Feb | 2023 | 0.0059664 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-02-02 10:52 | 2023-02-02 13:48 | 6 | 2:56 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | C23020200056 | New_Event | Animals | Include | Include | Wildlife | 176 | 2023-02-02 | 1056 | keep | 0 | Feb | 2023 | 0.00071924 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-02-02 10:52 | 2023-02-02 13:15 | 50 | 2:23 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23020200081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-02-02 | 7150 | keep | 0 | Feb | 2023 | 0.0048698 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-02 11:02 | 2023-02-02 12:10 | 7 | 1:08 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23020200057 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-02-02 | 476 | keep | 0 | Feb | 2023 | 0.0003242 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-02-02 11:10 | 2023-02-02 12:00 | 5 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23020200011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-02-02 | 250 | keep | 0 | Feb | 2023 | 0.00017027 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-02-02 11:19 | 2023-02-02 11:35 | 5 | 0:16 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR A PETICION PERSONAL EN CAMPO POR MACHETES EN MAL ESTADO EN AMARRE CON 1530-10. PARTE DE V/L D2023-2661 | S23020200139 | New_Event | Switch Failure | Include | Include | Equipment | 16 | 2023-02-02 | 80 | keep | 0 | Feb | 2023 | 5.4488e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-02-02 11:39 | 2023-02-02 14:14 | 5 | 2:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE REMPLAZO SECUNDARIA | S23020200149 | New_Event | Secondary Wire Break | Include | Include | Equipment | 155 | 2023-02-02 | 775 | keep | 0 | Feb | 2023 | 0.00052785 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-02-02 11:44 | 2023-02-02 11:46 | 1510 | 0:02 | T | DESGANCHE | DISPARO CERRADO X CONTROL | C23020200068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-02-02 | 3020 | keep | 0 | Feb | 2023 | 0.0020569 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2023-02-02 11:46 | 2023-02-02 13:19 | 185 | 1:33 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | C23020200081 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-02-02 | 17205 | keep | 0 | Feb | 2023 | 0.011718 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
VEGA BAJA | 2023-02-02 11:59 | 2023-02-02 12:00 | 215 | 0:01 | T | ANIMAL | DISPARO SE CERRO POR CONTROL | B23020200064 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-02 | 215 | keep | 0 | Feb | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-02-02 12:00 | 2023-02-02 15:02 | 50 | 3:02 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | B23020200066 | 1st_after_momentary | Animals | Include | Include | Wildlife | 182 | 2023-02-02 | 9100 | keep | 0 | Feb | 2023 | 0.006198 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-02 12:08 | 2023-02-02 16:40 | 8 | 4:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA Y BAJANTE SECUNDARIO | R23020200037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 272 | 2023-02-02 | 2176 | keep | 0 | Feb | 2023 | 0.0014821 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-02-02 12:13 | 2023-02-02 15:43 | 20 | 3:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23020200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-02-02 | 4200 | keep | 0 | Feb | 2023 | 0.0028606 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-02-02 12:22 | 2023-02-02 14:22 | 40 | 2:00 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23020200056 | New_Event | Animals | Include | Include | Wildlife | 120 | 2023-02-02 | 4800 | keep | 0 | Feb | 2023 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-02 12:23 | 2023-02-02 14:00 | 1 | 1:37 | P | NO SE REPORTO CAUSA | SE REMPLAZO 1 X 30 EN SUB. PRIVADA | S23020200174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2023-02-02 | 97 | keep | 0 | Feb | 2023 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-02 12:26 | 2023-02-02 13:52 | 15 | 1:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 15KVA X 37.5KVA | B23020200072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 86 | 2023-02-02 | 1290 | keep | 0 | Feb | 2023 | 0.00087861 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-02-02 12:30 | 2023-02-02 12:54 | 12 | 0:24 | P | TRANSFORMADOR AVERIADO | SE AJUSTO BUSHING NEUTRAL DE TRANSFORMADOR CLIENTES FLUCTUACIONES DE VOLTAJE EVENTO DE SITUACION PELIGROSA DEL DIA 2/01 A LAS 21:39 | P23020100251 | New_Event | Service Transformer Failure | Include | Include | Equipment | 24 | 2023-02-02 | 288 | keep | 0 | Feb | 2023 | 0.00019616 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-02 12:40 | 2023-02-02 13:18 | 1 | 0:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S23020200183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2023-02-02 | 38 | keep | 0 | Feb | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-02 12:42 | 2023-02-02 13:30 | 20 | 0:48 | P | DESGANCHE | SE ABRE CORTE DE LINEA PARA RETIRAR RAMA SOBRE LINEA PRIMARIA | A23020200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2023-02-02 | 960 | keep | 0 | Feb | 2023 | 0.00065385 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-02 12:46 | 2023-02-02 13:32 | 3 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON CONECTORES EN BAJANTE SECUNDARIO | B23020200075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2023-02-02 | 138 | keep | 0 | Feb | 2023 | 9.3991e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-02-02 13:14 | 2023-02-02 14:06 | 1 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23020200159 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-02-02 | 52 | keep | 0 | Feb | 2023 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-02 13:26 | 2023-02-02 13:46 | 8 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23020200110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-02-02 | 160 | keep | 0 | Feb | 2023 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-02-02 13:27 | 2023-02-02 14:05 | 9 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES EN LINEA SECUNDARIA | P23020200065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2023-02-02 | 342 | keep | 0 | Feb | 2023 | 0.00023293 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2023-02-02 13:30 | 2023-02-02 14:31 | 40 | 1:01 | P | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE CRUCETA PARTIDA | M23020200068 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 61 | 2023-02-02 | 2440 | keep | 0 | Feb | 2023 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-02 13:33 | 2023-02-02 14:35 | 9 | 1:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR 2 BARRAS EN PEDESTAL | C23020200124 | New_Event | Secondary Wire Break | Include | Include | Equipment | 62 | 2023-02-02 | 558 | keep | 0 | Feb | 2023 | 0.00038005 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-02-02 13:46 | 2023-02-02 17:02 | 64 | 3:16 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23020200085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-02-02 | 12544 | keep | 0 | Feb | 2023 | 0.0085437 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2023-02-02 13:47 | 2023-02-02 15:42 | 20 | 1:55 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23020200202 | New_Event | Primary Wire Break | Include | Include | Equipment | 115 | 2023-02-02 | 2300 | keep | 0 | Feb | 2023 | 0.0015665 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-02-02 13:49 | 2023-02-02 14:27 | 2 | 0:38 | P | CONDUCTOR ROTO O ABIERTO | ABRIR XMR PARA REPARAR BAJANTE PRIMARIO DE LINEA A CAJA | C23020200129 | New_Event | Primary Wire Break | Include | Include | Equipment | 38 | 2023-02-02 | 76 | keep | 0 | Feb | 2023 | 5.1763e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2023-02-02 13:55 | 2023-02-02 14:34 | 1 | 0:39 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R23020200044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2023-02-02 | 39 | keep | 0 | Feb | 2023 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-02 14:14 | 2023-02-02 15:47 | 1 | 1:33 | P | DESGANCHE | 2 X 8 EN TRANSFORMADOR DESGANCHE | R23020200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-02-02 | 93 | keep | 0 | Feb | 2023 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-02 14:20 | 2023-02-02 16:14 | 28 | 1:54 | P | TRANSFORMADOR AVERIADO | SE ABRE T-2 PARA REMPLAZO TRANSFORMADOR 37.5 KVA CON ESCAPE DE ACIETE | R23020200013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 114 | 2023-02-02 | 3192 | keep | 0 | Feb | 2023 | 0.0021741 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
MAYAGÃœEZ | 2023-02-02 14:21 | 2023-02-02 15:32 | 10 | 1:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA | M23020200131 | New_Event | Service Transformer Failure | Include | Include | Equipment | 71 | 2023-02-02 | 710 | keep | 0 | Feb | 2023 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-02 14:33 | 2023-02-02 18:52 | 40 | 4:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23020200137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-02-02 | 10360 | keep | 0 | Feb | 2023 | 0.0070561 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-02-02 14:35 | 2023-02-02 14:39 | 2486 | 0:04 | T | NO SE REPORTO CAUSA | SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | C23020200138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-02-02 | 9944 | keep | 0 | Feb | 2023 | 0.0067728 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
BARRANQUITAS | 2023-02-02 14:37 | 2023-02-03 10:11 | 50 | 19:34 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C23020200139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1174 | 2023-02-02 | 58700 | keep | 0 | Feb | 2023 | 0.03998 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-02-02 14:43 | 2023-02-02 16:48 | 226 | 2:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CL NO SE ENCONTRO CAUSA | A23020200076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2023-02-02 | 28250 | keep | 0 | Feb | 2023 | 0.019241 | 0.00015393 | Sustained | FALSE | FALSE | Not_TMED_Event | 226
VEGA BAJA | 2023-02-02 14:47 | 2023-02-02 19:35 | 125 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CL | A23020200079 | New_Event | Primary Wire Break | Include | Include | Equipment | 288 | 2023-02-02 | 36000 | keep | 0 | Feb | 2023 | 0.024519 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-02-02 15:01 | 2023-02-02 17:05 | 8 | 2:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDAIA POR IMPACTO DE CAMION | B23020200095 | New_Event | Secondary Wire Break | Include | Include | Equipment | 124 | 2023-02-02 | 992 | keep | 0 | Feb | 2023 | 0.00067565 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-02-02 15:07 | 2023-02-02 18:27 | 50 | 3:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23020200164 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 200 | 2023-02-02 | 10000 | keep | 0 | Feb | 2023 | 0.006811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-02-02 15:21 | 2023-02-02 16:20 | 7 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR 1 BARRA EN PEDESTAL | C23020200149 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2023-02-02 | 413 | keep | 0 | Feb | 2023 | 0.00028129 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-02-02 15:26 | 2023-02-02 18:11 | 307 | 2:45 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA LEVANTAR NEUTRAL PRIMARIO | C23020200155 | New_Event | Primary Wire Break | Include | Include | Equipment | 165 | 2023-02-02 | 50655 | keep | 0 | Feb | 2023 | 0.034501 | 0.0002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 307
FAJARDO | 2023-02-02 15:29 | 2023-02-02 22:56 | 1 | 7:27 | P | ANIMAL | 1 X 30 EN C/L 1 X 10 EN BANCO DE XMR CRUCE POR CULEBRA | R23020200054 | New_Event | Animals | Include | Include | Wildlife | 447 | 2023-02-02 | 447 | keep | 0 | Feb | 2023 | 0.00030445 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-02 15:30 | 2023-02-02 19:08 | 12 | 3:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23020200152 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 218 | 2023-02-02 | 2616 | keep | 0 | Feb | 2023 | 0.0017817 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-02-02 15:35 | 2023-02-02 18:50 | 40 | 3:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23020200085 | New_Event | Primary Wire Break | Include | Include | Equipment | 195 | 2023-02-02 | 7800 | keep | 0 | Feb | 2023 | 0.0053125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-02-02 15:37 | 2023-02-02 19:48 | 135 | 4:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C23020200156 | New_Event | Cutout Failure | Include | Include | Equipment | 251 | 2023-02-02 | 33885 | keep | 0 | Feb | 2023 | 0.023079 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
CAGUAS | 2023-02-02 15:38 | 2023-02-02 18:28 | 6 | 2:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | C23020200157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-02-02 | 1020 | keep | 0 | Feb | 2023 | 0.00069472 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-02-02 15:43 | 2023-02-02 20:35 | 25 | 4:52 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE | R23020200056 | New_Event | Animals | Include | Include | Wildlife | 292 | 2023-02-02 | 7300 | keep | 0 | Feb | 2023 | 0.004972 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-02 15:58 | 2023-02-02 17:05 | 1 | 1:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | S23020200238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2023-02-02 | 67 | keep | 0 | Feb | 2023 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-02 16:04 | 2023-02-02 17:23 | 2 | 1:19 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | B23020200102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-02-02 | 158 | keep | 0 | Feb | 2023 | 0.00010761 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-02-02 16:05 | 2023-02-02 16:45 | 210 | 0:40 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO TRAMO PARA REMPLAZO DE DOS POSTES PARTIDOS. | S23020200246 | New_Event | Primary Pole Failure | Include | Include | Equipment | 40 | 2023-02-02 | 8400 | keep | 0 | Feb | 2023 | 0.0057212 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
CAGUAS | 2023-02-02 16:27 | 2023-02-02 18:19 | 22 | 1:52 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 SMU 20 DE 25 AMP. CONTAMINACION EN SU-1 | C23020200168 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 112 | 2023-02-02 | 2464 | keep | 0 | Feb | 2023 | 0.0016782 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
FAJARDO | 2023-02-02 16:39 | 2023-02-02 16:40 | 2722 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR | R23020200059 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-02-02 | 2722 | keep | 0 | Feb | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2023-02-02 16:40 | 2023-02-02 18:23 | 381 | 1:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR Y SE LEVANTO FASE | R23020200061 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 103 | 2023-02-02 | 39243 | keep | 0 | Feb | 2023 | 0.026728 | 0.0002595 | Sustained | FALSE | FALSE | Not_TMED_Event | 381
SAN JUAN | 2023-02-02 16:45 | 2023-02-02 23:08 | 141 | 6:23 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO 2 POSTE PARTIDOS PIMARIOS 100% EN SERVICIO | S23020200246 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 383 | 2023-02-02 | 54003 | keep | 0 | Feb | 2023 | 0.036781 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-02-02 16:52 | 2023-02-02 19:18 | 80 | 2:26 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L LINEA ARRIADA CRUZO CON POSTE DE TELEFONO | P23020200094 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 146 | 2023-02-02 | 11680 | keep | 0 | Feb | 2023 | 0.0079552 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-02-02 16:59 | 2023-02-02 17:41 | 2 | 0:42 | P | DESGANCHE | 1 X 65 C/L Y DESGANCHE | S23020200249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2023-02-02 | 84 | keep | 0 | Feb | 2023 | 5.7212e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-02 17:00 | 2023-02-02 22:10 | 51 | 5:10 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23020200253 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2023-02-02 | 15810 | keep | 0 | Feb | 2023 | 0.010768 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
BARRANQUITAS | 2023-02-02 17:22 | 2023-02-02 20:04 | 76 | 2:42 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA IMPACTADA POR EXCAVADORA | C23020200159 | New_Event | Damage From Public | Include | Include | Public | 162 | 2023-02-02 | 12312 | keep | 0 | Feb | 2023 | 0.0083856 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
CANOVANAS | 2023-02-02 17:58 | 2023-02-02 18:45 | 15 | 0:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA | R23020200067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2023-02-02 | 705 | keep | 0 | Feb | 2023 | 0.00048017 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-02 18:23 | 2023-02-02 18:24 | 2722 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR AL REPONER FUSIBLE EN CORTE DE LINEA | R23020200069 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-02-02 | 2722 | keep | 0 | Feb | 2023 | 0.0018539 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-02-02 18:24 | 2023-02-02 19:53 | 381 | 1:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR Y SE LEVANTO FASE | R23020200061 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 89 | 2023-02-02 | 33909 | keep | 0 | Feb | 2023 | 0.023095 | 0.0002595 | Sustained | FALSE | FALSE | Not_TMED_Event | 381
SAN JUAN | 2023-02-02 18:33 | 2023-02-02 19:16 | 10 | 0:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 C/L REMPLAZO DE CAJA PRIMARIA | S23020200252 | New_Event | Cutout Failure | Include | Include | Equipment | 43 | 2023-02-02 | 430 | keep | 0 | Feb | 2023 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-02 18:54 | 2023-02-02 22:12 | 80 | 3:18 | P | DESGANCHE | 1 X 65 EN C/L SE REPARO PUENTE AVERIADO Y DESGANCHE | B23020200118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2023-02-02 | 15840 | keep | 0 | Feb | 2023 | 0.010789 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-02-02 19:14 | 2023-02-03 11:54 | 13 | 16:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23020200268 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1000 | 2023-02-02 | 13000 | keep | 0 | Feb | 2023 | 0.0088542 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2023-02-02 19:36 | 2023-02-02 20:56 | 75 | 1:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA EN C/L | P23020200123 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2023-02-02 | 6000 | keep | 0 | Feb | 2023 | 0.0040866 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-02-02 19:39 | 2023-02-03 00:05 | 3 | 4:26 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES QUEMADO | S23020200278 | New_Event | Switch Failure | Include | Include | Equipment | 266 | 2023-02-02 | 798 | keep | 0 | Feb | 2023 | 0.00054351 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-02-02 19:46 | 2023-02-02 21:32 | 37 | 1:46 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | S23020200270 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-02-02 | 3922 | keep | 0 | Feb | 2023 | 0.0026713 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CAGUAS | 2023-02-02 20:23 | 2023-02-02 20:24 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2302020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-02 | 2178 | keep | 0 | Feb | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
SAN JUAN | 2023-02-02 20:31 | 2023-02-03 09:18 | 57 | 12:47 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S23020200273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 767 | 2023-02-02 | 43719 | keep | 0 | Feb | 2023 | 0.029777 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2023-02-02 20:43 | 2023-02-03 13:29 | 62 | 16:46 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | S23020200275 | New_Event | Primary Wire Break | Include | Include | Equipment | 1006 | 2023-02-02 | 62372 | keep | 0 | Feb | 2023 | 0.042481 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
ARECIBO | 2023-02-02 21:11 | 2023-02-03 09:28 | 3 | 12:17 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA POR PAJAROS | A23020200127 | New_Event | Animals | Include | Include | Wildlife | 737 | 2023-02-02 | 2211 | keep | 0 | Feb | 2023 | 0.0015059 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-02-02 21:27 | 2023-02-02 21:34 | 17 | 0:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO CONECTOR EN BAJANTE SECUNDARIO | R23020200075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 7 | 2023-02-02 | 119 | keep | 0 | Feb | 2023 | 8.105e-05 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2023-02-02 22:41 | 2023-02-03 10:23 | 10 | 11:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE CAMBIO CAJA PRIMARIA | A23020200133 | New_Event | Cutout Failure | Include | Include | Equipment | 702 | 2023-02-02 | 7020 | keep | 0 | Feb | 2023 | 0.0047813 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-02-02 23:09 | 2023-02-03 09:26 | 8 | 10:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 15 EN TRANSFORMADOR SE REEMPLAZO BAJANTE SECUNDARIO | A23020200136 | New_Event | Secondary Wire Break | Include | Include | Equipment | 617 | 2023-02-02 | 4936 | keep | 0 | Feb | 2023 | 0.0033619 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-02-02 23:13 | 2023-02-02 23:14 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-02 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-02-03 00:13 | 2023-02-03 11:45 | 97 | 11:32 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN EL PB2 | C23020300001 | New_Event | Primary Wire Break | Include | Include | Equipment | 692 | 2023-02-03 | 67124 | keep | 0 | Feb | 2023 | 0.045718 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
CANOVANAS | 2023-02-03 01:00 | 2023-02-03 01:01 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23020300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-03 | 1026 | keep | 0 | Feb | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2023-02-03 02:14 | 2023-02-03 02:20 | 798 | 0:06 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA 1652-05 LLEVA EL 80% DEL 1301-03 | S23020300001 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-02-03 | 4788 | keep | 0 | Feb | 2023 | 0.0032611 | 0.00054351 | Sustained | FALSE | FALSE | Not_TMED_Event | 798
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:21 | 763 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | R23020300003 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-02-03 | 5341 | keep | 0 | Feb | 2023 | 0.0036377 | 0.00051968 | Sustained | FALSE | FALSE | Not_TMED_Event | 763
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:21 | 27 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | R23020300003 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-02-03 | 189 | keep | 0 | Feb | 2023 | 0.00012873 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:21 | 1259 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | R23020300003 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-02-03 | 8813 | keep | 0 | Feb | 2023 | 0.0060025 | 0.0008575 | Sustained | FALSE | FALSE | Not_TMED_Event | 1259
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:21 | 1051 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | R23020300003 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-02-03 | 7357 | keep | 0 | Feb | 2023 | 0.0050108 | 0.00071583 | Sustained | FALSE | FALSE | Not_TMED_Event | 1051
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:21 | 188 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | R23020300003 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-02-03 | 1316 | keep | 0 | Feb | 2023 | 0.00089632 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:20 | 1862 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | R23020300004 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-02-03 | 11172 | keep | 0 | Feb | 2023 | 0.0076092 | 0.0012682 | Sustained | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:20 | 1613 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | R23020300004 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-02-03 | 9678 | keep | 0 | Feb | 2023 | 0.0065916 | 0.0010986 | Sustained | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:20 | 1448 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | R23020300004 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-02-03 | 8688 | keep | 0 | Feb | 2023 | 0.0059174 | 0.00098623 | Sustained | FALSE | FALSE | Not_TMED_Event | 1448
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:15 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23020300002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-03 | 1026 | keep | 0 | Feb | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:20 | 614 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA EVENTO CAE EN REGION SJ | S23020300001 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-02-03 | 3684 | keep | 0 | Feb | 2023 | 0.0025092 | 0.00041819 | Sustained | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2023-02-03 02:14 | 2023-02-03 02:20 | 770 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | S23020300001 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-02-03 | 4620 | keep | 0 | Feb | 2023 | 0.0031467 | 0.00052444 | Sustained | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2023-02-03 02:14 | 2023-02-03 02:20 | 1271 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA | S23020300001 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-02-03 | 7626 | keep | 0 | Feb | 2023 | 0.005194 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
CANOVANAS | 2023-02-03 02:14 | 2023-02-03 02:20 | 247 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE SABANA LLANA 1652-05 LLEVA EL 80% DEL 1301-03 EVENTO CAE POR SJ | S23020300001 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-02-03 | 1482 | keep | 0 | Feb | 2023 | 0.0010094 | 0.00016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 247
VEGA BAJA | 2023-02-03 02:27 | 2023-02-03 02:28 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23020300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-03 | 308 | keep | 0 | Feb | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-02-03 02:47 | 2023-02-03 02:48 | 2147 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B23020300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-03 | 2147 | keep | 0 | Feb | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-02-03 02:48 | 2023-02-03 05:35 | 92 | 2:47 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23020300003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-02-03 | 15364 | keep | 0 | Feb | 2023 | 0.010464 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
VEGA BAJA | 2023-02-03 04:05 | 2023-02-03 09:08 | 25 | 5:03 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23020300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2023-02-03 | 7575 | keep | 0 | Feb | 2023 | 0.0051593 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-03 05:35 | 2023-02-03 05:36 | 2147 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23020300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-03 | 2147 | keep | 0 | Feb | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-02-03 05:36 | 2023-02-03 08:09 | 92 | 2:33 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23020300003 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-02-03 | 14076 | keep | 0 | Feb | 2023 | 0.0095871 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-03 05:45 | 2023-02-03 05:46 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23020300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-03 | 990 | keep | 0 | Feb | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BARRANQUITAS | 2023-02-03 05:46 | 2023-02-03 10:09 | 120 | 4:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C23020300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2023-02-03 | 31560 | keep | 0 | Feb | 2023 | 0.021495 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2023-02-03 06:12 | 2023-02-03 09:22 | 6 | 3:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S23020300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2023-02-03 | 1140 | keep | 0 | Feb | 2023 | 0.00077645 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-02-03 06:36 | 2023-02-03 07:05 | 1 | 0:29 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO FASE | P23020300001 | New_Event | Animals | Include | Include | Wildlife | 29 | 2023-02-03 | 29 | keep | 0 | Feb | 2023 | 1.9752e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-03 07:17 | 2023-02-03 10:04 | 1 | 2:47 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA CRUCE CON RATA | C23020300017 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-02-03 | 167 | keep | 0 | Feb | 2023 | 0.00011374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-02-03 07:19 | 2023-02-03 10:32 | 1 | 3:13 | P | NO SE REPORTO CAUSA | 2 X 25 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23020300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2023-02-03 | 193 | keep | 0 | Feb | 2023 | 0.00013145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-03 07:48 | 2023-02-03 09:58 | 480 | 2:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO PARA ABRIR PUENTES Y TRABAJAR CONDICION DE POSTE EN EL SUELO | C23020300184 | New_Event | Primary Pole Failure | Include | Include | Equipment | 130 | 2023-02-03 | 62400 | keep | 0 | Feb | 2023 | 0.0425 | 0.00032693 | Sustained | FALSE | FALSE | Not_TMED_Event | 480
CAGUAS | 2023-02-03 07:50 | 2023-02-03 09:38 | 5 | 1:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C23020300025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 108 | 2023-02-03 | 540 | keep | 0 | Feb | 2023 | 0.00036779 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-02-03 07:56 | 2023-02-03 09:48 | 53 | 1:52 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO DE MACHETE QUEMADO 1 X 65 EN CORTE DE LINEA | P23020300007 | New_Event | Switch Failure | Include | Include | Equipment | 112 | 2023-02-03 | 5936 | keep | 0 | Feb | 2023 | 0.004043 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BAYAMON | 2023-02-03 07:58 | 2023-02-03 10:55 | 80 | 2:57 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | B23020300017 | New_Event | Animals | Include | Include | Wildlife | 177 | 2023-02-03 | 14160 | keep | 0 | Feb | 2023 | 0.0096443 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-02-03 08:10 | 2023-02-04 08:50 | 3 | 24:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | A23010300068 | New_Event | Cutout Failure | Include | Include | Equipment | 1480 | 2023-02-03 | 4440 | keep | 0 | Feb | 2023 | 0.0030241 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2023-02-03 08:17 | 2023-02-03 10:21 | 23 | 2:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23020300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-02-03 | 2852 | keep | 0 | Feb | 2023 | 0.0019425 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
VEGA BAJA | 2023-02-03 08:27 | 2023-02-03 12:34 | 3 | 4:07 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | A23020300009 | New_Event | Primary Wire Break | Include | Include | Equipment | 247 | 2023-02-03 | 741 | keep | 0 | Feb | 2023 | 0.00050469 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2023-02-03 08:36 | 2023-02-03 14:17 | 50 | 5:41 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23020300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 341 | 2023-02-03 | 17050 | keep | 0 | Feb | 2023 | 0.011613 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-03 08:58 | 2023-02-03 08:59 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23020300024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-03 | 2605 | keep | 0 | Feb | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
SAN JUAN | 2023-02-03 09:10 | 2023-02-03 10:57 | 1 | 1:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR Y SE REPARO SECUNDARIA | S23020300014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 107 | 2023-02-03 | 107 | keep | 0 | Feb | 2023 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-03 09:10 | 2023-02-03 15:13 | 217 | 6:03 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | R23030300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2023-02-03 | 78771 | keep | 0 | Feb | 2023 | 0.053651 | 0.0001478 | Sustained | FALSE | FALSE | Not_TMED_Event | 217
HUMACAO | 2023-02-03 09:14 | 2023-02-03 11:29 | 50 | 2:15 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE SAFADO HACIA CAJA PRIMARIA | C23020300055 | New_Event | Primary Wire Break | Include | Include | Equipment | 135 | 2023-02-03 | 6750 | keep | 0 | Feb | 2023 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-02-03 09:34 | 2023-02-03 09:35 | 1076 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE LLEVA 5007-04 | P23020300017 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-03 | 1076 | keep | 0 | Feb | 2023 | 0.00073286 | 0.00073286 | Momentary | FALSE | FALSE | Not_TMED_Event | 1076
PONCE | 2023-02-03 09:34 | 2023-02-03 09:35 | 462 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE LA CARGA POR EL 5003-01 | P23020300017 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-03 | 462 | keep | 0 | Feb | 2023 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
BARRANQUITAS | 2023-02-03 09:58 | 2023-02-03 17:33 | 40 | 7:35 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE EN EL SUELO | C23020300184 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 455 | 2023-02-03 | 18200 | keep | 0 | Feb | 2023 | 0.012396 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-02-03 10:03 | 2023-02-03 12:53 | 1076 | 2:50 | T | CONDUCTOR ROTO O ABIERTO | ALIMENTADOR FUERA POR LINEA PRIMARIA EN EL PISO LLEVA 5007-04 | P23020300024 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2023-02-03 | 182920 | keep | 0 | Feb | 2023 | 0.12459 | 0.00073286 | Sustained | FALSE | FALSE | Not_TMED_Event | 1076
PONCE | 2023-02-03 10:03 | 2023-02-03 12:53 | 462 | 2:50 | T | ALIMENTADOR AMARRADO | LINEA PRIMARIA EN EL PISO SE TRANSFIERE CARGA A 5003-01 | P23020300024 | New_Event | Feeder Load Transferred | Include | Include | Other | 170 | 2023-02-03 | 78540 | keep | 0 | Feb | 2023 | 0.053493 | 0.00031467 | Sustained | FALSE | FALSE | Not_TMED_Event | 462
GUAYAMA | 2023-02-03 10:14 | 2023-02-03 11:20 | 1 | 1:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES SECUNDARIAS 1 X 8 EN TRANSFORMADOR | P23020300027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 66 | 2023-02-03 | 66 | keep | 0 | Feb | 2023 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-03 10:40 | 2023-02-03 14:15 | 211 | 3:35 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA | P23020300038 | New_Event | Primary Wire Break | Include | Include | Equipment | 215 | 2023-02-03 | 45365 | keep | 0 | Feb | 2023 | 0.030898 | 0.00014371 | Sustained | FALSE | FALSE | Not_TMED_Event | 211
BARRANQUITAS | 2023-02-03 11:09 | 2023-02-03 12:26 | 4 | 1:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SULFATADO EN LINEA SECUNDARIA | C23020300084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 77 | 2023-02-03 | 308 | keep | 0 | Feb | 2023 | 0.00020978 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-03 11:18 | 2023-02-03 12:26 | 11 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO Y CONECTORES | B23020300041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2023-02-03 | 748 | keep | 0 | Feb | 2023 | 0.00050946 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-02-03 11:20 | 2023-02-03 15:41 | 38 | 4:21 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO CONECTOR QUEMADO EN MACHETE | S23020300003 | New_Event | Primary Wire Break | Include | Include | Equipment | 261 | 2023-02-03 | 9918 | keep | 0 | Feb | 2023 | 0.0067551 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BARRANQUITAS | 2023-02-03 11:35 | 2023-02-03 12:48 | 5 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE CONECTORES SULFATADOS Y TOMA | C23020100267 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-02-03 | 365 | keep | 0 | Feb | 2023 | 0.0002486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-02-03 11:35 | 2023-02-03 16:55 | 46 | 5:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR PARTIDO | C23020300090 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 320 | 2023-02-03 | 14720 | keep | 0 | Feb | 2023 | 0.010026 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
FAJARDO | 2023-02-03 11:40 | 2023-02-03 11:41 | 3003 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2302030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-03 | 3003 | keep | 0 | Feb | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
UTUADO | 2023-02-03 11:43 | 2023-02-03 12:25 | 60 | 0:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A23020300042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2023-02-03 | 2520 | keep | 0 | Feb | 2023 | 0.0017164 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-02-03 11:45 | 2023-02-03 13:27 | 1607 | 1:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN EL PB2 | C23020300001 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 102 | 2023-02-03 | 163914 | keep | 0 | Feb | 2023 | 0.11164 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-03 12:12 | 2023-02-03 18:00 | 40 | 5:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2023-02-03 | 13920 | keep | 0 | Feb | 2023 | 0.0094808 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-03 12:22 | 2023-02-03 14:00 | 10 | 1:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BARRA SECUNDARIA | S23020200264 | New_Event | Secondary Wire Break | Include | Include | Equipment | 98 | 2023-02-03 | 980 | keep | 0 | Feb | 2023 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-03 12:37 | 2023-02-03 15:05 | 8 | 2:28 | P | DESGANCHE | 2 X 65 EN C/L Y DESGANCHE | R23020300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-02-03 | 1184 | keep | 0 | Feb | 2023 | 0.00080642 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-02-03 12:41 | 2023-02-03 16:36 | 40 | 3:55 | P | DESGANCHE | 1 X 30 EN C/L SE LEVANTO NEUTRAL PRIMARIO Y SECUNDARIA SE REALIZO DESGANCHE | B23020300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2023-02-03 | 9400 | keep | 0 | Feb | 2023 | 0.0064023 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-03 12:45 | 2023-02-03 16:07 | 36 | 3:22 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | S23020300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-02-03 | 7272 | keep | 0 | Feb | 2023 | 0.0049529 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2023-02-03 12:48 | 2023-02-03 14:30 | 60 | 1:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23020300054 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 102 | 2023-02-03 | 6120 | keep | 0 | Feb | 2023 | 0.0041683 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-02-03 12:52 | 2023-02-03 12:53 | 9 | 0:01 | T | ALIMENTADOR AMARRADO | SE ABRE ALIMENTADOR PARA TRANSFERIR CARGA DE 5003-01 Y 5004-04 | P23020300066 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-03 | 9 | keep | 0 | Feb | 2023 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2023-02-03 13:04 | 2023-02-03 13:46 | 18 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIÃ“ TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C23020300102 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2023-02-03 | 756 | keep | 0 | Feb | 2023 | 0.00051491 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2023-02-03 13:20 | 2023-02-03 13:30 | 7 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON CONECTORES Y BAJANTE DE TRANSFORMADOR | C23020300041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-02-03 | 70 | keep | 0 | Feb | 2023 | 4.7677e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-02-03 13:35 | 2023-02-03 15:45 | 200 | 2:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 140 EN CORTE DE LINEA | P23020300077 | New_Event | Cutout Failure | Include | Include | Equipment | 130 | 2023-02-03 | 26000 | keep | 0 | Feb | 2023 | 0.017708 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-02-03 13:45 | 2023-02-03 14:50 | 15 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REEMPLAZAR CONEXIONES SECUNDARIAS | P22100700296 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-02-03 | 975 | keep | 0 | Feb | 2023 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-03 13:46 | 2023-02-03 14:09 | 15 | 0:23 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | R23020300036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 23 | 2023-02-03 | 345 | keep | 0 | Feb | 2023 | 0.00023498 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-02-03 14:05 | 2023-02-03 14:30 | 82 | 0:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA PRIMARIA QUEMADA | P23020300087 | New_Event | Cutout Failure | Include | Include | Equipment | 25 | 2023-02-03 | 2050 | keep | 0 | Feb | 2023 | 0.0013962 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
YAUCO | 2023-02-03 14:10 | 2023-02-03 18:24 | 143 | 4:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23020300092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2023-02-03 | 36322 | keep | 0 | Feb | 2023 | 0.024739 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
BARRANQUITAS | 2023-02-03 14:10 | 2023-02-03 17:21 | 80 | 3:11 | P | NO SE REPORTO CAUSA | 3 X 80 EN C/L | C23020300115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2023-02-03 | 15280 | keep | 0 | Feb | 2023 | 0.010407 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-02-03 14:29 | 2023-02-03 15:21 | 12 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO PEDESTAL Y BARRA SECUNDARIA | R23020300040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-02-03 | 624 | keep | 0 | Feb | 2023 | 0.000425 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-03 14:30 | 2023-02-03 15:19 | 12 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO BARRA PEDESTAL | S23020300044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-02-03 | 588 | keep | 0 | Feb | 2023 | 0.00040048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-03 14:40 | 2023-02-03 16:40 | 8 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPRARA SECUNDARIA TRAS PATIO | S23020300070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2023-02-03 | 960 | keep | 0 | Feb | 2023 | 0.00065385 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-02-03 14:45 | 2023-02-03 15:20 | 12 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | P23020200082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-02-03 | 420 | keep | 0 | Feb | 2023 | 0.00028606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-02-03 14:52 | 2023-02-03 14:55 | 1571 | 0:03 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1658-14 LLEVA 70% DEL 1658-13 SE CERRO POR CONTROL DESGANCHE | R23030300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-02-03 | 4713 | keep | 0 | Feb | 2023 | 0.00321 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
CANOVANAS | 2023-02-03 14:52 | 2023-02-03 14:55 | 1 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1658-14 LLEVA 70% DEL 1658-13 CERRO POR CONTROL | R23030300041 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-03 | 3 | keep | 0 | Feb | 2023 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-03 14:55 | 2023-02-03 16:43 | 27 | 1:48 | P | DESGANCHE | 2 X 100 EN RISER Y DESGANCHE | R23020300044 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-02-03 | 2916 | keep | 0 | Feb | 2023 | 0.0019861 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
AGUADILLA | 2023-02-03 15:00 | 2023-02-04 11:55 | 8 | 20:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZAR BAJANTES SECUNDARIOS | M23020300076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1255 | 2023-02-03 | 10040 | keep | 0 | Feb | 2023 | 0.0068382 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-03 15:15 | 2023-02-03 16:30 | 250 | 1:15 | P | ANIMAL | 1 X 100 EN C/L PRINCIPAL Y 1 X 65 EN C/L INTERMEDIO. AVE CRUZO LINEAS | B23020300075 | New_Event | Animals | Include | Include | Wildlife | 75 | 2023-02-03 | 18750 | keep | 0 | Feb | 2023 | 0.012771 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-02-03 15:41 | 2023-02-03 18:42 | 115 | 3:01 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO CONECTOR QUEMADO EN MACHETE | S23020300003 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 181 | 2023-02-03 | 20815 | keep | 0 | Feb | 2023 | 0.014177 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-02-03 16:22 | 2023-02-03 18:16 | 1 | 1:54 | P | DESGANCHE | 1 X 15 EN C/L Y DESGANCHE | R23020300056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-02-03 | 114 | keep | 0 | Feb | 2023 | 7.7645e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-03 16:40 | 2023-02-03 19:15 | 115 | 2:35 | P | DESGANCHE | 1 X 65 EN C/L EN PRIMER CORTE DE LINEA SE REALIZO DESGANCHE 80 CLIENTES EN SERVICIO | B23020300086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-02-03 | 17825 | keep | 0 | Feb | 2023 | 0.012141 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
VEGA BAJA | 2023-02-03 16:40 | 2023-02-03 18:47 | 9 | 2:07 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA A LINEA EN XMR | B23020300087 | New_Event | Primary Wire Break | Include | Include | Equipment | 127 | 2023-02-03 | 1143 | keep | 0 | Feb | 2023 | 0.00077849 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2023-02-03 16:57 | 2023-02-04 14:15 | 30 | 21:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A23020300062 | New_Event | Cutout Failure | Include | Include | Equipment | 1278 | 2023-02-03 | 38340 | keep | 0 | Feb | 2023 | 0.026113 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-03 17:00 | 2023-02-03 17:40 | 4 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO 3 TRAMOS DE SECUNDARIA | S23020300046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-02-03 | 160 | keep | 0 | Feb | 2023 | 0.00010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-02-03 17:33 | 2023-02-03 19:33 | 480 | 2:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO PARA CERRAR PUENTES | C23020300184 | New_Event | Primary Pole Failure | Include | Include | Equipment | 120 | 2023-02-03 | 57600 | keep | 0 | Feb | 2023 | 0.039231 | 0.00032693 | Sustained | FALSE | FALSE | Not_TMED_Event | 480
VEGA BAJA | 2023-02-03 17:40 | 2023-02-03 18:20 | 8 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARAN CONEXIONES | A23020300112 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-02-03 | 320 | keep | 0 | Feb | 2023 | 0.00021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-03 18:20 | 2023-02-03 21:09 | 101 | 2:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA 1 X 30 EN RISER DESGANCHE | S23020300114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-02-03 | 17069 | keep | 0 | Feb | 2023 | 0.011626 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
BAYAMON | 2023-02-03 18:20 | 2023-02-03 18:21 | 2147 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23020300110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-03 | 2147 | keep | 0 | Feb | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
MAYAGÃœEZ | 2023-02-03 18:29 | 2023-02-04 09:15 | 30 | 14:46 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR / 1 X 30 Y 1 X 80 EN CORTES DE LINEA IGUANA CRUZO LINEAS | M23020300092 | New_Event | Animals | Include | Include | Wildlife | 886 | 2023-02-03 | 26580 | keep | 0 | Feb | 2023 | 0.018104 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-03 18:46 | 2023-02-03 21:37 | 1 | 2:51 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S23020300116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2023-02-03 | 171 | keep | 0 | Feb | 2023 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-03 18:47 | 2023-02-04 00:26 | 8 | 5:39 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTES PARTIDOS | M23020300074 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 339 | 2023-02-03 | 2712 | keep | 0 | Feb | 2023 | 0.0018471 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-02-03 19:05 | 2023-02-04 11:20 | 40 | 16:15 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES | M23020300100 | New_Event | Primary Wire Break | Include | Include | Equipment | 975 | 2023-02-03 | 39000 | keep | 0 | Feb | 2023 | 0.026563 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-03 19:15 | 2023-02-03 20:38 | 35 | 1:23 | P | DESGANCHE | 1 X 40 EN C/L EN CORTE DE LINEA INTERMEDIO SE REALIZO DESGANCHE | B23020300086 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-02-03 | 2905 | keep | 0 | Feb | 2023 | 0.0019786 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-03 19:17 | 2023-02-03 21:42 | 33 | 2:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23020300194 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2023-02-03 | 4785 | keep | 0 | Feb | 2023 | 0.003259 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
GUAYAMA | 2023-02-03 19:19 | 2023-02-04 10:36 | 18 | 15:17 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 37.5 KVA AVERIADO | P23020300157 | New_Event | Service Transformer Failure | Include | Include | Equipment | 917 | 2023-02-03 | 16506 | keep | 0 | Feb | 2023 | 0.011242 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-02-03 19:56 | 2023-02-03 19:57 | 2900 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23020300202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-03 | 2900 | keep | 0 | Feb | 2023 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
BARRANQUITAS | 2023-02-03 20:20 | 2023-02-04 08:48 | 14 | 12:28 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23020300206 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 748 | 2023-02-03 | 10472 | keep | 0 | Feb | 2023 | 0.0071324 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-02-03 20:29 | 2023-02-03 21:32 | 40 | 1:03 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | R23020300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-02-03 | 2520 | keep | 0 | Feb | 2023 | 0.0017164 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-02-03 22:10 | 2023-02-04 02:59 | 60 | 4:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2023-02-03 | 17340 | keep | 0 | Feb | 2023 | 0.01181 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-02-03 22:41 | 2023-02-04 08:46 | 130 | 10:05 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | R23020300074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 605 | 2023-02-03 | 78650 | keep | 0 | Feb | 2023 | 0.053568 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
VEGA BAJA | 2023-02-03 22:54 | 2023-02-04 07:23 | 37 | 8:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO PORTAFUSIBLE | B23020300132 | New_Event | Cutout Failure | Include | Include | Equipment | 509 | 2023-02-03 | 18833 | keep | 0 | Feb | 2023 | 0.012827 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2023-02-03 22:54 | 2023-02-04 00:08 | 110 | 1:14 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L SE LLEVO CONDUCTOR A AISLADOR , SE REPARO CONDUCTOR Y SE HIZO DESGANCHE EN VARIOS PUNTOS | B23020300111 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 74 | 2023-02-03 | 8140 | keep | 0 | Feb | 2023 | 0.0055441 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
ARECIBO | 2023-02-03 23:40 | 2023-02-04 01:29 | 100 | 1:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020300094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2023-02-03 | 10900 | keep | 0 | Feb | 2023 | 0.0074239 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-03 23:41 | 2023-02-04 02:46 | 200 | 3:05 | P | ANIMAL | 1X65 EN C/L CRUCE CON AVE | B23020300135 | New_Event | Animals | Include | Include | Wildlife | 185 | 2023-02-03 | 37000 | keep | 0 | Feb | 2023 | 0.025201 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-02-04 00:08 | 2023-02-04 00:09 | 2147 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | RECERRO AL HACER PRUEBA EN C/L | B23020400001 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 1 | 2023-02-04 | 2147 | keep | 0 | Feb | 2023 | 0.0014623 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-04 00:09 | 2023-02-04 10:14 | 110 | 10:05 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L SE LLEVO CONDUCTOR A AISLADOR , SE REPARO CONDUCTOR Y SE HIZO DESGANCHE EN VARIOS PUNTOS | B23020300111 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 605 | 2023-02-04 | 66550 | keep | 0 | Feb | 2023 | 0.045327 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
HUMACAO | 2023-02-04 03:25 | 2023-02-04 03:28 | 327 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 2603-06 LLEVA EL 2603-07 | C2302040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-04 | 981 | keep | 0 | Feb | 2023 | 0.00066815 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
CANOVANAS | 2023-02-04 03:37 | 2023-02-04 08:56 | 65 | 5:19 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | R23020400001 | New_Event | Animals | Include | Include | Wildlife | 319 | 2023-02-04 | 20735 | keep | 0 | Feb | 2023 | 0.014123 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-02-04 04:35 | 2023-02-04 09:10 | 120 | 4:35 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23020400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2023-02-04 | 33000 | keep | 0 | Feb | 2023 | 0.022476 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2023-02-04 04:39 | 2023-02-04 04:42 | 2124 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1657-04 SE CERRO POR CONTROL LLEVA 1118-07 | R2302040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-04 | 6372 | keep | 0 | Feb | 2023 | 0.0043399 | 0.0014466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2124
CANOVANAS | 2023-02-04 04:39 | 2023-02-04 04:42 | 14 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 1118-07 | R2302040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-04 | 42 | keep | 0 | Feb | 2023 | 2.8606e-05 | 9.5353e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-02-04 04:52 | 2023-02-04 08:41 | 90 | 3:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R23020400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-02-04 | 20610 | keep | 0 | Feb | 2023 | 0.014037 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2023-02-04 05:42 | 2023-02-04 09:30 | 36 | 3:48 | P | DESGANCHE | 1 X 50 EN C/L | C23020400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-02-04 | 8208 | keep | 0 | Feb | 2023 | 0.0055904 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
AGUADILLA | 2023-02-04 05:46 | 2023-02-04 05:47 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23020400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-04 | 1827 | keep | 0 | Feb | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CAGUAS | 2023-02-04 06:27 | 2023-02-04 09:25 | 170 | 2:58 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 15 EN BANCO DE XMRS CRUCE X AVE | C23020400004 | New_Event | Animals | Include | Include | Wildlife | 178 | 2023-02-04 | 30260 | keep | 0 | Feb | 2023 | 0.02061 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
GUAYAMA | 2023-02-04 07:00 | 2023-02-04 10:05 | 11 | 3:05 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | P23020400042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-02-04 | 2035 | keep | 0 | Feb | 2023 | 0.001386 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-02-04 07:26 | 2023-02-04 13:17 | 7 | 5:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR LEVANTO SECUNDARIA DEL SUELO | C23020400008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 351 | 2023-02-04 | 2457 | keep | 0 | Feb | 2023 | 0.0016735 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-02-04 07:41 | 2023-02-04 11:30 | 100 | 3:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR | A23020400005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 229 | 2023-02-04 | 22900 | keep | 0 | Feb | 2023 | 0.015597 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-02-04 07:53 | 2023-02-04 08:05 | 508 | 0:12 | T | DESGANCHE | DISPARO DE INTERRUPTOR TENIA RECIERRE EN OFF POR TRABAJOS EN LINEA 50200 LINEA PRIMARIA 5402-02 | P23020400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 12 | 2023-02-04 | 6096 | keep | 0 | Feb | 2023 | 0.004152 | 0.000346 | Sustained | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-02-04 07:53 | 2023-02-04 08:05 | 64 | 0:12 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR TENIA RECIERRE EN OFF POR EN LINEA PRIMARIA 5402-02 | P23020400017 | New_Event | Feeder Load Transferred | Include | Include | Other | 12 | 2023-02-04 | 768 | keep | 0 | Feb | 2023 | 0.00052308 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
HUMACAO | 2023-02-04 08:01 | 2023-02-04 08:02 | 1835 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23020400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-04 | 1835 | keep | 0 | Feb | 2023 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
YAUCO | 2023-02-04 08:05 | 2023-02-04 10:30 | 107 | 2:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23020400020 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 145 | 2023-02-04 | 15515 | keep | 0 | Feb | 2023 | 0.010567 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-04 08:20 | 2023-02-04 08:57 | 9 | 0:37 | P | FUEGO | ABRIO XMR PARA RETIRAR TOMA DE CASA QUEMADA | C23020400007 | New_Event | Fire | Include | Include | Public | 37 | 2023-02-04 | 333 | keep | 0 | Feb | 2023 | 0.0002268 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-02-04 08:31 | 2023-02-04 08:33 | 513 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 20% POR 1118-10 SE PROBO POR CONTROL QUEDO EN SERVICIO | S23020400000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-04 | 1026 | keep | 0 | Feb | 2023 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-02-04 08:31 | 2023-02-04 08:33 | 2782 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LLEVA 20% DEL 1111-01 SE PROBO POR CONTROL QUEDO EN SERVICIO | S23020400000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2023-02-04 | 5564 | keep | 0 | Feb | 2023 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2023-02-04 08:33 | 2023-02-04 11:36 | 100 | 3:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S23020400029 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 183 | 2023-02-04 | 18300 | keep | 0 | Feb | 2023 | 0.012464 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-02-04 08:50 | 2023-02-04 09:12 | 4 | 0:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA | B23020400013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 22 | 2023-02-04 | 88 | keep | 0 | Feb | 2023 | 5.9936e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-02-04 09:03 | 2023-02-04 10:03 | 7 | 1:00 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR PAJARO | M23020400003 | New_Event | Animals | Include | Include | Wildlife | 60 | 2023-02-04 | 420 | keep | 0 | Feb | 2023 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-02-04 09:05 | 2023-02-04 11:35 | 25 | 2:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23020400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-02-04 | 3750 | keep | 0 | Feb | 2023 | 0.0025541 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-02-04 09:06 | 2023-02-04 12:12 | 158 | 3:06 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRE CORTE DE LINEA PARA RETEZAR LINEA PRIMARIA 1 X 80 EN CONVERTIDOR | P23020400032 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 186 | 2023-02-04 | 29388 | keep | 0 | Feb | 2023 | 0.020016 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
SAN JUAN | 2023-02-04 09:13 | 2023-02-04 14:00 | 4 | 4:47 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN SU-20B2 SE CERRO PUENTE | S23020400027 | New_Event | Primary Wire Break | Include | Include | Equipment | 287 | 2023-02-04 | 1148 | keep | 0 | Feb | 2023 | 0.0007819 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-02-04 09:16 | 2023-02-04 20:10 | 5 | 10:54 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | P23020400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 654 | 2023-02-04 | 3270 | keep | 0 | Feb | 2023 | 0.0022272 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-02-04 09:28 | 2023-02-04 09:29 | 4085 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R23020400011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-02-04 | 4085 | keep | 0 | Feb | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-02-04 09:29 | 2023-02-04 13:23 | 100 | 3:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTES DE LINEA SE REEMPLAZARON DISCOS ROTOS | R23020400015 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 234 | 2023-02-04 | 23400 | keep | 0 | Feb | 2023 | 0.015938 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-02-04 09:31 | 2023-02-04 13:41 | 9 | 4:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | C23020400025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 250 | 2023-02-04 | 2250 | keep | 0 | Feb | 2023 | 0.0015325 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-02-04 09:35 | 2023-02-04 11:20 | 40 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR PARA REPARAR CONEXIONES | M23020300100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2023-02-04 | 4200 | keep | 0 | Feb | 2023 | 0.0028606 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-04 09:51 | 2023-02-04 09:53 | 1681 | 0:02 | T | CABLE SOTERRADO AVERIADO | DISPARO ALIMENTADOR AL CERRAR RISER PARA NORMALIZAR CARGA 1303-01 Y 4, LLEVA 1346-4,6 Y 1303-03 SE LIMPIEARON BANDERAS Y SE CERRO POR CONTROL SE ENCONTRO 3 CABLES DESCONECTADOS DETRAS INTERRUPTOR SE HIZO HDC PARA DESACOPLAR BKR. | S23020400032 | New_Event | UG Cable Fault | Include | Include | Equipment | 2 | 2023-02-04 | 3362 | keep | 0 | Feb | 2023 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-02-04 09:51 | 2023-02-04 09:53 | 726 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR AL CERRAR RISER PARA NORMALIZAR CARGA 1303-01 Y 4, LLEVA 1346-4,6 Y 1303-03 SE LIMPIEARON BANDERAS Y SE CERRO POR CONTROL | S23020400032 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-04 | 1452 | keep | 0 | Feb | 2023 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-02-04 09:51 | 2023-02-04 09:53 | 3932 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR AL CERRAR RISER PARA NORMALIZAR CARGA 1303-01 Y 4, LLEVA 1346-4,6 Y 1303-03 SE LIMPIEARON BANDERAS Y SE CERRO POR CONTROL | S23020400032 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-04 | 7864 | keep | 0 | Feb | 2023 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2023-02-04 09:51 | 2023-02-04 09:53 | 1598 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR AL CERRAR RISER PARA NORMALIZAR CARGA 1303-01 Y 4, LLEVA 1346-4,6 Y 1303-03 SE LIMPIEARON BANDERAS Y SE CERRO POR CONTROL | S23020400032 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-04 | 3196 | keep | 0 | Feb | 2023 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2023-02-04 10:00 | 2023-02-04 11:06 | 3 | 1:06 | P | ANIMAL | 1 X 15 EN XMR SE RETIRO CULEBRA | B23020400027 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-02-04 | 198 | keep | 0 | Feb | 2023 | 0.00013486 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-04 10:18 | 2023-02-04 11:34 | 3 | 1:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO CONECTORES SECUNDARIOS | S23020300120 | New_Event | Secondary Wire Break | Include | Include | Equipment | 76 | 2023-02-04 | 228 | keep | 0 | Feb | 2023 | 0.00015529 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-02-04 10:24 | 2023-02-04 10:52 | 1380 | 0:28 | T | DESGANCHE | DISPARO SE ENCONTRO INDICACION DE MANIJA EN VERDE SE CERRO INTERRUPTOR | R23020400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2023-02-04 | 38640 | keep | 0 | Feb | 2023 | 0.026318 | 0.00093991 | Sustained | FALSE | FALSE | Not_TMED_Event | 1380
CANOVANAS | 2023-02-04 10:52 | 2023-02-04 12:20 | 200 | 1:28 | P | DESGANCHE | 2 X 80 EN CORTES DE LINEA DESGANCHE | R23020400026 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-02-04 | 17600 | keep | 0 | Feb | 2023 | 0.011987 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-04 10:52 | 2023-02-04 10:53 | 2999 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23020400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-04 | 2999 | keep | 0 | Feb | 2023 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
GUAYAMA | 2023-02-04 10:57 | 2023-02-04 12:34 | 100 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P23020400050 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2023-02-04 | 9700 | keep | 0 | Feb | 2023 | 0.0066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-04 10:59 | 2023-02-04 13:56 | 120 | 2:57 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN RISER Y SE REEMPLAZO CAJA PRIMARIA 2 X 65 EN C/L | B23020400033 | New_Event | Primary Wire Break | Include | Include | Equipment | 177 | 2023-02-04 | 21240 | keep | 0 | Feb | 2023 | 0.014466 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
FAJARDO | 2023-02-04 11:20 | 2023-02-04 13:19 | 100 | 1:59 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | R23020400031 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-02-04 | 11900 | keep | 0 | Feb | 2023 | 0.008105 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-02-04 11:37 | 2023-02-04 11:50 | 508 | 0:13 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE ALIMENTADOR FUERTE LLUVIA | P23020400055 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 13 | 2023-02-04 | 6604 | keep | 0 | Feb | 2023 | 0.004498 | 0.000346 | Sustained | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-02-04 11:37 | 2023-02-04 11:50 | 64 | 0:13 | T | ALIMENTADOR AMARRADO | DISPARO DE ALIMENTADOR FUERTE LLUVIA | P23020400055 | New_Event | Feeder Load Transferred | Include | Include | Other | 13 | 2023-02-04 | 832 | keep | 0 | Feb | 2023 | 0.00056667 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2023-02-04 12:04 | 2023-02-04 12:05 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23020400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-04 | 3718 | keep | 0 | Feb | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CAGUAS | 2023-02-04 12:11 | 2023-02-04 15:00 | 200 | 2:49 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23020400056 | New_Event | Animals | Include | Include | Wildlife | 169 | 2023-02-04 | 33800 | keep | 0 | Feb | 2023 | 0.023021 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-02-04 12:24 | 2023-02-04 14:28 | 1 | 2:04 | P | SOBRECARGA | 1 X 25 EN C/L POR CARGA | B23020400045 | New_Event | Trip Due To Overload | Include | Include | Other | 124 | 2023-02-04 | 124 | keep | 0 | Feb | 2023 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-04 12:49 | 2023-02-04 14:43 | 150 | 1:54 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | M23020400024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-02-04 | 17100 | keep | 0 | Feb | 2023 | 0.011647 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-02-04 12:56 | 2023-02-04 15:03 | 75 | 2:07 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23020400063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-02-04 | 9525 | keep | 0 | Feb | 2023 | 0.0064874 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-02-04 12:56 | 2023-02-04 15:07 | 50 | 2:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M23020400026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-02-04 | 6550 | keep | 0 | Feb | 2023 | 0.0044612 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-02-04 12:59 | 2023-02-04 15:17 | 90 | 2:18 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | S23020400057 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-02-04 | 12420 | keep | 0 | Feb | 2023 | 0.0084592 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2023-02-04 13:18 | 2023-02-04 18:30 | 40 | 5:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M23020400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2023-02-04 | 12480 | keep | 0 | Feb | 2023 | 0.0085001 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-02-04 13:30 | 2023-02-04 17:34 | 70 | 4:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | A23020400040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 244 | 2023-02-04 | 17080 | keep | 0 | Feb | 2023 | 0.011633 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-02-04 13:36 | 2023-02-04 14:17 | 8 | 0:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA Y 1 X 15 EN XMR | R23020400039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 41 | 2023-02-04 | 328 | keep | 0 | Feb | 2023 | 0.0002234 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-04 13:46 | 2023-02-04 16:15 | 10 | 2:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 10 EN XMR | B23020400050 | New_Event | Cutout Failure | Include | Include | Equipment | 149 | 2023-02-04 | 1490 | keep | 0 | Feb | 2023 | 0.0010148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-02-04 13:46 | 2023-02-04 15:20 | 26 | 1:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23020400075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-02-04 | 2444 | keep | 0 | Feb | 2023 | 0.0016646 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
GUAYAMA | 2023-02-04 14:18 | 2023-02-04 15:25 | 57 | 1:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTE BRISA | P23020400078 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 67 | 2023-02-04 | 3819 | keep | 0 | Feb | 2023 | 0.0026011 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
VEGA BAJA | 2023-02-04 14:25 | 2023-02-04 16:00 | 6 | 1:35 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE Y SE REPARO LINEA SECUNDARIA AVERIADA | A23020400044 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 95 | 2023-02-04 | 570 | keep | 0 | Feb | 2023 | 0.00038822 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-02-04 14:37 | 2023-02-04 14:51 | 12 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTOR SECUNDARIO | R23020400045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2023-02-04 | 168 | keep | 0 | Feb | 2023 | 0.00011442 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-02-04 14:42 | 2023-02-04 19:36 | 2 | 4:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | M23020400050 | New_Event | Primary Wire Break | Include | Include | Equipment | 294 | 2023-02-04 | 588 | keep | 0 | Feb | 2023 | 0.00040048 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-02-04 14:43 | 2023-02-04 15:10 | 12 | 0:27 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR POR PAJARO | M23020400051 | New_Event | Animals | Include | Include | Wildlife | 27 | 2023-02-04 | 324 | keep | 0 | Feb | 2023 | 0.00022067 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-02-04 14:56 | 2023-02-04 14:57 | 1835 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | C23020400074 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-04 | 1835 | keep | 0 | Feb | 2023 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2023-02-04 14:57 | 2023-02-04 17:07 | 144 | 2:10 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23020400077 | 1st_after_momentary | Animals | Include | Include | Wildlife | 130 | 2023-02-04 | 18720 | keep | 0 | Feb | 2023 | 0.01275 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
GUAYAMA | 2023-02-04 15:00 | 2023-02-04 16:40 | 15 | 1:40 | P | PARARRAYOS DEFECTUOSO | SE ELIMINO PARARRAYO 1 X 5 EN TRANSFORMADOR | P23020400091 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 100 | 2023-02-04 | 1500 | keep | 0 | Feb | 2023 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-02-04 15:11 | 2023-02-04 17:37 | 30 | 2:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A23020400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-02-04 | 4380 | keep | 0 | Feb | 2023 | 0.0029832 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-04 15:39 | 2023-02-04 16:19 | 16 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23020400065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-02-04 | 640 | keep | 0 | Feb | 2023 | 0.0004359 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-02-04 16:00 | 2023-02-04 17:24 | 40 | 1:24 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER @ T-16 | S23020400067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2023-02-04 | 3360 | keep | 0 | Feb | 2023 | 0.0022885 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-04 16:06 | 2023-02-04 18:31 | 181 | 2:25 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23020400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2023-02-04 | 26245 | keep | 0 | Feb | 2023 | 0.017875 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
BAYAMON | 2023-02-04 17:02 | 2023-02-04 20:16 | 12 | 3:14 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE SECUNDARIO Y SE RETIRO SECUNDARIA QUEMADA | B23020400069 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 194 | 2023-02-04 | 2328 | keep | 0 | Feb | 2023 | 0.0015856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-02-04 17:12 | 2023-02-04 20:50 | 50 | 3:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M23020400073 | New_Event | Primary Wire Break | Include | Include | Equipment | 218 | 2023-02-04 | 10900 | keep | 0 | Feb | 2023 | 0.0074239 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-02-04 17:59 | 2023-02-05 00:05 | 300 | 6:06 | P | DESGANCHE | 2 X 80 EN CL SE RETIRO RAMA SOBRE LINEA PRIMARIA | P23020400106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 366 | 2023-02-04 | 109800 | keep | 0 | Feb | 2023 | 0.074784 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-02-04 18:05 | 2023-02-04 19:15 | 12 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S23020400063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-02-04 | 840 | keep | 0 | Feb | 2023 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-04 18:11 | 2023-02-04 18:12 | 4028 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-04 | 4028 | keep | 0 | Feb | 2023 | 0.0027435 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
HUMACAO | 2023-02-04 18:34 | 2023-02-04 18:35 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2302040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-04 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
CANOVANAS | 2023-02-04 18:38 | 2023-02-04 20:43 | 8 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23020400048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2023-02-04 | 1000 | keep | 0 | Feb | 2023 | 0.0006811 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-04 18:45 | 2023-02-04 20:51 | 38 | 2:06 | P | CAUSAS EXTERNAS | ALAMBRE PROVISIONALE EN EL PISO VIVO PERSONAL AJENA A LUMA TUMBANDO PALMA CAYO SOBRE LINEA SE ABRE INTERRUPTOR PARA SECCIONALIZAR | S23020400072 | New_Event | Damage From Public | Include | Include | Public | 126 | 2023-02-04 | 4788 | keep | 0 | Feb | 2023 | 0.0032611 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2023-02-04 18:47 | 2023-02-05 02:42 | 1 | 7:55 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2X100 DE SU-212 @ TRANSCLOSURE POR CONTAMINACION | B23020400075 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 475 | 2023-02-04 | 475 | keep | 0 | Feb | 2023 | 0.00032352 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-04 18:49 | 2023-02-04 22:00 | 30 | 3:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23020400086 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 191 | 2023-02-04 | 5730 | keep | 0 | Feb | 2023 | 0.0039027 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-04 19:24 | 2023-02-04 19:27 | 1784 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% 1711-04 Y LLEVA 10% 1717-01 SE CERRO POR CONTROL | B2302040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-04 | 5352 | keep | 0 | Feb | 2023 | 0.0036452 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2023-02-04 19:24 | 2023-02-04 19:27 | 453 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% 1711-04 Y LLEVA 10% 1717-01 SE CERRO POR CONTROL | B2302040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-04 | 1359 | keep | 0 | Feb | 2023 | 0.00092561 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-02-04 19:24 | 2023-02-04 19:27 | 186 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% 1711-04 Y LLEVA 10% 1717-01 SE CERRO POR CONTROL | B2302040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-04 | 558 | keep | 0 | Feb | 2023 | 0.00038005 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2023-02-04 20:07 | 2023-02-05 01:16 | 20 | 5:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA NO FUNDIO | S23020400171 | New_Event | Cutout Failure | Include | Include | Equipment | 309 | 2023-02-04 | 6180 | keep | 0 | Feb | 2023 | 0.0042092 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-04 20:07 | 2023-02-04 23:46 | 300 | 3:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L SE REMPLAZO PORTAFUSIBLE | S23020400078 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2023-02-04 | 65700 | keep | 0 | Feb | 2023 | 0.044748 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2023-02-04 20:11 | 2023-02-04 21:00 | 1 | 0:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO SE ENCONTRO CAUSA | A23020400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2023-02-04 | 49 | keep | 0 | Feb | 2023 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-04 20:49 | 2023-02-04 21:22 | 8 | 0:33 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23020400050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2023-02-04 | 264 | keep | 0 | Feb | 2023 | 0.00017981 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-04 20:51 | 2023-02-04 21:06 | 8679 | 0:15 | P | CAUSAS EXTERNAS | SE ABRE INTERRUPTOR A PETICION EMANUEL OTERO PARA SECCIONALIZAR TRAMO DE PROVISIONAL EN EL PISO VIVO PERSONA AJENA A LUMA TUMBO PALMA Y CAYO SOBRE LINEA 85% POR 1206-03 | S23020400072 | Additional_clients | Damage From Public | Include | Include | Public | 15 | 2023-02-04 | 130185 | keep | 0 | Feb | 2023 | 0.088668 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-04 20:51 | 2023-02-04 21:06 | 4133 | 0:15 | T | ALIMENTADOR AMARRADO | SE ABRE INTERRUPTOR A PETICION EMANUEL OTERO PARA SECCIONALIZAR TRAMO DE PROVISIONAL EN EL PISO VIVO PERSONA AJENA A LUMA TUMBO PALMA Y CAYO SOBRE LINEA LLEVA 85% DEL 1204-05 | S23020400072 | New_Event | Feeder Load Transferred | Include | Include | Other | 15 | 2023-02-04 | 61995 | keep | 0 | Feb | 2023 | 0.042225 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2023-02-04 21:06 | 2023-02-04 21:42 | 116 | 0:36 | P | CAUSAS EXTERNAS | SE LEVANTO TRAMO PROVISIONAL Y SE CERRO CORTE DE LINEA | S23020400072 | Partial_restoration | Damage From Public | Include | Include | Public | 36 | 2023-02-04 | 4176 | keep | 0 | Feb | 2023 | 0.0028443 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-04 21:12 | 2023-02-05 08:56 | 75 | 11:44 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA / AVE CRUZO FASE A TIERRA | M23020400110 | New_Event | Animals | Include | Include | Wildlife | 704 | 2023-02-04 | 52800 | keep | 0 | Feb | 2023 | 0.035962 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-02-04 21:26 | 2023-02-04 23:46 | 80 | 2:20 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO FASES | M23020400116 | New_Event | Animals | Include | Include | Wildlife | 140 | 2023-02-04 | 11200 | keep | 0 | Feb | 2023 | 0.0076283 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-02-04 21:26 | 2023-02-05 00:01 | 50 | 2:35 | P | OTRAS CAUSAS | 1 X 50 EN CORTE DE LINEA FUSIBLE PODRIDO | A23020400079 | New_Event | Other Causes | Include | Include | Other | 155 | 2023-02-04 | 7750 | keep | 0 | Feb | 2023 | 0.0052785 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-02-04 21:42 | 2023-02-05 08:20 | 6 | 10:38 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR POR LINEA SECUNDARIA CRUZADA | A23020400081 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 638 | 2023-02-04 | 3828 | keep | 0 | Feb | 2023 | 0.0026072 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-02-04 21:52 | 2023-02-05 00:30 | 60 | 2:38 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE ABIERTO | A23020400082 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2023-02-04 | 9480 | keep | 0 | Feb | 2023 | 0.0064568 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-02-04 22:03 | 2023-02-04 22:05 | 1879 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2302040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-04 | 3758 | keep | 0 | Feb | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
PONCE | 2023-02-04 22:15 | 2023-02-04 23:49 | 4009 | 1:34 | S | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SECUNDARIO PORTATIL 14 SE PATRULLO Y NO SE ENCONTRO CAUSA | P23020400115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2023-02-04 | 376846 | keep | 0 | Feb | 2023 | 0.25667 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
CANOVANAS | 2023-02-04 22:41 | 2023-02-05 09:14 | 57 | 10:33 | P | DESGANCHE | DESGANCHE Y 1 X 65 EN C/L | R23020400055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 633 | 2023-02-04 | 36081 | keep | 0 | Feb | 2023 | 0.024575 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
FAJARDO | 2023-02-04 23:42 | 2023-02-05 08:02 | 30 | 8:20 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESPEJE | R23020400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 500 | 2023-02-04 | 15000 | keep | 0 | Feb | 2023 | 0.010216 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-02-05 00:15 | 2023-02-05 00:16 | 619 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A23020500001 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-05 | 619 | keep | 0 | Feb | 2023 | 0.0004216 | 0.0004216 | Momentary | FALSE | FALSE | Not_TMED_Event | 619
ARECIBO | 2023-02-05 00:16 | 2023-02-05 03:24 | 100 | 3:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | A23020500003 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 188 | 2023-02-05 | 18800 | keep | 0 | Feb | 2023 | 0.012805 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-02-05 00:30 | 2023-02-05 01:23 | 75 | 0:53 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE ABIERTO | A23020400082 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 53 | 2023-02-05 | 3975 | keep | 0 | Feb | 2023 | 0.0027074 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-02-05 00:51 | 2023-02-05 03:24 | 4009 | 2:33 | S | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SECUNDARIO PORTATIL 14 NO SE ENCONTRO CAUSA | P23020500014 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 153 | 2023-02-05 | 613377 | keep | 0 | Feb | 2023 | 0.41777 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-05 01:02 | 2023-02-05 05:11 | 109 | 4:09 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | S23020500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2023-02-05 | 27141 | keep | 0 | Feb | 2023 | 0.018486 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
FAJARDO | 2023-02-05 01:49 | 2023-02-05 06:16 | 25 | 4:27 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L SE REEMPLAZO PUENTE PRIMARIO CAJA A LINEA EN C/L | R23020500002 | New_Event | Primary Wire Break | Include | Include | Equipment | 267 | 2023-02-05 | 6675 | keep | 0 | Feb | 2023 | 0.0045463 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-02-05 02:29 | 2023-02-05 04:39 | 10 | 2:10 | P | NO SE REPORTO CAUSA | 2 X 15 EN XMR | R23020500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2023-02-05 | 1300 | keep | 0 | Feb | 2023 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-05 03:00 | 2023-02-05 18:20 | 49 | 15:20 | P | CAUSAS EXTERNAS | 3 X 50 EN C/L SE REMPLAZO POSTE PRIMARIO PARTIDO POR VEHICULO | C23020500002 | New_Event | Damage From Public | Include | Include | Public | 920 | 2023-02-05 | 45080 | keep | 0 | Feb | 2023 | 0.030704 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
MAYAGÃœEZ | 2023-02-05 03:08 | 2023-02-05 09:36 | 10 | 6:28 | P | ANIMAL | 2 X 80 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23020500001 | New_Event | Animals | Include | Include | Wildlife | 388 | 2023-02-05 | 3880 | keep | 0 | Feb | 2023 | 0.0026427 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-05 03:10 | 2023-02-05 09:59 | 14 | 6:49 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DEL T-1 @ T-2 Y AVERIA VIEJA DEL T-4 @ RISER SE QUEDA FUERA 2,3 Y 4 SE REFIRIO AL PERSONAL DE SOTERRADO 1 X 50 EN C/L Y 1 X 25 EN RISER HACIA T-1 Y SE REMPLAZO BUSHING DEL T-1 | B23020500001 | New_Event | UG Cable Fault | Include | Include | Equipment | 409 | 2023-02-05 | 5726 | keep | 0 | Feb | 2023 | 0.0039 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-02-05 03:56 | 2023-02-05 08:51 | 12 | 4:55 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | A23020500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 295 | 2023-02-05 | 3540 | keep | 0 | Feb | 2023 | 0.0024111 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-02-05 04:42 | 2023-02-05 08:25 | 10 | 3:43 | P | NO SE REPORTO CAUSA | 2 X 15 EN XMR | R23020500005 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 223 | 2023-02-05 | 2230 | keep | 0 | Feb | 2023 | 0.0015188 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-02-05 05:50 | 2023-02-05 09:58 | 90 | 4:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23020500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-02-05 | 22320 | keep | 0 | Feb | 2023 | 0.015202 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2023-02-05 05:55 | 2023-02-05 09:00 | 1 | 3:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23020500002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 185 | 2023-02-05 | 185 | keep | 0 | Feb | 2023 | 0.000126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-05 06:16 | 2023-02-05 09:30 | 60 | 3:14 | P | DESGANCHE | DESGANCHE Y 1 X 50 EN C/L | R23020500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-02-05 | 11640 | keep | 0 | Feb | 2023 | 0.007928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-02-05 06:20 | 2023-02-05 07:15 | 120 | 0:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23020500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-02-05 | 6600 | keep | 0 | Feb | 2023 | 0.0044952 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2023-02-05 06:25 | 2023-02-05 10:50 | 60 | 4:25 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 1 X 25 EN CORTE DE LINEA SE REPARO BAJANTE | M23020500003 | New_Event | Primary Wire Break | Include | Include | Equipment | 265 | 2023-02-05 | 15900 | keep | 0 | Feb | 2023 | 0.010829 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-02-05 06:26 | 2023-02-05 09:00 | 130 | 2:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA LLUVIAS | C23020500011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 154 | 2023-02-05 | 20020 | keep | 0 | Feb | 2023 | 0.013636 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
PONCE | 2023-02-05 06:52 | 2023-02-05 06:53 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23020500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 2113 | keep | 0 | Feb | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
VEGA BAJA | 2023-02-05 07:13 | 2023-02-05 08:43 | 25 | 1:30 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR RATON CRUZANDO CON PARARRAYO | A23020500011 | New_Event | Animals | Include | Include | Wildlife | 90 | 2023-02-05 | 2250 | keep | 0 | Feb | 2023 | 0.0015325 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-05 07:17 | 2023-02-05 07:19 | 1483 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 30% POR 1336-09 | S23020500009 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-05 | 2966 | keep | 0 | Feb | 2023 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-02-05 07:17 | 2023-02-05 07:19 | 1531 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 15% POR 1336-09 | S23020500009 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-05 | 3062 | keep | 0 | Feb | 2023 | 0.0020855 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-02-05 07:17 | 2023-02-05 07:19 | 312 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 5% POR 1336-09 | S23020500009 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-05 | 624 | keep | 0 | Feb | 2023 | 0.000425 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-02-05 07:17 | 2023-02-05 07:19 | 4232 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 80% CARGA POR 1336-09 | S23020500009 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-05 | 8464 | keep | 0 | Feb | 2023 | 0.0057648 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
SAN JUAN | 2023-02-05 07:17 | 2023-02-05 07:19 | 207 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1336-08 LLEVA 15% DEL 1204-05 LLEVA 5% DEL 1336-07 Y LLEVA 30% DEL 1204-04 | S23020500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-05 | 414 | keep | 0 | Feb | 2023 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
MAYAGÃœEZ | 2023-02-05 07:20 | 2023-02-05 11:30 | 30 | 4:10 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23020500005 | New_Event | Animals | Include | Include | Wildlife | 250 | 2023-02-05 | 7500 | keep | 0 | Feb | 2023 | 0.0051082 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-02-05 07:26 | 2023-02-05 07:27 | 688 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23020500068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 688 | keep | 0 | Feb | 2023 | 0.00046859 | 0.00046859 | Momentary | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2023-02-05 07:26 | 2023-02-05 07:27 | 658 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23020500068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 658 | keep | 0 | Feb | 2023 | 0.00044816 | 0.00044816 | Momentary | FALSE | FALSE | Not_TMED_Event | 658
BAYAMON | 2023-02-05 07:35 | 2023-02-05 07:36 | 1526 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 POR NIDO DE AVE EN DORADO TC | B23020500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 1526 | keep | 0 | Feb | 2023 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
BAYAMON | 2023-02-05 07:35 | 2023-02-05 07:36 | 308 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 POR NIDO DE AVE EN DORADO TC | B23020500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 308 | keep | 0 | Feb | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-02-05 07:35 | 2023-02-05 07:36 | 1397 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 POR NIDO DE AVE EN DORADO TC | B23020500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 1397 | keep | 0 | Feb | 2023 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
BAYAMON | 2023-02-05 07:35 | 2023-02-05 07:36 | 2926 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 POR NIDO DE AVE EN DORADO TC | B23020500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 2926 | keep | 0 | Feb | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
BAYAMON | 2023-02-05 07:35 | 2023-02-05 07:36 | 27 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 POR NIDO DE AVE EN DORADO TC | B23020500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 27 | keep | 0 | Feb | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-02-05 07:35 | 2023-02-05 07:36 | 603 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 POR NIDO DE AVE EN DORADO TC | B23020500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 603 | keep | 0 | Feb | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-02-05 07:35 | 2023-02-05 07:36 | 6 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 POR NIDO DE AVE EN DORADO TC | B23020500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 6 | keep | 0 | Feb | 2023 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-05 07:35 | 2023-02-05 07:36 | 325 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 POR NIDO DE AVE EN DORADO TC | B23020500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 325 | keep | 0 | Feb | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-02-05 07:35 | 2023-02-05 07:36 | 172 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 POR NIDO DE AVE EN DORADO TC | B23020500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-05 | 172 | keep | 0 | Feb | 2023 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2023-02-05 08:25 | 2023-02-05 09:45 | 30 | 1:20 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRE TRANSFORMADOR PARA REMPLAZO DE BAJANTE SECUNDARIO Y 2 TOMAS | S23020500007 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 80 | 2023-02-05 | 2400 | keep | 0 | Feb | 2023 | 0.0016346 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-02-05 08:25 | 2023-02-05 09:55 | 5 | 1:30 | P | ANIMAL | 1 X 8 EN XMR CRUCE DE CULEBRA | B23020500010 | New_Event | Animals | Include | Include | Wildlife | 90 | 2023-02-05 | 450 | keep | 0 | Feb | 2023 | 0.00030649 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-02-05 08:29 | 2023-02-05 17:39 | 10 | 9:10 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA INSTALAR POSTE SECUNDARIO | P23020500071 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 550 | 2023-02-05 | 5500 | keep | 0 | Feb | 2023 | 0.003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-05 08:34 | 2023-02-05 10:41 | 70 | 2:07 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C23020500034 | New_Event | Animals | Include | Include | Wildlife | 127 | 2023-02-05 | 8890 | keep | 0 | Feb | 2023 | 0.0060549 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-02-05 09:03 | 2023-02-05 09:37 | 8 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | S23020400171 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-02-05 | 272 | keep | 0 | Feb | 2023 | 0.00018526 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-02-05 09:10 | 2023-02-05 13:18 | 50 | 4:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C23020500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-02-05 | 12400 | keep | 0 | Feb | 2023 | 0.0084456 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-05 09:27 | 2023-02-05 15:50 | 12 | 6:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5 KVA | B23020500017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 383 | 2023-02-05 | 4596 | keep | 0 | Feb | 2023 | 0.0031303 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-05 09:27 | 2023-02-05 16:45 | 30 | 7:18 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L PARA REMPLAZO POSTE PROYECTO FIONA | B23020500014 | New_Event | Primary Pole Failure | Include | Include | Equipment | 438 | 2023-02-05 | 13140 | keep | 0 | Feb | 2023 | 0.0089496 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-02-05 09:42 | 2023-02-05 15:06 | 120 | 5:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P23020500093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 324 | 2023-02-05 | 38880 | keep | 0 | Feb | 2023 | 0.026481 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
YAUCO | 2023-02-05 09:56 | 2023-02-05 12:26 | 60 | 2:30 | P | DESGANCHE | SE TERMINO DE ABRIR CORTE DE LINEA Y SE HIZO DESGANCHE MASIVO | P2302050097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-02-05 | 9000 | keep | 0 | Feb | 2023 | 0.0061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-02-05 09:57 | 2023-02-05 09:58 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2302050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 2722 | keep | 0 | Feb | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
BAYAMON | 2023-02-05 09:59 | 2023-02-05 17:25 | 30 | 7:26 | P | CABLE SOTERRADO AVERIADO | MEDIANTE GOI BY-230205-01 SE PREPARO PROVISIONAL AEREO | B23020500001 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 446 | 2023-02-05 | 13380 | keep | 0 | Feb | 2023 | 0.0091131 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-05 09:59 | 2023-02-05 12:03 | 11 | 2:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN C/L Y SE REEMPLAZO AISLADOR ROTO | B23020500020 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 124 | 2023-02-05 | 1364 | keep | 0 | Feb | 2023 | 0.00092901 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-02-05 10:08 | 2023-02-05 12:30 | 70 | 2:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020500018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-02-05 | 9940 | keep | 0 | Feb | 2023 | 0.0067701 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-02-05 10:09 | 2023-02-05 12:32 | 458 | 2:23 | P | DESGANCHE | 1 X 30 1 X 50 Y 1 X 65 EN DIFERENTES C/L Y DESGANCHE | R23020500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-02-05 | 65494 | keep | 0 | Feb | 2023 | 0.044608 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
FAJARDO | 2023-02-05 10:13 | 2023-02-05 10:14 | 1830 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23020500029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 1830 | keep | 0 | Feb | 2023 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
BARRANQUITAS | 2023-02-05 10:14 | 2023-02-05 11:47 | 40 | 1:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | C23020500052 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2023-02-05 | 3720 | keep | 0 | Feb | 2023 | 0.0025337 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-02-05 10:14 | 2023-02-05 13:11 | 25 | 2:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR FUERTES VIENTOS | A23020500021 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 177 | 2023-02-05 | 4425 | keep | 0 | Feb | 2023 | 0.0030138 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-02-05 10:15 | 2023-02-05 11:17 | 789 | 1:02 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR PRIMARIO PARTIDO Y SE CERRO INTELLIRUPTER. SE DIO SERVICIO A 350 CLIENTES | R23020500030 | New_Event | Primary Wire Break | Include | Include | Equipment | 62 | 2023-02-05 | 48918 | keep | 0 | Feb | 2023 | 0.033318 | 0.00053738 | Sustained | FALSE | FALSE | Not_TMED_Event | 789
YAUCO | 2023-02-05 10:25 | 2023-02-05 15:08 | 150 | 4:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23020500106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2023-02-05 | 42450 | keep | 0 | Feb | 2023 | 0.028913 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-02-05 10:36 | 2023-02-05 12:07 | 80 | 1:31 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23020500031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-02-05 | 7280 | keep | 0 | Feb | 2023 | 0.0049584 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-05 10:37 | 2023-02-05 12:12 | 50 | 1:35 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN C/L POR DESGANCHE | B23020500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-02-05 | 4750 | keep | 0 | Feb | 2023 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-02-05 10:48 | 2023-02-05 14:09 | 35 | 3:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | A23020500024 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 201 | 2023-02-05 | 7035 | keep | 0 | Feb | 2023 | 0.0047915 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2023-02-05 11:13 | 2023-02-05 13:24 | 100 | 2:11 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO CONDUCTOR ARRIADO | C23020500057 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 131 | 2023-02-05 | 13100 | keep | 0 | Feb | 2023 | 0.0089224 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-02-05 11:17 | 2023-02-05 12:05 | 439 | 0:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO Y SE LEVANTO CONDUCTOR PRIMARIO | R23020500030 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 48 | 2023-02-05 | 21072 | keep | 0 | Feb | 2023 | 0.014352 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-02-05 11:54 | 2023-02-05 14:22 | 1222 | 2:28 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE FIJO AISLADOR Y SE CERRO INTERRUPTOR | A23020500034 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 148 | 2023-02-05 | 180856 | keep | 0 | Feb | 2023 | 0.12318 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
VEGA BAJA | 2023-02-05 11:58 | 2023-02-05 15:24 | 25 | 3:26 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B23020500057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-02-05 | 5150 | keep | 0 | Feb | 2023 | 0.0035076 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2023-02-05 12:01 | 2023-02-05 13:25 | 7 | 1:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23020500037 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 84 | 2023-02-05 | 588 | keep | 0 | Feb | 2023 | 0.00040048 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-02-05 12:06 | 2023-02-05 12:07 | 1854 | 0:01 | T | DESGANCHE | RECIERRE | C23020500071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-05 | 1854 | keep | 0 | Feb | 2023 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
BARRANQUITAS | 2023-02-05 12:07 | 2023-02-05 14:51 | 135 | 2:44 | P | DESGANCHE | 2 X 80 EN C/L | C23020500075 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-02-05 | 22140 | keep | 0 | Feb | 2023 | 0.015079 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
VEGA BAJA | 2023-02-05 12:12 | 2023-02-05 14:11 | 30 | 1:59 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B23020500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-02-05 | 3570 | keep | 0 | Feb | 2023 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-02-05 12:17 | 2023-02-05 18:28 | 50 | 6:11 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO LINEA PRIMARIA ROTA | M23020500036 | New_Event | Primary Wire Break | Include | Include | Equipment | 371 | 2023-02-05 | 18550 | keep | 0 | Feb | 2023 | 0.012634 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-02-05 12:18 | 2023-02-05 15:00 | 30 | 2:42 | P | DESGANCHE | 1 X EN CORTE DE POR DESGANCHE | A23020500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-02-05 | 4860 | keep | 0 | Feb | 2023 | 0.0033101 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-05 12:20 | 2023-02-05 12:46 | 10 | 0:26 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR SE REPARO SECUNDARIA Y SE RETIRO ENREDADERA | S23020500026 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 26 | 2023-02-05 | 260 | keep | 0 | Feb | 2023 | 0.00017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-02-05 12:24 | 2023-02-05 12:25 | 2039 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | RECIERRE | P23020500130 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1 | 2023-02-05 | 2039 | keep | 0 | Feb | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2023-02-05 12:25 | 2023-02-05 16:04 | 50 | 3:39 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LIENA POR LINEAS ARRIADAS | P23020500162 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 219 | 2023-02-05 | 10950 | keep | 0 | Feb | 2023 | 0.007458 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-02-05 12:30 | 2023-02-05 13:30 | 4 | 1:00 | P | TRANSFORMADOR AVERIADO | ABRIO XMR PARA REMPLAZAR BUSHING SECUNDARIO | C23020500062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 60 | 2023-02-05 | 240 | keep | 0 | Feb | 2023 | 0.00016346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-02-05 12:32 | 2023-02-05 14:28 | 1 | 1:56 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23020500073 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-02-05 | 116 | keep | 0 | Feb | 2023 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-05 12:37 | 2023-02-05 12:38 | 1109 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23020500134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 1109 | keep | 0 | Feb | 2023 | 0.00075533 | 0.00075533 | Momentary | FALSE | FALSE | Not_TMED_Event | 1109
BARRANQUITAS | 2023-02-05 12:40 | 2023-02-05 14:48 | 5 | 2:08 | P | DESGANCHE | 1 X 30 EN C/L | C23020500076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-02-05 | 640 | keep | 0 | Feb | 2023 | 0.0004359 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-02-05 12:40 | 2023-02-05 14:45 | 8 | 2:05 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE CORRIGIO CONDICION DE CONECTOR CRUZANDO CON PERNO | M23020500041 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 125 | 2023-02-05 | 1000 | keep | 0 | Feb | 2023 | 0.0006811 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-05 12:51 | 2023-02-05 12:52 | 411 | 0:01 | P | DESGANCHE | RECERRE 30% DE SU CARGA POR 1204-01 | S23020500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-05 | 411 | keep | 0 | Feb | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2023-02-05 13:03 | 2023-02-05 21:01 | 6 | 7:58 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23020500045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 478 | 2023-02-05 | 2868 | keep | 0 | Feb | 2023 | 0.0019534 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-02-05 13:07 | 2023-02-05 17:42 | 100 | 4:35 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M23020500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2023-02-05 | 27500 | keep | 0 | Feb | 2023 | 0.01873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-05 13:11 | 2023-02-05 15:15 | 15 | 2:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO DE BARRA EN PEDESTAL | B23020500066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 124 | 2023-02-05 | 1860 | keep | 0 | Feb | 2023 | 0.0012668 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-02-05 13:14 | 2023-02-05 16:56 | 150 | 3:42 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN C/L RETEZO LINEA | C23020500082 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 222 | 2023-02-05 | 33300 | keep | 0 | Feb | 2023 | 0.02268 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-02-05 13:21 | 2023-02-06 11:20 | 175 | 21:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | A23020500059 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1319 | 2023-02-05 | 230825 | keep | 0 | Feb | 2023 | 0.15721 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
AGUADILLA | 2023-02-05 13:25 | 2023-02-05 15:45 | 150 | 2:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23020500054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-02-05 | 21000 | keep | 0 | Feb | 2023 | 0.014303 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-02-05 13:25 | 2023-02-05 16:07 | 77 | 2:42 | P | ANIMAL | 1 X 65 EN C/L SE RETIRO CULEBRA | B23020500070 | New_Event | Animals | Include | Include | Wildlife | 162 | 2023-02-05 | 12474 | keep | 0 | Feb | 2023 | 0.008496 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-02-05 13:29 | 2023-02-05 15:00 | 50 | 1:31 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23020500069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-02-05 | 4550 | keep | 0 | Feb | 2023 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-05 13:30 | 2023-02-05 16:00 | 15 | 2:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO POSTE PROYECTO FIONA | B23020500013 | New_Event | Primary Pole Failure | Include | Include | Equipment | 150 | 2023-02-05 | 2250 | keep | 0 | Feb | 2023 | 0.0015325 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-05 13:36 | 2023-02-05 14:28 | 1830 | 0:52 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR POR CONDUCTOR PRIMARIO EN EL SUELO Y SE CERRO POR SCADA. 35% EN SERVICIO SWF SJ-230205-51 | R23020500081 | New_Event | Primary Wire Break | Include | Include | Equipment | 52 | 2023-02-05 | 95160 | keep | 0 | Feb | 2023 | 0.064813 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
YAUCO | 2023-02-05 13:38 | 2023-02-05 16:11 | 60 | 2:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23020500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-02-05 | 9180 | keep | 0 | Feb | 2023 | 0.0062525 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-05 13:39 | 2023-02-05 14:39 | 414 | 1:00 | P | DESGANCHE | DISPARO DE BKR 1204-01 SE SECCIONALIZO PARA REALIZAR DESGANCHE LLEVA 30% DEL 1204-03 | S23020500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2023-02-05 | 24840 | keep | 0 | Feb | 2023 | 0.016918 | 0.00028197 | Sustained | FALSE | FALSE | Not_TMED_Event | 414
AGUADILLA | 2023-02-05 13:51 | 2023-02-05 15:12 | 100 | 1:21 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBU DE LAS LINEAS | M23020500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-02-05 | 8100 | keep | 0 | Feb | 2023 | 0.0055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-02-05 13:53 | 2023-02-05 17:47 | 30 | 3:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | C23020500089 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 234 | 2023-02-05 | 7020 | keep | 0 | Feb | 2023 | 0.0047813 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-05 13:54 | 2023-02-05 15:31 | 40 | 1:37 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23020500059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-02-05 | 3880 | keep | 0 | Feb | 2023 | 0.0026427 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-02-05 13:55 | 2023-02-05 16:30 | 29 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23020500106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2023-02-05 | 4495 | keep | 0 | Feb | 2023 | 0.0030615 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
ARECIBO | 2023-02-05 14:00 | 2023-02-05 17:26 | 60 | 3:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A23020500151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-02-05 | 12360 | keep | 0 | Feb | 2023 | 0.0084183 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-02-05 14:07 | 2023-02-05 18:32 | 1 | 4:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTE VIENTO | M23020500075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 265 | 2023-02-05 | 265 | keep | 0 | Feb | 2023 | 0.00018049 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-05 14:07 | 2023-02-05 21:05 | 40 | 6:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR | B23020500073 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 418 | 2023-02-05 | 16720 | keep | 0 | Feb | 2023 | 0.011388 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-02-05 14:08 | 2023-02-05 14:09 | 1093 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO HACE EVENTO NI DEJA CREARLO | P230205000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 1093 | keep | 0 | Feb | 2023 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
CAGUAS | 2023-02-05 14:10 | 2023-02-05 17:48 | 50 | 3:38 | P | DESGANCHE | 1 X 50 EN C/L | C23020500092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2023-02-05 | 10900 | keep | 0 | Feb | 2023 | 0.0074239 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-02-05 14:11 | 2023-02-05 17:00 | 1 | 2:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23020500077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-02-05 | 169 | keep | 0 | Feb | 2023 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-02-05 14:11 | 2023-02-05 15:55 | 40 | 1:44 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR BAMBUAS | A23020500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-02-05 | 4160 | keep | 0 | Feb | 2023 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-02-05 14:16 | 2023-02-05 15:57 | 30 | 1:41 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B23020500074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-02-05 | 3030 | keep | 0 | Feb | 2023 | 0.0020637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-02-05 14:22 | 2023-02-05 15:07 | 20 | 0:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA POR VIENTOS | A23020500056 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 45 | 2023-02-05 | 900 | keep | 0 | Feb | 2023 | 0.00061299 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2023-02-05 14:28 | 2023-02-05 18:32 | 1189 | 4:04 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO SWF SJ-230205-51 | R23020500081 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 244 | 2023-02-05 | 290116 | keep | 0 | Feb | 2023 | 0.1976 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-02-05 14:30 | 2023-02-05 16:36 | 100 | 2:06 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA PERSONA PRIVADA DEJO CAER RAMAS SOBRE LINEA | P23020500158 | New_Event | Damage From Public | Include | Include | Public | 126 | 2023-02-05 | 12600 | keep | 0 | Feb | 2023 | 0.0085818 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-05 14:30 | 2023-02-05 17:25 | 80 | 2:55 | P | DESGANCHE | 1 X 100, 1 X 80 EN C/L SE DESGANCHO | B23020500079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-02-05 | 14000 | keep | 0 | Feb | 2023 | 0.0095353 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-02-05 14:31 | 2023-02-05 16:22 | 26 | 1:51 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | S23020500080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-02-05 | 2886 | keep | 0 | Feb | 2023 | 0.0019656 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
YAUCO | 2023-02-05 14:31 | 2023-02-05 16:22 | 325 | 1:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LIENA DESGANCHE | P23020500160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-02-05 | 36075 | keep | 0 | Feb | 2023 | 0.024571 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-02-05 14:39 | 2023-02-05 15:10 | 21 | 0:31 | P | DESGANCHE | SE REALIZO DESGANCHE CON VARETA DESDE EL SUELO | S23020500052 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 31 | 2023-02-05 | 651 | keep | 0 | Feb | 2023 | 0.00044339 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-05 14:42 | 2023-02-05 14:43 | 888 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DE INTERRUPTOR ARBOL SOBRE LINEAS | M23020500088 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2023-02-05 | 888 | keep | 0 | Feb | 2023 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
HUMACAO | 2023-02-05 14:43 | 2023-02-05 14:44 | 3833 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23020500099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 3833 | keep | 0 | Feb | 2023 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
MAYAGÃœEZ | 2023-02-05 14:43 | 2023-02-05 17:34 | 100 | 2:51 | P | ARBOL SOBRE LINEA | 2 X 80 EN CORTE DE LINEA SE RETIRO ARBOL CAIDO SOBRE LAS LINEAS PRIMARIAS QUE ESTAN MAS BAJAS DE LO NORMAL | M23020500093 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 171 | 2023-02-05 | 17100 | keep | 0 | Feb | 2023 | 0.011647 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-02-05 14:45 | 2023-02-05 16:25 | 30 | 1:40 | P | CAUSAS EXTERNAS | 2 X 50 EN C/L CRUCE CON GLOBO | C23020500100 | New_Event | Damage From Public | Include | Include | Public | 100 | 2023-02-05 | 3000 | keep | 0 | Feb | 2023 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-02-05 14:48 | 2023-02-05 15:53 | 10 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONEXION EN BARRA DE PEDESTAL | P23020500166 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-02-05 | 650 | keep | 0 | Feb | 2023 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-05 15:07 | 2023-02-05 15:09 | 2466 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S2302050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-05 | 4932 | keep | 0 | Feb | 2023 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2023-02-05 15:14 | 2023-02-05 16:43 | 80 | 1:29 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23020500095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-02-05 | 7120 | keep | 0 | Feb | 2023 | 0.0048494 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-05 15:15 | 2023-02-05 15:16 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B23020500089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 4431 | keep | 0 | Feb | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BARRANQUITAS | 2023-02-05 15:16 | 2023-02-05 15:17 | 2565 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C2302050000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-05 | 2565 | keep | 0 | Feb | 2023 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2023-02-05 15:17 | 2023-02-05 15:55 | 1500 | 0:38 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO TRABAJADO CON EL GOI CG-230205-01 | C23020500109 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 38 | 2023-02-05 | 57000 | keep | 0 | Feb | 2023 | 0.038822 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
BAYAMON | 2023-02-05 15:21 | 2023-02-05 17:23 | 50 | 2:02 | P | DESGANCHE | 1 X 50 EN C/L POR DESGANCHE | B23020500092 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-02-05 | 6100 | keep | 0 | Feb | 2023 | 0.0041547 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-02-05 15:22 | 2023-02-05 17:10 | 400 | 1:48 | P | DESGANCHE | 1 X 100 EN CONVERTIDOR POR RAMA SOBRE LINEA | P23020500176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-02-05 | 43200 | keep | 0 | Feb | 2023 | 0.029423 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2023-02-05 15:24 | 2023-02-05 16:55 | 1 | 1:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23020500099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2023-02-05 | 91 | keep | 0 | Feb | 2023 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-05 15:44 | 2023-02-05 15:45 | 1606 | 0:01 | T | DESGANCHE | RECIERRE | C23020500124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-05 | 1606 | keep | 0 | Feb | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2023-02-05 15:45 | 2023-02-05 16:50 | 125 | 1:05 | P | DESGANCHE | 1 X 100 EN C/L | C23020500133 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 65 | 2023-02-05 | 8125 | keep | 0 | Feb | 2023 | 0.0055339 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
FAJARDO | 2023-02-05 15:53 | 2023-02-05 20:05 | 12 | 4:12 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | R23020500105 | New_Event | Animals | Include | Include | Wildlife | 252 | 2023-02-05 | 3024 | keep | 0 | Feb | 2023 | 0.0020596 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-02-05 15:55 | 2023-02-05 17:18 | 2565 | 1:23 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR PARA CERRAR PUENTE EN EL TRONCAL | C23020500109 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 83 | 2023-02-05 | 212895 | keep | 0 | Feb | 2023 | 0.145 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-02-05 15:57 | 2023-02-05 18:34 | 3 | 2:37 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M23020500112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-02-05 | 471 | keep | 0 | Feb | 2023 | 0.0003208 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-02-05 16:04 | 2023-02-05 17:44 | 9 | 1:40 | P | DESGANCHE | 1 X 50 EN C/L | C23020500136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-02-05 | 900 | keep | 0 | Feb | 2023 | 0.00061299 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
GUAYAMA | 2023-02-05 16:11 | 2023-02-05 17:08 | 25 | 0:57 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA RAMA SOBRE LINEA | P23020500194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2023-02-05 | 1425 | keep | 0 | Feb | 2023 | 0.00097056 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-02-05 16:14 | 2023-02-05 18:35 | 15 | 2:21 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C23020500142 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-02-05 | 2115 | keep | 0 | Feb | 2023 | 0.0014405 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-02-05 16:18 | 2023-02-06 14:00 | 3 | 21:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CABLE SECUNDARIO Y SE CERRO TRANSFORMADOR | M23020500125 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1302 | 2023-02-05 | 3906 | keep | 0 | Feb | 2023 | 0.0026604 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2023-02-05 16:28 | 2023-02-05 17:27 | 50 | 0:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL Y TIEMPO | P23020500196 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 59 | 2023-02-05 | 2950 | keep | 0 | Feb | 2023 | 0.0020092 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-02-05 16:31 | 2023-02-05 20:58 | 100 | 4:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M23020500122 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2023-02-05 | 26700 | keep | 0 | Feb | 2023 | 0.018185 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-02-05 16:41 | 2023-02-05 18:49 | 2 | 2:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO LINEA SECUNDARIA | R23020500108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 128 | 2023-02-05 | 256 | keep | 0 | Feb | 2023 | 0.00017436 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-02-05 16:42 | 2023-02-05 18:00 | 150 | 1:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M23020500124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-02-05 | 11700 | keep | 0 | Feb | 2023 | 0.0079688 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-02-05 16:49 | 2023-02-05 18:08 | 100 | 1:19 | P | DESGANCHE | 1 X 140 EN C/L DESGANCHE | S23020500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-02-05 | 7900 | keep | 0 | Feb | 2023 | 0.0053807 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-02-05 17:07 | 2023-02-06 08:40 | 30 | 15:33 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23020500073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 933 | 2023-02-05 | 27990 | keep | 0 | Feb | 2023 | 0.019064 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-02-05 17:08 | 2023-02-06 00:09 | 210 | 7:01 | P | DESGANCHE | 2 X 50 EN C/L | C23020500157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2023-02-05 | 88410 | keep | 0 | Feb | 2023 | 0.060216 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
VEGA BAJA | 2023-02-05 17:20 | 2023-02-05 18:39 | 15 | 1:19 | P | TRANSFORMADOR AVERIADO | SE ABRE MONTURA DE TRANSFORMADOR PARA CAMBIO DE TRANSFORMADOR AVERIA 37.5 KVA | A23020500025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 79 | 2023-02-05 | 1185 | keep | 0 | Feb | 2023 | 0.0008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-05 17:22 | 2023-02-05 19:15 | 10 | 1:53 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE SECUNDARIO | S23020500108 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 113 | 2023-02-05 | 1130 | keep | 0 | Feb | 2023 | 0.00076964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-02-05 17:23 | 2023-02-05 19:39 | 25 | 2:16 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R23020500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-02-05 | 3400 | keep | 0 | Feb | 2023 | 0.0023157 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-05 17:47 | 2023-02-05 21:55 | 12 | 4:08 | P | CONDUCTOR ROTO O ABIERTO | 1X10 EN XMR SE CERRO PUENTE PRIMARIO | S23020500112 | New_Event | Primary Wire Break | Include | Include | Equipment | 248 | 2023-02-05 | 2976 | keep | 0 | Feb | 2023 | 0.0020269 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-05 17:51 | 2023-02-05 20:43 | 80 | 2:52 | P | ARBOL SOBRE LINEA | 3 X 80 EN C/L SE RETIRO ARBOL SOBRE LINEA PRIMARIA | S23020500115 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 172 | 2023-02-05 | 13760 | keep | 0 | Feb | 2023 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-02-05 17:53 | 2023-02-05 18:35 | 167 | 0:42 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L SE RELOCALIZO NEUTRAL PRIMARIO | C23020500176 | New_Event | Primary Wire Break | Include | Include | Equipment | 42 | 2023-02-05 | 7014 | keep | 0 | Feb | 2023 | 0.0047772 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
BARRANQUITAS | 2023-02-05 18:00 | 2023-02-05 19:44 | 50 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23020500179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-02-05 | 5200 | keep | 0 | Feb | 2023 | 0.0035417 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-02-05 18:10 | 2023-02-05 18:55 | 4 | 0:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO CON ESCAPE DE ACEITE DE 50KVA POR LA MISMA CAPACIDAD | M23020500133 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2023-02-05 | 180 | keep | 0 | Feb | 2023 | 0.0001226 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-02-05 18:12 | 2023-02-05 18:13 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 3332 | keep | 0 | Feb | 2023 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
AGUADILLA | 2023-02-05 18:15 | 2023-02-05 18:16 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23020500135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 1192 | keep | 0 | Feb | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
SAN JUAN | 2023-02-05 18:34 | 2023-02-05 20:34 | 5 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23020500123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2023-02-05 | 600 | keep | 0 | Feb | 2023 | 0.00040866 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-02-05 18:47 | 2023-02-05 21:57 | 300 | 3:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CL SE REMPLAZO CAJA PRIMARIA EN CL | P23020500210 | New_Event | Cutout Failure | Include | Include | Equipment | 190 | 2023-02-05 | 57000 | keep | 0 | Feb | 2023 | 0.038822 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2023-02-05 18:58 | 2023-02-05 20:18 | 14 | 1:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R23020500114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2023-02-05 | 1120 | keep | 0 | Feb | 2023 | 0.00076283 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
FAJARDO | 2023-02-05 19:24 | 2023-02-05 20:52 | 10 | 1:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23020500117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2023-02-05 | 880 | keep | 0 | Feb | 2023 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-02-05 19:40 | 2023-02-05 19:51 | 10 | 0:11 | P | DESGANCHE | 1 X 40 EN C/L | C23020500212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 11 | 2023-02-05 | 110 | keep | 0 | Feb | 2023 | 7.492e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-05 19:41 | 2023-02-05 21:40 | 10 | 1:59 | P | DESGANCHE | 1 X 50 EN RISER DESGANCHE | S23020500128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-02-05 | 1190 | keep | 0 | Feb | 2023 | 0.0008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-05 19:55 | 2023-02-05 23:32 | 18 | 3:37 | P | PARARRAYOS DEFECTUOSO | 1X20 EN C/L SE RETIRO PARRAYO DEFECTUOSO | B23020500134 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 217 | 2023-02-05 | 3906 | keep | 0 | Feb | 2023 | 0.0026604 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
HUMACAO | 2023-02-05 20:30 | 2023-02-05 23:34 | 400 | 3:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | C23020500232 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2023-02-05 | 73600 | keep | 0 | Feb | 2023 | 0.050129 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BARRANQUITAS | 2023-02-05 20:43 | 2023-02-05 22:11 | 1565 | 1:28 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO TRABAJADO CON EL GOI CG-230205-02 | C23020500236 | New_Event | Primary Wire Break | Include | Include | Equipment | 88 | 2023-02-05 | 137720 | keep | 0 | Feb | 2023 | 0.0938 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
BAYAMON | 2023-02-05 20:45 | 2023-02-06 11:55 | 11 | 15:10 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO | B23020500139 | New_Event | Service Transformer Failure | Include | Include | Equipment | 910 | 2023-02-05 | 10010 | keep | 0 | Feb | 2023 | 0.0068178 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-02-05 21:04 | 2023-02-06 07:40 | 1 | 10:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA Y 1 X 30 EN RISER MAL TIEMPO LLUVIA | C23020500244 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 636 | 2023-02-05 | 636 | keep | 0 | Feb | 2023 | 0.00043318 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-05 21:20 | 2023-02-06 07:49 | 20 | 10:29 | P | CONDUCTOR ROTO O ABIERTO | SE SUBIO ALAMBRE PRIMARIO Y SE CERRO PUENTE | P23020500229 | New_Event | Primary Wire Break | Include | Include | Equipment | 629 | 2023-02-05 | 12580 | keep | 0 | Feb | 2023 | 0.0085682 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-05 21:24 | 2023-02-06 12:30 | 3 | 15:06 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ELIMINO POSTE SECUNDARIO Y SE RELOCALIZO LINEA | B23020500141 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 906 | 2023-02-05 | 2718 | keep | 0 | Feb | 2023 | 0.0018512 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-02-05 21:47 | 2023-02-05 21:48 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 652 | keep | 0 | Feb | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
YAUCO | 2023-02-05 21:57 | 2023-02-05 21:58 | 508 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR AL CERRAR CL SE REMPLAZO CAJA PRIMARIA | P23020500232 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-05 | 508 | keep | 0 | Feb | 2023 | 0.000346 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-02-05 21:57 | 2023-02-05 22:43 | 64 | 0:46 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 5402-01 CON CARGA DEL 5402-02 | P23020500232 | New_Event | Feeder Load Transferred | Include | Include | Other | 46 | 2023-02-05 | 2944 | keep | 0 | Feb | 2023 | 0.0020051 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
YAUCO | 2023-02-05 21:58 | 2023-02-05 22:33 | 300 | 0:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CL SE REMPLAZO CAJA PRIMARIA EN CL | P23020500210 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 35 | 2023-02-05 | 10500 | keep | 0 | Feb | 2023 | 0.0071515 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2023-02-05 22:11 | 2023-02-05 23:21 | 2565 | 1:10 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO EL BKR PARA CERRAR PUENTE EN EL TRONCAL | C23020500236 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 70 | 2023-02-05 | 179550 | keep | 0 | Feb | 2023 | 0.12229 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-02-05 23:20 | 2023-02-05 23:21 | 1717 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P23020500235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 1717 | keep | 0 | Feb | 2023 | 0.0011694 | 0.0011694 | Momentary | FALSE | FALSE | Not_TMED_Event | 1717
BAYAMON | 2023-02-05 23:32 | 2023-02-05 23:33 | 27 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23020500144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 27 | keep | 0 | Feb | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
PONCE | 2023-02-05 23:33 | 2023-02-05 23:34 | 1717 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P23020500236 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 1717 | keep | 0 | Feb | 2023 | 0.0011694 | 0.0011694 | Momentary | FALSE | FALSE | Not_TMED_Event | 1717
BARRANQUITAS | 2023-02-05 23:47 | 2023-02-05 23:48 | 2280 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-05 | 2280 | keep | 0 | Feb | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2023-02-05 23:51 | 2023-02-06 07:14 | 1494 | 7:23 | P | CAUSAS EXTERNAS | SE REEMPLAZO MACHETE AVERIADO POR IMPACTO DE VEHICULO, CON CG-230206-01 | C23020500266 | New_Event | Damage From Public | Include | Include | Public | 443 | 2023-02-05 | 661842 | keep | 0 | Feb | 2023 | 0.45078 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
BARRANQUITAS | 2023-02-06 00:04 | 2023-02-06 10:08 | 35 | 10:04 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | C23020600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 604 | 2023-02-06 | 21140 | keep | 0 | Feb | 2023 | 0.014398 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-02-06 01:43 | 2023-02-06 01:44 | 2280 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302060000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-06 | 2280 | keep | 0 | Feb | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2023-02-06 02:02 | 2023-02-06 02:03 | 2280 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302060000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-06 | 2280 | keep | 0 | Feb | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2023-02-06 02:51 | 2023-02-06 02:52 | 2280 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302060000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-06 | 2280 | keep | 0 | Feb | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
GUAYAMA | 2023-02-06 03:42 | 2023-02-06 11:42 | 10 | 8:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA AVERIADA | P23020600003 | New_Event | Secondary Wire Break | Include | Include | Equipment | 480 | 2023-02-06 | 4800 | keep | 0 | Feb | 2023 | 0.0032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-06 04:17 | 2023-02-06 04:19 | 3957 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23020600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-06 | 7914 | keep | 0 | Feb | 2023 | 0.0053902 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
VEGA BAJA | 2023-02-06 05:07 | 2023-02-06 08:00 | 50 | 2:53 | P | SECUNDARIA/DESGANCHE | 1 X 50 EN CORTE DE LINEA SE DESGANCHO EN LINEA SECUNDARIAS | A23020600002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 173 | 2023-02-06 | 8650 | keep | 0 | Feb | 2023 | 0.0058915 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-02-06 05:28 | 2023-02-06 07:45 | 50 | 2:17 | P | DESGANCHE | 1 X 40 Y 1X 30 EN CORTES DE LINEA DESGANCHE | C23020600069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-02-06 | 6850 | keep | 0 | Feb | 2023 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-02-06 05:28 | 2023-02-06 05:29 | 4381 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23020600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-06 | 4381 | keep | 0 | Feb | 2023 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
GUAYAMA | 2023-02-06 05:40 | 2023-02-06 12:19 | 13 | 6:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | P23020600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 399 | 2023-02-06 | 5187 | keep | 0 | Feb | 2023 | 0.0035328 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2023-02-06 06:53 | 2023-02-06 09:25 | 150 | 2:32 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23020600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2023-02-06 | 22800 | keep | 0 | Feb | 2023 | 0.015529 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-02-06 07:20 | 2023-02-06 07:22 | 1106 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL 60% X 1529-15 | S2302060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-06 | 2212 | keep | 0 | Feb | 2023 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-02-06 07:20 | 2023-02-06 07:22 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 60% 1346-02 | S2302060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-06 | 3604 | keep | 0 | Feb | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
HUMACAO | 2023-02-06 07:21 | 2023-02-06 07:22 | 800 | 0:01 | P | ALIMENTADOR AMARRADO | INTERRUPTOR 3205-07 RECERRO LLEVA 800 CLIENTES DEL 2603-08 | C23020700353 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-06 | 800 | keep | 0 | Feb | 2023 | 0.00054488 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
CAGUAS | 2023-02-06 07:21 | 2023-02-06 07:22 | 4634 | 0:01 | T | CAUSAS EXTERNAS | RECERRO INTERRUPTOR EN SERVICIO | C23020600122 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-02-06 | 4634 | keep | 0 | Feb | 2023 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2023-02-06 07:22 | 2023-02-06 09:27 | 80 | 2:05 | P | CAUSAS EXTERNAS | 1 X 140 EN C/L CAUSAS EXTERNAS CAMION IMPACTO POSTE. | C23020600124 | 1st_after_momentary | Damage From Public | Include | Include | Public | 125 | 2023-02-06 | 10000 | keep | 0 | Feb | 2023 | 0.006811 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-02-06 07:24 | 2023-02-06 13:05 | 6 | 5:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE TRANSFORMADOR | P23020600008 | New_Event | Primary Wire Break | Include | Include | Equipment | 341 | 2023-02-06 | 2046 | keep | 0 | Feb | 2023 | 0.0013935 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-02-06 07:27 | 2023-02-06 09:40 | 50 | 2:13 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23020600126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-02-06 | 6650 | keep | 0 | Feb | 2023 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-02-06 07:36 | 2023-02-06 09:15 | 3 | 1:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23020600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-02-06 | 297 | keep | 0 | Feb | 2023 | 0.00020229 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-06 07:44 | 2023-02-06 07:45 | 320 | 0:01 | T | ANIMAL | DISPARO Y SE CERRO POR CONTROL | B23020600003 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-06 | 320 | keep | 0 | Feb | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-02-06 07:45 | 2023-02-06 18:34 | 1 | 10:49 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | B23020600091 | 1st_after_momentary | Animals | Include | Include | Wildlife | 649 | 2023-02-06 | 649 | keep | 0 | Feb | 2023 | 0.00044203 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-06 07:52 | 2023-02-06 12:25 | 1 | 4:33 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | S23020600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2023-02-06 | 273 | keep | 0 | Feb | 2023 | 0.00018594 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-06 07:52 | 2023-02-06 07:53 | 1702 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C23020600135 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-06 | 1702 | keep | 0 | Feb | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-02-06 07:53 | 2023-02-06 10:48 | 120 | 2:55 | P | ANIMAL | 1 X 80 Y 1 X 65 EN CORTES DE LINEA CRUCE POR AVE | C23020600138 | 1st_after_momentary | Animals | Include | Include | Wildlife | 175 | 2023-02-06 | 21000 | keep | 0 | Feb | 2023 | 0.014303 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2023-02-06 08:00 | 2023-02-06 13:00 | 9 | 5:00 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23020600137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-02-06 | 2700 | keep | 0 | Feb | 2023 | 0.001839 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-02-06 08:07 | 2023-02-06 13:58 | 6 | 5:51 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M23020600012 | New_Event | Primary Wire Break | Include | Include | Equipment | 351 | 2023-02-06 | 2106 | keep | 0 | Feb | 2023 | 0.0014344 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-06 08:08 | 2023-02-06 11:44 | 20 | 3:36 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL Y SE CERRO CORTE LINEA | S23020600012 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 216 | 2023-02-06 | 4320 | keep | 0 | Feb | 2023 | 0.0029423 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-06 08:13 | 2023-02-06 20:52 | 1 | 12:39 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA Y SE REPARO BAJANTE DE CAJA A LINEA | B23020600005 | New_Event | Primary Wire Break | Include | Include | Equipment | 759 | 2023-02-06 | 759 | keep | 0 | Feb | 2023 | 0.00051695 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-02-06 08:20 | 2023-02-06 14:48 | 1 | 6:28 | P | TRANSFORMADOR AVERIADO | SE ABRE MONTURA DE TRANSFORMADOR PARA CAMBIO DE TRANSFORMADOR QUEMADO DE 25KVA | A23020600005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 388 | 2023-02-06 | 388 | keep | 0 | Feb | 2023 | 0.00026427 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-06 08:22 | 2023-02-06 15:30 | 7 | 7:08 | P | ANIMAL | 1 X 10 EN XMR CRUCE X REPTIL | R23020600051 | New_Event | Animals | Include | Include | Wildlife | 428 | 2023-02-06 | 2996 | keep | 0 | Feb | 2023 | 0.0020406 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-02-06 08:24 | 2023-02-06 11:39 | 1 | 3:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN CORTE DE LINEA FUERTE VIENTO | M23020600017 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 195 | 2023-02-06 | 195 | keep | 0 | Feb | 2023 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-06 08:24 | 2023-02-06 14:50 | 1 | 6:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO POR UNO DE 10KVA | B23020600038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 386 | 2023-02-06 | 386 | keep | 0 | Feb | 2023 | 0.0002629 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-06 08:26 | 2023-02-06 08:27 | 2280 | 0:01 | T | DESGANCHE | RECIERRE | C2302060000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-06 | 2280 | keep | 0 | Feb | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
HUMACAO | 2023-02-06 08:28 | 2023-02-06 10:06 | 1 | 1:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMDOR PARA REEMPLAZO DE TOMA SECUNDARIA Y SE REEMPLAZARON CONECTORES SULFATADOS EN TOMAS. | C23020600149 | New_Event | Secondary Wire Break | Include | Include | Equipment | 98 | 2023-02-06 | 98 | keep | 0 | Feb | 2023 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-06 08:31 | 2023-02-06 14:52 | 25 | 6:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE 100A CON 1 X 40 EN CORTE DE LINEA | P23020600018 | New_Event | Cutout Failure | Include | Include | Equipment | 381 | 2023-02-06 | 9525 | keep | 0 | Feb | 2023 | 0.0064874 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-06 08:31 | 2023-02-06 08:45 | 18 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA AJUSTAR BARRA EN PEDESTAL | B23020600009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2023-02-06 | 252 | keep | 0 | Feb | 2023 | 0.00017164 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-02-06 08:38 | 2023-02-06 08:39 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23020600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-06 | 4641 | keep | 0 | Feb | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2023-02-06 08:39 | 2023-02-06 10:30 | 50 | 1:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23020600036 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 111 | 2023-02-06 | 5550 | keep | 0 | Feb | 2023 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-06 08:54 | 2023-02-06 09:55 | 1 | 1:01 | P | DESGANCHE | 1 X 25 EN C/L 1 X 15 EN MONTURA | B23020600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2023-02-06 | 61 | keep | 0 | Feb | 2023 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-06 09:04 | 2023-02-06 10:03 | 15 | 0:59 | P | ANIMAL | 1 X 20 EN CORTE DE LINEA CRUCE CON AVE | R23020600011 | New_Event | Animals | Include | Include | Wildlife | 59 | 2023-02-06 | 885 | keep | 0 | Feb | 2023 | 0.00060277 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-06 09:53 | 2023-02-06 09:55 | 513 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL 1111-01 20% 1118-10 | S2302060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-06 | 1026 | keep | 0 | Feb | 2023 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-02-06 09:53 | 2023-02-06 09:55 | 2782 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 20% DEL 1111-01 | S2302060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-06 | 5564 | keep | 0 | Feb | 2023 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2023-02-06 10:00 | 2023-02-06 15:50 | 50 | 5:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | B23020600017 | New_Event | Primary Pole Failure | Include | Include | Equipment | 350 | 2023-02-06 | 17500 | keep | 0 | Feb | 2023 | 0.011919 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-06 10:03 | 2023-02-06 11:50 | 10 | 1:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B23020600031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 107 | 2023-02-06 | 1070 | keep | 0 | Feb | 2023 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-02-06 10:04 | 2023-02-06 10:07 | 3296 | 0:03 | T | DESGANCHE | DISPARO SE CERRO POR CONTROL. | C2302060000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-02-06 | 9888 | keep | 0 | Feb | 2023 | 0.0067347 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
AGUADILLA | 2023-02-06 10:05 | 2023-02-06 12:10 | 3 | 2:05 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | M23020600044 | New_Event | Primary Wire Break | Include | Include | Equipment | 125 | 2023-02-06 | 375 | keep | 0 | Feb | 2023 | 0.00025541 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-02-06 10:08 | 2023-02-06 10:24 | 3296 | 0:16 | T | DESGANCHE | SE RETIRO HOJA DE YAGRUMO, CERRADO POR CONTROL | C23020600200 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 16 | 2023-02-06 | 52736 | keep | 0 | Feb | 2023 | 0.035918 | 0.0022449 | Sustained | FALSE | FALSE | Not_TMED_Event | 3296
SAN JUAN | 2023-02-06 10:10 | 2023-02-06 12:45 | 50 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 65 C/L | S23020600025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2023-02-06 | 7750 | keep | 0 | Feb | 2023 | 0.0052785 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-02-06 10:10 | 2023-02-06 10:40 | 15 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23020600001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-02-06 | 450 | keep | 0 | Feb | 2023 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-06 10:29 | 2023-02-06 14:20 | 1 | 3:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y 2 X 5 EN XMR | B23020600035 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2023-02-06 | 231 | keep | 0 | Feb | 2023 | 0.00015733 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-06 10:34 | 2023-02-06 12:18 | 4 | 1:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON 3 BARRAS EN PEDESTAL Y SE RECONECTO TOMA DE CLIENTE. | C23020600206 | New_Event | Secondary Wire Break | Include | Include | Equipment | 104 | 2023-02-06 | 416 | keep | 0 | Feb | 2023 | 0.00028334 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-02-06 10:40 | 2023-02-06 12:22 | 12 | 1:42 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE. | C23020600213 | New_Event | Animals | Include | Include | Wildlife | 102 | 2023-02-06 | 1224 | keep | 0 | Feb | 2023 | 0.00083366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-02-06 10:53 | 2023-02-06 11:02 | 3744 | 0:09 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO INTERRUPTOR SE VERIFICA CON PERSONAL TRABAJANDO EN LA LINEA Y SE LE DA PRUEBA QUEDANDO EN SERVICIO | P23020600045 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 9 | 2023-02-06 | 33696 | keep | 0 | Feb | 2023 | 0.02295 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
FAJARDO | 2023-02-06 11:27 | 2023-02-06 13:50 | 16 | 2:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L REMPLAZO CAJA QUEMADA | R23020600022 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2023-02-06 | 2288 | keep | 0 | Feb | 2023 | 0.0015583 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-02-06 11:47 | 2023-02-06 11:55 | 7 | 0:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO CAJA PRIMARIA DE TRANSFORMADOR SEMI ABIERTA | R23020600023 | New_Event | Cutout Failure | Include | Include | Equipment | 8 | 2023-02-06 | 56 | keep | 0 | Feb | 2023 | 3.8141e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-02-06 11:50 | 2023-02-06 12:03 | 2280 | 0:13 | T | DESGANCHE | DISPARO INTERRUPTOR SE RETIRO BAMBUA DE LA LINEA CON VARETA, CERRADO POR CONTROL. | C23020600228 | New_Event | Vegetation Contact | Include | Include | Vegetation | 13 | 2023-02-06 | 29640 | keep | 0 | Feb | 2023 | 0.020188 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
SAN JUAN | 2023-02-06 11:52 | 2023-02-06 15:57 | 44 | 4:05 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S23020600056 | New_Event | Primary Wire Break | Include | Include | Equipment | 245 | 2023-02-06 | 10780 | keep | 0 | Feb | 2023 | 0.0073422 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BARRANQUITAS | 2023-02-06 12:18 | 2023-02-06 12:22 | 2280 | 0:04 | T | DESGANCHE | DISPARO INTERRUPTOR SE RETIRO BAMBUA DE LA LINEA, CERRADO POR CONTROL SE NORMALIZO R/R | C2302060000X | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4 | 2023-02-06 | 9120 | keep | 0 | Feb | 2023 | 0.0062116 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-06 12:24 | 2023-02-06 14:20 | 18 | 1:56 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO | B23020600055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 116 | 2023-02-06 | 2088 | keep | 0 | Feb | 2023 | 0.0014221 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2023-02-06 12:45 | 2023-02-06 17:23 | 55 | 4:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23020600056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 278 | 2023-02-06 | 15290 | keep | 0 | Feb | 2023 | 0.010414 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
GUAYAMA | 2023-02-06 13:26 | 2023-02-06 17:26 | 10 | 4:00 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA POR LINEAS ARRIADAS | P23020600066 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 240 | 2023-02-06 | 2400 | keep | 0 | Feb | 2023 | 0.0016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-06 13:33 | 2023-02-06 16:02 | 1 | 2:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23020600255 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2023-02-06 | 149 | keep | 0 | Feb | 2023 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-06 13:37 | 2023-02-06 16:15 | 113 | 2:38 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | C23020600258 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-02-06 | 17854 | keep | 0 | Feb | 2023 | 0.01216 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
CANOVANAS | 2023-02-06 13:55 | 2023-02-06 13:56 | 7621 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R23020600038 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-06 | 7621 | keep | 0 | Feb | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
FAJARDO | 2023-02-06 13:56 | 2023-02-06 14:23 | 1 | 0:27 | P | DESGANCHE | DESGANCHO Y FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | R23020600025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2023-02-06 | 27 | keep | 0 | Feb | 2023 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-06 13:56 | 2023-02-06 17:02 | 250 | 3:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN C/L REMPLAZO 2 CAJAS QUEMADAS | R23020600040 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 186 | 2023-02-06 | 46500 | keep | 0 | Feb | 2023 | 0.031671 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2023-02-06 14:00 | 2023-02-06 14:01 | 1117 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR CON LA CARGA DEL 6404-02 | M23020600097 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-06 | 1117 | keep | 0 | Feb | 2023 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2023-02-06 14:00 | 2023-02-06 14:01 | 1671 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR CON LA CARGA DEL 6404-02 | M23020600097 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-06 | 1671 | keep | 0 | Feb | 2023 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
MAYAGÃœEZ | 2023-02-06 14:00 | 2023-02-06 14:07 | 527 | 0:07 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR DEBIDO A PUENTE PRIMARIO ALIMENTADOR 6404-01 CRUZADO CON ALIMENTADOR 6404-03 | M23020600096 | New_Event | Primary Wire Break | Include | Include | Equipment | 7 | 2023-02-06 | 3689 | keep | 0 | Feb | 2023 | 0.0025126 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2023-02-06 14:01 | 2023-02-06 17:40 | 374 | 3:39 | P | CONDUCTOR ROTO O ABIERTO | GOI MY-230206-01A PARA CERRAR PUENTE EN TRONCAL PRIMARIO 6404-01 | M23020600087 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 219 | 2023-02-06 | 81906 | keep | 0 | Feb | 2023 | 0.055786 | 0.00025473 | Sustained | FALSE | FALSE | Not_TMED_Event | 374
MAYAGÃœEZ | 2023-02-06 14:01 | 2023-02-06 17:40 | 557 | 3:39 | P | ALIMENTADOR AMARRADO | GOI MY-230206-01A PARA CERRAR PUENTE EN TRONCAL PRIMARIO 6404-01 CON LA CARGA DEL 6404-02 | M23020600087 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 219 | 2023-02-06 | 121983 | keep | 0 | Feb | 2023 | 0.083082 | 0.00037937 | Sustained | FALSE | FALSE | Not_TMED_Event | 557
CAGUAS | 2023-02-06 14:20 | 2023-02-06 15:51 | 6 | 1:31 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23020600265 | New_Event | Animals | Include | Include | Wildlife | 91 | 2023-02-06 | 546 | keep | 0 | Feb | 2023 | 0.00037188 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-06 14:34 | 2023-02-06 16:12 | 2044 | 1:38 | P | EMPALME SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 20% DE SU CARGA POR EL 1118-10 Y LLEVA LA CARGA DEL 1115-03 SE SECCIONALIZO AVERIA PARA REPARAR EMPALME SOTERRADO AVERIADO Y SE CERRO INTERRUPTOR POR SCADA SJ-230206-01 | S23020600095 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 98 | 2023-02-06 | 200312 | keep | 0 | Feb | 2023 | 0.13643 | 0.0013922 | Sustained | FALSE | FALSE | Not_TMED_Event | 2044
SAN JUAN | 2023-02-06 14:34 | 2023-02-06 16:12 | 134 | 1:38 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1111-01 QUE LLEVA LA CARGA DEL 1115-03 SE SECCIONALIZO AVERIA PARA REPARAR EMPALME SOTERRADO AVERIADO Y SE CERRO INTERRUPTOR POR SCADA SJ-230206-01 | S23020600095 | New_Event | Feeder Load Transferred | Include | Include | Other | 98 | 2023-02-06 | 13132 | keep | 0 | Feb | 2023 | 0.0089441 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
PONCE | 2023-02-06 15:10 | 2023-02-06 16:09 | 50 | 0:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23020600079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-02-06 | 2950 | keep | 0 | Feb | 2023 | 0.0020092 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-02-06 15:16 | 2023-02-06 17:06 | 1 | 1:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 100 EN C/L | S23020600118 | New_Event | Cutout Failure | Include | Include | Equipment | 110 | 2023-02-06 | 110 | keep | 0 | Feb | 2023 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-06 15:16 | 2023-02-06 18:03 | 45 | 2:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23020600283 | New_Event | Cutout Failure | Include | Include | Equipment | 167 | 2023-02-06 | 7515 | keep | 0 | Feb | 2023 | 0.0051184 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2023-02-06 15:28 | 2023-02-06 17:47 | 45 | 2:19 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23020600088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-02-06 | 6255 | keep | 0 | Feb | 2023 | 0.0042603 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
YAUCO | 2023-02-06 15:30 | 2023-02-06 20:25 | 75 | 4:55 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | P23020600083 | New_Event | Primary Wire Break | Include | Include | Equipment | 295 | 2023-02-06 | 22125 | keep | 0 | Feb | 2023 | 0.015069 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2023-02-06 15:30 | 2023-02-06 19:03 | 17 | 3:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARA LINEA PRIMARIA PARTIDA | A23020600058 | New_Event | Primary Wire Break | Include | Include | Equipment | 213 | 2023-02-06 | 3621 | keep | 0 | Feb | 2023 | 0.0024662 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
GUAYAMA | 2023-02-06 15:41 | 2023-02-06 16:50 | 5 | 1:09 | P | TRANSFORMADOR AVERIADO | SE CAMBIO TRANSFORMADOR DE 25KVA A 4160 Y SE CAMBIARA POR UNO DE 37.5 A 4160 | P23020600088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 69 | 2023-02-06 | 345 | keep | 0 | Feb | 2023 | 0.00023498 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-02-06 15:47 | 2023-02-06 15:48 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23020600053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-06 | 4188 | keep | 0 | Feb | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
HUMACAO | 2023-02-06 15:53 | 2023-02-06 17:58 | 13 | 2:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y SE REEMPLAZO PROTAFUSIBLE | C23020600291 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2023-02-06 | 1625 | keep | 0 | Feb | 2023 | 0.0011068 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-02-06 16:00 | 2023-02-06 16:22 | 4 | 0:22 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y PARA REEMPLAZAR PEDESTAL | B23020600098 | New_Event |  |  |  |  | 22 | 2023-02-06 | 88 | keep | 0 | Feb | 2023 | 5.9936e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-06 16:05 | 2023-02-06 16:40 | 17 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO BARRAS EN PEDESTAL | B23020600095 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-02-06 | 595 | keep | 0 | Feb | 2023 | 0.00040525 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-02-06 16:12 | 2023-02-06 18:03 | 4 | 1:51 | P | EMPALME SOTERRADO AVERIADO | SE REPARO AVERIA EN EMPALME SOTERRADO EN MH-07 A CAJAS SECAS SJ-230206-01 | S23020600095 | Partial_restoration | UG Cable Splice Failure | Include | Include | Equipment | 111 | 2023-02-06 | 444 | keep | 0 | Feb | 2023 | 0.00030241 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-06 16:22 | 2023-02-06 19:30 | 10 | 3:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M23020600158 | New_Event | Cutout Failure | Include | Include | Equipment | 188 | 2023-02-06 | 1880 | keep | 0 | Feb | 2023 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-06 16:27 | 2023-02-06 20:17 | 41 | 3:50 | P | TRANSFORMADOR AVERIADO | T - 21 QUEMADO SE CERRO DE RISER AL T-22 | R23020600058 | New_Event | Service Transformer Failure | Include | Include | Equipment | 230 | 2023-02-06 | 9430 | keep | 0 | Feb | 2023 | 0.0064227 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
AGUADILLA | 2023-02-06 16:39 | 2023-02-06 16:40 | 1047 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-06 | 1047 | keep | 0 | Feb | 2023 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
VEGA BAJA | 2023-02-06 16:43 | 2023-02-06 18:36 | 1000 | 1:53 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y 1 X 80 EN C/L | B23020600103 | New_Event | Switch Failure | Include | Include | Equipment | 113 | 2023-02-06 | 113000 | keep | 0 | Feb | 2023 | 0.076964 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
YAUCO | 2023-02-06 16:45 | 2023-02-06 18:25 | 10 | 1:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA | M23020600123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2023-02-06 | 1000 | keep | 0 | Feb | 2023 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-06 17:09 | 2023-02-06 19:26 | 100 | 2:17 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | S23020600151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-02-06 | 13700 | keep | 0 | Feb | 2023 | 0.009331 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-02-06 17:22 | 2023-02-06 17:56 | 1 | 0:34 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | DESGANCHE Y SE REPARO BAJANTE SECUNDARIO | C23020600306 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 34 | 2023-02-06 | 34 | keep | 0 | Feb | 2023 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-06 17:40 | 2023-02-06 19:03 | 1117 | 1:23 | T | CONDUCTOR ROTO O ABIERTO | GOI MY-230206-01A PARA CERRAR PUENTE EN TRONCAL PRIMARIO CON CARGA 6404-02 Y CIRCUITO ALIMENTADOR 6404-03 | M23020600189 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 83 | 2023-02-06 | 92711 | keep | 0 | Feb | 2023 | 0.063145 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-06 17:40 | 2023-02-06 19:03 | 1671 | 1:23 | T | ALIMENTADOR AMARRADO | GOI MY-230206-01A PARA CERRAR PUENTE EN TRONCAL PRIMARIO CON CARGA 6404-02 Y CIRCUITO ALIMENTADOR 6404-03 | M23020600189 | Additional_clients | Feeder Load Transferred | Include | Include | Other | 83 | 2023-02-06 | 138693 | keep | 0 | Feb | 2023 | 0.094463 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-06 17:40 | 2023-02-06 19:03 | 527 | 1:23 | T | CONDUCTOR ROTO O ABIERTO | GOI MY-230206-01A PARA CERRAR PUENTE EN TRONCAL PRIMARIO CON CARGA 6404-02 Y CIRCUITO ALIMENTADOR 6404-03 | M23020600189 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 83 | 2023-02-06 | 43741 | keep | 0 | Feb | 2023 | 0.029792 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-06 18:01 | 2023-02-07 12:07 | 18 | 18:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON BARRAS EN PEDESTAL SECUNDARIOI SULFATADAS | C23020600315 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1086 | 2023-02-06 | 19548 | keep | 0 | Feb | 2023 | 0.013314 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-02-06 18:16 | 2023-02-06 21:00 | 20 | 2:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23020600166 | New_Event | Secondary Wire Break | Include | Include | Equipment | 164 | 2023-02-06 | 3280 | keep | 0 | Feb | 2023 | 0.002234 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-02-06 18:36 | 2023-02-06 18:37 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23020600120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-06 | 3000 | keep | 0 | Feb | 2023 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2023-02-06 18:37 | 2023-02-06 21:15 | 1000 | 2:38 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y 1 X 80 EN C/L | B23020600103 | Partial_restoration | Switch Failure | Include | Include | Equipment | 158 | 2023-02-06 | 158000 | keep | 0 | Feb | 2023 | 0.10761 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-02-06 18:45 | 2023-02-06 20:18 | 10 | 1:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA POR PORTAFUSIBLE EMBUCHADO | P23020600114 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2023-02-06 | 930 | keep | 0 | Feb | 2023 | 0.00063342 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-02-06 19:03 | 2023-02-06 22:15 | 60 | 3:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 Y 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23020600228 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 192 | 2023-02-06 | 11520 | keep | 0 | Feb | 2023 | 0.0078462 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-02-06 19:29 | 2023-02-06 22:40 | 75 | 3:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020600087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-02-06 | 14325 | keep | 0 | Feb | 2023 | 0.0097567 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2023-02-06 19:37 | 2023-02-07 15:40 | 15 | 20:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA POR LA MISMA CAPACIDAD | A23020600095 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1203 | 2023-02-06 | 18045 | keep | 0 | Feb | 2023 | 0.01229 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-02-06 19:47 | 2023-02-06 20:18 | 12 | 0:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO DE PORTAFUSIBLE 1 X 30 EN C/L | C23020600326 | New_Event | Cutout Failure | Include | Include | Equipment | 31 | 2023-02-06 | 372 | keep | 0 | Feb | 2023 | 0.00025337 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-02-06 20:13 | 2023-02-07 07:51 | 35 | 11:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23020600330 | New_Event | Vegetation Contact | Include | Include | Vegetation | 698 | 2023-02-06 | 24430 | keep | 0 | Feb | 2023 | 0.016639 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2023-02-06 20:16 | 2023-02-06 22:24 | 150 | 2:08 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | R23020600070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-02-06 | 19200 | keep | 0 | Feb | 2023 | 0.013077 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-02-06 20:17 | 2023-02-07 14:12 | 30 | 17:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR PM DE 75 KVA X 75 KVA | R23020600058 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1075 | 2023-02-06 | 32250 | keep | 0 | Feb | 2023 | 0.021965 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-06 20:39 | 2023-02-06 20:40 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-06 | 918 | keep | 0 | Feb | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
SAN JUAN | 2023-02-06 20:59 | 2023-02-06 21:20 | 1 | 0:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L Y SE REEMPLAZO PORTA FUSIBLE | S23020600174 | New_Event | Cutout Failure | Include | Include | Equipment | 21 | 2023-02-06 | 21 | keep | 0 | Feb | 2023 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-06 22:16 | 2023-02-07 07:00 | 8 | 8:44 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE CON AVE | C23020600353 | New_Event | Animals | Include | Include | Wildlife | 524 | 2023-02-06 | 4192 | keep | 0 | Feb | 2023 | 0.0028552 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-02-06 22:40 | 2023-02-07 00:40 | 175 | 2:00 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | P23020600144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-02-06 | 21000 | keep | 0 | Feb | 2023 | 0.014303 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
CAGUAS | 2023-02-07 00:26 | 2023-02-07 10:00 | 90 | 9:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23020700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 574 | 2023-02-07 | 51660 | keep | 0 | Feb | 2023 | 0.035185 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2023-02-07 01:56 | 2023-02-07 09:00 | 50 | 7:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23020700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 424 | 2023-02-07 | 21200 | keep | 0 | Feb | 2023 | 0.014439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-07 04:53 | 2023-02-07 09:40 | 1 | 4:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO SAFADO HACIA TRANSFORMADOR | C23020700003 | New_Event | Primary Wire Break | Include | Include | Equipment | 287 | 2023-02-07 | 287 | keep | 0 | Feb | 2023 | 0.00019547 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-07 05:44 | 2023-02-07 05:45 | 1380 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23020700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 1380 | keep | 0 | Feb | 2023 | 0.00093991 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
CANOVANAS | 2023-02-07 06:10 | 2023-02-07 09:10 | 220 | 3:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | R23020700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-02-07 | 39600 | keep | 0 | Feb | 2023 | 0.026971 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
PONCE | 2023-02-07 07:18 | 2023-02-07 11:47 | 75 | 4:29 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE ABRE TRANSFORMADOR FID 12463544 POR LINEA PROBAR MALA | P23020700017 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 269 | 2023-02-07 | 20175 | keep | 0 | Feb | 2023 | 0.013741 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-02-07 07:24 | 2023-02-07 10:35 | 100 | 3:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23020700003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 191 | 2023-02-07 | 19100 | keep | 0 | Feb | 2023 | 0.013009 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-02-07 07:39 | 2023-02-07 09:06 | 60 | 1:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REEMPLAZO POSTAFUSIBLE | R23020700013 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2023-02-07 | 5220 | keep | 0 | Feb | 2023 | 0.0035553 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-02-07 07:40 | 2023-02-07 10:40 | 16 | 3:00 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23020700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2023-02-07 | 2880 | keep | 0 | Feb | 2023 | 0.0019616 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-02-07 08:00 | 2023-02-07 12:02 | 10 | 4:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | R23020700016 | New_Event | Cutout Failure | Include | Include | Equipment | 242 | 2023-02-07 | 2420 | keep | 0 | Feb | 2023 | 0.0016483 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-07 08:08 | 2023-02-07 13:17 | 10 | 5:09 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 75KVA X 75KVA | S23020700005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 309 | 2023-02-07 | 3090 | keep | 0 | Feb | 2023 | 0.0021046 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-02-07 08:18 | 2023-02-08 09:58 | 1 | 25:40 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANSFORMADOR SE FIJO BUSHING Y SE RECONECTO NEUTRAL PRIMARIO EVENTO DEL DIA 7 | P23020700025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1540 | 2023-02-07 | 1540 | keep | 0 | Feb | 2023 | 0.0010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-07 08:23 | 2023-02-07 10:44 | 100 | 2:21 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR AVE | P23020700028 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-02-07 | 14100 | keep | 0 | Feb | 2023 | 0.0096034 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-02-07 08:31 | 2023-02-07 09:27 | 20 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES BAJANTE DEL XMR Y SE REPARARON SECUNDARIA AVERIADA | P23020700029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2023-02-07 | 1120 | keep | 0 | Feb | 2023 | 0.00076283 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-07 08:38 | 2023-02-07 10:05 | 90 | 1:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23020700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2023-02-07 | 7830 | keep | 0 | Feb | 2023 | 0.005333 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2023-02-07 08:58 | 2023-02-07 08:59 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23020700032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 1746 | keep | 0 | Feb | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2023-02-07 09:00 | 2023-02-07 12:16 | 10 | 3:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 140 EN RISER POR MAL TIEMPO | B23020700014 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 196 | 2023-02-07 | 1960 | keep | 0 | Feb | 2023 | 0.0013349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-07 09:07 | 2023-02-07 09:08 | 4830 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23020700022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 4830 | keep | 0 | Feb | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
AGUADILLA | 2023-02-07 09:15 | 2023-02-07 09:50 | 15 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES SECUNDARIOS | M23020600259 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-02-07 | 525 | keep | 0 | Feb | 2023 | 0.00035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-07 09:17 | 2023-02-07 12:47 | 8 | 3:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23020700010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 210 | 2023-02-07 | 1680 | keep | 0 | Feb | 2023 | 0.0011442 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-02-07 09:25 | 2023-02-07 17:00 | 10 | 7:35 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR POR DESGANCHE | P23020700039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 455 | 2023-02-07 | 4550 | keep | 0 | Feb | 2023 | 0.003099 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-02-07 09:29 | 2023-02-07 12:23 | 1 | 2:54 | P | PROBLEMA DEL CLIENTE | 1 X 40 EN C/L PUNTO CALIENTE EN BANCO DE XMR SE NOTIFICO AL CLIENTE | B23020700023 | New_Event | Customer-Related Interruption | Include | Include | Public | 174 | 2023-02-07 | 174 | keep | 0 | Feb | 2023 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-07 09:31 | 2023-02-07 15:30 | 40 | 5:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR BAMBUAS | M23020700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2023-02-07 | 14360 | keep | 0 | Feb | 2023 | 0.0097805 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-07 09:38 | 2023-02-07 13:25 | 12 | 3:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23020700025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 227 | 2023-02-07 | 2724 | keep | 0 | Feb | 2023 | 0.0018553 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-02-07 09:39 | 2023-02-07 10:46 | 190 | 1:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETE PARA REEMPLAZO DE AISLADOR ROTO POR RIGIDO CAUSANDO INTERRUPCION | R23020700030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 67 | 2023-02-07 | 12730 | keep | 0 | Feb | 2023 | 0.0086703 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
GUAYAMA | 2023-02-07 09:50 | 2023-02-07 13:54 | 300 | 4:04 | P | CAUSAS EXTERNAS | SE CAMBIARON 3 CAJAS PRIMARIAS 3 X 140 DE CORTE DE LINEA POR MUNICIPIO TUMBAR ARBOL | P23020700046 | New_Event | Damage From Public | Include | Include | Public | 244 | 2023-02-07 | 73200 | keep | 0 | Feb | 2023 | 0.049856 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2023-02-07 10:05 | 2023-02-07 14:10 | 30 | 4:05 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REMPLAZO DE POSTE | A23020700028 | New_Event | Primary Pole Failure | Include | Include | Equipment | 245 | 2023-02-07 | 7350 | keep | 0 | Feb | 2023 | 0.0050061 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-07 10:22 | 2023-02-07 13:30 | 6 | 3:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO CAJA PRIMARIA | S23020700020 | New_Event | Cutout Failure | Include | Include | Equipment | 188 | 2023-02-07 | 1128 | keep | 0 | Feb | 2023 | 0.00076828 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-02-07 10:24 | 2023-02-07 13:30 | 40 | 3:06 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A23020700040 | New_Event | Animals | Include | Include | Wildlife | 186 | 2023-02-07 | 7440 | keep | 0 | Feb | 2023 | 0.0050674 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-02-07 10:53 | 2023-02-07 12:13 | 11 | 1:20 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | R23020700042 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 80 | 2023-02-07 | 880 | keep | 0 | Feb | 2023 | 0.00059936 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-02-07 11:12 | 2023-02-07 14:26 | 5 | 3:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES SECUNDARIOS SULFATADOS | C23020700055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 194 | 2023-02-07 | 970 | keep | 0 | Feb | 2023 | 0.00066066 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-02-07 11:16 | 2023-02-07 11:17 | 1342 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | C2302070000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-02-07 | 1342 | keep | 0 | Feb | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
BARRANQUITAS | 2023-02-07 11:16 | 2023-02-07 12:32 | 8 | 1:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR TOMA SECUNDARIA SULFATADA | C23020700057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 76 | 2023-02-07 | 608 | keep | 0 | Feb | 2023 | 0.00041411 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-02-07 11:17 | 2023-02-07 15:38 | 68 | 4:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIAS | C23020700058 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 261 | 2023-02-07 | 17748 | keep | 0 | Feb | 2023 | 0.012088 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2023-02-07 11:28 | 2023-02-07 12:07 | 1 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23020700029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-02-07 | 39 | keep | 0 | Feb | 2023 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-07 11:29 | 2023-02-07 11:31 | 225 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO Y SE CERRO POR SCADA | S2302070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-07 | 450 | keep | 0 | Feb | 2023 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-02-07 11:29 | 2023-02-07 11:31 | 870 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2302070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-07 | 1740 | keep | 0 | Feb | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
FAJARDO | 2023-02-07 11:30 | 2023-02-07 12:15 | 3 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO DE TRANSFORMADORES PARA REEMPLAZO DE BARRA EN PULL BOX | R23020700019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-02-07 | 135 | keep | 0 | Feb | 2023 | 9.1948e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-02-07 11:40 | 2023-02-07 14:36 | 39 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C23020700065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2023-02-07 | 6864 | keep | 0 | Feb | 2023 | 0.004675 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CANOVANAS | 2023-02-07 11:41 | 2023-02-07 12:44 | 60 | 1:03 | P | ANIMAL | 2 SMU 20 DE 20AMP EN RISER CRUCE X AVE | R23020700046 | New_Event | Animals | Include | Include | Wildlife | 63 | 2023-02-07 | 3780 | keep | 0 | Feb | 2023 | 0.0025745 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-02-07 11:48 | 2023-02-07 19:38 | 5 | 7:50 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYE PROVICIONAL AEREO PARA ENERGIZAR T#6 POR AVERIA DEL T#7 AL T#6 | P23020700080 | New_Event | UG Cable Fault | Include | Include | Equipment | 470 | 2023-02-07 | 2350 | keep | 0 | Feb | 2023 | 0.0016006 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-02-07 12:40 | 2023-02-07 17:09 | 78 | 4:29 | P | DESGANCHE | SE REALIZO DESGANCHE EN VARIOS PUNTOS Y SE REMPLAZO 1X50 EN C/L | R23020700053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2023-02-07 | 20982 | keep | 0 | Feb | 2023 | 0.014291 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
CAGUAS | 2023-02-07 12:43 | 2023-02-07 15:47 | 1 | 3:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON BAJANTES PRIMARIOS HACIA TRANSFORMADORES | C23020700077 | New_Event | Primary Wire Break | Include | Include | Equipment | 184 | 2023-02-07 | 184 | keep | 0 | Feb | 2023 | 0.00012532 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-07 12:48 | 2023-02-07 12:49 | 2343 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C23020700082 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-07 | 2343 | keep | 0 | Feb | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
BARRANQUITAS | 2023-02-07 12:49 | 2023-02-07 15:15 | 200 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | C23020700092 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 146 | 2023-02-07 | 29200 | keep | 0 | Feb | 2023 | 0.019888 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-02-07 13:00 | 2023-02-07 16:09 | 129 | 3:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C23020700089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2023-02-07 | 24381 | keep | 0 | Feb | 2023 | 0.016606 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
BARRANQUITAS | 2023-02-07 13:00 | 2023-02-07 16:02 | 1 | 3:02 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C23020700088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2023-02-07 | 182 | keep | 0 | Feb | 2023 | 0.00012396 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-07 13:26 | 2023-02-07 15:27 | 150 | 2:01 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO PUENTE DE CAJA A LINEA Y CERRO CORTE DE LINEA | B23020700066 | New_Event | Primary Wire Break | Include | Include | Equipment | 121 | 2023-02-07 | 18150 | keep | 0 | Feb | 2023 | 0.012362 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-02-07 13:35 | 2023-02-07 14:10 | 1548 | 0:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA TRANSMISION 38KV ARECIBO SECT PARARRAYOS AVERIADO EN SUB. 8081 SKW BARRA 38KV ABRE YA QUE GCB 2350 NO DISPARA POR BAJO SF6 TAMBIEN PUENTE ABIERTO EN LINEA 2300 | A23020700088 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 35 | 2023-02-07 | 54180 | keep | 0 | Feb | 2023 | 0.036902 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2023-02-07 13:35 | 2023-02-07 14:10 | 274 | 0:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA TRANSMISION 38KV ARECIBO SECT PARARRAYOS AVERIADO EN SUB. 8081 SKW BARRA 38KV ABRE YA QUE GCB 2350 NO DISPARA POR BAJO SF6 TAMBIEN PUENTE ABIERTO EN LINEA 2300 | A23020700088 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 35 | 2023-02-07 | 9590 | keep | 0 | Feb | 2023 | 0.0065317 | 0.00018662 | Sustained | FALSE | FALSE | Not_TMED_Event | 274
ARECIBO | 2023-02-07 13:35 | 2023-02-07 14:10 | 185 | 0:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA TRANSMISION 38KV ARECIBO SECT PARARRAYOS AVERIADO EN SUB. 8081 SKW BARRA 38KV ABRE YA QUE GCB 2350 NO DISPARA POR BAJO SF6 TAMBIEN PUENTE ABIERTO EN LINEA 2300 | A23020700088 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 35 | 2023-02-07 | 6475 | keep | 0 | Feb | 2023 | 0.0044101 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2023-02-07 13:35 | 2023-02-07 14:10 | 9 | 0:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA TRANSMISION 38KV ARECIBO SECT PARARRAYOS AVERIADO EN SUB. 8081 SKW BARRA 38KV ABRE YA QUE GCB 2350 NO DISPARA POR BAJO SF6 TAMBIEN PUENTE ABIERTO EN LINEA 2300 | A23020700088 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 35 | 2023-02-07 | 315 | keep | 0 | Feb | 2023 | 0.00021455 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2023-02-07 13:35 | 2023-02-07 14:10 | 385 | 0:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA TRANSMISION 38KV ARECIBO SECT PARARRAYOS AVERIADO EN SUB. 8081 SKW BARRA 38KV ABRE YA QUE GCB 2350 NO DISPARA POR BAJO SF6 TAMBIEN PUENTE ABIERTO EN LINEA 2300 | A23020700090 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 35 | 2023-02-07 | 13475 | keep | 0 | Feb | 2023 | 0.0091778 | 0.00026222 | Sustained | FALSE | FALSE | Not_TMED_Event | 385
ARECIBO | 2023-02-07 13:35 | 2023-02-07 14:10 | 264 | 0:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA TRANSMISION 38KV ARECIBO SECT PARARRAYOS AVERIADO EN SUB. 8081 SKW BARRA 38KV ABRE YA QUE GCB 2350 NO DISPARA POR BAJO SF6 TAMBIEN PUENTE ABIERTO EN LINEA 2300 | A23020700090 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 35 | 2023-02-07 | 9240 | keep | 0 | Feb | 2023 | 0.0062933 | 0.00017981 | Sustained | FALSE | FALSE | Not_TMED_Event | 264
ARECIBO | 2023-02-07 13:35 | 2023-02-07 14:10 | 316 | 0:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA TRANSMISION 38KV ARECIBO SECT PARARRAYOS AVERIADO EN SUB. 8081 SKW BARRA 38KV ABRE YA QUE GCB 2350 NO DISPARA POR BAJO SF6 TAMBIEN PUENTE ABIERTO EN LINEA 2300 | A23020700087 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 35 | 2023-02-07 | 11060 | keep | 0 | Feb | 2023 | 0.0075329 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2023-02-07 13:35 | 2023-02-07 14:10 | 1227 | 0:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA TRANSMISION 38KV ARECIBO SECT PARARRAYOS AVERIADO EN SUB. 8081 SKW BARRA 38KV ABRE YA QUE GCB 2350 NO DISPARA POR BAJO SF6 TAMBIEN PUENTE ABIERTO EN LINEA 2300 | A23020700087 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 35 | 2023-02-07 | 42945 | keep | 0 | Feb | 2023 | 0.02925 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-02-07 13:35 | 2023-02-07 14:10 | 3431 | 0:35 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA TRANSMISION 38KV ARECIBO SECT PARARRAYOS AVERIADO EN SUB. 8081 SKW BARRA 38KV ABRE YA QUE GCB 2350 NO DISPARA POR BAJO SF6 TAMBIEN PUENTE ABIERTO EN LINEA 2300 | A23020700087 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 35 | 2023-02-07 | 120085 | keep | 0 | Feb | 2023 | 0.081789 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
MAYAGÃœEZ | 2023-02-07 13:48 | 2023-02-07 16:50 | 39 | 3:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO NO SE ENCONTRO CAUSA | M23020700081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2023-02-07 | 7098 | keep | 0 | Feb | 2023 | 0.0048344 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CANOVANAS | 2023-02-07 13:52 | 2023-02-07 17:07 | 13 | 3:15 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO PM 75 KVA POR 75 KVA | R23020700065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2023-02-07 | 2535 | keep | 0 | Feb | 2023 | 0.0017266 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-02-07 13:56 | 2023-02-07 13:57 | 2302 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C23020700113 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-02-07 | 2302 | keep | 0 | Feb | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
VEGA BAJA | 2023-02-07 14:01 | 2023-02-07 18:43 | 8 | 4:42 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23020700098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 282 | 2023-02-07 | 2256 | keep | 0 | Feb | 2023 | 0.0015366 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-02-07 14:03 | 2023-02-07 15:46 | 7 | 1:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA PRIMARIA EN TRANSFORMADOR Y 1 X 20 AMP EN XMRD | P23020700101 | New_Event | Cutout Failure | Include | Include | Equipment | 103 | 2023-02-07 | 721 | keep | 0 | Feb | 2023 | 0.00049107 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-02-07 14:05 | 2023-02-08 16:04 | 10 | 25:59 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZO DE TRANSFORMADOR DE 37.5KVA X 37.5KVA | A23012700135 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1559 | 2023-02-07 | 15590 | keep | 0 | Feb | 2023 | 0.010618 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-02-07 14:23 | 2023-02-07 17:59 | 1 | 3:36 | P | ANIMAL | 1 X 25 RISER AVE CRUZO PARARRAYO | M23020700093 | New_Event | Animals | Include | Include | Wildlife | 216 | 2023-02-07 | 216 | keep | 0 | Feb | 2023 | 0.00014712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-07 14:24 | 2023-02-07 15:15 | 1 | 0:51 | P | PROBLEMA DEL CLIENTE | 3 X 25 EN SU CLIENTE REEMPLAZO AISLADORES EN TRANSCLOSURE | C23020700129 | New_Event | Customer-Related Interruption | Include | Include | Public | 51 | 2023-02-07 | 51 | keep | 0 | Feb | 2023 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-07 14:34 | 2023-02-07 14:35 | 2302 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C2302070000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-02-07 | 2302 | keep | 0 | Feb | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2023-02-07 14:35 | 2023-02-07 19:06 | 107 | 4:31 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO SE ABRIO INTERRUPTOR PARA REEMPLAZARLO | C23020700247 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 271 | 2023-02-07 | 28997 | keep | 0 | Feb | 2023 | 0.01975 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
YAUCO | 2023-02-07 14:35 | 2023-02-07 16:19 | 5 | 1:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POE DESGANCHE | P23020700103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-02-07 | 520 | keep | 0 | Feb | 2023 | 0.00035417 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-02-07 14:45 | 2023-02-07 16:22 | 934 | 1:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23020700117 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 97 | 2023-02-07 | 90598 | keep | 0 | Feb | 2023 | 0.061706 | 0.00063614 | Sustained | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2023-02-07 14:45 | 2023-02-07 16:22 | 4 | 1:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23020700117 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 97 | 2023-02-07 | 388 | keep | 0 | Feb | 2023 | 0.00026427 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-02-07 14:45 | 2023-02-07 16:22 | 1479 | 1:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23020700117 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 97 | 2023-02-07 | 143463 | keep | 0 | Feb | 2023 | 0.097712 | 0.0010073 | Sustained | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2023-02-07 14:45 | 2023-02-07 16:22 | 1841 | 1:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23020700118 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 97 | 2023-02-07 | 178577 | keep | 0 | Feb | 2023 | 0.12163 | 0.0012539 | Sustained | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2023-02-07 14:45 | 2023-02-07 16:22 | 1950 | 1:37 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A23020700118 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 97 | 2023-02-07 | 189150 | keep | 0 | Feb | 2023 | 0.12883 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
BARRANQUITAS | 2023-02-07 15:15 | 2023-02-07 15:30 | 635 | 0:15 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO PARTE DE LA CARGA POR EL 3701-4 | C23020700092 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 15 | 2023-02-07 | 9525 | keep | 0 | Feb | 2023 | 0.0064874 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-07 15:19 | 2023-02-07 16:31 | 1 | 1:12 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23020700084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-02-07 | 72 | keep | 0 | Feb | 2023 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-07 15:22 | 2023-02-07 16:52 | 90 | 1:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M23020700115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-02-07 | 8100 | keep | 0 | Feb | 2023 | 0.0055169 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2023-02-07 15:30 | 2023-02-07 18:40 | 130 | 3:10 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR DEL SUELO | C23020700092 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 190 | 2023-02-07 | 24700 | keep | 0 | Feb | 2023 | 0.016823 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-07 15:38 | 2023-02-07 16:36 | 36 | 0:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN C/L MAL TIEMPO LLUVIAS | B23020700088 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 58 | 2023-02-07 | 2088 | keep | 0 | Feb | 2023 | 0.0014221 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2023-02-07 15:40 | 2023-02-07 17:49 | 3 | 2:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES QUEMADOS EN TOMAS | C23020700159 | New_Event | Secondary Wire Break | Include | Include | Equipment | 129 | 2023-02-07 | 387 | keep | 0 | Feb | 2023 | 0.00026358 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-07 15:40 | 2023-02-07 17:52 | 5 | 2:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23020700089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 132 | 2023-02-07 | 660 | keep | 0 | Feb | 2023 | 0.00044952 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-02-07 15:52 | 2023-02-07 18:24 | 150 | 2:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A23020700131 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 152 | 2023-02-07 | 22800 | keep | 0 | Feb | 2023 | 0.015529 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-02-07 16:03 | 2023-02-07 17:52 | 36 | 1:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L Y SE LEVANTO CONDUCTOR PRIMARIO | S23020700078 | New_Event | Primary Wire Break | Include | Include | Equipment | 109 | 2023-02-07 | 3924 | keep | 0 | Feb | 2023 | 0.0026726 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
GUAYAMA | 2023-02-07 16:03 | 2023-02-07 18:43 | 12 | 2:40 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO | P23020700110 | New_Event | Primary Wire Break | Include | Include | Equipment | 160 | 2023-02-07 | 1920 | keep | 0 | Feb | 2023 | 0.0013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-02-07 16:04 | 2023-02-07 20:35 | 8 | 4:31 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZO DESGANCHE Y SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A23020700134 | New_Event | Primary Wire Break | Include | Include | Equipment | 271 | 2023-02-07 | 2168 | keep | 0 | Feb | 2023 | 0.0014766 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-02-07 16:06 | 2023-02-07 19:55 | 30 | 3:49 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN CORTE DE LINEA SE SECCIONALIZO CABLE SOTERRADO AVERIADO | A23020700135 | New_Event | UG Cable Fault | Include | Include | Equipment | 229 | 2023-02-07 | 6870 | keep | 0 | Feb | 2023 | 0.0046791 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-02-07 16:10 | 2023-02-07 16:11 | 1604 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23020700169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 1604 | keep | 0 | Feb | 2023 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
SAN JUAN | 2023-02-07 16:15 | 2023-02-07 20:17 | 15 | 4:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REPARO SECUNDARIA | S23020700081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 242 | 2023-02-07 | 3630 | keep | 0 | Feb | 2023 | 0.0024724 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-07 16:25 | 2023-02-07 18:28 | 93 | 2:03 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23020700084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-02-07 | 11439 | keep | 0 | Feb | 2023 | 0.0077911 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
BAYAMON | 2023-02-07 16:28 | 2023-02-07 18:14 | 1 | 1:46 | P | ANIMAL | 1 X 20 EN C/L CRUCE X AVE | B23020700098 | New_Event | Animals | Include | Include | Wildlife | 106 | 2023-02-07 | 106 | keep | 0 | Feb | 2023 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-07 16:28 | 2023-02-07 19:21 | 12 | 2:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C23020700174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2023-02-07 | 2076 | keep | 0 | Feb | 2023 | 0.001414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-02-07 16:38 | 2023-02-07 18:14 | 94 | 1:36 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN CORTE DE LINEA | P23020700112 | New_Event | Primary Wire Break | Include | Include | Equipment | 96 | 2023-02-07 | 9024 | keep | 0 | Feb | 2023 | 0.0061462 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
VEGA BAJA | 2023-02-07 16:46 | 2023-02-07 19:24 | 70 | 2:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA Y SE REMPLAZO AISLADOR ROTO | B23020700099 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 158 | 2023-02-07 | 11060 | keep | 0 | Feb | 2023 | 0.0075329 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-02-07 16:47 | 2023-02-07 19:21 | 16 | 2:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23020700180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-02-07 | 2464 | keep | 0 | Feb | 2023 | 0.0016782 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
YAUCO | 2023-02-07 16:56 | 2023-02-07 23:19 | 1339 | 6:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 POR OPERACIONES POR PERSONAL DE LUMA ABRIERON AUX 13450A EN VEZ DEL 1250A DURANTE VIA LIBRE EMERGENCIA | M23020700240 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2023-02-07 | 512837 | keep | 0 | Feb | 2023 | 0.34929 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-02-07 16:56 | 2023-02-07 23:19 | 470 | 6:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 POR OPERACIONES POR PERSONAL DE LUMA ABRIERON AUX 13450A EN VEZ DEL 1250A DURANTE VIA LIBRE EMERGENCIA | M23020700240 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2023-02-07 | 180010 | keep | 0 | Feb | 2023 | 0.1226 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2023-02-07 16:56 | 2023-02-07 23:19 | 2483 | 6:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 POR OPERACIONES POR PERSONAL DE LUMA ABRIERON AUX 13450A EN VEZ DEL 1250A DURANTE VIA LIBRE EMERGENCIA | M23020700240 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2023-02-07 | 950989 | keep | 0 | Feb | 2023 | 0.64771 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2023-02-07 16:56 | 2023-02-07 23:19 | 2190 | 6:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 POR OPERACIONES POR PERSONAL DE LUMA ABRIERON AUX 13450A EN VEZ DEL 1250A DURANTE VIA LIBRE EMERGENCIA | M23020700240 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2023-02-07 | 838770 | keep | 0 | Feb | 2023 | 0.57128 | 0.0014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2023-02-07 16:56 | 2023-02-07 23:19 | 3006 | 6:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 POR OPERACIONES POR PERSONAL DE LUMA ABRIERON AUX 13450A EN VEZ DEL 1250A DURANTE VIA LIBRE EMERGENCIA | M23020700128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2023-02-07 | 1151298 | keep | 0 | Feb | 2023 | 0.78414 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2023-02-07 16:56 | 2023-02-07 23:19 | 179 | 6:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 POR OPERACIONES POR PERSONAL DE LUMA ABRIERON AUX 13450A EN VEZ DEL 1250A DURANTE VIA LIBRE EMERGENCIA | M23020700128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2023-02-07 | 68557 | keep | 0 | Feb | 2023 | 0.046694 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
FAJARDO | 2023-02-07 17:00 | 2023-02-07 17:29 | 32 | 0:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | R23020700083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2023-02-07 | 928 | keep | 0 | Feb | 2023 | 0.00063206 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
FAJARDO | 2023-02-07 17:06 | 2023-02-07 17:07 | 2722 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R23020700085 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-02-07 | 2722 | keep | 0 | Feb | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2023-02-07 17:07 | 2023-02-07 22:42 | 400 | 5:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 140 EN C/L Y SE REMPLAZO AISLADOR | R23020700090 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 335 | 2023-02-07 | 134000 | keep | 0 | Feb | 2023 | 0.091267 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
VEGA BAJA | 2023-02-07 17:08 | 2023-02-07 19:27 | 60 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 8O EN C/L MAL TIEMPO LLUVIA | B23020700103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-02-07 | 8340 | keep | 0 | Feb | 2023 | 0.0056803 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-02-07 17:14 | 2023-02-08 11:02 | 114 | 17:48 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | C23020700201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1068 | 2023-02-07 | 121752 | keep | 0 | Feb | 2023 | 0.082925 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
MAYAGÃœEZ | 2023-02-07 17:18 | 2023-02-07 19:06 | 45 | 1:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M23020700157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-02-07 | 4860 | keep | 0 | Feb | 2023 | 0.0033101 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-02-07 17:19 | 2023-02-07 21:40 | 40 | 4:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020700161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2023-02-07 | 10440 | keep | 0 | Feb | 2023 | 0.0071106 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-07 17:24 | 2023-02-07 18:48 | 16 | 1:24 | P | OTRAS CAUSAS | 1 X 15 EN XMR SE REMOVIO GLOBOS DE LINEA | S23020700088 | New_Event | Other Causes | Include | Include | Other | 84 | 2023-02-07 | 1344 | keep | 0 | Feb | 2023 | 0.00091539 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-02-07 17:26 | 2023-02-07 20:03 | 10 | 2:37 | P | ANIMAL | 1 X 10 EN CORTE DE LINEA CRUCE CON AVE | C23020700211 | New_Event | Animals | Include | Include | Wildlife | 157 | 2023-02-07 | 1570 | keep | 0 | Feb | 2023 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-02-07 17:30 | 2023-02-07 19:46 | 25 | 2:16 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE RETIRO BAMBU DE LAS LINEAS | A23020700157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-02-07 | 3400 | keep | 0 | Feb | 2023 | 0.0023157 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-02-07 17:33 | 2023-02-07 19:08 | 458 | 1:35 | P | DESGANCHE | 2 X 40 EN C/L Y 2 X 65 EN C/L DESGANCHE | R23020700095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-02-07 | 43510 | keep | 0 | Feb | 2023 | 0.029634 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
ARECIBO | 2023-02-07 17:33 | 2023-02-07 22:25 | 20 | 4:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23020700158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2023-02-07 | 5840 | keep | 0 | Feb | 2023 | 0.0039776 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-02-07 17:43 | 2023-02-07 17:44 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
SAN JUAN | 2023-02-07 17:54 | 2023-02-07 17:56 | 837 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1401-07 | S23020700092 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-07 | 1674 | keep | 0 | Feb | 2023 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-02-07 17:54 | 2023-02-07 17:56 | 908 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1401-06 SE CERRO POR SCADA | S23020700092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-07 | 1816 | keep | 0 | Feb | 2023 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2023-02-07 17:54 | 2023-02-07 17:56 | 929 | 0:02 | T | NO SE REPORTO CAUSA | DISPARON DE INTERRUPTOR SE CERRO POR SCADA | S23020700093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-07 | 1858 | keep | 0 | Feb | 2023 | 0.0012655 | 0.00063274 | Momentary | FALSE | FALSE | Not_TMED_Event | 929
PONCE | 2023-02-07 17:57 | 2023-02-07 19:15 | 15 | 1:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23020700122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-02-07 | 1170 | keep | 0 | Feb | 2023 | 0.00079688 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-07 17:59 | 2023-02-07 22:52 | 137 | 4:53 | P | PARARRAYOS DEFECTUOSO | 2X100 EN C/L SE RETIRO PARRAYO CRUZADO | S23020700094 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 293 | 2023-02-07 | 40141 | keep | 0 | Feb | 2023 | 0.02734 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
BAYAMON | 2023-02-07 18:10 | 2023-02-07 18:11 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23020700107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 4431 | keep | 0 | Feb | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
ARECIBO | 2023-02-07 18:10 | 2023-02-08 00:05 | 8 | 5:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020700159 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 355 | 2023-02-07 | 2840 | keep | 0 | Feb | 2023 | 0.0019343 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-02-07 18:14 | 2023-02-07 18:15 | 2201 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REQUIERE DESGANCHE | A23020700160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-07 | 2201 | keep | 0 | Feb | 2023 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-02-07 18:15 | 2023-02-07 22:40 | 2 | 4:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020700164 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 265 | 2023-02-07 | 530 | keep | 0 | Feb | 2023 | 0.00036098 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-07 18:17 | 2023-02-07 21:33 | 472 | 3:16 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23020700108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-02-07 | 92512 | keep | 0 | Feb | 2023 | 0.06301 | 0.00032148 | Sustained | FALSE | FALSE | Not_TMED_Event | 472
BAYAMON | 2023-02-07 18:19 | 2023-02-07 18:20 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 2605 | keep | 0 | Feb | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-02-07 18:20 | 2023-02-07 18:21 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23020700109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 5809 | keep | 0 | Feb | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
ARECIBO | 2023-02-07 18:21 | 2023-02-07 18:22 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23020700161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 1227 | keep | 0 | Feb | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
CANOVANAS | 2023-02-07 18:24 | 2023-02-07 20:08 | 22 | 1:44 | P | TERMINACION SOTERRADA AVERIADA | 1 X 25 EN AEREO PROVISIONAL Y SE LIMPIO TERMINACION EN T 224 | R23020700105 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 104 | 2023-02-07 | 2288 | keep | 0 | Feb | 2023 | 0.0015583 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-02-07 18:27 | 2023-02-07 20:06 | 100 | 1:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | B23020700115 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 99 | 2023-02-07 | 9900 | keep | 0 | Feb | 2023 | 0.0067428 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-02-07 18:29 | 2023-02-08 06:38 | 12 | 12:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S23020700104 | New_Event | Secondary Wire Break | Include | Include | Equipment | 729 | 2023-02-07 | 8748 | keep | 0 | Feb | 2023 | 0.0059582 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-07 18:29 | 2023-02-08 04:04 | 70 | 9:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X50 EN C/L POR LLUVIA | S23020700103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 575 | 2023-02-07 | 40250 | keep | 0 | Feb | 2023 | 0.027414 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-02-07 18:40 | 2023-02-07 18:50 | 3522 | 0:10 | T | FUEGO | ABRIR INTERRUPTOR DE EMERGENCIA POSTE EN FUEGO | M23020700252 | New_Event | Fire | Include | Include | Public | 10 | 2023-02-07 | 35220 | keep | 0 | Feb | 2023 | 0.023988 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
BAYAMON | 2023-02-07 18:49 | 2023-02-08 | 42 | 5:11 | P | DESGANCHE | 1 X 65 EN C/L | B23020700133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2023-02-07 | 13062 | keep | 0 | Feb | 2023 | 0.0088965 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
HUMACAO | 2023-02-07 18:55 | 2023-02-07 18:56 | 1835 | 0:01 | T | DESGANCHE | RECIERRE | C23020700241 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-07 | 1835 | keep | 0 | Feb | 2023 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2023-02-07 18:56 | 2023-02-07 22:12 | 92 | 3:16 | P | DESGANCHE | 1 X 65 EN C/L | C23020700250 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-02-07 | 18032 | keep | 0 | Feb | 2023 | 0.012282 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
CAGUAS | 2023-02-07 19:00 | 2023-02-07 19:46 | 10 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE RETIRO CONDUCTOR SECUNDARIO VACANTE AVERIADO | C23020700242 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2023-02-07 | 460 | keep | 0 | Feb | 2023 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-07 19:04 | 2023-02-07 19:05 | 13 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 13 | keep | 0 | Feb | 2023 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-02-07 19:06 | 2023-02-07 19:42 | 2302 | 0:36 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR MACHETE QUEMADO | C23020700247 | Additional_clients | Switch Failure | Include | Include | Equipment | 36 | 2023-02-07 | 82872 | keep | 0 | Feb | 2023 | 0.056444 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-07 19:08 | 2023-02-07 22:46 | 80 | 3:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L POR LLUVIAS | S23020700126 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 218 | 2023-02-07 | 17440 | keep | 0 | Feb | 2023 | 0.011878 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-02-07 19:09 | 2023-02-07 19:10 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23020700249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 1307 | keep | 0 | Feb | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
VEGA BAJA | 2023-02-07 19:12 | 2023-02-07 20:26 | 2 | 1:14 | P | DESGANCHE | 1 X 15 EN XMR Y SE RETIRO ENREDADERA DEL BUSHING | B23020700139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-02-07 | 148 | keep | 0 | Feb | 2023 | 0.0001008 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-02-07 19:21 | 2023-02-07 19:22 | 1893 | 0:01 | T | DESGANCHE | RECIERRE | C23020700259 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-07 | 1893 | keep | 0 | Feb | 2023 | 0.0012893 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-07 19:22 | 2023-02-07 21:18 | 100 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | B23020700147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2023-02-07 | 11600 | keep | 0 | Feb | 2023 | 0.0079007 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-02-07 19:22 | 2023-02-07 19:45 | 16 | 0:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23020700180 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 23 | 2023-02-07 | 368 | keep | 0 | Feb | 2023 | 0.00025064 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-02-07 19:42 | 2023-02-07 20:07 | 323 | 0:25 | P | DESCONECTIVO DEFECTUOSO | CG-230207-02 SE REEMPLAZO MACHETE QUEMADO | C23020700114 | Partial_restoration | Switch Failure | Include | Include | Equipment | 25 | 2023-02-07 | 8075 | keep | 0 | Feb | 2023 | 0.0054998 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-07 19:42 | 2023-02-07 19:45 | 3387 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B2302070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-07 | 10161 | keep | 0 | Feb | 2023 | 0.0069206 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
ARECIBO | 2023-02-07 19:55 | 2023-02-07 19:56 | 2694 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23020700173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 2694 | keep | 0 | Feb | 2023 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2023-02-07 19:56 | 2023-02-07 21:00 | 30 | 1:04 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN CORTE DE LINEA SE SECCIONALIZO CABLE SOTERRADO AVERIADO ESA ES LA SECCIONALIZACION | A23020700135 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 64 | 2023-02-07 | 1920 | keep | 0 | Feb | 2023 | 0.0013077 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-02-07 20:05 | 2023-02-07 20:06 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23020700175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 3431 | keep | 0 | Feb | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2023-02-07 20:26 | 2023-02-08 09:07 | 8 | 12:41 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | B23020700183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 761 | 2023-02-07 | 6088 | keep | 0 | Feb | 2023 | 0.0041465 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-02-07 21:00 | 2023-02-08 09:02 | 12 | 12:02 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO LINEA AEREA PROVISIONAL | A23020700135 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 722 | 2023-02-07 | 8664 | keep | 0 | Feb | 2023 | 0.005901 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-07 21:16 | 2023-02-07 22:34 | 727 | 1:18 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO EN RISER DE SALIDA MEDIANTE G.O.I. SJ-230207-01 | S23020700172 | New_Event | Switch Failure | Include | Include | Equipment | 78 | 2023-02-07 | 56706 | keep | 0 | Feb | 2023 | 0.038622 | 0.00049516 | Sustained | FALSE | FALSE | Not_TMED_Event | 727
CAGUAS | 2023-02-07 21:25 | 2023-02-08 08:55 | 350 | 11:30 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE ELIMINO PARARRAYO DE MONTURA VIEJA | C23020700286 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 690 | 2023-02-07 | 241500 | keep | 0 | Feb | 2023 | 0.16448 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2023-02-07 21:46 | 2023-02-07 21:47 | 4089 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23020700192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-07 | 4089 | keep | 0 | Feb | 2023 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BAYAMON | 2023-02-07 22:02 | 2023-02-08 05:09 | 10 | 7:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIA | B23020700194 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 427 | 2023-02-07 | 4270 | keep | 0 | Feb | 2023 | 0.0029083 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-02-07 22:36 | 2023-02-07 22:37 | 508 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR AL CERRAR CL SE REMPLAZO CAJA PRIMARIA | P23020500232 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-07 | 508 | keep | 0 | Feb | 2023 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
SAN JUAN | 2023-02-07 22:44 | 2023-02-08 01:44 | 89 | 3:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR LLUVIA | S23020700184 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 180 | 2023-02-07 | 16020 | keep | 0 | Feb | 2023 | 0.010911 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
MAYAGÃœEZ | 2023-02-07 23:05 | 2023-02-08 09:45 | 30 | 10:40 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M23020700315 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 640 | 2023-02-07 | 19200 | keep | 0 | Feb | 2023 | 0.013077 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-02-07 23:05 | 2023-02-08 08:44 | 25 | 9:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020700315 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 579 | 2023-02-07 | 14475 | keep | 0 | Feb | 2023 | 0.0098589 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-02-07 23:08 | 2023-02-08 09:18 | 20 | 10:10 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23020700129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 610 | 2023-02-07 | 12200 | keep | 0 | Feb | 2023 | 0.0083094 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-07 23:51 | 2023-02-08 05:39 | 60 | 5:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 2X65 EN RISER POR LLUVIA | S23020700187 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 348 | 2023-02-07 | 20880 | keep | 0 | Feb | 2023 | 0.014221 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-02-08 00:03 | 2023-02-08 07:25 | 50 | 7:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23020800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2023-02-08 | 22100 | keep | 0 | Feb | 2023 | 0.015052 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-02-08 00:20 | 2023-02-08 07:25 | 60 | 7:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 425 | 2023-02-08 | 25500 | keep | 0 | Feb | 2023 | 0.017368 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-02-08 00:24 | 2023-02-08 10:30 | 27 | 10:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE DESGANCHO PALMA | C23020800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 606 | 2023-02-08 | 16362 | keep | 0 | Feb | 2023 | 0.011144 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2023-02-08 00:57 | 2023-02-08 07:54 | 30 | 6:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 417 | 2023-02-08 | 12510 | keep | 0 | Feb | 2023 | 0.0085205 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-02-08 01:02 | 2023-02-08 01:18 | 2524 | 0:16 | T | PARARRAYOS DEFECTUOSO | DISPARO CERRADO X CONTROL | R23020800002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 16 | 2023-02-08 | 40384 | keep | 0 | Feb | 2023 | 0.027505 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2023-02-08 01:18 | 2023-02-08 06:09 | 200 | 4:51 | P | PARARRAYOS DEFECTUOSO | 2 X 100 EN C/L SE ELIMINO PARARRAYO | R23020800004 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 291 | 2023-02-08 | 58200 | keep | 0 | Feb | 2023 | 0.03964 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-02-08 01:22 | 2023-02-08 10:50 | 14 | 9:28 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | C23020800004 | New_Event | Primary Wire Break | Include | Include | Equipment | 568 | 2023-02-08 | 7952 | keep | 0 | Feb | 2023 | 0.0054161 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-02-08 01:30 | 2023-02-08 09:10 | 60 | 7:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 460 | 2023-02-08 | 27600 | keep | 0 | Feb | 2023 | 0.018798 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-02-08 02:23 | 2023-02-08 03:56 | 40 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIA | B23020800002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2023-02-08 | 3720 | keep | 0 | Feb | 2023 | 0.0025337 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-02-08 03:31 | 2023-02-08 08:40 | 10 | 5:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA | R23020800013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 309 | 2023-02-08 | 3090 | keep | 0 | Feb | 2023 | 0.0021046 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-02-08 05:30 | 2023-02-08 10:20 | 40 | 4:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 290 | 2023-02-08 | 11600 | keep | 0 | Feb | 2023 | 0.0079007 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-02-08 05:31 | 2023-02-08 05:32 | 1227 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23020800019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-02-08 | 1227 | keep | 0 | Feb | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-02-08 05:33 | 2023-02-08 05:34 | 1227 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DEL INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | A23020800021 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-02-08 | 1227 | keep | 0 | Feb | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-02-08 05:34 | 2023-02-08 12:00 | 20 | 6:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800024 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 386 | 2023-02-08 | 7720 | keep | 0 | Feb | 2023 | 0.0052581 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-08 05:42 | 2023-02-08 13:30 | 56 | 7:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23020800009 | New_Event | Cutout Failure | Include | Include | Equipment | 468 | 2023-02-08 | 26208 | keep | 0 | Feb | 2023 | 0.01785 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
CANOVANAS | 2023-02-08 05:55 | 2023-02-08 10:25 | 90 | 4:30 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN C/L SE LEVANTO 2 ALAMBRES PROVISIONALES ARRIADOS | R23020800019 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 270 | 2023-02-08 | 24300 | keep | 0 | Feb | 2023 | 0.016551 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2023-02-08 06:09 | 2023-02-08 06:13 | 2524 | 0:04 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | R23020800020 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 4 | 2023-02-08 | 10096 | keep | 0 | Feb | 2023 | 0.0068763 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-02-08 06:13 | 2023-02-08 06:52 | 200 | 0:39 | P | PARARRAYOS DEFECTUOSO | 2 X 100 EN C/L SE ELIMINO PARARRAYO | R23020800004 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 39 | 2023-02-08 | 7800 | keep | 0 | Feb | 2023 | 0.0053125 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-02-08 06:25 | 2023-02-08 06:26 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-08 | 5252 | keep | 0 | Feb | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2023-02-08 06:27 | 2023-02-08 10:34 | 322 | 4:07 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B23020800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2023-02-08 | 79534 | keep | 0 | Feb | 2023 | 0.05417 | 0.00021931 | Sustained | FALSE | FALSE | Not_TMED_Event | 322
ARECIBO | 2023-02-08 06:28 | 2023-02-08 12:45 | 100 | 6:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800030 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 377 | 2023-02-08 | 37700 | keep | 0 | Feb | 2023 | 0.025677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-08 06:33 | 2023-02-08 06:34 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-08 | 57 | keep | 0 | Feb | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2023-02-08 06:40 | 2023-02-08 12:55 | 60 | 6:15 | P | DESGANCHE | 2 X 100 EN C/L Y DESGANCHE | S23020800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2023-02-08 | 22500 | keep | 0 | Feb | 2023 | 0.015325 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-02-08 06:58 | 2023-02-08 10:45 | 3 | 3:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800031 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 227 | 2023-02-08 | 681 | keep | 0 | Feb | 2023 | 0.00046383 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-02-08 07:00 | 2023-02-08 11:30 | 2 | 4:30 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M23020800035 | New_Event | Animals | Include | Include | Wildlife | 270 | 2023-02-08 | 540 | keep | 0 | Feb | 2023 | 0.00036779 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-02-08 07:11 | 2023-02-08 07:12 | 1261 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23020800021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-08 | 1261 | keep | 0 | Feb | 2023 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
SAN JUAN | 2023-02-08 07:23 | 2023-02-08 09:15 | 4 | 1:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23020800013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2023-02-08 | 448 | keep | 0 | Feb | 2023 | 0.00030513 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-02-08 07:37 | 2023-02-08 10:40 | 80 | 3:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800039 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 183 | 2023-02-08 | 14640 | keep | 0 | Feb | 2023 | 0.0099712 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-02-08 07:41 | 2023-02-08 16:00 | 12 | 8:19 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR DE 100 KVA AVERIADO SE LE DA SERVICIO A LOS CLIENTES DE OTRO CIRCUITO EL LO QUE SE CONSIGUE TRANSFORMADOR NUEVO | P23020800075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 499 | 2023-02-08 | 5988 | keep | 0 | Feb | 2023 | 0.0040784 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-08 08:03 | 2023-02-08 09:27 | 6 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA SE SUBIO TAP DEL 1 AL 2 124V POR FASE | B23020800014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2023-02-08 | 504 | keep | 0 | Feb | 2023 | 0.00034327 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-02-08 08:04 | 2023-02-08 13:47 | 14 | 5:43 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | ABRIR C/L DE EMERGENCIA PARA REEMPLAZO DE POSTE PARTIDO EN EL SUELO | R23020800030 | New_Event | Primary Pole Failure | Include | Include | Equipment | 343 | 2023-02-08 | 4802 | keep | 0 | Feb | 2023 | 0.0032706 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
FAJARDO | 2023-02-08 08:09 | 2023-02-08 08:55 | 3 | 0:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO PORTAFUSIBLE | R23020800028 | New_Event | Cutout Failure | Include | Include | Equipment | 46 | 2023-02-08 | 138 | keep | 0 | Feb | 2023 | 9.3991e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-02-08 08:17 | 2023-02-08 13:50 | 80 | 5:33 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASES | M23020800023 | New_Event | Animals | Include | Include | Wildlife | 333 | 2023-02-08 | 26640 | keep | 0 | Feb | 2023 | 0.018144 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-02-08 08:33 | 2023-02-08 11:07 | 80 | 2:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23020800027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 154 | 2023-02-08 | 12320 | keep | 0 | Feb | 2023 | 0.0083911 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-02-08 08:35 | 2023-02-08 11:10 | 40 | 2:35 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23020800034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-02-08 | 6200 | keep | 0 | Feb | 2023 | 0.0042228 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-02-08 08:38 | 2023-02-08 13:57 | 10 | 5:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23020800028 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 319 | 2023-02-08 | 3190 | keep | 0 | Feb | 2023 | 0.0021727 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-08 08:49 | 2023-02-08 10:05 | 25 | 1:16 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23020800032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-02-08 | 1900 | keep | 0 | Feb | 2023 | 0.0012941 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-02-08 09:02 | 2023-02-08 09:46 | 2694 | 0:44 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR POR LINEA SAFADA DEL AISLADOR Y CRUZANDO CON SECUNDARIA | A23020800061 | New_Event | Primary Wire Break | Include | Include | Equipment | 44 | 2023-02-08 | 118536 | keep | 0 | Feb | 2023 | 0.080734 | 0.0018349 | Sustained | FALSE | FALSE | Not_TMED_Event | 2694
VEGA BAJA | 2023-02-08 09:08 | 2023-02-08 13:14 | 7 | 4:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR POR PORTAFUSIBLE QUEMADO | A23020800063 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2023-02-08 | 1722 | keep | 0 | Feb | 2023 | 0.0011728 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-02-08 09:11 | 2023-02-08 12:00 | 121 | 2:49 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | B23020800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-02-08 | 20449 | keep | 0 | Feb | 2023 | 0.013928 | 8.2413e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 121
SAN JUAN | 2023-02-08 09:15 | 2023-02-08 12:48 | 5 | 3:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA | S23020800027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2023-02-08 | 1065 | keep | 0 | Feb | 2023 | 0.00072537 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-02-08 09:23 | 2023-02-08 09:25 | 1588 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2302080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-08 | 3176 | keep | 0 | Feb | 2023 | 0.0021632 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
MAYAGÃœEZ | 2023-02-08 09:25 | 2023-02-08 15:15 | 10 | 5:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | M23020800039 | New_Event | Primary Pole Failure | Include | Include | Equipment | 350 | 2023-02-08 | 3500 | keep | 0 | Feb | 2023 | 0.0023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-08 09:29 | 2023-02-08 13:15 | 13 | 3:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C23020800060 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2023-02-08 | 2938 | keep | 0 | Feb | 2023 | 0.0020011 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2023-02-08 09:39 | 2023-02-08 12:43 | 13 | 3:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | C23020800065 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2023-02-08 | 2392 | keep | 0 | Feb | 2023 | 0.0016292 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2023-02-08 09:45 | 2023-02-08 10:57 | 6 | 1:12 | P | CAUSAS EXTERNAS | 2 X 80 EN C/L PERSONAS AJENAS A LUMA CORTARON UNAS RAMAS Y CAYERON ENCIMA DE LA LINEA | R23020800044 | New_Event | Damage From Public | Include | Include | Public | 72 | 2023-02-08 | 432 | keep | 0 | Feb | 2023 | 0.00029423 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-02-08 09:46 | 2023-02-08 15:20 | 12 | 5:34 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO LINEA AEREA PROVISIONAL | A23020700135 | New_Event | UG Cable Fault | Include | Include | Equipment | 334 | 2023-02-08 | 4008 | keep | 0 | Feb | 2023 | 0.0027298 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-02-08 09:46 | 2023-02-08 11:39 | 800 | 1:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA SAFADA DEL AISLADOR | A23020800102 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 113 | 2023-02-08 | 90400 | keep | 0 | Feb | 2023 | 0.061571 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-08 09:51 | 2023-02-08 17:22 | 3 | 7:31 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEA ARRIADA | S23020800035 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 451 | 2023-02-08 | 1353 | keep | 0 | Feb | 2023 | 0.00092152 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-08 09:53 | 2023-02-08 09:56 | 4431 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2302080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-08 | 13293 | keep | 0 | Feb | 2023 | 0.0090538 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2023-02-08 09:54 | 2023-02-08 12:39 | 16 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIEMPO LLUVIAS | B23020800033 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-02-08 | 2640 | keep | 0 | Feb | 2023 | 0.0017981 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-02-08 09:56 | 2023-02-08 11:17 | 154 | 1:21 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23020800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-02-08 | 12474 | keep | 0 | Feb | 2023 | 0.008496 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2023-02-08 09:57 | 2023-02-08 15:03 | 60 | 5:06 | P | TERMINACION SOTERRADA AVERIADA | 1 X 65 EN PROVISIONAL SE RETIRO TERMINACION EN DESHUSO | S23020800038 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 306 | 2023-02-08 | 18360 | keep | 0 | Feb | 2023 | 0.012505 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-02-08 10:00 | 2023-02-08 12:40 | 3 | 2:40 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23020800093 | New_Event | Animals | Include | Include | Wildlife | 160 | 2023-02-08 | 480 | keep | 0 | Feb | 2023 | 0.00032693 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-02-08 10:01 | 2023-02-08 12:00 | 13 | 1:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA X 25KVA LIQUEANDO | R23020800049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 119 | 2023-02-08 | 1547 | keep | 0 | Feb | 2023 | 0.0010537 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-02-08 10:08 | 2023-02-08 11:34 | 348 | 1:26 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | B23020800043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-02-08 | 29928 | keep | 0 | Feb | 2023 | 0.020384 | 0.00023702 | Sustained | FALSE | FALSE | Not_TMED_Event | 348
VEGA BAJA | 2023-02-08 10:10 | 2023-02-08 10:11 | 4027 | 0:01 | T | DESGANCHE | RCIERRE DE INTERRUPTOR | B2302080000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-08 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-02-08 10:11 | 2023-02-08 13:06 | 20 | 2:55 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE PRIMARIO | B23020800045 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-02-08 | 3500 | keep | 0 | Feb | 2023 | 0.0023838 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-08 10:11 | 2023-02-08 10:12 | 2234 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DE INTERRUPTOR | B2302080000X | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2023-02-08 | 2234 | keep | 0 | Feb | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
VEGA BAJA | 2023-02-08 10:12 | 2023-02-08 15:37 | 20 | 5:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO VIENTOS | B23020800106 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 325 | 2023-02-08 | 6500 | keep | 0 | Feb | 2023 | 0.0044271 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-08 10:12 | 2023-02-08 13:18 | 169 | 3:06 | P | ARBOL SOBRE LINEA | 3 X 80 EN C/L SE REMOVIO ARBOL | B23020800046 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 186 | 2023-02-08 | 31434 | keep | 0 | Feb | 2023 | 0.02141 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
PONCE | 2023-02-08 10:17 | 2023-02-08 12:09 | 1 | 1:52 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER/ NO SE ENCUENTRAN CAUSAS | P23020800079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2023-02-08 | 112 | keep | 0 | Feb | 2023 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-08 10:23 | 2023-02-08 17:48 | 14 | 7:25 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE SECUNDARIO SE REEMPLAZARON 100'1/0 Y 20 3/4 | C23020800079 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 445 | 2023-02-08 | 6230 | keep | 0 | Feb | 2023 | 0.0042432 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-02-08 10:24 | 2023-02-08 12:20 | 15 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L | S23020800044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2023-02-08 | 1740 | keep | 0 | Feb | 2023 | 0.0011851 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-02-08 10:24 | 2023-02-08 17:42 | 134 | 7:18 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L Y SE LEVANTO CONDUCTOR PRIMARIO | C23020800080 | New_Event | Primary Wire Break | Include | Include | Equipment | 438 | 2023-02-08 | 58692 | keep | 0 | Feb | 2023 | 0.039975 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2023-02-08 10:30 | 2023-02-08 10:49 | 35 | 0:19 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23020800051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 19 | 2023-02-08 | 665 | keep | 0 | Feb | 2023 | 0.00045293 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-02-08 10:33 | 2023-02-08 14:31 | 75 | 3:58 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARARON LINEAS PRIMARIAS CRUZADAS | A23020800108 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 238 | 2023-02-08 | 17850 | keep | 0 | Feb | 2023 | 0.012158 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-02-08 10:34 | 2023-02-08 12:45 | 5 | 2:11 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE REPARO CONEXIONES PRIMARIAS | S23020800049 | New_Event | Primary Wire Break | Include | Include | Equipment | 131 | 2023-02-08 | 655 | keep | 0 | Feb | 2023 | 0.00044612 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-02-08 10:39 | 2023-02-08 17:50 | 25 | 7:11 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN XMR SE REEMPLAZO XMR DE 25KVA X UNO DE 50KVA | R23020800055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 431 | 2023-02-08 | 10775 | keep | 0 | Feb | 2023 | 0.0073388 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-08 10:43 | 2023-02-08 13:28 | 50 | 2:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CL 1 X 50 EN BANCO SE REMPLAZO CAJA PRIMARIA | S23020800054 | New_Event | Cutout Failure | Include | Include | Equipment | 165 | 2023-02-08 | 8250 | keep | 0 | Feb | 2023 | 0.005619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-08 10:47 | 2023-02-08 10:48 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2302080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-08 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
VEGA BAJA | 2023-02-08 11:27 | 2023-02-08 11:28 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-08 | 3000 | keep | 0 | Feb | 2023 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2023-02-08 11:30 | 2023-02-08 18:15 | 7 | 6:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23020800066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 405 | 2023-02-08 | 2835 | keep | 0 | Feb | 2023 | 0.0019309 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-02-08 11:41 | 2023-02-08 13:46 | 828 | 2:05 | T | NO SE REPORTO CAUSA | SE ABRIO CORTE DE LINEA Y SE CERRO INTERRUPTOR PARA CONTINUAR PATRULLANDO | M23020800063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2023-02-08 | 103500 | keep | 0 | Feb | 2023 | 0.070493 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
ARECIBO | 2023-02-08 11:43 | 2023-02-08 15:19 | 15 | 3:36 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23020800130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2023-02-08 | 3240 | keep | 0 | Feb | 2023 | 0.0022067 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-02-08 11:45 | 2023-02-08 15:22 | 20 | 3:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE LINEAS SECUNDARIAS | A23020800038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 217 | 2023-02-08 | 4340 | keep | 0 | Feb | 2023 | 0.002956 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-02-08 12:04 | 2023-02-08 14:20 | 80 | 2:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020800068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-02-08 | 10880 | keep | 0 | Feb | 2023 | 0.0074103 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-02-08 12:14 | 2023-02-08 12:32 | 3 | 0:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23020800020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 18 | 2023-02-08 | 54 | keep | 0 | Feb | 2023 | 3.6779e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-02-08 12:21 | 2023-02-08 16:00 | 32 | 3:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 40 EN C/L | C23020800118 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2023-02-08 | 7008 | keep | 0 | Feb | 2023 | 0.0047731 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BARRANQUITAS | 2023-02-08 12:34 | 2023-02-08 13:53 | 24 | 1:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23020800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-02-08 | 1896 | keep | 0 | Feb | 2023 | 0.0012914 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-02-08 12:49 | 2023-02-08 14:46 | 50 | 1:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23020800096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-02-08 | 5850 | keep | 0 | Feb | 2023 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-08 12:56 | 2023-02-08 14:59 | 4 | 2:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y PORTA FUSIBLE Y SE REPUSO 1X40 EN RISER. | C23020800122 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 123 | 2023-02-08 | 492 | keep | 0 | Feb | 2023 | 0.0003351 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-02-08 12:56 | 2023-02-08 14:15 | 5 | 1:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23020800096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 79 | 2023-02-08 | 395 | keep | 0 | Feb | 2023 | 0.00026903 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-02-08 12:58 | 2023-02-08 17:58 | 30 | 5:00 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23020800140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-02-08 | 9000 | keep | 0 | Feb | 2023 | 0.0061299 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-08 12:59 | 2023-02-08 13:07 | 842 | 0:08 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S23020800101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2023-02-08 | 6736 | keep | 0 | Feb | 2023 | 0.0045879 | 0.00057348 | Sustained | FALSE | FALSE | Not_TMED_Event | 842
ARECIBO | 2023-02-08 13:00 | 2023-02-08 15:50 | 30 | 2:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800141 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 170 | 2023-02-08 | 5100 | keep | 0 | Feb | 2023 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-02-08 13:01 | 2023-02-08 16:46 | 100 | 3:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CL FUERTES VIENTOS | M23020800101 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 225 | 2023-02-08 | 22500 | keep | 0 | Feb | 2023 | 0.015325 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-02-08 13:10 | 2023-02-08 13:42 | 7 | 0:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23020800125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2023-02-08 | 224 | keep | 0 | Feb | 2023 | 0.00015257 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-02-08 13:11 | 2023-02-08 16:38 | 14 | 3:27 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23020800088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-02-08 | 2898 | keep | 0 | Feb | 2023 | 0.0019738 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-02-08 13:25 | 2023-02-08 13:26 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23020800109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-08 | 2067 | keep | 0 | Feb | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
BAYAMON | 2023-02-08 13:30 | 2023-02-08 16:11 | 20 | 2:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23020800058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 161 | 2023-02-08 | 3220 | keep | 0 | Feb | 2023 | 0.0021931 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-02-08 13:31 | 2023-02-08 13:32 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23020800113 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-08 | 2067 | keep | 0 | Feb | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
HUMACAO | 2023-02-08 13:37 | 2023-02-08 15:14 | 10 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO VIENTOS | C23020800135 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2023-02-08 | 970 | keep | 0 | Feb | 2023 | 0.00066066 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-08 13:40 | 2023-02-08 16:55 | 3 | 3:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA EN XMR | R23020800066 | New_Event | Primary Wire Break | Include | Include | Equipment | 195 | 2023-02-08 | 585 | keep | 0 | Feb | 2023 | 0.00039844 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-02-08 13:44 | 2023-02-08 15:20 | 152 | 1:36 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO PARA CERRAR PUENTE PRIMARIO | S23020800115 | New_Event | Primary Wire Break | Include | Include | Equipment | 96 | 2023-02-08 | 14592 | keep | 0 | Feb | 2023 | 0.0099385 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
AGUADILLA | 2023-02-08 13:46 | 2023-02-08 14:49 | 400 | 1:03 | P | NO SE REPORTO CAUSA | SE PATRULLO EL ALIMENTADOR NO SE IDENTIFICO CAUSA SE CERRO CORTE DE LINEA | M23020800063 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 63 | 2023-02-08 | 25200 | keep | 0 | Feb | 2023 | 0.017164 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-08 14:34 | 2023-02-08 17:03 | 20 | 2:29 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | S23020800141 | New_Event | Primary Wire Break | Include | Include | Equipment | 149 | 2023-02-08 | 2980 | keep | 0 | Feb | 2023 | 0.0020297 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-08 14:35 | 2023-02-08 18:10 | 30 | 3:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23020800143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2023-02-08 | 6450 | keep | 0 | Feb | 2023 | 0.0043931 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-02-08 14:41 | 2023-02-08 17:49 | 170 | 3:08 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23020800152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-02-08 | 31960 | keep | 0 | Feb | 2023 | 0.021768 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
BAYAMON | 2023-02-08 14:52 | 2023-02-08 18:25 | 16 | 3:33 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23020800147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-02-08 | 3408 | keep | 0 | Feb | 2023 | 0.0023212 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
YAUCO | 2023-02-08 15:23 | 2023-02-10 18:30 | 1 | 51:07 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANSFORMADOR SE FIJO BUSHING Y SE RECONECTO NEUTRAL PRIMARIO EVENTO DEL DIA 7 | P23020700025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3067 | 2023-02-08 | 3067 | keep | 0 | Feb | 2023 | 0.0020889 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-02-08 15:27 | 2023-02-08 17:10 | 12 | 1:43 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO LINEA AEREA PROVISIONAL | A23020700135 | New_Event | UG Cable Fault | Include | Include | Equipment | 103 | 2023-02-08 | 1236 | keep | 0 | Feb | 2023 | 0.00084183 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-08 15:33 | 2023-02-08 16:08 | 152 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO PARA CERRAR PUENTE PRIMARIO | S23020800115 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 35 | 2023-02-08 | 5320 | keep | 0 | Feb | 2023 | 0.0036234 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-02-08 15:40 | 2023-02-08 18:30 | 10 | 2:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZAR BAJANTES SECUNDARIOS | A23020800190 | New_Event | Secondary Wire Break | Include | Include | Equipment | 170 | 2023-02-08 | 1700 | keep | 0 | Feb | 2023 | 0.0011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-02-08 15:57 | 2023-02-08 17:41 | 8 | 1:44 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23020800240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-02-08 | 832 | keep | 0 | Feb | 2023 | 0.00056667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-02-08 15:58 | 2023-02-08 16:52 | 150 | 0:54 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMA | P23020800215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2023-02-08 | 8100 | keep | 0 | Feb | 2023 | 0.0055169 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-02-08 15:59 | 2023-02-08 17:35 | 40 | 1:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CL FUERTES VIENTOS | M23020800189 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2023-02-08 | 3840 | keep | 0 | Feb | 2023 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-08 16:08 | 2023-02-08 17:09 | 778 | 1:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y SE NORMALIZO CARGA | S23020800115 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 61 | 2023-02-08 | 47458 | keep | 0 | Feb | 2023 | 0.032323 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-08 16:30 | 2023-02-08 20:33 | 16 | 4:03 | P | DESGANCHE | 2 X 100 EN C/L | B23020800240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-02-08 | 3888 | keep | 0 | Feb | 2023 | 0.0026481 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2023-02-08 16:41 | 2023-02-08 19:10 | 16 | 2:29 | P | ERROR HUMANO | 2 X 65 EN CORTE DE LINEA COMP.WRIGH TREE REALIZANDO DESGANCHE CRUZARON FASE | P23020800232 | New_Event | Human Error | Include | Include | Other | 149 | 2023-02-08 | 2384 | keep | 0 | Feb | 2023 | 0.0016237 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2023-02-08 16:42 | 2023-02-08 18:18 | 8 | 1:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23020800223 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2023-02-08 | 768 | keep | 0 | Feb | 2023 | 0.00052308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-02-08 16:47 | 2023-02-08 17:40 | 1474 | 0:53 | T | PROBLEMA DEL CLIENTE | DISPARO DE INTERRUPTOR AL HACER PRUEBA EN SUBESTACION DE CLIENTE (PROA) PERSONAL DE SUBESTACIONES INSPECCIONO BKR POR FTO Y ENCONTRO NO HABIA AC. SE CERRO POR CONTROL | R23020800226 | New_Event | Customer-Related Interruption | Include | Include | Public | 53 | 2023-02-08 | 78122 | keep | 0 | Feb | 2023 | 0.053209 | 0.0010039 | Sustained | FALSE | FALSE | Not_TMED_Event | 1474
AGUADILLA | 2023-02-08 16:52 | 2023-02-08 20:30 | 80 | 3:38 | P | CAUSAS EXTERNAS | 1 X 100 EN CL CAMION CAUSA CURCE DE FASE Y NEUTRAL PRIMARIO | M23020800243 | New_Event | Damage From Public | Include | Include | Public | 218 | 2023-02-08 | 17440 | keep | 0 | Feb | 2023 | 0.011878 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-02-08 17:44 | 2023-02-08 20:16 | 104 | 2:32 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L CAMION SE CRUZO CABLES DE COMUNICACION | C23020800336 | New_Event | Damage From Public | Include | Include | Public | 152 | 2023-02-08 | 15808 | keep | 0 | Feb | 2023 | 0.010767 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
BAYAMON | 2023-02-08 17:55 | 2023-02-08 18:21 | 1 | 0:26 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23020800298 | New_Event | Animals | Include | Include | Wildlife | 26 | 2023-02-08 | 26 | keep | 0 | Feb | 2023 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-08 18:02 | 2023-02-08 18:27 | 13 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | C23020800343 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-02-08 | 325 | keep | 0 | Feb | 2023 | 0.00022136 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2023-02-08 18:16 | 2023-02-09 09:15 | 100 | 14:59 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA CAMION IMPACTO LINEAS | M23020800235 | New_Event | Damage From Public | Include | Include | Public | 899 | 2023-02-08 | 89900 | keep | 0 | Feb | 2023 | 0.06123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-08 18:20 | 2023-02-08 20:42 | 8 | 2:22 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN C/L DESGANCHE | B23020800314 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-02-08 | 1136 | keep | 0 | Feb | 2023 | 0.00077372 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-08 18:20 | 2023-02-08 19:00 | 15 | 0:40 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS CRUZADOS | M23020800211 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 40 | 2023-02-08 | 600 | keep | 0 | Feb | 2023 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-02-08 18:21 | 2023-02-08 20:23 | 30 | 2:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23020800255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-02-08 | 3660 | keep | 0 | Feb | 2023 | 0.0024928 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-08 18:22 | 2023-02-08 19:46 | 62 | 1:24 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S23020800424 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2023-02-08 | 5208 | keep | 0 | Feb | 2023 | 0.0035471 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
CAGUAS | 2023-02-08 18:33 | 2023-02-08 18:51 | 4 | 0:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | C23020800371 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2023-02-08 | 72 | keep | 0 | Feb | 2023 | 4.9039e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-02-08 19:14 | 2023-02-09 13:10 | 75 | 17:56 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERRIA PARA SER TRABAJADA | C23020800399 | New_Event | UG Cable Fault | Include | Include | Equipment | 1076 | 2023-02-08 | 80700 | keep | 0 | Feb | 2023 | 0.054964 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2023-02-08 19:26 | 2023-02-08 20:39 | 30 | 1:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23020800265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-02-08 | 2190 | keep | 0 | Feb | 2023 | 0.0014916 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-08 19:27 | 2023-02-08 20:49 | 37 | 1:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S23020800449 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 82 | 2023-02-08 | 3034 | keep | 0 | Feb | 2023 | 0.0020664 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CANOVANAS | 2023-02-08 19:40 | 2023-02-08 20:51 | 99 | 1:11 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23020800301 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-02-08 | 7029 | keep | 0 | Feb | 2023 | 0.0047874 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
VEGA BAJA | 2023-02-08 19:42 | 2023-02-08 22:16 | 70 | 2:34 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | B23020800350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-02-08 | 10780 | keep | 0 | Feb | 2023 | 0.0073422 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-02-08 19:48 | 2023-02-08 21:21 | 15 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23020800267 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2023-02-08 | 1395 | keep | 0 | Feb | 2023 | 0.00095013 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-08 20:18 | 2023-02-08 21:36 | 20 | 1:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | S23020800458 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2023-02-08 | 1560 | keep | 0 | Feb | 2023 | 0.0010625 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-02-08 20:44 | 2023-02-09 08:44 | 50 | 12:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23020800351 | New_Event | Vegetation Contact | Include | Include | Vegetation | 720 | 2023-02-08 | 36000 | keep | 0 | Feb | 2023 | 0.024519 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-08 20:54 | 2023-02-09 13:43 | 19 | 16:49 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE SE SECCIONALIZO ARREA PARA DESGANCHE | B23020800360 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1009 | 2023-02-08 | 19171 | keep | 0 | Feb | 2023 | 0.013057 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2023-02-08 21:11 | 2023-02-08 23:54 | 70 | 2:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REEMPLAZO AISLADOR | C23020800416 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 163 | 2023-02-08 | 11410 | keep | 0 | Feb | 2023 | 0.0077713 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2023-02-08 21:25 | 2023-02-09 02:03 | 50 | 4:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C23020800420 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 278 | 2023-02-08 | 13900 | keep | 0 | Feb | 2023 | 0.0094672 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-02-08 22:00 | 2023-02-09 07:09 | 19 | 9:09 | P | CAUSAS EXTERNAS | 1 X 25 EN XMR SE RETIRO TENSOR CRUZADO | S23020800456 | New_Event | Damage From Public | Include | Include | Public | 549 | 2023-02-08 | 10431 | keep | 0 | Feb | 2023 | 0.0071045 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2023-02-08 22:37 | 2023-02-09 08:25 | 12 | 9:48 | P | ARBOL SOBRE LINEA | 1 X 10 EN XMR 1 X 30 EN C/L SE RETIRO ARBOL SOBRE LINEA | C23020800016 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 588 | 2023-02-08 | 7056 | keep | 0 | Feb | 2023 | 0.0048058 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-02-08 22:45 | 2023-02-09 10:48 | 60 | 12:03 | P | TERMINACION SOTERRADA AVERIADA | 1 X 65 Y 1 X 40 EN AEREO PROVISIONAL SE REPARO TERMINACION EN AEREO PROVISIONAL | R23020800309 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 723 | 2023-02-08 | 43380 | keep | 0 | Feb | 2023 | 0.029546 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 22:51 | 1894 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800344 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-02-08 | 1894 | keep | 0 | Feb | 2023 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 22:51 | 4154 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800344 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-02-08 | 4154 | keep | 0 | Feb | 2023 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 22:51 | 424 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800344 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-02-08 | 424 | keep | 0 | Feb | 2023 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 22:51 | 2708 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800345 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-02-08 | 2708 | keep | 0 | Feb | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 22:51 | 2524 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800345 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-02-08 | 2524 | keep | 0 | Feb | 2023 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 22:51 | 1648 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800345 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-02-08 | 1648 | keep | 0 | Feb | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 22:54 | 3838 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800341 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-02-08 | 15352 | keep | 0 | Feb | 2023 | 0.010456 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 22:54 | 817 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800341 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-02-08 | 3268 | keep | 0 | Feb | 2023 | 0.0022258 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 22:54 | 1124 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800341 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-02-08 | 4496 | keep | 0 | Feb | 2023 | 0.0030622 | 0.00076555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1124
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 23:02 | 2580 | 0:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800347 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2023-02-08 | 30960 | keep | 0 | Feb | 2023 | 0.021087 | 0.0017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2023-02-08 22:50 | 2023-02-08 23:02 | 500 | 0:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE CANOVANAS TC PUENTE ABIERTO EN ACB 11101B | R23020800347 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2023-02-08 | 6000 | keep | 0 | Feb | 2023 | 0.0040866 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2023-02-08 22:51 | 2023-02-09 01:40 | 30 | 2:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | B23020800392 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 169 | 2023-02-08 | 5070 | keep | 0 | Feb | 2023 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-08 22:57 | 2023-02-09 00:59 | 1519 | 2:02 | P | DESGANCHE | SE RETIRO RAMA SOBRE LINEA CON VARETA DE PISO Y SE CERRO PB-1B | B23020800394 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-02-08 | 185318 | keep | 0 | Feb | 2023 | 0.12622 | 0.0010346 | Sustained | FALSE | FALSE | Not_TMED_Event | 1519
VEGA BAJA | 2023-02-08 23:44 | 2023-02-09 10:57 | 12 | 11:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23020800406 | New_Event | Secondary Wire Break | Include | Include | Equipment | 673 | 2023-02-08 | 8076 | keep | 0 | Feb | 2023 | 0.0055005 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-02-09 01:17 | 2023-02-09 01:18 | 6285 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23020900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 6285 | keep | 0 | Feb | 2023 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
VEGA BAJA | 2023-02-09 01:28 | 2023-02-09 07:15 | 38 | 5:47 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23020900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2023-02-09 | 13186 | keep | 0 | Feb | 2023 | 0.0089809 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CANOVANAS | 2023-02-09 02:12 | 2023-02-09 09:14 | 10 | 7:02 | P | ANIMAL | 1 X 140 EN C/L CRUCE POR AVE | R23020900012 | New_Event | Animals | Include | Include | Wildlife | 422 | 2023-02-09 | 4220 | keep | 0 | Feb | 2023 | 0.0028742 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-09 03:08 | 2023-02-09 05:34 | 62 | 2:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S23020900005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 146 | 2023-02-09 | 9052 | keep | 0 | Feb | 2023 | 0.0061653 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-02-09 03:09 | 2023-02-09 09:47 | 15 | 6:38 | P | ANIMAL | SE REEMPLAZO CAJA Y 1 X 25 EN XMR CRUCE POR IGUANA | S23020900006 | New_Event | Animals | Include | Include | Wildlife | 398 | 2023-02-09 | 5970 | keep | 0 | Feb | 2023 | 0.0040661 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-02-09 03:48 | 2023-02-09 03:49 | 108 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR RAMAS SOBRE LAS LINEAS | M23020900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-09 | 108 | keep | 0 | Feb | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2023-02-09 03:49 | 2023-02-09 10:15 | 100 | 6:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020900010 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 386 | 2023-02-09 | 38600 | keep | 0 | Feb | 2023 | 0.02629 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-09 04:24 | 2023-02-09 04:25 | 3871 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECERRO INTERRUPTOR | B23020900000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-02-09 | 3871 | keep | 0 | Feb | 2023 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
BAYAMON | 2023-02-09 04:25 | 2023-02-09 11:05 | 10 | 6:40 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRYO SE CERRO XMR | B23020900048 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 400 | 2023-02-09 | 4000 | keep | 0 | Feb | 2023 | 0.0027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-09 04:49 | 2023-02-09 04:50 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | B23020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 5252 | keep | 0 | Feb | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2023-02-09 04:50 | 2023-02-09 09:23 | 105 | 4:33 | P | ANIMAL | 1 X 65 CRUCE POR AVE | B23020900009 | New_Event | Animals | Include | Include | Wildlife | 273 | 2023-02-09 | 28665 | keep | 0 | Feb | 2023 | 0.019524 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
SAN JUAN | 2023-02-09 04:56 | 2023-02-09 09:49 | 1 | 4:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR Y SE REMPLAZO CAJA A PRIMARIA | S23020900010 | New_Event | Cutout Failure | Include | Include | Equipment | 293 | 2023-02-09 | 293 | keep | 0 | Feb | 2023 | 0.00019956 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-09 05:12 | 2023-02-09 07:38 | 70 | 2:26 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23020900010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-02-09 | 10220 | keep | 0 | Feb | 2023 | 0.0069608 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-02-09 05:30 | 2023-02-09 10:30 | 8 | 5:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE TRANSFORMADOR | A23020900002 | New_Event | Cutout Failure | Include | Include | Equipment | 300 | 2023-02-09 | 2400 | keep | 0 | Feb | 2023 | 0.0016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-02-09 05:36 | 2023-02-09 10:01 | 12 | 4:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRRANSFORMADOR SE REMPLAZO CAJA AVERIADA | A23020900003 | New_Event | Cutout Failure | Include | Include | Equipment | 265 | 2023-02-09 | 3180 | keep | 0 | Feb | 2023 | 0.0021659 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-09 06:02 | 2023-02-09 15:16 | 46 | 9:14 | S | PARARRAYOS DEFECTUOSO | FUNDIO FUSIBLE 38KV 3 X 150 STD SPEED Y SE INSTALO TIERRAS EN PARARRAYO EN BARRA SE LAS HABIAN HRUTADO | S23020900080 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 554 | 2023-02-09 | 25484 | keep | 0 | Feb | 2023 | 0.017357 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
BARRANQUITAS | 2023-02-09 06:25 | 2023-02-09 10:10 | 30 | 3:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO AISLADOR AVERIADO | C23020900012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 225 | 2023-02-09 | 6750 | keep | 0 | Feb | 2023 | 0.0045974 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-02-09 06:31 | 2023-02-09 09:00 | 8 | 2:29 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR SE DESCONECTO CLIENTE CON BASE DE CONTADOR QUEMADA | A23020900005 | New_Event | Other Causes | Include | Include | Other | 149 | 2023-02-09 | 1192 | keep | 0 | Feb | 2023 | 0.00081187 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-09 06:36 | 2023-02-09 10:34 | 100 | 3:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23020900015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 238 | 2023-02-09 | 23800 | keep | 0 | Feb | 2023 | 0.01621 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-02-09 06:45 | 2023-02-09 10:05 | 60 | 3:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23020900017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-02-09 | 12000 | keep | 0 | Feb | 2023 | 0.0081731 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-02-09 06:51 | 2023-02-09 06:52 | 4028 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B23020900010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-09 | 4028 | keep | 0 | Feb | 2023 | 0.0027435 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2023-02-09 06:52 | 2023-02-09 11:55 | 25 | 5:03 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23020900026 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 303 | 2023-02-09 | 7575 | keep | 0 | Feb | 2023 | 0.0051593 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-02-09 07:06 | 2023-02-09 10:08 | 3 | 3:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA Y BAJANTE DE LINEA A CAJA | A23020900007 | New_Event | Cutout Failure | Include | Include | Equipment | 182 | 2023-02-09 | 546 | keep | 0 | Feb | 2023 | 0.00037188 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-09 07:19 | 2023-02-09 07:20 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23020900017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 5252 | keep | 0 | Feb | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2023-02-09 07:23 | 2023-02-09 07:24 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23020900018 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 5252 | keep | 0 | Feb | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
PONCE | 2023-02-09 07:36 | 2023-02-09 10:10 | 50 | 2:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P23020900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-02-09 | 7700 | keep | 0 | Feb | 2023 | 0.0052444 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-02-09 07:36 | 2023-02-09 12:35 | 15 | 4:59 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | P23020900018 | New_Event | Primary Wire Break | Include | Include | Equipment | 299 | 2023-02-09 | 4485 | keep | 0 | Feb | 2023 | 0.0030547 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-09 07:40 | 2023-02-09 13:35 | 10 | 5:55 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23020900016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2023-02-09 | 3550 | keep | 0 | Feb | 2023 | 0.0024179 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-09 07:40 | 2023-02-09 10:30 | 50 | 2:50 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23020900019 | New_Event | Animals | Include | Include | Wildlife | 170 | 2023-02-09 | 8500 | keep | 0 | Feb | 2023 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-02-09 07:41 | 2023-02-09 13:01 | 1 | 5:20 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23020900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2023-02-09 | 320 | keep | 0 | Feb | 2023 | 0.00021795 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-09 08:05 | 2023-02-09 15:00 | 100 | 6:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2023-02-09 | 41500 | keep | 0 | Feb | 2023 | 0.028265 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-09 08:16 | 2023-02-09 12:58 | 4 | 4:42 | P | DESGANCHE | 2 X 100 EN C/L POR DESGANCHE | S23020900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2023-02-09 | 1128 | keep | 0 | Feb | 2023 | 0.00076828 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-02-09 08:20 | 2023-02-09 10:32 | 90 | 2:12 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | R23020900089 | New_Event | Animals | Include | Include | Wildlife | 132 | 2023-02-09 | 11880 | keep | 0 | Feb | 2023 | 0.0080914 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-02-09 08:21 | 2023-02-09 10:42 | 10 | 2:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23020900029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2023-02-09 | 1410 | keep | 0 | Feb | 2023 | 0.00096034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-09 08:30 | 2023-02-09 11:57 | 200 | 3:27 | P | DESGANCHE | 2 X 65 EN RISER DESGANCHE | S23020900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-02-09 | 41400 | keep | 0 | Feb | 2023 | 0.028197 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2023-02-09 08:30 | 2023-02-09 12:19 | 5 | 3:49 | P | ANIMAL | 1 X 80 EN C/L SE RETIRO LAGARTIJO CRUZO C/L | R23020900097 | New_Event | Animals | Include | Include | Wildlife | 229 | 2023-02-09 | 1145 | keep | 0 | Feb | 2023 | 0.00077985 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-02-09 08:39 | 2023-02-09 13:00 | 12 | 4:21 | P | DESGANCHE | 1 X 40 EN RISER 1 X 50 EN SU DESGANCHE | S23020900032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2023-02-09 | 3132 | keep | 0 | Feb | 2023 | 0.0021332 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-02-09 08:43 | 2023-02-09 11:58 | 15 | 3:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR FUERTES VIENTOS | M23020900041 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 195 | 2023-02-09 | 2925 | keep | 0 | Feb | 2023 | 0.0019922 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-02-09 08:46 | 2023-02-09 08:53 | 2580 | 0:07 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR A PETICION PERSONAL EN EL CAMPO PARA PASAR CARGA AL 2401-03 POR PUENTE ABIERTO EN LINEA 11100 | R23020900101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-02-09 | 18060 | keep | 0 | Feb | 2023 | 0.012301 | 0.0017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2023-02-09 08:46 | 2023-02-09 08:53 | 500 | 0:07 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR A PETICION PERSONAL EN EL CAMPO PARA PASAR CARGA AL 2401-03 POR PUENTE ABIERTO EN LINEA 11100 | R23020900101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-02-09 | 3500 | keep | 0 | Feb | 2023 | 0.0023838 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2023-02-09 08:49 | 2023-02-09 08:52 | 271 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2302090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-09 | 813 | keep | 0 | Feb | 2023 | 0.00055373 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
GUAYAMA | 2023-02-09 08:50 | 2023-02-09 10:54 | 80 | 2:04 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 200 EN CORTE DE LINEA POR LINEAS ARRIADAS | P23020900042 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 124 | 2023-02-09 | 9920 | keep | 0 | Feb | 2023 | 0.0067565 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-09 09:09 | 2023-02-09 09:45 | 15 | 0:36 | P | PROBLEMA DEL CLIENTE | 1 X 25 EN C/L Y 1X15 EN XMR SE ORIENTO A CLIENTE SOBRE MANTENIMIENTO DE MONTURA | B23020900036 | New_Event | Customer-Related Interruption | Include | Include | Public | 36 | 2023-02-09 | 540 | keep | 0 | Feb | 2023 | 0.00036779 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-09 09:13 | 2023-02-09 12:28 | 13 | 3:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO NEUTRAL | S23020900041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 195 | 2023-02-09 | 2535 | keep | 0 | Feb | 2023 | 0.0017266 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-02-09 09:22 | 2023-02-09 11:01 | 15 | 1:39 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L SE REEMPLAZO PARARRAYO | B23020900041 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 99 | 2023-02-09 | 1485 | keep | 0 | Feb | 2023 | 0.0010114 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-02-09 09:31 | 2023-02-09 11:50 | 60 | 2:19 | P | DESGANCHE | 1 X 25 Y 1 X 65 EN DIFERENTES CORTES DE LINEA REQUIERE DESGANCHE | A23020900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-02-09 | 8340 | keep | 0 | Feb | 2023 | 0.0056803 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-02-09 10:08 | 2023-02-09 10:18 | 1986 | 0:10 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DEL AREA Y SE CERRO INTERRUPTOR | A23020900054 | New_Event | Cutout Failure | Include | Include | Equipment | 10 | 2023-02-09 | 19860 | keep | 0 | Feb | 2023 | 0.013527 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
SAN JUAN | 2023-02-09 10:12 | 2023-02-09 13:38 | 867 | 3:26 | S | ANIMAL | SE RETIRO LAGARTO Y SE LIMPIO PORCELANAS DEL BKR 1115-05 SJ230209-02 | S23020900109 | New_Event | Animals | Include | Include | Wildlife | 206 | 2023-02-09 | 178602 | keep | 0 | Feb | 2023 | 0.12165 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2023-02-09 10:12 | 2023-02-09 12:44 | 863 | 2:32 | T | ALIMENTADOR AMARRADO | SE RETIRO LAGARTO Y SE LIMPIO PORCELANAS DEL BKR 1115-05 CARGA DEL 1119-04 LLEVANDO 1119-02 POR 1115-01 SJ230209-02 SE CERRO N/O BKR A BKR | S23020900109 | New_Event | Feeder Load Transferred | Include | Include | Other | 152 | 2023-02-09 | 131176 | keep | 0 | Feb | 2023 | 0.089343 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2023-02-09 10:12 | 2023-02-09 12:44 | 2720 | 2:32 | T | ALIMENTADOR AMARRADO | SE RETIRO LAGARTO Y SE LIMPIO PORCELANAS DEL BKR 1115-05 CARGA DEL 1119-04 LLEVANDO 1119-02 POR 1115-01 SJ230209-02 SE CERRO N/O BKR A BKR | S23020900109 | New_Event | Feeder Load Transferred | Include | Include | Other | 152 | 2023-02-09 | 413440 | keep | 0 | Feb | 2023 | 0.28159 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2023-02-09 10:18 | 2023-02-09 12:07 | 3 | 1:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA Y BAJANTE DE LINEA A CAJA | A23020900007 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 109 | 2023-02-09 | 327 | keep | 0 | Feb | 2023 | 0.00022272 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-09 10:19 | 2023-02-09 13:34 | 12 | 3:15 | P | DESGANCHE | 1 X 40 EN C/L | B23020900061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-02-09 | 2340 | keep | 0 | Feb | 2023 | 0.0015938 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-02-09 10:30 | 2023-02-09 18:59 | 15 | 8:29 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020900143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 509 | 2023-02-09 | 7635 | keep | 0 | Feb | 2023 | 0.0052002 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-09 10:34 | 2023-02-09 10:35 | 1394 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2302090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 1394 | keep | 0 | Feb | 2023 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
CANOVANAS | 2023-02-09 10:35 | 2023-02-09 12:23 | 10 | 1:48 | P | DESGANCHE | 2 X 25 EN C/L SE REALIZO DESGANCHE | R23020900130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-02-09 | 1080 | keep | 0 | Feb | 2023 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-09 10:39 | 2023-02-09 12:40 | 10 | 2:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23020900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2023-02-09 | 1210 | keep | 0 | Feb | 2023 | 0.00082413 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-02-09 10:39 | 2023-02-09 17:55 | 13 | 7:16 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L POR EMERGENCIA Y SE LEVANTO CONDUCTOR PRIMARIO | C23020900062 | New_Event | Primary Wire Break | Include | Include | Equipment | 436 | 2023-02-09 | 5668 | keep | 0 | Feb | 2023 | 0.0038604 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-02-09 10:47 | 2023-02-09 11:10 | 41 | 0:23 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZAR POSTE PRIMARIO PARTIDO | S23020900427 | New_Event | Primary Pole Failure | Include | Include | Equipment | 23 | 2023-02-09 | 943 | keep | 0 | Feb | 2023 | 0.00064227 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
AGUADILLA | 2023-02-09 10:50 | 2023-02-09 11:10 | 40 | 0:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23020900067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2023-02-09 | 800 | keep | 0 | Feb | 2023 | 0.00054488 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-02-09 11:05 | 2023-02-09 17:45 | 8 | 6:40 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO POSTE SECUNDARIO | R23020900134 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 400 | 2023-02-09 | 3200 | keep | 0 | Feb | 2023 | 0.0021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-09 11:06 | 2023-02-09 13:02 | 90 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO VIENTO | B23020900075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2023-02-09 | 10440 | keep | 0 | Feb | 2023 | 0.0071106 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
YAUCO | 2023-02-09 11:09 | 2023-02-09 13:47 | 1 | 2:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P23020900096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-02-09 | 158 | keep | 0 | Feb | 2023 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-09 11:21 | 2023-02-09 14:00 | 40 | 2:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23020900067 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 159 | 2023-02-09 | 6360 | keep | 0 | Feb | 2023 | 0.0043318 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-09 11:24 | 2023-02-09 20:07 | 41 | 8:43 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZAR POSTE PRIMARIO PARTIDO | S23020900427 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 523 | 2023-02-09 | 21443 | keep | 0 | Feb | 2023 | 0.014605 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-09 11:51 | 2023-02-09 13:00 | 2 | 1:09 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR PARA CAMBIAR EL PATRON DE CONSTRUCCION DEL PARARRAYO | C23020900126 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 69 | 2023-02-09 | 138 | keep | 0 | Feb | 2023 | 9.3991e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-02-09 11:53 | 2023-02-09 18:16 | 200 | 6:23 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETES EN CONVERTIDOR | M23020900086 | New_Event | Switch Failure | Include | Include | Equipment | 383 | 2023-02-09 | 76600 | keep | 0 | Feb | 2023 | 0.052172 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-02-09 11:56 | 2023-02-09 15:20 | 60 | 3:24 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23020900089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-02-09 | 12240 | keep | 0 | Feb | 2023 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-02-09 11:59 | 2023-02-09 15:39 | 101 | 3:40 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23020900124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-02-09 | 22220 | keep | 0 | Feb | 2023 | 0.015134 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
CANOVANAS | 2023-02-09 12:08 | 2023-02-09 14:06 | 70 | 1:58 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | R23020900184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-02-09 | 8260 | keep | 0 | Feb | 2023 | 0.0056258 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-02-09 12:14 | 2023-02-09 15:05 | 8 | 2:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23020900231 | New_Event | Secondary Wire Break | Include | Include | Equipment | 171 | 2023-02-09 | 1368 | keep | 0 | Feb | 2023 | 0.00093174 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-09 12:18 | 2023-02-09 13:42 | 470 | 1:24 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | B23020900132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-02-09 | 39480 | keep | 0 | Feb | 2023 | 0.02689 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
ARECIBO | 2023-02-09 12:27 | 2023-02-09 12:28 | 1986 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A23020900096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-09 | 1986 | keep | 0 | Feb | 2023 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2023-02-09 12:28 | 2023-02-09 18:38 | 6 | 6:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020900191 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 370 | 2023-02-09 | 2220 | keep | 0 | Feb | 2023 | 0.001512 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-02-09 12:30 | 2023-02-09 16:10 | 60 | 3:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23020900113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-02-09 | 13200 | keep | 0 | Feb | 2023 | 0.0089905 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-02-09 12:32 | 2023-02-09 13:43 | 20 | 1:11 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGANCHE | R23020900191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-02-09 | 1420 | keep | 0 | Feb | 2023 | 0.00096716 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-09 12:33 | 2023-02-09 14:21 | 14 | 1:48 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23020900142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-02-09 | 1512 | keep | 0 | Feb | 2023 | 0.0010298 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-02-09 12:39 | 2023-02-09 15:07 | 120 | 2:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23020900259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-02-09 | 17760 | keep | 0 | Feb | 2023 | 0.012096 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2023-02-09 12:40 | 2023-02-09 15:15 | 5 | 2:35 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REUBICAR LINEA SECUNDARIA POR POSTE PARTIDO | A22120200099 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 155 | 2023-02-09 | 775 | keep | 0 | Feb | 2023 | 0.00052785 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-02-09 12:44 | 2023-02-09 16:19 | 80 | 3:35 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA SE RETIRO TENSOR DE TELEFONO CRUZANDO CON LINEA PRIMARIA | M23020900101 | New_Event | Damage From Public | Include | Include | Public | 215 | 2023-02-09 | 17200 | keep | 0 | Feb | 2023 | 0.011715 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-02-09 12:48 | 2023-02-09 20:08 | 40 | 7:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020900176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2023-02-09 | 17600 | keep | 0 | Feb | 2023 | 0.011987 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-09 12:53 | 2023-02-09 15:09 | 10 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR SE REPARO SECUNDARIA | S23020900266 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2023-02-09 | 1360 | keep | 0 | Feb | 2023 | 0.00092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-09 12:55 | 2023-02-09 15:16 | 30 | 2:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO AISLADOR | R23020900195 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 141 | 2023-02-09 | 4230 | keep | 0 | Feb | 2023 | 0.002881 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-02-09 13:00 | 2023-02-10 21:10 | 60 | 32:10 | P | TERMINACION SOTERRADA AVERIADA | SE CORRIGIO TERMNACIONES SOTERRADAS | M23020900110 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1930 | 2023-02-09 | 115800 | keep | 0 | Feb | 2023 | 0.078871 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-02-09 13:04 | 2023-02-09 14:32 | 11 | 1:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L VIENTOS | C23020900152 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 88 | 2023-02-09 | 968 | keep | 0 | Feb | 2023 | 0.0006593 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-02-09 13:10 | 2023-02-09 18:32 | 53 | 5:22 | P | CABLE SOTERRADO AVERIADO | SE REPARO ALAMBRE SOTERRADO CON CG-230209-01 | C23020800399 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 322 | 2023-02-09 | 17066 | keep | 0 | Feb | 2023 | 0.011624 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-09 13:12 | 2023-02-09 13:14 | 842 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23020900277 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-09 | 1684 | keep | 0 | Feb | 2023 | 0.001147 | 0.00057348 | Momentary | FALSE | FALSE | Not_TMED_Event | 842
BARRANQUITAS | 2023-02-09 13:22 | 2023-02-09 15:46 | 127 | 2:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO VIENTOS | C23020900158 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 144 | 2023-02-09 | 18288 | keep | 0 | Feb | 2023 | 0.012456 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
BAYAMON | 2023-02-09 13:22 | 2023-02-09 15:20 | 7 | 1:58 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | B23020900159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-02-09 | 826 | keep | 0 | Feb | 2023 | 0.00056258 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-02-09 13:23 | 2023-02-09 17:36 | 244 | 4:13 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA CRUCE POR AVE | C23020900161 | New_Event | Animals | Include | Include | Wildlife | 253 | 2023-02-09 | 61732 | keep | 0 | Feb | 2023 | 0.042045 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
SAN JUAN | 2023-02-09 13:29 | 2023-02-09 14:42 | 100 | 1:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | S23020900287 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-02-09 | 7300 | keep | 0 | Feb | 2023 | 0.004972 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-02-09 13:30 | 2023-02-09 18:32 | 12 | 5:02 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBU | A23020900167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2023-02-09 | 3624 | keep | 0 | Feb | 2023 | 0.0024683 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-02-09 13:34 | 2023-02-09 14:54 | 1 | 1:20 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23020900166 | New_Event | Animals | Include | Include | Wildlife | 80 | 2023-02-09 | 80 | keep | 0 | Feb | 2023 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-09 13:42 | 2023-02-09 15:03 | 404 | 1:21 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23020900171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-02-09 | 32724 | keep | 0 | Feb | 2023 | 0.022288 | 0.00027516 | Sustained | FALSE | FALSE | Not_TMED_Event | 404
BAYAMON | 2023-02-09 13:43 | 2023-02-09 18:44 | 80 | 5:01 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | B23020800360 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 301 | 2023-02-09 | 24080 | keep | 0 | Feb | 2023 | 0.016401 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-09 13:47 | 2023-02-09 18:10 | 403 | 4:23 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B23020900171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2023-02-09 | 105989 | keep | 0 | Feb | 2023 | 0.072189 | 0.00027448 | Sustained | FALSE | FALSE | Not_TMED_Event | 403
CAGUAS | 2023-02-09 13:51 | 2023-02-09 13:53 | 1290 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR | C23020900174 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-02-09 | 2580 | keep | 0 | Feb | 2023 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
VEGA BAJA | 2023-02-09 13:52 | 2023-02-09 19:09 | 10 | 5:17 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REPARO BUSHING SECUNDARIO | B23020900174 | New_Event | Service Transformer Failure | Include | Include | Equipment | 317 | 2023-02-09 | 3170 | keep | 0 | Feb | 2023 | 0.0021591 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-09 14:00 | 2023-02-09 14:41 | 1 | 0:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZ CAJA DE TRANSFORMADOR | S23020900305 | New_Event | Cutout Failure | Include | Include | Equipment | 41 | 2023-02-09 | 41 | keep | 0 | Feb | 2023 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-09 14:03 | 2023-02-09 16:05 | 75 | 2:02 | P | DESGANCHE | SE HIZO DESGANCHE 1 X 100 EN CORTE DE LINEA | B23020900177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-02-09 | 9150 | keep | 0 | Feb | 2023 | 0.006232 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-02-09 14:15 | 2023-02-09 14:16 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 3070 | keep | 0 | Feb | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
FAJARDO | 2023-02-09 14:20 | 2023-02-09 14:38 | 1 | 0:18 | P | ANIMAL | 1 X 10 EN BANCO XMR CRUCE POR AVE | R23020900210 | New_Event | Animals | Include | Include | Wildlife | 18 | 2023-02-09 | 18 | keep | 0 | Feb | 2023 | 1.226e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-09 14:21 | 2023-02-09 14:55 | 137 | 0:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN RISER MAL TIEMPO LLUVIA | C23020900188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 34 | 2023-02-09 | 4658 | keep | 0 | Feb | 2023 | 0.0031725 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
BAYAMON | 2023-02-09 14:27 | 2023-02-09 14:28 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302090000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 3070 | keep | 0 | Feb | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
SAN JUAN | 2023-02-09 14:30 | 2023-02-09 15:30 | 7 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR DE EMERGENCIA PARA LEVANTAR LINEA SECUNDARIA VIVA EN EL PISO | S23020900380 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-02-09 | 420 | keep | 0 | Feb | 2023 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-02-09 14:30 | 2023-02-09 17:08 | 50 | 2:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020900152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-02-09 | 7900 | keep | 0 | Feb | 2023 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-02-09 14:30 | 2023-02-09 18:54 | 45 | 4:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020900166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2023-02-09 | 11880 | keep | 0 | Feb | 2023 | 0.0080914 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-02-09 14:32 | 2023-02-09 18:55 | 60 | 4:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020900138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2023-02-09 | 15780 | keep | 0 | Feb | 2023 | 0.010748 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-02-09 14:32 | 2023-02-09 18:00 | 75 | 3:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23020900137 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 208 | 2023-02-09 | 15600 | keep | 0 | Feb | 2023 | 0.010625 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-02-09 14:35 | 2023-02-09 18:21 | 1047 | 3:46 | P | ARBOL SOBRE LINEA | SE ABRIO MACHETE REALIZO DESGANCHE MASIVO Y SE CERRO PUENTE DE LINEA A CAJA | B23020900186 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 226 | 2023-02-09 | 236622 | keep | 0 | Feb | 2023 | 0.16116 | 0.00071311 | Sustained | FALSE | FALSE | Not_TMED_Event | 1047
UTUADO | 2023-02-09 14:37 | 2023-02-09 18:09 | 30 | 3:32 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | A23020900142 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 212 | 2023-02-09 | 6360 | keep | 0 | Feb | 2023 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-09 14:39 | 2023-02-10 06:30 | 25 | 15:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L VIENTO FUERTE | B23020900188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 951 | 2023-02-09 | 23775 | keep | 0 | Feb | 2023 | 0.016193 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-02-09 14:56 | 2023-02-09 16:43 | 30 | 1:47 | P | DESGANCHE | 1 X 25 EN C/L SE REALIZO DESGANCHE | R23020900217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-02-09 | 3210 | keep | 0 | Feb | 2023 | 0.0021863 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-02-09 14:59 | 2023-02-09 16:19 | 3 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRAS SECUNDARIAS | R23020900218 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-02-09 | 240 | keep | 0 | Feb | 2023 | 0.00016346 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-09 15:05 | 2023-02-10 00:47 | 50 | 9:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA PUNTO CALIENTE PARTE DE ABAJO DE LA CAJA | B23020900197 | New_Event | Cutout Failure | Include | Include | Equipment | 582 | 2023-02-09 | 29100 | keep | 0 | Feb | 2023 | 0.01982 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-02-09 15:06 | 2023-02-09 15:07 | 2276 | 0:01 | T | ERROR HUMANO | SE ABRIO X ERROR SE CERRO POR CONTROL | C23020900211 | New_Event | Human Error | Include | Include | Other | 1 | 2023-02-09 | 2276 | keep | 0 | Feb | 2023 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
AGUADILLA | 2023-02-09 15:06 | 2023-02-09 18:04 | 100 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23020900147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-02-09 | 17800 | keep | 0 | Feb | 2023 | 0.012123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-02-09 15:07 | 2023-02-09 18:25 | 1290 | 3:18 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR POR EMERGENCIA ALAMBRE VIVO EN EL SUELO SE LEVANTO CONDUCTOR PRIMARIO EN EL SUELO CON EL CG-230209-02 SE CERRO BKR POR CONTROL | C23020900212 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 198 | 2023-02-09 | 255420 | keep | 0 | Feb | 2023 | 0.17397 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
VEGA BAJA | 2023-02-09 15:09 | 2023-02-09 18:00 | 110 | 2:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | B23020900200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-02-09 | 18810 | keep | 0 | Feb | 2023 | 0.012811 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
AGUADILLA | 2023-02-09 15:13 | 2023-02-09 18:18 | 100 | 3:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020900150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-02-09 | 18500 | keep | 0 | Feb | 2023 | 0.0126 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-02-09 15:15 | 2023-02-09 15:30 | 16 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | S23020700107 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-02-09 | 240 | keep | 0 | Feb | 2023 | 0.00016346 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-02-09 15:20 | 2023-02-09 16:05 | 1 | 0:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO BANCO DE XMR PARA REEMPLAZAR AISLADOR PARTIDO | R23020900216 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 45 | 2023-02-09 | 45 | keep | 0 | Feb | 2023 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-02-09 15:20 | 2023-02-09 17:10 | 6 | 1:50 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO PUENTES PARA REPARAR LINEA ARRIADA | A23020900020 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 110 | 2023-02-09 | 660 | keep | 0 | Feb | 2023 | 0.00044952 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-09 15:26 | 2023-02-09 15:27 | 1242 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 90% DE SU CARGA SU CARGA POR 1204-01 | S23020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 1242 | keep | 0 | Feb | 2023 | 0.00084592 | 0.00084592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1242
FAJARDO | 2023-02-09 15:26 | 2023-02-09 19:00 | 20 | 3:34 | P | DESGANCHE | 1 X 30 Y 1 X 20 SE REALIZO DESPEJE DE LINEA | R23020900221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2023-02-09 | 4280 | keep | 0 | Feb | 2023 | 0.0029151 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-02-09 15:26 | 2023-02-09 17:04 | 138 | 1:38 | P | CAUSAS EXTERNAS | 1 X 50 Y 1 X 40 EN C/L SE RETIRO GLOBO METALICO | R23020900220 | New_Event | Damage From Public | Include | Include | Public | 98 | 2023-02-09 | 13524 | keep | 0 | Feb | 2023 | 0.0092111 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
AGUADILLA | 2023-02-09 15:26 | 2023-02-09 18:10 | 60 | 2:44 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA CAMION CRUZO FASES | A23020900155 | New_Event | Damage From Public | Include | Include | Public | 164 | 2023-02-09 | 9840 | keep | 0 | Feb | 2023 | 0.006702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-02-09 15:34 | 2023-02-09 18:52 | 80 | 3:18 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESPEJE DE LINEA | R23020900222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2023-02-09 | 15840 | keep | 0 | Feb | 2023 | 0.010789 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-02-09 15:35 | 2023-02-09 15:36 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA NO CREO EVENTO NI SE PUDO CREAR EN OMS | M23020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 1827 | keep | 0 | Feb | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CAGUAS | 2023-02-09 15:38 | 2023-02-09 17:47 | 90 | 2:09 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23020900225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-02-09 | 11610 | keep | 0 | Feb | 2023 | 0.0079075 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2023-02-09 15:54 | 2023-02-09 19:52 | 3 | 3:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23020900163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-02-09 | 714 | keep | 0 | Feb | 2023 | 0.0004863 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-02-09 16:23 | 2023-02-09 16:24 | 598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 3405-03 SE CERRO POR CONTROL LLEVA EL 3403-01 | C23020900236 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-09 | 598 | keep | 0 | Feb | 2023 | 0.0004073 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2023-02-09 16:23 | 2023-02-09 16:24 | 1001 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL LLEVA EL 3403-01 | C23020900236 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 1001 | keep | 0 | Feb | 2023 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2023-02-09 17:40 | 2023-02-09 18:20 | 8 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | S23020900397 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-02-09 | 320 | keep | 0 | Feb | 2023 | 0.00021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-09 17:43 | 2023-02-09 20:13 | 40 | 2:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23020900204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-02-09 | 6000 | keep | 0 | Feb | 2023 | 0.0040866 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-02-09 17:45 | 2023-02-09 17:59 | 5 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE ZAFADO DE CAJA A TRANSFORMADOR | A23020900173 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2023-02-09 | 70 | keep | 0 | Feb | 2023 | 4.7677e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2023-02-09 17:46 | 2023-02-09 18:46 | 16 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO | C23020900257 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-02-09 | 960 | keep | 0 | Feb | 2023 | 0.00065385 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-02-09 17:47 | 2023-02-09 18:05 | 6 | 0:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR REPARAR BAJANTE SECUNDARIO | S23020900371 | New_Event | Secondary Wire Break | Include | Include | Equipment | 18 | 2023-02-09 | 108 | keep | 0 | Feb | 2023 | 7.3558e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-02-09 17:57 | 2023-02-09 20:14 | 25 | 2:17 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23020900212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-02-09 | 3425 | keep | 0 | Feb | 2023 | 0.0023328 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-02-09 18:06 | 2023-02-10 06:53 | 15 | 12:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN XMR | C23020900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 767 | 2023-02-09 | 11505 | keep | 0 | Feb | 2023 | 0.007836 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-09 18:23 | 2023-02-10 11:19 | 26 | 16:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 20 EN RISER | S23020900407 | New_Event | Cutout Failure | Include | Include | Equipment | 1016 | 2023-02-09 | 26416 | keep | 0 | Feb | 2023 | 0.017992 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
ARECIBO | 2023-02-09 18:28 | 2023-02-09 21:30 | 10 | 3:02 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A23020900196 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 182 | 2023-02-09 | 1820 | keep | 0 | Feb | 2023 | 0.0012396 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-09 18:34 | 2023-02-09 18:35 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23020900263 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 551 | keep | 0 | Feb | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
SAN JUAN | 2023-02-09 19:04 | 2023-02-09 21:41 | 60 | 2:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 Y 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S23020900419 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 157 | 2023-02-09 | 9420 | keep | 0 | Feb | 2023 | 0.0064159 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-02-09 19:11 | 2023-02-10 07:04 | 25 | 11:53 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23020900273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 713 | 2023-02-09 | 17825 | keep | 0 | Feb | 2023 | 0.012141 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-09 19:12 | 2023-02-09 21:25 | 1 | 2:13 | P | DESGANCHE | 1 X 25 EN TRAMSFORMADOR DESGANCHE | S23020900423 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-02-09 | 133 | keep | 0 | Feb | 2023 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-09 19:14 | 2023-02-10 08:26 | 20 | 13:12 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23020900275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 792 | 2023-02-09 | 15840 | keep | 0 | Feb | 2023 | 0.010789 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-09 19:19 | 2023-02-09 21:43 | 1834 | 2:24 | S | OTRAS CAUSAS | DISPARO MECANICO DE PORTATIL #11 SE REENERGIZO MAIN TRANSFORME DE LA 9203-00 DORADO TC 8KV | B23020900493 | New_Event | Other Causes | Include | Include | Other | 144 | 2023-02-09 | 264096 | keep | 0 | Feb | 2023 | 0.17987 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2023-02-09 19:19 | 2023-02-09 21:43 | 2324 | 2:24 | S | OTRAS CAUSAS | DISPARO MECANICO DE PORTATIL #11 SE REENERGIZO MAIN TRANSFORME DE LA 9203-00 DORADO TC 8KV | B23020900493 | New_Event | Other Causes | Include | Include | Other | 144 | 2023-02-09 | 334656 | keep | 0 | Feb | 2023 | 0.22793 | 0.0015829 | Sustained | FALSE | FALSE | Not_TMED_Event | 2324
BAYAMON | 2023-02-09 19:19 | 2023-02-09 21:43 | 1570 | 2:24 | S | OTRAS CAUSAS | DISPARO MECANICO DE PORTATIL #11 SE REENERGIZO MAIN TRANSFORME DE LA 9203-00 DORADO TC 8KV | B23020900493 | New_Event | Other Causes | Include | Include | Other | 144 | 2023-02-09 | 226080 | keep | 0 | Feb | 2023 | 0.15398 | 0.0010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 1570
CANOVANAS | 2023-02-09 19:27 | 2023-02-09 22:33 | 40 | 3:06 | P | EMPALME SOTERRADO AVERIADO | 1 X 40 EN C/L REPARO EMPLAME EN PROVICIONAL AEREO | R23020900244 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 186 | 2023-02-09 | 7440 | keep | 0 | Feb | 2023 | 0.0050674 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-09 20:00 | 2023-02-10 16:07 | 15 | 20:07 | P | ARBOL SOBRE LINEA | 1 X 40 EN C/LSE LEVANTO ALAMBRE EN EL SUELO A CAUSA DE ARBOL SOBRE LINEA | C23020900280 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1207 | 2023-02-09 | 18105 | keep | 0 | Feb | 2023 | 0.012331 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-09 20:02 | 2023-02-09 20:03 | 308 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 17% POR 9202-03 | B23020900426 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 308 | keep | 0 | Feb | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-02-09 20:02 | 2023-02-09 20:03 | 237 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 17% DE SU CARGA POR EL 9202-02 | B23020900426 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-09 | 237 | keep | 0 | Feb | 2023 | 0.00016142 | 0.00016142 | Momentary | FALSE | FALSE | Not_TMED_Event | 237
CAGUAS | 2023-02-09 20:06 | 2023-02-10 08:29 | 8 | 12:23 | P | ANIMAL | 1 X 15 EN XMR Y X 30 EN C/L CRUCE X AVE | C23020900281 | New_Event | Animals | Include | Include | Wildlife | 743 | 2023-02-09 | 5944 | keep | 0 | Feb | 2023 | 0.0040484 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-02-09 20:26 | 2023-02-09 20:29 | 4304 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR UN SOLO RECIERRE SE CERRO POR SCADA NO SE REPORTO CAUSA | M23020900239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-09 | 12912 | keep | 0 | Feb | 2023 | 0.0087943 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2023-02-09 20:29 | 2023-02-10 10:40 | 80 | 14:11 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M23020900264 | New_Event | Animals | Include | Include | Wildlife | 851 | 2023-02-09 | 68080 | keep | 0 | Feb | 2023 | 0.046369 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-02-09 20:48 | 2023-02-09 20:49 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23020900212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 2697 | keep | 0 | Feb | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
SAN JUAN | 2023-02-09 20:57 | 2023-02-10 09:39 | 8 | 12:42 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y DESGANCHE SECUNDARIO | S23020900434 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 762 | 2023-02-09 | 6096 | keep | 0 | Feb | 2023 | 0.004152 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-09 21:15 | 2023-02-10 14:15 | 35 | 17:00 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | M23020900255 | New_Event | Primary Wire Break | Include | Include | Equipment | 1020 | 2023-02-09 | 35700 | keep | 0 | Feb | 2023 | 0.024315 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2023-02-09 22:12 | 2023-02-10 06:16 | 10 | 8:04 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23020900289 | New_Event | Animals | Include | Include | Wildlife | 484 | 2023-02-09 | 4840 | keep | 0 | Feb | 2023 | 0.0032965 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-09 22:50 | 2023-02-10 18:55 | 23 | 20:05 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REPARO POSTE PRIMARIO PARTIDO | S23020900438 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1205 | 2023-02-09 | 27715 | keep | 0 | Feb | 2023 | 0.018877 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2023-02-09 23:02 | 2023-02-10 16:45 | 9 | 17:43 | P | DESGANCHE | 1 X 50 EN C/L | S23020900444 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1063 | 2023-02-09 | 9567 | keep | 0 | Feb | 2023 | 0.006516 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-02-09 23:57 | 2023-02-09 23:58 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-09 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
HUMACAO | 2023-02-10 | 2023-02-10 07:24 | 15 | 7:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23021000001 | New_Event | Cutout Failure | Include | Include | Equipment | 444 | 2023-02-10 | 6660 | keep | 0 | Feb | 2023 | 0.0045361 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-10 00:01 | 2023-02-10 02:39 | 121 | 2:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | B23021000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-02-10 | 19118 | keep | 0 | Feb | 2023 | 0.013021 | 8.2413e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 121
AGUADILLA | 2023-02-10 00:32 | 2023-02-10 02:41 | 100 | 2:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23021000001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 129 | 2023-02-10 | 12900 | keep | 0 | Feb | 2023 | 0.0087861 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-02-10 00:45 | 2023-02-10 11:40 | 20 | 10:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5 X 37.5KVA Y 2 X 25 EN XMR | S23021000004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 655 | 2023-02-10 | 13100 | keep | 0 | Feb | 2023 | 0.0089224 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-02-10 00:49 | 2023-02-10 00:50 | 2999 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23021000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 2999 | keep | 0 | Feb | 2023 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
AGUADILLA | 2023-02-10 01:51 | 2023-02-10 10:08 | 60 | 8:17 | P | DESGANCHE | 1 X 30 Y 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23021000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 497 | 2023-02-10 | 29820 | keep | 0 | Feb | 2023 | 0.02031 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-02-10 02:09 | 2023-02-10 02:10 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23021000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 4533 | keep | 0 | Feb | 2023 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
UTUADO | 2023-02-10 03:07 | 2023-02-10 14:50 | 40 | 11:43 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 Y 1 X 50 EN CORTES DE LINEA SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23021000004 | New_Event | Primary Wire Break | Include | Include | Equipment | 703 | 2023-02-10 | 28120 | keep | 0 | Feb | 2023 | 0.019152 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-02-10 05:07 | 2023-02-10 09:15 | 30 | 4:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23021000007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 248 | 2023-02-10 | 7440 | keep | 0 | Feb | 2023 | 0.0050674 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-10 06:25 | 2023-02-10 12:14 | 60 | 5:49 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | B23021000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2023-02-10 | 20940 | keep | 0 | Feb | 2023 | 0.014262 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-10 07:15 | 2023-02-10 13:42 | 30 | 6:27 | P | DESGANCHE | DESGANCHE SE CERRO PUENTE DE LINEA A CAJA 1 X 65 EN C/L | S23021000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 387 | 2023-02-10 | 11610 | keep | 0 | Feb | 2023 | 0.0079075 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-02-10 07:18 | 2023-02-10 07:19 | 1227 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23021000013 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-10 | 1227 | keep | 0 | Feb | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-02-10 07:19 | 2023-02-10 10:30 | 1 | 3:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23021000015 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 191 | 2023-02-10 | 191 | keep | 0 | Feb | 2023 | 0.00013009 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-10 07:32 | 2023-02-10 16:44 | 15 | 9:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23021000019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 552 | 2023-02-10 | 8280 | keep | 0 | Feb | 2023 | 0.0056395 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-10 07:46 | 2023-02-10 19:44 | 10 | 11:58 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | S23021000020 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 718 | 2023-02-10 | 7180 | keep | 0 | Feb | 2023 | 0.0048903 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-02-10 08:10 | 2023-02-10 08:11 | 1494 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA SE CERRO POR SCADA | A23021000016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 1494 | keep | 0 | Feb | 2023 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
SAN JUAN | 2023-02-10 08:35 | 2023-02-10 10:29 | 15 | 1:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23021000010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 114 | 2023-02-10 | 1710 | keep | 0 | Feb | 2023 | 0.0011647 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-10 08:37 | 2023-02-10 11:37 | 28 | 3:00 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEAS | B23021000016 | New_Event | Animals | Include | Include | Wildlife | 180 | 2023-02-10 | 5040 | keep | 0 | Feb | 2023 | 0.0034327 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
AGUADILLA | 2023-02-10 08:46 | 2023-02-10 12:52 | 10 | 4:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE QUEMADO | M23021000018 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2023-02-10 | 2460 | keep | 0 | Feb | 2023 | 0.0016755 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-10 09:00 | 2023-02-10 12:16 | 10 | 3:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA, DOS TOMA Y BAJANTE DE XMR | R23021000008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 196 | 2023-02-10 | 1960 | keep | 0 | Feb | 2023 | 0.0013349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-02-10 09:00 | 2023-02-10 09:47 | 75 | 0:47 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23021000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2023-02-10 | 3525 | keep | 0 | Feb | 2023 | 0.0024009 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-02-10 09:23 | 2023-02-10 11:24 | 30 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021000028 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2023-02-10 | 3630 | keep | 0 | Feb | 2023 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-02-10 09:45 | 2023-02-10 10:35 | 2 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS AVERIADAS | A23021000018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-02-10 | 100 | keep | 0 | Feb | 2023 | 6.811e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-02-10 09:48 | 2023-02-10 14:52 | 25 | 5:04 | P | DESGANCHE | 1 X 40 Y 1 X 65 EN C/L DESGANCHE | C23021000040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2023-02-10 | 7600 | keep | 0 | Feb | 2023 | 0.0051763 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-10 09:51 | 2023-02-10 12:17 | 1085 | 2:26 | T | ARBOL SOBRE LINEA | DISPARO DE INTERRUPTOR SE SECCIONALIZO ARBOL SOBRE LINEA SJ-230210-01 | S23021000041 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 146 | 2023-02-10 | 158410 | keep | 0 | Feb | 2023 | 0.10789 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
CANOVANAS | 2023-02-10 10:05 | 2023-02-10 14:23 | 1 | 4:18 | P | OTRAS CAUSAS | 1 NX DE 18 AMP Y SE REPARO EQUIPO DE MEDICION | R23021000010 | New_Event | Other Causes | Include | Include | Other | 258 | 2023-02-10 | 258 | keep | 0 | Feb | 2023 | 0.00017572 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-10 10:08 | 2023-02-10 14:25 | 2 | 4:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23021000046 | New_Event | Cutout Failure | Include | Include | Equipment | 257 | 2023-02-10 | 514 | keep | 0 | Feb | 2023 | 0.00035008 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-10 10:11 | 2023-02-10 14:51 | 1 | 4:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR POR CONTAMINACION EN LA CAJA | B23021000028 | New_Event | Cutout Failure | Include | Include | Equipment | 280 | 2023-02-10 | 280 | keep | 0 | Feb | 2023 | 0.00019071 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-10 10:11 | 2023-02-10 13:30 | 80 | 3:19 | P | ANIMAL | 1 X 80 Y 1 X 100 EN DIFERENTES CORTES DE LINEA AVE CRUZO FASES | M23021000035 | New_Event | Animals | Include | Include | Wildlife | 199 | 2023-02-10 | 15920 | keep | 0 | Feb | 2023 | 0.010843 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-10 10:13 | 2023-02-10 17:55 | 15 | 7:42 | P | ANIMAL | 1 X 140 EN C/L CRUCE POR AVE | B23021000029 | New_Event | Animals | Include | Include | Wildlife | 462 | 2023-02-10 | 6930 | keep | 0 | Feb | 2023 | 0.00472 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-02-10 10:13 | 2023-02-10 10:42 | 10 | 0:29 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO EN XMR | P23021000036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 29 | 2023-02-10 | 290 | keep | 0 | Feb | 2023 | 0.00019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-02-10 10:20 | 2023-02-10 10:35 | 10 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE BAJANTES SECUNDARIOS | A23020900186 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-02-10 | 150 | keep | 0 | Feb | 2023 | 0.00010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-10 10:24 | 2023-02-10 13:19 | 10 | 2:55 | P | ANIMAL | 1 X 20 EN XMR SE RETIRO CULEBRA | B23021000031 | New_Event | Animals | Include | Include | Wildlife | 175 | 2023-02-10 | 1750 | keep | 0 | Feb | 2023 | 0.0011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-10 10:31 | 2023-02-10 13:35 | 30 | 3:04 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23021000050 | New_Event | Animals | Include | Include | Wildlife | 184 | 2023-02-10 | 5520 | keep | 0 | Feb | 2023 | 0.0037596 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-10 10:37 | 2023-02-11 10:40 | 20 | 24:03 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y SE CERRARON LOS MACHETES | S23021000077 | New_Event | Primary Wire Break | Include | Include | Equipment | 1443 | 2023-02-10 | 28860 | keep | 0 | Feb | 2023 | 0.019656 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-10 11:01 | 2023-02-10 14:27 | 150 | 3:26 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B23021000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-02-10 | 30900 | keep | 0 | Feb | 2023 | 0.021046 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-02-10 11:08 | 2023-02-10 13:56 | 200 | 2:48 | P | ANIMAL | 2 X 65 EN C/L CRUCE X AVE | C23021000055 | New_Event | Animals | Include | Include | Wildlife | 168 | 2023-02-10 | 33600 | keep | 0 | Feb | 2023 | 0.022885 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-02-10 11:09 | 2023-02-10 14:52 | 10 | 3:43 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN XMR Y SE REPARO CONEXIONES SECUNDARIAS. SE DEJO FUERA CLIENTE CON TOMA AVERIADA | B23021000041 | New_Event | Customer-Related Interruption | Include | Include | Public | 223 | 2023-02-10 | 2230 | keep | 0 | Feb | 2023 | 0.0015188 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-10 11:20 | 2023-02-10 12:49 | 5 | 1:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | B23021000046 | New_Event | Cutout Failure | Include | Include | Equipment | 89 | 2023-02-10 | 445 | keep | 0 | Feb | 2023 | 0.00030309 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-02-10 11:31 | 2023-02-10 11:33 | 4431 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2302100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-10 | 8862 | keep | 0 | Feb | 2023 | 0.0060359 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
YAUCO | 2023-02-10 11:33 | 2023-02-10 14:28 | 40 | 2:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23021000056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-02-10 | 7000 | keep | 0 | Feb | 2023 | 0.0047677 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-10 11:39 | 2023-02-10 14:09 | 13 | 2:30 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23021000062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-02-10 | 1950 | keep | 0 | Feb | 2023 | 0.0013281 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
GUAYAMA | 2023-02-10 11:42 | 2023-02-10 12:10 | 8 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTES Y SECUNDARIA | P23021000048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-02-10 | 224 | keep | 0 | Feb | 2023 | 0.00015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-02-10 11:45 | 2023-02-10 12:52 | 11 | 1:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23021000030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 67 | 2023-02-10 | 737 | keep | 0 | Feb | 2023 | 0.00050197 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-02-10 11:49 | 2023-02-10 13:18 | 8 | 1:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23021000113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 89 | 2023-02-10 | 712 | keep | 0 | Feb | 2023 | 0.00048494 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-02-10 11:49 | 2023-02-10 13:56 | 3 | 2:07 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE TRANSFORMADOR | M23021000062 | New_Event | Primary Wire Break | Include | Include | Equipment | 127 | 2023-02-10 | 381 | keep | 0 | Feb | 2023 | 0.0002595 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-10 11:50 | 2023-02-10 21:43 | 30 | 9:53 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | S23021000114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 593 | 2023-02-10 | 17790 | keep | 0 | Feb | 2023 | 0.012117 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-02-10 11:53 | 2023-02-10 13:19 | 50 | 1:26 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23021000051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-02-10 | 4300 | keep | 0 | Feb | 2023 | 0.0029287 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-10 11:58 | 2023-02-10 11:59 | 2675 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CERRADO POR CONTROL | R2302100000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-10 | 2675 | keep | 0 | Feb | 2023 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2023-02-10 11:59 | 2023-02-10 13:49 | 1 | 1:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 CL Y REMPLAZO DE CAJA PRIMARIA | R23021000033 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 110 | 2023-02-10 | 110 | keep | 0 | Feb | 2023 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-10 12:05 | 2023-02-10 14:38 | 3 | 2:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 200 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021000066 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 153 | 2023-02-10 | 459 | keep | 0 | Feb | 2023 | 0.00031262 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-02-10 12:17 | 2023-02-10 17:51 | 108 | 5:34 | P | ARBOL SOBRE LINEA | SE RELIZO PODA DE ARBOL SOBRE LINEAS PRIMARIAS SJ-230210-01 | S23021000041 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 334 | 2023-02-10 | 36072 | keep | 0 | Feb | 2023 | 0.024568 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
GUAYAMA | 2023-02-10 12:26 | 2023-02-10 14:58 | 107 | 2:32 | P | CONDUCTOR ROTO O ABIERTO | SE ABREN MACHETES PARA REPARAR ALAMBRE SAFADO DE CRUCETA Y LLEVAR LINEA AL AISLADOR, SE REMPLAZO AISLADOR Y SE REPARO LINEA PRIMARIA | P23021000057 | New_Event | Primary Wire Break | Include | Include | Equipment | 152 | 2023-02-10 | 16264 | keep | 0 | Feb | 2023 | 0.011077 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
VEGA BAJA | 2023-02-10 12:26 | 2023-02-10 14:53 | 21 | 2:27 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B23021000058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-02-10 | 3087 | keep | 0 | Feb | 2023 | 0.0021025 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2023-02-10 12:43 | 2023-02-10 15:03 | 52 | 2:20 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B23021000064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-02-10 | 7280 | keep | 0 | Feb | 2023 | 0.0049584 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2023-02-10 12:45 | 2023-02-10 17:30 | 16 | 4:45 | P | DESGANCHE | 1 X 80 EN C/L Y 1 X 65 EN C/L | S23021000146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2023-02-10 | 4560 | keep | 0 | Feb | 2023 | 0.0031058 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2023-02-10 12:55 | 2023-02-10 17:34 | 9 | 4:39 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN XMR SE REPARO PUENTE SAFADO DE CAJA A XMR | C23021000083 | New_Event | Primary Wire Break | Include | Include | Equipment | 279 | 2023-02-10 | 2511 | keep | 0 | Feb | 2023 | 0.0017102 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-02-10 12:57 | 2023-02-10 18:40 | 25 | 5:43 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEAS CRUZADAS | M23021000080 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 343 | 2023-02-10 | 8575 | keep | 0 | Feb | 2023 | 0.0058404 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-02-10 12:58 | 2023-02-10 15:48 | 3431 | 2:50 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE REPARO LINEA PRIMARIA ROTA | A23021000064 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2023-02-10 | 583270 | keep | 0 | Feb | 2023 | 0.39726 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
FAJARDO | 2023-02-10 12:59 | 2023-02-10 13:00 | 625 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO CERRADO POR | R2302100000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-10 | 625 | keep | 0 | Feb | 2023 | 0.00042568 | 0.00042568 | Momentary | FALSE | FALSE | Not_TMED_Event | 625
FAJARDO | 2023-02-10 13:00 | 2023-02-10 14:37 | 80 | 1:37 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO CON SJ-230210-50 | R23021000036 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 97 | 2023-02-10 | 7760 | keep | 0 | Feb | 2023 | 0.0052853 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-02-10 13:00 | 2023-02-10 13:33 | 12 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23020900205 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-02-10 | 396 | keep | 0 | Feb | 2023 | 0.00026971 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-02-10 13:23 | 2023-02-10 14:45 | 100 | 1:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | M23021000085 | New_Event | Primary Wire Break | Include | Include | Equipment | 82 | 2023-02-10 | 8200 | keep | 0 | Feb | 2023 | 0.005585 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-02-10 13:31 | 2023-02-10 15:00 | 170 | 1:29 | P | ANIMAL | 2 X 200 EN C/L CRUCE X RANA CUBANA | C23021000093 | New_Event | Animals | Include | Include | Wildlife | 89 | 2023-02-10 | 15130 | keep | 0 | Feb | 2023 | 0.010305 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
UTUADO | 2023-02-10 13:40 | 2023-02-10 17:13 | 30 | 3:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23021000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-02-10 | 6390 | keep | 0 | Feb | 2023 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-10 14:10 | 2023-02-10 15:09 | 8 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23021000021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2023-02-10 | 472 | keep | 0 | Feb | 2023 | 0.00032148 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-10 14:11 | 2023-02-10 17:29 | 30 | 3:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L Y 1 X 8 EN PM | S23021000162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2023-02-10 | 5940 | keep | 0 | Feb | 2023 | 0.0040457 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-02-10 14:15 | 2023-02-10 16:12 | 16 | 1:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23021000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-02-10 | 1872 | keep | 0 | Feb | 2023 | 0.001275 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-02-10 14:20 | 2023-02-10 15:37 | 33 | 1:17 | P | ARBOL SOBRE LINEA | SE SECCIONALIZO TRAMO Y SE PODO ARBOL SOBRE LINEA PRIMARIA SJ-230210-02 | S23021000163 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 77 | 2023-02-10 | 2541 | keep | 0 | Feb | 2023 | 0.0017307 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
ARECIBO | 2023-02-10 14:20 | 2023-02-10 16:05 | 50 | 1:45 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A23021000081 | New_Event | Primary Wire Break | Include | Include | Equipment | 105 | 2023-02-10 | 5250 | keep | 0 | Feb | 2023 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-02-10 14:21 | 2023-02-10 17:03 | 15 | 2:42 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA PLANCHA DE ZINC CRUZANDO LINEA | A23021000082 | New_Event | Damage From Public | Include | Include | Public | 162 | 2023-02-10 | 2430 | keep | 0 | Feb | 2023 | 0.0016551 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-02-10 14:22 | 2023-02-10 14:23 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23021000081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 1310 | keep | 0 | Feb | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BARRANQUITAS | 2023-02-10 14:30 | 2023-02-10 16:30 | 12 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA RELOCALIZAR SECUNDARIA A NUEVO POSTE | C23021000115 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2023-02-10 | 1440 | keep | 0 | Feb | 2023 | 0.00098078 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-02-10 14:32 | 2023-02-10 16:25 | 50 | 1:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23021000088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-02-10 | 5650 | keep | 0 | Feb | 2023 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-02-10 14:35 | 2023-02-10 14:36 | 2286 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23021000039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 2286 | keep | 0 | Feb | 2023 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2023-02-10 14:37 | 2023-02-10 16:36 | 420 | 1:59 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO CON SJ-230210-50 | R23021000036 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 119 | 2023-02-10 | 49980 | keep | 0 | Feb | 2023 | 0.034041 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-10 14:47 | 2023-02-10 14:48 | 1105 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2302100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 1105 | keep | 0 | Feb | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
UTUADO | 2023-02-10 14:50 | 2023-02-10 16:45 | 50 | 1:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23021000101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-02-10 | 5750 | keep | 0 | Feb | 2023 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-10 14:52 | 2023-02-10 16:36 | 20 | 1:44 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | R23021000041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-02-10 | 2080 | keep | 0 | Feb | 2023 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-02-10 14:57 | 2023-02-10 14:58 | 1952 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23021000078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 1952 | keep | 0 | Feb | 2023 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
VEGA BAJA | 2023-02-10 14:58 | 2023-02-10 20:37 | 25 | 5:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5KVA | A23021000104 | New_Event | Service Transformer Failure | Include | Include | Equipment | 339 | 2023-02-10 | 8475 | keep | 0 | Feb | 2023 | 0.0057723 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-02-10 15:01 | 2023-02-10 17:20 | 50 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021000107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-02-10 | 6950 | keep | 0 | Feb | 2023 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-10 15:02 | 2023-02-11 00:01 | 3 | 8:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | B23021000082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 539 | 2023-02-10 | 1617 | keep | 0 | Feb | 2023 | 0.0011013 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-10 15:08 | 2023-02-10 17:51 | 15 | 2:43 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESPEJE | B23021000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-02-10 | 2445 | keep | 0 | Feb | 2023 | 0.0016653 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-10 15:16 | 2023-02-10 17:47 | 35 | 2:31 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR CRUCE POR AVE | R23021000045 | New_Event | Animals | Include | Include | Wildlife | 151 | 2023-02-10 | 5285 | keep | 0 | Feb | 2023 | 0.0035996 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-02-10 15:29 | 2023-02-10 15:31 | 1510 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23021000139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-02-10 | 3020 | keep | 0 | Feb | 2023 | 0.0020569 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
SAN JUAN | 2023-02-10 15:30 | 2023-02-10 17:02 | 9 | 1:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23021000185 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2023-02-10 | 828 | keep | 0 | Feb | 2023 | 0.00056395 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-02-10 15:31 | 2023-02-10 17:04 | 91 | 1:33 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | C23021000146 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-02-10 | 8463 | keep | 0 | Feb | 2023 | 0.0057641 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
BARRANQUITAS | 2023-02-10 15:32 | 2023-02-10 17:01 | 50 | 1:29 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23021000141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-02-10 | 4450 | keep | 0 | Feb | 2023 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-02-10 15:33 | 2023-02-10 21:31 | 11 | 5:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C23021000142 | New_Event | Cutout Failure | Include | Include | Equipment | 358 | 2023-02-10 | 3938 | keep | 0 | Feb | 2023 | 0.0026822 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2023-02-10 15:45 | 2023-02-10 17:35 | 3 | 1:50 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P23021000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-02-10 | 330 | keep | 0 | Feb | 2023 | 0.00022476 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-02-10 15:56 | 2023-02-10 18:16 | 500 | 2:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y 2 X 140 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23021000180 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2023-02-10 | 70000 | keep | 0 | Feb | 2023 | 0.047677 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2023-02-10 15:57 | 2023-02-10 17:05 | 3630 | 1:08 | T | CONDUCTOR ROTO O ABIERTO | SE REALIZO PRUEBA A PETICION PERSONAL DE CAMPO QUEDANDO EN SERVICIO | M23021000119 | New_Event | Primary Wire Break | Include | Include | Equipment | 68 | 2023-02-10 | 246840 | keep | 0 | Feb | 2023 | 0.16812 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
BAYAMON | 2023-02-10 15:59 | 2023-02-10 16:28 | 8 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIAS | B23021000091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-02-10 | 232 | keep | 0 | Feb | 2023 | 0.00015801 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-02-10 16:08 | 2023-02-10 16:25 | 7 | 0:17 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRIR XMR POR SEGURIDAD UNA FASE ESTABA A PUNTO DE TOCAR EL POSTE Y SE DESPEGO LA LINEA | C23021000172 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 17 | 2023-02-10 | 119 | keep | 0 | Feb | 2023 | 8.105e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-02-10 16:12 | 2023-02-10 16:13 | 1089 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23021000188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 1089 | keep | 0 | Feb | 2023 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
AGUADILLA | 2023-02-10 16:13 | 2023-02-11 09:50 | 40 | 17:37 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS HABIA EVENTOS DESDE 16:13 DEL DIA 10 LOS CANCELARON(147,222,251,284,296,326) | M23021100358 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1057 | 2023-02-10 | 42280 | keep | 0 | Feb | 2023 | 0.028797 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-02-10 16:19 | 2023-02-10 18:56 | 1339 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000203 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-10 | 210223 | keep | 0 | Feb | 2023 | 0.14318 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-02-10 16:19 | 2023-02-10 18:56 | 470 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000203 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-10 | 73790 | keep | 0 | Feb | 2023 | 0.050258 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2023-02-10 16:19 | 2023-02-10 18:56 | 2483 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000203 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-10 | 389831 | keep | 0 | Feb | 2023 | 0.26551 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2023-02-10 16:19 | 2023-02-10 18:56 | 2190 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000203 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-10 | 343830 | keep | 0 | Feb | 2023 | 0.23418 | 0.0014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2023-02-10 16:19 | 2023-02-10 18:56 | 3006 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-10 | 471942 | keep | 0 | Feb | 2023 | 0.32144 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2023-02-10 16:19 | 2023-02-10 18:56 | 179 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-10 | 28103 | keep | 0 | Feb | 2023 | 0.019141 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2023-02-10 16:19 | 2023-02-10 18:56 | 107 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000211 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-10 | 16799 | keep | 0 | Feb | 2023 | 0.011442 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2023-02-10 16:19 | 2023-02-10 18:56 | 1666 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000211 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-10 | 261562 | keep | 0 | Feb | 2023 | 0.17815 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2023-02-10 16:19 | 2023-02-10 18:56 | 4387 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000211 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-10 | 688759 | keep | 0 | Feb | 2023 | 0.46911 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2023-02-10 16:19 | 2023-02-10 18:59 | 3147 | 2:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000213 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 160 | 2023-02-10 | 503520 | keep | 0 | Feb | 2023 | 0.34295 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2023-02-10 16:19 | 2023-02-10 18:59 | 4304 | 2:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23021000213 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 160 | 2023-02-10 | 688640 | keep | 0 | Feb | 2023 | 0.46903 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
ARECIBO | 2023-02-10 16:22 | 2023-02-10 18:45 | 8 | 2:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA (SOTERRADA) | A23021000021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 143 | 2023-02-10 | 1144 | keep | 0 | Feb | 2023 | 0.00077917 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-02-10 16:57 | 2023-02-10 20:40 | 95 | 3:43 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A23021000135 | New_Event | Primary Wire Break | Include | Include | Equipment | 223 | 2023-02-10 | 21185 | keep | 0 | Feb | 2023 | 0.014429 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
PONCE | 2023-02-10 16:58 | 2023-02-10 16:59 | 2163 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 ARBOLES EN EL AREA DE EMPRESAS VASALLO | P23021000098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-10 | 2163 | keep | 0 | Feb | 2023 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
PONCE | 2023-02-10 16:58 | 2023-02-10 16:59 | 1340 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 ARBOLES EN EL AREA DE EMPRESAS VASALLO | P23021000098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-10 | 1340 | keep | 0 | Feb | 2023 | 0.00091267 | 0.00091267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1340
PONCE | 2023-02-10 16:58 | 2023-02-10 16:59 | 2039 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 ARBOLES EN EL AREA DE EMPRESAS VASALLO | P23021000098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-10 | 2039 | keep | 0 | Feb | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2023-02-10 16:58 | 2023-02-10 16:59 | 485 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 ARBOLES EN EL AREA DE EMPRESAS VASALLO | P23021000098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-10 | 485 | keep | 0 | Feb | 2023 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
PONCE | 2023-02-10 16:58 | 2023-02-10 16:59 | 732 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 ARBOLES EN EL AREA DE EMPRESAS VASALLO | P23021000098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-10 | 732 | keep | 0 | Feb | 2023 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
MAYAGÃœEZ | 2023-02-10 17:25 | 2023-02-10 17:45 | 3630 | 0:20 | T | CONDUCTOR ROTO O ABIERTO | DISPARO NUEVAMENTE SE SECCIONALIZO PUENTE PRIMARIO ROTO SE ABRIO MACHETES EN MR SPECIAL | M23021000119 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 20 | 2023-02-10 | 72600 | keep | 0 | Feb | 2023 | 0.049448 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-10 17:45 | 2023-02-10 22:27 | 3014 | 4:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEAS PRIMARIAS PARTIDAS Y SE CERRO MACHETES | M23021000119 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 282 | 2023-02-10 | 849948 | keep | 0 | Feb | 2023 | 0.5789 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-10 17:56 | 2023-02-10 18:42 | 14 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REPARO BAJANTE SECUNDARIO Y SE REGULO VOLTAJE DEL TAP 3 AL 2 SE DEJO EN 124V | C23021000233 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2023-02-10 | 644 | keep | 0 | Feb | 2023 | 0.00043863 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-02-10 18:42 | 2023-02-10 19:19 | 14 | 0:37 | P | DESGANCHE | 1 X 25 EN C/L SE REALIZO DESPEJE | B23021000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2023-02-10 | 518 | keep | 0 | Feb | 2023 | 0.00035281 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-02-10 18:51 | 2023-02-10 19:37 | 40 | 0:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S23021000251 | New_Event | Cutout Failure | Include | Include | Equipment | 46 | 2023-02-10 | 1840 | keep | 0 | Feb | 2023 | 0.0012532 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-10 18:51 | 2023-02-11 00:10 | 3 | 5:19 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE A PARARRAYO | B23021000136 | New_Event | Primary Wire Break | Include | Include | Equipment | 319 | 2023-02-10 | 957 | keep | 0 | Feb | 2023 | 0.00065181 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-02-10 18:52 | 2023-02-11 08:42 | 10 | 13:50 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | M23021000405 | New_Event | Vegetation Contact | Include | Include | Vegetation | 830 | 2023-02-10 | 8300 | keep | 0 | Feb | 2023 | 0.0056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-10 18:57 | 2023-02-10 19:30 | 15 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR Y SE REPARO SECUNDARIA | S23021000255 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-02-10 | 495 | keep | 0 | Feb | 2023 | 0.00033714 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-02-10 19:03 | 2023-02-11 08:35 | 13 | 13:32 | P | ANIMAL | 1 X 10 EN XMR CRUCE X IGUANA SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | C23021000244 | New_Event | Animals | Include | Include | Wildlife | 812 | 2023-02-10 | 10556 | keep | 0 | Feb | 2023 | 0.0071896 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-02-10 19:07 | 2023-02-11 07:54 | 11 | 12:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B23021000137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 767 | 2023-02-10 | 8437 | keep | 0 | Feb | 2023 | 0.0057464 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-02-10 19:10 | 2023-02-10 20:23 | 199 | 1:13 | P | DESGANCHE | DISPARO DE INTERRUPTOR SOLO LLEVA 20% DE SU CARGA SE SECCIONALIZO TRAMO Y SE REALIZO DESGANCHE SJ-230210-03 | S23021000285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-02-10 | 14527 | keep | 0 | Feb | 2023 | 0.0098943 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-02-10 19:50 | 2023-02-10 21:00 | 3 | 1:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23021000153 | New_Event | Primary Wire Break | Include | Include | Equipment | 70 | 2023-02-10 | 210 | keep | 0 | Feb | 2023 | 0.00014303 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2023-02-10 20:08 | 2023-02-10 21:09 | 1633 | 1:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 AISLADOR ROTO EN TRAMO ACB 1945 AL ACB 1909B | A23021000184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2023-02-10 | 99613 | keep | 0 | Feb | 2023 | 0.067846 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2023-02-10 20:08 | 2023-02-10 21:09 | 1624 | 1:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 AISLADOR ROTO EN TRAMO ACB 1945 AL ACB 1909B | A23021000184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2023-02-10 | 99064 | keep | 0 | Feb | 2023 | 0.067472 | 0.0011061 | Sustained | FALSE | FALSE | Not_TMED_Event | 1624
SAN JUAN | 2023-02-10 20:23 | 2023-02-10 21:15 | 95 | 0:52 | P | DESGANCHE | DISPARO DE INTERRUPTOR SOLO LLEVA 20% DE SU CARGA SE SECCIONALIZO TRAMO Y SE REALIZO DESGANCHE SJ-230210-03 | S23021000285 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 52 | 2023-02-10 | 4940 | keep | 0 | Feb | 2023 | 0.0033646 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-02-10 20:36 | 2023-02-11 09:33 | 3 | 12:57 | P | CONDUCTOR ROTO O ABIERTO | REPARAR PUENTE PRIMARIO EN CAJA PRIMARIA | C23021000260 | New_Event | Primary Wire Break | Include | Include | Equipment | 777 | 2023-02-10 | 2331 | keep | 0 | Feb | 2023 | 0.0015876 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2023-02-10 20:41 | 2023-02-10 21:38 | 50 | 0:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23021000186 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 57 | 2023-02-10 | 2850 | keep | 0 | Feb | 2023 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-10 20:48 | 2023-02-10 22:05 | 259 | 1:17 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | R23021000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-02-10 | 19943 | keep | 0 | Feb | 2023 | 0.013583 | 0.0001764 | Sustained | FALSE | FALSE | Not_TMED_Event | 259
HUMACAO | 2023-02-10 21:05 | 2023-02-10 23:28 | 100 | 2:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C23021000264 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2023-02-10 | 14300 | keep | 0 | Feb | 2023 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-02-10 21:09 | 2023-02-11 14:00 | 3 | 16:51 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | A23021000195 | New_Event | Primary Wire Break | Include | Include | Equipment | 1011 | 2023-02-10 | 3033 | keep | 0 | Feb | 2023 | 0.0020658 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-10 21:30 | 2023-02-10 21:31 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23021000154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 1859 | keep | 0 | Feb | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2023-02-10 22:10 | 2023-02-11 04:34 | 4 | 6:24 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | B23021000159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 384 | 2023-02-10 | 1536 | keep | 0 | Feb | 2023 | 0.0010462 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-02-10 23:09 | 2023-02-11 09:34 | 90 | 10:25 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | S23021000290 | New_Event | Vegetation Contact | Include | Include | Vegetation | 625 | 2023-02-10 | 56250 | keep | 0 | Feb | 2023 | 0.038312 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-02-10 23:31 | 2023-02-10 23:32 | 31 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR SU CARGA POR 9207-06 | B23021000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-10 | 31 | keep | 0 | Feb | 2023 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-02-10 23:56 | 2023-02-11 09:24 | 34 | 9:28 | P | CONDUCTOR ROTO O ABIERTO | SE LLEVO PUENTE PRIMARIO DE LINEA @ CAJA NO FUNDIO | S23021000292 | New_Event | Primary Wire Break | Include | Include | Equipment | 568 | 2023-02-10 | 19312 | keep | 0 | Feb | 2023 | 0.013153 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
MAYAGÃœEZ | 2023-02-11 00:18 | 2023-02-11 07:01 | 3014 | 6:43 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA REPARAR LINEA PRIMARIA ROTA | M23021100008 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 403 | 2023-02-11 | 1214642 | keep | 0 | Feb | 2023 | 0.82729 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-02-11 01:10 | 2023-02-11 09:40 | 100 | 8:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO SE REALIZO DESGANCHE | M23021100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 510 | 2023-02-11 | 51000 | keep | 0 | Feb | 2023 | 0.034736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-02-11 02:40 | 2023-02-11 06:43 | 90 | 4:03 | P | ANIMAL | 2 X 100 EN C/L CRUCE X AVE | B23021100003 | New_Event | Animals | Include | Include | Wildlife | 243 | 2023-02-11 | 21870 | keep | 0 | Feb | 2023 | 0.014896 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-02-11 02:50 | 2023-02-11 05:16 | 231 | 2:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCE | B23021100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-02-11 | 33726 | keep | 0 | Feb | 2023 | 0.022971 | 0.00015733 | Sustained | FALSE | FALSE | Not_TMED_Event | 231
YAUCO | 2023-02-11 03:18 | 2023-02-11 10:20 | 250 | 7:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA PRIMAIA Y 1 X 200 EN CORTE DE LINEA | P23021100020 | New_Event | Cutout Failure | Include | Include | Equipment | 422 | 2023-02-11 | 105500 | keep | 0 | Feb | 2023 | 0.071856 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-02-11 03:55 | 2023-02-11 09:01 | 70 | 5:06 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23021100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2023-02-11 | 21420 | keep | 0 | Feb | 2023 | 0.014589 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-02-11 05:55 | 2023-02-11 11:30 | 40 | 5:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23021100002 | New_Event | Cutout Failure | Include | Include | Equipment | 335 | 2023-02-11 | 13400 | keep | 0 | Feb | 2023 | 0.0091267 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-02-11 06:32 | 2023-02-11 10:21 | 50 | 3:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | M23021100061 | New_Event | Cutout Failure | Include | Include | Equipment | 229 | 2023-02-11 | 11450 | keep | 0 | Feb | 2023 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-11 06:38 | 2023-02-11 09:37 | 150 | 2:59 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23021100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-02-11 | 26850 | keep | 0 | Feb | 2023 | 0.018287 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-02-11 07:16 | 2023-02-11 07:17 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2302110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-11 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
AGUADILLA | 2023-02-11 07:20 | 2023-02-11 11:45 | 30 | 4:25 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23021100073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2023-02-11 | 7950 | keep | 0 | Feb | 2023 | 0.0054147 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-02-11 07:21 | 2023-02-11 11:10 | 120 | 3:49 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23021100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-02-11 | 27480 | keep | 0 | Feb | 2023 | 0.018717 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2023-02-11 07:26 | 2023-02-11 07:27 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23021100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-11 | 3699 | keep | 0 | Feb | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2023-02-11 07:27 | 2023-02-11 07:28 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23021100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-11 | 7621 | keep | 0 | Feb | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
ARECIBO | 2023-02-11 07:40 | 2023-02-11 09:23 | 1 | 1:43 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO RISER Y SE REPARO PUENTE ABIERTO | A23021100006 | New_Event | Primary Wire Break | Include | Include | Equipment | 103 | 2023-02-11 | 103 | keep | 0 | Feb | 2023 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-11 08:02 | 2023-02-11 14:50 | 20 | 6:48 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS | M23021100082 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 408 | 2023-02-11 | 8160 | keep | 0 | Feb | 2023 | 0.0055577 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-02-11 08:07 | 2023-02-11 10:45 | 75 | 2:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LINEA | A23021100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-02-11 | 11850 | keep | 0 | Feb | 2023 | 0.008071 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-02-11 08:28 | 2023-02-11 10:14 | 14 | 1:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON BARRAS EN PEDESTAL RECTANGULAR | R23021100007 | New_Event | Secondary Wire Break | Include | Include | Equipment | 106 | 2023-02-11 | 1484 | keep | 0 | Feb | 2023 | 0.0010107 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-02-11 08:30 | 2023-02-11 11:00 | 20 | 2:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA PORTAFUSIBLE | M23021100091 | New_Event | Cutout Failure | Include | Include | Equipment | 150 | 2023-02-11 | 3000 | keep | 0 | Feb | 2023 | 0.0020433 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-11 08:43 | 2023-02-11 14:31 | 20 | 5:48 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23021100019 | New_Event | Animals | Include | Include | Wildlife | 348 | 2023-02-11 | 6960 | keep | 0 | Feb | 2023 | 0.0047404 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-11 08:49 | 2023-02-11 10:29 | 14 | 1:40 | P | CRUCETA DEFECTUOSA O AVERIADA | 1X40 EN C/L SE REFIRIO PARA REMPLAZO DE CRUCETA PODRIDA | S23021100013 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 100 | 2023-02-11 | 1400 | keep | 0 | Feb | 2023 | 0.00095353 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2023-02-11 08:56 | 2023-02-11 11:13 | 30 | 2:17 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23021100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-02-11 | 4110 | keep | 0 | Feb | 2023 | 0.0027993 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-02-11 09:36 | 2023-02-11 18:28 | 15 | 8:52 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN C/L PROBO MALO DE SU#3 @ T-18 SE REFIERE A SOTERRADO QUEDAN 8 CLIENTES FUERA | C23021100031 | New_Event | UG Cable Fault | Include | Include | Equipment | 532 | 2023-02-11 | 7980 | keep | 0 | Feb | 2023 | 0.0054351 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-02-11 09:37 | 2023-02-11 09:39 | 3420 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2302110000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-02-11 | 6840 | keep | 0 | Feb | 2023 | 0.0046587 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-11 09:39 | 2023-02-11 10:12 | 150 | 0:33 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23021100003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 33 | 2023-02-11 | 4950 | keep | 0 | Feb | 2023 | 0.0033714 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-02-11 09:55 | 2023-02-11 09:57 | 2141 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23021100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-11 | 4282 | keep | 0 | Feb | 2023 | 0.0029165 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
BAYAMON | 2023-02-11 10:01 | 2023-02-11 16:00 | 11 | 5:59 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE RELOCALIZO LINEAS SECUNDARIA A POSTES NUEVOS | S23021100021 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 359 | 2023-02-11 | 3949 | keep | 0 | Feb | 2023 | 0.0026896 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-02-11 10:06 | 2023-02-11 14:43 | 35 | 4:37 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN PROVISIONAL AEREO SE SECCIONALIZO AVERIA T-222 @ T-221 | B23021100027 | New_Event | UG Cable Fault | Include | Include | Equipment | 277 | 2023-02-11 | 9695 | keep | 0 | Feb | 2023 | 0.0066032 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-02-11 10:17 | 2023-02-11 12:35 | 9 | 2:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO PM PARA REMPLAZO DE CONEXIONES SECUNDARIAS | A23021100026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 138 | 2023-02-11 | 1242 | keep | 0 | Feb | 2023 | 0.00084592 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-02-11 10:18 | 2023-02-12 16:34 | 15 | 30:16 | P | CABLE SOTERRADO AVERIADO | MEDIANTE GOI BY-230211-04 SE REPARO TRAMO SOTERRADO | B23021100029 | New_Event | UG Cable Fault | Include | Include | Equipment | 1816 | 2023-02-11 | 27240 | keep | 0 | Feb | 2023 | 0.018553 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-11 10:20 | 2023-02-11 10:48 | 200 | 0:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R23021100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2023-02-11 | 5600 | keep | 0 | Feb | 2023 | 0.0038141 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2023-02-11 10:29 | 2023-02-13 10:41 | 3 | 48:12 | P | TRANSFORMADOR AVERIADO | SE REPAPRO BUSHING SECUNDARIO Y SE TIRO SECUNDARIA NUEVA HABIA EVENTO P23021100055 SITUACION PELIGROSA, FOREMAN INDICA QUE ESTABN SIN SERVICIO | P23021300024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2892 | 2023-02-11 | 8676 | keep | 0 | Feb | 2023 | 0.0059092 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-02-11 10:30 | 2023-02-11 11:15 | 10 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO SECUNDARIAS | M23021100058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-02-11 | 450 | keep | 0 | Feb | 2023 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-11 10:35 | 2023-02-11 12:00 | 60 | 1:25 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23021100044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-02-11 | 5100 | keep | 0 | Feb | 2023 | 0.0034736 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-11 10:36 | 2023-02-11 11:33 | 26 | 0:57 | P | CAUSAS EXTERNAS | 1X100 EN C/L CAMION SE ENRREDO EN EL 4KV | S23021100024 | New_Event | Damage From Public | Include | Include | Public | 57 | 2023-02-11 | 1482 | keep | 0 | Feb | 2023 | 0.0010094 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
PONCE | 2023-02-11 10:39 | 2023-02-11 10:42 | 3744 | 0:03 | T | ERROR HUMANO | AL REALIZAR TRABAJO EN CAMBIO DE POSTE HUBO CONTACTO DE RAMA DE ARBOL CON LINEA PRIMARIA SACANDO ALIMENTADOR DE SERVICIO, RECIERRE ESTABA EN OFF | P23021100057 | New_Event | Human Error | Include | Include | Other | 3 | 2023-02-11 | 11232 | keep | 0 | Feb | 2023 | 0.0076501 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
ARECIBO | 2023-02-11 10:55 | 2023-02-11 16:15 | 5 | 5:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A23021100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2023-02-11 | 1600 | keep | 0 | Feb | 2023 | 0.0010898 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-02-11 11:29 | 2023-02-11 18:46 | 13 | 7:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARARON CONEXIONES SECUNDARIAS | P23021100061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 437 | 2023-02-11 | 5681 | keep | 0 | Feb | 2023 | 0.0038693 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2023-02-11 11:37 | 2023-02-11 14:25 | 80 | 2:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A23021100036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-02-11 | 13440 | keep | 0 | Feb | 2023 | 0.0091539 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-02-11 11:41 | 2023-02-11 17:45 | 25 | 6:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPAR0 BAJANTE PRIMARIO | M23021100130 | New_Event | Primary Wire Break | Include | Include | Equipment | 364 | 2023-02-11 | 9100 | keep | 0 | Feb | 2023 | 0.006198 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-11 11:42 | 2023-02-11 13:53 | 733 | 2:11 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE TRANSFIRIO CARGA AL 1206-04 PARA REMPLAZO DE MACHETE PRIMARIO QUEMADO | S23021100035 | New_Event | Switch Failure | Include | Include | Equipment | 131 | 2023-02-11 | 96023 | keep | 0 | Feb | 2023 | 0.065401 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2023-02-11 11:48 | 2023-02-11 12:27 | 14 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA NO FUNDIO | S23021100036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-02-11 | 546 | keep | 0 | Feb | 2023 | 0.00037188 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2023-02-11 12:03 | 2023-02-11 12:04 | 508 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23021100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-11 | 508 | keep | 0 | Feb | 2023 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-02-11 12:03 | 2023-02-11 12:04 | 64 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23021100066 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-11 | 64 | keep | 0 | Feb | 2023 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
HUMACAO | 2023-02-11 12:24 | 2023-02-11 13:35 | 70 | 1:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA SE REEMPLAZO AISLADOR | C23021100057 | New_Event | Cutout Failure | Include | Include | Equipment | 71 | 2023-02-11 | 4970 | keep | 0 | Feb | 2023 | 0.003385 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2023-02-11 12:30 | 2023-02-11 14:30 | 8 | 2:00 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN TRANSFORMADOR LINEAS CRUZADAS | M23021100136 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 120 | 2023-02-11 | 960 | keep | 0 | Feb | 2023 | 0.00065385 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-11 12:33 | 2023-02-11 16:02 | 200 | 3:29 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA PRINCIPAL 1 X 65 EN CORTE DE LINEA SECUNDARIO DESGANCHE | S23021100047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-02-11 | 41800 | keep | 0 | Feb | 2023 | 0.02847 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-02-11 12:34 | 2023-02-11 16:28 | 43 | 3:54 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO RAMA | B23021100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2023-02-11 | 10062 | keep | 0 | Feb | 2023 | 0.0068532 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
VEGA BAJA | 2023-02-11 12:42 | 2023-02-11 15:30 | 40 | 2:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 30 EN DISTINTOS CORTE DE LINEA LLUVIA Y VIENTO | A23021100043 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 168 | 2023-02-11 | 6720 | keep | 0 | Feb | 2023 | 0.004577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-02-11 12:50 | 2023-02-11 15:20 | 250 | 2:30 | P | PARARRAYOS DEFECTUOSO | SE RETIRA PARARRAYO Y CABLE CRUZADO EN RISER | P23021100069 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 150 | 2023-02-11 | 37500 | keep | 0 | Feb | 2023 | 0.025541 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-02-11 12:52 | 2023-02-11 15:30 | 50 | 2:38 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE LEVANTO PRIMARIA | S23021100057 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2023-02-11 | 7900 | keep | 0 | Feb | 2023 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-11 13:01 | 2023-02-11 17:39 | 100 | 4:38 | P | CONDUCTOR ROTO O ABIERTO | CON GOI BY 230211-03 SE REPARO CONDUCTOR | B23021100063 | New_Event | Primary Wire Break | Include | Include | Equipment | 278 | 2023-02-11 | 27800 | keep | 0 | Feb | 2023 | 0.018934 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-02-11 13:04 | 2023-02-11 13:35 | 272 | 0:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | C23021100066 | New_Event | Primary Wire Break | Include | Include | Equipment | 31 | 2023-02-11 | 8432 | keep | 0 | Feb | 2023 | 0.005743 | 0.00018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 272
MAYAGÃœEZ | 2023-02-11 13:04 | 2023-02-11 15:20 | 90 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021100140 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2023-02-11 | 12240 | keep | 0 | Feb | 2023 | 0.0083366 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
GUAYAMA | 2023-02-11 13:10 | 2023-02-11 13:11 | 1093 | 0:01 | T | PROTECCION DEFECTUOSA | RECIERRE | P23021100071 | New_Event | Protection Miscoordination | Include | Include | Other | 1 | 2023-02-11 | 1093 | keep | 0 | Feb | 2023 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
MAYAGÃœEZ | 2023-02-11 13:11 | 2023-02-11 16:17 | 10 | 3:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M23021100142 | New_Event | Cutout Failure | Include | Include | Equipment | 186 | 2023-02-11 | 1860 | keep | 0 | Feb | 2023 | 0.0012668 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-02-11 13:16 | 2023-02-11 13:25 | 3744 | 0:09 | T | DESGANCHE | ARBOL SOBRE LINEA DEBIDO A FUERTE BRISA | P23021100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 9 | 2023-02-11 | 33696 | keep | 0 | Feb | 2023 | 0.02295 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
ARECIBO | 2023-02-11 13:18 | 2023-02-11 15:07 | 1227 | 1:49 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR SE INSTALO AISLACION A FASE QUE ESTA CRUZANDO CON CRUCETA Y CERCA DE UNA FASE DEL 8002-03 Y SE CERRO EL INTERRUPTOR ESTA CONDICION ESTA PROGRAMADA PARA REPARARCE ESTA SEMANA | A23021100053 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 109 | 2023-02-11 | 133743 | keep | 0 | Feb | 2023 | 0.091092 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
CAGUAS | 2023-02-11 13:22 | 2023-02-11 15:56 | 1 | 2:34 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23021100076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-02-11 | 154 | keep | 0 | Feb | 2023 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-11 13:27 | 2023-02-11 16:10 | 146 | 2:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON TRES CAJAS PRIMARIAS 3 X 100 Y 3 X 140 EN SENDOS CORTES DE LINEAS | P23021100076 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2023-02-11 | 23798 | keep | 0 | Feb | 2023 | 0.016209 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
PONCE | 2023-02-11 13:34 | 2023-02-11 16:05 | 1717 | 2:31 | S | LINEA DE TRANSMISION 38KV | POSTE PARTIDO | P23021100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2023-02-11 | 259267 | keep | 0 | Feb | 2023 | 0.17659 | 0.0011694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1717
PONCE | 2023-02-11 13:34 | 2023-02-11 16:05 | 974 | 2:31 | S | LINEA DE TRANSMISION 38KV | POSTE PARTIDO | P23021100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2023-02-11 | 147074 | keep | 0 | Feb | 2023 | 0.10017 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
PONCE | 2023-02-11 13:34 | 2023-02-11 16:05 | 1905 | 2:31 | S | LINEA DE TRANSMISION 38KV | POSTE PARTIDO | P23021100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2023-02-11 | 287655 | keep | 0 | Feb | 2023 | 0.19592 | 0.0012975 | Sustained | FALSE | FALSE | Not_TMED_Event | 1905
PONCE | 2023-02-11 13:34 | 2023-02-11 16:05 | 1262 | 2:31 | S | LINEA DE TRANSMISION 38KV | POSTE PARTIDO | P23021100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2023-02-11 | 190562 | keep | 0 | Feb | 2023 | 0.12979 | 0.00085954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1262
PONCE | 2023-02-11 13:34 | 2023-02-11 16:05 | 200 | 2:31 | S | LINEA DE TRANSMISION 38KV | POSTE PARTIDO | P23021100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2023-02-11 | 30200 | keep | 0 | Feb | 2023 | 0.020569 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2023-02-11 13:34 | 2023-02-11 16:05 | 222 | 2:31 | S | LINEA DE TRANSMISION 38KV | POSTE PARTIDO | P23021100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2023-02-11 | 33522 | keep | 0 | Feb | 2023 | 0.022832 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
PONCE | 2023-02-11 13:34 | 2023-02-11 16:05 | 537 | 2:31 | S | LINEA DE TRANSMISION 38KV | POSTE PARTIDO | P23021100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2023-02-11 | 81087 | keep | 0 | Feb | 2023 | 0.055228 | 0.00036575 | Sustained | FALSE | FALSE | Not_TMED_Event | 537
PONCE | 2023-02-11 13:34 | 2023-02-11 16:06 | 1033 | 2:32 | S | LINEA DE TRANSMISION 38KV | POSTE PARTIDO | P23021100087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2023-02-11 | 157016 | keep | 0 | Feb | 2023 | 0.10694 | 0.00070357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1033
SAN JUAN | 2023-02-11 13:35 | 2023-02-11 13:36 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRRE DE INTERRUPTOR 1206-03 LLEVA 85% DEL 1204-05 | S2302110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-11 | 8679 | keep | 0 | Feb | 2023 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-02-11 13:35 | 2023-02-11 13:36 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRRE DE INTERRUPTOR 1206-03 LLEVA 85% DEL 1204-05 | S2302110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-11 | 4133 | keep | 0 | Feb | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
HUMACAO | 2023-02-11 13:35 | 2023-02-11 13:36 | 519 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | C23021100077 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-11 | 519 | keep | 0 | Feb | 2023 | 0.00035349 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-11 13:36 | 2023-02-11 14:51 | 70 | 1:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA SE REEMPLAZO AISLADOR | C23021100057 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 75 | 2023-02-11 | 5250 | keep | 0 | Feb | 2023 | 0.0035758 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-02-11 13:41 | 2023-02-11 18:42 | 66 | 5:01 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN C/L SE SECCIONALIZO CONDUCTOR EN EL SUELO | B23021100074 | New_Event | Primary Wire Break | Include | Include | Equipment | 301 | 2023-02-11 | 19866 | keep | 0 | Feb | 2023 | 0.013531 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
VEGA BAJA | 2023-02-11 13:46 | 2023-02-11 13:47 | 4027 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE | B2302110000X | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2023-02-11 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-02-11 13:47 | 2023-02-11 17:57 | 132 | 4:10 | P | ARBOL SOBRE LINEA | 1 X 30 EN C/L SE RETIRO ARBOL DE LA LINEA | B23021100083 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 250 | 2023-02-11 | 33000 | keep | 0 | Feb | 2023 | 0.022476 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
CANOVANAS | 2023-02-11 13:58 | 2023-02-11 14:27 | 5 | 0:29 | P | NO SE REPORTO CAUSA | 1 X 25 EN AEREO PROVISIONAL | R23021100026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2023-02-11 | 145 | keep | 0 | Feb | 2023 | 9.8759e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-02-11 14:43 | 2023-02-12 02:56 | 37 | 12:13 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL DE EXISTENTE A T-219 AVERIA DE RISER A T-219 | B23021100027 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 733 | 2023-02-11 | 27121 | keep | 0 | Feb | 2023 | 0.018472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-11 14:47 | 2023-02-11 15:18 | 2697 | 0:31 | T | CONDUCTOR ARRIADO O CRUZADO | INTERRUPTOR OPERO Y JUAN RESTO LLAMO Y PIDIO POR SEGURIDAD QUE SE DEJARA ABIERTO LUEGO ABRIO MACHETES Y SECCIONALIZO BAJANTE PRIMARIO ZAFADO Y CRUZANDO EN EL TRONCAL DEL ALIMENTADOR SE CERRO EL INTERRUPTOR | A23021100076 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 31 | 2023-02-11 | 83607 | keep | 0 | Feb | 2023 | 0.056944 | 0.0018369 | Sustained | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-02-11 15:18 | 2023-02-11 17:05 | 800 | 1:47 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO LOS TRES PARARRAYOS Y LOS TRES BAJANTES PRIMARIOS DE LA MONTURA QUE SE DAÃ‘ARON CON EL BAJANTE PRIMARIO QUE SE DESPRENDIO Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A23021100086 | New_Event | Primary Wire Break | Include | Include | Equipment | 107 | 2023-02-11 | 85600 | keep | 0 | Feb | 2023 | 0.058302 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
VEGA BAJA | 2023-02-11 15:23 | 2023-02-11 19:14 | 25 | 3:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B23021100086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2023-02-11 | 5775 | keep | 0 | Feb | 2023 | 0.0039333 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-11 15:30 | 2023-02-11 16:40 | 3 | 1:10 | P | ERROR HUMANO | 1 X 100 EN C/L PERSONAL DE PODA TIRO RAMA SOBRE LA LINEA | B23021100087 | New_Event | Human Error | Include | Include | Other | 70 | 2023-02-11 | 210 | keep | 0 | Feb | 2023 | 0.00014303 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-02-11 15:36 | 2023-02-11 19:20 | 110 | 3:44 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M23021100157 | New_Event | Primary Wire Break | Include | Include | Equipment | 224 | 2023-02-11 | 24640 | keep | 0 | Feb | 2023 | 0.016782 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2023-02-11 15:50 | 2023-02-11 23:30 | 25 | 7:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN RISER POR MAL TIEMPO | M23021100160 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 460 | 2023-02-11 | 11500 | keep | 0 | Feb | 2023 | 0.0078326 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-02-11 16:09 | 2023-02-11 17:25 | 20 | 1:16 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23021100092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-02-11 | 1520 | keep | 0 | Feb | 2023 | 0.0010353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-11 17:00 | 2023-02-11 22:43 | 11 | 5:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA POR 50KVA | B23021100095 | New_Event | Service Transformer Failure | Include | Include | Equipment | 343 | 2023-02-11 | 3773 | keep | 0 | Feb | 2023 | 0.0025698 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-02-11 17:47 | 2023-02-11 21:00 | 12 | 3:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23021100104 | New_Event | Secondary Wire Break | Include | Include | Equipment | 193 | 2023-02-11 | 2316 | keep | 0 | Feb | 2023 | 0.0015774 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-02-11 17:53 | 2023-02-11 22:41 | 100 | 4:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR VIENTOS | M23021100177 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 288 | 2023-02-11 | 28800 | keep | 0 | Feb | 2023 | 0.019616 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-02-11 18:08 | 2023-02-12 10:40 | 12 | 16:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE REPARO SECUNDARIA | C23021100098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 992 | 2023-02-11 | 11904 | keep | 0 | Feb | 2023 | 0.0081078 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-02-11 18:20 | 2023-02-12 10:50 | 200 | 16:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | M23021100185 | New_Event | Primary Wire Break | Include | Include | Equipment | 990 | 2023-02-11 | 198000 | keep | 0 | Feb | 2023 | 0.13486 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-02-11 18:28 | 2023-02-12 17:33 | 8 | 23:05 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERIADO AVERIADO DEL SU#3 AL T-18 | C23021100031 | New_Event | UG Cable Fault | Include | Include | Equipment | 1385 | 2023-02-11 | 11080 | keep | 0 | Feb | 2023 | 0.0075465 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-11 18:40 | 2023-02-11 19:10 | 6 | 0:30 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRE TRANSFORMADOR PARA REPARAR LINEA ARRIADA | S23021100107 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 30 | 2023-02-11 | 180 | keep | 0 | Feb | 2023 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-11 18:42 | 2023-02-12 18:00 | 10 | 23:18 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO PRIMARIA Y SE CERRO PUENTE | B23021100074 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1398 | 2023-02-11 | 13980 | keep | 0 | Feb | 2023 | 0.0095217 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-11 19:21 | 2023-02-11 19:22 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2302110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-11 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2023-02-11 20:06 | 2023-02-12 02:43 | 84 | 6:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS | B23021100117 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 397 | 2023-02-11 | 33348 | keep | 0 | Feb | 2023 | 0.022713 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
UTUADO | 2023-02-11 20:32 | 2023-02-12 09:00 | 25 | 12:28 | P | CONDUCTOR ROTO O ABIERTO | REPARAR BAJANTE PRIMARIO DE CAJA PRIMARIA EN CORTE DE LINEA A LINEA PRIMARIA | A23021100103 | New_Event | Primary Wire Break | Include | Include | Equipment | 748 | 2023-02-11 | 18700 | keep | 0 | Feb | 2023 | 0.012736 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-02-11 20:40 | 2023-02-12 08:15 | 10 | 11:35 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23021100103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 695 | 2023-02-11 | 6950 | keep | 0 | Feb | 2023 | 0.0047336 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-11 20:48 | 2023-02-11 22:29 | 25 | 1:41 | P | TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO TERMINACION AEREA DE PROVISIONAL QUEMADO | R23021100040 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 101 | 2023-02-11 | 2525 | keep | 0 | Feb | 2023 | 0.0017198 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-11 22:42 | 2023-02-12 00:25 | 50 | 1:43 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO FASE | S23021100114 | New_Event | Animals | Include | Include | Wildlife | 103 | 2023-02-11 | 5150 | keep | 0 | Feb | 2023 | 0.0035076 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-12 00:51 | 2023-02-12 09:43 | 15 | 8:52 | P | DESGANCHE | 1 X 20 EN XMR SE REEMPLAZO PORTAFUSIBLE Y SE REALIZO DESGANCHE PRIMARIO | R23021200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 532 | 2023-02-12 | 7980 | keep | 0 | Feb | 2023 | 0.0054351 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-02-12 01:02 | 2023-02-12 03:37 | 4830 | 2:35 | P | CAUSAS EXTERNAS | DISPARO | C23021200023 | New_Event | Damage From Public | Include | Include | Public | 155 | 2023-02-12 | 748650 | keep | 0 | Feb | 2023 | 0.5099 | 0.0032897 | Sustained | FALSE | FALSE | Not_TMED_Event | 4830
HUMACAO | 2023-02-12 03:37 | 2023-02-12 04:16 | 2578 | 0:39 | P | CAUSAS EXTERNAS | SE SECCIONALIZARON DISCOS ROTOS EN TRONCAL DE LA LINEA DEBIDO A CRUCE CON GLOBO | C23021200023 | Partial_restoration | Damage From Public | Include | Include | Public | 39 | 2023-02-12 | 100542 | keep | 0 | Feb | 2023 | 0.068479 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-12 04:16 | 2023-02-12 06:12 | 2015 | 1:56 | P | CAUSAS EXTERNAS | SE REEMPLAZARON DISCOS PARTIDOS EN TRONCAL DEBIDO A CRUCE CON GLOBO Y SE CERRARON MACHETES 100% EN SERVICIO | C23021200023 | Partial_restoration | Damage From Public | Include | Include | Public | 116 | 2023-02-12 | 233740 | keep | 0 | Feb | 2023 | 0.1592 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-12 04:53 | 2023-02-12 09:29 | 1 | 4:36 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN XMR PROA SE DESCONECTO CLIENTE CON AVERIA INTERNA | B23021200003 | New_Event | Customer-Related Interruption | Include | Include | Public | 276 | 2023-02-12 | 276 | keep | 0 | Feb | 2023 | 0.00018798 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-12 05:24 | 2023-02-12 10:43 | 252 | 5:19 | P | TERMINACION SOTERRADA AVERIADA | 1X65 EN C/L, 1X50 EN C/L, 1X40 EN OTRO C/L Y SE REMPLAZO PISTOLA QUEMADA DE RISER @ T-22 | S23021200003 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 319 | 2023-02-12 | 80388 | keep | 0 | Feb | 2023 | 0.054752 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-02-12 05:42 | 2023-02-12 06:35 | 1 | 0:53 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN C/L SE REMPLAZO PARARRAYO | B23021200004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 53 | 2023-02-12 | 53 | keep | 0 | Feb | 2023 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-12 05:58 | 2023-02-12 08:27 | 50 | 2:29 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | A23021200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-02-12 | 7450 | keep | 0 | Feb | 2023 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-12 06:32 | 2023-02-12 06:33 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23021200042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-12 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2023-02-12 07:05 | 2023-02-12 12:06 | 10 | 5:01 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASES | M23021200003 | New_Event | Animals | Include | Include | Wildlife | 301 | 2023-02-12 | 3010 | keep | 0 | Feb | 2023 | 0.0020501 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-12 07:29 | 2023-02-12 09:44 | 30 | 2:15 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | B23021200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-02-12 | 4050 | keep | 0 | Feb | 2023 | 0.0027584 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-02-12 07:40 | 2023-02-12 13:05 | 15 | 5:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE TRANSFORMADOR | M23021200005 | New_Event | Cutout Failure | Include | Include | Equipment | 325 | 2023-02-12 | 4875 | keep | 0 | Feb | 2023 | 0.0033203 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-02-12 07:50 | 2023-02-12 10:37 | 100 | 2:47 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P23021200013 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-02-12 | 16700 | keep | 0 | Feb | 2023 | 0.011374 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-02-12 08:03 | 2023-02-12 08:05 | 1681 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 1303-04, SU CARGA ESTA TRANSFERIDA AL 1303-05 LLEVA EL 1346-04 LLEVA EL 1303-03 LLEVA EL 1346-06 LLEVA EL 1303-01 SE CERRO POR CONTROL | S23021220000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-12 | 3362 | keep | 0 | Feb | 2023 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-02-12 08:03 | 2023-02-12 08:05 | 726 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DEL INTERRUPTOR 1303-04, SU CARGA ESTA TRANSFERIDA AL 1303-05 LLEVA EL 1346-04 LLEVA EL 1303-06 LLEVA EL 1346-06 LLEVA EL 1303-01 SE CERRO POR CONTROL | S23021220000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-12 | 1452 | keep | 0 | Feb | 2023 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-02-12 08:03 | 2023-02-12 08:05 | 3932 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DEL INTERRUPTOR 1303-04, SU CARGA ESTA TRANSFERIDA AL 1303-05 LLEVA EL 1346-04 LLEVA EL 1303-06 LLEVA EL 1346-06 LLEVA EL 1303-01 SE CERRO POR CONTROL | S23021220000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-12 | 7864 | keep | 0 | Feb | 2023 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2023-02-12 08:03 | 2023-02-12 08:05 | 1598 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DEL INTERRUPTOR 1303-04, SU CARGA ESTA TRANSFERIDA AL 1303-05 LLEVA EL 1346-04 LLEVA EL 1303-06 LLEVA EL 1346-06 LLEVA EL 1303-01 SE CERRO POR CONTROL | S23021220000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-12 | 3196 | keep | 0 | Feb | 2023 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
VEGA BAJA | 2023-02-12 08:10 | 2023-02-12 08:11 | 67 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23021200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-12 | 67 | keep | 0 | Feb | 2023 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-02-12 08:45 | 2023-02-12 09:23 | 9 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REMPLAZARON BARRAS SECUNDARIAS EN PEDESTAL | S23021200015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2023-02-12 | 342 | keep | 0 | Feb | 2023 | 0.00023293 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-02-12 08:45 | 2023-02-12 10:05 | 15 | 1:20 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE CONEXIONES SECUNDARIAS | M23021000412 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 80 | 2023-02-12 | 1200 | keep | 0 | Feb | 2023 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-12 09:02 | 2023-02-12 11:19 | 20 | 2:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO QUEMADO | S23021200019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 137 | 2023-02-12 | 2740 | keep | 0 | Feb | 2023 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-12 09:09 | 2023-02-12 10:02 | 29 | 0:53 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S23021200020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2023-02-12 | 1537 | keep | 0 | Feb | 2023 | 0.0010468 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
VEGA BAJA | 2023-02-12 09:21 | 2023-02-12 10:15 | 300 | 0:54 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SOBRE CRUCETA SE ABRE INTERRUPTOR PARA CORREGIR CONDICION | A23021200013 | New_Event | Primary Wire Break | Include | Include | Equipment | 54 | 2023-02-12 | 16200 | keep | 0 | Feb | 2023 | 0.011034 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-02-12 09:25 | 2023-02-12 11:25 | 10 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23021100104 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2023-02-12 | 1200 | keep | 0 | Feb | 2023 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-12 09:33 | 2023-02-12 15:50 | 10 | 6:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | M23021200019 | New_Event | Cutout Failure | Include | Include | Equipment | 377 | 2023-02-12 | 3770 | keep | 0 | Feb | 2023 | 0.0025677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-02-12 09:40 | 2023-02-12 11:06 | 12 | 1:26 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO CAUSA | P23021200019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2023-02-12 | 1032 | keep | 0 | Feb | 2023 | 0.00070289 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-12 09:45 | 2023-02-12 09:46 | 1 | 0:01 | P | ANIMAL | 1 X 15 EN XMR POR CRUCE DE AVE | B23021200005 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-12 | 1 | keep | 0 | Feb | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-12 09:58 | 2023-02-12 10:58 | 37 | 1:00 | P | ANIMAL | SE REEMPLAZO CAJA PRIMARIA QUEMADA. CRUCE POR AVE. | R23021200005 | New_Event | Animals | Include | Include | Wildlife | 60 | 2023-02-12 | 2220 | keep | 0 | Feb | 2023 | 0.001512 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
MAYAGÃœEZ | 2023-02-12 10:10 | 2023-02-12 12:50 | 6 | 2:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REMPLAZO LA CAJA PRIMARIA Y LOS BAJANTES | M23021200024 | New_Event | Cutout Failure | Include | Include | Equipment | 160 | 2023-02-12 | 960 | keep | 0 | Feb | 2023 | 0.00065385 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-02-12 10:15 | 2023-02-12 10:40 | 2132 | 0:25 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO Y SE COLOCO INTERRUPTOR EN SERVICIO | A23021200013 | New_Event | Primary Wire Break | Include | Include | Equipment | 25 | 2023-02-12 | 53300 | keep | 0 | Feb | 2023 | 0.036302 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
FAJARDO | 2023-02-12 10:21 | 2023-02-12 12:05 | 1 | 1:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR SE REEMPLAZO CAJA | R23021200007 | New_Event | Cutout Failure | Include | Include | Equipment | 104 | 2023-02-12 | 104 | keep | 0 | Feb | 2023 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-12 10:46 | 2023-02-12 15:25 | 23 | 4:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO VIENTOS | C23021200055 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 279 | 2023-02-12 | 6417 | keep | 0 | Feb | 2023 | 0.0043706 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2023-02-12 10:53 | 2023-02-12 11:31 | 12 | 0:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA @ CAJA EN C/L | S23021200025 | New_Event | Primary Wire Break | Include | Include | Equipment | 38 | 2023-02-12 | 456 | keep | 0 | Feb | 2023 | 0.00031058 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-02-12 11:14 | 2023-02-12 12:18 | 25 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23021200056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2023-02-12 | 1600 | keep | 0 | Feb | 2023 | 0.0010898 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-02-12 11:16 | 2023-02-12 11:35 | 7 | 0:19 | P | TRANSFORMADOR AVERIADO | SE REPARARON BUSHINGS SECUNDARIOS | P23021200022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 19 | 2023-02-12 | 133 | keep | 0 | Feb | 2023 | 9.0586e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-02-12 11:25 | 2023-02-12 14:00 | 1 | 2:35 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23021200058 | New_Event | Animals | Include | Include | Wildlife | 155 | 2023-02-12 | 155 | keep | 0 | Feb | 2023 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-12 11:32 | 2023-02-12 13:21 | 5 | 1:49 | P | ANIMAL | 1 X 10 EN XMR | C23021200059 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-02-12 | 545 | keep | 0 | Feb | 2023 | 0.0003712 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-02-12 11:35 | 2023-02-12 12:15 | 20 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR CONECTOR NEUTRAL SEC Y SE REGULO VOLTAJE | R23021200013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-02-12 | 800 | keep | 0 | Feb | 2023 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-02-12 11:37 | 2023-02-12 14:04 | 24 | 2:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REEMPLAZO AISLADOR ROTO | R23021200014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 147 | 2023-02-12 | 3528 | keep | 0 | Feb | 2023 | 0.0024029 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-02-12 11:39 | 2023-02-12 11:40 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23021200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-12 | 2234 | keep | 0 | Feb | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2023-02-12 11:50 | 2023-02-12 12:00 | 10 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTOR SECUNDARIO | A23020700038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-02-12 | 100 | keep | 0 | Feb | 2023 | 6.811e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-02-12 11:58 | 2023-02-12 13:40 | 10 | 1:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | P23021200025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 102 | 2023-02-12 | 1020 | keep | 0 | Feb | 2023 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-12 12:24 | 2023-02-12 14:41 | 10 | 2:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO EN XMR | S23021200030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 137 | 2023-02-12 | 1370 | keep | 0 | Feb | 2023 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-12 12:40 | 2023-02-12 12:41 | 2675 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23021200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-12 | 2675 | keep | 0 | Feb | 2023 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
BAYAMON | 2023-02-12 12:45 | 2023-02-12 13:07 | 40 | 0:22 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | B23021200025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-02-12 | 880 | keep | 0 | Feb | 2023 | 0.00059936 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-02-12 12:47 | 2023-02-12 14:29 | 60 | 1:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021200035 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 102 | 2023-02-12 | 6120 | keep | 0 | Feb | 2023 | 0.0041683 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-02-12 13:12 | 2023-02-12 13:13 | 1702 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | C23021200064 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-02-12 | 1702 | keep | 0 | Feb | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-02-12 13:13 | 2023-02-12 14:40 | 120 | 1:27 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETE ABIERTO | C23021200066 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 87 | 2023-02-12 | 10440 | keep | 0 | Feb | 2023 | 0.0071106 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-02-12 13:16 | 2023-02-12 16:29 | 7 | 3:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23021200026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 193 | 2023-02-12 | 1351 | keep | 0 | Feb | 2023 | 0.00092016 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2023-02-12 13:16 | 2023-02-12 14:35 | 20 | 1:19 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA POR CANOPY | P23021200027 | New_Event | Damage From Public | Include | Include | Public | 79 | 2023-02-12 | 1580 | keep | 0 | Feb | 2023 | 0.0010761 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-12 13:19 | 2023-02-12 16:00 | 40 | 2:41 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA @ CAJA NO FUNDIO | S23021200033 | New_Event | Primary Wire Break | Include | Include | Equipment | 161 | 2023-02-12 | 6440 | keep | 0 | Feb | 2023 | 0.0043863 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-02-12 13:26 | 2023-02-12 13:27 | 464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23021200029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-12 | 464 | keep | 0 | Feb | 2023 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2023-02-12 13:38 | 2023-02-12 14:11 | 1 | 0:33 | P | ANIMAL | 1 X 30 EN TRANSFORMADOR AVE | P23021200031 | New_Event | Animals | Include | Include | Wildlife | 33 | 2023-02-12 | 33 | keep | 0 | Feb | 2023 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-12 13:49 | 2023-02-12 15:48 | 7 | 1:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23021200068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2023-02-12 | 833 | keep | 0 | Feb | 2023 | 0.00056735 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-02-12 13:52 | 2023-02-12 15:55 | 109 | 2:03 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L SE RETEZO LINEA | B23021200028 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 123 | 2023-02-12 | 13407 | keep | 0 | Feb | 2023 | 0.0091314 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
MAYAGÃœEZ | 2023-02-12 14:12 | 2023-02-12 17:30 | 10 | 3:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021200058 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 198 | 2023-02-12 | 1980 | keep | 0 | Feb | 2023 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-12 14:20 | 2023-02-12 15:40 | 12 | 1:20 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMAFOR Y SE REPARO BUSHING SECUNDARIO DE XMR | B23021200031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 80 | 2023-02-12 | 960 | keep | 0 | Feb | 2023 | 0.00065385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-02-12 14:27 | 2023-02-12 17:20 | 1 | 2:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23021200060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-02-12 | 173 | keep | 0 | Feb | 2023 | 0.00011783 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-12 14:28 | 2023-02-12 16:33 | 50 | 2:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA RAMA SOBRE LINEA | P23021200033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-02-12 | 6250 | keep | 0 | Feb | 2023 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-02-12 14:32 | 2023-02-12 18:30 | 90 | 3:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021200061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 238 | 2023-02-12 | 21420 | keep | 0 | Feb | 2023 | 0.014589 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2023-02-12 14:34 | 2023-02-13 10:22 | 5 | 19:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 KVA X UNO DE 50KVA | B23021200034 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1188 | 2023-02-12 | 5940 | keep | 0 | Feb | 2023 | 0.0040457 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-02-12 14:44 | 2023-02-12 16:21 | 40 | 1:37 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B23021200036 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-02-12 | 3880 | keep | 0 | Feb | 2023 | 0.0026427 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-12 14:59 | 2023-02-12 15:00 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2302120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-12 | 45 | keep | 0 | Feb | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-02-12 15:01 | 2023-02-12 18:45 | 1 | 3:44 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE SECUNDARIA | M23021200075 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 224 | 2023-02-12 | 224 | keep | 0 | Feb | 2023 | 0.00015257 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-12 15:07 | 2023-02-12 17:28 | 134 | 2:21 | P | CAUSAS EXTERNAS | 1X100 EN C/L SE RETIRO GLOBO DE HULE | S23021200039 | New_Event | Damage From Public | Include | Include | Public | 141 | 2023-02-12 | 18894 | keep | 0 | Feb | 2023 | 0.012869 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
YAUCO | 2023-02-12 15:07 | 2023-02-13 07:47 | 9 | 16:40 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | P23021200035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1000 | 2023-02-12 | 9000 | keep | 0 | Feb | 2023 | 0.0061299 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2023-02-12 15:53 | 2023-02-12 16:00 | 10 | 0:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REMPLAZO CONECTOR SECUNDARIO | A22121900032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 7 | 2023-02-12 | 70 | keep | 0 | Feb | 2023 | 4.7677e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-12 16:11 | 2023-02-12 18:40 | 66 | 2:29 | P | ANIMAL | 1 X 80 EN C/L SE RETIRO IGUANA | S23021200047 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-02-12 | 9834 | keep | 0 | Feb | 2023 | 0.0066979 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2023-02-12 16:18 | 2023-02-12 17:05 | 12 | 0:47 | P | DESGANCHE | 2 X 25 EN C/L DESGANCHE | B23021200043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2023-02-12 | 564 | keep | 0 | Feb | 2023 | 0.00038414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-02-12 16:30 | 2023-02-12 17:28 | 1 | 0:58 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN MONTURA TRIFASICA PROBLEMA DEL CLIENTE | P23021200042 | New_Event | Customer-Related Interruption | Include | Include | Public | 58 | 2023-02-12 | 58 | keep | 0 | Feb | 2023 | 3.9504e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-02-12 17:22 | 2023-02-12 18:50 | 10 | 1:28 | P | ANIMAL | 1 X 30 EN CL IGUANA | A23021200052 | New_Event | Animals | Include | Include | Wildlife | 88 | 2023-02-12 | 880 | keep | 0 | Feb | 2023 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-12 17:46 | 2023-02-12 19:02 | 174 | 1:16 | P | ANIMAL | 1 X 65 Y 1 X 50 EN C/L AVE CRUZO LINEAS | R23021200027 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-02-12 | 13224 | keep | 0 | Feb | 2023 | 0.0090068 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
CANOVANAS | 2023-02-12 17:50 | 2023-02-12 17:51 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23021200029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-12 | 4085 | keep | 0 | Feb | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
BAYAMON | 2023-02-12 18:35 | 2023-02-13 11:20 | 13 | 16:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE CERRO PUENTE DE CAJA A TRANSFORMADOR | B23021200053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1005 | 2023-02-12 | 13065 | keep | 0 | Feb | 2023 | 0.0088985 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2023-02-12 18:40 | 2023-02-13 08:38 | 9 | 13:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P23021200050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 838 | 2023-02-12 | 7542 | keep | 0 | Feb | 2023 | 0.0051368 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-02-12 18:41 | 2023-02-12 20:25 | 60 | 1:44 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23021200055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-02-12 | 6240 | keep | 0 | Feb | 2023 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2023-02-12 19:15 | 2023-02-13 08:50 | 1 | 13:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO PRIMARIO DE TRANSFORMADOR | P23021200056 | New_Event | Primary Wire Break | Include | Include | Equipment | 815 | 2023-02-12 | 815 | keep | 0 | Feb | 2023 | 0.00055509 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-12 19:29 | 2023-02-12 19:30 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-12 | 1859 | keep | 0 | Feb | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
HUMACAO | 2023-02-12 20:54 | 2023-02-12 23:51 | 8 | 2:57 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO BAJANTE QUEMADO HACIA CAJA PRIMARIA | C23021200090 | New_Event | Primary Wire Break | Include | Include | Equipment | 177 | 2023-02-12 | 1416 | keep | 0 | Feb | 2023 | 0.00096443 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-02-12 21:08 | 2023-02-13 10:40 | 80 | 13:32 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 Y 1 X 50 EN CORTE DE LINEA DISTINTOS SE RELOCALIZO LINEA SECUNDARIA QUE ESTABA CRUZANDO CON LA LINEA PRIMARIA POR EL VIENTO | A23021200064 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 812 | 2023-02-12 | 64960 | keep | 0 | Feb | 2023 | 0.044244 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-02-12 21:19 | 2023-02-13 06:40 | 2 | 9:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P23021200063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 561 | 2023-02-12 | 1122 | keep | 0 | Feb | 2023 | 0.00076419 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-02-12 23:51 | 2023-02-13 12:55 | 6 | 13:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23021200063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 784 | 2023-02-12 | 4704 | keep | 0 | Feb | 2023 | 0.0032039 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-02-13 00:15 | 2023-02-13 07:38 | 12 | 7:23 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | R23021300003 | New_Event | Animals | Include | Include | Wildlife | 443 | 2023-02-13 | 5316 | keep | 0 | Feb | 2023 | 0.0036207 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-02-13 01:05 | 2023-02-13 08:15 | 281 | 7:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 40 EN C/L | C23021300001 | New_Event | Cutout Failure | Include | Include | Equipment | 430 | 2023-02-13 | 120830 | keep | 0 | Feb | 2023 | 0.082297 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
CANOVANAS | 2023-02-13 03:16 | 2023-02-13 12:39 | 15 | 9:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 DEL SU-7C @ PROVISIONAL AEREO SE REMPLAZO CAJA PRIMARIA | R23021300005 | New_Event | Cutout Failure | Include | Include | Equipment | 563 | 2023-02-13 | 8445 | keep | 0 | Feb | 2023 | 0.0057519 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-02-13 05:49 | 2023-02-13 05:50 | 1862 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23021300007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-13 | 1862 | keep | 0 | Feb | 2023 | 0.0012682 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2023-02-13 05:49 | 2023-02-13 05:50 | 1613 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23021300007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-13 | 1613 | keep | 0 | Feb | 2023 | 0.0010986 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2023-02-13 05:49 | 2023-02-13 05:50 | 1448 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23021300007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-13 | 1448 | keep | 0 | Feb | 2023 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
SAN JUAN | 2023-02-13 05:50 | 2023-02-13 05:51 | 1356 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 1356 | keep | 0 | Feb | 2023 | 0.00092357 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
GUAYAMA | 2023-02-13 06:10 | 2023-02-13 11:03 | 1 | 4:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA RAMA SOBRE LINEA | P23021300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2023-02-13 | 293 | keep | 0 | Feb | 2023 | 0.00019956 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-13 06:21 | 2023-02-13 08:19 | 61 | 1:58 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | R23021300009 | New_Event | Animals | Include | Include | Wildlife | 118 | 2023-02-13 | 7198 | keep | 0 | Feb | 2023 | 0.0049025 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2023-02-13 06:24 | 2023-02-13 09:03 | 60 | 2:39 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23021300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2023-02-13 | 9540 | keep | 0 | Feb | 2023 | 0.0064977 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-02-13 06:33 | 2023-02-13 06:34 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R2302130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 1648 | keep | 0 | Feb | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
BAYAMON | 2023-02-13 06:41 | 2023-02-13 06:42 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 4533 | keep | 0 | Feb | 2023 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
CANOVANAS | 2023-02-13 06:46 | 2023-02-13 08:45 | 1045 | 1:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2,090 DE SUS CLIENTES TRANSFERIDOS AL 2403-02, SE CERRO INTERRUPTOR 2403-02 MANUALMENTE EN LA SUBESTACION Y SE SECCIONALIZARON LOS 1,045 QUE FALTAN DEL 2403-01 POR DISCO PRIMARIO PARTIDO | R23021300013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 119 | 2023-02-13 | 124355 | keep | 0 | Feb | 2023 | 0.084698 | 0.00071174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1045
CANOVANAS | 2023-02-13 06:46 | 2023-02-13 08:45 | 500 | 1:59 | T | ALIMENTADOR AMARRADO | SE CERRO MANUALMENTE INTERRUPTOR EN LA SUBESTACION LLEVA 2,090 CLIENTES DEL 2403-01 DE LOS CUALES SE SECCIONALIZO LA MITAD (1,045) POR DISCO PRIMARIO PARTIDO | R23021300013 | New_Event | Feeder Load Transferred | Include | Include | Other | 119 | 2023-02-13 | 59500 | keep | 0 | Feb | 2023 | 0.040525 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2023-02-13 06:48 | 2023-02-13 06:49 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23021300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 4188 | keep | 0 | Feb | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
ARECIBO | 2023-02-13 07:16 | 2023-02-13 09:20 | 1 | 2:04 | P | OTRAS CAUSAS | 1 X 25 EN MONTURA DE TRANSFORMADORES FUSIBLE CORRIDO | A23021300002 | New_Event | Other Causes | Include | Include | Other | 124 | 2023-02-13 | 124 | keep | 0 | Feb | 2023 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-13 07:28 | 2023-02-13 07:52 | 1 | 0:24 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN C/L SE REMPLAZO PARARRAYO | B23021300008 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 24 | 2023-02-13 | 24 | keep | 0 | Feb | 2023 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-13 07:40 | 2023-02-13 09:55 | 43 | 2:15 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23021300045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-02-13 | 5805 | keep | 0 | Feb | 2023 | 0.0039538 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BARRANQUITAS | 2023-02-13 08:08 | 2023-02-13 08:32 | 10 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23021300011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-02-13 | 240 | keep | 0 | Feb | 2023 | 0.00016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-02-13 08:11 | 2023-02-13 08:50 | 60 | 0:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA @ CAJA NO FUNDIO | R23021300057 | New_Event | Primary Wire Break | Include | Include | Equipment | 39 | 2023-02-13 | 2340 | keep | 0 | Feb | 2023 | 0.0015938 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-13 08:16 | 2023-02-13 08:17 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R2302130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 4981 | keep | 0 | Feb | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
AGUADILLA | 2023-02-13 08:17 | 2023-02-13 14:40 | 1 | 6:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN RISER | A23021300011 | New_Event | Primary Wire Break | Include | Include | Equipment | 383 | 2023-02-13 | 383 | keep | 0 | Feb | 2023 | 0.00026086 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-13 08:29 | 2023-02-13 11:38 | 140 | 3:09 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETEZO LINEA PRIMARIA Y 3 X 80 EN C/L | C23021300012 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 189 | 2023-02-13 | 26460 | keep | 0 | Feb | 2023 | 0.018022 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CANOVANAS | 2023-02-13 08:45 | 2023-02-13 10:26 | 1045 | 1:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO DISCO PRIMARIO PARTIDO (RADIAL) EN SERVICIO TOTAL LOS 1,045 CLIENTES QUE FALTABAN | R23021300013 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 101 | 2023-02-13 | 105545 | keep | 0 | Feb | 2023 | 0.071886 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-13 08:54 | 2023-02-13 11:25 | 4 | 2:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA Y VIENTO EVENTO LO DIERON CON ESA INFORMACION | B23021300014 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 151 | 2023-02-13 | 604 | keep | 0 | Feb | 2023 | 0.00041138 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-13 08:58 | 2023-02-13 14:57 | 1 | 5:59 | P | ANIMAL | 2 X 20 EN BANCO DE XMR CRUCE POR AVE | B23021300015 | New_Event | Animals | Include | Include | Wildlife | 359 | 2023-02-13 | 359 | keep | 0 | Feb | 2023 | 0.00024451 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-13 08:59 | 2023-02-13 09:00 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
CANOVANAS | 2023-02-13 09:03 | 2023-02-13 11:26 | 15 | 2:23 | P | NO SE REPORTO CAUSA | 1 X 25 DEL T-110 @ T-111 | R23021300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2023-02-13 | 2145 | keep | 0 | Feb | 2023 | 0.0014609 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-02-13 09:12 | 2023-02-13 10:35 | 40 | 1:23 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN DISTINTOS CORTES DE LINEA SE REALIZO DESGANCHE MASIVO | A23021300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-02-13 | 3320 | keep | 0 | Feb | 2023 | 0.0022612 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-02-13 09:14 | 2023-02-13 09:51 | 10 | 0:37 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | R23021300086 | New_Event | Animals | Include | Include | Wildlife | 37 | 2023-02-13 | 370 | keep | 0 | Feb | 2023 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-13 09:28 | 2023-02-13 12:18 | 120 | 2:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y 1 X 200 EN C/L | C23021300025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 170 | 2023-02-13 | 20400 | keep | 0 | Feb | 2023 | 0.013894 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2023-02-13 09:30 | 2023-02-13 13:15 | 1 | 3:45 | P | ANIMAL | 1 X 25 EN RISER CRUCE X AVE | C23021300026 | New_Event | Animals | Include | Include | Wildlife | 225 | 2023-02-13 | 225 | keep | 0 | Feb | 2023 | 0.00015325 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-13 09:32 | 2023-02-13 12:00 | 16 | 2:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | C23021300029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 148 | 2023-02-13 | 2368 | keep | 0 | Feb | 2023 | 0.0016128 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-02-13 09:42 | 2023-02-13 12:17 | 6 | 2:35 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | R23021300092 | New_Event | Animals | Include | Include | Wildlife | 155 | 2023-02-13 | 930 | keep | 0 | Feb | 2023 | 0.00063342 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-13 10:02 | 2023-02-13 12:04 | 40 | 2:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 Y 1 X 50 EN C/L SE REMPLAZO AISLADOR ROTO | B23021300025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 122 | 2023-02-13 | 4880 | keep | 0 | Feb | 2023 | 0.0033237 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-02-13 10:42 | 2023-02-13 11:16 | 1 | 0:34 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN RISER SE ELIMINO PARARRAYOS QUEMADO | R23021300102 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 34 | 2023-02-13 | 34 | keep | 0 | Feb | 2023 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-13 10:45 | 2023-02-13 14:10 | 12 | 3:25 | P | DESGANCHE | 1 X 25 EN RISER SE RETIRO RAMAS SOBRE LAS LINEAS | M23021300029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-02-13 | 2460 | keep | 0 | Feb | 2023 | 0.0016755 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-02-13 10:50 | 2023-02-13 12:10 | 8 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A23021300043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-02-13 | 640 | keep | 0 | Feb | 2023 | 0.0004359 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-13 11:12 | 2023-02-13 11:13 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2302130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 45 | keep | 0 | Feb | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-02-13 11:12 | 2023-02-13 17:08 | 1 | 5:56 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN RISER HACIA EL TRANSCLOSURE SE CERRO PUENTE DE LINEA A CAJA | C23021300063 | New_Event | Primary Wire Break | Include | Include | Equipment | 356 | 2023-02-13 | 356 | keep | 0 | Feb | 2023 | 0.00024247 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-13 11:17 | 2023-02-13 18:06 | 1 | 6:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S23021300038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 409 | 2023-02-13 | 409 | keep | 0 | Feb | 2023 | 0.00027857 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-13 11:25 | 2023-02-13 12:55 | 10 | 1:30 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CL PARA REPARAR NEUTRAL PRIMARIO CRUZADO DEBIDO A AVERIA EN CABLE DE COMUNICACION | M23021300017 | New_Event | Primary Wire Break | Include | Include | Equipment | 90 | 2023-02-13 | 900 | keep | 0 | Feb | 2023 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-02-13 11:25 | 2023-02-13 17:15 | 13 | 5:50 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA POR 75 KVA | A23021300054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 350 | 2023-02-13 | 4550 | keep | 0 | Feb | 2023 | 0.003099 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2023-02-13 11:33 | 2023-02-13 15:13 | 50 | 3:40 | P | ANIMAL | 1 X 50 Y 1 X 40 EN RISER CRUCE POR IGUANA | C23021300067 | New_Event | Animals | Include | Include | Wildlife | 220 | 2023-02-13 | 11000 | keep | 0 | Feb | 2023 | 0.007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-02-13 11:40 | 2023-02-13 17:00 | 8 | 5:20 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE SECUNDARIO SE CERRO CAJAS DE TRANSFORMADOR | M23021300035 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 320 | 2023-02-13 | 2560 | keep | 0 | Feb | 2023 | 0.0017436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-02-13 11:44 | 2023-02-13 12:57 | 7 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23021300072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-02-13 | 511 | keep | 0 | Feb | 2023 | 0.00034804 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-02-13 11:48 | 2023-02-13 12:11 | 2 | 0:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIA | B23021300040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 23 | 2023-02-13 | 46 | keep | 0 | Feb | 2023 | 3.133e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-13 11:59 | 2023-02-13 13:20 | 3 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23021300042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2023-02-13 | 243 | keep | 0 | Feb | 2023 | 0.00016551 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-02-13 12:14 | 2023-02-13 12:15 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2302130000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 45 | keep | 0 | Feb | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-02-13 12:15 | 2023-02-13 18:41 | 82 | 6:26 | P | DESGANCHE | 1 X 65 Y 2 X 50 EN C/LS SE REALIZO DESGANCHE Y SE REEMPLAZO CAJA | B23021300044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2023-02-13 | 31652 | keep | 0 | Feb | 2023 | 0.021558 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
ARECIBO | 2023-02-13 12:16 | 2023-02-13 14:40 | 50 | 2:24 | P | CONDUCTOR ARRIADO O CRUZADO | 3 X 50 EN CORTE DE LINEA LINEAS CRUZADAS | A23021300062 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 144 | 2023-02-13 | 7200 | keep | 0 | Feb | 2023 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-02-13 12:18 | 2023-02-13 13:46 | 2 | 1:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA @ CAJA NO FUNDIO | R23021300109 | New_Event | Primary Wire Break | Include | Include | Equipment | 88 | 2023-02-13 | 176 | keep | 0 | Feb | 2023 | 0.00011987 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-02-13 12:21 | 2023-02-13 15:26 | 1 | 3:05 | P | DESGANCHE | 1 X 50 EN C/L | R23021300110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-02-13 | 185 | keep | 0 | Feb | 2023 | 0.000126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-13 12:53 | 2023-02-13 13:32 | 1 | 0:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE ENCONTRO CAUSA | A23021300066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2023-02-13 | 39 | keep | 0 | Feb | 2023 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-13 13:03 | 2023-02-13 16:43 | 81 | 3:40 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B23021300058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-02-13 | 17820 | keep | 0 | Feb | 2023 | 0.012137 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2023-02-13 13:09 | 2023-02-13 16:03 | 2 | 2:54 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B23021300059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2023-02-13 | 348 | keep | 0 | Feb | 2023 | 0.00023702 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-02-13 13:10 | 2023-02-13 15:35 | 6 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | M23020600059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-02-13 | 870 | keep | 0 | Feb | 2023 | 0.00059255 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-02-13 13:15 | 2023-02-13 14:25 | 40 | 1:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23021300068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-02-13 | 2800 | keep | 0 | Feb | 2023 | 0.0019071 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-13 13:21 | 2023-02-13 15:16 | 11 | 1:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO CARGA X 1106-05 | S23021300048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 115 | 2023-02-13 | 1265 | keep | 0 | Feb | 2023 | 0.00086159 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-02-13 13:37 | 2023-02-13 16:03 | 488 | 2:26 | P | CAUSAS EXTERNAS | 1 X 80 EN CORTE DE LINEA SE SECCIONALIZO ALAMBRE PRIMARIO EN EL SUELO IMPACTADO POR DEEGER | C23021300087 | New_Event | Damage From Public | Include | Include | Public | 146 | 2023-02-13 | 71248 | keep | 0 | Feb | 2023 | 0.048527 | 0.00033237 | Sustained | FALSE | FALSE | Not_TMED_Event | 488
CANOVANAS | 2023-02-13 13:56 | 2023-02-13 15:29 | 99 | 1:33 | P | DESGANCHE | 1 X 65 EN C/L | R23021300116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-02-13 | 9207 | keep | 0 | Feb | 2023 | 0.0062708 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
BAYAMON | 2023-02-13 14:07 | 2023-02-13 17:50 | 132 | 3:43 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN C/L SE RETEZO LINEA PRIMARIA | B23021300067 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 223 | 2023-02-13 | 29436 | keep | 0 | Feb | 2023 | 0.020049 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
FAJARDO | 2023-02-13 14:13 | 2023-02-13 14:32 | 22 | 0:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R23021300117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-02-13 | 418 | keep | 0 | Feb | 2023 | 0.0002847 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-02-13 14:23 | 2023-02-13 17:23 | 1 | 3:00 | P | DESGANCHE | 1 X 50 Y DESGANCHE | S23021300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-02-13 | 180 | keep | 0 | Feb | 2023 | 0.0001226 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-13 14:25 | 2023-02-13 17:26 | 30 | 3:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P23021300072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-02-13 | 5430 | keep | 0 | Feb | 2023 | 0.0036983 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-02-13 14:50 | 2023-02-13 15:05 | 10 | 0:15 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS CRUZADAS | M23021200032 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 15 | 2023-02-13 | 150 | keep | 0 | Feb | 2023 | 0.00010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-13 14:59 | 2023-02-13 17:25 | 54 | 2:26 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C23021300123 | New_Event | Animals | Include | Include | Wildlife | 146 | 2023-02-13 | 7884 | keep | 0 | Feb | 2023 | 0.0053698 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
VEGA BAJA | 2023-02-13 15:05 | 2023-02-13 17:00 | 6 | 1:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REPARAR BARRAS SECUNDARIAS | A23021300082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 115 | 2023-02-13 | 690 | keep | 0 | Feb | 2023 | 0.00046996 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-13 15:29 | 2023-02-13 18:35 | 80 | 3:06 | P | DESGANCHE | 1 X 100 C/L DESGANCHE | S23021300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-02-13 | 14880 | keep | 0 | Feb | 2023 | 0.010135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-13 16:00 | 2023-02-13 17:38 | 1 | 1:38 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B23021300088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2023-02-13 | 98 | keep | 0 | Feb | 2023 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-13 16:03 | 2023-02-13 22:38 | 10 | 6:35 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE IMPACTADO POR CAMION PRIVADO | C23021300087 | Partial_restoration | Damage From Public | Include | Include | Public | 395 | 2023-02-13 | 3950 | keep | 0 | Feb | 2023 | 0.0026903 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-13 16:07 | 2023-02-13 17:20 | 15 | 1:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA Y 2 X 50 EN RISER MAL TIEMPO VIENTOS FUERTES | M23021300066 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 73 | 2023-02-13 | 1095 | keep | 0 | Feb | 2023 | 0.0007458 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-02-13 16:20 | 2023-02-13 16:35 | 18 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23021300002 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-02-13 | 270 | keep | 0 | Feb | 2023 | 0.0001839 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2023-02-13 16:41 | 2023-02-13 18:11 | 25 | 1:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P23021300091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-02-13 | 2250 | keep | 0 | Feb | 2023 | 0.0015325 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-02-13 17:00 | 2023-02-13 17:37 | 10 | 0:37 | P | DESGANCHE | SE CERRO TRANSFORMADOR POR DESGANCHE | P23021300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2023-02-13 | 370 | keep | 0 | Feb | 2023 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-02-13 17:16 | 2023-02-13 18:39 | 35 | 1:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23021300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-02-13 | 2905 | keep | 0 | Feb | 2023 | 0.0019786 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2023-02-13 17:44 | 2023-02-13 17:45 | 752 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23021300102 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-13 | 752 | keep | 0 | Feb | 2023 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2023-02-13 17:44 | 2023-02-13 17:45 | 2696 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO LLEVA LA CARGA DEL 5011-04 | P23021300102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 2696 | keep | 0 | Feb | 2023 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
SAN JUAN | 2023-02-13 17:50 | 2023-02-13 17:51 | 178 | 0:01 | T | NO SE REPORTO CAUSA | CERRADO POR CONTROL LLEVA 1912-10 | S2302130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 178 | keep | 0 | Feb | 2023 | 0.00012123 | 0.00012123 | Momentary | FALSE | FALSE | Not_TMED_Event | 178
BAYAMON | 2023-02-13 17:50 | 2023-02-13 17:51 | 23 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1529-13 CERRRADO POR CONTROL CARGA X 1529-13 | S2302130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-13 | 23 | keep | 0 | Feb | 2023 | 1.5665e-05 | 1.5665e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 23
YAUCO | 2023-02-13 19:05 | 2023-02-14 08:12 | 28 | 13:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23021300111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 787 | 2023-02-13 | 22036 | keep | 0 | Feb | 2023 | 0.015009 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
MAYAGÃœEZ | 2023-02-13 19:54 | 2023-02-15 11:30 | 1 | 39:36 | P | NO SE REPORTO CAUSA | 3 X 20 EN CL NO SE ENCONTRO CAUSA | M23021300080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2376 | 2023-02-13 | 2376 | keep | 0 | Feb | 2023 | 0.0016183 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-13 22:03 | 2023-02-14 01:15 | 12 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | FIJO NEUTRAL PRIMARIO A TIERRA REMPLAZO BAJANTE SECUNDARIO NO FUNDIO | B23021300101 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2023-02-13 | 2304 | keep | 0 | Feb | 2023 | 0.0015692 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-02-13 22:13 | 2023-02-13 22:14 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-13 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2023-02-13 22:49 | 2023-02-14 14:33 | 121 | 15:44 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU-5, AVERIA NUEVA DE T-44 @ T-45 Y AVERIA VIEJA DE T-49 @ SU-16, 5 XMRS FUERA | S23021300081 | New_Event | UG Cable Fault | Include | Include | Equipment | 944 | 2023-02-13 | 114224 | keep | 0 | Feb | 2023 | 0.077797 | 8.2413e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 121
CAGUAS | 2023-02-13 22:56 | 2023-02-14 07:25 | 112 | 8:29 | P | ANIMAL | 1 X 65 C/L CRUCE X AVE | C23021300156 | New_Event | Animals | Include | Include | Wildlife | 509 | 2023-02-13 | 57008 | keep | 0 | Feb | 2023 | 0.038828 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
VEGA BAJA | 2023-02-14 02:18 | 2023-02-14 09:55 | 318 | 7:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CL | A23021400005 | New_Event | Primary Wire Break | Include | Include | Equipment | 457 | 2023-02-14 | 145326 | keep | 0 | Feb | 2023 | 0.098981 | 0.00021659 | Sustained | FALSE | FALSE | Not_TMED_Event | 318
CANOVANAS | 2023-02-14 02:20 | 2023-02-14 10:14 | 160 | 7:54 | P | DESGANCHE | 1 X 65 EN C/L | R23021400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 474 | 2023-02-14 | 75840 | keep | 0 | Feb | 2023 | 0.051654 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
MAYAGÃœEZ | 2023-02-14 04:10 | 2023-02-14 05:35 | 25 | 1:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR VIENTOS | M23021400003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 85 | 2023-02-14 | 2125 | keep | 0 | Feb | 2023 | 0.0014473 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-02-14 05:57 | 2023-02-14 10:33 | 13 | 4:36 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23021400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2023-02-14 | 3588 | keep | 0 | Feb | 2023 | 0.0024438 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2023-02-14 06:05 | 2023-02-14 12:40 | 8 | 6:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | A23021400026 | New_Event | Cutout Failure | Include | Include | Equipment | 395 | 2023-02-14 | 3160 | keep | 0 | Feb | 2023 | 0.0021523 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-02-14 06:27 | 2023-02-14 07:50 | 7 | 1:23 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR RETIRO ENREDADERA DEL XMR | C23021400007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 83 | 2023-02-14 | 581 | keep | 0 | Feb | 2023 | 0.00039572 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-02-14 06:41 | 2023-02-14 09:40 | 80 | 2:59 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRON CAUSA | M23021400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2023-02-14 | 14320 | keep | 0 | Feb | 2023 | 0.0097533 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-02-14 06:42 | 2023-02-14 12:18 | 116 | 5:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | S23021400002 | New_Event | Cutout Failure | Include | Include | Equipment | 336 | 2023-02-14 | 38976 | keep | 0 | Feb | 2023 | 0.026546 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
CANOVANAS | 2023-02-14 06:55 | 2023-02-14 08:35 | 252 | 1:40 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 40 C/L CRUCE X AVE | R23021400010 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-02-14 | 25200 | keep | 0 | Feb | 2023 | 0.017164 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
MAYAGÃœEZ | 2023-02-14 07:18 | 2023-02-14 09:30 | 50 | 2:12 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M23021400008 | New_Event | Animals | Include | Include | Wildlife | 132 | 2023-02-14 | 6600 | keep | 0 | Feb | 2023 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-02-14 07:30 | 2023-02-14 10:25 | 2 | 2:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L Y 1 X 25 EN C/L SE REMPLAZO PORTAFUSIBLE | R23021400015 | New_Event | Cutout Failure | Include | Include | Equipment | 175 | 2023-02-14 | 350 | keep | 0 | Feb | 2023 | 0.00023838 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-02-14 07:32 | 2023-02-14 11:08 | 1 | 3:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P23021400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2023-02-14 | 216 | keep | 0 | Feb | 2023 | 0.00014712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-14 07:34 | 2023-02-14 10:00 | 8 | 2:26 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C23021400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2023-02-14 | 1168 | keep | 0 | Feb | 2023 | 0.00079552 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-14 07:57 | 2023-02-14 11:39 | 75 | 3:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X40 EN PROVISIONAL AEREO SE REMPLAZO PORTAFUSIBLE | B23021400004 | New_Event | Cutout Failure | Include | Include | Equipment | 222 | 2023-02-14 | 16650 | keep | 0 | Feb | 2023 | 0.01134 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-02-14 08:45 | 2023-02-14 11:20 | 282 | 2:35 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | C23021400028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-02-14 | 43710 | keep | 0 | Feb | 2023 | 0.029771 | 0.00019207 | Sustained | FALSE | FALSE | Not_TMED_Event | 282
HUMACAO | 2023-02-14 08:46 | 2023-02-14 11:10 | 1 | 2:24 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPLAZO UN SMU-20 DE 20 AMP EN TRANCLUSURE CONTAMINACION EN SU | C23021400029 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 144 | 2023-02-14 | 144 | keep | 0 | Feb | 2023 | 9.8078e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-14 08:52 | 2023-02-14 12:35 | 43 | 3:43 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | C23021400030 | New_Event | Animals | Include | Include | Wildlife | 223 | 2023-02-14 | 9589 | keep | 0 | Feb | 2023 | 0.006531 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
GUAYAMA | 2023-02-14 08:52 | 2023-02-14 11:47 | 7 | 2:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPRO CONEXION PRIMARIA DE THREE WIRE | P23021400015 | New_Event | Primary Wire Break | Include | Include | Equipment | 175 | 2023-02-14 | 1225 | keep | 0 | Feb | 2023 | 0.00083434 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-02-14 08:57 | 2023-02-14 10:14 | 80 | 1:17 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CL SE FIJO BANTE DE LINEA PRIMARIO | B23021400009 | New_Event | Primary Wire Break | Include | Include | Equipment | 77 | 2023-02-14 | 6160 | keep | 0 | Feb | 2023 | 0.0041955 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-02-14 09:05 | 2023-02-14 11:33 | 8 | 2:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO SECUNDARIA | R23021400026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 148 | 2023-02-14 | 1184 | keep | 0 | Feb | 2023 | 0.00080642 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-14 09:10 | 2023-02-14 09:11 | 390 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23021400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-14 | 390 | keep | 0 | Feb | 2023 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2023-02-14 09:21 | 2023-02-14 18:46 | 1 | 9:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN RISER Y SE REMPLAZO CAJA PRIMARIA | S23021400011 | New_Event | Cutout Failure | Include | Include | Equipment | 565 | 2023-02-14 | 565 | keep | 0 | Feb | 2023 | 0.00038482 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-14 09:24 | 2023-02-14 09:25 | 2891 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | R23021400027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-14 | 2891 | keep | 0 | Feb | 2023 | 0.001969 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
MAYAGÃœEZ | 2023-02-14 09:35 | 2023-02-14 12:00 | 5 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23021400031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-02-14 | 725 | keep | 0 | Feb | 2023 | 0.00049379 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-02-14 09:41 | 2023-02-14 11:15 | 1 | 1:34 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23021400035 | New_Event | Animals | Include | Include | Wildlife | 94 | 2023-02-14 | 94 | keep | 0 | Feb | 2023 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-14 09:45 | 2023-02-14 11:02 | 9 | 1:17 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | R23021400028 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-02-14 | 693 | keep | 0 | Feb | 2023 | 0.000472 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-02-14 09:46 | 2023-02-14 09:47 | 3012 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | R2302140000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-14 | 3012 | keep | 0 | Feb | 2023 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2023-02-14 09:47 | 2023-02-14 12:14 | 31 | 2:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L Y 1 X 20 EN C/L Y SE REMPLAZO CAJA PRIMARIA | R23021400031 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 147 | 2023-02-14 | 4557 | keep | 0 | Feb | 2023 | 0.0031038 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
VEGA BAJA | 2023-02-14 09:55 | 2023-02-14 09:56 | 2107 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23021400072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-14 | 2107 | keep | 0 | Feb | 2023 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
CANOVANAS | 2023-02-14 09:56 | 2023-02-14 12:44 | 3 | 2:48 | P | NO SE REPORTO CAUSA | 3 X 50 EN CORTE DE LINEA Y 3 X 40 EN RISER EVENTO TRANSFERIDO DE ARECIBO | A23021400071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2023-02-14 | 504 | keep | 0 | Feb | 2023 | 0.00034327 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-02-14 09:58 | 2023-02-14 12:40 | 7 | 2:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23021300151 | New_Event | Secondary Wire Break | Include | Include | Equipment | 162 | 2023-02-14 | 1134 | keep | 0 | Feb | 2023 | 0.00077236 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-02-14 10:20 | 2023-02-14 12:29 | 25 | 2:09 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | R23021400030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2023-02-14 | 3225 | keep | 0 | Feb | 2023 | 0.0021965 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-14 10:30 | 2023-02-14 17:27 | 13 | 6:57 | P | TERMINACION SOTERRADA AVERIADA | SE REMPLAZARON TERMINACIONES EN CABLE DE RISER DE SALIDA DEL INTERRUPTOR MEDIANTE G.O.I. BY-220915-02 | B23021400066 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 417 | 2023-02-14 | 5421 | keep | 0 | Feb | 2023 | 0.0036922 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-02-14 10:31 | 2023-02-14 11:28 | 6 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LE REPARO LA SECUNDARIA @ LA SALIDA DEL XMR | B23021400022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-02-14 | 342 | keep | 0 | Feb | 2023 | 0.00023293 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-14 10:45 | 2023-02-14 15:30 | 35 | 4:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO DE METAL DE 40' NO FUNDIO | B23021400023 | New_Event | Primary Pole Failure | Include | Include | Equipment | 285 | 2023-02-14 | 9975 | keep | 0 | Feb | 2023 | 0.0067939 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-02-14 10:55 | 2023-02-14 18:23 | 63 | 7:28 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23021400057 | New_Event | Animals | Include | Include | Wildlife | 448 | 2023-02-14 | 28224 | keep | 0 | Feb | 2023 | 0.019223 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
YAUCO | 2023-02-14 10:55 | 2023-02-14 16:36 | 16 | 5:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO | P23021400029 | New_Event | Primary Wire Break | Include | Include | Equipment | 341 | 2023-02-14 | 5456 | keep | 0 | Feb | 2023 | 0.0037161 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2023-02-14 11:13 | 2023-02-14 14:40 | 1 | 3:27 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE NO FUNDIO | C23021400060 | New_Event | Primary Wire Break | Include | Include | Equipment | 207 | 2023-02-14 | 207 | keep | 0 | Feb | 2023 | 0.00014099 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-14 11:16 | 2023-02-14 11:24 | 11 | 0:08 | P | TERMINACION SOTERRADA AVERIADA | ABRIR TRANSFORMADOR PARA LIMPIAR BUSHING CAP Y TAPARLO YA QUE ESTA EXPUESTO | P23021400036 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 8 | 2023-02-14 | 88 | keep | 0 | Feb | 2023 | 5.9936e-05 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2023-02-14 11:55 | 2023-02-14 14:30 | 2340 | 2:35 | T | CAUSAS EXTERNAS | SE ELIMINO TRAMO DE LINEA FUERA DE SERVICIO MAQUINA DE MUNICIPIO PARTIO POSTE | P23021400042 | New_Event | Damage From Public | Include | Include | Public | 155 | 2023-02-14 | 362700 | keep | 0 | Feb | 2023 | 0.24703 | 0.0015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 2340
VEGA BAJA | 2023-02-14 11:55 | 2023-02-14 15:40 | 25 | 3:45 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A23021400099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2023-02-14 | 5625 | keep | 0 | Feb | 2023 | 0.0038312 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-02-14 12:16 | 2023-02-14 13:57 | 13 | 1:41 | P | DESGANCHE | 1 X 20 Y 1 X 30 EN CORTES DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23021400071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-02-14 | 1313 | keep | 0 | Feb | 2023 | 0.00089428 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2023-02-14 12:35 | 2023-02-14 12:45 | 35 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23021300038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-02-14 | 350 | keep | 0 | Feb | 2023 | 0.00023838 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-02-14 12:37 | 2023-02-14 17:44 | 10 | 5:07 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | B23021400039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 307 | 2023-02-14 | 3070 | keep | 0 | Feb | 2023 | 0.002091 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-14 12:47 | 2023-02-14 15:57 | 90 | 3:10 | P | DESGANCHE | SJ-230214-02 SE REALIZO DESGANCHE | S23021400041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-02-14 | 17100 | keep | 0 | Feb | 2023 | 0.011647 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2023-02-14 12:47 | 2023-02-14 14:44 | 40 | 1:57 | P | PROBLEMA DEL CLIENTE | 1 X 30 EN RISER PROA | C23021400076 | New_Event | Customer-Related Interruption | Include | Include | Public | 117 | 2023-02-14 | 4680 | keep | 0 | Feb | 2023 | 0.0031875 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-14 12:52 | 2023-02-14 14:03 | 1 | 1:11 | P | ANIMAL | 1X20 DEL SU-1 @ RISER CRUCE POR IGUANA | B23021400040 | New_Event | Animals | Include | Include | Wildlife | 71 | 2023-02-14 | 71 | keep | 0 | Feb | 2023 | 4.8358e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-14 13:00 | 2023-02-14 14:41 | 1 | 1:41 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN XMR SE FIJO BAJANTE PRIMARIO EN MONTURA | P23021400059 | New_Event | Primary Wire Break | Include | Include | Equipment | 101 | 2023-02-14 | 101 | keep | 0 | Feb | 2023 | 6.8791e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-14 13:02 | 2023-02-14 16:33 | 2 | 3:31 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23021400078 | New_Event | Animals | Include | Include | Wildlife | 211 | 2023-02-14 | 422 | keep | 0 | Feb | 2023 | 0.00028742 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-14 13:02 | 2023-02-14 14:53 | 1 | 1:51 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | B23021400042 | New_Event | Primary Wire Break | Include | Include | Equipment | 111 | 2023-02-14 | 111 | keep | 0 | Feb | 2023 | 7.5602e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-14 13:12 | 2023-02-14 17:49 | 6 | 4:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 3 CAJAS PRIMARIAS Y 3 PARARRAYO | S23021400075 | New_Event | Cutout Failure | Include | Include | Equipment | 277 | 2023-02-14 | 1662 | keep | 0 | Feb | 2023 | 0.001132 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-02-14 13:14 | 2023-02-14 15:03 | 2 | 1:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARARA NEUTRAL SECUNDARIO | R23021400038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 109 | 2023-02-14 | 218 | keep | 0 | Feb | 2023 | 0.00014848 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-02-14 13:20 | 2023-02-14 14:10 | 4 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REMPLAZO DE BARRAS EN PEDESTAL SECUNDARIO | A23012300126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-02-14 | 200 | keep | 0 | Feb | 2023 | 0.00013622 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-02-14 13:30 | 2023-02-14 13:31 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23021400089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-14 | 3718 | keep | 0 | Feb | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2023-02-14 13:33 | 2023-02-14 17:33 | 10 | 4:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23021400090 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 240 | 2023-02-14 | 2400 | keep | 0 | Feb | 2023 | 0.0016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-14 13:38 | 2023-02-14 14:32 | 8 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO TRAMO APROX. 100' SECUNDARIA CALIBRE # 3/2 - AL | B23021400050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2023-02-14 | 432 | keep | 0 | Feb | 2023 | 0.00029423 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-14 13:45 | 2023-02-14 17:19 | 40 | 3:34 | P | ANIMAL | 1X30 DE PROVISIONAL AEREO @ T-44 CRUCE POR AVE | B23021400051 | New_Event | Animals | Include | Include | Wildlife | 214 | 2023-02-14 | 8560 | keep | 0 | Feb | 2023 | 0.0058302 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-14 13:49 | 2023-02-14 15:01 | 206 | 1:12 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR 1424-08 QUE LLEVA 80% DEL 1348-06 POR EMERGENCIA 15:01 @ 1517 S23021400171 | S23021400102 | New_Event | Primary Wire Break | Include | Include | Equipment | 72 | 2023-02-14 | 14832 | keep | 0 | Feb | 2023 | 0.010102 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
SAN JUAN | 2023-02-14 14:10 | 2023-02-14 16:54 | 60 | 2:44 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23021400121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2023-02-14 | 9840 | keep | 0 | Feb | 2023 | 0.006702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-02-14 14:23 | 2023-02-14 15:59 | 1 | 1:36 | P | PROBLEMA DEL CLIENTE | 1 X 30 EN RISER Y 1 X 50 EN C/L PROA | R23021400043 | New_Event | Customer-Related Interruption | Include | Include | Public | 96 | 2023-02-14 | 96 | keep | 0 | Feb | 2023 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-14 14:33 | 2023-02-15 16:38 | 40 | 26:05 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA SOTERRADA DEL T-44 @ T-45 | S23021400081 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1565 | 2023-02-14 | 62600 | keep | 0 | Feb | 2023 | 0.042637 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-14 14:43 | 2023-02-14 16:15 | 7 | 1:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23021400096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2023-02-14 | 644 | keep | 0 | Feb | 2023 | 0.00043863 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-02-14 14:43 | 2023-02-14 15:55 | 25 | 1:12 | P | CAUSAS EXTERNAS | 1 X 50 EN CL VEHICULO IMPACTA POSTE Y CREA CRUCE CON TENSOR | A23021400130 | New_Event | Damage From Public | Include | Include | Public | 72 | 2023-02-14 | 1800 | keep | 0 | Feb | 2023 | 0.001226 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-02-14 14:52 | 2023-02-14 19:55 | 1 | 5:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN RISER MAL TIEMPO LLUVIA | C23021400098 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 303 | 2023-02-14 | 303 | keep | 0 | Feb | 2023 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-14 15:01 | 2023-02-14 15:17 | 1058 | 0:16 | P | ALIMENTADOR AMARRADO | SE ABRIO BKR POR EMERGENCIA 1424-08 CERRADO POR CONTROL A PETICION DE ELVIN MORALES POR CONDUCTOR PARTIDO CRUZANDO FASES LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400171 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-02-14 | 16928 | keep | 0 | Feb | 2023 | 0.01153 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-02-14 15:01 | 2023-02-14 15:07 | 1000 | 0:06 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR POR EMERGENCIA 1424-08 CERRADO POR CONTROL A PETICION DE ELVIN MORALES POR CONDUCTOR PARTIDO CRUZANDO FASES LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400171 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 6 | 2023-02-14 | 6000 | keep | 0 | Feb | 2023 | 0.0040866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-14 15:01 | 2023-02-14 15:17 | 278 | 0:16 | T | ALIMENTADOR AMARRADO | SE ABRIO BKR POR EMERGENCIA 1424-08 CERRADO POR CONTROL A PETICION DE ELVIN MORALES POR CONDUCTOR PARTIDO CRUZANDO FASES LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400171 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-02-14 | 4448 | keep | 0 | Feb | 2023 | 0.0030295 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-02-14 15:01 | 2023-02-14 15:17 | 1295 | 0:16 | T | ALIMENTADOR AMARRADO | SE ABRIO BKR POR EMERGENCIA 1424-08 CERRADO POR CONTROL A PETICION DE ELVIN MORALES POR CONDUCTOR PARTIDO CRUZANDO FASES LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400171 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-02-14 | 20720 | keep | 0 | Feb | 2023 | 0.014112 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-02-14 15:01 | 2023-02-14 15:17 | 9 | 0:16 | T | ALIMENTADOR AMARRADO | SE ABRIO BKR POR EMERGENCIA 1424-08 CERRADO POR CONTROL A PETICION DE ELVIN MORALES POR CONDUCTOR PARTIDO CRUZANDO FASES LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400171 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-02-14 | 144 | keep | 0 | Feb | 2023 | 9.8078e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-02-14 15:14 | 2023-02-14 17:48 | 7 | 2:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON BARRAS EN PEDESTAL RECTANGULAR | B23021400061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 154 | 2023-02-14 | 1078 | keep | 0 | Feb | 2023 | 0.00073422 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-02-14 15:17 | 2023-02-14 15:34 | 206 | 0:17 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 SE REMPLAZO JUMPER PRIMARIO DE LINEA A CAJA | S23021400102 | New_Event | Primary Wire Break | Include | Include | Equipment | 17 | 2023-02-14 | 3502 | keep | 0 | Feb | 2023 | 0.0023852 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
GUAYAMA | 2023-02-14 15:30 | 2023-02-14 16:40 | 25 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23021400077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-02-14 | 1750 | keep | 0 | Feb | 2023 | 0.0011919 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-14 15:34 | 2023-02-14 15:36 | 1058 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 1424-08 CERRADO POR CONTROL (NO SE REPORTO CAUSA) LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400215 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-14 | 2116 | keep | 0 | Feb | 2023 | 0.0014412 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-14 15:34 | 2023-02-14 15:36 | 1000 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 1424-08 CERRADO POR CONTROL (NO SE REPORTO CAUSA) LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400215 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-14 | 2000 | keep | 0 | Feb | 2023 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-02-14 15:34 | 2023-02-14 15:36 | 278 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO 1424-08 CERRADO POR CONTROL (NO SE REPORTO CAUSA) LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400215 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-14 | 556 | keep | 0 | Feb | 2023 | 0.00037869 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-14 15:34 | 2023-02-14 15:36 | 1295 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO 1424-08 CERRADO POR CONTROL (NO SE REPORTO CAUSA) LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400215 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-14 | 2590 | keep | 0 | Feb | 2023 | 0.001764 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-14 15:34 | 2023-02-14 15:36 | 9 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL ( NO SE REPORTO CAUSA) LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 | S23021400215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-14 | 18 | keep | 0 | Feb | 2023 | 1.226e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-02-14 15:36 | 2023-02-14 16:51 | 206 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 SE REMPLAZO JUMPER PRIMARIO DE LINEA A CAJA | S23021400102 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 75 | 2023-02-14 | 15450 | keep | 0 | Feb | 2023 | 0.010523 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-02-14 15:42 | 2023-02-14 18:11 | 1 | 2:29 | P | ANIMAL | 1 X 15 EN XMR AVE CRUZO LINEAS | P23021400078 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-02-14 | 149 | keep | 0 | Feb | 2023 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-14 15:46 | 2023-02-14 20:08 | 6 | 4:22 | P | TRANSFORMADOR AVERIADO | XMR AVERIADO SE ENERGIZO DE OTRO XMR | P23021400080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 262 | 2023-02-14 | 1572 | keep | 0 | Feb | 2023 | 0.0010707 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-02-14 15:53 | 2023-02-14 18:39 | 1 | 2:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN MONTURA | P23021400082 | New_Event | Primary Wire Break | Include | Include | Equipment | 166 | 2023-02-14 | 166 | keep | 0 | Feb | 2023 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-14 15:56 | 2023-02-14 18:50 | 30 | 2:54 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN BOOSTER SE REPARO LINEA PRIMARIA | M23021400074 | New_Event | Primary Wire Break | Include | Include | Equipment | 174 | 2023-02-14 | 5220 | keep | 0 | Feb | 2023 | 0.0035553 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-14 15:57 | 2023-02-14 16:05 | 2435 | 0:08 | T | DESGANCHE | DISPARO CERRADO POR CONTROL RELACIONADO A SJ-230214-02 | S23021400041 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 8 | 2023-02-14 | 19480 | keep | 0 | Feb | 2023 | 0.013268 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-14 16:05 | 2023-02-14 18:13 | 90 | 2:08 | P | DESGANCHE | SJ-230214-02 SE REALIZO DESGANCHE | S23021400041 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-02-14 | 11520 | keep | 0 | Feb | 2023 | 0.0078462 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-02-14 16:10 | 2023-02-14 16:50 | 1 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23021400067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-02-14 | 40 | keep | 0 | Feb | 2023 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-14 16:22 | 2023-02-14 18:00 | 10 | 1:38 | P | DESGANCHE | 1 X 100 C/L DESGANCHE | S23021400281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-02-14 | 980 | keep | 0 | Feb | 2023 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-14 16:26 | 2023-02-14 18:22 | 414 | 1:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA 1 X 100 EN C/L | C23021400119 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2023-02-14 | 48024 | keep | 0 | Feb | 2023 | 0.032709 | 0.00028197 | Sustained | FALSE | FALSE | Not_TMED_Event | 414
CAGUAS | 2023-02-14 16:26 | 2023-02-14 18:22 | 207 | 1:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA AVERIADA | C23021400119 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2023-02-14 | 24012 | keep | 0 | Feb | 2023 | 0.016354 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2023-02-14 16:28 | 2023-02-14 17:16 | 10 | 0:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIA | S23021400288 | New_Event | Cutout Failure | Include | Include | Equipment | 48 | 2023-02-14 | 480 | keep | 0 | Feb | 2023 | 0.00032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-14 16:33 | 2023-02-14 16:44 | 189 | 0:11 | P | CAUSAS EXTERNAS | 3 X 65 EN C/L SE SECCIONALIZO POSTE PRIMARIO IMPACTADO X CAMION QUEDAN 30 CLIENTES FUERA | C23021400095 | New_Event | Damage From Public | Include | Include | Public | 11 | 2023-02-14 | 2079 | keep | 0 | Feb | 2023 | 0.001416 | 0.00012873 | Sustained | FALSE | FALSE | Not_TMED_Event | 189
CAGUAS | 2023-02-14 16:44 | 2023-02-15 03:16 | 30 | 10:32 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 3 X 65 EN C/L SE REMPLAZO POSTE PRIMARIO PARTIDO | C23021400095 | New_Event | Primary Pole Failure | Include | Include | Equipment | 632 | 2023-02-14 | 18960 | keep | 0 | Feb | 2023 | 0.012914 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-02-14 17:07 | 2023-02-14 19:55 | 7 | 2:48 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23021400124 | New_Event | Animals | Include | Include | Wildlife | 168 | 2023-02-14 | 1176 | keep | 0 | Feb | 2023 | 0.00080097 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-02-14 17:32 | 2023-02-14 17:48 | 1 | 0:16 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO SE ENCONTRO CAUSA | C23021400116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-02-14 | 16 | keep | 0 | Feb | 2023 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-14 17:50 | 2023-02-14 21:08 | 15 | 3:18 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE | P23021400095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2023-02-14 | 2970 | keep | 0 | Feb | 2023 | 0.0020229 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-02-14 17:52 | 2023-02-15 11:47 | 32 | 17:55 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23021400129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1075 | 2023-02-14 | 34400 | keep | 0 | Feb | 2023 | 0.02343 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BARRANQUITAS | 2023-02-14 18:46 | 2023-02-15 09:17 | 4 | 14:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR Y SE RETIRO ENREDADERA | C23021400137 | New_Event | Cutout Failure | Include | Include | Equipment | 871 | 2023-02-14 | 3484 | keep | 0 | Feb | 2023 | 0.0023729 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-02-14 19:04 | 2023-02-14 22:27 | 100 | 3:23 | P | ANIMAL | 1 X 40 Y 1 X 50 EN CORTE DE LINEA POR AVES | M23021400090 | New_Event | Animals | Include | Include | Wildlife | 203 | 2023-02-14 | 20300 | keep | 0 | Feb | 2023 | 0.013826 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-02-14 19:30 | 2023-02-15 17:40 | 70 | 22:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23021400157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1330 | 2023-02-14 | 93100 | keep | 0 | Feb | 2023 | 0.06341 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-02-14 19:37 | 2023-02-14 20:55 | 120 | 1:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021400094 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 78 | 2023-02-14 | 9360 | keep | 0 | Feb | 2023 | 0.0063751 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2023-02-14 19:44 | 2023-02-14 21:35 | 20 | 1:51 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR Y 1 X 40 EN CL IGUANA | A23021400160 | New_Event | Animals | Include | Include | Wildlife | 111 | 2023-02-14 | 2220 | keep | 0 | Feb | 2023 | 0.001512 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-02-14 20:52 | 2023-02-15 00:56 | 100 | 4:04 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA POR RAYOS | A23021400169 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 244 | 2023-02-14 | 24400 | keep | 0 | Feb | 2023 | 0.016619 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-02-14 21:24 | 2023-02-14 23:19 | 14 | 1:55 | P | CAUSAS EXTERNAS | 1 X 15 EN TRANSFORMADOR SE REPARARON TOMAS DERRIBADAS POR CAMION | B23021400080 | New_Event | Damage From Public | Include | Include | Public | 115 | 2023-02-14 | 1610 | keep | 0 | Feb | 2023 | 0.0010966 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2023-02-14 22:14 | 2023-02-15 01:02 | 457 | 2:48 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE NO FUNDIO | C23021400146 | New_Event | Primary Wire Break | Include | Include | Equipment | 168 | 2023-02-14 | 76776 | keep | 0 | Feb | 2023 | 0.052292 | 0.00031126 | Sustained | FALSE | FALSE | Not_TMED_Event | 457
SAN JUAN | 2023-02-14 22:43 | 2023-02-15 00:52 | 737 | 2:09 | P | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SECUNDARIO DE LA PORTATIL #19 SE INSPECCIONO BARRA Y SE CERRO LOCALMENTE (PARTE DE LA CARGA POR EL 1529-15) EN PATRULLAJE SE ENCONTRO PARARRAYOS AVERIADO | S23021400403 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 129 | 2023-02-14 | 95073 | keep | 0 | Feb | 2023 | 0.064754 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2023-02-14 22:43 | 2023-02-15 00:52 | 2422 | 2:09 | S | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SECUNDARIO DE LA PORTATIL #19 SE INSPECCIONO BARRA Y SE CERRO LOCALMENTE EN PATRULLAJE SE ENCONTRO PARARRAYOS AVERIADO | S23021400403 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 129 | 2023-02-14 | 312438 | keep | 0 | Feb | 2023 | 0.2128 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
VEGA BAJA | 2023-02-14 23:00 | 2023-02-15 | 80 | 1:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B23021400083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-02-14 | 4800 | keep | 0 | Feb | 2023 | 0.0032693 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-02-15 03:09 | 2023-02-15 13:00 | 60 | 9:51 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 3 X 65 EN CORTE DE LINEA REMPLAZO DE POSTE PRIMARIO PARTIDO | A23021500001 | New_Event | Primary Pole Failure | Include | Include | Equipment | 591 | 2023-02-15 | 35460 | keep | 0 | Feb | 2023 | 0.024152 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-02-15 03:16 | 2023-02-15 03:17 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2302150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 6197 | keep | 0 | Feb | 2023 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
SAN JUAN | 2023-02-15 03:58 | 2023-02-15 05:09 | 2040 | 1:11 | T | NO SE REPORTO CAUSA | DISPARO DEL 1115-01 SE CERRO LOCALMENTE | S23021500019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2023-02-15 | 144840 | keep | 0 | Feb | 2023 | 0.09865 | 0.0013894 | Sustained | FALSE | FALSE | Not_TMED_Event | 2040
BAYAMON | 2023-02-15 04:39 | 2023-02-15 04:40 | 2435 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL INTERRUPTOR 1909-08 | S23021500030 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-15 | 2435 | keep | 0 | Feb | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-02-15 04:39 | 2023-02-15 04:40 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA DEL 1907-05 | S23021500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 2956 | keep | 0 | Feb | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
CANOVANAS | 2023-02-15 04:43 | 2023-02-15 10:11 | 11 | 5:28 | P | TERMINACION SOTERRADA AVERIADA | 1 X 50 EN C/L Y SE REPARO TERMINACION EN BAJANTE PROVISIONAL AEREO | R23021500001 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 328 | 2023-02-15 | 3608 | keep | 0 | Feb | 2023 | 0.0024574 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-02-15 05:35 | 2023-02-15 05:36 | 3701 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23021500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 3701 | keep | 0 | Feb | 2023 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2023-02-15 06:03 | 2023-02-15 06:04 | 3701 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23021500003 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 3701 | keep | 0 | Feb | 2023 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
VEGA BAJA | 2023-02-15 06:41 | 2023-02-15 08:29 | 159 | 1:48 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B23021500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2023-02-15 | 17172 | keep | 0 | Feb | 2023 | 0.011696 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
BAYAMON | 2023-02-15 06:46 | 2023-02-15 06:47 | 603 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 9206-09 | B2302150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 603 | keep | 0 | Feb | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-02-15 06:46 | 2023-02-15 06:47 | 6 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 9206-08 CARGA X 9206-08 | B2302150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-15 | 6 | keep | 0 | Feb | 2023 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-02-15 07:11 | 2023-02-15 10:40 | 1 | 3:29 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO SE IDENTIFICO CAUSA | A23021500036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2023-02-15 | 209 | keep | 0 | Feb | 2023 | 0.00014235 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-15 07:18 | 2023-02-15 07:19 | 2073 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13500 | M23021500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-15 | 2073 | keep | 0 | Feb | 2023 | 0.0014119 | 0.0014119 | Momentary | FALSE | FALSE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2023-02-15 07:18 | 2023-02-15 07:19 | 637 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13500 | M23021500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-15 | 637 | keep | 0 | Feb | 2023 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2023-02-15 07:18 | 2023-02-15 07:19 | 1491 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13500 | M23021500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-15 | 1491 | keep | 0 | Feb | 2023 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2023-02-15 07:18 | 2023-02-15 07:19 | 4892 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13500 | M23021500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-15 | 4892 | keep | 0 | Feb | 2023 | 0.0033319 | 0.0033319 | Momentary | FALSE | FALSE | Not_TMED_Event | 4892
MAYAGÃœEZ | 2023-02-15 07:18 | 2023-02-15 07:19 | 160 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13500 | M23021500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-15 | 160 | keep | 0 | Feb | 2023 | 0.00010898 | 0.00010898 | Momentary | FALSE | FALSE | Not_TMED_Event | 160
SAN JUAN | 2023-02-15 07:35 | 2023-02-15 07:36 | 138 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1206-04 LLEVA 10% DEL 1204-03 LLEVA 40% DEL 1204-04 | S2302150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-15 | 138 | keep | 0 | Feb | 2023 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-02-15 07:35 | 2023-02-15 07:36 | 1977 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1206-04 LLEVA 10% DEL 1204-03 LLEVA 40% DEL 1204-04 | S2302150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-15 | 1977 | keep | 0 | Feb | 2023 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2023-02-15 07:35 | 2023-02-15 07:36 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04 LLEVA 10% DEL 1204-03 LLEVA 40% DEL 1204-04 | S2302150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 1799 | keep | 0 | Feb | 2023 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
BARRANQUITAS | 2023-02-15 07:40 | 2023-02-15 11:32 | 30 | 3:52 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | C23021500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-02-15 | 6960 | keep | 0 | Feb | 2023 | 0.0047404 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-15 07:51 | 2023-02-15 07:53 | 1356 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | S23021500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-15 | 2712 | keep | 0 | Feb | 2023 | 0.0018471 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
CANOVANAS | 2023-02-15 08:11 | 2023-02-15 11:05 | 1 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE XMR | R23021500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2023-02-15 | 174 | keep | 0 | Feb | 2023 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-15 08:14 | 2023-02-15 11:50 | 50 | 3:36 | P | ANIMAL | 1 X 100 EN RISER CRUCE X AVE | C23021500023 | New_Event | Animals | Include | Include | Wildlife | 216 | 2023-02-15 | 10800 | keep | 0 | Feb | 2023 | 0.0073558 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-02-15 08:19 | 2023-02-15 13:41 | 3 | 5:22 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO EN PM 6 1 CLIENTE SIN SERVICIO Y T4 FUERA | P23021500014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 322 | 2023-02-15 | 966 | keep | 0 | Feb | 2023 | 0.00065794 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-02-15 08:24 | 2023-02-15 13:51 | 29 | 5:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO BAJANTES SECUNDARIO | C23021500024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 327 | 2023-02-15 | 9483 | keep | 0 | Feb | 2023 | 0.0064588 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
YAUCO | 2023-02-15 08:26 | 2023-02-15 08:55 | 10 | 0:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA 1 X 40 EN TRANSFORMADOR | P23021500015 | New_Event | Cutout Failure | Include | Include | Equipment | 29 | 2023-02-15 | 290 | keep | 0 | Feb | 2023 | 0.00019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-15 08:29 | 2023-02-15 08:30 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1909-09 | B2302150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 222 | keep | 0 | Feb | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-02-15 08:29 | 2023-02-15 08:30 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE CARGA X 1907-03 | B2302150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-15 | 4456 | keep | 0 | Feb | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
MAYAGÃœEZ | 2023-02-15 08:42 | 2023-02-15 09:15 | 8 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23021500001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-02-15 | 264 | keep | 0 | Feb | 2023 | 0.00017981 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-02-15 08:55 | 2023-02-15 21:35 | 7 | 12:40 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | C23021500035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 760 | 2023-02-15 | 5320 | keep | 0 | Feb | 2023 | 0.0036234 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-02-15 08:56 | 2023-02-15 09:25 | 15 | 0:29 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR Y SE REEMPLAZO CONECTOR EN BAJANTE DE LINEA A CAJA | R23021500015 | New_Event | Primary Wire Break | Include | Include | Equipment | 29 | 2023-02-15 | 435 | keep | 0 | Feb | 2023 | 0.00029628 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-15 08:59 | 2023-02-15 10:37 | 75 | 1:38 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | R23021500016 | New_Event | Animals | Include | Include | Wildlife | 98 | 2023-02-15 | 7350 | keep | 0 | Feb | 2023 | 0.0050061 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-02-15 09:26 | 2023-02-15 11:45 | 10 | 2:19 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA REPARAR BARRA EN PEDESTAL | B23021500039 | New_Event |  |  |  |  | 139 | 2023-02-15 | 1390 | keep | 0 | Feb | 2023 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-02-15 09:50 | 2023-02-15 11:50 | 13 | 2:00 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23021500030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-02-15 | 1560 | keep | 0 | Feb | 2023 | 0.0010625 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2023-02-15 09:53 | 2023-02-15 09:54 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23021500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 2379 | keep | 0 | Feb | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
CAGUAS | 2023-02-15 10:01 | 2023-02-15 11:52 | 60 | 1:51 | P | ANIMAL | 2 X 80 EN C/L CRUCE X AVE | C23021500052 | New_Event | Animals | Include | Include | Wildlife | 111 | 2023-02-15 | 6660 | keep | 0 | Feb | 2023 | 0.0045361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-02-15 10:07 | 2023-02-15 12:20 | 7 | 2:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23021500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2023-02-15 | 931 | keep | 0 | Feb | 2023 | 0.0006341 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-02-15 10:19 | 2023-02-15 13:05 | 15 | 2:46 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO FASE A TIERRA | M23021500024 | New_Event | Animals | Include | Include | Wildlife | 166 | 2023-02-15 | 2490 | keep | 0 | Feb | 2023 | 0.0016959 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-02-15 10:24 | 2023-02-15 15:10 | 40 | 4:46 | P | CAUSAS EXTERNAS | 2 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR CAMION IMPACTO POSTE SECUNDARIO Y CRUZO LAS LINEAS | A23021500029 | New_Event | Damage From Public | Include | Include | Public | 286 | 2023-02-15 | 11440 | keep | 0 | Feb | 2023 | 0.0077917 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-15 10:29 | 2023-02-15 12:50 | 40 | 2:21 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23021500061 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-02-15 | 5640 | keep | 0 | Feb | 2023 | 0.0038414 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-02-15 10:49 | 2023-02-15 12:15 | 19 | 1:26 | P | TERMINACION SOTERRADA AVERIADA | 1 X 30 EN PROVISIONAL AEREO Y SE REPARO TERMINACION | R23021500035 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 86 | 2023-02-15 | 1634 | keep | 0 | Feb | 2023 | 0.0011129 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
GUAYAMA | 2023-02-15 10:51 | 2023-02-15 11:59 | 20 | 1:08 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | P23021500041 | New_Event | Primary Wire Break | Include | Include | Equipment | 68 | 2023-02-15 | 1360 | keep | 0 | Feb | 2023 | 0.00092629 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-15 11:10 | 2023-02-15 14:18 | 71 | 3:08 | P | ANIMAL | 1 X 30 EN C/L SE RETIRO PALOMA | B23021500060 | New_Event | Animals | Include | Include | Wildlife | 188 | 2023-02-15 | 13348 | keep | 0 | Feb | 2023 | 0.0090913 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
AGUADILLA | 2023-02-15 11:11 | 2023-02-15 15:30 | 12 | 4:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 75KVA | M23021500010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 259 | 2023-02-15 | 3108 | keep | 0 | Feb | 2023 | 0.0021168 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-15 11:22 | 2023-02-15 13:33 | 10 | 2:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 SE REMPLAZO CAJA PRIMARIO Y SE LLEVO PUENTE DE LINEA A CAJA | B23021500063 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2023-02-15 | 1310 | keep | 0 | Feb | 2023 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-02-15 11:31 | 2023-02-15 19:26 | 30 | 7:55 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU, 1 X 65 EN RISER SE SECCIONALIZO AVERIA SOTERRADA DE PM-14 @ PM-15 NO QUEDO NADIE SIN SERVICIO | M23021500042 | New_Event | UG Cable Fault | Include | Include | Equipment | 475 | 2023-02-15 | 14250 | keep | 0 | Feb | 2023 | 0.0097056 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-15 11:32 | 2023-02-15 12:48 | 3 | 1:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y SE REMPLAZO CAJA PRIMARIA | B2302150000X | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2023-02-15 | 228 | keep | 0 | Feb | 2023 | 0.00015529 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-02-15 11:33 | 2023-02-15 18:28 | 1 | 6:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50KVA X 75KVA POR DERRAME DE ACEITE EN BANCO DE XMR | P23021500047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 415 | 2023-02-15 | 415 | keep | 0 | Feb | 2023 | 0.00028265 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-15 11:34 | 2023-02-15 13:52 | 30 | 2:18 | P | ANIMAL | 1 X 40 C/L CRUCE POR AVE | CARR 894 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-02-15 | 4140 | keep | 0 | Feb | 2023 | 0.0028197 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-02-15 11:40 | 2023-02-15 13:30 | 12 | 1:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23020900198 | New_Event | Secondary Wire Break | Include | Include | Equipment | 110 | 2023-02-15 | 1320 | keep | 0 | Feb | 2023 | 0.00089905 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-02-15 11:41 | 2023-02-15 13:58 | 8 | 2:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO CONECTORES DEL BAJANTE DEL XMR | C23021500081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 137 | 2023-02-15 | 1096 | keep | 0 | Feb | 2023 | 0.00074648 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-15 12:03 | 2023-02-15 13:16 | 14 | 1:13 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23021500082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-02-15 | 1022 | keep | 0 | Feb | 2023 | 0.00069608 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-02-15 12:08 | 2023-02-15 16:31 | 112 | 4:23 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23021500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2023-02-15 | 29456 | keep | 0 | Feb | 2023 | 0.020062 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
FAJARDO | 2023-02-15 12:12 | 2023-02-15 12:16 | 11 | 0:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | I X 10 EN XMR Y SE REEMPLAZO PORTAFUSIBLE | R23021500042 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2023-02-15 | 44 | keep | 0 | Feb | 2023 | 2.9968e-05 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-02-15 12:22 | 2023-02-15 12:24 | 362 | 0:02 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% DEL 1336-10 SE CERRO POR CONTROL | S23021500086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-02-15 | 724 | keep | 0 | Feb | 2023 | 0.00049311 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-02-15 12:22 | 2023-02-15 12:24 | 36 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% DEL 1336-10 SE CERRO POR CONTROL | S23021500086 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-15 | 72 | keep | 0 | Feb | 2023 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-02-15 12:24 | 2023-02-15 14:32 | 63 | 2:08 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23021500088 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-02-15 | 8064 | keep | 0 | Feb | 2023 | 0.0054924 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
VEGA BAJA | 2023-02-15 12:30 | 2023-02-15 13:30 | 8 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS AVERIADAS | A23021500028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-02-15 | 480 | keep | 0 | Feb | 2023 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-15 12:31 | 2023-02-15 12:35 | 1106 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE CERRO POR CONTROL LUEGO DE CONFIRMAR PERSONAL FUERA DE LAS LINEAS | S23021500089 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-02-15 | 4424 | keep | 0 | Feb | 2023 | 0.0030132 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-02-15 12:31 | 2023-02-15 12:35 | 1802 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE CERRO POR CONTROL LUEGO DE CONFIRMAR PERSONAL FUERA DE LAS LINEAS | S23021500089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-02-15 | 7208 | keep | 0 | Feb | 2023 | 0.0049093 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
PONCE | 2023-02-15 12:32 | 2023-02-15 13:45 | 30 | 1:13 | P | CABLE SOTERRADO AVERIADO | SE ELIMINO PROVISIONAL Y SE CONECTO CABLE SOTERRADO | P23021500052 | New_Event | UG Cable Fault | Include | Include | Equipment | 73 | 2023-02-15 | 2190 | keep | 0 | Feb | 2023 | 0.0014916 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-02-15 12:51 | 2023-02-15 15:40 | 30 | 2:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23021500073 | New_Event | Primary Wire Break | Include | Include | Equipment | 169 | 2023-02-15 | 5070 | keep | 0 | Feb | 2023 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-02-15 12:52 | 2023-02-15 17:22 | 30 | 4:30 | P | DESGANCHE | 1 X 65 EN C/L | C23021500091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2023-02-15 | 8100 | keep | 0 | Feb | 2023 | 0.0055169 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-02-15 12:57 | 2023-02-15 14:00 | 125 | 1:03 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | R23021500045 | New_Event | Animals | Include | Include | Wildlife | 63 | 2023-02-15 | 7875 | keep | 0 | Feb | 2023 | 0.0053636 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-02-15 13:15 | 2023-02-15 15:03 | 40 | 1:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR | B23021500088 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 108 | 2023-02-15 | 4320 | keep | 0 | Feb | 2023 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-02-15 13:21 | 2023-02-15 13:22 | 1076 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23021500058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 1076 | keep | 0 | Feb | 2023 | 0.00073286 | 0.00073286 | Momentary | FALSE | FALSE | Not_TMED_Event | 1076
FAJARDO | 2023-02-15 13:24 | 2023-02-15 13:58 | 4 | 0:34 | P | ANIMAL | 1 X EN XMR 1 X 50 C/L CRUCE X AVE | R23021500049 | New_Event | Animals | Include | Include | Wildlife | 34 | 2023-02-15 | 136 | keep | 0 | Feb | 2023 | 9.2629e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-15 13:25 | 2023-02-15 13:26 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | B2302150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 4431 | keep | 0 | Feb | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
AGUADILLA | 2023-02-15 13:40 | 2023-02-15 15:30 | 12 | 1:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | M23021500078 | New_Event | Cutout Failure | Include | Include | Equipment | 110 | 2023-02-15 | 1320 | keep | 0 | Feb | 2023 | 0.00089905 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-02-15 13:41 | 2023-02-15 16:56 | 1 | 3:15 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE BUSHING AVERIADO EN T#4 | P23021500014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2023-02-15 | 195 | keep | 0 | Feb | 2023 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-15 14:13 | 2023-02-15 20:22 | 18 | 6:09 | P | ANIMAL | 1 X 15 EN XMR SE RETIRO IGUANA | S23021500114 | New_Event | Animals | Include | Include | Wildlife | 369 | 2023-02-15 | 6642 | keep | 0 | Feb | 2023 | 0.0045238 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2023-02-15 14:17 | 2023-02-15 16:16 | 4 | 1:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23021500106 | New_Event | Secondary Wire Break | Include | Include | Equipment | 119 | 2023-02-15 | 476 | keep | 0 | Feb | 2023 | 0.0003242 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-02-15 14:20 | 2023-02-15 14:23 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S2302150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-15 | 2610 | keep | 0 | Feb | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2023-02-15 14:35 | 2023-02-15 14:36 | 2077 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE DE INTERRUPTOR | M23021500094 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-02-15 | 2077 | keep | 0 | Feb | 2023 | 0.0014146 | 0.0014146 | Momentary | FALSE | FALSE | Not_TMED_Event | 2077
MAYAGÃœEZ | 2023-02-15 14:36 | 2023-02-15 17:30 | 100 | 2:54 | P | CAUSAS EXTERNAS | 2 X 140 EN RISER Y 1 X 20 EN TRANSFORMADOR CAMION IMPACTO LINEAS | M23021500116 | 1st_after_momentary | Damage From Public | Include | Include | Public | 174 | 2023-02-15 | 17400 | keep | 0 | Feb | 2023 | 0.011851 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-02-15 14:47 | 2023-02-15 16:46 | 7 | 1:59 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE RELOCALIZO XMR Y NEUTRAL PRIMARIO POR CAMBIO DE POSTE SECUNDARIO EN EL LUGAR | C23021500118 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 119 | 2023-02-15 | 833 | keep | 0 | Feb | 2023 | 0.00056735 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-02-15 14:55 | 2023-02-15 15:33 | 1681 | 0:38 | T | DESGANCHE | DISPARO DE INTERRUPTOR LLEVA 1346-06 SE DEJO SECCIONALIZADO. 20%1303-01 EN SERVICIO Y SE ABRIO AMARRE CONTRA 1346-06 | S23021500121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2023-02-15 | 63878 | keep | 0 | Feb | 2023 | 0.043507 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-02-15 14:55 | 2023-02-15 15:33 | 1598 | 0:38 | T | ALIMENTADOR AMARRADO | CARGA 1346-06 EN SERVICIO CERRANDO AMARRE CONTRA 1303-01 POR DESGANCHE EN ALIMENTADOR 1303-01 | S23021500121 | New_Event | Feeder Load Transferred | Include | Include | Other | 38 | 2023-02-15 | 60724 | keep | 0 | Feb | 2023 | 0.041359 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
VEGA BAJA | 2023-02-15 15:11 | 2023-02-15 20:53 | 6 | 5:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA | A23021500098 | New_Event | Service Transformer Failure | Include | Include | Equipment | 342 | 2023-02-15 | 2052 | keep | 0 | Feb | 2023 | 0.0013976 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-02-15 15:12 | 2023-02-15 16:28 | 8 | 1:16 | P | CAUSAS EXTERNAS | 1 X 10 EN TRANSFORMADOR SE LEVANTO SECUNDARIA IMPACTADA POR CAMION | R23021500067 | New_Event | Damage From Public | Include | Include | Public | 76 | 2023-02-15 | 608 | keep | 0 | Feb | 2023 | 0.00041411 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-15 15:27 | 2023-02-15 16:25 | 8 | 0:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23021500109 | New_Event | Secondary Wire Break | Include | Include | Equipment | 58 | 2023-02-15 | 464 | keep | 0 | Feb | 2023 | 0.00031603 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-15 15:33 | 2023-02-15 16:30 | 1344 | 0:57 | P | DESGANCHE | SE SECCIONALIZO PARA REALIZAR DESGANCHE 90% EN SERVICIO | S23021500121 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 57 | 2023-02-15 | 76608 | keep | 0 | Feb | 2023 | 0.052177 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-15 15:38 | 2023-02-15 16:54 | 35 | 1:16 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO FASES | M23021500125 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-02-15 | 2660 | keep | 0 | Feb | 2023 | 0.0018117 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-02-15 15:49 | 2023-02-15 20:02 | 1 | 4:13 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SEC | C23021500125 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 253 | 2023-02-15 | 253 | keep | 0 | Feb | 2023 | 0.00017232 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-15 15:53 | 2023-02-15 16:58 | 99 | 1:05 | P | OTRAS CAUSAS | 1 X 50 EN CORTE DE LINEA FUSIBLE CORROIDO POR EL SALITRE | P23021500088 | New_Event | Other Causes | Include | Include | Other | 65 | 2023-02-15 | 6435 | keep | 0 | Feb | 2023 | 0.0043828 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
BARRANQUITAS | 2023-02-15 16:00 | 2023-02-15 17:38 | 7 | 1:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SEC | C23021500123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 98 | 2023-02-15 | 686 | keep | 0 | Feb | 2023 | 0.00046723 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-02-15 16:14 | 2023-02-15 17:59 | 42 | 1:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R23021500082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-02-15 | 4410 | keep | 0 | Feb | 2023 | 0.0030036 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2023-02-15 16:30 | 2023-02-15 17:02 | 168 | 0:32 | P | DESGANCHE | SE REALIZO DESGANCHE CON VARETA 100% EN SERVICIO | S23021500121 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 32 | 2023-02-15 | 5376 | keep | 0 | Feb | 2023 | 0.0036616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-15 16:30 | 2023-02-15 16:57 | 1 | 0:27 | P | ANIMAL | 1 X 30 EN C/L SE RETIRO AVE | B23021500145 | New_Event | Animals | Include | Include | Wildlife | 27 | 2023-02-15 | 27 | keep | 0 | Feb | 2023 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-15 16:40 | 2023-02-15 16:50 | 2 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23021500032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-02-15 | 20 | keep | 0 | Feb | 2023 | 1.3622e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-02-15 16:49 | 2023-02-15 18:05 | 70 | 1:16 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R23021500092 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-02-15 | 5320 | keep | 0 | Feb | 2023 | 0.0036234 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-02-15 17:01 | 2023-02-15 17:57 | 19 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23021500150 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2023-02-15 | 1064 | keep | 0 | Feb | 2023 | 0.00072469 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-02-15 17:23 | 2023-02-15 17:25 | 1066 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S23021500241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-15 | 2132 | keep | 0 | Feb | 2023 | 0.0014521 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
BAYAMON | 2023-02-15 17:56 | 2023-02-15 20:02 | 174 | 2:06 | P | TERMINACION SOTERRADA AVERIADA | 1 X 40 EN PROVISIONAL AEREO SE REMPLAZO TERMINACION | B23021500157 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 126 | 2023-02-15 | 21924 | keep | 0 | Feb | 2023 | 0.014932 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
HUMACAO | 2023-02-15 18:35 | 2023-02-15 20:10 | 25 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23021500136 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2023-02-15 | 2375 | keep | 0 | Feb | 2023 | 0.0016176 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-02-15 18:40 | 2023-02-15 19:00 | 8 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONECTORES EN LINEA SECUNDARIA | P23011500051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-02-15 | 160 | keep | 0 | Feb | 2023 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-02-15 19:09 | 2023-02-15 21:10 | 35 | 2:01 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23021500164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-02-15 | 4235 | keep | 0 | Feb | 2023 | 0.0028844 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-02-15 19:19 | 2023-02-16 15:45 | 12 | 20:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23021500163 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1226 | 2023-02-15 | 14712 | keep | 0 | Feb | 2023 | 0.01002 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-02-15 19:37 | 2023-02-16 08:55 | 10 | 13:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23021500175 | New_Event | Primary Wire Break | Include | Include | Equipment | 798 | 2023-02-15 | 7980 | keep | 0 | Feb | 2023 | 0.0054351 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-15 19:48 | 2023-02-15 19:49 | 478 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 478 | keep | 0 | Feb | 2023 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2023-02-15 19:48 | 2023-02-15 19:49 | 949 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 949 | keep | 0 | Feb | 2023 | 0.00064636 | 0.00064636 | Momentary | FALSE | FALSE | Not_TMED_Event | 949
AGUADILLA | 2023-02-15 20:03 | 2023-02-15 20:04 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23021500178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 1827 | keep | 0 | Feb | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
HUMACAO | 2023-02-15 20:27 | 2023-02-15 21:30 | 40 | 1:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO | C23021500151 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 63 | 2023-02-15 | 2520 | keep | 0 | Feb | 2023 | 0.0017164 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-15 20:33 | 2023-02-15 23:20 | 128 | 2:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 80 EN C/LS LLUVIAS | C23021500152 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 167 | 2023-02-15 | 21376 | keep | 0 | Feb | 2023 | 0.014559 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2023-02-15 20:44 | 2023-02-16 13:18 | 236 | 16:34 | P | DESGANCHE | 3 X 140 EN CORTE DE LINEA Y 1 X 80 EN RISER | C23021500156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 994 | 2023-02-15 | 234584 | keep | 0 | Feb | 2023 | 0.15977 | 0.00016074 | Sustained | FALSE | FALSE | Not_TMED_Event | 236
MAYAGÃœEZ | 2023-02-15 20:44 | 2023-02-15 21:30 | 100 | 0:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23021500189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 46 | 2023-02-15 | 4600 | keep | 0 | Feb | 2023 | 0.003133 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-15 20:44 | 2023-02-16 01:11 | 9 | 4:27 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR SECUNDARIA | B23021500170 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 267 | 2023-02-15 | 2403 | keep | 0 | Feb | 2023 | 0.0016367 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-02-15 20:59 | 2023-02-15 22:03 | 20 | 1:04 | P | CAUSAS EXTERNAS | 1 X 100 EN C/L A CAUSA DE IMPACTO DE VEHICULO | B23021500172 | New_Event | Damage From Public | Include | Include | Public | 64 | 2023-02-15 | 1280 | keep | 0 | Feb | 2023 | 0.0008718 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-02-15 21:09 | 2023-02-15 21:10 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23021500193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 1192 | keep | 0 | Feb | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BARRANQUITAS | 2023-02-15 21:36 | 2023-02-16 00:50 | 1458 | 3:14 | P | DESGANCHE | SE CERRO EL IR | C23021500184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-02-15 | 282852 | keep | 0 | Feb | 2023 | 0.19265 | 0.00099304 | Sustained | FALSE | FALSE | Not_TMED_Event | 1458
HUMACAO | 2023-02-15 21:50 | 2023-02-16 07:45 | 45 | 9:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA | C23021500191 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 595 | 2023-02-15 | 26775 | keep | 0 | Feb | 2023 | 0.018236 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-02-15 22:35 | 2023-02-16 00:12 | 50 | 1:37 | P | DESGANCHE | SE CERRO PUENTE DE LINEA A CAJA TRASPATIO Y DESGANCHE | B23021500175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-02-15 | 4850 | keep | 0 | Feb | 2023 | 0.0033033 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-02-15 22:50 | 2023-02-16 02:30 | 1617 | 3:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23021500207 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 220 | 2023-02-15 | 355740 | keep | 0 | Feb | 2023 | 0.24229 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2023-02-15 22:50 | 2023-02-16 02:30 | 1017 | 3:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23021500207 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 220 | 2023-02-15 | 223740 | keep | 0 | Feb | 2023 | 0.15239 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2023-02-15 22:50 | 2023-02-16 02:30 | 828 | 3:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23021500207 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 220 | 2023-02-15 | 182160 | keep | 0 | Feb | 2023 | 0.12407 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2023-02-15 22:50 | 2023-02-16 02:30 | 863 | 3:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23021500208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 220 | 2023-02-15 | 189860 | keep | 0 | Feb | 2023 | 0.12931 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2023-02-15 22:50 | 2023-02-16 02:30 | 309 | 3:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23021500208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 220 | 2023-02-15 | 67980 | keep | 0 | Feb | 2023 | 0.046301 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2023-02-15 22:50 | 2023-02-16 02:30 | 176 | 3:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23021500208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 220 | 2023-02-15 | 38720 | keep | 0 | Feb | 2023 | 0.026372 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2023-02-15 22:50 | 2023-02-16 08:53 | 974 | 10:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M23021500212 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 603 | 2023-02-15 | 587322 | keep | 0 | Feb | 2023 | 0.40002 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
MAYAGÃœEZ | 2023-02-15 22:52 | 2023-02-16 09:45 | 12 | 10:53 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23021500197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 653 | 2023-02-15 | 7836 | keep | 0 | Feb | 2023 | 0.0053371 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-02-15 23:33 | 2023-02-15 23:34 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 1310 | keep | 0 | Feb | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CANOVANAS | 2023-02-15 23:38 | 2023-02-15 23:39 | 3012 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23021500109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 3012 | keep | 0 | Feb | 2023 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2023-02-15 23:47 | 2023-02-16 01:45 | 143 | 1:58 | P | ANIMAL | 1 X 100 EN RISER CRUCE X RATON | R23021500111 | New_Event | Animals | Include | Include | Wildlife | 118 | 2023-02-15 | 16874 | keep | 0 | Feb | 2023 | 0.011493 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-02-15 23:49 | 2023-02-15 23:50 | 849 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S23021500304 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-15 | 849 | keep | 0 | Feb | 2023 | 0.00057825 | 0.00057825 | Momentary | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2023-02-16 00:15 | 2023-02-16 13:40 | 229 | 13:25 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | S23021600001 | New_Event | Primary Wire Break | Include | Include | Equipment | 805 | 2023-02-16 | 184345 | keep | 0 | Feb | 2023 | 0.12556 | 0.00015597 | Sustained | FALSE | FALSE | Not_TMED_Event | 229
ARECIBO | 2023-02-16 01:16 | 2023-02-16 09:20 | 40 | 8:04 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE | A23021600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 484 | 2023-02-16 | 19360 | keep | 0 | Feb | 2023 | 0.013186 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-02-16 02:14 | 2023-02-16 05:47 | 318 | 3:33 | P | DESGANCHE | 1 X 80 EN C/L Y 1 X 100 EN C/L DESGANCHE | B23021600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-02-16 | 67734 | keep | 0 | Feb | 2023 | 0.046133 | 0.00021659 | Sustained | FALSE | FALSE | Not_TMED_Event | 318
BAYAMON | 2023-02-16 03:06 | 2023-02-16 06:32 | 150 | 3:26 | P | DESGANCHE | 1 X 80 1 X 65 1 X 50 DESGANCHE | S23021600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-02-16 | 30900 | keep | 0 | Feb | 2023 | 0.021046 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-02-16 03:24 | 2023-02-16 08:34 | 6 | 5:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIA VIENTO | C23021600020 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 310 | 2023-02-16 | 1860 | keep | 0 | Feb | 2023 | 0.0012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-02-16 04:46 | 2023-02-16 14:34 | 120 | 9:48 | P | DESGANCHE | 1 X 100 EN C/L | C23021600024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 588 | 2023-02-16 | 70560 | keep | 0 | Feb | 2023 | 0.048058 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2023-02-16 05:34 | 2023-02-16 15:09 | 98 | 9:35 | P | DESGANCHE | 1 X 50 Y 1 X 65 C/LS | C2302160027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 575 | 2023-02-16 | 56350 | keep | 0 | Feb | 2023 | 0.03838 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
SAN JUAN | 2023-02-16 06:07 | 2023-02-16 06:08 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2302160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-16 | 45 | keep | 0 | Feb | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-02-16 06:12 | 2023-02-16 11:40 | 14 | 5:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO 3 BARRAS EN PEDESTAL Y SE REPARO CONDUCTOR | C23021600136 | New_Event | Secondary Wire Break | Include | Include | Equipment | 328 | 2023-02-16 | 4592 | keep | 0 | Feb | 2023 | 0.0031276 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2023-02-16 06:12 | 2023-02-16 09:04 | 1 | 2:52 | P | DESGANCHE | 1 X 25 EN C/L | C23021600030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-02-16 | 172 | keep | 0 | Feb | 2023 | 0.00011715 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-16 06:26 | 2023-02-16 10:53 | 70 | 4:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L REEMPLAZO AISLADOR | C23021600033 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 267 | 2023-02-16 | 18690 | keep | 0 | Feb | 2023 | 0.01273 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-02-16 06:32 | 2023-02-16 10:22 | 5 | 3:50 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23021600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2023-02-16 | 1150 | keep | 0 | Feb | 2023 | 0.00078326 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-02-16 06:37 | 2023-02-16 06:38 | 2708 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR | R23021600002 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-16 | 2708 | keep | 0 | Feb | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-02-16 06:38 | 2023-02-16 08:39 | 44 | 2:01 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | R23021600004 | 1st_after_momentary | Animals | Include | Include | Wildlife | 121 | 2023-02-16 | 5324 | keep | 0 | Feb | 2023 | 0.0036262 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
SAN JUAN | 2023-02-16 06:52 | 2023-02-16 10:43 | 75 | 3:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | S23021600086 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2023-02-16 | 17325 | keep | 0 | Feb | 2023 | 0.0118 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-02-16 07:22 | 2023-02-16 07:30 | 7 | 0:08 | P | OTRAS CAUSAS | SE ABRIO BANCO DE XMR PARA CONECTAR LUMINARIA | C23021600056 | New_Event | Other Causes | Include | Include | Other | 8 | 2023-02-16 | 56 | keep | 0 | Feb | 2023 | 3.8141e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-02-16 07:31 | 2023-02-16 12:00 | 30 | 4:29 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CL FASE PRIMARIAS CRUZADA POR BAJANTE DE CAJA PRIMARIA EN DESHUSO SE RETIRO CAJAS VERIFCO EVENTO EN OMS CREADO P | P23021600019 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 269 | 2023-02-16 | 8070 | keep | 0 | Feb | 2023 | 0.0054964 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-02-16 08:00 | 2023-02-16 09:57 | 14 | 1:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE TRANSFORMADOR 1 X 20 | P23021600022 | New_Event | Cutout Failure | Include | Include | Equipment | 117 | 2023-02-16 | 1638 | keep | 0 | Feb | 2023 | 0.0011156 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-02-16 08:10 | 2023-02-16 11:20 | 30 | 3:10 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO FASES | M23021600023 | New_Event | Animals | Include | Include | Wildlife | 190 | 2023-02-16 | 5700 | keep | 0 | Feb | 2023 | 0.0038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-02-16 08:13 | 2023-02-16 09:30 | 5 | 1:17 | P | NO SE REPORTO CAUSA | 1 X 80 EN XMR | B23021600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2023-02-16 | 385 | keep | 0 | Feb | 2023 | 0.00026222 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-02-16 08:16 | 2023-02-16 13:09 | 8 | 4:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M23021600027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 293 | 2023-02-16 | 2344 | keep | 0 | Feb | 2023 | 0.0015965 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-16 08:16 | 2023-02-16 13:10 | 60 | 4:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23021600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-02-16 | 17640 | keep | 0 | Feb | 2023 | 0.012015 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-02-16 08:20 | 2023-02-16 08:21 | 2791 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23021600013 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-16 | 2791 | keep | 0 | Feb | 2023 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
BAYAMON | 2023-02-16 08:21 | 2023-02-16 11:40 | 52 | 3:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B23021600045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2023-02-16 | 10348 | keep | 0 | Feb | 2023 | 0.007048 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
VEGA BAJA | 2023-02-16 08:21 | 2023-02-16 09:54 | 1860 | 1:33 | P | ANIMAL | AVE CAUSA CRUCE Y FUNDE 2 FUSIBLES DE 115KV | A23021600086 | 1st_after_momentary | Animals | Include | Include | Wildlife | 93 | 2023-02-16 | 172980 | keep | 0 | Feb | 2023 | 0.11782 | 0.0012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 1860
VEGA BAJA | 2023-02-16 08:21 | 2023-02-16 09:54 | 976 | 1:33 | P | ANIMAL | AVE CAUSA CRUCE Y FUNDE 2 FUSIBLES DE 115KV | A23021600086 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-02-16 | 90768 | keep | 0 | Feb | 2023 | 0.061822 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
VEGA BAJA | 2023-02-16 08:21 | 2023-02-16 09:54 | 506 | 1:33 | P | ANIMAL | AVE CAUSA CRUCE Y FUNDE 2 FUSIBLES DE 115KV | A23021600086 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-02-16 | 47058 | keep | 0 | Feb | 2023 | 0.032051 | 0.00034463 | Sustained | FALSE | FALSE | Not_TMED_Event | 506
VEGA BAJA | 2023-02-16 08:21 | 2023-02-16 09:54 | 1000 | 1:33 | P | ANIMAL | AVE CAUSA CRUCE Y FUNDE 2 FUSIBLES DE 115KV | A23021600086 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-02-16 | 93000 | keep | 0 | Feb | 2023 | 0.063342 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
AGUADILLA | 2023-02-16 08:45 | 2023-02-16 19:50 | 2 | 11:05 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA RETIRAR CARGA Y REMPLAZAR TRES POSTES OCTAGONALES AVERIADOS | A23021400003 | New_Event | Primary Pole Failure | Include | Include | Equipment | 665 | 2023-02-16 | 1330 | keep | 0 | Feb | 2023 | 0.00090586 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-02-16 09:08 | 2023-02-16 09:10 | 125 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C2302160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-16 | 250 | keep | 0 | Feb | 2023 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-02-16 09:18 | 2023-02-16 16:07 | 40 | 6:49 | P | DESGANCHE | 1 X 65 EN C/L | C23021600131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 409 | 2023-02-16 | 16360 | keep | 0 | Feb | 2023 | 0.011143 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-16 09:26 | 2023-02-16 12:57 | 6 | 3:31 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y SE REPARO PEDESTAL | B23021600032 | New_Event |  |  |  |  | 211 | 2023-02-16 | 1266 | keep | 0 | Feb | 2023 | 0.00086227 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-02-16 09:28 | 2023-02-16 11:03 | 120 | 1:35 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTE DE LINEA DESGANCHE | R23021600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-02-16 | 11400 | keep | 0 | Feb | 2023 | 0.0077645 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BARRANQUITAS | 2023-02-16 09:47 | 2023-02-16 14:15 | 13 | 4:28 | P | CONDUCTOR ROTO O ABIERTO | ABRIO XMR PARA REPARAR BAJANTE Y NEUTRAL PRIMARIO | C23021600015 | New_Event | Primary Wire Break | Include | Include | Equipment | 268 | 2023-02-16 | 3484 | keep | 0 | Feb | 2023 | 0.0023729 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-02-16 09:54 | 2023-02-16 15:38 | 2791 | 5:44 | S | ANIMAL | AVE CRUZA CAJA DE SERVICE TRANSFORMER CON BARRA 8.32KV; SE REMPLAZO AISLADOR DE BARRA, SE AISLO CAJA DE SERVICE TRANSFORMER Y SE REMPLAZO 2 FUSIBLES DE 115KV | A23021600103 | Additional_clients | Animals | Include | Include | Wildlife | 344 | 2023-02-16 | 960104 | keep | 0 | Feb | 2023 | 0.65392 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-16 09:54 | 2023-02-16 15:38 | 1464 | 5:44 | S | ANIMAL | AVE CRUZA CAJA DE SERVICE TRANSFORMER CON BARRA 8.32KV; SE REMPLAZO AISLADOR DE BARRA, SE AISLO CAJA DE SERVICE TRANSFORMER Y SE REMPLAZO 2 FUSIBLES DE 115KV | A23021600103 | Additional_clients | Animals | Include | Include | Wildlife | 344 | 2023-02-16 | 503616 | keep | 0 | Feb | 2023 | 0.34301 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-16 09:54 | 2023-02-16 15:38 | 759 | 5:44 | S | ANIMAL | AVE CRUZA CAJA DE SERVICE TRANSFORMER CON BARRA 8.32KV; SE REMPLAZO AISLADOR DE BARRA, SE AISLO CAJA DE SERVICE TRANSFORMER Y SE REMPLAZO 2 FUSIBLES DE 115KV | A23021600103 | Additional_clients | Animals | Include | Include | Wildlife | 344 | 2023-02-16 | 261096 | keep | 0 | Feb | 2023 | 0.17783 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-16 09:54 | 2023-02-16 15:38 | 1500 | 5:44 | S | ANIMAL | AVE CRUZA CAJA DE SERVICE TRANSFORMER CON BARRA 8.32KV; SE REMPLAZO AISLADOR DE BARRA, SE AISLO CAJA DE SERVICE TRANSFORMER Y SE REMPLAZO 2 FUSIBLES DE 115KV | A23021600103 | Additional_clients | Animals | Include | Include | Wildlife | 344 | 2023-02-16 | 516000 | keep | 0 | Feb | 2023 | 0.35145 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-16 10:04 | 2023-02-16 11:50 | 7 | 1:46 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | B23021600043 | New_Event | Animals | Include | Include | Wildlife | 106 | 2023-02-16 | 742 | keep | 0 | Feb | 2023 | 0.00050537 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-02-16 10:09 | 2023-02-16 14:49 | 30 | 4:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23021600096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2023-02-16 | 8400 | keep | 0 | Feb | 2023 | 0.0057212 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-02-16 10:10 | 2023-02-16 14:16 | 6 | 4:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA CON ESCAPE DE ACEITE | M23021600091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 246 | 2023-02-16 | 1476 | keep | 0 | Feb | 2023 | 0.0010053 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-16 10:20 | 2023-02-16 11:07 | 11 | 0:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN RISER LLUVIA | B23021600046 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 47 | 2023-02-16 | 517 | keep | 0 | Feb | 2023 | 0.00035213 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-02-16 10:30 | 2023-02-16 18:06 | 4 | 7:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23021600188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 456 | 2023-02-16 | 1824 | keep | 0 | Feb | 2023 | 0.0012423 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-02-16 10:31 | 2023-02-16 11:44 | 10 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C23021600175 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-02-16 | 730 | keep | 0 | Feb | 2023 | 0.0004972 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-02-16 10:32 | 2023-02-16 15:32 | 8 | 5:00 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A23021600118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-02-16 | 2400 | keep | 0 | Feb | 2023 | 0.0016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-02-16 10:33 | 2023-02-16 11:01 | 25 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO T-324 PARA LIMPIAR PEDESTAL Y BARRA BOTANDO HUMO | R23021600021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-02-16 | 700 | keep | 0 | Feb | 2023 | 0.00047677 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-02-16 10:33 | 2023-02-16 10:34 | 2826 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23021600178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-16 | 2826 | keep | 0 | Feb | 2023 | 0.0019248 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
SAN JUAN | 2023-02-16 10:35 | 2023-02-16 10:42 | 4 | 0:07 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA PASAR SECUNDARIA A POSTE NUEVO | S23021600094 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 7 | 2023-02-16 | 28 | keep | 0 | Feb | 2023 | 1.9071e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-02-16 10:45 | 2023-02-16 15:07 | 200 | 4:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | C23021600182 | New_Event | Cutout Failure | Include | Include | Equipment | 262 | 2023-02-16 | 52400 | keep | 0 | Feb | 2023 | 0.035689 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-02-16 10:47 | 2023-02-16 17:25 | 40 | 6:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REEMPLAZO CAJA PRIMARIA | B23021600054 | New_Event | Cutout Failure | Include | Include | Equipment | 398 | 2023-02-16 | 15920 | keep | 0 | Feb | 2023 | 0.010843 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-16 10:57 | 2023-02-16 13:57 | 35 | 3:00 | P | TERMINACION SOTERRADA AVERIADA | 1 X 50 EN PROVISIONAL AEREO SE REEMPLAZO TERMINACION | B23021600065 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 180 | 2023-02-16 | 6300 | keep | 0 | Feb | 2023 | 0.0042909 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-02-16 11:10 | 2023-02-16 13:12 | 93 | 2:02 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23021600107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-02-16 | 11346 | keep | 0 | Feb | 2023 | 0.0077277 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2023-02-16 11:10 | 2023-02-16 13:45 | 20 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23021600133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2023-02-16 | 3100 | keep | 0 | Feb | 2023 | 0.0021114 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-02-16 11:20 | 2023-02-16 11:22 | 2826 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23021600196 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-16 | 5652 | keep | 0 | Feb | 2023 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
AGUADILLA | 2023-02-16 11:31 | 2023-02-16 16:00 | 100 | 4:29 | P | ARBOL SOBRE LINEA | 1 X 65 Y 1 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M23021600143 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 269 | 2023-02-16 | 26900 | keep | 0 | Feb | 2023 | 0.018321 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-16 11:32 | 2023-02-16 11:54 | 5 | 0:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONECTORES EN SALIDA DEL XMR | B23021600063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 22 | 2023-02-16 | 110 | keep | 0 | Feb | 2023 | 7.492e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-02-16 11:41 | 2023-02-16 15:26 | 100 | 3:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL AEREO 1 X 30 EN RISER | S23021600117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2023-02-16 | 22500 | keep | 0 | Feb | 2023 | 0.015325 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-16 11:53 | 2023-02-16 12:26 | 43 | 0:33 | P | CAUSAS EXTERNAS | SE REMPLAZO CAJA PRIMARIA AVERIADA POR VEHICULO QUE ARRANCO LINEA | B23021600061 | New_Event | Damage From Public | Include | Include | Public | 33 | 2023-02-16 | 1419 | keep | 0 | Feb | 2023 | 0.00096647 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BARRANQUITAS | 2023-02-16 11:58 | 2023-02-16 15:17 | 7 | 3:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | C23021600217 | New_Event | Secondary Wire Break | Include | Include | Equipment | 199 | 2023-02-16 | 1393 | keep | 0 | Feb | 2023 | 0.00094877 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-02-16 12:06 | 2023-02-16 12:57 | 1 | 0:51 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO BANCO DE XMR PARA REPARAR BAJANTE DE LINEA A CAJA | C23021600218 | New_Event | Primary Wire Break | Include | Include | Equipment | 51 | 2023-02-16 | 51 | keep | 0 | Feb | 2023 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-16 12:08 | 2023-02-16 13:21 | 8 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REALIZO DESGANCHE Y SE CAMBIARON TODOS LOS CONECTORES DEL BAJANTE SECUNDARIO | P23021600069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-02-16 | 584 | keep | 0 | Feb | 2023 | 0.00039776 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-16 12:10 | 2023-02-16 12:28 | 603 | 0:18 | T | ERROR HUMANO | SE ABRIO A PETICION DE JESUS TORRES POR TRABAJOS EN SU CON BY-230211-02 PARA LIBERAR BKR 9206-08 QUE LLEVA 9206-09 | B23021600075 | New_Event | Human Error | Include | Include | Other | 18 | 2023-02-16 | 10854 | keep | 0 | Feb | 2023 | 0.0073926 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-02-16 12:10 | 2023-02-16 12:28 | 6 | 0:18 | T | ALIMENTADOR AMARRADO | SE ABRIO A PETICION DE JESUS TORRES POR TRABAJOS EN 9206-09 CON BY-230211-02 PARA LIBERAR BKR 9206-08 CARGA X 9206-08 | B23021600075 | New_Event | Feeder Load Transferred | Include | Include | Other | 18 | 2023-02-16 | 108 | keep | 0 | Feb | 2023 | 7.3558e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-02-16 12:24 | 2023-02-16 15:18 | 1 | 2:54 | P | PROBLEMA DEL CLIENTE | SE CERRO CAJA PROBLEMA INTERNO SIN FUSIBLE | P23021600071 | New_Event | Customer-Related Interruption | Include | Include | Public | 174 | 2023-02-16 | 174 | keep | 0 | Feb | 2023 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-16 12:28 | 2023-02-16 19:19 | 8 | 6:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 10 KVA QUEMADO | M23021600224 | New_Event | Service Transformer Failure | Include | Include | Equipment | 411 | 2023-02-16 | 3288 | keep | 0 | Feb | 2023 | 0.0022394 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-02-16 12:29 | 2023-02-16 13:00 | 12 | 0:31 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE DE LINEA A CAJA TRANSFORMADOR | R23021600026 | New_Event | Primary Wire Break | Include | Include | Equipment | 31 | 2023-02-16 | 372 | keep | 0 | Feb | 2023 | 0.00025337 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-02-16 12:37 | 2023-02-16 14:40 | 60 | 2:03 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | A23021600140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-02-16 | 7380 | keep | 0 | Feb | 2023 | 0.0050265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-02-16 12:39 | 2023-02-16 14:35 | 28 | 1:56 | P | DESGANCHE | 1 X 40 EN C/L | C23021600229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-02-16 | 3248 | keep | 0 | Feb | 2023 | 0.0022122 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
AGUADILLA | 2023-02-16 12:50 | 2023-02-16 16:13 | 33 | 3:23 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REFIRIO PARA REPARAR LINEAS ARRIADAS | M23021600175 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 203 | 2023-02-16 | 6699 | keep | 0 | Feb | 2023 | 0.0045627 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
CAGUAS | 2023-02-16 13:14 | 2023-02-16 18:09 | 20 | 4:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C23021600239 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 295 | 2023-02-16 | 5900 | keep | 0 | Feb | 2023 | 0.0040185 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-16 13:34 | 2023-02-16 21:45 | 6 | 8:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | B23021600091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 491 | 2023-02-16 | 2946 | keep | 0 | Feb | 2023 | 0.0020065 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-02-16 13:34 | 2023-02-16 13:58 | 1 | 0:24 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | C23021600257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2023-02-16 | 24 | keep | 0 | Feb | 2023 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-16 13:40 | 2023-02-16 16:17 | 135 | 2:37 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR A PETICION PERSONAL EN EL CAMPO PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO A LA SALIDA DE ALIMENTADOR. SE LEVANTO CONDUCTOR | S23021600150 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 157 | 2023-02-16 | 21195 | keep | 0 | Feb | 2023 | 0.014436 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-16 14:02 | 2023-02-16 14:05 | 5191 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23021600095 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-02-16 | 15573 | keep | 0 | Feb | 2023 | 0.010607 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
PONCE | 2023-02-16 14:04 | 2023-02-16 15:39 | 80 | 1:35 | P | CONDUCTOR ARRIADO O CRUZADO | CRUCE DE PROVISIONAL DE AP CON PROVISIONAL PRIMARIO 1 X 65 ENTRADA RISER 1 X 50 EN SALIDA Y 2 X 40 EN PROVISIONALES AEREOS | P23021600089 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 95 | 2023-02-16 | 7600 | keep | 0 | Feb | 2023 | 0.0051763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-16 14:05 | 2023-02-16 17:50 | 4 | 3:45 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN XMR SE REEMPLAZO BAJANTE PRIMARIO | B23021600106 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 225 | 2023-02-16 | 900 | keep | 0 | Feb | 2023 | 0.00061299 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2023-02-16 14:06 | 2023-02-16 18:08 | 25 | 4:02 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | R23021600033 | New_Event | Animals | Include | Include | Wildlife | 242 | 2023-02-16 | 6050 | keep | 0 | Feb | 2023 | 0.0041206 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-02-16 14:08 | 2023-02-16 17:00 | 30 | 2:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P23021600090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-02-16 | 5160 | keep | 0 | Feb | 2023 | 0.0035145 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-16 14:23 | 2023-02-16 16:39 | 15 | 2:16 | P | ANIMAL | 1 X 15 EN XMR CRUCE X IGUANA | B23021600101 | New_Event | Animals | Include | Include | Wildlife | 136 | 2023-02-16 | 2040 | keep | 0 | Feb | 2023 | 0.0013894 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-02-16 14:43 | 2023-02-16 16:20 | 30 | 1:37 | P | DESGANCHE | 1 X 30 EN C/L | C23021600294 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-02-16 | 2910 | keep | 0 | Feb | 2023 | 0.001982 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-02-16 14:44 | 2023-02-16 17:16 | 40 | 2:32 | P | DESGANCHE | 2 X 30 EN CL DESGANCHE | A23021600146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-02-16 | 6080 | keep | 0 | Feb | 2023 | 0.0041411 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-02-16 15:02 | 2023-02-16 17:31 | 50 | 2:29 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L CRUCE X GLOBOS | C23021600301 | New_Event | Damage From Public | Include | Include | Public | 149 | 2023-02-16 | 7450 | keep | 0 | Feb | 2023 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-16 15:10 | 2023-02-16 16:11 | 40 | 1:01 | P | OTRAS CAUSAS | SE CERRO EN EL SU - 11 @ SU - 2 SE QUEDO SIN CERRAR AL NORMALIZAR CARGAS | C23021600305 | New_Event | Other Causes | Include | Include | Other | 61 | 2023-02-16 | 2440 | keep | 0 | Feb | 2023 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-02-16 15:22 | 2023-02-16 18:02 | 6 | 2:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23021600241 | New_Event | Secondary Wire Break | Include | Include | Equipment | 160 | 2023-02-16 | 960 | keep | 0 | Feb | 2023 | 0.00065385 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-02-16 15:33 | 2023-02-16 18:23 | 30 | 2:50 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETIRO FASE PEGADA A TENSOR 1 X 65 EN CORTE DE LINEA | P23021600102 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 170 | 2023-02-16 | 5100 | keep | 0 | Feb | 2023 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-16 15:40 | 2023-02-16 16:20 | 60 | 0:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L VIENTOS | B23021600114 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 40 | 2023-02-16 | 2400 | keep | 0 | Feb | 2023 | 0.0016346 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-16 15:45 | 2023-02-16 18:21 | 78 | 2:36 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S23021600178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-02-16 | 12168 | keep | 0 | Feb | 2023 | 0.0082876 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
BARRANQUITAS | 2023-02-16 15:45 | 2023-02-16 17:37 | 7 | 1:52 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C23021600318 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 112 | 2023-02-16 | 784 | keep | 0 | Feb | 2023 | 0.00053398 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-02-16 15:46 | 2023-02-16 15:47 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-16 | 3070 | keep | 0 | Feb | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
HUMACAO | 2023-02-16 16:10 | 2023-02-16 17:55 | 10 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO Y SUBIO TAP 1 AL 3 QUEDO EN 122/244V | C23021600326 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2023-02-16 | 1050 | keep | 0 | Feb | 2023 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-16 16:13 | 2023-02-16 16:17 | 3 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23021600341 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-02-16 | 12 | keep | 0 | Feb | 2023 | 8.1731e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-16 16:19 | 2023-02-16 20:41 | 96 | 4:22 | P | DESGANCHE | 2 X 80 EN C/L Y 2 X 100 EN C/L DESGANCHE | S23021600186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2023-02-16 | 25152 | keep | 0 | Feb | 2023 | 0.017131 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
BAYAMON | 2023-02-16 16:32 | 2023-02-16 19:40 | 316 | 3:08 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 100 EN C/L SE DESENREDO LINEA CRUZADA SE CAMBIO CAJA PRIMARIA | B23021600128 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 188 | 2023-02-16 | 59408 | keep | 0 | Feb | 2023 | 0.040463 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
PONCE | 2023-02-16 16:43 | 2023-02-16 19:32 | 194 | 2:49 | P | DESGANCHE | DESGANCHE 2 X 80 EN CORTE DE LINEA | P23021600112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-02-16 | 32786 | keep | 0 | Feb | 2023 | 0.02233 | 0.00013213 | Sustained | FALSE | FALSE | Not_TMED_Event | 194
VEGA BAJA | 2023-02-16 16:52 | 2023-02-16 19:04 | 20 | 2:12 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23021600130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-02-16 | 2640 | keep | 0 | Feb | 2023 | 0.0017981 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-02-16 16:56 | 2023-02-16 18:25 | 125 | 1:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23021600268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-02-16 | 11125 | keep | 0 | Feb | 2023 | 0.0075772 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-02-16 17:10 | 2023-02-16 18:29 | 1 | 1:19 | P | NO SE REPORTO CAUSA | 2 X 100 EN RISER Y 1 X 50 EN BOVEDA DE PESCADERIA | S23021600196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2023-02-16 | 79 | keep | 0 | Feb | 2023 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-16 17:15 | 2023-02-16 20:02 | 20 | 2:47 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23021600133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-02-16 | 3340 | keep | 0 | Feb | 2023 | 0.0022749 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-02-16 17:21 | 2023-02-16 19:22 | 40 | 2:01 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A23021600158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-02-16 | 4840 | keep | 0 | Feb | 2023 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-02-16 17:24 | 2023-02-16 19:58 | 90 | 2:34 | P | DESGANCHE | 2 X 50 EN C/L | C23021600344 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-02-16 | 13860 | keep | 0 | Feb | 2023 | 0.00944 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2023-02-16 17:40 | 2023-02-16 17:58 | 15 | 0:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REMPLAZO BARRA PEDESTAL | R23021600048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 18 | 2023-02-16 | 270 | keep | 0 | Feb | 2023 | 0.0001839 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-02-16 17:49 | 2023-02-16 19:59 | 114 | 2:10 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L SE REPARO SECUNDARIA PERSONAL DE LIBERTY CRUZO LAS LINEAS | C23021600347 | New_Event | Damage From Public | Include | Include | Public | 130 | 2023-02-16 | 14820 | keep | 0 | Feb | 2023 | 0.010094 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
PONCE | 2023-02-16 17:58 | 2023-02-16 20:57 | 12 | 2:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | P23021600123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 179 | 2023-02-16 | 2148 | keep | 0 | Feb | 2023 | 0.001463 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-02-16 18:04 | 2023-02-17 01:20 | 80 | 7:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23021600283 | New_Event | Cutout Failure | Include | Include | Equipment | 436 | 2023-02-16 | 34880 | keep | 0 | Feb | 2023 | 0.023757 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-02-16 18:12 | 2023-02-16 19:32 | 10 | 1:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | A23021600163 | New_Event | Primary Wire Break | Include | Include | Equipment | 80 | 2023-02-16 | 800 | keep | 0 | Feb | 2023 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-16 18:19 | 2023-02-16 19:45 | 200 | 1:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021600290 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 86 | 2023-02-16 | 17200 | keep | 0 | Feb | 2023 | 0.011715 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-02-16 18:22 | 2023-02-16 19:58 | 3798 | 1:36 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE DESDE EL SUELO CON VARETA Y SE CERRO POR CONTROL | B23021600141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-02-16 | 364608 | keep | 0 | Feb | 2023 | 0.24833 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
MAYAGÃœEZ | 2023-02-16 18:42 | 2023-02-17 12:00 | 3 | 17:18 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR ROEDOR CRUZO LINEAS | M23021600297 | New_Event | Animals | Include | Include | Wildlife | 1038 | 2023-02-16 | 3114 | keep | 0 | Feb | 2023 | 0.0021209 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-02-16 19:03 | 2023-02-17 09:05 | 25 | 14:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23021600169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 842 | 2023-02-16 | 21050 | keep | 0 | Feb | 2023 | 0.014337 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-16 19:17 | 2023-02-16 22:37 | 100 | 3:20 | P | DESGANCHE | SE REEMPLAZO 2 RIGIDOS SE ELIMINO CRUZETA QUEMADA Y SE REALIZO DESGANCHE MASIVO | S23021600217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-02-16 | 20000 | keep | 0 | Feb | 2023 | 0.013622 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-02-16 20:31 | 2023-02-17 08:26 | 13 | 11:55 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C23021600361 | New_Event | Animals | Include | Include | Wildlife | 715 | 2023-02-16 | 9295 | keep | 0 | Feb | 2023 | 0.0063308 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2023-02-16 20:42 | 2023-02-17 08:47 | 6 | 12:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23021600177 | New_Event | Primary Wire Break | Include | Include | Equipment | 725 | 2023-02-16 | 4350 | keep | 0 | Feb | 2023 | 0.0029628 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-16 21:19 | 2023-02-17 13:33 | 10 | 16:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN CL | S23021600238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 974 | 2023-02-16 | 9740 | keep | 0 | Feb | 2023 | 0.0066339 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-02-16 21:24 | 2023-02-16 21:26 | 2826 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23021600368 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-16 | 5652 | keep | 0 | Feb | 2023 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
SAN JUAN | 2023-02-16 21:29 | 2023-02-17 00:10 | 1825 | 2:41 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE BKR SE PATRULLO Y SE DETERMINO QUE LA CAUSA FUE POR VIENTOS FUERTES SOBRE 17MPH SE CERRO POR CONTORL 100% EN SERVICIO | S23021600239 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 161 | 2023-02-16 | 293825 | keep | 0 | Feb | 2023 | 0.20012 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
VEGA BAJA | 2023-02-16 21:33 | 2023-02-17 01:40 | 3332 | 4:07 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE BKR SE REEMPLAZO AISLADOR EN LA SALIDA DEL ALIMENTADOR Y SE CERRO POR CONTROL | B23021600229 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 247 | 2023-02-16 | 823004 | keep | 0 | Feb | 2023 | 0.56054 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
BAYAMON | 2023-02-16 22:40 | 2023-02-17 00:09 | 50 | 1:29 | P | DESGANCHE | 1 X 50 Y 1 X 100 EN C/L DESGANCHE | B23021600256 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-02-16 | 4450 | keep | 0 | Feb | 2023 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-02-16 22:41 | 2023-02-17 01:44 | 151 | 3:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 100 Y 1 X 50 EN C/LS FUERTES VIENTOS | R23021600057 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 183 | 2023-02-16 | 27633 | keep | 0 | Feb | 2023 | 0.018821 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
FAJARDO | 2023-02-16 22:59 | 2023-02-16 23:00 | 956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23021600070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-16 | 956 | keep | 0 | Feb | 2023 | 0.00065113 | 0.00065113 | Momentary | FALSE | FALSE | Not_TMED_Event | 956
BAYAMON | 2023-02-16 23:01 | 2023-02-17 01:11 | 30 | 2:10 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23021600260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-02-16 | 3900 | keep | 0 | Feb | 2023 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-02-16 23:40 | 2023-02-17 00:50 | 100 | 1:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23021600183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-02-16 | 7000 | keep | 0 | Feb | 2023 | 0.0047677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-02-16 23:47 | 2023-02-17 09:15 | 50 | 9:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23021600184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 568 | 2023-02-16 | 28400 | keep | 0 | Feb | 2023 | 0.019343 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-17 00:02 | 2023-02-17 04:33 | 3 | 4:31 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XMR DESGANCHE | R23021700001 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 271 | 2023-02-17 | 813 | keep | 0 | Feb | 2023 | 0.00055373 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2023-02-17 00:50 | 2023-02-17 13:00 | 50 | 12:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23021600183 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 730 | 2023-02-17 | 36500 | keep | 0 | Feb | 2023 | 0.02486 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-02-17 01:02 | 2023-02-17 01:03 | 4085 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | R23021700004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-02-17 | 4085 | keep | 0 | Feb | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-02-17 01:03 | 2023-02-17 11:00 | 3 | 9:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23021700056 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 597 | 2023-02-17 | 1791 | keep | 0 | Feb | 2023 | 0.0012198 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-02-17 01:09 | 2023-02-17 01:13 | 2179 | 0:04 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO CERRADO X CONTROL | R23021700005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 4 | 2023-02-17 | 8716 | keep | 0 | Feb | 2023 | 0.0059364 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CAGUAS | 2023-02-17 01:12 | 2023-02-17 08:43 | 29 | 7:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C23021700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 451 | 2023-02-17 | 13079 | keep | 0 | Feb | 2023 | 0.008908 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CANOVANAS | 2023-02-17 01:13 | 2023-02-17 02:24 | 175 | 1:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L FUERTES VIENTOS | R23021700016 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2023-02-17 | 12425 | keep | 0 | Feb | 2023 | 0.0084626 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
CAGUAS | 2023-02-17 01:18 | 2023-02-17 09:52 | 13 | 8:34 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C23021700004 | New_Event | Animals | Include | Include | Wildlife | 514 | 2023-02-17 | 6682 | keep | 0 | Feb | 2023 | 0.0045511 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-02-17 01:45 | 2023-02-17 02:04 | 3332 | 0:19 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE BKR SE CERRO POR CONTROL PARA HACERLE PRUEBA | B23021600010 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 19 | 2023-02-17 | 63308 | keep | 0 | Feb | 2023 | 0.043119 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-02-17 02:00 | 2023-02-17 02:01 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23021700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-17 | 4132 | keep | 0 | Feb | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
VEGA BAJA | 2023-02-17 02:07 | 2023-02-17 02:36 | 3332 | 0:29 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE BKR SE TRANSFIRIO EL 60% DE LA CARGA AL 9001-02 | B23021600011 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 29 | 2023-02-17 | 96628 | keep | 0 | Feb | 2023 | 0.065813 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-02-17 02:31 | 2023-02-17 10:55 | 705 | 8:24 | T | ALIMENTADOR AMARRADO | SE RETIRO TENSOR SOBRE LAS LINEAS (8104-05) SE CERRO INTERRUPTOR PORTATIL EN LA SUBESTACION | A23021700004 | New_Event | Feeder Load Transferred | Include | Include | Other | 504 | 2023-02-17 | 355320 | keep | 0 | Feb | 2023 | 0.24201 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2023-02-17 02:31 | 2023-02-17 10:55 | 882 | 8:24 | T | CAUSAS EXTERNAS | SE RETIRO TENSOR SOBRE LAS LINEAS (8104-05) SE CERRO INTERRUPTOR PORTATIL EN LA SUBESTACION | A23021700004 | New_Event | Damage From Public | Include | Include | Public | 504 | 2023-02-17 | 444528 | keep | 0 | Feb | 2023 | 0.30277 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
SAN JUAN | 2023-02-17 02:36 | 2023-02-17 03:35 | 143 | 0:59 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR SE ABRIO N/O CONTRA EL 1404-07 QUE LLEVA EL 80% | S23021700008 | New_Event | Feeder Load Transferred | Include | Include | Other | 59 | 2023-02-17 | 8437 | keep | 0 | Feb | 2023 | 0.0057464 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-02-17 02:36 | 2023-02-17 04:16 | 1086 | 1:40 | P | DESGANCHE | DISPARO DE BKR 1404-06 LLEVA 80% DE 1404-07 SE SECICONALIZO PARA REALIZAR DESGANCHE | S23021700008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-02-17 | 108600 | keep | 0 | Feb | 2023 | 0.073967 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
VEGA BAJA | 2023-02-17 02:36 | 2023-02-17 04:04 | 1333 | 1:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO DISCO PARTIDO 100% EN SERVICIO | B23021600011 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 88 | 2023-02-17 | 117304 | keep | 0 | Feb | 2023 | 0.079895 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-02-17 02:40 | 2023-02-17 02:42 | 2826 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO CERRADO X CONTROL | C23021700005 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-02-17 | 5652 | keep | 0 | Feb | 2023 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
BARRANQUITAS | 2023-02-17 03:13 | 2023-02-17 03:15 | 2826 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO CERRADO X CONTROL | C23021700013 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2023-02-17 | 5652 | keep | 0 | Feb | 2023 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
CANOVANAS | 2023-02-17 03:20 | 2023-02-17 05:13 | 18 | 1:53 | P | DESGANCHE | 1 X 30 EN C/L | R23021700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-02-17 | 2034 | keep | 0 | Feb | 2023 | 0.0013853 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-02-17 03:50 | 2023-02-17 09:42 | 80 | 5:52 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA RATA CRUZO FASE | R23021700027 | New_Event | Animals | Include | Include | Wildlife | 352 | 2023-02-17 | 28160 | keep | 0 | Feb | 2023 | 0.01918 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-02-17 04:16 | 2023-02-17 04:54 | 218 | 0:38 | P | DESGANCHE | SE REALIZO DESGANCHE CON VARETA DEDE EL SUELO 100% EN SERVICIO | S23021700008 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 38 | 2023-02-17 | 8284 | keep | 0 | Feb | 2023 | 0.0056422 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 04:20 | 2023-02-17 14:30 | 23 | 10:10 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PARTIDO CON PROVISIONAL AEREO. IMPACTADO POR VEHICULO | B23021700019 | New_Event | Damage From Public | Include | Include | Public | 610 | 2023-02-17 | 14030 | keep | 0 | Feb | 2023 | 0.0095558 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-02-17 04:22 | 2023-02-17 11:28 | 20 | 7:06 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN EL TRONCAL | B23021700030 | New_Event | Primary Wire Break | Include | Include | Equipment | 426 | 2023-02-17 | 8520 | keep | 0 | Feb | 2023 | 0.0058029 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-02-17 05:15 | 2023-02-17 05:17 | 2216 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 60% DEL 9002-03 SE CERRO POR CONTROL | B23021700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-17 | 4432 | keep | 0 | Feb | 2023 | 0.0030186 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2023-02-17 05:15 | 2023-02-17 05:17 | 2000 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 9001-02 LLEVA 60% DEL 9002-03 SE CERRO POR CONTROL | B23021700020 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-17 | 4000 | keep | 0 | Feb | 2023 | 0.0027244 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
PONCE | 2023-02-17 05:40 | 2023-02-17 10:20 | 100 | 4:40 | P | TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CL AVERIA EN PROVISIONAL AEREO AL T-58 | P23021700010 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 280 | 2023-02-17 | 28000 | keep | 0 | Feb | 2023 | 0.019071 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-02-17 05:54 | 2023-02-17 06:29 | 1921 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO Y SE CERRO N/O CON 9703-02 | C23021700026 | New_Event | Primary Wire Break | Include | Include | Equipment | 35 | 2023-02-17 | 67235 | keep | 0 | Feb | 2023 | 0.045793 | 0.0013084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1921
VEGA BAJA | 2023-02-17 05:56 | 2023-02-17 15:34 | 25 | 9:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJAS PRIMARIAS AVERIADAS | A23021700012 | New_Event | Cutout Failure | Include | Include | Equipment | 578 | 2023-02-17 | 14450 | keep | 0 | Feb | 2023 | 0.0098418 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-17 06:14 | 2023-02-17 15:53 | 150 | 9:39 | P | DESGANCHE | 1 X 80 C/L Y 1 X 65 EN C/L DESGANCHE | S23021700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 579 | 2023-02-17 | 86850 | keep | 0 | Feb | 2023 | 0.059153 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-02-17 06:29 | 2023-02-17 08:48 | 32 | 2:19 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO FASE | R23021700034 | New_Event | Animals | Include | Include | Wildlife | 139 | 2023-02-17 | 4448 | keep | 0 | Feb | 2023 | 0.0030295 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BARRANQUITAS | 2023-02-17 06:29 | 2023-02-17 09:54 | 444 | 3:25 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO, SE CERRO MACHETES Y NORMALIZARON LAS CARGAS 100%EN SERVICIO | C23021700026 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 205 | 2023-02-17 | 91020 | keep | 0 | Feb | 2023 | 0.061993 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-17 06:32 | 2023-02-17 10:05 | 9189 | 3:33 | P | CONDUCTOR ROTO O ABIERTO | SJ-230217-02 SE SECCIONALIZO CONDUCTOR EN EL SUELO DEL 1204-05 Y SE CERRO N/O CONTRA 1206-04 ENTRANDO 80% EN SERVICIO QUEDANDO SOLO 5% DEL 1204-05 FUERA PARA SUBIR ALAMBRE | S23021700086 | New_Event | Primary Wire Break | Include | Include | Equipment | 213 | 2023-02-17 | 1957257 | keep | 0 | Feb | 2023 | 1.3331 | 0.0062586 | Sustained | FALSE | FALSE | Not_TMED_Event | 9189
SAN JUAN | 2023-02-17 06:32 | 2023-02-17 07:39 | 4133 | 1:07 | T | ALIMENTADOR AMARRADO | SJ-230217-02 SE SECCIONALIZO CONDUCTOR EN EL SUELO ABRIENDO N/O CONTRA EL 1204-05 Y SE CERRO POR SCADA 1206-03 ENTRANDO 100% EN SERVICIO Y DEJANDO FUERA EL 85% DEL 1204-05 QUE ESTABA TRANSFERIDO AL 1206-03 AL ESTE DISPARAR | S23021700086 | New_Event | Feeder Load Transferred | Include | Include | Other | 67 | 2023-02-17 | 276911 | keep | 0 | Feb | 2023 | 0.1886 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
VEGA BAJA | 2023-02-17 07:04 | 2023-02-17 14:00 | 8 | 6:56 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A23021700015 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 416 | 2023-02-17 | 3328 | keep | 0 | Feb | 2023 | 0.0022667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-02-17 07:20 | 2023-02-17 07:21 | 1342 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C2302170000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-17 | 1342 | keep | 0 | Feb | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2023-02-17 07:21 | 2023-02-17 17:15 | 32 | 9:54 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C23021700154 | 1st_after_momentary | Animals | Include | Include | Wildlife | 594 | 2023-02-17 | 19008 | keep | 0 | Feb | 2023 | 0.012946 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2023-02-17 07:29 | 2023-02-17 07:31 | 1681 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRRADO POR CONTROL LLEVA 1346-03 | S23021700023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-17 | 3362 | keep | 0 | Feb | 2023 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-02-17 07:29 | 2023-02-17 07:31 | 2422 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO CERRRADO POR CONTROL CARGA 1303-01 | S23021700023 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-17 | 4844 | keep | 0 | Feb | 2023 | 0.0032992 | 0.0016496 | Momentary | FALSE | FALSE | Not_TMED_Event | 2422
BAYAMON | 2023-02-17 07:42 | 2023-02-17 09:49 | 4 | 2:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA | B23021700030 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2023-02-17 | 508 | keep | 0 | Feb | 2023 | 0.000346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-02-17 07:43 | 2023-02-17 13:15 | 70 | 5:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23021700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 332 | 2023-02-17 | 23240 | keep | 0 | Feb | 2023 | 0.015829 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-02-17 08:05 | 2023-02-17 13:00 | 6 | 4:55 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REPARO SECUNDARIA Y SE DESGANCHO | S23021700216 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 295 | 2023-02-17 | 1770 | keep | 0 | Feb | 2023 | 0.0012055 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-02-17 08:11 | 2023-02-17 12:55 | 20 | 4:44 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | P23021700018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2023-02-17 | 5680 | keep | 0 | Feb | 2023 | 0.0038686 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-02-17 08:17 | 2023-02-17 12:15 | 25 | 3:58 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | P23021700019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-02-17 | 5950 | keep | 0 | Feb | 2023 | 0.0040525 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-02-17 08:35 | 2023-02-17 08:36 | 108 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23021700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-17 | 108 | keep | 0 | Feb | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2023-02-17 08:36 | 2023-02-17 14:00 | 100 | 5:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23021700035 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 324 | 2023-02-17 | 32400 | keep | 0 | Feb | 2023 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-02-17 09:01 | 2023-02-17 18:52 | 4 | 9:51 | P | DESGANCHE | SE REPARO BAJANTE LINEA A CAJA Y SE REALIZO DESPEJE PRIMARIO | B23021700039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 591 | 2023-02-17 | 2364 | keep | 0 | Feb | 2023 | 0.0016101 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-02-17 09:07 | 2023-02-17 21:45 | 40 | 12:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M23021700020 | New_Event | Primary Pole Failure | Include | Include | Equipment | 758 | 2023-02-17 | 30320 | keep | 0 | Feb | 2023 | 0.020651 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-02-17 09:28 | 2023-02-17 15:00 | 45 | 5:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTE BRISA | P23021700039 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 332 | 2023-02-17 | 14940 | keep | 0 | Feb | 2023 | 0.010176 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-02-17 09:37 | 2023-02-17 10:03 | 40 | 0:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR DESGANCHE | R23021700061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2023-02-17 | 1040 | keep | 0 | Feb | 2023 | 0.00070834 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-17 09:37 | 2023-02-17 12:45 | 2 | 3:08 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C23021700072 | New_Event | Animals | Include | Include | Wildlife | 188 | 2023-02-17 | 376 | keep | 0 | Feb | 2023 | 0.00025609 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-17 09:40 | 2023-02-17 13:50 | 100 | 4:10 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE LLEVO LINEA A AISLADOR | B23021700047 | New_Event | Primary Wire Break | Include | Include | Equipment | 250 | 2023-02-17 | 25000 | keep | 0 | Feb | 2023 | 0.017027 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-02-17 09:46 | 2023-02-17 10:57 | 20 | 1:11 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA IGUANA CRUZO FASE | R23021700063 | New_Event | Animals | Include | Include | Wildlife | 71 | 2023-02-17 | 1420 | keep | 0 | Feb | 2023 | 0.00096716 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-02-17 09:46 | 2023-02-17 13:02 | 60 | 3:16 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | P23021700042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-02-17 | 11760 | keep | 0 | Feb | 2023 | 0.0080097 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-02-17 09:54 | 2023-02-17 09:56 | 2826 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23021700080 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 2 | 2023-02-17 | 5652 | keep | 0 | Feb | 2023 | 0.0038496 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-02-17 09:56 | 2023-02-17 11:45 | 444 | 1:49 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO, SE CERRO MACHETES Y NORMALIZARON LAS CARGAS 100% EN SERVICIO | C23021700026 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 109 | 2023-02-17 | 48396 | keep | 0 | Feb | 2023 | 0.032962 | 0.00030241 | Sustained | FALSE | FALSE | Not_TMED_Event | 444
VEGA BAJA | 2023-02-17 09:59 | 2023-02-17 16:35 | 80 | 6:36 | P | DESGANCHE | 1 X 80 EN C/L Y 1 X 15 EN XMR SE REALIZO DESPEJE PRIMARIO | B23021700050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 396 | 2023-02-17 | 31680 | keep | 0 | Feb | 2023 | 0.021577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-02-17 10:02 | 2023-02-17 20:37 | 1105 | 10:35 | S | DESGANCHE | DISPARO DE LA SUBESTACION SE INFORMO QUE SE ENCONTRO PUENTES PRIMARIOS ABIERTOS Y SE REALIZO DESGANCHE EN OTRO PUNTO | A23021700057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 635 | 2023-02-17 | 701675 | keep | 0 | Feb | 2023 | 0.47791 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2023-02-17 10:05 | 2023-02-17 15:05 | 510 | 5:00 | P | CONDUCTOR ROTO O ABIERTO | SJ-230217-02 SE REPARO CONDUCTOR EN EL SUELO DEL 1204-05 Y SE NORMALIZO LAS CARGAS | S23021700086 | New_Event | Primary Wire Break | Include | Include | Equipment | 300 | 2023-02-17 | 153000 | keep | 0 | Feb | 2023 | 0.10421 | 0.00034736 | Sustained | FALSE | FALSE | Not_TMED_Event | 510
FAJARDO | 2023-02-17 10:05 | 2023-02-17 10:40 | 4 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R23021700066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-02-17 | 140 | keep | 0 | Feb | 2023 | 9.5353e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-17 10:07 | 2023-02-17 11:02 | 7 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23021700055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-02-17 | 385 | keep | 0 | Feb | 2023 | 0.00026222 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-02-17 10:10 | 2023-02-17 10:12 | 790 | 0:02 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | DISPARO CERRADO POR CONTROL | S23021700325 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2 | 2023-02-17 | 1580 | keep | 0 | Feb | 2023 | 0.0010761 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
MAYAGÃœEZ | 2023-02-17 10:10 | 2023-02-17 11:31 | 12 | 1:21 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A23021700039 | New_Event | Animals | Include | Include | Wildlife | 81 | 2023-02-17 | 972 | keep | 0 | Feb | 2023 | 0.00066202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-17 10:12 | 2023-02-17 11:12 | 158 | 1:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | POSTES PRIMARIOS PARTIDOS | S23021700377 | 1st_after_momentary | Primary Pole Failure | Include | Include | Equipment | 60 | 2023-02-17 | 9480 | keep | 0 | Feb | 2023 | 0.0064568 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
CAGUAS | 2023-02-17 10:15 | 2023-02-17 11:51 | 85 | 1:36 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | C23021700085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-02-17 | 8160 | keep | 0 | Feb | 2023 | 0.0055577 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BARRANQUITAS | 2023-02-17 10:17 | 2023-02-17 10:45 | 14 | 0:28 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REALIZAR DESGANCHE SECUNDARIO | C23021700087 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 28 | 2023-02-17 | 392 | keep | 0 | Feb | 2023 | 0.00026699 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-02-17 10:20 | 2023-02-17 16:24 | 45 | 6:04 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE CON EL GOI SJ-230217-50 | R23021700073 | New_Event | Primary Pole Failure | Include | Include | Equipment | 364 | 2023-02-17 | 16380 | keep | 0 | Feb | 2023 | 0.011156 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2023-02-17 10:20 | 2023-02-17 19:33 | 10 | 9:13 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION Y SE REEMPLAZO CAJA PRIMARIA EN RISER | P23021700059 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 553 | 2023-02-17 | 5530 | keep | 0 | Feb | 2023 | 0.0037665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-17 10:54 | 2023-02-17 16:16 | 50 | 5:22 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA EN C/L. | B23021700063 | New_Event | Primary Wire Break | Include | Include | Equipment | 322 | 2023-02-17 | 16100 | keep | 0 | Feb | 2023 | 0.010966 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-17 11:08 | 2023-02-17 13:54 | 24 | 2:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23021700124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-02-17 | 3984 | keep | 0 | Feb | 2023 | 0.0027135 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-02-17 11:12 | 2023-02-17 12:15 | 790 | 1:03 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230217-03 SE ABRE EL INTERRUPTOR PARA SECCIONALIZAR POSTES PRIMARIOS PARTIDOS. 80% 1519-02 EN SERVICIO | S23021700377 | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 63 | 2023-02-17 | 49770 | keep | 0 | Feb | 2023 | 0.033898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-02-17 11:12 | 2023-02-17 12:25 | 118 | 1:13 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | R23021700083 | New_Event | Animals | Include | Include | Wildlife | 73 | 2023-02-17 | 8614 | keep | 0 | Feb | 2023 | 0.005867 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
PONCE | 2023-02-17 11:15 | 2023-02-17 11:16 | 234 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR CON CARGA DEL 5817-02SE ENCONTRO DESGANCHE EN AMBOS ALIMENTADORES | P23021700067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-17 | 234 | keep | 0 | Feb | 2023 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2023-02-17 11:15 | 2023-02-17 11:16 | 2468 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR CON CARGA DEL 5817-02SE ENCONTRO PUNTOS DE DESGANCHE EN AMBOS ALIMENTADORES | P23021700067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-17 | 2468 | keep | 0 | Feb | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
AGUADILLA | 2023-02-17 11:17 | 2023-02-17 14:54 | 10 | 3:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE AJUSTO FUSIBLE SUELTO | M23021700055 | New_Event | Cutout Failure | Include | Include | Equipment | 217 | 2023-02-17 | 2170 | keep | 0 | Feb | 2023 | 0.001478 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 652 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 9128 | keep | 0 | Feb | 2023 | 0.006217 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2023-02-17 11:24 | 2023-02-17 11:38 | 2704 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 37856 | keep | 0 | Feb | 2023 | 0.025784 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 1526 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 21364 | keep | 0 | Feb | 2023 | 0.014551 | 0.0010394 | Sustained | FALSE | FALSE | Not_TMED_Event | 1526
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 308 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 4312 | keep | 0 | Feb | 2023 | 0.0029369 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 1397 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 19558 | keep | 0 | Feb | 2023 | 0.013321 | 0.00095149 | Sustained | FALSE | FALSE | Not_TMED_Event | 1397
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 2926 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 40964 | keep | 0 | Feb | 2023 | 0.0279 | 0.0019929 | Sustained | FALSE | FALSE | Not_TMED_Event | 2926
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 27 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 378 | keep | 0 | Feb | 2023 | 0.00025745 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 603 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 8442 | keep | 0 | Feb | 2023 | 0.0057498 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 6 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 84 | keep | 0 | Feb | 2023 | 5.7212e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 325 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 4550 | keep | 0 | Feb | 2023 | 0.003099 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-02-17 11:24 | 2023-02-17 11:38 | 172 | 0:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23021700090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-02-17 | 2408 | keep | 0 | Feb | 2023 | 0.0016401 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
PONCE | 2023-02-17 11:25 | 2023-02-17 11:26 | 234 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR CON CARGA DEL 5817-02SE ENCONTRO PUNTOS DE DESGANCHE EN AMBOS ALIMENTADORES | P23021700068 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-17 | 234 | keep | 0 | Feb | 2023 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2023-02-17 11:25 | 2023-02-17 11:26 | 2468 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR CON CARGA DEL 5817-02SE ENCONTRO PUNTOS DE DESGANCHE EN AMBOS ALIMENTADORES | P23021700068 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-17 | 2468 | keep | 0 | Feb | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
SAN JUAN | 2023-02-17 11:27 | 2023-02-17 16:48 | 12 | 5:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 75KVA POR UNO DE 75KVA | S23021700379 | New_Event | Service Transformer Failure | Include | Include | Equipment | 321 | 2023-02-17 | 3852 | keep | 0 | Feb | 2023 | 0.0026236 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-02-17 11:28 | 2023-02-17 11:29 | 234 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR CON CARGA DEL 5817-02 SE ENCONTRO PUNTOS DE DESGANCHE EN AMBOS ALIMENTADORES | P23021700070 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-17 | 234 | keep | 0 | Feb | 2023 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2023-02-17 11:28 | 2023-02-17 11:29 | 2468 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR CON CARGA DEL 5817-02 SE ENCONTRO DESGANCHE EN AMBOS ALIMENTADORES | P23021700070 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-17 | 2468 | keep | 0 | Feb | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
BAYAMON | 2023-02-17 11:29 | 2023-02-17 12:30 | 60 | 1:01 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO Y SE CERRO PUENTE ABIERTO EN EL TRONCAL | B23021700030 | New_Event | Primary Wire Break | Include | Include | Equipment | 61 | 2023-02-17 | 3660 | keep | 0 | Feb | 2023 | 0.0024928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-02-17 11:33 | 2023-02-17 11:34 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2302170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-17 | 3332 | keep | 0 | Feb | 2023 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
CAGUAS | 2023-02-17 11:34 | 2023-02-17 16:29 | 189 | 4:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C23021700134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2023-02-17 | 55755 | keep | 0 | Feb | 2023 | 0.037974 | 0.00012873 | Sustained | FALSE | FALSE | Not_TMED_Event | 189
GUAYAMA | 2023-02-17 11:45 | 2023-02-17 13:30 | 10 | 1:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DE TRANSFORMADOR T-4, 50KVA @ 2.4KV CON BUSHING SECUNDARIO AVERIADO | P23021700062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 105 | 2023-02-17 | 1050 | keep | 0 | Feb | 2023 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-02-17 11:45 | 2023-02-17 15:12 | 33 | 3:27 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR POSTE SECUNDARIO | M23021700151 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 207 | 2023-02-17 | 6831 | keep | 0 | Feb | 2023 | 0.0046526 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BARRANQUITAS | 2023-02-17 11:45 | 2023-02-17 11:46 | 2826 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR SE CERRO POR CONTROL | C23021700141 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-17 | 2826 | keep | 0 | Feb | 2023 | 0.0019248 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
BARRANQUITAS | 2023-02-17 11:46 | 2023-02-17 13:21 | 444 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO, SE CERRO MACHETES Y NORMALIZARON LAS CARGAS 100% EN SERVICIO | C23021700026 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 95 | 2023-02-17 | 42180 | keep | 0 | Feb | 2023 | 0.028729 | 0.00030241 | Sustained | FALSE | FALSE | Not_TMED_Event | 444
YAUCO | 2023-02-17 11:50 | 2023-02-17 17:35 | 85 | 5:45 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA EN EL PISO 1 X 80 1 X 65 EN SENDOS CORTES DE LINEA | P23021700076 | New_Event | Primary Wire Break | Include | Include | Equipment | 345 | 2023-02-17 | 29325 | keep | 0 | Feb | 2023 | 0.019973 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 652 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 EN SERVICIO LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700094 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 7824 | keep | 0 | Feb | 2023 | 0.0053289 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-17 12:04 | 2023-02-17 12:16 | 2704 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 EN SERVICIO LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700094 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 32448 | keep | 0 | Feb | 2023 | 0.0221 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 1526 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 EN SERVICIO LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRAMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700093 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 18312 | keep | 0 | Feb | 2023 | 0.012472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 308 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 EN SERVICIO LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700093 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 3696 | keep | 0 | Feb | 2023 | 0.0025173 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 1397 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 EN SERVICIO LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700093 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 16764 | keep | 0 | Feb | 2023 | 0.011418 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 2926 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 EN SERVICIO LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700093 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 35112 | keep | 0 | Feb | 2023 | 0.023915 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 27 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700090 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 324 | keep | 0 | Feb | 2023 | 0.00022067 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 603 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700090 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 7236 | keep | 0 | Feb | 2023 | 0.0049284 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 6 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700090 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 72 | keep | 0 | Feb | 2023 | 4.9039e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 325 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700090 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 3900 | keep | 0 | Feb | 2023 | 0.0026563 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 12:04 | 2023-02-17 12:16 | 172 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700090 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-17 | 2064 | keep | 0 | Feb | 2023 | 0.0014058 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-17 12:15 | 2023-02-17 13:40 | 158 | 1:25 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE CIERRA AMARRE CONTRA 1530-09 CON ALIMENTADOR SECCIONALIZADO POR POSTES PRIMARIOS PARTIDOS. 90% EN SERVICIO | S23021700377 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 85 | 2023-02-17 | 13430 | keep | 0 | Feb | 2023 | 0.0091471 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-17 12:15 | 2023-02-17 14:55 | 30 | 2:40 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA | M23021700065 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 160 | 2023-02-17 | 4800 | keep | 0 | Feb | 2023 | 0.0032693 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-02-17 12:15 | 2023-02-17 14:48 | 80 | 2:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23021700084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-02-17 | 12240 | keep | 0 | Feb | 2023 | 0.0083366 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-17 12:18 | 2023-02-17 15:10 | 160 | 2:52 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESPEJE DE LINEA | B23021700139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-02-17 | 27520 | keep | 0 | Feb | 2023 | 0.018744 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
MAYAGÃœEZ | 2023-02-17 12:21 | 2023-02-17 16:10 | 100 | 3:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M23021700069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-02-17 | 22900 | keep | 0 | Feb | 2023 | 0.015597 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-17 12:21 | 2023-02-17 17:38 | 93 | 5:17 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESPEJE DE LINEA | C23021700157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2023-02-17 | 29481 | keep | 0 | Feb | 2023 | 0.020079 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2023-02-17 12:27 | 2023-02-17 14:39 | 100 | 2:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M23021700075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-02-17 | 13200 | keep | 0 | Feb | 2023 | 0.0089905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-02-17 12:31 | 2023-02-17 17:08 | 80 | 4:37 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23021700081 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 277 | 2023-02-17 | 22160 | keep | 0 | Feb | 2023 | 0.015093 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-02-17 12:35 | 2023-02-17 12:36 | 1606 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERIVCIO | C23021700168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-17 | 1606 | keep | 0 | Feb | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2023-02-17 12:36 | 2023-02-17 13:47 | 26 | 1:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C23021700169 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-02-17 | 1846 | keep | 0 | Feb | 2023 | 0.0012573 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BAYAMON | 2023-02-17 12:41 | 2023-02-17 17:13 | 2 | 4:32 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR POSTE PRIMARIO Y TRANSFERIR LINEAS | B23021700157 | New_Event | Primary Pole Failure | Include | Include | Equipment | 272 | 2023-02-17 | 544 | keep | 0 | Feb | 2023 | 0.00037052 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-17 13:07 | 2023-02-17 15:49 | 15 | 2:42 | P | DESGANCHE | 1 X 15 EN XMR SE REALIZO DESPEJE PRIMARIO | B23021700175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-02-17 | 2430 | keep | 0 | Feb | 2023 | 0.0016551 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-17 13:07 | 2023-02-17 17:46 | 652 | 4:39 | S | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA DE SUBESTACION A PETICION DE CCE POR PUENTE ABIERTO EN LINEA 7800 | B23021700209 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 279 | 2023-02-17 | 181908 | keep | 0 | Feb | 2023 | 0.1239 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-17 13:07 | 2023-02-17 17:46 | 2704 | 4:39 | S | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA DE SUBESTACION A PETICION DE CCE POR PUENTE ABIERTO EN LINEA 7800 | B23021700209 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 279 | 2023-02-17 | 754416 | keep | 0 | Feb | 2023 | 0.51383 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-02-17 13:12 | 2023-02-17 15:40 | 50 | 2:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23021700105 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 148 | 2023-02-17 | 7400 | keep | 0 | Feb | 2023 | 0.0050401 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-02-17 13:37 | 2023-02-17 16:47 | 6 | 3:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23021700092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2023-02-17 | 1140 | keep | 0 | Feb | 2023 | 0.00077645 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-17 13:40 | 2023-02-17 14:40 | 79 | 1:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE PUENTES PRIMARIOS PARA ACABAR DE SECCIONALIZAR POSTES PRIMARIOS PARTIDOS Y SE CIERRA NACHETES 95% EN SERVICIO | S23021700377 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 60 | 2023-02-17 | 4740 | keep | 0 | Feb | 2023 | 0.0032284 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-02-17 13:45 | 2023-02-17 15:45 | 3 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23021700093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2023-02-17 | 360 | keep | 0 | Feb | 2023 | 0.00024519 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2023-02-17 13:48 | 2023-02-17 14:23 | 1 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN BANCO DE XMRS LEVANTO TEASER | R23021700102 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-02-17 | 35 | keep | 0 | Feb | 2023 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-17 13:49 | 2023-02-17 14:48 | 1219 | 0:59 | P | DESGANCHE | SE ABREN MACHETES PARA HACER DESGANCHE | P23021700102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-02-17 | 71921 | keep | 0 | Feb | 2023 | 0.048985 | 0.00083026 | Sustained | FALSE | FALSE | Not_TMED_Event | 1219
ARECIBO | 2023-02-17 13:50 | 2023-02-17 16:44 | 50 | 2:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | ABRIR CAJAS PARA REPARAR RISER SITUACION PELIGROSA | A23021700118 | New_Event | Cutout Failure | Include | Include | Equipment | 174 | 2023-02-17 | 8700 | keep | 0 | Feb | 2023 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-02-17 13:51 | 2023-02-17 17:15 | 60 | 3:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23021700097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 204 | 2023-02-17 | 12240 | keep | 0 | Feb | 2023 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-02-17 13:59 | 2023-02-17 15:33 | 54 | 1:34 | P | DESGANCHE | 1 X 65 EN C/L | C23021700104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-02-17 | 5076 | keep | 0 | Feb | 2023 | 0.0034572 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
AGUADILLA | 2023-02-17 14:05 | 2023-02-17 17:45 | 100 | 3:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA CAJA DEFECTUOSA | M23021700119 | New_Event | Cutout Failure | Include | Include | Equipment | 220 | 2023-02-17 | 22000 | keep | 0 | Feb | 2023 | 0.014984 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-02-17 14:06 | 2023-02-17 14:07 | 1084 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23021700200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-17 | 1084 | keep | 0 | Feb | 2023 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
CAGUAS | 2023-02-17 14:07 | 2023-02-17 16:15 | 9 | 2:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA EN TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C23021700203 | New_Event | Secondary Wire Break | Include | Include | Equipment | 128 | 2023-02-17 | 1152 | keep | 0 | Feb | 2023 | 0.00078462 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-02-17 14:10 | 2023-02-17 14:11 | 74 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1521-02 QUE LLEVA 1912-07 | S2302170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-17 | 74 | keep | 0 | Feb | 2023 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2023-02-17 14:10 | 2023-02-17 14:11 | 57 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE 1521-02 QUE LLEVA 1912-07 | S2302170000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-17 | 57 | keep | 0 | Feb | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-02-17 14:23 | 2023-02-17 14:41 | 1526 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700220 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2023-02-17 | 27468 | keep | 0 | Feb | 2023 | 0.018708 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:23 | 2023-02-17 14:41 | 308 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700220 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2023-02-17 | 5544 | keep | 0 | Feb | 2023 | 0.003776 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:23 | 2023-02-17 14:41 | 1397 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700220 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2023-02-17 | 25146 | keep | 0 | Feb | 2023 | 0.017127 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:23 | 2023-02-17 14:41 | 2926 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700220 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2023-02-17 | 52668 | keep | 0 | Feb | 2023 | 0.035872 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:23 | 2023-02-17 14:41 | 27 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700221 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2023-02-17 | 486 | keep | 0 | Feb | 2023 | 0.00033101 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:23 | 2023-02-17 14:41 | 603 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700221 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2023-02-17 | 10854 | keep | 0 | Feb | 2023 | 0.0073926 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:23 | 2023-02-17 14:41 | 6 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700221 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2023-02-17 | 108 | keep | 0 | Feb | 2023 | 7.3558e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:23 | 2023-02-17 14:41 | 325 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700221 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2023-02-17 | 5850 | keep | 0 | Feb | 2023 | 0.0039844 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:23 | 2023-02-17 14:41 | 172 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13200 LINEA 13200 ENLAZADA CON LINEA 7800 POR VIA LIBRE PROGRMADA BARRA 38KV DORADO TC PUENTES ABIERTOS EN LINEA 7800 | B23021700221 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2023-02-17 | 3096 | keep | 0 | Feb | 2023 | 0.0021087 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:29 | 2023-02-17 16:48 | 106 | 2:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REEMPLAZO AISLADOR | B23021700223 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 139 | 2023-02-17 | 14734 | keep | 0 | Feb | 2023 | 0.010035 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
BAYAMON | 2023-02-17 14:33 | 2023-02-17 17:19 | 17 | 2:46 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESPEJE DE LINEA | B23021700225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-02-17 | 2822 | keep | 0 | Feb | 2023 | 0.0019221 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-02-17 14:40 | 2023-02-18 13:49 | 40 | 23:09 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE MACHETES DE AMARRE CONTRA 1530-09 PARA PODER LEVANTAR Y ENCABEZAR TRAMO DE ALAMBRE PRIMARIO FALTANTE. INTERRUPCION AUMENTA A 15% | S23021700377 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1389 | 2023-02-17 | 55560 | keep | 0 | Feb | 2023 | 0.037842 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-17 14:40 | 2023-02-17 16:38 | 6 | 1:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L SE REPORTA MAL TIEMPO EN LA ZONA | B23021700230 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2023-02-17 | 708 | keep | 0 | Feb | 2023 | 0.00048222 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-02-17 14:41 | 2023-02-17 16:19 | 846 | 1:38 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO Y SE CERRO CORTE DE LINEA | C23021700021 | New_Event | Primary Wire Break | Include | Include | Equipment | 98 | 2023-02-17 | 82908 | keep | 0 | Feb | 2023 | 0.056468 | 0.00057621 | Sustained | FALSE | FALSE | Not_TMED_Event | 846
UTUADO | 2023-02-17 14:43 | 2023-02-17 16:50 | 1 | 2:07 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23021700111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2023-02-17 | 127 | keep | 0 | Feb | 2023 | 8.6499e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-17 14:46 | 2023-02-17 16:05 | 21 | 1:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN TRANSFORMADOR FUERTE VIENTO | P23021700110 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 79 | 2023-02-17 | 1659 | keep | 0 | Feb | 2023 | 0.0011299 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CANOVANAS | 2023-02-17 15:12 | 2023-02-17 15:37 | 2675 | 0:25 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL SE VERIFICO PERSONAL FUERA | R23021700111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2023-02-17 | 66875 | keep | 0 | Feb | 2023 | 0.045548 | 0.0018219 | Sustained | FALSE | FALSE | Not_TMED_Event | 2675
FAJARDO | 2023-02-17 15:13 | 2023-02-18 00:45 | 40 | 9:32 | P | CAUSAS EXTERNAS | ABRIO C/L PARA REMPLAZAR POSTE PARTIDO POR CAMION | R23021700110 | New_Event | Damage From Public | Include | Include | Public | 572 | 2023-02-17 | 22880 | keep | 0 | Feb | 2023 | 0.015583 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-02-17 15:17 | 2023-02-17 16:55 | 30 | 1:38 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23021700141 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 98 | 2023-02-17 | 2940 | keep | 0 | Feb | 2023 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-17 15:20 | 2023-02-17 18:22 | 15 | 3:02 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE CERRO C/L | S23021700428 | New_Event | Primary Wire Break | Include | Include | Equipment | 182 | 2023-02-17 | 2730 | keep | 0 | Feb | 2023 | 0.0018594 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-02-17 15:28 | 2023-02-17 18:56 | 10 | 3:28 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C23021700239 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 208 | 2023-02-17 | 2080 | keep | 0 | Feb | 2023 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-17 15:29 | 2023-02-17 15:31 | 2466 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | B2302170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-17 | 4932 | keep | 0 | Feb | 2023 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
CANOVANAS | 2023-02-17 15:51 | 2023-02-17 17:00 | 20 | 1:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L PORTAFUSIBLE QUEMADO | R23021700119 | New_Event | Cutout Failure | Include | Include | Equipment | 69 | 2023-02-17 | 1380 | keep | 0 | Feb | 2023 | 0.00093991 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-02-17 15:53 | 2023-02-17 20:51 | 50 | 4:58 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23021700438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2023-02-17 | 14900 | keep | 0 | Feb | 2023 | 0.010148 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-17 15:59 | 2023-02-17 16:00 | 551 | 0:01 | T | ANIMAL | RECIERRE | C23021700247 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-17 | 551 | keep | 0 | Feb | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2023-02-17 16:00 | 2023-02-17 19:30 | 8 | 3:30 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR PALOMA | C23021700252 | 1st_after_momentary | Animals | Include | Include | Wildlife | 210 | 2023-02-17 | 1680 | keep | 0 | Feb | 2023 | 0.0011442 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-17 16:23 | 2023-02-17 21:33 | 30 | 5:10 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S23021700444 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 310 | 2023-02-17 | 9300 | keep | 0 | Feb | 2023 | 0.0063342 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-17 16:25 | 2023-02-17 19:07 | 126 | 2:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR | S23021700446 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 162 | 2023-02-17 | 20412 | keep | 0 | Feb | 2023 | 0.013903 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
MAYAGÃœEZ | 2023-02-17 16:30 | 2023-02-17 18:05 | 25 | 1:35 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23021700163 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 95 | 2023-02-17 | 2375 | keep | 0 | Feb | 2023 | 0.0016176 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-17 17:02 | 2023-02-18 01:36 | 12 | 8:34 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO Y REPARO SECUNDARIA | B23021700281 | New_Event | Primary Pole Failure | Include | Include | Equipment | 514 | 2023-02-17 | 6168 | keep | 0 | Feb | 2023 | 0.004201 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-02-17 17:18 | 2023-02-17 17:20 | 863 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M23021700173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-17 | 1726 | keep | 0 | Feb | 2023 | 0.0011756 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2023-02-17 17:32 | 2023-02-17 20:59 | 30 | 3:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23021700467 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 207 | 2023-02-17 | 6210 | keep | 0 | Feb | 2023 | 0.0042296 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-02-17 17:39 | 2023-02-17 19:30 | 136 | 1:51 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE SAFADO EN CORTE DE LINEA | P23021700145 | New_Event | Primary Wire Break | Include | Include | Equipment | 111 | 2023-02-17 | 15096 | keep | 0 | Feb | 2023 | 0.010282 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
VEGA BAJA | 2023-02-17 18:23 | 2023-02-17 19:35 | 80 | 1:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L VIENTO FUERTE | B23021700300 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 72 | 2023-02-17 | 5760 | keep | 0 | Feb | 2023 | 0.0039231 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-02-17 18:33 | 2023-02-17 21:15 | 6 | 2:42 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO RAMA | A23021700153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-02-17 | 972 | keep | 0 | Feb | 2023 | 0.00066202 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-02-17 18:33 | 2023-02-17 19:31 | 8 | 0:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN XMR | B23021700299 | New_Event | Cutout Failure | Include | Include | Equipment | 58 | 2023-02-17 | 464 | keep | 0 | Feb | 2023 | 0.00031603 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-02-17 18:54 | 2023-02-17 20:05 | 12 | 1:11 | P | OTRAS CAUSAS | 1 X 15 EN XMR FUSIBLE FATIGADO | R23021700132 | New_Event | Other Causes | Include | Include | Other | 71 | 2023-02-17 | 852 | keep | 0 | Feb | 2023 | 0.00058029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-02-17 18:57 | 2023-02-17 20:50 | 835 | 1:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 200 EN CORTE DE LINEA | P23021700155 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2023-02-17 | 94355 | keep | 0 | Feb | 2023 | 0.064265 | 0.00056871 | Sustained | FALSE | FALSE | Not_TMED_Event | 835
SAN JUAN | 2023-02-17 19:14 | 2023-02-17 19:25 | 12 | 0:11 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 100 EN C/L POSTE PARTIDO OCASIONO CRUCE DE LINEAS SE ASEGURO POSTE Y SE DIO SERVICIO | S23021700479 | New_Event | Primary Pole Failure | Include | Include | Equipment | 11 | 2023-02-17 | 132 | keep | 0 | Feb | 2023 | 8.9905e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-02-17 19:17 | 2023-02-17 21:20 | 21 | 2:03 | P | CAUSAS EXTERNAS | SE SECCIONALIZO POSTE PRIMARIO PARTIDO POR CAMION CG-230217-02 | C23021700263 | New_Event | Damage From Public | Include | Include | Public | 123 | 2023-02-17 | 2583 | keep | 0 | Feb | 2023 | 0.0017593 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
AGUADILLA | 2023-02-17 19:23 | 2023-02-17 21:21 | 10 | 1:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23021700194 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2023-02-17 | 1180 | keep | 0 | Feb | 2023 | 0.00080369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-17 19:45 | 2023-02-17 19:47 | 1746 | 0:02 | P | TERMINACION SOTERRADA AVERIADA | DISPARO CERRADO X CONTROL 15% X 1646-03 | R23021700132 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 2 | 2023-02-17 | 3492 | keep | 0 | Feb | 2023 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
CANOVANAS | 2023-02-17 19:47 | 2023-02-17 22:03 | 15 | 2:16 | P | TERMINACION SOTERRADA AVERIADA | 1 X 30 C/L LIMPIO TERMINACION | R23021700139 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 136 | 2023-02-17 | 2040 | keep | 0 | Feb | 2023 | 0.0013894 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-02-17 20:12 | 2023-02-17 21:16 | 434 | 1:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO NADA | P23021700210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2023-02-17 | 27776 | keep | 0 | Feb | 2023 | 0.018918 | 0.0002956 | Sustained | FALSE | FALSE | Not_TMED_Event | 434
YAUCO | 2023-02-17 20:31 | 2023-02-17 22:50 | 125 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 40 EN CORTES DE LINEA MAL TIEMPO VIENTOS FUERTES | P23021700205 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-02-17 | 17375 | keep | 0 | Feb | 2023 | 0.011834 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2023-02-17 20:37 | 2023-02-17 20:46 | 612 | 0:09 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO MACHETES (FID:33776403) QUE SE ABRIO PARA SECCIONALIZAR Y PODER ENERGIZAR LA SUBESTACION 8005 NO SE PIDIO ORDENES PARA ABRIR MACHETES | A23021700057 | New_Event | Primary Wire Break | Include | Include | Equipment | 9 | 2023-02-17 | 5508 | keep | 0 | Feb | 2023 | 0.0037515 | 0.00041683 | Sustained | FALSE | FALSE | Not_TMED_Event | 612
GUAYAMA | 2023-02-17 20:43 | 2023-02-18 09:04 | 5 | 12:21 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23021700214 | New_Event | Primary Wire Break | Include | Include | Equipment | 741 | 2023-02-17 | 3705 | keep | 0 | Feb | 2023 | 0.0025235 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-02-17 20:50 | 2023-02-17 20:51 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A23021700165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-17 | 308 | keep | 0 | Feb | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-02-17 20:51 | 2023-02-17 22:29 | 15 | 1:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN PROVISIONAL AEREO VIENTOS FUERTES | B23021700314 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 98 | 2023-02-17 | 1470 | keep | 0 | Feb | 2023 | 0.0010012 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-02-17 21:20 | 2023-02-18 11:24 | 24 | 14:04 | P | CAUSAS EXTERNAS | SE TRANSFIRIO LA CARGA A OTRO XMR QUE ESTABA ENERGIZADO, SE DEJO SECCIONALIZADO POSTE PRIMARIO PARTIDO | C23021700263 | Additional_clients | Damage From Public | Include | Include | Public | 844 | 2023-02-17 | 20256 | keep | 0 | Feb | 2023 | 0.013796 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-02-17 21:36 | 2023-02-18 14:18 | 6 | 16:42 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CL BAJANTE PRIMARIO CRUZANDO CON NEUTRAL | P23021700217 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1002 | 2023-02-17 | 6012 | keep | 0 | Feb | 2023 | 0.0040947 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-02-17 21:45 | 2023-02-18 06:45 | 500 | 9:00 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTELIRRUPTER (17347990) SE REPARO LINEA PRIMARIA | M23021700212 | New_Event | Primary Wire Break | Include | Include | Equipment | 540 | 2023-02-17 | 270000 | keep | 0 | Feb | 2023 | 0.1839 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2023-02-17 22:13 | 2023-02-17 23:37 | 20 | 1:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER SE REEMPLAZO PORTAFUSIBLE QUEMADO | B23021700316 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2023-02-17 | 1680 | keep | 0 | Feb | 2023 | 0.0011442 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-02-17 22:30 | 2023-02-18 08:54 | 6 | 10:24 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | B23021700319 | New_Event | Vegetation Contact | Include | Include | Vegetation | 624 | 2023-02-17 | 3744 | keep | 0 | Feb | 2023 | 0.00255 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-02-17 23:10 | 2023-02-17 23:12 | 1937 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R23021700156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-17 | 3874 | keep | 0 | Feb | 2023 | 0.0026386 | 0.0013193 | Momentary | FALSE | FALSE | Not_TMED_Event | 1937
YAUCO | 2023-02-17 23:13 | 2023-02-18 11:43 | 50 | 12:30 | P | DESGANCHE | 3 X 40 EN C/L DESGANCHE | P23021700221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 750 | 2023-02-17 | 37500 | keep | 0 | Feb | 2023 | 0.025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-02-17 23:40 | 2023-02-18 08:20 | 4 | 8:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN TRANSFORMADOR FUERTE VIENTO | P23021700222 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 520 | 2023-02-17 | 2080 | keep | 0 | Feb | 2023 | 0.0014167 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-02-18 02:13 | 2023-02-18 16:42 | 8 | 14:29 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M23021800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 869 | 2023-02-18 | 6952 | keep | 0 | Feb | 2023 | 0.004735 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-02-18 02:46 | 2023-02-18 02:48 | 3387 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23021800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-18 | 6774 | keep | 0 | Feb | 2023 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
SAN JUAN | 2023-02-18 03:03 | 2023-02-18 10:31 | 20 | 7:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE REPARO SEC AVERIADA | S23021800001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 448 | 2023-02-18 | 8960 | keep | 0 | Feb | 2023 | 0.0061026 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-02-18 03:18 | 2023-02-18 03:19 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-18 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
CANOVANAS | 2023-02-18 04:31 | 2023-02-18 09:14 | 70 | 4:43 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R23021800003 | New_Event | Animals | Include | Include | Wildlife | 283 | 2023-02-18 | 19810 | keep | 0 | Feb | 2023 | 0.013493 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-02-18 04:59 | 2023-02-18 06:15 | 150 | 1:16 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23021800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-02-18 | 11400 | keep | 0 | Feb | 2023 | 0.0077645 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-02-18 05:06 | 2023-02-18 05:07 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302180000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-18 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-02-18 05:08 | 2023-02-18 05:09 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302180000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-18 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
BAYAMON | 2023-02-18 06:18 | 2023-02-18 06:19 | 3798 | 0:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23021800004 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-18 | 3798 | keep | 0 | Feb | 2023 | 0.0025868 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-18 06:19 | 2023-02-18 09:20 | 150 | 3:01 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23021800002 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-02-18 | 27150 | keep | 0 | Feb | 2023 | 0.018492 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-02-18 07:46 | 2023-02-18 07:47 | 2675 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | RECIERRE | R23021800005 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1 | 2023-02-18 | 2675 | keep | 0 | Feb | 2023 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
VEGA BAJA | 2023-02-18 08:14 | 2023-02-18 11:46 | 4 | 3:32 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR POR TRANSFORMADOR AVERIADO DURA POCO TIEMPO INFORMAN QUE LO CAMBIARAN | A23021800006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 212 | 2023-02-18 | 848 | keep | 0 | Feb | 2023 | 0.00057757 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-18 08:14 | 2023-02-18 13:18 | 10 | 5:04 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR DESGANCHE SECUNDARIO | B23021800007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 304 | 2023-02-18 | 3040 | keep | 0 | Feb | 2023 | 0.0020705 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-18 08:15 | 2023-02-18 08:18 | 2234 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23021800006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-18 | 6702 | keep | 0 | Feb | 2023 | 0.0045647 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
PONCE | 2023-02-18 09:00 | 2023-02-18 11:58 | 36 | 2:58 | P | TERMINACION SOTERRADA AVERIADA | XMR ARQUEANDO EN TERMINACION DE PM SE REMPLAZO TERMENACIONES PREVENTIVAMENTE | P23021800013 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 178 | 2023-02-18 | 6408 | keep | 0 | Feb | 2023 | 0.0043645 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2023-02-18 09:20 | 2023-02-18 11:30 | 8 | 2:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M23021700227 | New_Event | Secondary Wire Break | Include | Include | Equipment | 130 | 2023-02-18 | 1040 | keep | 0 | Feb | 2023 | 0.00070834 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-18 09:20 | 2023-02-18 11:35 | 116 | 2:15 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23021800011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-02-18 | 15660 | keep | 0 | Feb | 2023 | 0.010666 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
BAYAMON | 2023-02-18 09:27 | 2023-02-18 12:32 | 2 | 3:05 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE REPARO EL BAJANTE DE CAJA A XMR | B23021800012 | New_Event | Primary Wire Break | Include | Include | Equipment | 185 | 2023-02-18 | 370 | keep | 0 | Feb | 2023 | 0.00025201 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-02-18 09:35 | 2023-02-18 12:40 | 20 | 3:05 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE | A23021800010 | New_Event | Primary Pole Failure | Include | Include | Equipment | 185 | 2023-02-18 | 3700 | keep | 0 | Feb | 2023 | 0.0025201 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-02-18 09:37 | 2023-02-18 10:04 | 17 | 0:27 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R23021800034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2023-02-18 | 459 | keep | 0 | Feb | 2023 | 0.00031262 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-02-18 10:00 | 2023-02-18 11:25 | 10 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIAY SE REALIZO DESGANCHE | B23021700276 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2023-02-18 | 850 | keep | 0 | Feb | 2023 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-18 10:06 | 2023-02-18 14:28 | 1 | 4:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50 KVA X 50 KVA | S23021800016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 262 | 2023-02-18 | 262 | keep | 0 | Feb | 2023 | 0.00017845 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-18 10:09 | 2023-02-18 16:05 | 8 | 5:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES SECUNDARIOS | S23021800022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 356 | 2023-02-18 | 2848 | keep | 0 | Feb | 2023 | 0.0019398 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-02-18 10:10 | 2023-02-18 14:45 | 40 | 4:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M23021800033 | New_Event | Cutout Failure | Include | Include | Equipment | 275 | 2023-02-18 | 11000 | keep | 0 | Feb | 2023 | 0.007492 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-18 10:10 | 2023-02-18 16:21 | 8 | 6:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN XMR SE REMPLAZO CAJA PRIMARIA | B23021800019 | New_Event | Cutout Failure | Include | Include | Equipment | 371 | 2023-02-18 | 2968 | keep | 0 | Feb | 2023 | 0.0020215 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-18 10:18 | 2023-02-18 11:44 | 20 | 1:26 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23021800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-02-18 | 1720 | keep | 0 | Feb | 2023 | 0.0011715 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-18 10:38 | 2023-02-18 10:40 | 1879 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 3006-02 LLEVA LA CARGA DEL 3006-05 SE CERRO POR CONTROL | C2302180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-18 | 3758 | keep | 0 | Feb | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-02-18 10:38 | 2023-02-18 10:40 | 3005 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 3006-02 LLEVA LA CARGA DEL 3006-05 SE CERRO POR CONTROL | C2302180000X | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-02-18 | 6010 | keep | 0 | Feb | 2023 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2023-02-18 10:40 | 2023-02-18 10:56 | 500 | 0:16 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO EN EL SUELO | C2302180000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 16 | 2023-02-18 | 8000 | keep | 0 | Feb | 2023 | 0.0054488 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
FAJARDO | 2023-02-18 10:55 | 2023-02-18 11:30 | 60 | 0:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R23021800049 | New_Event | Cutout Failure | Include | Include | Equipment | 35 | 2023-02-18 | 2100 | keep | 0 | Feb | 2023 | 0.0014303 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-02-18 10:56 | 2023-02-18 11:54 | 1879 | 0:58 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR 3006-02 QUE LLEVA EL 3006-05 POR CONDUCTOR PRIMARIO EN EL SUELO A CONSECUENCIA DE UN DESGANCHE DE BAMBUAS REALIZADO POR PERSONAS AJENAS A LUMA.. ENTRO 100% EL 3006-02 Y 50% DEL 3006-05 CG-230218-01 | C23021800091 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 58 | 2023-02-18 | 108982 | keep | 0 | Feb | 2023 | 0.074227 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-02-18 10:56 | 2023-02-18 11:54 | 3005 | 0:58 | T | CAUSAS EXTERNAS | SE ABRIO INTERRUPTOR 3006-02 QUE LLEVA EL 3006-05 POR CONDUCTOR PRIMARIO EN EL SUELO A CONSECUENCIA DE UN DESGANCHE DE BAMBUAS REALIZADO POR PERSONAS AJENAS A LUMA. ENTRO 100% EL 3006-02 Y 50% DEL 3006-05 CG-230218-01 | C23021800091 | New_Event | Damage From Public | Include | Include | Public | 58 | 2023-02-18 | 174290 | keep | 0 | Feb | 2023 | 0.11871 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2023-02-18 10:59 | 2023-02-18 12:00 | 10 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23021800044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2023-02-18 | 610 | keep | 0 | Feb | 2023 | 0.00041547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-02-18 11:01 | 2023-02-18 12:15 | 12 | 1:14 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA REEMPLAZO DE BARRAS EN PEDESTAL Y PEDESTAL | B23021800022 | New_Event |  |  |  |  | 74 | 2023-02-18 | 888 | keep | 0 | Feb | 2023 | 0.00060481 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-18 11:42 | 2023-02-18 13:02 | 25 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON LAS CONEXIONES SECUNDARIAS | S23021800026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-02-18 | 2000 | keep | 0 | Feb | 2023 | 0.0013622 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-02-18 11:46 | 2023-02-18 14:19 | 10 | 2:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA VERIFCADO EN OMS EVENTO CREADO EN VEGA BAJA | B23021800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-02-18 | 1530 | keep | 0 | Feb | 2023 | 0.0010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-18 11:54 | 2023-02-18 21:35 | 1488 | 9:41 | P | CAUSAS EXTERNAS | SE REPARO CONDUCTOR EN EL SUELO Y SE CERRO MACHETE MEDIANTE CG-230218-01 | C23021800091 | Partial_restoration | Damage From Public | Include | Include | Public | 581 | 2023-02-18 | 864528 | keep | 0 | Feb | 2023 | 0.58883 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-18 12:34 | 2023-02-18 14:46 | 1483 | 2:12 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ARBOL CRUZANDO LINEAS Y PUENTE PRIMARIO ABIERTO. SE CERRO N/O CONTRA 1206-04. EN SERVICIO 80% 1303-02 Y 30% 1204-04 | S23021800051 | New_Event | Feeder Load Transferred | Include | Include | Other | 132 | 2023-02-18 | 195756 | keep | 0 | Feb | 2023 | 0.13333 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-02-18 12:34 | 2023-02-18 14:46 | 2435 | 2:12 | T | ARBOL SOBRE LINEA | SE SECCIONALIZO ARBOL CRUZANDO LINEAS Y PUENTE PRIMARIO ABIERTO. SE CERRO N/O CONTRA 1206-04. EN SERVICIO 80% 1303-02 Y 30% 1204-04 | S23021800051 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 132 | 2023-02-18 | 321420 | keep | 0 | Feb | 2023 | 0.21892 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-02-18 12:37 | 2023-02-18 12:38 | 1243 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE BKR 1204-01 LLEVA 90% 1204-03 | S2302180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-18 | 1243 | keep | 0 | Feb | 2023 | 0.0008466 | 0.0008466 | Momentary | FALSE | FALSE | Not_TMED_Event | 1243
UTUADO | 2023-02-18 12:45 | 2023-02-18 16:24 | 1 | 3:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A23021800021 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 219 | 2023-02-18 | 219 | keep | 0 | Feb | 2023 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-18 12:47 | 2023-02-18 16:00 | 60 | 3:13 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M23021800055 | New_Event | Primary Wire Break | Include | Include | Equipment | 193 | 2023-02-18 | 11580 | keep | 0 | Feb | 2023 | 0.0078871 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-02-18 12:56 | 2023-02-18 15:22 | 17 | 2:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR | C23021800094 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 146 | 2023-02-18 | 2482 | keep | 0 | Feb | 2023 | 0.0016905 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2023-02-18 13:03 | 2023-02-18 18:32 | 478 | 5:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y SE REMPLAZO PORTAFUSIBLE | C23021800097 | New_Event | Cutout Failure | Include | Include | Equipment | 329 | 2023-02-18 | 157262 | keep | 0 | Feb | 2023 | 0.10711 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2023-02-18 13:03 | 2023-02-18 13:04 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23021800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-18 | 325 | keep | 0 | Feb | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CANOVANAS | 2023-02-18 13:21 | 2023-02-18 13:32 | 2675 | 0:11 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | R23021800068 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 11 | 2023-02-18 | 29425 | keep | 0 | Feb | 2023 | 0.020041 | 0.0018219 | Sustained | FALSE | FALSE | Not_TMED_Event | 2675
VEGA BAJA | 2023-02-18 13:22 | 2023-02-18 13:59 | 1 | 0:37 | P | PROBLEMA DEL CLIENTE | 1X30 EN GABINETE DE ELLOS POR CONTAMINACION EN FACILIDADES PRIVADAS SE ORIENTO AL CLIENTE | B23021800024 | New_Event | Customer-Related Interruption | Include | Include | Public | 37 | 2023-02-18 | 37 | keep | 0 | Feb | 2023 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-02-18 13:36 | 2023-02-18 16:03 | 20 | 2:27 | P | NO SE REPORTO CAUSA | 1 X 25 EN CONVERTIDOR NO SE REPORTO CAUSA | A23021800025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2023-02-18 | 2940 | keep | 0 | Feb | 2023 | 0.0020024 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-18 13:43 | 2023-02-18 15:09 | 1 | 1:26 | P | PROBLEMA DEL CLIENTE | 2X100 DEL SU-13H @ BOVEDA DEL CLIENTE POR AVERIA INTERIOR SE ORIENTO AL CLIENTE | B23021800038 | New_Event | Customer-Related Interruption | Include | Include | Public | 86 | 2023-02-18 | 86 | keep | 0 | Feb | 2023 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-18 13:49 | 2023-02-18 17:27 | 118 | 3:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZARON POSTES PRIMARIOS Y SE ABRE MACHETES PARA PODER CERRAR PUENTES PRIMARIOS SIN CARGA. INTERRUPCION AUMENTA A 20% | S23021700377 | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 218 | 2023-02-18 | 25724 | keep | 0 | Feb | 2023 | 0.01752 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-18 13:56 | 2023-02-19 13:42 | 6 | 23:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO BARRA SECUNDARIA | B23021800039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1426 | 2023-02-18 | 8556 | keep | 0 | Feb | 2023 | 0.0058275 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-02-18 13:59 | 2023-02-18 14:10 | 2675 | 0:11 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | R23021800077 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 11 | 2023-02-18 | 29425 | keep | 0 | Feb | 2023 | 0.020041 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-02-18 14:00 | 2023-02-18 20:45 | 30 | 6:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A23021800030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2023-02-18 | 12150 | keep | 0 | Feb | 2023 | 0.0082753 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-18 14:12 | 2023-02-18 14:15 | 138 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1206-04 LLEVANDO 10% 1204-03 Y 40% 1204-04 AL CERRAR AMARRE CONTRA 1303-02. HABIA ARBOL EN ALIMENTADOR 1303-02 | S2302180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-18 | 414 | keep | 0 | Feb | 2023 | 0.00028197 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-02-18 14:12 | 2023-02-18 14:15 | 1978 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1206-04 LLEVANDO 10% 1204-03 Y 40% 1204-04 AL CERRAR AMARRE CONTRA 1303-02. HABIA ARBOL EN ALIMENTADOR 1303-02 | S2302180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-18 | 5934 | keep | 0 | Feb | 2023 | 0.0040416 | 0.0013472 | Momentary | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2023-02-18 14:12 | 2023-02-18 14:15 | 1799 | 0:03 | T | OTRAS CAUSAS | DISPARO DE INTERRUPTOR 1206-04 LLEVANDO 10% 1204-03 Y 40% 1204-04 AL CERRAR AMARRE CONTRA 1303-02. HABIA ARBOL EN ALIMENTADOR 1303-02 | S2302180000X | New_Event | Other Causes | Include | Include | Other | 3 | 2023-02-18 | 5397 | keep | 0 | Feb | 2023 | 0.0036759 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
BAYAMON | 2023-02-18 14:18 | 2023-02-18 14:54 | 6 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO/SUBIO SECUNDARIA PARTIDA DEL SUELO | B23021800042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2023-02-18 | 216 | keep | 0 | Feb | 2023 | 0.00014712 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-02-18 14:22 | 2023-02-18 14:23 | 3087 | 0:01 | T | ERROR HUMANO | SE ABRIO EL INTERRUPTOR HACIENDO PRUEBA DE QUE SE PODIA ABRIR EL INTERRUPTOR CON TAG C DURANTE ORIENTACION DEL DESPACHADOR JOSE LEON | M23021800062 | New_Event | Human Error | Include | Include | Other | 1 | 2023-02-18 | 3087 | keep | 0 | Feb | 2023 | 0.0021025 | 0.0021025 | Momentary | FALSE | FALSE | Not_TMED_Event | 3087
BAYAMON | 2023-02-18 14:26 | 2023-02-19 10:05 | 10 | 19:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5KVA | S23021800260 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1179 | 2023-02-18 | 11790 | keep | 0 | Feb | 2023 | 0.0080301 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-02-18 14:26 | 2023-02-18 15:32 | 80 | 1:06 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | P23021800049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2023-02-18 | 5280 | keep | 0 | Feb | 2023 | 0.0035962 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-02-18 14:34 | 2023-02-18 14:36 | 154 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1342-04 LLEVANDO 25% 1203-03 | S2302180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-18 | 308 | keep | 0 | Feb | 2023 | 0.00020978 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2023-02-18 14:34 | 2023-02-18 14:36 | 390 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1342-04 LLEVANDO 25% 1203-03 | S2302180000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-02-18 | 780 | keep | 0 | Feb | 2023 | 0.00053125 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
CANOVANAS | 2023-02-18 14:35 | 2023-02-18 14:43 | 2675 | 0:08 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | R23021800084 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 8 | 2023-02-18 | 21400 | keep | 0 | Feb | 2023 | 0.014575 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-18 14:36 | 2023-02-18 17:25 | 199 | 2:49 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | S23021800268 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-02-18 | 33631 | keep | 0 | Feb | 2023 | 0.022906 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2023-02-18 14:46 | 2023-02-18 15:54 | 487 | 1:08 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEAS Y SE CERRO MACHETES. DEJANDO SECCIONALIZADO PUENTE PRIMARIO ABIERTO. 95% 1303-02 EN SERVICIO. | S23021800051 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 68 | 2023-02-18 | 33116 | keep | 0 | Feb | 2023 | 0.022555 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-02-18 15:00 | 2023-02-18 16:50 | 60 | 1:50 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | R23021800093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2023-02-18 | 6600 | keep | 0 | Feb | 2023 | 0.0044952 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-02-18 15:00 | 2023-02-18 16:03 | 2049 | 1:03 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO PB-A PARA RETEZAR CONDUCTOR ARRIADO SE RETEZO CONDUCTOR | R23021800095 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 63 | 2023-02-18 | 129087 | keep | 0 | Feb | 2023 | 0.087921 | 0.0013956 | Sustained | FALSE | FALSE | Not_TMED_Event | 2049
AGUADILLA | 2023-02-18 15:10 | 2023-02-18 17:09 | 250 | 1:59 | P | CONDUCTOR ROTO O ABIERTO | 3 X 50 Y 2 X 100 EN CORTE DE LINEAS SE REPARO LINEA PRIMARIA ROTA | M23021800081 | New_Event | Primary Wire Break | Include | Include | Equipment | 119 | 2023-02-18 | 29750 | keep | 0 | Feb | 2023 | 0.020263 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-02-18 15:27 | 2023-02-18 16:56 | 87 | 1:29 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | B23021800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-02-18 | 7743 | keep | 0 | Feb | 2023 | 0.0052737 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
BAYAMON | 2023-02-18 15:38 | 2023-02-18 18:12 | 150 | 2:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X65 EN C/L & 1X50 EN OTRO C/L SE REMPLAZO AISLADOR | B23021800048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 154 | 2023-02-18 | 23100 | keep | 0 | Feb | 2023 | 0.015733 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-02-18 15:41 | 2023-02-18 16:38 | 100 | 0:57 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23021800128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2023-02-18 | 5700 | keep | 0 | Feb | 2023 | 0.0038822 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-02-18 15:45 | 2023-02-18 16:16 | 10 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M23021800065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2023-02-18 | 310 | keep | 0 | Feb | 2023 | 0.00021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-18 15:51 | 2023-02-18 15:53 | 125 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2302180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-18 | 250 | keep | 0 | Feb | 2023 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-02-18 15:54 | 2023-02-18 17:00 | 122 | 1:06 | P | ARBOL SOBRE LINEA | SE CERRO PUENTE PRIMARIO ABIERTO QUE ABRIO POR CRUCE POR ARBOL | S23021800051 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 66 | 2023-02-18 | 8052 | keep | 0 | Feb | 2023 | 0.0054842 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-02-18 15:57 | 2023-02-18 15:58 | 1212 | 0:01 | T | CRUCETA DEFECTUOSA O AVERIADA | RECIERRE DE INTERRUPTOR REALIZA TRES OPERACIONES Y QUEDA EN SERVICIO | P23021800063 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 1 | 2023-02-18 | 1212 | keep | 0 | Feb | 2023 | 0.00082549 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
PONCE | 2023-02-18 16:16 | 2023-02-18 16:34 | 1212 | 0:18 | T | CRUCETA DEFECTUOSA O AVERIADA | GOI PC-230218-01A SE ABRE INTERRUPTOR DEBIDO A CRUCETA DE METAL SUELTA SOBRE FASES PRIMARIAS | P23021800072 | 1st_after_momentary | Primary Crossarm Failure | Include | Include | Equipment | 18 | 2023-02-18 | 21816 | keep | 0 | Feb | 2023 | 0.014859 | 0.00082549 | Sustained | FALSE | FALSE | Not_TMED_Event | 1212
BARRANQUITAS | 2023-02-18 16:16 | 2023-02-18 16:51 | 2 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO CONECTORES DE BAJANTE SECUNDARIO | C23021800143 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-02-18 | 70 | keep | 0 | Feb | 2023 | 4.7677e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-02-18 16:33 | 2023-02-19 16:30 | 5 | 23:57 | P | ERROR HUMANO | SE SECCIONALIZO CABLE SOTERRADO AVERIADO POR PERSONAL DE QUANTA INSTALANDO POSTE DE ALUMBRADO ENTRE EL SU-1 Y SU-2 Y SE CERRO N/O EN RISER PARA ENERGIZAR SU-1 | A23021800040 | New_Event | Human Error | Include | Include | Other | 1437 | 2023-02-18 | 7185 | keep | 0 | Feb | 2023 | 0.0048937 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-02-18 16:34 | 2023-02-18 18:21 | 30 | 1:47 | P | CRUCETA DEFECTUOSA O AVERIADA | GOI PC-230218-01A SE TRANSFIERE CARGA AL 5005-02 PARA REPARAR CONDICION DE CRUCETA DE METAL SOBRE FASES PRMARIAS Y LUEGO SE NORMALIZAN CARGAS | P23021800064 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 107 | 2023-02-18 | 3210 | keep | 0 | Feb | 2023 | 0.0021863 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-18 17:27 | 2023-02-18 19:36 | 158 | 2:09 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE CERRO PUENTES PRIMARIOS Y SE CERRO MACHETES. EN SERVICIO TOTAL | S23021700377 | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 129 | 2023-02-18 | 20382 | keep | 0 | Feb | 2023 | 0.013882 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-18 17:31 | 2023-02-18 19:32 | 30 | 2:01 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23021800064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-02-18 | 3630 | keep | 0 | Feb | 2023 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-02-18 17:40 | 2023-02-18 20:06 | 70 | 2:26 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23021800155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2023-02-18 | 10220 | keep | 0 | Feb | 2023 | 0.0069608 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-02-18 17:55 | 2023-02-19 10:02 | 10 | 16:07 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZA DESGANCHE Y SE REPARA SECUNDARIA | M23021800104 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 967 | 2023-02-18 | 9670 | keep | 0 | Feb | 2023 | 0.0065862 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-02-18 18:00 | 2023-02-18 20:45 | 6 | 2:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZA TRANSFORMADOR AVERIADO 37.5KVA A 2.4KV | P23021800069 | New_Event | Service Transformer Failure | Include | Include | Equipment | 165 | 2023-02-18 | 990 | keep | 0 | Feb | 2023 | 0.00067428 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-18 18:09 | 2023-02-18 22:12 | 1 | 4:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIAS | S23021800331 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 243 | 2023-02-18 | 243 | keep | 0 | Feb | 2023 | 0.00016551 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-18 18:10 | 2023-02-18 19:01 | 60 | 0:51 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23021800162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2023-02-18 | 3060 | keep | 0 | Feb | 2023 | 0.0020842 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-18 18:14 | 2023-02-18 20:29 | 1106 | 2:15 | P | ANIMAL | SE RETIRO IGUANA Y SE REEMPLAZO CAJA PRIMARIA ROTA. SE CERRO AMARRE CONTRA 1529-15 | S23021800332 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-02-18 | 149310 | keep | 0 | Feb | 2023 | 0.10169 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-02-18 18:14 | 2023-02-18 18:52 | 1802 | 0:38 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1529-15 LLEVANDO 60% 1346-02 SE ABRIO AMARRE POR IGUANA QUE CRUZO CAJA PRIMARIA EN CARGA PERTENECIENTE AL 1346-02. EN SERVICIO 1529-15 FUERA 60% 1346-02 | S23021800332 | New_Event | Feeder Load Transferred | Include | Include | Other | 38 | 2023-02-18 | 68476 | keep | 0 | Feb | 2023 | 0.046639 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
PONCE | 2023-02-18 18:24 | 2023-02-18 20:20 | 30 | 1:56 | P | CAUSAS EXTERNAS | CAMION CREA CRUCE DE LINEAS SECUNDARIAS Y SE QUEMAN CONECTORES SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR AVERIA SECUNDARIA | P23021800091 | New_Event | Damage From Public | Include | Include | Public | 116 | 2023-02-18 | 3480 | keep | 0 | Feb | 2023 | 0.0023702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-02-18 18:26 | 2023-02-18 20:45 | 400 | 2:19 | P | DESCONECTIVO DEFECTUOSO | AVERIA EN MACHETE FASE DEL CENTRO SE CIERRA AMARRE CON 5001-03 Y SE ABREN MACHETES | P23021800093 | New_Event | Switch Failure | Include | Include | Equipment | 139 | 2023-02-18 | 55600 | keep | 0 | Feb | 2023 | 0.037869 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2023-02-18 18:37 | 2023-02-19 09:21 | 9 | 14:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 5 EN TRANSFORMADOR POR LLUVIAS | M23021800107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 884 | 2023-02-18 | 7956 | keep | 0 | Feb | 2023 | 0.0054188 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-02-18 18:43 | 2023-02-18 23:32 | 20 | 4:49 | P | ANIMAL | 1X20 EN RISER Y 1X20 EN SU-1 CRUCE POR AVE | B23021800069 | New_Event | Animals | Include | Include | Wildlife | 289 | 2023-02-18 | 5780 | keep | 0 | Feb | 2023 | 0.0039367 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-02-18 20:08 | 2023-02-19 10:40 | 50 | 14:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23021800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 872 | 2023-02-18 | 43600 | keep | 0 | Feb | 2023 | 0.029696 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-02-18 20:17 | 2023-02-19 08:37 | 5 | 12:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | A23021800048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 740 | 2023-02-18 | 3700 | keep | 0 | Feb | 2023 | 0.0025201 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-02-18 20:23 | 2023-02-19 06:11 | 8 | 9:48 | P | ANIMAL | 1 X 15 EN C/L CRUCE X AVE | C23021800180 | New_Event | Animals | Include | Include | Wildlife | 588 | 2023-02-18 | 4704 | keep | 0 | Feb | 2023 | 0.0032039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-02-18 20:30 | 2023-02-19 09:50 | 7 | 13:20 | P | ANIMAL | 1 X 25 EN XMR AVE CRUZO LINEAS | P23021800114 | New_Event | Animals | Include | Include | Wildlife | 800 | 2023-02-18 | 5600 | keep | 0 | Feb | 2023 | 0.0038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-02-18 21:34 | 2023-02-19 00:06 | 50 | 2:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | R23021800127 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2023-02-18 | 7600 | keep | 0 | Feb | 2023 | 0.0051763 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-02-18 21:40 | 2023-02-19 10:04 | 10 | 12:24 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S23021800362 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 744 | 2023-02-18 | 7440 | keep | 0 | Feb | 2023 | 0.0050674 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-18 21:40 | 2023-02-19 09:30 | 8 | 11:50 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | A23021800055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 710 | 2023-02-18 | 5680 | keep | 0 | Feb | 2023 | 0.0038686 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-02-18 22:08 | 2023-02-19 09:54 | 45 | 11:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR VIENTOS | M23021800119 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 706 | 2023-02-18 | 31770 | keep | 0 | Feb | 2023 | 0.021638 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-02-18 23:11 | 2023-02-19 02:02 | 70 | 2:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIAS | R23021800133 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 171 | 2023-02-18 | 11970 | keep | 0 | Feb | 2023 | 0.0081527 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-02-18 23:30 | 2023-02-19 08:26 | 15 | 8:56 | P | ARBOL SOBRE LINEA | 1 X 40 EN C/L SE RETIRO ARBOL DE LA LINEA | B23021800085 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 536 | 2023-02-18 | 8040 | keep | 0 | Feb | 2023 | 0.005476 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-18 23:50 | 2023-02-19 01:36 | 16 | 1:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN XMR SE REMPLAZO PORTAFUSIBLE | B23021800087 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2023-02-18 | 1696 | keep | 0 | Feb | 2023 | 0.0011551 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2023-02-19 01:01 | 2023-02-19 09:00 | 8 | 7:59 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN TRANSFORMADOR | A23021900002 | New_Event | Primary Wire Break | Include | Include | Equipment | 479 | 2023-02-19 | 3832 | keep | 0 | Feb | 2023 | 0.00261 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-02-19 02:22 | 2023-02-19 02:23 | 424 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23021900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-19 | 424 | keep | 0 | Feb | 2023 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
BAYAMON | 2023-02-19 02:26 | 2023-02-19 02:27 | 603 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-08 LLEVA LA CARGA DEL 9206-09 | B23021900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-19 | 603 | keep | 0 | Feb | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-02-19 02:26 | 2023-02-19 02:27 | 6 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-08 LLEVA LA CARGA DEL 9206-09 | B23021900002 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-19 | 6 | keep | 0 | Feb | 2023 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-02-19 02:37 | 2023-02-19 08:27 | 100 | 5:50 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | R23021900005 | New_Event | Animals | Include | Include | Wildlife | 350 | 2023-02-19 | 35000 | keep | 0 | Feb | 2023 | 0.023838 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-02-19 02:47 | 2023-02-19 13:28 | 45 | 10:41 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L Y SE LEVANTO CONDUCTOR PRIMARIO | S23021900002 | New_Event | Primary Wire Break | Include | Include | Equipment | 641 | 2023-02-19 | 28845 | keep | 0 | Feb | 2023 | 0.019646 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-02-19 03:39 | 2023-02-19 11:47 | 33 | 8:08 | P | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO C/L TOTAL PARA REEMPLAZO DE CRUCETA PARTIDA Y SE LEVANTO CONDUCTOR PRIMARIO | S23021900004 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 488 | 2023-02-19 | 16104 | keep | 0 | Feb | 2023 | 0.010968 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
SAN JUAN | 2023-02-19 03:46 | 2023-02-19 11:57 | 24 | 8:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL AEREO | S23021900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 491 | 2023-02-19 | 11784 | keep | 0 | Feb | 2023 | 0.008026 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
PONCE | 2023-02-19 03:53 | 2023-02-19 03:54 | 1712 | 0:01 | T | DESGANCHE | RECIERRE LLEVA CARGA DE 5010-04 | P23021900010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-19 | 1712 | keep | 0 | Feb | 2023 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2023-02-19 03:53 | 2023-02-19 03:54 | 7 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE SU CARGA X 5005-03 | P23021900010 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-19 | 7 | keep | 0 | Feb | 2023 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-02-19 03:54 | 2023-02-19 15:32 | 50 | 11:38 | P | DESGANCHE | 2 X 80 EN C/L SE REALIZO DESGANCHE | S23021900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 698 | 2023-02-19 | 34900 | keep | 0 | Feb | 2023 | 0.02377 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-19 03:59 | 2023-02-19 09:00 | 50 | 5:01 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23021900001 | New_Event | Animals | Include | Include | Wildlife | 301 | 2023-02-19 | 15050 | keep | 0 | Feb | 2023 | 0.01025 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-02-19 04:03 | 2023-02-19 04:04 | 1712 | 0:01 | T | DESGANCHE | RECIERRE LLEVA CARGA DE 5010-04 | P23021900011 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-19 | 1712 | keep | 0 | Feb | 2023 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2023-02-19 04:03 | 2023-02-19 04:04 | 7 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE SU CARGA X 5005-03 | P23021900011 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-19 | 7 | keep | 0 | Feb | 2023 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-02-19 04:09 | 2023-02-19 04:10 | 1712 | 0:01 | T | DESGANCHE | DISPARO DE ALIMENTADOR LLEVA CARGA DE 5010-04 | P23021900015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-19 | 1712 | keep | 0 | Feb | 2023 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2023-02-19 04:09 | 2023-02-19 04:10 | 7 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE SU CARGA X 5005-03 | P23021900015 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-19 | 7 | keep | 0 | Feb | 2023 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-02-19 04:21 | 2023-02-19 10:31 | 10 | 6:10 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | C23021900002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 370 | 2023-02-19 | 3700 | keep | 0 | Feb | 2023 | 0.0025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-02-19 04:46 | 2023-02-19 13:40 | 30 | 8:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO VIENTOS | P23021900028 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 534 | 2023-02-19 | 16020 | keep | 0 | Feb | 2023 | 0.010911 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-19 05:07 | 2023-02-19 07:26 | 40 | 2:19 | P | NO SE REPORTO CAUSA | 1 X 65 AEREO Y EN SU-12 1 X 50 RBA | S23021900009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2023-02-19 | 5560 | keep | 0 | Feb | 2023 | 0.0037869 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-19 05:25 | 2023-02-19 05:26 | 74 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1521-02 LLEVA LA CARGA DEL 1912-07 | S2302190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-19 | 74 | keep | 0 | Feb | 2023 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2023-02-19 05:25 | 2023-02-19 05:26 | 57 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1521-02 LLEVA LA CARGA DEL 1912-07 | S2302190000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-19 | 57 | keep | 0 | Feb | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
PONCE | 2023-02-19 06:20 | 2023-02-19 06:43 | 1712 | 0:23 | T | DESGANCHE | SE SECCIONALIZO EN FID10987859 Y SE CERRO PUENTE ABIERTO | P23021900024 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 23 | 2023-02-19 | 39376 | keep | 0 | Feb | 2023 | 0.026819 | 0.001166 | Sustained | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2023-02-19 06:20 | 2023-02-19 06:43 | 7 | 0:23 | T | ALIMENTADOR AMARRADO | RECIERRE LLEVA CARGA DE 5010-04 | P23021900024 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 23 | 2023-02-19 | 161 | keep | 0 | Feb | 2023 | 0.00010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-02-19 06:29 | 2023-02-19 06:30 | 27 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-19 | 27 | keep | 0 | Feb | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
PONCE | 2023-02-19 06:43 | 2023-02-19 08:55 | 470 | 2:12 | P | DESGANCHE | SE DESGANCHO Y SE CERRO PUENTE ABIERTO | P23021900024 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-02-19 | 62040 | keep | 0 | Feb | 2023 | 0.042255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-19 06:48 | 2023-02-19 06:49 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23021900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-19 | 2126 | keep | 0 | Feb | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
AGUADILLA | 2023-02-19 07:26 | 2023-02-19 09:00 | 20 | 1:34 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA POR DESGANCHE | M23021900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-02-19 | 1880 | keep | 0 | Feb | 2023 | 0.0012805 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-19 07:35 | 2023-02-19 08:59 | 30 | 1:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23021900014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-02-19 | 2520 | keep | 0 | Feb | 2023 | 0.0017164 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-02-19 08:24 | 2023-02-19 12:17 | 22 | 3:53 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23021900021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2023-02-19 | 5126 | keep | 0 | Feb | 2023 | 0.0034913 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2023-02-19 09:07 | 2023-02-19 12:14 | 8 | 3:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23021900029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2023-02-19 | 1496 | keep | 0 | Feb | 2023 | 0.0010189 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-02-19 09:09 | 2023-02-19 10:47 | 1879 | 1:38 | T | ANIMAL | DISPARO DE INTERRUPTOR SE REALIZRON OPERACIONES PARA SECCIONALIZAR LLEVA 3006-05 | C23021900032 | New_Event | Animals | Include | Include | Wildlife | 98 | 2023-02-19 | 184142 | keep | 0 | Feb | 2023 | 0.12542 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-02-19 09:09 | 2023-02-19 11:32 | 3005 | 2:23 | T | ALIMENTADOR AMARRADO | SE REALIZO DESGANCHE Y SE REMPLAZO CAJA PRIMARIA QUEMADA A CAUSA DE CRUCE X IGUANA | C23021900032 | New_Event | Feeder Load Transferred | Include | Include | Other | 143 | 2023-02-19 | 429715 | keep | 0 | Feb | 2023 | 0.29268 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
SAN JUAN | 2023-02-19 09:14 | 2023-02-19 13:08 | 100 | 3:54 | P | ANIMAL | 1 X 40 Y 1 X 65 EN C/L CRUCE X AVE | S23021900021 | New_Event | Animals | Include | Include | Wildlife | 234 | 2023-02-19 | 23400 | keep | 0 | Feb | 2023 | 0.015938 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-02-19 09:23 | 2023-02-19 10:40 | 2 | 1:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO TOMAS SECUNDARIAS QUEMADAS | R23021900013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 77 | 2023-02-19 | 154 | keep | 0 | Feb | 2023 | 0.00010489 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-19 09:27 | 2023-02-19 12:47 | 40 | 3:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B23021900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2023-02-19 | 8000 | keep | 0 | Feb | 2023 | 0.0054488 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-02-19 09:30 | 2023-02-19 16:10 | 4 | 6:40 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR 50 KVA A 2.4 KV AVERIADO SE TIRA 100 PIES DE LINEA SECUNDARIA Y SE PASAN LOS CLIENTES A TRANSFORMADOR ALEDAÃ‘O | P23021900088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 400 | 2023-02-19 | 1600 | keep | 0 | Feb | 2023 | 0.0010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-02-19 09:32 | 2023-02-19 09:33 | 2457 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | C23021900032 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-02-19 | 2457 | keep | 0 | Feb | 2023 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
BAYAMON | 2023-02-19 09:44 | 2023-02-19 10:13 | 50 | 0:29 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23021900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 29 | 2023-02-19 | 1450 | keep | 0 | Feb | 2023 | 0.00098759 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-02-19 09:46 | 2023-02-19 16:40 | 1 | 6:54 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | P23021900053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 414 | 2023-02-19 | 414 | keep | 0 | Feb | 2023 | 0.00028197 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-19 09:48 | 2023-02-19 14:54 | 8 | 5:06 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO PUENTE DE LINEA A CAJA | B23021900020 | New_Event | Primary Wire Break | Include | Include | Equipment | 306 | 2023-02-19 | 2448 | keep | 0 | Feb | 2023 | 0.0016673 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-02-19 10:06 | 2023-02-19 10:37 | 8 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 8 EN TRANSFORMADOR SE REEMPLAZARON CONECTORES QUEMADOS | C23021900054 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2023-02-19 | 248 | keep | 0 | Feb | 2023 | 0.00016891 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-02-19 10:27 | 2023-02-19 10:28 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23021900058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-19 | 1702 | keep | 0 | Feb | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
VEGA BAJA | 2023-02-19 10:37 | 2023-02-19 10:38 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-19 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
CAGUAS | 2023-02-19 10:39 | 2023-02-19 12:46 | 25 | 2:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23021900063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-02-19 | 3175 | keep | 0 | Feb | 2023 | 0.0021625 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-19 10:46 | 2023-02-19 14:15 | 104 | 3:29 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESPEJE DE LINEA | S23021900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-02-19 | 21736 | keep | 0 | Feb | 2023 | 0.014804 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
CAGUAS | 2023-02-19 10:47 | 2023-02-19 11:28 | 180 | 0:41 | P | ANIMAL | SE REALIZO DESGANCHE Y SE REMPLAZO CAJA PRIMARIA QUEMADA A CAUSA DE CRUCE X IGUANA. 100% EN SERVICIO | C23021900032 | New_Event | Animals | Include | Include | Wildlife | 41 | 2023-02-19 | 7380 | keep | 0 | Feb | 2023 | 0.0050265 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CANOVANAS | 2023-02-19 10:53 | 2023-02-19 12:50 | 3 | 1:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES SECUNDARIOS QUEMADOS | R23021900015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 117 | 2023-02-19 | 351 | keep | 0 | Feb | 2023 | 0.00023906 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-02-19 11:14 | 2023-02-19 17:57 | 100 | 6:43 | P | DESGANCHE | 1 X 100 EN C/L Y SE REALIZO DESPEJE DE LINEA | S23021900046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 403 | 2023-02-19 | 40300 | keep | 0 | Feb | 2023 | 0.027448 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-02-19 11:24 | 2023-02-19 12:13 | 70 | 0:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | M23021900032 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 49 | 2023-02-19 | 3430 | keep | 0 | Feb | 2023 | 0.0023362 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-02-19 11:42 | 2023-02-19 14:29 | 80 | 2:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M23021900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-02-19 | 13360 | keep | 0 | Feb | 2023 | 0.0090994 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-02-19 11:44 | 2023-02-19 13:33 | 30 | 1:49 | P | ANIMAL | 1 X 50 EN C/L Y 1 X 65 EN C/L | C23021900112 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-02-19 | 3270 | keep | 0 | Feb | 2023 | 0.0022272 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-02-19 11:52 | 2023-02-19 11:53 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23021900011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-19 | 476 | keep | 0 | Feb | 2023 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-02-19 11:52 | 2023-02-19 11:53 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23021900011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-19 | 1655 | keep | 0 | Feb | 2023 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-02-19 11:52 | 2023-02-19 11:53 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23021900011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-19 | 361 | keep | 0 | Feb | 2023 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-02-19 11:52 | 2023-02-19 11:53 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23021900011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-19 | 2842 | keep | 0 | Feb | 2023 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-02-19 11:52 | 2023-02-19 11:53 | 1702 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23021900011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-19 | 1702 | keep | 0 | Feb | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-02-19 11:52 | 2023-02-19 11:53 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23021900011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-19 | 918 | keep | 0 | Feb | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-02-19 11:52 | 2023-02-19 11:53 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23021900011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-19 | 1725 | keep | 0 | Feb | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
SAN JUAN | 2023-02-19 12:15 | 2023-02-19 17:21 | 43 | 5:06 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | S23021900061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2023-02-19 | 13158 | keep | 0 | Feb | 2023 | 0.0089619 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BAYAMON | 2023-02-19 12:30 | 2023-02-19 13:28 | 3295 | 0:58 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO POR PUENTE ABIERTO MEDINATE GOI BY-230219-01 Y ENTRO 50% EN SERVICIO | B23021900045 | New_Event | Primary Wire Break | Include | Include | Equipment | 58 | 2023-02-19 | 191110 | keep | 0 | Feb | 2023 | 0.13016 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
CANOVANAS | 2023-02-19 12:49 | 2023-02-19 13:50 | 30 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA SULFATADA | R23021900019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2023-02-19 | 1830 | keep | 0 | Feb | 2023 | 0.0012464 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-02-19 12:56 | 2023-02-19 15:17 | 20 | 2:21 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | C23021900134 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-02-19 | 2820 | keep | 0 | Feb | 2023 | 0.0019207 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-02-19 13:03 | 2023-02-19 14:52 | 15 | 1:49 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | M23021900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2023-02-19 | 1635 | keep | 0 | Feb | 2023 | 0.0011136 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-19 13:23 | 2023-02-19 16:08 | 162 | 2:45 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23021900063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-02-19 | 26730 | keep | 0 | Feb | 2023 | 0.018206 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
BAYAMON | 2023-02-19 13:28 | 2023-02-19 14:50 | 1647 | 1:22 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO POR PUENTE ABIERTO MEDINATE GOI BY-230219-01 Y ENTRO 20% EN SERVICIO | B23021900045 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 82 | 2023-02-19 | 135054 | keep | 0 | Feb | 2023 | 0.091985 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-19 13:30 | 2023-02-19 15:59 | 30 | 2:29 | P | DESGANCHE | 2X40 EN C/L DESGANCHE (EVENTO CAYO POR REGION SJ) | S23021900072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-02-19 | 4470 | keep | 0 | Feb | 2023 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-02-19 13:34 | 2023-02-19 15:15 | 6 | 1:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA EVENTO TRANSFERIDO A VEGA BAJA | A23021900049 | New_Event | Primary Wire Break | Include | Include | Equipment | 101 | 2023-02-19 | 606 | keep | 0 | Feb | 2023 | 0.00041274 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-02-19 13:35 | 2023-02-19 14:15 | 12 | 0:40 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M23021900033 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 40 | 2023-02-19 | 480 | keep | 0 | Feb | 2023 | 0.00032693 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-02-19 13:37 | 2023-02-19 14:50 | 40 | 1:13 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE REALIZO DESGANCHE PERO SE REQUIERE MAS DESGANCHE | A23021900050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-02-19 | 2920 | keep | 0 | Feb | 2023 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-02-19 13:39 | 2023-02-19 14:35 | 25 | 0:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X30 EN CL FUERTE VIENTO | P23021900079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 56 | 2023-02-19 | 1400 | keep | 0 | Feb | 2023 | 0.00095353 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-19 13:47 | 2023-02-19 18:45 | 40 | 4:58 | P | DESGANCHE | 1 X 100 EN C/L Y SE REALIZO DESGANCHE | S23021900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2023-02-19 | 11920 | keep | 0 | Feb | 2023 | 0.0081187 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-02-19 13:52 | 2023-02-19 14:27 | 6 | 0:35 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR PARA AJUSTAR BUSHING SECUNDARIOS NO FUNDIO | C23021900143 | New_Event | Service Transformer Failure | Include | Include | Equipment | 35 | 2023-02-19 | 210 | keep | 0 | Feb | 2023 | 0.00014303 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-19 14:00 | 2023-02-19 17:31 | 25 | 3:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA | S23021900083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 211 | 2023-02-19 | 5275 | keep | 0 | Feb | 2023 | 0.0035928 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-02-19 14:00 | 2023-02-19 14:38 | 70 | 0:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R23021900024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2023-02-19 | 2660 | keep | 0 | Feb | 2023 | 0.0018117 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-02-19 14:00 | 2023-02-19 15:47 | 60 | 1:47 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | M23021900046 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 107 | 2023-02-19 | 6420 | keep | 0 | Feb | 2023 | 0.0043726 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-02-19 14:01 | 2023-02-19 15:39 | 20 | 1:38 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | C23021900144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2023-02-19 | 1960 | keep | 0 | Feb | 2023 | 0.0013349 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-02-19 14:03 | 2023-02-19 14:05 | 1745 | 0:02 | P | NO SE REPORTO CAUSA | RECIERRE 15% DE LA CARGA POR EL 1646-03 | R2202190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-19 | 3490 | keep | 0 | Feb | 2023 | 0.002377 | 0.0011885 | Momentary | FALSE | FALSE | Not_TMED_Event | 1745
SAN JUAN | 2023-02-19 14:13 | 2023-02-19 14:45 | 1 | 0:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REEMPLAZO PORTAFUSIBLE | S23021900080 | New_Event | Cutout Failure | Include | Include | Equipment | 32 | 2023-02-19 | 32 | keep | 0 | Feb | 2023 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-19 14:20 | 2023-02-19 14:34 | 8 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR CONECTORES EN SECUNDARIA | C23021900145 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2023-02-19 | 112 | keep | 0 | Feb | 2023 | 7.6283e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-19 14:21 | 2023-02-19 15:57 | 253 | 1:36 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23021900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-02-19 | 24288 | keep | 0 | Feb | 2023 | 0.016542 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
SAN JUAN | 2023-02-19 14:23 | 2023-02-19 16:42 | 8 | 2:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BARRAS SECUNDARIAS EN XMR | S23021900081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 139 | 2023-02-19 | 1112 | keep | 0 | Feb | 2023 | 0.00075738 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-19 14:29 | 2023-02-19 18:55 | 92 | 4:26 | P | DESGANCHE | MEDIANTE GOI BY-230219-01 SE REALIZO DESGANCHE EN VARIOS PUNTOS | B23021900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-02-19 | 24472 | keep | 0 | Feb | 2023 | 0.016668 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
SAN JUAN | 2023-02-19 14:35 | 2023-02-19 18:08 | 30 | 3:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO TRASPATIO | S23021900085 | New_Event | Primary Wire Break | Include | Include | Equipment | 213 | 2023-02-19 | 6390 | keep | 0 | Feb | 2023 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-19 14:50 | 2023-02-19 15:00 | 989 | 0:10 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO MACHETE Y SE REPARO PUENTE PRIMARIO ENTRO 30% ADICIONAL PARA UN 100% EN SERVICIO | B23021900045 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 10 | 2023-02-19 | 9890 | keep | 0 | Feb | 2023 | 0.006736 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-19 15:06 | 2023-02-19 17:22 | 140 | 2:16 | P | DESGANCHE | 3X80 EN C/L DESGANCHE | C23021900151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-02-19 | 19040 | keep | 0 | Feb | 2023 | 0.012968 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
MAYAGÃœEZ | 2023-02-19 15:10 | 2023-02-19 16:55 | 2 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M23021900056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2023-02-19 | 210 | keep | 0 | Feb | 2023 | 0.00014303 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-02-19 15:23 | 2023-02-19 17:35 | 36 | 2:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO SAFADO HACIA CAJA DE TRANSFORMADOR | R23021900030 | New_Event | Primary Wire Break | Include | Include | Equipment | 132 | 2023-02-19 | 4752 | keep | 0 | Feb | 2023 | 0.0032366 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2023-02-19 15:32 | 2023-02-19 18:24 | 60 | 2:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A23021900057 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 172 | 2023-02-19 | 10320 | keep | 0 | Feb | 2023 | 0.0070289 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-19 15:50 | 2023-02-19 18:46 | 65 | 2:56 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S23021900102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2023-02-19 | 11440 | keep | 0 | Feb | 2023 | 0.0077917 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2023-02-19 16:18 | 2023-02-19 20:16 | 30 | 3:58 | P | DESGANCHE | 2X40 EN C/L DESGANCHE | C23021900160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-02-19 | 7140 | keep | 0 | Feb | 2023 | 0.004863 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-02-19 16:48 | 2023-02-19 20:18 | 25 | 3:30 | P | DESGANCHE | 1X30 EN C/L DESGANCHE | C23021900163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-02-19 | 5250 | keep | 0 | Feb | 2023 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-02-19 17:20 | 2023-02-19 20:19 | 60 | 2:59 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE LEVANTO NEUTRAL | M23021900063 | New_Event | Primary Wire Break | Include | Include | Equipment | 179 | 2023-02-19 | 10740 | keep | 0 | Feb | 2023 | 0.007315 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-02-19 17:33 | 2023-02-19 21:10 | 55 | 3:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M23021900064 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 217 | 2023-02-19 | 11935 | keep | 0 | Feb | 2023 | 0.0081289 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2023-02-19 17:39 | 2023-02-19 20:51 | 1 | 3:12 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 50 EN SU Y 1 X 80 EN RISER SE REPORTA CONTAMINACION EN SU | S23021900153 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 192 | 2023-02-19 | 192 | keep | 0 | Feb | 2023 | 0.00013077 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-02-19 18:01 | 2023-02-19 21:00 | 25 | 2:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTE VIENTO | A23021900075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 179 | 2023-02-19 | 4475 | keep | 0 | Feb | 2023 | 0.0030479 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-02-19 18:09 | 2023-02-19 18:45 | 30 | 0:36 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | R23021900038 | New_Event | Animals | Include | Include | Wildlife | 36 | 2023-02-19 | 1080 | keep | 0 | Feb | 2023 | 0.00073558 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-02-19 18:11 | 2023-02-19 20:23 | 100 | 2:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE CORRIGIO TEMPORERAMENTE AVERIA EN CAJA PRIMARIA PERO HAY QUE VOLVER MAÃ‘ANA PARA REMPLAZAR LA CAJA PRIMARIA QUE ESTA EN MALAS CONDICIONES | A23021900080 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2023-02-19 | 13200 | keep | 0 | Feb | 2023 | 0.0089905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-02-19 18:20 | 2023-02-19 19:33 | 8 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 15 XMR Y SE REPARARON CONEXIONES SECUNDARIAS | S23021900124 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-02-19 | 584 | keep | 0 | Feb | 2023 | 0.00039776 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-19 18:29 | 2023-02-19 23:04 | 30 | 4:35 | P | ANIMAL | 1 X 20 EN XMR Y 1 X 80 EN C/L CRUCE X AVE | B23021900170 | New_Event | Animals | Include | Include | Wildlife | 275 | 2023-02-19 | 8250 | keep | 0 | Feb | 2023 | 0.005619 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-19 18:37 | 2023-02-19 19:53 | 6 | 1:16 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | R23021900040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2023-02-19 | 456 | keep | 0 | Feb | 2023 | 0.00031058 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-02-19 18:50 | 2023-02-20 11:58 | 8 | 17:08 | P | SECUNDARIA/DESGANCHE | DESGANCHE 1 X 10 EN XMR | C23021900187 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1028 | 2023-02-19 | 8224 | keep | 0 | Feb | 2023 | 0.0056013 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-19 19:28 | 2023-02-19 21:57 | 10 | 2:29 | P | DESGANCHE | 1 X 10 EN XMR Y DESGANCHE PRIMARIO | B23021900181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-02-19 | 1490 | keep | 0 | Feb | 2023 | 0.0010148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-19 19:38 | 2023-02-19 20:30 | 35 | 0:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R23021900041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2023-02-19 | 1820 | keep | 0 | Feb | 2023 | 0.0012396 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-02-19 20:02 | 2023-02-20 14:20 | 4 | 18:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM-19 MEDIANTE GOI BY-230220-03 | S23021900129 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1098 | 2023-02-19 | 4392 | keep | 0 | Feb | 2023 | 0.0029914 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-02-19 20:48 | 2023-02-19 22:48 | 100 | 2:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23021900094 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 120 | 2023-02-19 | 12000 | keep | 0 | Feb | 2023 | 0.0081731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-02-19 22:19 | 2023-02-20 00:05 | 94 | 1:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR VIENTOS | P23021900112 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 106 | 2023-02-19 | 9964 | keep | 0 | Feb | 2023 | 0.0067864 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
BAYAMON | 2023-02-19 22:33 | 2023-02-20 03:33 | 40 | 5:00 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23021900193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-02-19 | 12000 | keep | 0 | Feb | 2023 | 0.0081731 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-20 00:23 | 2023-02-20 01:42 | 1 | 1:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REEMPLAZO PORTAFUSIBLE | S23022000002 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2023-02-20 | 79 | keep | 0 | Feb | 2023 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-20 00:31 | 2023-02-20 10:49 | 87 | 10:18 | P | ANIMAL | 2 X 65 EN C/L CRUCE POR AVE | C23022000003 | New_Event | Animals | Include | Include | Wildlife | 618 | 2023-02-20 | 53766 | keep | 0 | Feb | 2023 | 0.03662 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
VEGA BAJA | 2023-02-20 00:33 | 2023-02-20 00:35 | 3387 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23022000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-20 | 6774 | keep | 0 | Feb | 2023 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
CAGUAS | 2023-02-20 01:53 | 2023-02-20 01:54 | 2608 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C2302200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-20 | 2608 | keep | 0 | Feb | 2023 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
VEGA BAJA | 2023-02-20 02:01 | 2023-02-20 06:54 | 40 | 4:53 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO RAMA EVENTO TRANSFERIDO | C23022000012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2023-02-20 | 11720 | keep | 0 | Feb | 2023 | 0.0079824 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-20 02:09 | 2023-02-20 06:09 | 123 | 4:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA CONTAMINACION, SE DESCONTAMINO CORTE DE LINEA | C23022000013 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2023-02-20 | 29520 | keep | 0 | Feb | 2023 | 0.020106 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
BARRANQUITAS | 2023-02-20 02:30 | 2023-02-20 02:31 | 1604 | 0:01 | T | CRUCETA DEFECTUOSA O AVERIADA | RECERRO | C23022000015 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 1 | 2023-02-20 | 1604 | keep | 0 | Feb | 2023 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2023-02-20 02:31 | 2023-02-20 13:17 | 69 | 10:46 | P | CRUCETA DEFECTUOSA O AVERIADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CRUCETA PARTIDA | C23022000018 | 1st_after_momentary | Primary Crossarm Failure | Include | Include | Equipment | 646 | 2023-02-20 | 44574 | keep | 0 | Feb | 2023 | 0.030359 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
CANOVANAS | 2023-02-20 03:53 | 2023-02-20 09:33 | 50 | 5:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L CAJA DEFECTUOSA | R23022000001 | New_Event | Cutout Failure | Include | Include | Equipment | 340 | 2023-02-20 | 17000 | keep | 0 | Feb | 2023 | 0.011579 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-02-20 05:25 | 2023-02-20 09:08 | 1 | 3:43 | P | ANIMAL | 2 X 10 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | C23022000020 | New_Event | Animals | Include | Include | Wildlife | 223 | 2023-02-20 | 223 | keep | 0 | Feb | 2023 | 0.00015188 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-20 05:50 | 2023-02-20 08:13 | 70 | 2:23 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C23022000024 | New_Event | Animals | Include | Include | Wildlife | 143 | 2023-02-20 | 10010 | keep | 0 | Feb | 2023 | 0.0068178 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-02-20 06:03 | 2023-02-20 06:04 | 3046 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE | R23022000002 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-02-20 | 3046 | keep | 0 | Feb | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-02-20 06:04 | 2023-02-20 09:36 | 40 | 3:32 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 SMU 20 DE 80 AMP EN SU-1A CONTAMINACION | R23022000003 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 212 | 2023-02-20 | 8480 | keep | 0 | Feb | 2023 | 0.0057757 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-02-20 06:18 | 2023-02-20 12:35 | 70 | 6:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN C/L MAL TIEMPO VIENTOS | P23022000012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 377 | 2023-02-20 | 26390 | keep | 0 | Feb | 2023 | 0.017974 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-02-20 07:01 | 2023-02-20 07:04 | 1588 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B23022000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-20 | 4764 | keep | 0 | Feb | 2023 | 0.0032447 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
VEGA BAJA | 2023-02-20 07:01 | 2023-02-20 07:05 | 4702 | 0:04 | T | DESCONECTIVO DEFECTUOSO | DISPARO Y SE CERRO POR CONTROL | B23022000009 | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2023-02-20 | 18808 | keep | 0 | Feb | 2023 | 0.01281 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-02-20 07:14 | 2023-02-20 07:42 | 4702 | 0:28 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR POR CONTROL PARA SECCIONALIZAR MACHETE ARQUEANDO SWITCH FORM BY-230220-01 ENTRO 90% EN SERVICIO | B23022000014 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 28 | 2023-02-20 | 131656 | keep | 0 | Feb | 2023 | 0.08967 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-02-20 07:42 | 2023-02-20 10:55 | 470 | 3:13 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y SE CERRO VIA DE V/S CON SWITCH FORM BY-230220-01 | B23022000014 | Partial_restoration | Switch Failure | Include | Include | Equipment | 193 | 2023-02-20 | 90710 | keep | 0 | Feb | 2023 | 0.061782 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-20 07:43 | 2023-02-20 12:30 | 11 | 4:47 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN BANCO DE XMR DESGANCHE SECUNDARIO | S23022000006 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 287 | 2023-02-20 | 3157 | keep | 0 | Feb | 2023 | 0.0021502 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-02-20 08:00 | 2023-02-20 21:50 | 60 | 13:50 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23022000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 830 | 2023-02-20 | 49800 | keep | 0 | Feb | 2023 | 0.033919 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-02-20 08:06 | 2023-02-20 10:17 | 100 | 2:11 | P | DESGANCHE | SE ABRIO C/L Y SE REALIZO DESGANCHE | B23022000032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-02-20 | 13100 | keep | 0 | Feb | 2023 | 0.0089224 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-02-20 08:09 | 2023-02-20 10:14 | 1339 | 2:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2023-02-20 | 167375 | keep | 0 | Feb | 2023 | 0.114 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-02-20 08:09 | 2023-02-20 10:14 | 470 | 2:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2023-02-20 | 58750 | keep | 0 | Feb | 2023 | 0.040014 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2023-02-20 08:09 | 2023-02-20 10:14 | 2483 | 2:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2023-02-20 | 310375 | keep | 0 | Feb | 2023 | 0.21139 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2023-02-20 08:09 | 2023-02-20 10:14 | 2190 | 2:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2023-02-20 | 273750 | keep | 0 | Feb | 2023 | 0.18645 | 0.0014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2023-02-20 08:09 | 2023-02-20 10:14 | 3006 | 2:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2023-02-20 | 375750 | keep | 0 | Feb | 2023 | 0.25592 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2023-02-20 08:09 | 2023-02-20 10:14 | 179 | 2:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2023-02-20 | 22375 | keep | 0 | Feb | 2023 | 0.01524 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2023-02-20 08:09 | 2023-02-20 08:10 | 107 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-20 | 107 | keep | 0 | Feb | 2023 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2023-02-20 08:09 | 2023-02-20 08:10 | 1666 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-20 | 1666 | keep | 0 | Feb | 2023 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2023-02-20 08:09 | 2023-02-20 08:10 | 4387 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-20 | 4387 | keep | 0 | Feb | 2023 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2023-02-20 08:09 | 2023-02-20 08:10 | 3147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-20 | 3147 | keep | 0 | Feb | 2023 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2023-02-20 08:09 | 2023-02-20 08:10 | 4304 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 SE RETESO FASE ARRIADA | M23022000013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-20 | 4304 | keep | 0 | Feb | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
SAN JUAN | 2023-02-20 08:10 | 2023-02-20 20:24 | 38 | 12:14 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S23022000008 | New_Event | Primary Wire Break | Include | Include | Equipment | 734 | 2023-02-20 | 27892 | keep | 0 | Feb | 2023 | 0.018997 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CANOVANAS | 2023-02-20 08:23 | 2023-02-20 11:26 | 40 | 3:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN C/L REEMPLAZO AISLADOR | R23022000009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 183 | 2023-02-20 | 7320 | keep | 0 | Feb | 2023 | 0.0049856 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-02-20 08:32 | 2023-02-20 11:11 | 8 | 2:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | R23022000010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 159 | 2023-02-20 | 1272 | keep | 0 | Feb | 2023 | 0.00086635 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-20 08:33 | 2023-02-20 08:35 | 870 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO X CONTROL | S2302200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-20 | 1740 | keep | 0 | Feb | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2023-02-20 08:53 | 2023-02-20 08:54 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23022000047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-20 | 1352 | keep | 0 | Feb | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
PONCE | 2023-02-20 08:54 | 2023-02-20 09:46 | 40 | 0:52 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23022000032 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-02-20 | 2080 | keep | 0 | Feb | 2023 | 0.0014167 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-02-20 08:58 | 2023-02-20 12:15 | 6 | 3:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR EL BAJANTE SECUNDARIO | R23022000013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 197 | 2023-02-20 | 1182 | keep | 0 | Feb | 2023 | 0.00080505 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-02-20 09:01 | 2023-02-20 12:20 | 50 | 3:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M23022000048 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2023-02-20 | 9950 | keep | 0 | Feb | 2023 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-02-20 09:02 | 2023-02-20 14:38 | 30 | 5:36 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | P23022000034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2023-02-20 | 10080 | keep | 0 | Feb | 2023 | 0.0068654 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-02-20 09:03 | 2023-02-20 09:51 | 6 | 0:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | R23022000014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 48 | 2023-02-20 | 288 | keep | 0 | Feb | 2023 | 0.00019616 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-20 09:12 | 2023-02-20 11:00 | 80 | 1:48 | P | ANIMAL | 1 X 100 EN C/L SE RETIRO AVE | B23022000041 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-02-20 | 8640 | keep | 0 | Feb | 2023 | 0.0058847 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-02-20 09:13 | 2023-02-20 13:13 | 60 | 4:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23022000026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2023-02-20 | 14400 | keep | 0 | Feb | 2023 | 0.0098078 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2023-02-20 09:28 | 2023-02-20 11:23 | 10 | 1:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23022000047 | New_Event | Primary Wire Break | Include | Include | Equipment | 115 | 2023-02-20 | 1150 | keep | 0 | Feb | 2023 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-20 09:40 | 2023-02-20 10:05 | 10 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARO SECUNDARIA | S23022000003 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-02-20 | 250 | keep | 0 | Feb | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-02-20 09:50 | 2023-02-20 12:55 | 1 | 3:05 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO SE IDENTIFICO CAUSA | M23022000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2023-02-20 | 185 | keep | 0 | Feb | 2023 | 0.000126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-20 09:55 | 2023-02-20 12:53 | 10 | 2:58 | P | DESGANCHE | 1 X 550 EN C/L DESGANCHE | P23022000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-02-20 | 1780 | keep | 0 | Feb | 2023 | 0.0012123 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-20 10:00 | 2023-02-20 12:29 | 30 | 2:29 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE. | C23022000066 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-02-20 | 4470 | keep | 0 | Feb | 2023 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-20 10:15 | 2023-02-20 13:10 | 72 | 2:55 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X SMU-20 DE 100A EN SU-27 MANTENIMIENTO DE SU-27 | S23022000027 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 175 | 2023-02-20 | 12600 | keep | 0 | Feb | 2023 | 0.0085818 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
UTUADO | 2023-02-20 10:30 | 2023-02-20 13:19 | 2 | 2:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADO Y SE REPARA SECUNDARIA | A23021900056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 169 | 2023-02-20 | 338 | keep | 0 | Feb | 2023 | 0.00023021 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-02-20 10:36 | 2023-02-20 11:45 | 25 | 1:09 | P | ANIMAL | 1 X 30 Y 1 X 40 EN CORTE DE LINEA POR PAJARO | A23022000024 | New_Event | Animals | Include | Include | Wildlife | 69 | 2023-02-20 | 1725 | keep | 0 | Feb | 2023 | 0.0011749 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-20 10:46 | 2023-02-20 11:25 | 30 | 0:39 | P | OTRAS CAUSAS | 1 X 40 EN C/L AISLACION CONTAMINADA | B23022000074 | New_Event | Other Causes | Include | Include | Other | 39 | 2023-02-20 | 1170 | keep | 0 | Feb | 2023 | 0.00079688 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-02-20 10:54 | 2023-02-20 13:26 | 180 | 2:32 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR RAMA SOBRE LINEA | A23022000030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-02-20 | 27360 | keep | 0 | Feb | 2023 | 0.018635 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
HUMACAO | 2023-02-20 10:55 | 2023-02-20 10:58 | 2126 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL. | C23022000082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-20 | 6378 | keep | 0 | Feb | 2023 | 0.004344 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
AGUADILLA | 2023-02-20 11:15 | 2023-02-20 11:40 | 8 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR REMPLAZO CONECTORES SECUNDARIOS | M23022000073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-02-20 | 200 | keep | 0 | Feb | 2023 | 0.00013622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-20 11:20 | 2023-02-20 11:22 | 828 | 0:02 | T | CAUSAS EXTERNAS | DISPARO INTERRUPTOR SE REALIZO PRUEBA QUEDO EN SERVICIO | M23022000088 | New_Event | Damage From Public | Include | Include | Public | 2 | 2023-02-20 | 1656 | keep | 0 | Feb | 2023 | 0.0011279 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
BAYAMON | 2023-02-20 11:20 | 2023-02-20 14:55 | 25 | 3:35 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L Y SE LEVANTO LINEA PRIMARIA | B23022000082 | New_Event | Primary Wire Break | Include | Include | Equipment | 215 | 2023-02-20 | 5375 | keep | 0 | Feb | 2023 | 0.0036609 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-02-20 11:26 | 2023-02-20 11:27 | 7621 | 0:01 | T | DESGANCHE | RECIERRE | R23022000022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-20 | 7621 | keep | 0 | Feb | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2023-02-20 11:27 | 2023-02-20 13:47 | 40 | 2:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN C/L REEMPLAZO AISLADOR | R23022000009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 140 | 2023-02-20 | 5600 | keep | 0 | Feb | 2023 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-02-20 11:27 | 2023-02-20 13:13 | 122 | 1:46 | P | DESGANCHE | 2 X 100 EN C/L | R23022000023 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-02-20 | 12932 | keep | 0 | Feb | 2023 | 0.0088079 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
SAN JUAN | 2023-02-20 11:39 | 2023-02-20 16:57 | 1 | 5:18 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | S23022000051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2023-02-20 | 318 | keep | 0 | Feb | 2023 | 0.00021659 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-20 11:39 | 2023-02-20 13:51 | 3 | 2:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARA SECUNDARIA | A23021900072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 132 | 2023-02-20 | 396 | keep | 0 | Feb | 2023 | 0.00026971 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-02-20 11:41 | 2023-02-20 14:25 | 828 | 2:44 | T | CAUSAS EXTERNAS | SE SECCIONALIZO ALIMENTADOR Y SE CERRO INTERRUPTOR SE CONTINUA PATRULLANDO | M23022000088 | 1st_after_momentary | Damage From Public | Include | Include | Public | 164 | 2023-02-20 | 135792 | keep | 0 | Feb | 2023 | 0.092487 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
PONCE | 2023-02-20 11:42 | 2023-02-20 13:55 | 14 | 2:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZA CAJA PRIMARIA EN TRANSFORMADAOR | P23022000077 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2023-02-20 | 1862 | keep | 0 | Feb | 2023 | 0.0012682 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-02-20 11:45 | 2023-02-20 13:15 | 18 | 1:30 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO 25 KVA POR 37.5 KVA NO REGULA VOLTAJE | M23022000087 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2023-02-20 | 1620 | keep | 0 | Feb | 2023 | 0.0011034 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
YAUCO | 2023-02-20 11:47 | 2023-02-20 14:05 | 20 | 2:18 | P | ANIMAL | 1 X 40 EN CL AVE CRUZA FASE PRIMARIA | P23022000078 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-02-20 | 2760 | keep | 0 | Feb | 2023 | 0.0018798 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-20 12:02 | 2023-02-20 13:49 | 9 | 1:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23022000084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 107 | 2023-02-20 | 963 | keep | 0 | Feb | 2023 | 0.00065589 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2023-02-20 12:39 | 2023-02-20 14:21 | 80 | 1:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A23022000067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-02-20 | 8160 | keep | 0 | Feb | 2023 | 0.0055577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-20 13:02 | 2023-02-20 17:51 | 15 | 4:49 | P | ANIMAL | 1 X 50 EN SU-5 CRUCE X RATON | B23022000090 | New_Event | Animals | Include | Include | Wildlife | 289 | 2023-02-20 | 4335 | keep | 0 | Feb | 2023 | 0.0029525 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-20 13:13 | 2023-02-20 14:43 | 40 | 1:30 | P | CONDUCTOR ROTO O ABIERTO | REPARO BAJANTE PRIMARIO DE CAJA A LINEA NO FUNDIO | R23022000037 | New_Event | Primary Wire Break | Include | Include | Equipment | 90 | 2023-02-20 | 3600 | keep | 0 | Feb | 2023 | 0.0024519 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-20 13:27 | 2023-02-20 18:56 | 205 | 5:29 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23022000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 329 | 2023-02-20 | 67445 | keep | 0 | Feb | 2023 | 0.045936 | 0.00013962 | Sustained | FALSE | FALSE | Not_TMED_Event | 205
BAYAMON | 2023-02-20 13:47 | 2023-02-20 15:58 | 37 | 2:11 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23022000098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-02-20 | 4847 | keep | 0 | Feb | 2023 | 0.0033013 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
YAUCO | 2023-02-20 13:55 | 2023-02-20 15:55 | 12 | 2:00 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN TRANSFORMADOR CRUCE INTERNO EN RESIDENCIA | P23022000097 | New_Event | Customer-Related Interruption | Include | Include | Public | 120 | 2023-02-20 | 1440 | keep | 0 | Feb | 2023 | 0.00098078 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-02-20 14:05 | 2023-02-20 18:10 | 2 | 4:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CL SE REMPLAZAN DOS CAJAS PRIMARIAS Y DOS PARARRAYOS AVERIADOS | P23022000098 | New_Event | Cutout Failure | Include | Include | Equipment | 245 | 2023-02-20 | 490 | keep | 0 | Feb | 2023 | 0.00033374 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-20 14:09 | 2023-02-20 19:51 | 13 | 5:42 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN C/L DESGANCHE | B23022000107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2023-02-20 | 4446 | keep | 0 | Feb | 2023 | 0.0030282 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2023-02-20 14:19 | 2023-02-20 18:35 | 10 | 4:16 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SECUNDARIA CRUZADA | M23022000112 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 256 | 2023-02-20 | 2560 | keep | 0 | Feb | 2023 | 0.0017436 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-20 14:20 | 2023-02-20 21:14 | 12 | 6:54 | P | ERROR HUMANO | EN REMPLAZO DE PM AL REALIZAR OPERACIONES COLOCARON PISTOLA EN PARKING BUSHING INADVERTIDAMENTE, SE COLOCO PISTOLA EN BUSHING PRIMARIO Y QUEDO EN SERVICIO | S23022000174 | New_Event | Human Error | Include | Include | Other | 414 | 2023-02-20 | 4968 | keep | 0 | Feb | 2023 | 0.0033837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-02-20 14:25 | 2023-02-20 15:42 | 420 | 1:17 | P | CAUSAS EXTERNAS | CORTE DE LINEA ABIERTO SE DISPARO INTERRUPTOR | M23022000091 | Partial_restoration | Damage From Public | Include | Include | Public | 77 | 2023-02-20 | 32340 | keep | 0 | Feb | 2023 | 0.022027 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-20 14:27 | 2023-02-20 14:52 | 10 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022000089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-02-20 | 250 | keep | 0 | Feb | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-02-20 14:31 | 2023-02-20 19:15 | 12 | 4:44 | P | DESGANCHE | 2 X 50 EN CL DESGANCHE | P23022000100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2023-02-20 | 3408 | keep | 0 | Feb | 2023 | 0.0023212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-02-20 14:58 | 2023-02-20 15:39 | 5 | 0:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR CONECTOR SECUNDARIO EN BAJANTE DE XMR | C23021900161 | New_Event | Secondary Wire Break | Include | Include | Equipment | 41 | 2023-02-20 | 205 | keep | 0 | Feb | 2023 | 0.00013962 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-02-20 15:21 | 2023-02-20 17:01 | 10 | 1:40 | P | CAUSAS EXTERNAS | 1 X 10 EN XMR SE REMPLAZO XMR DE 50 KVA X 50 KVA AVERIADO POR DISPAROS | R23022000042 | New_Event | Damage From Public | Include | Include | Public | 100 | 2023-02-20 | 1000 | keep | 0 | Feb | 2023 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-02-20 15:22 | 2023-02-20 15:23 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23022000111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-20 | 2379 | keep | 0 | Feb | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2023-02-20 15:32 | 2023-02-20 16:40 | 1 | 1:08 | P | DESGANCHE | 1 X 15 EN C/L Y DESGANCHE | B23022000118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-02-20 | 68 | keep | 0 | Feb | 2023 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-20 15:36 | 2023-02-20 18:10 | 1 | 2:34 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN RISER APARENTE AVERIA EN CABLE SOTERRADO DEL CLIENTE | P23022000112 | New_Event | Customer-Related Interruption | Include | Include | Public | 154 | 2023-02-20 | 154 | keep | 0 | Feb | 2023 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-20 15:42 | 2023-02-20 15:58 | 828 | 0:16 | T | CONDUCTOR ARRIADO O CRUZADO | SE VERIFICO CON PERSONAL QUE PATRULLA EL ALIMENTADOR Y SE CERRO INTERRUPTOR | M23022000121 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 16 | 2023-02-20 | 13248 | keep | 0 | Feb | 2023 | 0.0090232 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
YAUCO | 2023-02-20 15:50 | 2023-02-20 18:55 | 75 | 3:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M23022000122 | New_Event | Primary Wire Break | Include | Include | Equipment | 185 | 2023-02-20 | 13875 | keep | 0 | Feb | 2023 | 0.0094502 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-02-20 15:58 | 2023-02-20 17:45 | 420 | 1:47 | P | CAUSAS EXTERNAS | SE CORRIGIO CONDICION DE LINEA CRUZADA CON TENSOR Y SE CERRO CORTE DE LINEA | M23022000140 | Partial_restoration | Damage From Public | Include | Include | Public | 107 | 2023-02-20 | 44940 | keep | 0 | Feb | 2023 | 0.030608 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-20 16:00 | 2023-02-20 18:46 | 100 | 2:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y SE REMPLAZO CAJA PRIMARIA | B23022000125 | New_Event | Cutout Failure | Include | Include | Equipment | 166 | 2023-02-20 | 16600 | keep | 0 | Feb | 2023 | 0.011306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-02-20 16:02 | 2023-02-20 18:38 | 80 | 2:36 | P | DESGANCHE | 2 X 50 EN CL DESGANCHE | P23022000117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-02-20 | 12480 | keep | 0 | Feb | 2023 | 0.0085001 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-02-20 16:20 | 2023-02-20 21:17 | 30 | 4:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M23022000127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2023-02-20 | 8910 | keep | 0 | Feb | 2023 | 0.0060686 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-02-20 16:52 | 2023-02-20 18:00 | 32 | 1:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTE VIENTO | M23022000136 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 68 | 2023-02-20 | 2176 | keep | 0 | Feb | 2023 | 0.0014821 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2023-02-20 17:14 | 2023-02-21 14:08 | 1 | 20:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B23022000128 | New_Event | Cutout Failure | Include | Include | Equipment | 1254 | 2023-02-20 | 1254 | keep | 0 | Feb | 2023 | 0.00085409 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-20 17:22 | 2023-02-20 22:47 | 31 | 5:25 | P | TERMINACION SOTERRADA AVERIADA | 1 SMU 20 DE 100 AMP EN SU-8A SE REPARARON TERMINACIONES SOTERADAS | R23022000051 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 325 | 2023-02-20 | 10075 | keep | 0 | Feb | 2023 | 0.006862 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-02-20 17:31 | 2023-02-20 22:00 | 94 | 4:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO PORTAFUSIBLES | S23022000151 | New_Event | Cutout Failure | Include | Include | Equipment | 269 | 2023-02-20 | 25286 | keep | 0 | Feb | 2023 | 0.017222 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
UTUADO | 2023-02-20 17:31 | 2023-02-20 19:50 | 80 | 2:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LINEAS | A23022000098 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-02-20 | 11120 | keep | 0 | Feb | 2023 | 0.0075738 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-20 17:53 | 2023-02-20 18:27 | 1 | 0:34 | P | ERROR HUMANO | SE CERRO FUSIBLE EN XMR PERSONAL DE LUMA QUE ABRIO PREVIAMENTE EL XMR PARA INSTALAR C/L NUEVO, OLVIDO CERRAR DE VUELTA EL MISMO | C23022000131 | New_Event | Human Error | Include | Include | Other | 34 | 2023-02-20 | 34 | keep | 0 | Feb | 2023 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-20 18:04 | 2023-02-20 19:37 | 80 | 1:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L Y SE LEVANTO CONDUCTOR PRIMARIO | S23022000166 | New_Event | Primary Wire Break | Include | Include | Equipment | 93 | 2023-02-20 | 7440 | keep | 0 | Feb | 2023 | 0.0050674 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-02-20 18:46 | 2023-02-21 13:15 | 1 | 18:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23022000164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1109 | 2023-02-20 | 1109 | keep | 0 | Feb | 2023 | 0.00075533 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-20 18:47 | 2023-02-20 19:25 | 1 | 0:38 | P | ANIMAL | 1X40 EN C/L CRUCE POR AVE | C23022000133 | New_Event | Animals | Include | Include | Wildlife | 38 | 2023-02-20 | 38 | keep | 0 | Feb | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-02-20 18:59 | 2023-02-20 20:00 | 30 | 1:01 | P | DESGANCHE | 2 X 50 EN CL DESGANCHE | P23022000130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2023-02-20 | 1830 | keep | 0 | Feb | 2023 | 0.0012464 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-02-20 19:14 | 2023-02-21 06:40 | 10 | 11:26 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23022000134 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 686 | 2023-02-20 | 6860 | keep | 0 | Feb | 2023 | 0.0046723 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-20 19:29 | 2023-02-20 19:30 | 4 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C2302200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-20 | 4 | keep | 0 | Feb | 2023 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-20 19:51 | 2023-02-20 19:52 | 3438 | 0:01 | T | DESGANCHE | RECIERRE | B23022000145 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-20 | 3438 | keep | 0 | Feb | 2023 | 0.0023416 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-20 19:52 | 2023-02-20 20:23 | 13 | 0:31 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN C/L DESGANCHE | B23022000107 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 31 | 2023-02-20 | 403 | keep | 0 | Feb | 2023 | 0.00027448 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-02-20 20:05 | 2023-02-21 04:45 | 30 | 8:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REMPLAZO CAJA PRIMARIA | S23022000184 | New_Event | Cutout Failure | Include | Include | Equipment | 520 | 2023-02-20 | 15600 | keep | 0 | Feb | 2023 | 0.010625 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-20 20:12 | 2023-02-21 09:40 | 25 | 13:28 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B23022000150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 808 | 2023-02-20 | 20200 | keep | 0 | Feb | 2023 | 0.013758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-20 21:14 | 2023-02-20 21:15 | 2435 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVA LA CARGA 1907-05 | B2302200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-20 | 2435 | keep | 0 | Feb | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-02-20 21:14 | 2023-02-20 21:15 | 2956 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1909-08 LLEVA LA CARGA 1907-05 | B2302200000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-20 | 2956 | keep | 0 | Feb | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-02-20 21:15 | 2023-02-21 10:23 | 12 | 13:08 | P | ERROR HUMANO | EN REMPLAZO DE PM AL REALIZAR OPERACIONES COLOCARON PISTOLA EN PARKING BUSHING INADVERTIDAMENTE, SE COLOCO PISTOLA EN BUSHING PRIMARIO Y QUEDO EN SERVICIO | S23022000174 | Partial_restoration | Human Error | Include | Include | Other | 788 | 2023-02-20 | 9456 | keep | 0 | Feb | 2023 | 0.0064404 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-20 21:27 | 2023-02-21 11:45 | 348 | 14:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-C 1 X 50 RISER @ SU-E | S23022000195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 858 | 2023-02-20 | 298584 | keep | 0 | Feb | 2023 | 0.20336 | 0.00023702 | Sustained | FALSE | FALSE | Not_TMED_Event | 348
GUAYAMA | 2023-02-20 21:52 | 2023-02-21 11:04 | 17 | 13:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PRIMARIO | P23022000142 | New_Event | Primary Wire Break | Include | Include | Equipment | 792 | 2023-02-20 | 13464 | keep | 0 | Feb | 2023 | 0.0091703 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-02-20 22:22 | 2023-02-20 22:23 | 154 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1342-04 QUE LLEVA 25% DEL 1203-03 | S2302200000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-20 | 154 | keep | 0 | Feb | 2023 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2023-02-20 22:22 | 2023-02-20 22:23 | 390 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL 1342-04 QUE LLEVA 25% DEL 1203-03 | S2302200000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-20 | 390 | keep | 0 | Feb | 2023 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2023-02-20 22:23 | 2023-02-21 00:35 | 199 | 2:12 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR POR CONDUCTOR VIVO EN EL SUELO SJ-230221-01 | S23022000209 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 132 | 2023-02-20 | 26268 | keep | 0 | Feb | 2023 | 0.017891 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
CANOVANAS | 2023-02-20 22:30 | 2023-02-21 08:26 | 68 | 9:56 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | R23022000082 | New_Event | Animals | Include | Include | Wildlife | 596 | 2023-02-20 | 40528 | keep | 0 | Feb | 2023 | 0.027603 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2023-02-20 22:47 | 2023-02-20 22:48 | 118 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CARGA POR EL 1117-09 | S2302200000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-20 | 118 | keep | 0 | Feb | 2023 | 8.0369e-05 | 8.0369e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 118
SAN JUAN | 2023-02-20 22:47 | 2023-02-20 22:48 | 114 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CARGA POR EL 1117-09 | S2302200000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-20 | 114 | keep | 0 | Feb | 2023 | 7.7645e-05 | 7.7645e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 114
SAN JUAN | 2023-02-20 22:47 | 2023-02-20 22:48 | 316 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1115-02 Y EL 1115-04 | S2302200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-20 | 316 | keep | 0 | Feb | 2023 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
SAN JUAN | 2023-02-21 00:35 | 2023-02-21 02:59 | 154 | 2:24 | P | ALIMENTADOR AMARRADO | SE ABRE INTERRUPTOR 1342-04 QUE LLEVA 25% DEL 1203-03 PARA LEVANTAR PRIMARIA MEDIANTE SJ-230221-01 Y LUEGO SE NORMALIZO LAS CARGAS | S2302200000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 144 | 2023-02-21 | 22176 | keep | 0 | Feb | 2023 | 0.015104 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2023-02-21 00:35 | 2023-02-21 02:59 | 390 | 2:24 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR 1342-04 QUE LLEVA 25% DEL 1203-03 PARA LEVANTAR PRIMARIA MEDIANTE SJ-230221-01 Y LUEGO SE NORMALIZO LAS CARGAS | S23022000209 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 144 | 2023-02-21 | 56160 | keep | 0 | Feb | 2023 | 0.03825 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-02-21 00:53 | 2023-02-21 09:33 | 10 | 8:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR POSTAFUSIBLE AVERIADO | M23022100001 | New_Event | Cutout Failure | Include | Include | Equipment | 520 | 2023-02-21 | 5200 | keep | 0 | Feb | 2023 | 0.0035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-21 01:36 | 2023-02-21 10:40 | 50 | 9:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A23022100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 544 | 2023-02-21 | 27200 | keep | 0 | Feb | 2023 | 0.018526 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-21 05:22 | 2023-02-21 05:23 | 551 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR EN SERVICIO | C23022100001 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-21 | 551 | keep | 0 | Feb | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2023-02-21 05:23 | 2023-02-21 11:26 | 1 | 6:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L REMPLAZO 2 CAJAS AVERIADAS | C23022100015 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 363 | 2023-02-21 | 363 | keep | 0 | Feb | 2023 | 0.00024724 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-21 05:50 | 2023-02-21 11:51 | 76 | 6:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REEMPLAZO CAJA AVERIADA | C23022100003 | New_Event | Cutout Failure | Include | Include | Equipment | 361 | 2023-02-21 | 27436 | keep | 0 | Feb | 2023 | 0.018687 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
CAGUAS | 2023-02-21 05:58 | 2023-02-21 05:59 | 1702 | 0:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C23022100004 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2023-02-21 | 1702 | keep | 0 | Feb | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-02-21 05:59 | 2023-02-21 11:15 | 217 | 5:16 | P | CABLE SOTERRADO AVERIADO | 1 FASE DEL RISER ESTA AVERIADA, SE COLOCO JUMPER | C23022100005 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 316 | 2023-02-21 | 68572 | keep | 0 | Feb | 2023 | 0.046704 | 0.0001478 | Sustained | FALSE | FALSE | Not_TMED_Event | 217
PONCE | 2023-02-21 06:28 | 2023-02-21 11:00 | 60 | 4:32 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PRIMARIO | P23022100031 | New_Event | Primary Wire Break | Include | Include | Equipment | 272 | 2023-02-21 | 16320 | keep | 0 | Feb | 2023 | 0.011115 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-21 06:30 | 2023-02-21 12:59 | 15 | 6:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S23022100019 | New_Event | Cutout Failure | Include | Include | Equipment | 389 | 2023-02-21 | 5835 | keep | 0 | Feb | 2023 | 0.0039742 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-21 06:49 | 2023-02-21 06:50 | 1483 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 SE CERRO POR SCADA LLEVA 30% DEL 1204-04 | S2302210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-21 | 1483 | keep | 0 | Feb | 2023 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-02-21 06:49 | 2023-02-21 06:50 | 1531 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 SE CERRO POR SCADA LLEVA 15% DE 1204-05 | S2302210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-21 | 1531 | keep | 0 | Feb | 2023 | 0.0010428 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-02-21 06:49 | 2023-02-21 06:50 | 312 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 5% DE SU CARGA POR EL 1336-08 | S2302210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-21 | 312 | keep | 0 | Feb | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-02-21 06:49 | 2023-02-21 06:50 | 5290 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 5% DEL 1336-07 LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 | S2302210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-21 | 5290 | keep | 0 | Feb | 2023 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
ARECIBO | 2023-02-21 07:11 | 2023-02-21 09:30 | 80 | 2:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REPARO AISLADOR | A23022100006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 139 | 2023-02-21 | 11120 | keep | 0 | Feb | 2023 | 0.0075738 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-02-21 07:12 | 2023-02-21 12:14 | 75 | 5:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEAS POR DESGANCHE | M23022100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2023-02-21 | 22650 | keep | 0 | Feb | 2023 | 0.015427 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-02-21 08:10 | 2023-02-21 13:46 | 15 | 5:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | S23022100025 | New_Event | Cutout Failure | Include | Include | Equipment | 336 | 2023-02-21 | 5040 | keep | 0 | Feb | 2023 | 0.0034327 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-02-21 08:13 | 2023-02-21 09:27 | 10 | 1:14 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23022100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2023-02-21 | 740 | keep | 0 | Feb | 2023 | 0.00050401 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-21 08:23 | 2023-02-21 08:24 | 138 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1206-04 LLEVA 10% DEL 1204-03 | S2302210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-21 | 138 | keep | 0 | Feb | 2023 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-02-21 08:23 | 2023-02-21 08:24 | 1425 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1206-04 QUE LLEVA 40% DEL 1204-04 | S2302210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-21 | 1425 | keep | 0 | Feb | 2023 | 0.00097056 | 0.00097056 | Momentary | FALSE | FALSE | Not_TMED_Event | 1425
SAN JUAN | 2023-02-21 08:23 | 2023-02-21 08:24 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 10% DEL 1204-03 LLEVA 40% DEL 1204-04 | S2302210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-21 | 1799 | keep | 0 | Feb | 2023 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
BAYAMON | 2023-02-21 08:34 | 2023-02-21 15:04 | 15 | 6:30 | P | NO SE REPORTO CAUSA | SE CERRO SU-6 DE PLAZA DORADO | B23022100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 390 | 2023-02-21 | 5850 | keep | 0 | Feb | 2023 | 0.0039844 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-21 08:47 | 2023-02-21 14:57 | 10 | 6:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23021000151 | New_Event | Secondary Wire Break | Include | Include | Equipment | 370 | 2023-02-21 | 3700 | keep | 0 | Feb | 2023 | 0.0025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-21 08:52 | 2023-02-21 08:54 | 1894 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 SE ENCONTRÃ“ VEGETACIÃ“N Y 2 FUSIBLES FUNDIDOS EN SUB. 2476 AAA | R23022100021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-02-21 | 3788 | keep | 0 | Feb | 2023 | 0.00258 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2023-02-21 08:52 | 2023-02-21 08:54 | 4154 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 SE ENCONTRÃ“ VEGETACIÃ“N Y 2 FUSIBLES FUNDIDOS EN SUB. 2476 AAA | R23022100021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-02-21 | 8308 | keep | 0 | Feb | 2023 | 0.0056585 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2023-02-21 08:52 | 2023-02-21 08:54 | 424 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 SE ENCONTRÃ“ VEGETACIÃ“N Y 2 FUSIBLES FUNDIDOS EN SUB. 2476 AAA | R23022100021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-02-21 | 848 | keep | 0 | Feb | 2023 | 0.00057757 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2023-02-21 08:52 | 2023-02-21 09:05 | 2708 | 0:13 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 SE ENCONTRÃ“ VEGETACIÃ“N Y 2 FUSIBLES FUNDIDOS EN SUB. 2476 AAA | R23022100022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2023-02-21 | 35204 | keep | 0 | Feb | 2023 | 0.023977 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-02-21 08:52 | 2023-02-21 10:33 | 2524 | 1:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100, SE SECCIONALIZO ALIMENTADOR ABRIENDO EN SU-11 AL SU-12 SE ENCONTRÃ“ VEGETACIÃ“N Y 2 FUSIBLES FUNDIDOS EN SUB. 2476 AAA | R23022100022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 101 | 2023-02-21 | 254924 | keep | 0 | Feb | 2023 | 0.17363 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2023-02-21 08:52 | 2023-02-21 09:27 | 1648 | 0:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 SE ENCONTRÃ“ VEGETACIÃ“N Y 2 FUSIBLES FUNDIDOS EN SUB. 2476 AAA | R23022100022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2023-02-21 | 57680 | keep | 0 | Feb | 2023 | 0.039286 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-02-21 08:52 | 2023-02-21 08:54 | 2580 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 SE ENCONTRÃ“ VEGETACIÃ“N Y 2 FUSIBLES FUNDIDOS EN SUB. 2476 AAA | R23022100022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-02-21 | 5160 | keep | 0 | Feb | 2023 | 0.0035145 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2023-02-21 08:52 | 2023-02-21 08:54 | 500 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 SE ENCONTRÃ“ VEGETACIÃ“N Y 2 FUSIBLES FUNDIDOS EN SUB. 2476 AAA | R23022100022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-02-21 | 1000 | keep | 0 | Feb | 2023 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2023-02-21 08:53 | 2023-02-21 16:09 | 10 | 7:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 30 EN C/L REEMPLAZO CAJA Y BAJANTE | C23022100014 | New_Event | Cutout Failure | Include | Include | Equipment | 436 | 2023-02-21 | 4360 | keep | 0 | Feb | 2023 | 0.0029696 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-21 08:55 | 2023-02-21 19:12 | 6 | 10:17 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO | S23022100031 | New_Event | Primary Pole Failure | Include | Include | Equipment | 617 | 2023-02-21 | 3702 | keep | 0 | Feb | 2023 | 0.0025214 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-02-21 08:55 | 2023-02-21 11:20 | 1 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23022100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-02-21 | 145 | keep | 0 | Feb | 2023 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-21 09:14 | 2023-02-21 12:40 | 15 | 3:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | M23022100033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 206 | 2023-02-21 | 3090 | keep | 0 | Feb | 2023 | 0.0021046 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-02-21 09:24 | 2023-02-21 12:15 | 1 | 2:51 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23022100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2023-02-21 | 171 | keep | 0 | Feb | 2023 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-21 09:46 | 2023-02-21 14:00 | 40 | 4:14 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO PARTIDO | M23022100085 | New_Event | Primary Pole Failure | Include | Include | Equipment | 254 | 2023-02-21 | 10160 | keep | 0 | Feb | 2023 | 0.0069199 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-21 09:59 | 2023-02-21 15:28 | 1 | 5:29 | P | DESGANCHE | DESGANCHO Y REPARO BAJANTE DE LINEA A CAJA NO FUNDIO | C23022100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 329 | 2023-02-21 | 329 | keep | 0 | Feb | 2023 | 0.00022408 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-21 10:03 | 2023-02-21 11:50 | 50 | 1:47 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA POR IMPACTO DE CAMION | M23022100042 | New_Event | Damage From Public | Include | Include | Public | 107 | 2023-02-21 | 5350 | keep | 0 | Feb | 2023 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-21 10:25 | 2023-02-21 12:50 | 59 | 2:25 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | R23022100004 | New_Event | Animals | Include | Include | Wildlife | 145 | 2023-02-21 | 8555 | keep | 0 | Feb | 2023 | 0.0058268 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
CANOVANAS | 2023-02-21 10:33 | 2023-02-21 11:20 | 1767 | 0:47 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPLAZO CAJA QUEMADA EN EL SU-11 SE DESCONTAMINO TERMINACION DE SU-11 A RISER DE SALIDA | R23022100022 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 47 | 2023-02-21 | 83049 | keep | 0 | Feb | 2023 | 0.056564 | 0.0012035 | Sustained | FALSE | FALSE | Not_TMED_Event | 1767
BAYAMON | 2023-02-21 10:40 | 2023-02-21 12:17 | 25 | 1:37 | P | DESGANCHE | 1 X 30 EN C/L SE RETIRO RAMA | S23022100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-02-21 | 2425 | keep | 0 | Feb | 2023 | 0.0016517 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-02-21 11:03 | 2023-02-21 12:50 | 1 | 1:47 | P | DESGANCHE | 1 X 30 EN C/L | C23022100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-02-21 | 107 | keep | 0 | Feb | 2023 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-21 11:15 | 2023-02-21 14:38 | 50 | 3:23 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEA | S23022100050 | New_Event | Animals | Include | Include | Wildlife | 203 | 2023-02-21 | 10150 | keep | 0 | Feb | 2023 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-02-21 11:15 | 2023-02-21 11:20 | 1702 | 0:05 | T | CABLE SOTERRADO AVERIADO | DISPARO PERSONAL REALIZANDO PRUEBAS CERRADO X CONTROL | C23022100045 | New_Event | UG Cable Fault | Include | Include | Equipment | 5 | 2023-02-21 | 8510 | keep | 0 | Feb | 2023 | 0.0057961 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BAYAMON | 2023-02-21 11:18 | 2023-02-21 11:40 | 13 | 0:22 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR PARA CONECTAR CLIENTE | B23022100048 | New_Event | Customer-Related Interruption | Include | Include | Public | 22 | 2023-02-21 | 286 | keep | 0 | Feb | 2023 | 0.00019479 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-02-21 11:20 | 2023-02-21 13:55 | 217 | 2:35 | P | CABLE SOTERRADO AVERIADO | 1 FASE DEL RISER ESTA AVERIADA, SE COLOCO JUMPER | C23022100005 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 155 | 2023-02-21 | 33635 | keep | 0 | Feb | 2023 | 0.022909 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-21 11:45 | 2023-02-21 17:20 | 27 | 5:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50KVA X 37.5KVA | S23022100081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 335 | 2023-02-21 | 9045 | keep | 0 | Feb | 2023 | 0.0061605 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2023-02-21 11:47 | 2023-02-21 12:54 | 30 | 1:07 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE CRITICO RAMAS CRUZANDO FASES | R23022100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2023-02-21 | 2010 | keep | 0 | Feb | 2023 | 0.001369 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-21 11:50 | 2023-02-21 11:51 | 450 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-21 | 450 | keep | 0 | Feb | 2023 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
FAJARDO | 2023-02-21 11:54 | 2023-02-21 11:55 | 2041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2302210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-21 | 2041 | keep | 0 | Feb | 2023 | 0.0013901 | 0.0013901 | Momentary | FALSE | FALSE | Not_TMED_Event | 2041
GUAYAMA | 2023-02-21 11:54 | 2023-02-21 13:49 | 50 | 1:55 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23022100116 | New_Event | Animals | Include | Include | Wildlife | 115 | 2023-02-21 | 5750 | keep | 0 | Feb | 2023 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-21 12:27 | 2023-02-21 17:17 | 2 | 4:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 15 EN XMR Y SE REPARO SECUNDARIA | B23022100056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 290 | 2023-02-21 | 580 | keep | 0 | Feb | 2023 | 0.00039504 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-02-21 12:45 | 2023-02-21 13:18 | 10 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTES SECUNDARIOS | P23022100126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-02-21 | 330 | keep | 0 | Feb | 2023 | 0.00022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-21 12:47 | 2023-02-21 15:08 | 10 | 2:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022100072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 141 | 2023-02-21 | 1410 | keep | 0 | Feb | 2023 | 0.00096034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-21 13:18 | 2023-02-21 18:55 | 241 | 5:37 | P | DESGANCHE | SE DESGANCHO Y SE RETEZO LINEA PRIMARIA SE REPUSO 1X100 CL | S23022100083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2023-02-21 | 81217 | keep | 0 | Feb | 2023 | 0.055317 | 0.00016414 | Sustained | FALSE | FALSE | Not_TMED_Event | 241
BAYAMON | 2023-02-21 13:18 | 2023-02-21 13:19 | 2402 | 0:01 | T | DESGANCHE | RECERRO LLEVA 1720-08 | S2302210000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-21 | 2402 | keep | 0 | Feb | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2023-02-21 13:18 | 2023-02-21 13:19 | 1 | 0:01 | T | ALIMENTADOR AMARRADO | 1709-02 RECERRO Y LLEVA 1720-08 | S2302210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-21 | 1 | keep | 0 | Feb | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-21 13:19 | 2023-02-21 17:00 | 85 | 3:41 | P | DESGANCHE | 2 X 65 EN RISER DESGANCHE | S23022100090 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 221 | 2023-02-21 | 18785 | keep | 0 | Feb | 2023 | 0.012794 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CANOVANAS | 2023-02-21 13:26 | 2023-02-21 13:46 | 10 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BARRA SULFATADA EN PEDESTAL | R23022100002 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-02-21 | 200 | keep | 0 | Feb | 2023 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-21 13:34 | 2023-02-21 14:48 | 80 | 1:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23022100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-02-21 | 5920 | keep | 0 | Feb | 2023 | 0.0040321 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-02-21 13:36 | 2023-02-21 14:42 | 1342 | 1:06 | T | CABLE SOTERRADO AVERIADO | DISPARO SE SECCIONALIZO EL ALIMENTADOR 2 CLIENTES EN SERVICIO CG-230221-01 | C23022100062 | New_Event | UG Cable Fault | Include | Include | Equipment | 66 | 2023-02-21 | 88572 | keep | 0 | Feb | 2023 | 0.060326 | 0.00091403 | Sustained | FALSE | FALSE | Not_TMED_Event | 1342
SAN JUAN | 2023-02-21 13:42 | 2023-02-21 21:30 | 14 | 7:48 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PRIMARIO CAMION DE BASURA IMPACTA POSTE PRIMARIO | S23022100093 | New_Event | Damage From Public | Include | Include | Public | 468 | 2023-02-21 | 6552 | keep | 0 | Feb | 2023 | 0.0044625 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-02-21 13:46 | 2023-02-21 13:51 | 396 | 0:05 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR ERRONEO A PETICION DE JUAN C RAMOS POR AVERIA SE CERRO POR SCADA | S2302210000X | New_Event | Human Error | Include | Include | Other | 5 | 2023-02-21 | 1980 | keep | 0 | Feb | 2023 | 0.0013486 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
SAN JUAN | 2023-02-21 13:51 | 2023-02-21 15:29 | 15 | 1:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | S23022100025 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2023-02-21 | 1470 | keep | 0 | Feb | 2023 | 0.0010012 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-21 14:04 | 2023-02-21 14:58 | 390 | 0:54 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO BKR A PETICION DE JUAN C RAMOS PARA REPARA AVERIA SE REEMPLAZO CAJA PRIMARIA SE CERRO POR CONTROL | S23022100099 | New_Event | Cutout Failure | Include | Include | Equipment | 54 | 2023-02-21 | 21060 | keep | 0 | Feb | 2023 | 0.014344 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
FAJARDO | 2023-02-21 14:24 | 2023-02-21 17:49 | 6 | 3:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5KVA X 37.5KVA AVERIADO INTERNAMENTE | R23022100075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 205 | 2023-02-21 | 1230 | keep | 0 | Feb | 2023 | 0.00083775 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-02-21 14:42 | 2023-02-21 14:49 | 1340 | 0:07 | P | CABLE SOTERRADO AVERIADO | SE REALIZARON OPERACIONES EN EL CAMPO | C23022100062 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 7 | 2023-02-21 | 9380 | keep | 0 | Feb | 2023 | 0.0063887 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-02-21 14:45 | 2023-02-21 17:06 | 12 | 2:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO INTERNAMENTE 75KVA X 75KVA Y 1X10 EN XMR | R23022100076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 141 | 2023-02-21 | 1692 | keep | 0 | Feb | 2023 | 0.0011524 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-02-21 14:49 | 2023-02-21 14:54 | 1342 | 0:05 | T | CABLE SOTERRADO AVERIADO | DISPARO SE SECCIONALIZO EL ALIMENTADOR CG-230221-01 | C23022100062 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 5 | 2023-02-21 | 6710 | keep | 0 | Feb | 2023 | 0.0045702 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-21 14:54 | 2023-02-21 15:58 | 1340 | 1:04 | P | CABLE SOTERRADO AVERIADO | SE REALIZARON OPERACIONES 25% EN SERVICIO | C23022100062 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 64 | 2023-02-21 | 85760 | keep | 0 | Feb | 2023 | 0.058411 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-21 15:03 | 2023-02-21 18:42 | 1426 | 3:39 | P | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR PARTE POR 1346-02 SE CERRO MANUAL EN EL CAMPO INTERRUPTOR POR PORTATIL #19. LUEGO SE IDENTIFICO PARARRAYOS AVERIADO | S23022100119 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 219 | 2023-02-21 | 312294 | keep | 0 | Feb | 2023 | 0.2127 | 0.00097124 | Sustained | FALSE | FALSE | Not_TMED_Event | 1426
CAGUAS | 2023-02-21 15:04 | 2023-02-21 15:26 | 329 | 0:22 | T | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR N/O CONTRA EL 3015-06 RELACIONADO A AVERIA SOTERRADA DEL 3015-06 | C23022100094 | New_Event | UG Cable Fault | Include | Include | Equipment | 22 | 2023-02-21 | 7238 | keep | 0 | Feb | 2023 | 0.0049298 | 0.00022408 | Sustained | FALSE | FALSE | Not_TMED_Event | 329
UTUADO | 2023-02-21 15:04 | 2023-02-21 17:50 | 1 | 2:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23022100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-02-21 | 166 | keep | 0 | Feb | 2023 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-21 15:19 | 2023-02-21 15:20 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2302210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-21 | 3070 | keep | 0 | Feb | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
CAGUAS | 2023-02-21 15:58 | 2023-02-21 16:50 | 1006 | 0:52 | P | CABLE SOTERRADO AVERIADO | SE REALIZARON OPERACIONES ENTRO 60% EN SERVICIO | C23022100062 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 52 | 2023-02-21 | 52312 | keep | 0 | Feb | 2023 | 0.035629 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-21 15:58 | 2023-02-21 19:52 | 100 | 3:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 Y 2 X 65 EN DISTINTOS CORTES DE LINEAS FUERTE VIENTO | M23022100102 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 234 | 2023-02-21 | 23400 | keep | 0 | Feb | 2023 | 0.015938 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-02-21 16:01 | 2023-02-21 17:12 | 40 | 1:11 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | M23022100103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-02-21 | 2840 | keep | 0 | Feb | 2023 | 0.0019343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-02-21 16:05 | 2023-02-21 17:26 | 1 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | C23022100112 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2023-02-21 | 81 | keep | 0 | Feb | 2023 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-21 16:15 | 2023-02-21 21:28 | 8 | 5:13 | P | ANIMAL | 1 X 40 EN RISER CRUCE X AVE | B23022100091 | New_Event | Animals | Include | Include | Wildlife | 313 | 2023-02-21 | 2504 | keep | 0 | Feb | 2023 | 0.0017055 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-21 16:15 | 2023-02-21 17:28 | 50 | 1:13 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA BAJANTE DE LINEA PRIMARIA A CAJA EN CORTE DE LINEA | M23022100105 | New_Event | Primary Wire Break | Include | Include | Equipment | 73 | 2023-02-21 | 3650 | keep | 0 | Feb | 2023 | 0.002486 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-02-21 16:17 | 2023-02-21 17:40 | 54 | 1:23 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE, CERRO PUENTES Y NORMALIZO LAS CARGAS GOI CG-230217-02 | C23022100134 | New_Event | Primary Pole Failure | Include | Include | Equipment | 83 | 2023-02-21 | 4482 | keep | 0 | Feb | 2023 | 0.0030527 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
MAYAGÃœEZ | 2023-02-21 16:35 | 2023-02-21 16:36 | 411 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23022100110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-21 | 411 | keep | 0 | Feb | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
BAYAMON | 2023-02-21 16:47 | 2023-02-21 17:58 | 80 | 1:11 | P | CAUSAS EXTERNAS | 2 X 80 EN C/L SE RETIRO GLOBO | S23022100162 | New_Event | Damage From Public | Include | Include | Public | 71 | 2023-02-21 | 5680 | keep | 0 | Feb | 2023 | 0.0038686 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-02-21 16:50 | 2023-02-21 17:44 | 537 | 0:54 | P | CABLE SOTERRADO AVERIADO | SE CERRO N/O CONTRA EL 3006-01 98% EN SERVICIO CG-230221-01 | C23022100062 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 54 | 2023-02-21 | 28998 | keep | 0 | Feb | 2023 | 0.01975 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-21 16:56 | 2023-02-21 17:04 | 329 | 0:08 | T | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR N/O CONTRA EL 3015-06 RELACIONADO A AVERIA SOTERRADA DEL 3015-06 | C23022100094 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 8 | 2023-02-21 | 2632 | keep | 0 | Feb | 2023 | 0.0017926 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-02-21 17:40 | 2023-02-21 18:38 | 15 | 0:58 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23022100166 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-02-21 | 870 | keep | 0 | Feb | 2023 | 0.00059255 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-02-21 17:44 | 2023-02-22 22:51 | 17 | 29:07 | P | CABLE SOTERRADO AVERIADO | SE RAPARO CABLE SOTERRADO AVERIADO, SE CERRO DEL MH-2 HACIA MHA-3 CG-230221-01 | C23022100062 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1747 | 2023-02-21 | 29699 | keep | 0 | Feb | 2023 | 0.020228 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-02-21 18:29 | 2023-02-21 20:15 | 15 | 1:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23022100093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-02-21 | 1590 | keep | 0 | Feb | 2023 | 0.0010829 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-02-21 18:41 | 2023-02-21 18:42 | 800 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 3205-07 | C23022100148 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-21 | 800 | keep | 0 | Feb | 2023 | 0.00054488 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
CAGUAS | 2023-02-21 18:41 | 2023-02-21 18:42 | 3026 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE LLEVA 800 CLIENTES DEL 2603-08 1608 CLIENTES DEL 3205-07 X 3201-01 | C23022100148 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-21 | 3026 | keep | 0 | Feb | 2023 | 0.002061 | 0.002061 | Momentary | FALSE | FALSE | Not_TMED_Event | 3026
SAN JUAN | 2023-02-21 18:42 | 2023-02-21 19:34 | 50 | 0:52 | P | NO SE REPORTO CAUSA | 3 X 80 EN RISER 1 X 80 EN AEREO PROVISIONAL | S23022100119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2023-02-21 | 2600 | keep | 0 | Feb | 2023 | 0.0017708 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-02-21 18:42 | 2023-02-21 19:41 | 50 | 0:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | C23022100133 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 59 | 2023-02-21 | 2950 | keep | 0 | Feb | 2023 | 0.0020092 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-21 18:58 | 2023-02-21 20:31 | 11 | 1:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN XMR SE REMPLAZO CAJA PRIMARIA | R23022100091 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2023-02-21 | 1023 | keep | 0 | Feb | 2023 | 0.00069676 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-02-21 19:21 | 2023-02-21 21:49 | 100 | 2:28 | P | DESGANCHE | 1 X 100 EN C/L | C23022100144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-02-21 | 14800 | keep | 0 | Feb | 2023 | 0.01008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-02-21 20:43 | 2023-02-21 20:55 | 50 | 0:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN C/L | P23022100169 | New_Event | Primary Wire Break | Include | Include | Equipment | 12 | 2023-02-21 | 600 | keep | 0 | Feb | 2023 | 0.00040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-02-21 21:07 | 2023-02-22 07:20 | 1 | 10:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23022100106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 613 | 2023-02-21 | 613 | keep | 0 | Feb | 2023 | 0.00041751 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-02-21 21:46 | 2023-02-22 10:20 | 20 | 12:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A23022100110 | New_Event | Primary Wire Break | Include | Include | Equipment | 754 | 2023-02-21 | 15080 | keep | 0 | Feb | 2023 | 0.010271 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-21 21:51 | 2023-02-22 00:46 | 41 | 2:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR Y 1 X 50 EN C/L | C23022100159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2023-02-21 | 7175 | keep | 0 | Feb | 2023 | 0.0048869 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
AGUADILLA | 2023-02-21 22:27 | 2023-02-22 09:20 | 25 | 10:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23022100143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2023-02-21 | 16325 | keep | 0 | Feb | 2023 | 0.011119 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-02-21 22:46 | 2023-02-21 22:47 | 752 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE ALIMENTADOR , LLEVA CARGA DE 5011-04 | P23022100148 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-21 | 752 | keep | 0 | Feb | 2023 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2023-02-21 22:46 | 2023-02-21 22:47 | 2696 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CON RR EN OFF TIENE HOJA DE CONSERVACION PC-74280 LLEVA LA CARGA DEL 5011-04 | P23022100178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-21 | 2696 | keep | 0 | Feb | 2023 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
BAYAMON | 2023-02-22 00:56 | 2023-02-22 02:22 | 177 | 1:26 | P | ANIMAL | 1 X 100 EN RISER AVE | S23022200002 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-02-22 | 15222 | keep | 0 | Feb | 2023 | 0.010368 | 0.00012055 | Sustained | FALSE | FALSE | Not_TMED_Event | 177
CANOVANAS | 2023-02-22 03:20 | 2023-02-22 08:15 | 115 | 4:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN RISER MAL TIEMPO LLUVIA | R23022200003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 295 | 2023-02-22 | 33925 | keep | 0 | Feb | 2023 | 0.023106 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
VEGA BAJA | 2023-02-22 05:38 | 2023-02-22 19:26 | 20 | 13:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L Y Y SE REMPLAZO AISLADOR | B23022200091 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 828 | 2023-02-22 | 16560 | keep | 0 | Feb | 2023 | 0.011279 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-02-22 06:18 | 2023-02-22 08:47 | 2124 | 2:29 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR CARGA POR EL 1657-04 SE PATRULLO NO SE ENCONTRO CAUSA SE TRANSFIRIO LA CARGA AL 1658-12 YA QUE EL 1657-04 SE LLEVO LA ALTA. 30% EN SERVICIO | R23022200009 | New_Event | Feeder Load Transferred | Include | Include | Other | 149 | 2023-02-22 | 316476 | keep | 0 | Feb | 2023 | 0.21555 | 0.0014466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2124
CANOVANAS | 2023-02-22 06:18 | 2023-02-22 06:19 | 165 | 0:01 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | EN OPERACION DEL 1657-04 SE LLEVO LA ALTA, C.C.E. CERRO 0010 | R23022200012 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1 | 2023-02-22 | 165 | keep | 0 | Feb | 2023 | 0.00011238 | 0.00011238 | Momentary | FALSE | FALSE | Not_TMED_Event | 165
CANOVANAS | 2023-02-22 06:18 | 2023-02-22 06:19 | 1937 | 0:01 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | EN OPERACION DEL 1657-04 SE LLEVO LA ALTA, C.C.E. CERRO 0010 | R23022200012 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1 | 2023-02-22 | 1937 | keep | 0 | Feb | 2023 | 0.0013193 | 0.0013193 | Momentary | FALSE | FALSE | Not_TMED_Event | 1937
CANOVANAS | 2023-02-22 06:18 | 2023-02-22 06:19 | 363 | 0:01 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | EN OPERACION DEL 1657-04 SE LLEVO LA ALTA, C.C.E. CERRO 0010 | R23022200012 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1 | 2023-02-22 | 363 | keep | 0 | Feb | 2023 | 0.00024724 | 0.00024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 363
CANOVANAS | 2023-02-22 06:18 | 2023-02-22 06:19 | 14 | 0:01 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | EN OPERACION DEL 1657-04 SE LLEVO LA ALTA, C.C.E. CERRO 0010 | R23022200012 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1 | 2023-02-22 | 14 | keep | 0 | Feb | 2023 | 9.5353e-06 | 9.5353e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-02-22 06:19 | 2023-02-22 08:47 | 14 | 2:28 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 1118-07 SE PATRULLO NO SE ENCONTRO CAUSA SE TRANSFIRIO LA CARGA AL 1658-12 YA QUE SE LLEVO LA ALTA | R23022200009 | 1st_after_momentary | Feeder Breaker Failure | Include | Include | Equipment | 148 | 2023-02-22 | 2072 | keep | 0 | Feb | 2023 | 0.0014112 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
FAJARDO | 2023-02-22 07:16 | 2023-02-22 08:16 | 16 | 1:00 | P | DESGANCHE | 1 X 20 EN RISER SE RETIRO RAMA | R23022200039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2023-02-22 | 960 | keep | 0 | Feb | 2023 | 0.00065385 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-02-22 07:26 | 2023-02-22 12:06 | 10 | 4:40 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y SE REALIZO DESGANCHE SECUNDARIO | B23022200004 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 280 | 2023-02-22 | 2800 | keep | 0 | Feb | 2023 | 0.0019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-22 07:29 | 2023-02-22 11:25 | 25 | 3:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23022200003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 236 | 2023-02-22 | 5900 | keep | 0 | Feb | 2023 | 0.0040185 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-02-22 08:15 | 2023-02-22 09:30 | 8 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA RECONECTAR NEUTRAL SECUNDARIO | P23022200027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-02-22 | 600 | keep | 0 | Feb | 2023 | 0.00040866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-22 08:19 | 2023-02-22 08:20 | 74 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO LLEVA LA CARGA DEL 1912-07 | S2302220000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-22 | 74 | keep | 0 | Feb | 2023 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2023-02-22 08:19 | 2023-02-22 08:20 | 57 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO CARGA POR 1521-02 | S2302220000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-22 | 57 | keep | 0 | Feb | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2023-02-22 08:20 | 2023-02-22 12:00 | 30 | 3:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L Y 2 X 100 EN C/L ALTERNO | S23022200014 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 220 | 2023-02-22 | 6600 | keep | 0 | Feb | 2023 | 0.0044952 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-02-22 08:23 | 2023-02-22 08:28 | 752 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE ALIMENTADOR | P23022200012 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-02-22 | 3760 | keep | 0 | Feb | 2023 | 0.0025609 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2023-02-22 08:23 | 2023-02-22 08:28 | 2696 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR , LLEVA CARGA DE 5011-04 | P23022200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-02-22 | 13480 | keep | 0 | Feb | 2023 | 0.0091812 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
YAUCO | 2023-02-22 08:30 | 2023-02-22 09:19 | 10 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CRUCE EN LINEA SECUNDARIA 1 X 10 EN TRANSFORMADOR | P23022200016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-02-22 | 490 | keep | 0 | Feb | 2023 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-22 08:38 | 2023-02-22 11:19 | 8 | 2:41 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23022200017 | New_Event | Animals | Include | Include | Wildlife | 161 | 2023-02-22 | 1288 | keep | 0 | Feb | 2023 | 0.00087725 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-02-22 08:43 | 2023-02-22 08:44 | 1924 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23022200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-22 | 1924 | keep | 0 | Feb | 2023 | 0.0013104 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
CANOVANAS | 2023-02-22 08:47 | 2023-02-22 08:55 | 1487 | 0:08 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR CARGA POR EL 1657-04 SE PATRULLO NO SE ENCONTRO CAUSA SE TRANSFIRIO LA CARGA AL 1658-12 YA QUE EL 1657-04 SE LLEVO LA ALTA. 45% EN SERVICIO | R23022200009 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 8 | 2023-02-22 | 11896 | keep | 0 | Feb | 2023 | 0.0081023 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-02-22 08:55 | 2023-02-22 09:09 | 1699 | 0:14 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR CARGA POR EL 1657-04 SE PATRULLO NO SE ENCONTRO CAUSA SE TRANSFIRIO LA CARGA AL 1658-12 YA QUE EL 1657-04 SE LLEVO LA ALTA. 80% EN SERVICIO | R23022200009 | Additional_clients | Feeder Load Transferred | Include | Include | Other | 14 | 2023-02-22 | 23786 | keep | 0 | Feb | 2023 | 0.016201 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-02-22 09:09 | 2023-02-22 09:44 | 425 | 0:35 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR CARGA POR EL 1657-04 SE PATRULLO NO SE ENCONTRO CAUSA SE TRANSFIRIO LA CARGA AL 1658-12 YA QUE EL 1657-04 SE LLEVO LA ALTA. 100% EN SERVICIO | R23022200009 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 35 | 2023-02-22 | 14875 | keep | 0 | Feb | 2023 | 0.010131 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-02-22 09:10 | 2023-02-22 14:15 | 3 | 5:05 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN CORTE DE LINEA SE AJUSTO BUSHING FLOJOS A TRANSFORMADOR | A23022200015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 305 | 2023-02-22 | 915 | keep | 0 | Feb | 2023 | 0.0006232 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2023-02-22 09:10 | 2023-02-22 16:08 | 7 | 6:58 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN DISTINTOS CORTES DE LINEA SE REALIZO DESGANCHE | A23022200032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 418 | 2023-02-22 | 2926 | keep | 0 | Feb | 2023 | 0.0019929 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-02-22 09:26 | 2023-02-22 11:00 | 1 | 1:34 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER EVENTO TRANSFERIDO | A23022200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2023-02-22 | 94 | keep | 0 | Feb | 2023 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-22 09:45 | 2023-02-22 11:56 | 150 | 2:11 | P | CAUSAS EXTERNAS | 1 X 200 EN C/L CRUCE X GLOBO | C23022200030 | New_Event | Damage From Public | Include | Include | Public | 131 | 2023-02-22 | 19650 | keep | 0 | Feb | 2023 | 0.013384 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-02-22 09:51 | 2023-02-22 10:55 | 2 | 1:04 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR PAJARO | M23022200016 | New_Event | Animals | Include | Include | Wildlife | 64 | 2023-02-22 | 128 | keep | 0 | Feb | 2023 | 8.718e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-02-22 10:08 | 2023-02-22 11:02 | 12 | 0:54 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZO DE POSTE PRIMARIO PARTIDO | S23022200034 | New_Event | Primary Pole Failure | Include | Include | Equipment | 54 | 2023-02-22 | 648 | keep | 0 | Feb | 2023 | 0.00044135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-02-22 10:11 | 2023-02-22 10:50 | 9 | 0:39 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZO DE PARARAYO | C23022200043 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 39 | 2023-02-22 | 351 | keep | 0 | Feb | 2023 | 0.00023906 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2023-02-22 10:38 | 2023-02-22 12:20 | 2 | 1:42 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA MAQUINARIA PESADA LIMPIANDO TERRENO IMPACTA POSTE Y LINEAS SE CRUZARON | P23022200037 | New_Event | Damage From Public | Include | Include | Public | 102 | 2023-02-22 | 204 | keep | 0 | Feb | 2023 | 0.00013894 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-02-22 10:44 | 2023-02-22 13:16 | 5 | 2:32 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO DE XMR DE 37.5KVA X 50KVA | S23022200042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 152 | 2023-02-22 | 760 | keep | 0 | Feb | 2023 | 0.00051763 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-02-22 10:56 | 2023-02-22 10:58 | 726 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA LA CARGA DEL 1346-04 | S2302220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-22 | 1452 | keep | 0 | Feb | 2023 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-02-22 10:56 | 2023-02-22 10:58 | 3932 | 0:02 | T | ALIMENTADOR AMARRADO | SE CERRO POR SCADA CARGA POR 1303-03 | S2302220000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-22 | 7864 | keep | 0 | Feb | 2023 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2023-02-22 11:02 | 2023-02-22 11:07 | 4291 | 0:05 | T | NO SE REPORTO CAUSA | SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | S23022200048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-02-22 | 21455 | keep | 0 | Feb | 2023 | 0.014613 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
CAGUAS | 2023-02-22 11:02 | 2023-02-22 14:08 | 1 | 3:06 | P | TRANSFORMADOR AVERIADO | 2 X 15 EN XMR REEMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | C23022200066 | New_Event | Service Transformer Failure | Include | Include | Equipment | 186 | 2023-02-22 | 186 | keep | 0 | Feb | 2023 | 0.00012668 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-22 11:07 | 2023-02-22 17:25 | 12 | 6:18 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZO DE POSTE PRIMARIO PARTIDO | S23022200034 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 378 | 2023-02-22 | 4536 | keep | 0 | Feb | 2023 | 0.0030894 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-02-22 11:16 | 2023-02-22 13:37 | 11 | 2:21 | P | DESGANCHE | 1 X 30 NEN CORTE DE LINEA POR DESGANCHE | P23022200044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-02-22 | 1551 | keep | 0 | Feb | 2023 | 0.0010564 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2023-02-22 11:25 | 2023-02-22 23:00 | 1125 | 11:35 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PUENTE ABIERTO MEDIANTE BY-230222-03 Y SE CERRO N/O CONTRA 8404-04, TODO EL MUNDO EN SERVICIO | B23022200126 | New_Event | Primary Wire Break | Include | Include | Equipment | 695 | 2023-02-22 | 781875 | keep | 0 | Feb | 2023 | 0.53253 | 0.00076623 | Sustained | FALSE | FALSE | Not_TMED_Event | 1125
CAGUAS | 2023-02-22 11:29 | 2023-02-22 12:49 | 8 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C23022200075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-02-22 | 640 | keep | 0 | Feb | 2023 | 0.0004359 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-22 11:44 | 2023-02-22 12:16 | 10 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022200066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2023-02-22 | 320 | keep | 0 | Feb | 2023 | 0.00021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-22 11:49 | 2023-02-22 12:56 | 11 | 1:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE DE NEUTRAL SECUNDARIO | S23022200068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 67 | 2023-02-22 | 737 | keep | 0 | Feb | 2023 | 0.00050197 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-02-22 11:56 | 2023-02-22 13:08 | 37 | 1:12 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23022200044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-02-22 | 2664 | keep | 0 | Feb | 2023 | 0.0018144 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
GUAYAMA | 2023-02-22 12:30 | 2023-02-22 13:32 | 25 | 1:02 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA LINEAS SE CRUZARON AL TRABAJAR RETEZANDO | P23022200051 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 62 | 2023-02-22 | 1550 | keep | 0 | Feb | 2023 | 0.0010557 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-02-22 12:47 | 2023-02-22 14:19 | 8 | 1:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA SULFATADA. | R23022200105 | New_Event | Cutout Failure | Include | Include | Equipment | 92 | 2023-02-22 | 736 | keep | 0 | Feb | 2023 | 0.00050129 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-22 13:00 | 2023-02-22 13:45 | 10 | 0:45 | P | TRANSFORMADOR AVERIADO | ABRE TRANSFORMADOR Y SE AJUSTA BUSHING SECUNDARIOS | M23022200037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2023-02-22 | 450 | keep | 0 | Feb | 2023 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-02-22 13:23 | 2023-02-22 19:45 | 60 | 6:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M23022200038 | New_Event | Cutout Failure | Include | Include | Equipment | 382 | 2023-02-22 | 22920 | keep | 0 | Feb | 2023 | 0.015611 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-02-22 13:33 | 2023-02-22 13:50 | 8 | 0:17 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE PRIMARIO EN TRANSFORMADOR | A23022200052 | New_Event | Primary Wire Break | Include | Include | Equipment | 17 | 2023-02-22 | 136 | keep | 0 | Feb | 2023 | 9.2629e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-22 13:45 | 2023-02-22 16:08 | 18 | 2:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO TRAMO SECUNDARIO PARTIDO | S23022200090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 143 | 2023-02-22 | 2574 | keep | 0 | Feb | 2023 | 0.0017531 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2023-02-22 13:53 | 2023-02-22 14:09 | 8 | 0:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | A23022200058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 16 | 2023-02-22 | 128 | keep | 0 | Feb | 2023 | 8.718e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-02-22 13:56 | 2023-02-22 15:41 | 18 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR Y REEMPLAZARON CONECTORES SULFATADOS EN SECUNDARIA. | R23022200107 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2023-02-22 | 1890 | keep | 0 | Feb | 2023 | 0.0012873 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2023-02-22 14:18 | 2023-02-22 14:21 | 2364 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR Y CERRO POR CONTROL | B2302220000X | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-02-22 | 7092 | keep | 0 | Feb | 2023 | 0.0048303 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
VEGA BAJA | 2023-02-22 14:18 | 2023-02-22 18:10 | 15 | 3:52 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23022200061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-02-22 | 3480 | keep | 0 | Feb | 2023 | 0.0023702 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-22 14:21 | 2023-02-22 20:29 | 1197 | 6:08 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO MACHETE Y SE REPARO PUENTE PRIMARIO MEDIANTE GOI-BY-230222-01 | B23022200077 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 368 | 2023-02-22 | 440496 | keep | 0 | Feb | 2023 | 0.30002 | 0.00081527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1197
MAYAGÃœEZ | 2023-02-22 14:44 | 2023-02-22 14:45 | 637 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23022200053 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-22 | 637 | keep | 0 | Feb | 2023 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2023-02-22 14:45 | 2023-02-22 18:55 | 50 | 4:10 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M23022200060 | 1st_after_momentary | Animals | Include | Include | Wildlife | 250 | 2023-02-22 | 12500 | keep | 0 | Feb | 2023 | 0.0085137 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-02-22 14:56 | 2023-02-22 14:57 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23022200074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-22 | 2697 | keep | 0 | Feb | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
PONCE | 2023-02-22 15:31 | 2023-02-22 17:09 | 101 | 1:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RERMPLAZO DE CAJA PIMARIA QUEMADA 1 X 65 EN CORTE DE LINEA | P23022200083 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2023-02-22 | 9898 | keep | 0 | Feb | 2023 | 0.0067415 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
SAN JUAN | 2023-02-22 15:47 | 2023-02-22 16:39 | 20 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL SECUNDARIO ABIERTO Y SE REMPLAZO BAJANTE SECUNDARIO EN XMR | S23022200120 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-02-22 | 1040 | keep | 0 | Feb | 2023 | 0.00070834 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-22 15:52 | 2023-02-22 17:30 | 11 | 1:38 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO NEUTRAL SECUNDARIO ABIERTO | S23022200121 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 98 | 2023-02-22 | 1078 | keep | 0 | Feb | 2023 | 0.00073422 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2023-02-22 15:52 | 2023-02-22 16:55 | 9 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23022200073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2023-02-22 | 567 | keep | 0 | Feb | 2023 | 0.00038618 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-02-22 16:05 | 2023-02-22 19:02 | 8 | 2:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS AVERIADAS | M23022200066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 177 | 2023-02-22 | 1416 | keep | 0 | Feb | 2023 | 0.00096443 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-22 16:09 | 2023-02-22 21:18 | 200 | 5:09 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | B23022200074 | New_Event | Primary Wire Break | Include | Include | Equipment | 309 | 2023-02-22 | 61800 | keep | 0 | Feb | 2023 | 0.042092 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2023-02-22 16:09 | 2023-02-22 16:10 | 1843 | 0:01 | T | DESGANCHE | RECIERRE | C23022200106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-22 | 1843 | keep | 0 | Feb | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-02-22 16:10 | 2023-02-22 18:36 | 84 | 2:26 | P | DESGANCHE | 2 X 80 EN C/L SE DESGANCHO | C23022200107 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-02-22 | 12264 | keep | 0 | Feb | 2023 | 0.008353 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
AGUADILLA | 2023-02-22 16:21 | 2023-02-22 17:37 | 10 | 1:16 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE SECUNDARIO | M23022200071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 76 | 2023-02-22 | 760 | keep | 0 | Feb | 2023 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-02-22 16:22 | 2023-02-22 16:23 | 2039 | 0:01 | T | DESGANCHE | RECIERRE | P23022200089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-22 | 2039 | keep | 0 | Feb | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2023-02-22 16:23 | 2023-02-22 18:05 | 94 | 1:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23022200090 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-02-22 | 9588 | keep | 0 | Feb | 2023 | 0.0065303 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
CAGUAS | 2023-02-22 16:34 | 2023-02-22 19:28 | 8 | 2:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23022200110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 174 | 2023-02-22 | 1392 | keep | 0 | Feb | 2023 | 0.00094808 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-22 16:52 | 2023-02-22 19:24 | 16 | 2:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE DIERON CONECTORES NUEVOS EN SECUNDARIA | S23022200130 | New_Event | Secondary Wire Break | Include | Include | Equipment | 152 | 2023-02-22 | 2432 | keep | 0 | Feb | 2023 | 0.0016564 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-02-22 17:10 | 2023-02-22 23:13 | 82 | 6:03 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L SE RETIRO SECUNDARIA ENREDADA CON PRIMARIA IMPACTADA POR CAMION | B23022200086 | New_Event | Damage From Public | Include | Include | Public | 363 | 2023-02-22 | 29766 | keep | 0 | Feb | 2023 | 0.020273 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
UTUADO | 2023-02-22 17:17 | 2023-02-24 11:56 | 1 | 42:39 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO SE REPORTO CAUSA VERIFICADO EN OMS ES DEL DIA 22 DE FEB DE 2023 COMO FASE FUERA/SERVICIO | A23022200083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2559 | 2023-02-22 | 2559 | keep | 0 | Feb | 2023 | 0.0017429 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-22 17:36 | 2023-02-22 18:25 | 6 | 0:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCOTRO CAUSA | A23022200086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2023-02-22 | 294 | keep | 0 | Feb | 2023 | 0.00020024 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-02-22 17:58 | 2023-02-22 17:59 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23022200095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-22 | 2113 | keep | 0 | Feb | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
BAYAMON | 2023-02-22 19:05 | 2023-02-22 23:58 | 139 | 4:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | B23022200110 | New_Event | Cutout Failure | Include | Include | Equipment | 293 | 2023-02-22 | 40727 | keep | 0 | Feb | 2023 | 0.027739 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
SAN JUAN | 2023-02-22 19:21 | 2023-02-22 22:00 | 17 | 2:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022200179 | New_Event | Secondary Wire Break | Include | Include | Equipment | 159 | 2023-02-22 | 2703 | keep | 0 | Feb | 2023 | 0.001841 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-02-22 19:33 | 2023-02-22 21:00 | 7 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | A23022200090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2023-02-22 | 609 | keep | 0 | Feb | 2023 | 0.00041479 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-02-22 19:45 | 2023-02-22 21:00 | 4 | 1:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | A23022200091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 75 | 2023-02-22 | 300 | keep | 0 | Feb | 2023 | 0.00020433 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-02-22 20:08 | 2023-02-23 10:53 | 3 | 14:45 | P | CONDUCTOR ROTO O ABIERTO | 1 X 5 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23022200084 | New_Event | Primary Wire Break | Include | Include | Equipment | 885 | 2023-02-22 | 2655 | keep | 0 | Feb | 2023 | 0.0018083 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2023-02-22 20:33 | 2023-02-22 23:47 | 25 | 3:14 | P | CABLE SOTERRADO AVERIADO | AVERIA DE RISER A T-10 SE DIO SERVICIO A TRAVES DEL NO EN T-8 | P23022200103 | New_Event | UG Cable Fault | Include | Include | Equipment | 194 | 2023-02-22 | 4850 | keep | 0 | Feb | 2023 | 0.0033033 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-02-22 21:24 | 2023-02-22 21:25 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23022200112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-22 | 1746 | keep | 0 | Feb | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
SAN JUAN | 2023-02-22 21:30 | 2023-02-22 21:31 | 1268 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2302220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-22 | 1268 | keep | 0 | Feb | 2023 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
VEGA BAJA | 2023-02-22 22:00 | 2023-02-23 00:10 | 75 | 2:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23022200093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-02-22 | 9750 | keep | 0 | Feb | 2023 | 0.0066407 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-02-23 01:06 | 2023-02-23 03:26 | 1381 | 2:20 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE BKR NO CERRO POR SCADA FAIL TO OPERATE. TAMPOCO CERRO EN EL CAMPO SE TRANSFIRIO POR B/I AL 1204-01. SJ-230223-01 | S23022300002 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 140 | 2023-02-23 | 193340 | keep | 0 | Feb | 2023 | 0.13168 | 0.00094059 | Sustained | FALSE | FALSE | Not_TMED_Event | 1381
BAYAMON | 2023-02-23 02:26 | 2023-02-23 02:27 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1907-04 Y SE CERRO POR SCADA | S2302230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-23 | 2466 | keep | 0 | Feb | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
CAGUAS | 2023-02-23 03:51 | 2023-02-23 10:50 | 30 | 6:59 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23022300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 419 | 2023-02-23 | 12570 | keep | 0 | Feb | 2023 | 0.0085614 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-02-23 04:22 | 2023-02-23 09:30 | 20 | 5:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE LLUVIA | P23022300001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 308 | 2023-02-23 | 6160 | keep | 0 | Feb | 2023 | 0.0041955 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-02-23 04:53 | 2023-02-23 11:00 | 100 | 6:07 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23022300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2023-02-23 | 36700 | keep | 0 | Feb | 2023 | 0.024996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-02-23 05:19 | 2023-02-23 08:10 | 1320 | 2:51 | T | CAUSAS EXTERNAS | DISPARO DE BKR SE SECCIONALIZO AVERIA 60% EN SERVICIO | C23022300008 | New_Event | Damage From Public | Include | Include | Public | 171 | 2023-02-23 | 225720 | keep | 0 | Feb | 2023 | 0.15374 | 0.00089905 | Sustained | FALSE | FALSE | Not_TMED_Event | 1320
HUMACAO | 2023-02-23 05:38 | 2023-02-23 05:39 | 2354 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C2302230000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-02-23 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-02-23 05:40 | 2023-02-23 07:32 | 2354 | 1:52 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE SECCIONALIZO AVERIA 30% EN SERVICIO | C23022300018 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 112 | 2023-02-23 | 263648 | keep | 0 | Feb | 2023 | 0.17957 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
VEGA BAJA | 2023-02-23 06:15 | 2023-02-23 17:23 | 1 | 11:08 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CULEBRA EN BUSHING PRIMARIO | A23022300003 | New_Event | Animals | Include | Include | Wildlife | 668 | 2023-02-23 | 668 | keep | 0 | Feb | 2023 | 0.00045497 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-23 07:13 | 2023-02-23 09:43 | 77 | 2:30 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | R23022300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-02-23 | 11550 | keep | 0 | Feb | 2023 | 0.0078667 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
HUMACAO | 2023-02-23 07:13 | 2023-02-23 10:39 | 75 | 3:26 | P | ANIMAL | 2 X 65 EN C/L CRUCE X AVE | C23022300051 | New_Event | Animals | Include | Include | Wildlife | 206 | 2023-02-23 | 15450 | keep | 0 | Feb | 2023 | 0.010523 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
FAJARDO | 2023-02-23 07:15 | 2023-02-23 09:52 | 3 | 2:37 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | R23022300023 | New_Event | Animals | Include | Include | Wildlife | 157 | 2023-02-23 | 471 | keep | 0 | Feb | 2023 | 0.0003208 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-02-23 07:16 | 2023-02-23 14:52 | 54 | 7:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO PORTAFUSIBLE | C23022300054 | New_Event | Cutout Failure | Include | Include | Equipment | 456 | 2023-02-23 | 24624 | keep | 0 | Feb | 2023 | 0.016771 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
FAJARDO | 2023-02-23 07:18 | 2023-02-23 07:20 | 2286 | 0:02 | T | NO SE REPORTO CAUSA | RECERRO | R23022300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-23 | 4572 | keep | 0 | Feb | 2023 | 0.003114 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2023-02-23 07:20 | 2023-02-23 07:21 | 2286 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23022300004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-23 | 2286 | keep | 0 | Feb | 2023 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
BAYAMON | 2023-02-23 07:24 | 2023-02-23 12:49 | 117 | 5:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | B23022300002 | New_Event | Cutout Failure | Include | Include | Equipment | 325 | 2023-02-23 | 38025 | keep | 0 | Feb | 2023 | 0.025899 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
FAJARDO | 2023-02-23 07:27 | 2023-02-23 08:37 | 60 | 1:10 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | R23022300005 | New_Event | Animals | Include | Include | Wildlife | 70 | 2023-02-23 | 4200 | keep | 0 | Feb | 2023 | 0.0028606 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-02-23 07:32 | 2023-02-23 07:50 | 1648 | 0:18 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZARON OPERACIONES 99% EN SERVICIO SOLO QUEDA 1 CLIENTE FUERA | C23022300018 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 18 | 2023-02-23 | 29664 | keep | 0 | Feb | 2023 | 0.020204 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-02-23 07:48 | 2023-02-23 10:46 | 40 | 2:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23022300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-02-23 | 7120 | keep | 0 | Feb | 2023 | 0.0048494 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-23 07:49 | 2023-02-23 15:00 | 72 | 7:11 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR 1 X 40 EN C/L | C23022300072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 431 | 2023-02-23 | 31032 | keep | 0 | Feb | 2023 | 0.021136 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
HUMACAO | 2023-02-23 07:50 | 2023-02-23 13:15 | 1 | 5:25 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO Y SE ENERGIZO EL CLIENTE QUE FALTABA | C23022300018 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 325 | 2023-02-23 | 325 | keep | 0 | Feb | 2023 | 0.00022136 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-23 08:02 | 2023-02-23 15:14 | 40 | 7:12 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN RISER Y 1 X 50 EN C/L SE REEMPLAZO BUSHING DE PM (T-6) Y ELBOW T | C23022300075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 432 | 2023-02-23 | 17280 | keep | 0 | Feb | 2023 | 0.011769 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-02-23 08:06 | 2023-02-23 10:25 | 40 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C23022300078 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-02-23 | 5560 | keep | 0 | Feb | 2023 | 0.0037869 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-02-23 08:10 | 2023-02-23 09:26 | 528 | 1:16 | P | CAUSAS EXTERNAS | SE RETIRO GUY WIRE QUE ESTABA SOBRE LA LINEA PRIMARIA POR IMPACTO DE VEHICULO Y SE ENERGIZO 100% EN SERVICIO | C23022300008 | Partial_restoration | Damage From Public | Include | Include | Public | 76 | 2023-02-23 | 40128 | keep | 0 | Feb | 2023 | 0.027331 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-23 08:13 | 2023-02-23 08:14 | 1514 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR SCADA | B23022300016 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-23 | 1514 | keep | 0 | Feb | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-02-23 08:14 | 2023-02-23 12:40 | 10 | 4:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN XMR SE REEMPLAZARON 2 CAJAS PRIMARIAS | B23022300023 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 266 | 2023-02-23 | 2660 | keep | 0 | Feb | 2023 | 0.0018117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-23 08:43 | 2023-02-23 10:48 | 40 | 2:05 | P | TERMINACION SOTERRADA AVERIADA | 1 X 15 EN PROVISIONAL 1 X 50 EN PROVISIONAL SE REPARO TERMINACION EN AEREO PROVISIONAL | R23022300013 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 125 | 2023-02-23 | 5000 | keep | 0 | Feb | 2023 | 0.0034055 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-23 08:52 | 2023-02-23 08:53 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | B2302230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-23 | 222 | keep | 0 | Feb | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-02-23 08:52 | 2023-02-23 08:53 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | B2302230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-23 | 4456 | keep | 0 | Feb | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
SAN JUAN | 2023-02-23 08:55 | 2023-02-23 11:30 | 20 | 2:35 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE PRIMARIO | S23022300049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-02-23 | 3100 | keep | 0 | Feb | 2023 | 0.0021114 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-23 08:56 | 2023-02-23 14:45 | 91 | 5:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE REPARO CONDICION DE CONDUCTOR PRIMARIO PARTIDO | C23022300094 | New_Event | Primary Wire Break | Include | Include | Equipment | 349 | 2023-02-23 | 31759 | keep | 0 | Feb | 2023 | 0.021631 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
HUMACAO | 2023-02-23 09:00 | 2023-02-23 10:30 | 1227 | 1:30 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRIPSAVER PARA SECCIONALIZAR TRAMO RADIAL Y PODER TRABAJAR LEVANTANDO CONDUCTOR PRIMARIO DEL ALIMENTADOR 2604-01 | C23022300101 | New_Event | Primary Wire Break | Include | Include | Equipment | 90 | 2023-02-23 | 110430 | keep | 0 | Feb | 2023 | 0.075213 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
BAYAMON | 2023-02-23 09:03 | 2023-02-23 09:05 | 450 | 0:02 | T | DESGANCHE | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | B23022300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-02-23 | 900 | keep | 0 | Feb | 2023 | 0.00061299 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
UTUADO | 2023-02-23 09:05 | 2023-02-23 12:04 | 9 | 2:59 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON BAJANTES PRIMARIOS PARTIDOS | A23022300014 | New_Event | Primary Wire Break | Include | Include | Equipment | 179 | 2023-02-23 | 1611 | keep | 0 | Feb | 2023 | 0.0010972 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-02-23 09:08 | 2023-02-23 14:00 | 23 | 4:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23022300055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 292 | 2023-02-23 | 6716 | keep | 0 | Feb | 2023 | 0.0045742 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-02-23 09:11 | 2023-02-23 14:19 | 1 | 5:08 | P | PROBLEMA DEL CLIENTE | 1 X 40 EN SU 1 Y 1 X 30 EN TRANSCLOUSURE PRIVADO REQUIERE MANTENIMIENTO | B23022300036 | New_Event | Customer-Related Interruption | Include | Include | Public | 308 | 2023-02-23 | 308 | keep | 0 | Feb | 2023 | 0.00020978 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-02-23 09:17 | 2023-02-23 09:18 | 1924 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23022300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-23 | 1924 | keep | 0 | Feb | 2023 | 0.0013104 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
CAGUAS | 2023-02-23 09:20 | 2023-02-23 18:02 | 6 | 8:42 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23022300107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 522 | 2023-02-23 | 3132 | keep | 0 | Feb | 2023 | 0.0021332 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-23 09:29 | 2023-02-23 17:32 | 30 | 8:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN XMR SE REMPLAZO CAJA PRIMARIA | B23022300042 | New_Event | Cutout Failure | Include | Include | Equipment | 483 | 2023-02-23 | 14490 | keep | 0 | Feb | 2023 | 0.0098691 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-02-23 09:29 | 2023-02-23 13:14 | 5 | 3:45 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23022300109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2023-02-23 | 1125 | keep | 0 | Feb | 2023 | 0.00076623 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-02-23 09:31 | 2023-02-23 14:47 | 45 | 5:16 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA 1 X 65 EN C/L | S23022300063 | New_Event | Primary Wire Break | Include | Include | Equipment | 316 | 2023-02-23 | 14220 | keep | 0 | Feb | 2023 | 0.0096852 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-02-23 09:33 | 2023-02-23 13:45 | 10 | 4:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE **EVENTO TRANSFERIDO DE PONCE PARA CANOVANAS** | P23022300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2023-02-23 | 2520 | keep | 0 | Feb | 2023 | 0.0017164 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-02-23 09:34 | 2023-02-23 11:38 | 176 | 2:04 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | R23022300027 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 124 | 2023-02-23 | 21824 | keep | 0 | Feb | 2023 | 0.014864 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2023-02-23 09:38 | 2023-02-23 16:15 | 100 | 6:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M23022300018 | New_Event | Cutout Failure | Include | Include | Equipment | 397 | 2023-02-23 | 39700 | keep | 0 | Feb | 2023 | 0.027039 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-02-23 09:40 | 2023-02-23 12:07 | 74 | 2:27 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES BUSCANDO AVERIA SE ABRIO N/O Y SE CERRO POR SCADA LLEVA LA CARGA DEL 1912-07 | S23022300075 | New_Event | Primary Wire Break | Include | Include | Equipment | 147 | 2023-02-23 | 10878 | keep | 0 | Feb | 2023 | 0.007409 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2023-02-23 09:40 | 2023-02-23 15:55 | 57 | 6:15 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES Y SE CERRO POR SCADA CARGA POR EL 1521-02 | S23022300075 | New_Event | Feeder Load Transferred | Include | Include | Other | 375 | 2023-02-23 | 21375 | keep | 0 | Feb | 2023 | 0.014558 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
VEGA BAJA | 2023-02-23 09:44 | 2023-02-23 09:45 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-23 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
BAYAMON | 2023-02-23 09:45 | 2023-02-23 16:50 | 3 | 7:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONEXIONES SECUNDARIAS | S23022300001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 425 | 2023-02-23 | 1275 | keep | 0 | Feb | 2023 | 0.0008684 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-02-23 09:49 | 2023-02-23 16:46 | 15 | 6:57 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23022300115 | New_Event | Animals | Include | Include | Wildlife | 417 | 2023-02-23 | 6255 | keep | 0 | Feb | 2023 | 0.0042603 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-02-23 09:53 | 2023-02-23 13:54 | 10 | 4:01 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | C23022300116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2023-02-23 | 2410 | keep | 0 | Feb | 2023 | 0.0016414 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-23 09:59 | 2023-02-23 17:12 | 60 | 7:13 | P | TERMINACION SOTERRADA AVERIADA | 1 X 50 EN C/L Y SE REEMPLAZO TERMINACION SOTERRADA | S23022300074 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 433 | 2023-02-23 | 25980 | keep | 0 | Feb | 2023 | 0.017695 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-02-23 10:11 | 2023-02-23 18:41 | 18 | 8:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L TOTAL Y SE REEMPLAZO POSTE PRIMARIO | S23022300083 | New_Event | Primary Pole Failure | Include | Include | Equipment | 510 | 2023-02-23 | 9180 | keep | 0 | Feb | 2023 | 0.0062525 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
HUMACAO | 2023-02-23 10:11 | 2023-02-23 12:02 | 15 | 1:51 | P | ANIMAL | 1 X 10 EN XMR Y 1 X 40 EN C/L CRUCE X AVE | C23022300123 | New_Event | Animals | Include | Include | Wildlife | 111 | 2023-02-23 | 1665 | keep | 0 | Feb | 2023 | 0.001134 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-23 10:30 | 2023-02-23 15:56 | 15 | 5:26 | P | DESGANCHE | SE ABRIO CORTE DE LINEA SE REALIZO DESGANCHE CRITICO | R23022300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2023-02-23 | 4890 | keep | 0 | Feb | 2023 | 0.0033306 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-02-23 10:34 | 2023-02-23 18:45 | 40 | 8:11 | P | DESGANCHE | 1 X 100 EN CL SE REALIZO DESGANCHE | A23022300035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 491 | 2023-02-23 | 19640 | keep | 0 | Feb | 2023 | 0.013377 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-02-23 10:48 | 2023-02-23 14:27 | 1 | 3:39 | T | CONDUCTOR ARRIADO O CRUZADO | SE ABRE ALIMENTADOR PARA PODER INSTALAR CRUCETA Y CONSTRUIR RISER PARA COMPLETAR SALIDA DE ALIMENTADOR *NOTA ALIMENTADOR DA SERVICIO A TECNICA DE PONCE Y QUEDARON EN PLANTA DE EMERGENCIA | P23022300037 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 219 | 2023-02-23 | 219 | keep | 0 | Feb | 2023 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-23 10:53 | 2023-02-23 12:44 | 77 | 1:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23022300035 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 111 | 2023-02-23 | 8547 | keep | 0 | Feb | 2023 | 0.0058213 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-02-23 11:05 | 2023-02-23 13:18 | 450 | 2:13 | T | DESGANCHE | SE REALIZO DESPEJE DE LINEAS CON VARETA SWF BY-230223-01 | B23022300075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-02-23 | 59850 | keep | 0 | Feb | 2023 | 0.040764 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
VEGA BAJA | 2023-02-23 11:05 | 2023-02-23 17:41 | 56 | 6:36 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | B23022300072 | New_Event | Animals | Include | Include | Wildlife | 396 | 2023-02-23 | 22176 | keep | 0 | Feb | 2023 | 0.015104 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
FAJARDO | 2023-02-23 11:17 | 2023-02-23 13:31 | 50 | 2:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23022300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-02-23 | 6700 | keep | 0 | Feb | 2023 | 0.0045633 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-02-23 11:17 | 2023-02-23 19:12 | 40 | 7:55 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 30 EN CL LINEA SPACER CRUZADA CON RACK | A23022300044 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 475 | 2023-02-23 | 19000 | keep | 0 | Feb | 2023 | 0.012941 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-02-23 11:20 | 2023-02-23 11:22 | 719 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | SE DISPARO INTERRUPTOR A PETICION DE FRANKIE RAMOS PARA SECCIONALIZAR PUENTE ABIERTO TRAMO RADIAL SJ-230223-03 | S23022300113 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-02-23 | 1438 | keep | 0 | Feb | 2023 | 0.00097942 | 0.00048971 | Momentary | FALSE | FALSE | Not_TMED_Event | 719
SAN JUAN | 2023-02-23 11:22 | 2023-02-23 13:45 | 100 | 2:23 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN TRAMO RADIAL SJ-230223-03 | S23022300113 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 143 | 2023-02-23 | 14300 | keep | 0 | Feb | 2023 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-02-23 11:36 | 2023-02-23 14:00 | 80 | 2:24 | P | CONDUCTOR ROTO O ABIERTO | 1 X 140 EN CL BAJANTE PRIMARIO PARTIDO | A23022300050 | New_Event | Primary Wire Break | Include | Include | Equipment | 144 | 2023-02-23 | 11520 | keep | 0 | Feb | 2023 | 0.0078462 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-02-23 11:51 | 2023-02-23 11:52 | 1428 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23022300042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-23 | 1428 | keep | 0 | Feb | 2023 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
SAN JUAN | 2023-02-23 11:55 | 2023-02-23 13:25 | 12 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022300046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-02-23 | 1080 | keep | 0 | Feb | 2023 | 0.00073558 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-23 12:07 | 2023-02-23 13:52 | 40 | 1:45 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO Y SE LEVANTO NEUTRAL PRIMARIO Y SE CERRO PUENTE ABIERTO | S23022300075 | New_Event | Primary Wire Break | Include | Include | Equipment | 105 | 2023-02-23 | 4200 | keep | 0 | Feb | 2023 | 0.0028606 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-23 12:11 | 2023-02-23 18:13 | 40 | 6:02 | P | ANIMAL | 1 X 15 EN XMR 1 X 65 EN C/L CRUCE X AVE | S23022300120 | New_Event | Animals | Include | Include | Wildlife | 362 | 2023-02-23 | 14480 | keep | 0 | Feb | 2023 | 0.0098623 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-02-23 12:35 | 2023-02-23 16:20 | 12 | 3:45 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR PARA RECONSTRUIR LINEA NEUTRAL COMUN | A23022300045 | New_Event | Primary Wire Break | Include | Include | Equipment | 225 | 2023-02-23 | 2700 | keep | 0 | Feb | 2023 | 0.001839 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-02-23 12:42 | 2023-02-23 13:27 | 8 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23022300030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-02-23 | 360 | keep | 0 | Feb | 2023 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-02-23 12:54 | 2023-02-23 15:07 | 32 | 2:13 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO FASE | P23022300053 | New_Event | Animals | Include | Include | Wildlife | 133 | 2023-02-23 | 4256 | keep | 0 | Feb | 2023 | 0.0028987 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2023-02-23 13:13 | 2023-02-23 13:29 | 534 | 0:16 | T | NO SE REPORTO CAUSA | SE VERIFICO PERSONAL FUERA SE CERO POR SCADA CARGA POR EL 1519-05 | S23022300137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-02-23 | 8544 | keep | 0 | Feb | 2023 | 0.0058193 | 0.0003637 | Sustained | FALSE | FALSE | Not_TMED_Event | 534
SAN JUAN | 2023-02-23 13:13 | 2023-02-23 13:29 | 558 | 0:16 | T | NO SE REPORTO CAUSA | SE VERIFICO PERSONAL FUERA SE CERO POR SCADA LLEVA LA CARGA DEL 1519-01 | S23022300137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-02-23 | 8928 | keep | 0 | Feb | 2023 | 0.0060808 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
BAYAMON | 2023-02-23 13:13 | 2023-02-23 13:14 | 1368 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL. | S23022300152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-23 | 1368 | keep | 0 | Feb | 2023 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
CANOVANAS | 2023-02-23 13:23 | 2023-02-23 15:31 | 25 | 2:08 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO | R23022300057 | New_Event | Primary Wire Break | Include | Include | Equipment | 128 | 2023-02-23 | 3200 | keep | 0 | Feb | 2023 | 0.0021795 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-23 13:27 | 2023-02-23 15:08 | 152 | 1:41 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23022300148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-02-23 | 15352 | keep | 0 | Feb | 2023 | 0.010456 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
BAYAMON | 2023-02-23 13:48 | 2023-02-23 18:16 | 22 | 4:28 | P | DESGANCHE | 2 X 80 EN C/L DESPEJE DE LINEA | B23022300120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2023-02-23 | 5896 | keep | 0 | Feb | 2023 | 0.0040157 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-02-23 13:52 | 2023-02-23 14:31 | 271 | 0:39 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | REALIZANDO OPERACIONES EN ALIMENTADOR 1521-02 DISPARO ALIMENTADOR Y SE LLEVO LA ALTA DEL TRANSFORMADOR, OPERO LENTO SEGUN PERSONAL DE SUBESTACIONES | S23022300145 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 39 | 2023-02-23 | 10569 | keep | 0 | Feb | 2023 | 0.0071985 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2023-02-23 13:52 | 2023-02-23 15:55 | 74 | 2:03 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | REALIZANDO OPERACIONES EN ALIMENTADOR 1521-02 DISPARO ALIMENTADOR Y SE LLEVO LA ALTA DEL TRANSFORMADOR LLEVA LA CARGA DEL 1912-07, INTERRUPTOR OPERO LENTO SEGUN PERSONAL DE SUBESTACIONES | S23022300145 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 123 | 2023-02-23 | 9102 | keep | 0 | Feb | 2023 | 0.0061993 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2023-02-23 13:53 | 2023-02-23 16:00 | 12 | 2:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022300159 | New_Event | Secondary Wire Break | Include | Include | Equipment | 127 | 2023-02-23 | 1524 | keep | 0 | Feb | 2023 | 0.001038 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-02-23 14:00 | 2023-02-23 15:44 | 8 | 1:44 | P | CAUSAS EXTERNAS | 1 X 15 EN TRANSFORMADOR CAMION CRUZO SECUNDARIA | M23022300063 | New_Event | Damage From Public | Include | Include | Public | 104 | 2023-02-23 | 832 | keep | 0 | Feb | 2023 | 0.00056667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-02-23 14:24 | 2023-02-23 15:40 | 6 | 1:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R23022300066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 76 | 2023-02-23 | 456 | keep | 0 | Feb | 2023 | 0.00031058 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-02-23 14:42 | 2023-02-23 19:39 | 222 | 4:57 | P | ERROR HUMANO | SE ABRE CORTE DE LINEA POR AVERIA DE TUBERIA DE AGUAS CRUDAS ROTA AL REALIZAR HOYO PARA PARAR POSTE PERSONAL DE QUANTA CON CAMION BARRENA PERFORO EL TUBO DE AAA | P23022300069 | New_Event | Human Error | Include | Include | Other | 297 | 2023-02-23 | 65934 | keep | 0 | Feb | 2023 | 0.044907 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
YAUCO | 2023-02-23 14:47 | 2023-02-23 15:49 | 2484 | 1:02 | T | CAUSAS EXTERNAS | CAJA PRIMARIA CRUZADA CON TENZOR | P23022300070 | New_Event | Damage From Public | Include | Include | Public | 62 | 2023-02-23 | 154008 | keep | 0 | Feb | 2023 | 0.10489 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
ARECIBO | 2023-02-23 14:49 | 2023-02-23 18:32 | 1 | 3:43 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A23022300082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2023-02-23 | 223 | keep | 0 | Feb | 2023 | 0.00015188 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-23 14:54 | 2023-02-23 15:12 | 12 | 0:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y REPARAR BAJANTE SECUNDARIO | R23022300049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 18 | 2023-02-23 | 216 | keep | 0 | Feb | 2023 | 0.00014712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-23 15:15 | 2023-02-23 15:17 | 5191 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | B2302230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-23 | 10382 | keep | 0 | Feb | 2023 | 0.0070711 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
CAGUAS | 2023-02-23 15:46 | 2023-02-23 16:39 | 6 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR BARRAS EN PEDESTAL | C23022300141 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-02-23 | 318 | keep | 0 | Feb | 2023 | 0.00021659 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-02-23 15:48 | 2023-02-23 16:30 | 12 | 0:42 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR PARA REPARAR TOMA SECUNDARIA SOTERRADA PERO NO SE PUEDO REPARAR LA TOMA DEL CLIENTE PROA | C23022200103 | New_Event | Customer-Related Interruption | Include | Include | Public | 42 | 2023-02-23 | 504 | keep | 0 | Feb | 2023 | 0.00034327 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-02-23 15:49 | 2023-02-23 17:00 | 632 | 1:11 | P | CAUSAS EXTERNAS | CAJA PRIMARIA QUEMADA EN EQUIPO DE MEDICION | P23022300086 | Partial_restoration | Damage From Public | Include | Include | Public | 71 | 2023-02-23 | 44872 | keep | 0 | Feb | 2023 | 0.030562 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-23 16:08 | 2023-02-23 17:23 | 100 | 1:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA EN RISER | C23022300182 | New_Event | Cutout Failure | Include | Include | Equipment | 75 | 2023-02-23 | 7500 | keep | 0 | Feb | 2023 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-02-23 16:25 | 2023-02-23 17:15 | 15 | 0:50 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022300193 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 50 | 2023-02-23 | 750 | keep | 0 | Feb | 2023 | 0.00051082 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-23 16:25 | 2023-02-23 17:48 | 4 | 1:23 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23022300149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-02-23 | 332 | keep | 0 | Feb | 2023 | 0.00022612 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-02-23 16:58 | 2023-02-23 21:39 | 1 | 4:41 | P | SECUNDARIA/DESGANCHE | X 10 EN XMR Y DESGANCHE SECUNDARIO | S23022300197 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 281 | 2023-02-23 | 281 | keep | 0 | Feb | 2023 | 0.00019139 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-02-23 17:18 | 2023-02-24 09:50 | 14 | 16:32 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A23022300010 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 992 | 2023-02-23 | 13888 | keep | 0 | Feb | 2023 | 0.0094591 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
GUAYAMA | 2023-02-23 17:30 | 2023-02-23 17:31 | 4132 | 0:01 | T | ANIMAL | RECIERRE | P23022300098 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-23 | 4132 | keep | 0 | Feb | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
BAYAMON | 2023-02-23 17:31 | 2023-02-23 18:21 | 2402 | 0:50 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR LLEVANDO 1720-08 SE SECCIONALIZO Y SE CERRO X SCADA 100% 1720-08 EN SERVICIO Y UN 75% 1709-02 | B23022300162 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 50 | 2023-02-23 | 120100 | keep | 0 | Feb | 2023 | 0.0818 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2023-02-23 17:31 | 2023-02-23 18:21 | 1 | 0:50 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR LLEVANDO 1720-08 SE SECCIONALIZO Y SE CERRO X SCADA 100% 1720-08 EN SERVICIO Y UN 75% 1709-02 | B23022300162 | New_Event | Feeder Load Transferred | Include | Include | Other | 50 | 2023-02-23 | 50 | keep | 0 | Feb | 2023 | 3.4055e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-02-23 17:31 | 2023-02-23 19:10 | 21 | 1:39 | P | ANIMAL | 1 X 65 1 X 80 EN SENDOS CORTES DE LINEA PAJARO CRUZO FASE | P23022300099 | 1st_after_momentary | Animals | Include | Include | Wildlife | 99 | 2023-02-23 | 2079 | keep | 0 | Feb | 2023 | 0.001416 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
AGUADILLA | 2023-02-23 17:42 | 2023-02-23 19:05 | 50 | 1:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M23022300090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-02-23 | 4150 | keep | 0 | Feb | 2023 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-02-23 17:43 | 2023-02-23 18:40 | 5 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BARRAS EN PESDESTAL | C23022300161 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-02-23 | 285 | keep | 0 | Feb | 2023 | 0.00019411 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-02-23 17:50 | 2023-02-23 20:35 | 125 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23022300095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-02-23 | 20625 | keep | 0 | Feb | 2023 | 0.014048 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2023-02-23 18:11 | 2023-02-23 18:55 | 100 | 0:44 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN CORTES DE LINEA REQUIERE DESGANCHE | M23022300104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2023-02-23 | 4400 | keep | 0 | Feb | 2023 | 0.0029968 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-23 18:21 | 2023-02-23 18:47 | 600 | 0:26 | P | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR POR CONDUCTOR ENREDADOS ENTRO EN SERVICIO UN 85% 1709-02 | B23022300162 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 26 | 2023-02-23 | 15600 | keep | 0 | Feb | 2023 | 0.010625 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-23 18:47 | 2023-02-23 20:37 | 360 | 1:50 | P | CONDUCTOR ARRIADO O CRUZADO | SE DESENREDO CONDUCTORES PRIMARIOS Y SE CERRO MACHETES 100% EN SERVICIO | B23022300162 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 110 | 2023-02-23 | 39600 | keep | 0 | Feb | 2023 | 0.026971 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-23 19:33 | 2023-02-24 10:12 | 29 | 14:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S23022300244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 879 | 2023-02-23 | 25491 | keep | 0 | Feb | 2023 | 0.017362 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2023-02-23 19:39 | 2023-02-23 19:51 | 3744 | 0:12 | T | ERROR HUMANO | SE ABRE INTERRUPTOR DE EMERGENCIA PARA PODER RETIRAR GRUA DE QUANTA DE AREA INUNDADA POR AVERIA EN TUBO DE 64 '"TRONCAL DE AGUAS CRUDAS PERSONAL DE QUANTA CAMION BARRENA AVERIO TUBO DE AAA | P23022300110 | Additional_clients | Human Error | Include | Include | Other | 12 | 2023-02-23 | 44928 | keep | 0 | Feb | 2023 | 0.0306 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-23 19:40 | 2023-02-23 23:56 | 80 | 4:16 | P | EMPALME SOTERRADO AVERIADO | SE REPUSO 1 RBA DE 50 EN SU EN RIO CIALITOS 1 X 40 EN PROVISIONAL AEREO. AVERIA NUEVA T-16 A T15 SE QUEDAN 5 XMR FUERA T10, T11, T12, T13, T14, T15 | B23022300188 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 256 | 2023-02-23 | 20480 | keep | 0 | Feb | 2023 | 0.013949 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-02-23 19:50 | 2023-02-23 21:50 | 1479 | 2:00 | P | ERROR HUMANO | SE VOLVIO ABRIR MACHETES POR ERROR DE COMPANIA (LORD) REALIZANDO V/L D2023-2944 QUE TRANSPOSICIONO LINEAS PRIMARIAS | B23022300011 | New_Event | Human Error | Include | Include | Other | 120 | 2023-02-23 | 177480 | keep | 0 | Feb | 2023 | 0.12088 | 0.0010073 | Sustained | FALSE | FALSE | Not_TMED_Event | 1479
BAYAMON | 2023-02-23 19:51 | 2023-02-24 19:20 | 1 | 23:29 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L TOTAL PARA CAMBIO DE POSTE PRIMARIO | B23022300195 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1409 | 2023-02-23 | 1409 | keep | 0 | Feb | 2023 | 0.00095966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-02-23 20:22 | 2023-02-23 20:55 | 17 | 0:33 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA REPARAR BAJANTE Y CONECTOR DE LINEA A CAJA PRIMARIA | R23022300082 | New_Event | Primary Wire Break | Include | Include | Equipment | 33 | 2023-02-23 | 561 | keep | 0 | Feb | 2023 | 0.00038209 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-02-23 20:59 | 2023-02-24 13:05 | 1 | 16:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23022300113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 966 | 2023-02-23 | 966 | keep | 0 | Feb | 2023 | 0.00065794 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-23 21:18 | 2023-02-23 22:13 | 90 | 0:55 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23022300192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-02-23 | 4950 | keep | 0 | Feb | 2023 | 0.0033714 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-02-23 21:31 | 2023-02-23 23:40 | 229 | 2:09 | P | TERMINACION SOTERRADA AVERIADA | 1 X 40 EN PROVISIONAL SE REPARO TERMINACION | B23022300226 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 129 | 2023-02-23 | 29541 | keep | 0 | Feb | 2023 | 0.02012 | 0.00015597 | Sustained | FALSE | FALSE | Not_TMED_Event | 229
YAUCO | 2023-02-23 22:00 | 2023-02-24 08:39 | 1 | 10:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23022300121 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 639 | 2023-02-23 | 639 | keep | 0 | Feb | 2023 | 0.00043522 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-23 22:23 | 2023-02-23 22:24 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23022300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-23 | 4304 | keep | 0 | Feb | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2023-02-23 22:37 | 2023-02-24 17:40 | 23 | 19:03 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR POSTES PRIMARIOS REFERENTE A TRABAJOS V/L D2023-3013 | B23022300024 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1143 | 2023-02-23 | 26289 | keep | 0 | Feb | 2023 | 0.017905 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
PONCE | 2023-02-23 22:50 | 2023-02-23 22:51 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23022300142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-23 | 2039 | keep | 0 | Feb | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
BAYAMON | 2023-02-23 23:56 | 2023-02-24 15:27 | 6 | 15:31 | P | EMPALME SOTERRADO AVERIADO | SE REPARO EMPALME SOTERRADO AVERIADO | B23022300188 | Partial_restoration | UG Cable Splice Failure | Include | Include | Equipment | 931 | 2023-02-23 | 5586 | keep | 0 | Feb | 2023 | 0.0038046 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-24 02:00 | 2023-02-24 07:53 | 50 | 5:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A23022400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2023-02-24 | 17650 | keep | 0 | Feb | 2023 | 0.012021 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-24 02:36 | 2023-02-24 02:37 | 341 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | RECIERRE | B23022400003 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2023-02-24 | 341 | keep | 0 | Feb | 2023 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2023-02-24 02:37 | 2023-02-24 04:47 | 35 | 2:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L TOTAL PARA REEMPLAZO DE 2 POSTES PRIMARIOS | B23022400004 | 1st_after_momentary | Primary Pole Failure | Include | Include | Equipment | 130 | 2023-02-24 | 4550 | keep | 0 | Feb | 2023 | 0.003099 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-02-24 04:41 | 2023-02-24 08:10 | 12 | 3:29 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23022400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2023-02-24 | 2508 | keep | 0 | Feb | 2023 | 0.0017082 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-24 04:47 | 2023-02-24 04:48 | 341 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B23022400005 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-02-24 | 341 | keep | 0 | Feb | 2023 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2023-02-24 04:48 | 2023-02-24 07:35 | 300 | 2:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 140 EN RISER SE REEMPLAZO PORTAFUSIBLE QUEMADO | B23022400007 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 167 | 2023-02-24 | 50100 | keep | 0 | Feb | 2023 | 0.034123 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-02-24 04:48 | 2023-02-24 16:43 | 35 | 11:55 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L TOTAL PARA REEMPLAZO DE 2 POSTE PRIMARIO | B23022400004 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 715 | 2023-02-24 | 25025 | keep | 0 | Feb | 2023 | 0.017044 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-24 05:51 | 2023-02-24 16:35 | 20 | 10:44 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO DE XMR 37.5KVA X 50KVA AVERRIADO T-21 Y SE ENERGIZARON | C23022400002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 644 | 2023-02-24 | 12880 | keep | 0 | Feb | 2023 | 0.0087725 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-02-24 06:27 | 2023-02-24 09:15 | 20 | 2:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO 1 X 20 EN TRANSFORMADOR | P23022400011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 168 | 2023-02-24 | 3360 | keep | 0 | Feb | 2023 | 0.0022885 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-02-24 06:27 | 2023-02-24 09:46 | 20 | 3:19 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 25 EN CORTE DE LINEAS SE ELIMINO BAJANTE DE TRANSFORMADOR FUERA DE USO QUE CRUZO LINEAS | A23022400002 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 199 | 2023-02-24 | 3980 | keep | 0 | Feb | 2023 | 0.0027108 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-24 06:30 | 2023-02-24 10:32 | 40 | 4:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23022400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 242 | 2023-02-24 | 9680 | keep | 0 | Feb | 2023 | 0.006593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-02-24 07:11 | 2023-02-24 09:25 | 56 | 2:14 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PALOMA CRUZO FASE | P23022400013 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-02-24 | 7504 | keep | 0 | Feb | 2023 | 0.0051109 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
PONCE | 2023-02-24 08:04 | 2023-02-24 08:07 | 752 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE ALIMENTADOR | P23022400024 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-24 | 2256 | keep | 0 | Feb | 2023 | 0.0015366 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2023-02-24 08:04 | 2023-02-24 08:07 | 2696 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR | P23022400024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-24 | 8088 | keep | 0 | Feb | 2023 | 0.0055087 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
AGUADILLA | 2023-02-24 08:11 | 2023-02-24 11:20 | 20 | 3:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M23022400003 | New_Event | Cutout Failure | Include | Include | Equipment | 189 | 2023-02-24 | 3780 | keep | 0 | Feb | 2023 | 0.0025745 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-02-24 08:15 | 2023-02-24 12:45 | 20 | 4:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23022400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2023-02-24 | 5400 | keep | 0 | Feb | 2023 | 0.0036779 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-02-24 08:17 | 2023-02-24 08:18 | 2571 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 4800 SUBESTACIÃ“N 4677 T-2 FUNDIÃ“ FUSIBLE | P23022400027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 2571 | keep | 0 | Feb | 2023 | 0.0017511 | 0.0017511 | Momentary | FALSE | FALSE | Not_TMED_Event | 2571
GUAYAMA | 2023-02-24 08:17 | 2023-02-24 08:18 | 2235 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 4800 SUBESTACIÃ“N 4677 T-2 FUNDIÃ“ FUSIBLE | P23022400027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 2235 | keep | 0 | Feb | 2023 | 0.0015222 | 0.0015222 | Momentary | FALSE | FALSE | Not_TMED_Event | 2235
GUAYAMA | 2023-02-24 08:17 | 2023-02-24 08:18 | 713 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 4800 SUBESTACIÃ“N 4677 T-2 FUNDIÃ“ FUSIBLE | P23022400027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 713 | keep | 0 | Feb | 2023 | 0.00048562 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
GUAYAMA | 2023-02-24 08:17 | 2023-02-24 08:18 | 1067 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 4800 SUBESTACIÃ“N 4677 T-2 FUNDIÃ“ FUSIBLE | P23022400027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 1067 | keep | 0 | Feb | 2023 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
GUAYAMA | 2023-02-24 08:17 | 2023-02-24 08:18 | 1293 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 4800 SUBESTACIÃ“N 4677 T-2 FUNDIÃ“ FUSIBLE | P23022400027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 1293 | keep | 0 | Feb | 2023 | 0.00088066 | 0.00088066 | Momentary | FALSE | FALSE | Not_TMED_Event | 1293
GUAYAMA | 2023-02-24 08:17 | 2023-02-24 08:18 | 426 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 4800 SUBESTACIÃ“N 4677 T-2 FUNDIÃ“ FUSIBLE | P23022400027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 426 | keep | 0 | Feb | 2023 | 0.00029015 | 0.00029015 | Momentary | FALSE | FALSE | Not_TMED_Event | 426
GUAYAMA | 2023-02-24 08:17 | 2023-02-24 08:18 | 907 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 4800 SUBESTACIÃ“N 4677 T-2 FUNDIÃ“ FUSIBLE | P23022400027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 907 | keep | 0 | Feb | 2023 | 0.00061775 | 0.00061775 | Momentary | FALSE | FALSE | Not_TMED_Event | 907
CANOVANAS | 2023-02-24 08:23 | 2023-02-24 09:40 | 1 | 1:17 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE EVENTO TRANSFERIDO | P23022400025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-02-24 | 77 | keep | 0 | Feb | 2023 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-24 08:28 | 2023-02-24 13:30 | 60 | 5:02 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23022400012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2023-02-24 | 18120 | keep | 0 | Feb | 2023 | 0.012341 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-02-24 08:44 | 2023-02-24 13:35 | 290 | 4:51 | P | PROBLEMA DEL CLIENTE | 2 X 80 EN SMU-20 EN SU-2 SE DEJO FUERA CENTRO COMUNAL RIVERSIDE POR AVERIA PRIVADA | B23022400088 | New_Event | Customer-Related Interruption | Include | Include | Public | 291 | 2023-02-24 | 84390 | keep | 0 | Feb | 2023 | 0.057478 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
PONCE | 2023-02-24 08:50 | 2023-02-24 09:30 | 1 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO BAJANTE EN TRANSFORMADOR | P23022400030 | New_Event | Primary Wire Break | Include | Include | Equipment | 40 | 2023-02-24 | 40 | keep | 0 | Feb | 2023 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-24 08:51 | 2023-02-24 15:23 | 12 | 6:32 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | C23022400016 | New_Event | Animals | Include | Include | Wildlife | 392 | 2023-02-24 | 4704 | keep | 0 | Feb | 2023 | 0.0032039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-02-24 09:00 | 2023-02-24 13:57 | 35 | 4:57 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L SE RETIRO ARBOL SOBRE LINEA QUE A CAUSA DE CIUDADANO PODANDO | C23022400018 | New_Event | Damage From Public | Include | Include | Public | 297 | 2023-02-24 | 10395 | keep | 0 | Feb | 2023 | 0.00708 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2023-02-24 09:01 | 2023-02-24 13:15 | 1 | 4:14 | P | CONDUCTOR ARRIADO O CRUZADO | SE FIJO BAJANTE SAFADO EN RISER | P23022400033 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 254 | 2023-02-24 | 254 | keep | 0 | Feb | 2023 | 0.000173 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-24 09:07 | 2023-02-24 09:30 | 1 | 0:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIAS | C23022400019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 23 | 2023-02-24 | 23 | keep | 0 | Feb | 2023 | 1.5665e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-02-24 09:21 | 2023-02-24 09:22 | 4830 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 800 CLIENTES POR 3205-07 | C23022400024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-24 | 4830 | keep | 0 | Feb | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
VEGA BAJA | 2023-02-24 09:23 | 2023-02-24 15:55 | 13 | 6:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23022400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2023-02-24 | 5096 | keep | 0 | Feb | 2023 | 0.0034709 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2023-02-24 09:33 | 2023-02-24 11:07 | 10 | 1:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23022400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-02-24 | 940 | keep | 0 | Feb | 2023 | 0.00064023 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-24 09:33 | 2023-02-24 14:30 | 8 | 4:57 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO PARTIDO | M23022400018 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 297 | 2023-02-24 | 2376 | keep | 0 | Feb | 2023 | 0.0016183 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-24 09:37 | 2023-02-24 12:43 | 6 | 3:06 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23022400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-02-24 | 1116 | keep | 0 | Feb | 2023 | 0.0007601 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-24 09:59 | 2023-02-24 11:44 | 10 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022400021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2023-02-24 | 1050 | keep | 0 | Feb | 2023 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-02-24 10:00 | 2023-02-24 13:00 | 120 | 3:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A23022400030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-02-24 | 21600 | keep | 0 | Feb | 2023 | 0.014712 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2023-02-24 10:06 | 2023-02-24 10:07 | 271 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | S2302240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-24 | 271 | keep | 0 | Feb | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2023-02-24 10:07 | 2023-02-24 11:25 | 25 | 1:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIO | S23022400023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 78 | 2023-02-24 | 1950 | keep | 0 | Feb | 2023 | 0.0013281 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-02-24 10:31 | 2023-02-24 15:25 | 70 | 4:54 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23022400039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-02-24 | 20580 | keep | 0 | Feb | 2023 | 0.014017 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-02-24 10:58 | 2023-02-24 11:00 | 614 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R23022400029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-02-24 | 1228 | keep | 0 | Feb | 2023 | 0.00083639 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2023-02-24 10:58 | 2023-02-24 11:00 | 770 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R23022400029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-02-24 | 1540 | keep | 0 | Feb | 2023 | 0.0010489 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2023-02-24 10:58 | 2023-02-24 11:00 | 1271 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R23022400029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-02-24 | 2542 | keep | 0 | Feb | 2023 | 0.0017313 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CANOVANAS | 2023-02-24 10:58 | 2023-02-24 11:00 | 247 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R23022400029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-02-24 | 494 | keep | 0 | Feb | 2023 | 0.00033646 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
FAJARDO | 2023-02-24 11:22 | 2023-02-24 12:25 | 3 | 1:03 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR BAJANTE DE LINEA A CAJA | R23022400014 | New_Event | Primary Wire Break | Include | Include | Equipment | 63 | 2023-02-24 | 189 | keep | 0 | Feb | 2023 | 0.00012873 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-02-24 11:23 | 2023-02-24 15:57 | 7 | 4:34 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA CAMBIO DE POSTE PRIMARIO | B23022400103 | New_Event | Primary Pole Failure | Include | Include | Equipment | 274 | 2023-02-24 | 1918 | keep | 0 | Feb | 2023 | 0.0013063 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-02-24 11:35 | 2023-02-24 12:10 | 8 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO NEUTRAL Y CONECTORES SECUNDARIOS | B23022400117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-02-24 | 280 | keep | 0 | Feb | 2023 | 0.00019071 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-24 11:50 | 2023-02-24 12:16 | 20 | 0:26 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23022400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2023-02-24 | 520 | keep | 0 | Feb | 2023 | 0.00035417 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-24 11:50 | 2023-02-24 13:13 | 60 | 1:23 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C23022400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-02-24 | 4980 | keep | 0 | Feb | 2023 | 0.0033919 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-02-24 11:55 | 2023-02-24 14:00 | 10 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23022400050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2023-02-24 | 1250 | keep | 0 | Feb | 2023 | 0.00085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-24 12:11 | 2023-02-24 13:54 | 8 | 1:43 | P | CAUSAS EXTERNAS | 1 X 8 EN TRANSFORMADOR SE RETIRO TENSOR SOBRE LA CAJA | R23022400020 | New_Event | Damage From Public | Include | Include | Public | 103 | 2023-02-24 | 824 | keep | 0 | Feb | 2023 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-02-24 12:11 | 2023-02-24 12:14 | 2126 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23022400058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-24 | 6378 | keep | 0 | Feb | 2023 | 0.004344 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
PONCE | 2023-02-24 12:20 | 2023-02-24 12:21 | 2379 | 0:01 | T | DESGANCHE | RECIERRE | P23022400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-24 | 2379 | keep | 0 | Feb | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2023-02-24 12:21 | 2023-02-24 15:44 | 150 | 3:23 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | P23022400060 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 203 | 2023-02-24 | 30450 | keep | 0 | Feb | 2023 | 0.020739 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-02-24 12:40 | 2023-02-24 13:46 | 12 | 1:06 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C23022400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2023-02-24 | 792 | keep | 0 | Feb | 2023 | 0.00053943 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-02-24 12:41 | 2023-02-24 14:38 | 40 | 1:57 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23022400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-02-24 | 4680 | keep | 0 | Feb | 2023 | 0.0031875 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-02-24 12:48 | 2023-02-24 12:54 | 1448 | 0:06 | T | ERROR HUMANO | DISPARO PERSONAL DESPEJANDO LINEA CAYO RAMA SE VERIFICO PERSONAL QUEDO EN SERVICIO | R23022400022 | New_Event | Human Error | Include | Include | Other | 6 | 2023-02-24 | 8688 | keep | 0 | Feb | 2023 | 0.0059174 | 0.00098623 | Sustained | FALSE | FALSE | Not_TMED_Event | 1448
BAYAMON | 2023-02-24 12:48 | 2023-02-24 15:12 | 7 | 2:24 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23022400126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2023-02-24 | 1008 | keep | 0 | Feb | 2023 | 0.00068654 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-02-24 12:53 | 2023-02-24 12:55 | 548 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2302240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-24 | 1096 | keep | 0 | Feb | 2023 | 0.00074648 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
SAN JUAN | 2023-02-24 13:10 | 2023-02-24 15:49 | 30 | 2:39 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE RETEZO SECUNDARIA | S23022400043 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 159 | 2023-02-24 | 4770 | keep | 0 | Feb | 2023 | 0.0032488 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-24 13:14 | 2023-02-24 13:51 | 4 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON CONECTORES EN BAJANTES DE XMR | B23022400127 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-02-24 | 148 | keep | 0 | Feb | 2023 | 0.0001008 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-24 13:45 | 2023-02-24 13:55 | 71 | 0:10 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO VACUM SWITCH 15 PARA REPARAR PUENTES PRIMARIOS HACIA RISER | B23022400131 | New_Event | Primary Wire Break | Include | Include | Equipment | 10 | 2023-02-24 | 710 | keep | 0 | Feb | 2023 | 0.00048358 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
SAN JUAN | 2023-02-24 14:25 | 2023-02-24 18:55 | 60 | 4:30 | P | TERMINACION SOTERRADA AVERIADA | SE REPARARO TEMINACION EN T-31 MEDIANTE SJ-230224-01 | S23022400050 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 270 | 2023-02-24 | 16200 | keep | 0 | Feb | 2023 | 0.011034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-24 14:32 | 2023-02-24 15:36 | 8 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23022400053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2023-02-24 | 512 | keep | 0 | Feb | 2023 | 0.00034872 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-24 15:00 | 2023-02-24 22:22 | 92 | 7:22 | P | DESGANCHE | SE ABRIO C/L PARA REALIZAR DESGANCHE COMPLETO DESGANCHE | B23022400143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2023-02-24 | 40664 | keep | 0 | Feb | 2023 | 0.027696 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
CAGUAS | 2023-02-24 15:14 | 2023-02-24 18:46 | 68 | 3:32 | P | CABLE SOTERRADO AVERIADO | 1 NX X 40 EN SU-22 AVERIA SOTERRADA NUEVA DEL T-58 @ T-58A Y AVERIA VIEJA DEL RISER @ T-60. SIGUEN FUERA 53 CLIENTES AFECTADOS. | C23022400083 | New_Event | UG Cable Fault | Include | Include | Equipment | 212 | 2023-02-24 | 14416 | keep | 0 | Feb | 2023 | 0.0098187 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2023-02-24 15:18 | 2023-02-24 15:58 | 737 | 0:40 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 60% DE LA CARGA DEL 1529-15 AJUSTES PROTECCIÃ“N DIFERENCIAL DE LINEA | S23022400074 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-02-24 | 29480 | keep | 0 | Feb | 2023 | 0.020079 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
BAYAMON | 2023-02-24 15:18 | 2023-02-24 15:58 | 1368 | 0:40 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 AJUSTES PROTECCIÃ“N DIFERENCIAL DE LINEA | S23022400074 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-02-24 | 54720 | keep | 0 | Feb | 2023 | 0.03727 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2023-02-24 15:18 | 2023-02-24 15:58 | 1984 | 0:40 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 AJUSTES PROTECCIÃ“N DIFERENCIAL DE LINEA | S23022400074 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-02-24 | 79360 | keep | 0 | Feb | 2023 | 0.054052 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
SAN JUAN | 2023-02-24 15:18 | 2023-02-24 15:58 | 178 | 0:40 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 AJUSTES PROTECCIÃ“N DIFERENCIAL DE LINEA | S23022400074 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-02-24 | 7120 | keep | 0 | Feb | 2023 | 0.0048494 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
SAN JUAN | 2023-02-24 15:18 | 2023-02-24 15:58 | 1802 | 0:40 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 LLEVA 60% DEL 1346-02 AJUSTES PROTECCIÃ“N DIFERENCIAL DE LINEA | S23022400074 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-02-24 | 72080 | keep | 0 | Feb | 2023 | 0.049093 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2023-02-24 15:18 | 2023-02-24 15:19 | 478 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2302240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-24 | 478 | keep | 0 | Feb | 2023 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
AGUADILLA | 2023-02-24 15:19 | 2023-02-24 19:15 | 150 | 3:56 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA | M23022400073 | New_Event | Primary Wire Break | Include | Include | Equipment | 236 | 2023-02-24 | 35400 | keep | 0 | Feb | 2023 | 0.024111 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-02-24 15:24 | 2023-02-24 16:12 | 12 | 0:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S23022400065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 48 | 2023-02-24 | 576 | keep | 0 | Feb | 2023 | 0.00039231 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-02-24 15:39 | 2023-02-24 18:40 | 100 | 3:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23022400107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2023-02-24 | 18100 | keep | 0 | Feb | 2023 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-02-24 16:37 | 2023-02-24 17:30 | 10 | 0:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23022400093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 53 | 2023-02-24 | 530 | keep | 0 | Feb | 2023 | 0.00036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-24 16:40 | 2023-02-24 19:25 | 60 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23022400095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-02-24 | 9900 | keep | 0 | Feb | 2023 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-02-24 16:43 | 2023-02-24 16:44 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23022400096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-24 | 2302 | keep | 0 | Feb | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
BAYAMON | 2023-02-24 16:52 | 2023-02-24 16:53 | 3070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 115KV FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400163 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 3070 | keep | 0 | Feb | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-02-24 16:52 | 2023-02-24 16:53 | 2735 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 115KV FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400163 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 2735 | keep | 0 | Feb | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2023-02-24 16:52 | 2023-02-24 16:53 | 1070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 115KV FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400163 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 1070 | keep | 0 | Feb | 2023 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2023-02-24 16:52 | 2023-02-24 16:53 | 1647 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 115KV FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400162 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 1647 | keep | 0 | Feb | 2023 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-02-24 16:52 | 2023-02-24 16:53 | 3295 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 115KV FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400162 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 3295 | keep | 0 | Feb | 2023 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-02-24 16:52 | 2023-02-24 16:53 | 1180 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 115KV FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400162 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 1180 | keep | 0 | Feb | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2023-02-24 16:52 | 2023-02-24 16:53 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 115KV FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400166 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 320 | keep | 0 | Feb | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-02-24 16:52 | 2023-02-24 16:53 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 115KV FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400166 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-24 | 2234 | keep | 0 | Feb | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
VEGA BAJA | 2023-02-24 17:10 | 2023-02-24 17:40 | 8 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23022400117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-02-24 | 240 | keep | 0 | Feb | 2023 | 0.00016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-02-24 17:21 | 2023-02-27 09:57 | 1 | 64:36 | P | ERROR HUMANO | 1 X 15 EN TRANSFORMADOR POR VIA LIBRE D2023-2985 DEL DIA 24 CLIENTE SE QUEDO SIN SERVICIO. | A23022700019 | New_Event | Human Error | Include | Include | Other | 3876 | 2023-02-24 | 3876 | keep | 0 | Feb | 2023 | 0.0026399 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-24 17:23 | 2023-02-24 20:00 | 50 | 2:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23022400120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 157 | 2023-02-24 | 7850 | keep | 0 | Feb | 2023 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-02-24 17:38 | 2023-02-24 18:16 | 9 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R23022400034 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2023-02-24 | 342 | keep | 0 | Feb | 2023 | 0.00023293 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-02-24 17:45 | 2023-02-24 20:00 | 272 | 2:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R23022400036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-02-24 | 36720 | keep | 0 | Feb | 2023 | 0.02501 | 0.00018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 272
SAN JUAN | 2023-02-24 18:17 | 2023-02-25 09:18 | 20 | 15:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REEMPLAZO PORTA FUSIBLE | S23022400145 | New_Event | Cutout Failure | Include | Include | Equipment | 901 | 2023-02-24 | 18020 | keep | 0 | Feb | 2023 | 0.012273 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-24 18:20 | 2023-02-24 18:21 | 3511 | 0:01 | T | OTRAS CAUSAS | RECIERRE DE BKR AL REALIZAR OPERACIONES EN V/L D2023-3034 | B2302240000X | New_Event | Other Causes | Include | Include | Other | 1 | 2023-02-24 | 3511 | keep | 0 | Feb | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2023-02-24 18:22 | 2023-02-24 18:28 | 3511 | 0:06 | T | OTRAS CAUSAS | SE DISPARO FEEDER A PETICION DE PERSONAL DE CAMPO POR OPERACION EN EL CAMPO | B2302240000X | 1st_after_momentary | Other Causes | Include | Include | Other | 6 | 2023-02-24 | 21066 | keep | 0 | Feb | 2023 | 0.014348 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
CAGUAS | 2023-02-24 18:46 | 2023-02-25 15:45 | 53 | 20:59 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA SOTERRADA DE T-58 A T-58A | C23022400083 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1259 | 2023-02-24 | 66727 | keep | 0 | Feb | 2023 | 0.045447 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-24 18:56 | 2023-02-25 11:25 | 4 | 16:29 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23022400129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 989 | 2023-02-24 | 3956 | keep | 0 | Feb | 2023 | 0.0026944 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-24 19:01 | 2023-02-25 01:18 | 1647 | 6:17 | S | LINEA DE TRANSMISION 115KV | BY-230224-02 SE REMPLAZO FUSIBLE FUNDIDO EN LA ALTA DE XMR Y SE NORMALIZO LAS CARGAS FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400351 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 377 | 2023-02-24 | 620919 | keep | 0 | Feb | 2023 | 0.42291 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-02-24 19:01 | 2023-02-25 01:18 | 3295 | 6:17 | S | LINEA DE TRANSMISION 115KV | BY-230224-02 SE REMPLAZO FUSIBLE FUNDIDO EN LA ALTA DE XMR Y SE NORMALIZO LAS CARGAS FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400351 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 377 | 2023-02-24 | 1242215 | keep | 0 | Feb | 2023 | 0.84607 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-02-24 19:01 | 2023-02-25 01:18 | 1180 | 6:17 | S | LINEA DE TRANSMISION 115KV | BY-230224-02 SE REMPLAZO FUSIBLE FUNDIDO EN LA ALTA DE XMR Y SE NORMALIZO LAS CARGAS FUSIBLE FUNDIDO EN SUBESTACIÃ“N 9502 MONTERREY | B23022400351 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 377 | 2023-02-24 | 444860 | keep | 0 | Feb | 2023 | 0.30299 | 0.00080369 | Sustained | FALSE | FALSE | Not_TMED_Event | 1180
AGUADILLA | 2023-02-24 19:08 | 2023-02-24 21:10 | 15 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23022400108 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2023-02-24 | 1830 | keep | 0 | Feb | 2023 | 0.0012464 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-02-24 19:14 | 2023-02-24 21:00 | 50 | 1:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN C/L | P23022400129 | New_Event | Primary Wire Break | Include | Include | Equipment | 106 | 2023-02-24 | 5300 | keep | 0 | Feb | 2023 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-02-24 19:16 | 2023-02-25 08:52 | 39 | 13:36 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETEZO LINEA PRIMARIA Y 1 X 100 EN C/L | B23022400368 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 816 | 2023-02-24 | 31824 | keep | 0 | Feb | 2023 | 0.021675 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2023-02-24 19:21 | 2023-02-25 07:49 | 70 | 12:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA PORTAFUSIBLE QUEMADO | M23022400111 | New_Event | Cutout Failure | Include | Include | Equipment | 748 | 2023-02-24 | 52360 | keep | 0 | Feb | 2023 | 0.035662 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-02-24 19:37 | 2023-02-24 21:40 | 80 | 2:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23022400114 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 123 | 2023-02-24 | 9840 | keep | 0 | Feb | 2023 | 0.006702 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-02-24 20:00 | 2023-02-24 20:19 | 25 | 0:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R23022400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-02-24 | 475 | keep | 0 | Feb | 2023 | 0.00032352 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-02-24 21:26 | 2023-02-24 23:25 | 881 | 1:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23022400138 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 119 | 2023-02-24 | 104839 | keep | 0 | Feb | 2023 | 0.071405 | 0.00060005 | Sustained | FALSE | FALSE | Not_TMED_Event | 881
BAYAMON | 2023-02-24 21:33 | 2023-02-24 23:04 | 27 | 1:31 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23022400437 | New_Event | Animals | Include | Include | Wildlife | 91 | 2023-02-24 | 2457 | keep | 0 | Feb | 2023 | 0.0016735 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2023-02-24 22:33 | 2023-02-25 15:07 | 10 | 16:34 | P | DESGANCHE | 1 X 15 EN XMR SE DESGANCHO PRIMARIA | S23022400160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 994 | 2023-02-24 | 9940 | keep | 0 | Feb | 2023 | 0.0067701 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-24 22:33 | 2023-02-25 09:00 | 15 | 10:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23022400159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 627 | 2023-02-24 | 9405 | keep | 0 | Feb | 2023 | 0.0064057 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-24 22:35 | 2023-02-25 00:38 | 61 | 2:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIA | B23022400446 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 123 | 2023-02-24 | 7503 | keep | 0 | Feb | 2023 | 0.0051103 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
VEGA BAJA | 2023-02-24 22:35 | 2023-02-25 01:43 | 416 | 3:08 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23022400155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-02-24 | 78208 | keep | 0 | Feb | 2023 | 0.053267 | 0.00028334 | Sustained | FALSE | FALSE | Not_TMED_Event | 416
BAYAMON | 2023-02-24 22:37 | 2023-02-25 01:14 | 320 | 2:37 | T | LINEA DE TRANSMISION 115KV | SE RETIRO LA CARGA A PETICION DEL CCE PARA PODER ABRIR EL GOAB 36103 EN OPERACIONES DE SUB 9502-00 SE HICIERON OPERACIONES CON BY-230224-02 | B23022400448 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-24 | 50240 | keep | 0 | Feb | 2023 | 0.034218 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-02-24 22:38 | 2023-02-25 01:15 | 2234 | 2:37 | T | LINEA DE TRANSMISION 115KV | SE RETIRO LA CARGA A PETICION DEL CCE PARA PODER ABRIR EL GOAB 36103 EN OPERACIONES DE SUB 9502-00 SE HICIERON OPERACIONES CON BY-230224-02 | B23022400449 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-02-24 | 350738 | keep | 0 | Feb | 2023 | 0.23889 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-02-24 23:04 | 2023-02-24 23:05 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23022400449 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-24 | 1859 | keep | 0 | Feb | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2023-02-24 23:05 | 2023-02-25 09:18 | 27 | 10:13 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23022400437 | Partial_restoration | Animals | Include | Include | Wildlife | 613 | 2023-02-24 | 16551 | keep | 0 | Feb | 2023 | 0.011273 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-24 23:23 | 2023-02-24 23:34 | 3070 | 0:11 | T | LINEA DE TRANSMISION 115KV | SE RETIRO LA CARGA A PETICION DEL CCE PARA PODER ABRIR EL GOAB 36103 EN OPERACIONES DE SUB 9502-00 | B23022400462 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-02-24 | 33770 | keep | 0 | Feb | 2023 | 0.023001 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-02-24 23:23 | 2023-02-24 23:34 | 2735 | 0:11 | T | LINEA DE TRANSMISION 115KV | SE RETIRO LA CARGA A PETICION DEL CCE PARA PODER ABRIR EL GOAB 36103 EN OPERACIONES DE SUB 9502-00 | B23022400463 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-02-24 | 30085 | keep | 0 | Feb | 2023 | 0.020491 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2023-02-24 23:23 | 2023-02-24 23:35 | 1070 | 0:12 | T | LINEA DE TRANSMISION 115KV | SE RETIRO LA CARGA A PETICION DEL CCE PARA PODER ABRIR EL GOAB 36103 EN OPERACIONES DE SUB 9502-00 | B23022400464 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-02-24 | 12840 | keep | 0 | Feb | 2023 | 0.0087453 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
FAJARDO | 2023-02-24 23:41 | 2023-02-25 10:06 | 30 | 10:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 Y 1 X 30 EN CORTE DE LINEA SE REMPLAZO PIN | R23022400058 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 625 | 2023-02-24 | 18750 | keep | 0 | Feb | 2023 | 0.012771 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-02-25 00:19 | 2023-02-25 07:12 | 931 | 6:53 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE Y 1 X 100 EN C/L | B23022500005 | New_Event | Switch Failure | Include | Include | Equipment | 413 | 2023-02-25 | 384503 | keep | 0 | Feb | 2023 | 0.26188 | 0.0006341 | Sustained | FALSE | FALSE | Not_TMED_Event | 931
CANOVANAS | 2023-02-25 00:21 | 2023-02-25 09:34 | 160 | 9:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R23022500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 553 | 2023-02-25 | 88480 | keep | 0 | Feb | 2023 | 0.060263 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
SAN JUAN | 2023-02-25 00:43 | 2023-02-25 11:13 | 34 | 10:30 | P | DESGANCHE | 2 X 100 EN C/L Y 2 X 65 EN C/L DESGANCHE PRIMARIO | S23022500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 630 | 2023-02-25 | 21420 | keep | 0 | Feb | 2023 | 0.014589 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
YAUCO | 2023-02-25 00:47 | 2023-02-25 02:33 | 1637 | 1:46 | T | LINEA DE TRANSMISION 38KV | SE ELIMINO OVER HEAD DE LINEA 38 KV LINEA 700 | P23022500011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2023-02-25 | 173522 | keep | 0 | Feb | 2023 | 0.11819 | 0.001115 | Sustained | FALSE | FALSE | Not_TMED_Event | 1637
SAN JUAN | 2023-02-25 00:53 | 2023-02-25 00:55 | 1681 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE 1303-01 QUE LLEVA 1346-06, CERRADO POR SCADA | S23022500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-25 | 3362 | keep | 0 | Feb | 2023 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-02-25 00:53 | 2023-02-25 00:55 | 1598 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE 1303-01 QUE LLEVA 1346-06, CERRADO POR SCADA | S23022500006 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-25 | 3196 | keep | 0 | Feb | 2023 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
CANOVANAS | 2023-02-25 01:09 | 2023-02-25 10:43 | 20 | 9:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | R23022500008 | New_Event | Cutout Failure | Include | Include | Equipment | 574 | 2023-02-25 | 11480 | keep | 0 | Feb | 2023 | 0.007819 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-02-25 01:19 | 2023-02-25 11:38 | 13 | 10:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR LLUVIAS | C23022500001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 619 | 2023-02-25 | 8047 | keep | 0 | Feb | 2023 | 0.0054808 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-02-25 01:23 | 2023-02-25 01:24 | 450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 450 | keep | 0 | Feb | 2023 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
BARRANQUITAS | 2023-02-25 01:38 | 2023-02-25 01:39 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23022500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 1565 | keep | 0 | Feb | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-02-25 01:38 | 2023-02-25 01:39 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23022500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 976 | keep | 0 | Feb | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-02-25 01:38 | 2023-02-25 01:39 | 548 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA | C23022500002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 548 | keep | 0 | Feb | 2023 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-02-25 01:38 | 2023-02-25 01:39 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA SE REMOVIÃ“ BAMBUA ENTRE EL BKR 0830 Y EL ACB 0829A | C23022500003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 315 | keep | 0 | Feb | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-02-25 01:38 | 2023-02-25 01:39 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA SE REMOVIÃ“ BAMBUA ENTRE EL BKR 0830 Y EL ACB 0829A | C23022500003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 870 | keep | 0 | Feb | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-02-25 01:38 | 2023-02-25 01:39 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA SE REMOVIO BAMBUA ENTRE EL BKR 0830 Y EL ACB 0829A | C23022500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 2906 | keep | 0 | Feb | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-02-25 01:38 | 2023-02-25 01:39 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA SE REMOVIO BAMBUA ENTRE EL BKR 0830 Y EL ACB 0829A | C23022500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 2343 | keep | 0 | Feb | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
BARRANQUITAS | 2023-02-25 01:44 | 2023-02-25 08:57 | 60 | 7:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIAS | C23022500005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 433 | 2023-02-25 | 25980 | keep | 0 | Feb | 2023 | 0.017695 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-02-25 01:45 | 2023-02-25 09:30 | 40 | 7:45 | P | DESGANCHE | 1 X 80 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23022500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2023-02-25 | 18600 | keep | 0 | Feb | 2023 | 0.012668 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-02-25 01:47 | 2023-02-25 01:48 | 2192 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR CARGA POR EL 9605-01 | C2302250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-25 | 2192 | keep | 0 | Feb | 2023 | 0.001493 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
BARRANQUITAS | 2023-02-25 01:47 | 2023-02-25 01:48 | 2410 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 9601-01 | C2302250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 2410 | keep | 0 | Feb | 2023 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
SAN JUAN | 2023-02-25 01:50 | 2023-02-25 01:51 | 143 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1404-06 LLEVA 80% DEL 1404-07 | S2302250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 143 | keep | 0 | Feb | 2023 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-02-25 01:50 | 2023-02-25 01:51 | 1085 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE 1404-06 LLEVA 80% DEL 1404-07 | S2302250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-25 | 1085 | keep | 0 | Feb | 2023 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BARRANQUITAS | 2023-02-25 01:53 | 2023-02-25 09:46 | 65 | 7:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CORTE DE LINEA LLUVIAS | C23022500007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 473 | 2023-02-25 | 30745 | keep | 0 | Feb | 2023 | 0.02094 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-02-25 02:16 | 2023-02-25 02:17 | 3798 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B23022500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 3798 | keep | 0 | Feb | 2023 | 0.0025868 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
BAYAMON | 2023-02-25 02:26 | 2023-02-25 10:54 | 85 | 8:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO AISLADOR | B23022500024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 508 | 2023-02-25 | 43180 | keep | 0 | Feb | 2023 | 0.02941 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2023-02-25 02:36 | 2023-02-25 02:37 | 3798 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B23022500027 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 3798 | keep | 0 | Feb | 2023 | 0.0025868 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
UTUADO | 2023-02-25 03:04 | 2023-02-25 03:05 | 3502 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA SE CERRO POR SCADA | A23022500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 3502 | keep | 0 | Feb | 2023 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
SAN JUAN | 2023-02-25 03:07 | 2023-02-25 03:08 | 1825 | 0:01 | T | PARARRAYOS DEFECTUOSO | DISPARO DE BKR SE CERO POR CONTROL | S23022500026 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-02-25 | 1825 | keep | 0 | Feb | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-02-25 03:10 | 2023-02-25 04:41 | 1825 | 1:31 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES BUSCANDO AVERIA | S23022500026 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 91 | 2023-02-25 | 166075 | keep | 0 | Feb | 2023 | 0.11311 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
HUMACAO | 2023-02-25 03:12 | 2023-02-25 17:46 | 25 | 14:34 | P | TRANSFORMADOR AVERIADO | 1 RBA X 50 EN SU-2 SE REPARO BASE DE FUSIBLE NX EN XMR | C23022500010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 874 | 2023-02-25 | 21850 | keep | 0 | Feb | 2023 | 0.014882 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-25 03:33 | 2023-02-25 03:34 | 651 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO X CONTROL | B2302250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 651 | keep | 0 | Feb | 2023 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
CANOVANAS | 2023-02-25 03:42 | 2023-02-25 03:43 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23022500011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 3464 | keep | 0 | Feb | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
VEGA BAJA | 2023-02-25 03:45 | 2023-02-25 03:46 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-02-25 03:47 | 2023-02-25 03:48 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2302250000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 4027 | keep | 0 | Feb | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
BAYAMON | 2023-02-25 03:52 | 2023-02-25 08:21 | 1399 | 4:29 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO CONDUCTOR CRUZADO Y SE CERRO POR SCADA. EN SERVICIO 50% 1704-01 | B23022500044 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 269 | 2023-02-25 | 376331 | keep | 0 | Feb | 2023 | 0.25632 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
ARECIBO | 2023-02-25 03:52 | 2023-02-25 06:28 | 2201 | 2:36 | T | CRUCETA DEFECTUOSA O AVERIADA | GOI # AR--23025-01A REPARAR CRUCETAS DE METAL ZAFADAS | A23022500006 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 156 | 2023-02-25 | 343356 | keep | 0 | Feb | 2023 | 0.23386 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
BAYAMON | 2023-02-25 03:52 | 2023-02-25 03:57 | 652 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-02-25 | 3260 | keep | 0 | Feb | 2023 | 0.0022204 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2023-02-25 03:52 | 2023-02-25 03:57 | 2704 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-02-25 | 13520 | keep | 0 | Feb | 2023 | 0.0092084 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
FAJARDO | 2023-02-25 04:03 | 2023-02-25 04:04 | 956 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23022500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 956 | keep | 0 | Feb | 2023 | 0.00065113 | 0.00065113 | Momentary | FALSE | FALSE | Not_TMED_Event | 956
BARRANQUITAS | 2023-02-25 04:05 | 2023-02-25 04:06 | 327 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23022500013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 327 | keep | 0 | Feb | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
SAN JUAN | 2023-02-25 04:20 | 2023-02-25 10:45 | 15 | 6:25 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23022500031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2023-02-25 | 5775 | keep | 0 | Feb | 2023 | 0.0039333 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-25 04:21 | 2023-02-25 04:22 | 1526 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500052 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 1526 | keep | 0 | Feb | 2023 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
BAYAMON | 2023-02-25 04:21 | 2023-02-25 04:22 | 308 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500052 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 308 | keep | 0 | Feb | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-02-25 04:21 | 2023-02-25 04:22 | 1397 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500052 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 1397 | keep | 0 | Feb | 2023 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
BAYAMON | 2023-02-25 04:21 | 2023-02-25 04:22 | 2926 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500052 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 2926 | keep | 0 | Feb | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
BAYAMON | 2023-02-25 04:29 | 2023-02-25 04:30 | 27 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 27 | keep | 0 | Feb | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-02-25 04:29 | 2023-02-25 04:30 | 603 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 603 | keep | 0 | Feb | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-02-25 04:29 | 2023-02-25 04:30 | 6 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 6 | keep | 0 | Feb | 2023 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-25 04:29 | 2023-02-25 04:30 | 325 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 325 | keep | 0 | Feb | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-02-25 04:29 | 2023-02-25 04:30 | 172 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7,800 | B23022500053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-02-25 | 172 | keep | 0 | Feb | 2023 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
VEGA BAJA | 2023-02-25 04:31 | 2023-02-25 12:20 | 30 | 7:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23022500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 469 | 2023-02-25 | 14070 | keep | 0 | Feb | 2023 | 0.009583 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-25 04:41 | 2023-02-25 05:05 | 1369 | 0:24 | P | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES BUSCANDO AVERIA | S23022500026 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 24 | 2023-02-25 | 32856 | keep | 0 | Feb | 2023 | 0.022378 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-25 04:58 | 2023-02-25 15:16 | 24 | 10:18 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 20 EN XMR 1 X 10 EN C/L SE RETIRO PELIGRO CABLE PRIMARIO VACANTE TOCANDO ESTRUCTURA | B23022500078 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 618 | 2023-02-25 | 14832 | keep | 0 | Feb | 2023 | 0.010102 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-02-25 05:05 | 2023-02-25 05:07 | 1825 | 0:02 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES BUSCANDO AVERIA | S23022500026 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2023-02-25 | 3650 | keep | 0 | Feb | 2023 | 0.002486 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-25 05:07 | 2023-02-25 05:21 | 1369 | 0:14 | P | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES BUSCANDO AVERIA | S23022500026 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 14 | 2023-02-25 | 19166 | keep | 0 | Feb | 2023 | 0.013054 | 0.00093242 | Sustained | FALSE | FALSE | Not_TMED_Event | 1369
MAYAGÃœEZ | 2023-02-25 05:09 | 2023-02-25 10:42 | 39 | 5:33 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR POR LLUVIAS Y VIENTOS FUERTES SE OPERO MANAULMENTE RTU FUERA DE SERVICIO | M23022500004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 333 | 2023-02-25 | 12987 | keep | 0 | Feb | 2023 | 0.0088454 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
VEGA BAJA | 2023-02-25 05:09 | 2023-02-25 10:25 | 50 | 5:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23022500018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2023-02-25 | 15800 | keep | 0 | Feb | 2023 | 0.010761 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-02-25 05:21 | 2023-02-25 05:23 | 1825 | 0:02 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES BUSCANDO AVERIA | S23022500026 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2023-02-25 | 3650 | keep | 0 | Feb | 2023 | 0.002486 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-25 05:23 | 2023-02-25 06:54 | 1369 | 1:31 | P | PARARRAYOS DEFECTUOSO | SE ENCONTRARON DOS PARARAYOS AVERIADOS SE DESCONECTARON Y SE SECCIONALIZO AVERIA | S23022500026 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 91 | 2023-02-25 | 124579 | keep | 0 | Feb | 2023 | 0.08485 | 0.00093242 | Sustained | FALSE | FALSE | Not_TMED_Event | 1369
MAYAGÃœEZ | 2023-02-25 05:38 | 2023-02-25 10:30 | 10 | 4:52 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO FASES | M23022500009 | New_Event | Animals | Include | Include | Wildlife | 292 | 2023-02-25 | 2920 | keep | 0 | Feb | 2023 | 0.0019888 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-02-25 05:49 | 2023-02-25 11:12 | 22 | 5:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C23022500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2023-02-25 | 7106 | keep | 0 | Feb | 2023 | 0.0048399 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-02-25 05:53 | 2023-02-25 09:45 | 15 | 3:52 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S23022500052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2023-02-25 | 3480 | keep | 0 | Feb | 2023 | 0.0023702 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-02-25 05:55 | 2023-02-25 05:56 | 2610 | 0:01 | T | DESGANCHE | DISPARO DE BKR SE CERRO X CONTROL | B2302250000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-25 | 2610 | keep | 0 | Feb | 2023 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2023-02-25 05:56 | 2023-02-25 16:18 | 50 | 10:22 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23022500145 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 622 | 2023-02-25 | 31100 | keep | 0 | Feb | 2023 | 0.021182 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-02-25 05:59 | 2023-02-25 09:25 | 101 | 3:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23022500040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-02-25 | 20806 | keep | 0 | Feb | 2023 | 0.014171 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
AGUADILLA | 2023-02-25 06:03 | 2023-02-25 10:07 | 20 | 4:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23022500011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2023-02-25 | 4880 | keep | 0 | Feb | 2023 | 0.0033237 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-25 06:05 | 2023-02-25 06:06 | 1225 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 75% DE LA CARGA DEL 1203-03 | S2302250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 1225 | keep | 0 | Feb | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-02-25 06:05 | 2023-02-25 06:06 | 462 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 75% DE LA CARGA POR EL 1203-01 | S2302250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-25 | 462 | keep | 0 | Feb | 2023 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
CANOVANAS | 2023-02-25 06:14 | 2023-02-25 06:15 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23022500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 4188 | keep | 0 | Feb | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
SAN JUAN | 2023-02-25 06:59 | 2023-02-25 16:30 | 15 | 9:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 75KVA AVERIADO | S23022500071 | New_Event | Service Transformer Failure | Include | Include | Equipment | 571 | 2023-02-25 | 8565 | keep | 0 | Feb | 2023 | 0.0058336 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-25 06:59 | 2023-02-25 19:39 | 16 | 12:40 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR SE DESGANCHO SECUNDARIA | S23022500188 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 760 | 2023-02-25 | 12160 | keep | 0 | Feb | 2023 | 0.0082821 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2023-02-25 06:59 | 2023-02-25 12:43 | 20 | 5:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA PARTIDA | C23022500032 | New_Event | Cutout Failure | Include | Include | Equipment | 344 | 2023-02-25 | 6880 | keep | 0 | Feb | 2023 | 0.0046859 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-02-25 07:00 | 2023-02-25 09:57 | 60 | 2:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M23022500012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2023-02-25 | 10620 | keep | 0 | Feb | 2023 | 0.0072332 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-02-25 07:06 | 2023-02-25 09:59 | 15 | 2:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M23022500013 | New_Event | Cutout Failure | Include | Include | Equipment | 173 | 2023-02-25 | 2595 | keep | 0 | Feb | 2023 | 0.0017674 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-02-25 07:11 | 2023-02-25 16:54 | 25 | 9:43 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23022500034 | New_Event | Animals | Include | Include | Wildlife | 583 | 2023-02-25 | 14575 | keep | 0 | Feb | 2023 | 0.009927 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-02-25 07:24 | 2023-02-25 08:54 | 40 | 1:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23022500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-02-25 | 3600 | keep | 0 | Feb | 2023 | 0.0024519 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-02-25 07:28 | 2023-02-25 15:00 | 80 | 7:32 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | A23022500036 | New_Event | Primary Wire Break | Include | Include | Equipment | 452 | 2023-02-25 | 36160 | keep | 0 | Feb | 2023 | 0.024628 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-02-25 07:35 | 2023-02-25 14:31 | 47 | 6:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23022500027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2023-02-25 | 19552 | keep | 0 | Feb | 2023 | 0.013317 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
CANOVANAS | 2023-02-25 07:35 | 2023-02-25 12:09 | 100 | 4:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23022500026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 274 | 2023-02-25 | 27400 | keep | 0 | Feb | 2023 | 0.018662 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-02-25 07:54 | 2023-02-25 12:10 | 1 | 4:16 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R23022500034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2023-02-25 | 256 | keep | 0 | Feb | 2023 | 0.00017436 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-02-25 07:55 | 2023-02-25 10:22 | 20 | 2:27 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE SECUNDARIO | C23022500041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 147 | 2023-02-25 | 2940 | keep | 0 | Feb | 2023 | 0.0020024 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-02-25 07:56 | 2023-02-25 08:03 | 3630 | 0:07 | T | CAPACITOR DEFECTUOSO O AVERIADO | SE DESCONECTO BAJANTE DE BANCO DE CAPACITORES FUERA DE SERVICIO QUE ESTABAN QUEMANDOSE | M23022500024 | New_Event | Capacitor Failure | Include | Include | Equipment | 7 | 2023-02-25 | 25410 | keep | 0 | Feb | 2023 | 0.017307 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
AGUADILLA | 2023-02-25 08:03 | 2023-02-25 10:20 | 10 | 2:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO PORTE FUSIBLE | A23022500043 | New_Event | Cutout Failure | Include | Include | Equipment | 137 | 2023-02-25 | 1370 | keep | 0 | Feb | 2023 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-25 08:21 | 2023-02-25 08:32 | 699 | 0:11 | P | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR AL SECCIONALIZAR CONDUCTOR PEGADO A CRUCETA | B23022500044 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 11 | 2023-02-25 | 7689 | keep | 0 | Feb | 2023 | 0.0052369 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-25 08:21 | 2023-02-25 14:30 | 23 | 6:09 | P | CONDUCTOR ARRIADO O CRUZADO | 1X10 EN XMR SE DESENRREDO EL 13KV QUE ESTABA ARRIADO HACIENDO CONTACTO CON CABLES VACANTES | B23022500205 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 369 | 2023-02-25 | 8487 | keep | 0 | Feb | 2023 | 0.0057805 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-02-25 08:32 | 2023-02-25 09:48 | 1399 | 1:16 | T | CONDUCTOR ARRIADO O CRUZADO | SE CERRO INTERRUPTOR SECCIONALIZANDO ALIMENTADOR POR CONDUCTOR PEGADO A CRUCETA. 50% EN SERVICIO. PERSONAL DE SUBESTACIONES TUVO QUE TRABAJAR CON BKR POR NO QUERER OPERAR POR CONTROL | B23022500044 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 76 | 2023-02-25 | 106324 | keep | 0 | Feb | 2023 | 0.072417 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-02-25 08:33 | 2023-02-25 11:00 | 5 | 2:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M23022500029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 147 | 2023-02-25 | 735 | keep | 0 | Feb | 2023 | 0.00050061 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-02-25 08:37 | 2023-02-25 15:54 | 40 | 7:17 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L MAL TIEMPO RAYOS | P23022500075 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 437 | 2023-02-25 | 17480 | keep | 0 | Feb | 2023 | 0.011906 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-02-25 08:38 | 2023-02-25 09:35 | 1018 | 0:57 | P | FUEGO | SE ABRE CORTE DE LINEA PARA QUE BOMBEROS APAGUEN FUEGO EN POSTE CRUCETA AVERIADA | P23022500078 | New_Event | Fire | Include | Include | Public | 57 | 2023-02-25 | 58026 | keep | 0 | Feb | 2023 | 0.039521 | 0.00069336 | Sustained | FALSE | FALSE | Not_TMED_Event | 1018
YAUCO | 2023-02-25 08:46 | 2023-02-25 12:00 | 75 | 3:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23022500082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-02-25 | 14550 | keep | 0 | Feb | 2023 | 0.0099099 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-02-25 08:53 | 2023-02-25 12:45 | 25 | 3:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO BAJANTE SECUNDARIO | S23022500122 | New_Event | Secondary Wire Break | Include | Include | Equipment | 232 | 2023-02-25 | 5800 | keep | 0 | Feb | 2023 | 0.0039504 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-02-25 08:56 | 2023-02-25 09:43 | 25 | 0:47 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE POSTE PODRIDO | C23022500064 | New_Event | Primary Pole Failure | Include | Include | Equipment | 47 | 2023-02-25 | 1175 | keep | 0 | Feb | 2023 | 0.00080029 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-02-25 08:56 | 2023-02-25 15:57 | 15 | 7:01 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | VIA LIBRE EXPRESS X2023-230 SE REEMPLAZO POSTE PRIMARIO PROYECTO FIONA | C23022500058 | New_Event | Primary Pole Failure | Include | Include | Equipment | 421 | 2023-02-25 | 6315 | keep | 0 | Feb | 2023 | 0.0043011 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-25 09:48 | 2023-02-25 09:55 | 699 | 0:07 | P | CONDUCTOR ARRIADO O CRUZADO | SE SEPARO CONDUCTOR PEGADO A CRUCETA CON VARETA Y SE CERRO MACHETES. EN SERVICIO | B23022500044 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 7 | 2023-02-25 | 4893 | keep | 0 | Feb | 2023 | 0.0033326 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-02-25 09:55 | 2023-02-25 10:38 | 1 | 0:43 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE | R23022500051 | New_Event | Animals | Include | Include | Wildlife | 43 | 2023-02-25 | 43 | keep | 0 | Feb | 2023 | 2.9287e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-25 09:58 | 2023-02-25 12:31 | 150 | 2:33 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | B23022500231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-02-25 | 22950 | keep | 0 | Feb | 2023 | 0.015631 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2023-02-25 10:00 | 2023-02-25 10:50 | 8 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REEMPLAZO DE BARRAS SULFATADAS EN PEDESTAL | P23022500091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-02-25 | 400 | keep | 0 | Feb | 2023 | 0.00027244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-02-25 10:01 | 2023-02-25 13:31 | 11 | 3:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 15 EN XMR Y 1 X 50 EN AEREO PROVICIONAL SE REEMPLASO ASILADOR | S23022500050 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 210 | 2023-02-25 | 2310 | keep | 0 | Feb | 2023 | 0.0015733 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-02-25 10:01 | 2023-02-25 12:02 | 11 | 2:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN XMR Y SE REEMPLAZO BAJANTE DE CAJA A XMR | S23022500147 | New_Event | Secondary Wire Break | Include | Include | Equipment | 121 | 2023-02-25 | 1331 | keep | 0 | Feb | 2023 | 0.00090654 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-02-25 10:04 | 2023-02-25 10:05 | 4085 | 0:01 | T | CABLE SOTERRADO AVERIADO | RECERRO | R23022500000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2023-02-25 | 4085 | keep | 0 | Feb | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-02-25 10:05 | 2023-02-25 10:10 | 200 | 0:05 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA T-13 A T-14 AVERIA VIEJA T-22 A T-13 1 X 40 EN PROVISIONAL | R23022500018 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 5 | 2023-02-25 | 1000 | keep | 0 | Feb | 2023 | 0.0006811 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-02-25 10:10 | 2023-02-25 23:10 | 120 | 13:00 | P | CABLE SOTERRADO AVERIADO | SE CONTRUYO PROVISIONAL AEREO T-4 @ T-14 POR AVERIA POR SOTERRADA DEL T-13 AL T-14 | R23022500018 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 780 | 2023-02-25 | 93600 | keep | 0 | Feb | 2023 | 0.063751 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-25 10:10 | 2023-02-25 11:54 | 6 | 1:44 | P | DESGANCHE | 1 X 15 EN XMR SE RETIRO RAMA CRUZANDO LINEA PRIMARIA | B23022500235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-02-25 | 624 | keep | 0 | Feb | 2023 | 0.000425 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-25 10:46 | 2023-02-25 14:09 | 60 | 3:23 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23022500245 | New_Event | Animals | Include | Include | Wildlife | 203 | 2023-02-25 | 12180 | keep | 0 | Feb | 2023 | 0.0082957 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-02-25 10:47 | 2023-02-25 14:46 | 20 | 3:59 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA POR ARBOL SOBRE LINEA | M23022500047 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 239 | 2023-02-25 | 4780 | keep | 0 | Feb | 2023 | 0.0032556 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-02-25 10:52 | 2023-02-25 11:29 | 1 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | CONECCIONES SECUNDARIAS SULFATADAS | P23022500102 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-02-25 | 37 | keep | 0 | Feb | 2023 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-25 10:58 | 2023-02-25 10:59 | 1180 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B2302250000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-25 | 1180 | keep | 0 | Feb | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2023-02-25 10:59 | 2023-02-26 01:05 | 75 | 14:06 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23022500408 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 846 | 2023-02-25 | 63450 | keep | 0 | Feb | 2023 | 0.043216 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-02-25 11:00 | 2023-02-25 13:56 | 100 | 2:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLASO CAJA DE XMR | S23022500169 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2023-02-25 | 17600 | keep | 0 | Feb | 2023 | 0.011987 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-02-25 11:18 | 2023-02-25 13:21 | 20 | 2:03 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA TENSOR PARTIDO CRUZANDO CON CAJA PRIMARIA | M23022500049 | New_Event | Damage From Public | Include | Include | Public | 123 | 2023-02-25 | 2460 | keep | 0 | Feb | 2023 | 0.0016755 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-02-25 11:29 | 2023-02-25 12:27 | 12 | 0:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR SECUNDARIA PARTIDA | B23022500254 | New_Event | Secondary Wire Break | Include | Include | Equipment | 58 | 2023-02-25 | 696 | keep | 0 | Feb | 2023 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-02-25 11:42 | 2023-02-25 15:00 | 12 | 3:18 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR DESGANCHE | R23022500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2023-02-25 | 2376 | keep | 0 | Feb | 2023 | 0.0016183 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-02-25 11:44 | 2023-02-25 15:18 | 100 | 3:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23022500107 | New_Event | Primary Wire Break | Include | Include | Equipment | 214 | 2023-02-25 | 21400 | keep | 0 | Feb | 2023 | 0.014575 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-02-25 12:00 | 2023-02-25 13:15 | 4 | 1:15 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR LIQUEO ESCAPE DE 37.5 POR 37.5 KVA | A23022500078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 75 | 2023-02-25 | 300 | keep | 0 | Feb | 2023 | 0.00020433 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-02-25 12:25 | 2023-02-25 15:41 | 676 | 3:16 | T | ARBOL SOBRE LINEA | DISPARO DE BKR SE RETIRO ARBOL SOBRE LINEA SE CERRO POR CONTROL | C23022500107 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 196 | 2023-02-25 | 132496 | keep | 0 | Feb | 2023 | 0.090242 | 0.00046042 | Sustained | FALSE | FALSE | Not_TMED_Event | 676
UTUADO | 2023-02-25 12:30 | 2023-02-25 15:55 | 30 | 3:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23022500084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-02-25 | 6150 | keep | 0 | Feb | 2023 | 0.0041887 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-02-25 12:36 | 2023-02-25 12:48 | 1 | 0:12 | P | ANIMAL | 1 X 15 EN CORTE DE LINEA AVE CRUZO FASE | R23022500066 | New_Event | Animals | Include | Include | Wildlife | 12 | 2023-02-25 | 12 | keep | 0 | Feb | 2023 | 8.1731e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-25 12:52 | 2023-02-25 14:56 | 200 | 2:04 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23022500266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-02-25 | 24800 | keep | 0 | Feb | 2023 | 0.016891 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-02-25 13:01 | 2023-02-25 16:02 | 1 | 3:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 10 EN BANCO DE XMR Y SE REEMPLAZARON CONEXIONES SECUNDARIA | B23022500268 | New_Event | Secondary Wire Break | Include | Include | Equipment | 181 | 2023-02-25 | 181 | keep | 0 | Feb | 2023 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-25 13:34 | 2023-02-25 15:04 | 40 | 1:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M23022500057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-02-25 | 3600 | keep | 0 | Feb | 2023 | 0.0024519 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-25 13:46 | 2023-02-25 15:40 | 94 | 1:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN AEREO PROVISIONAL NO CAUSA | B23022500297 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2023-02-25 | 10716 | keep | 0 | Feb | 2023 | 0.0072986 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
MAYAGÃœEZ | 2023-02-25 13:50 | 2023-02-25 15:36 | 8 | 1:46 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23022500059 | New_Event | Animals | Include | Include | Wildlife | 106 | 2023-02-25 | 848 | keep | 0 | Feb | 2023 | 0.00057757 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-25 13:52 | 2023-02-25 18:10 | 7 | 4:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BARRAS DE PEDESTAL | B23022500302 | New_Event | Secondary Wire Break | Include | Include | Equipment | 258 | 2023-02-25 | 1806 | keep | 0 | Feb | 2023 | 0.0012301 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-02-25 13:59 | 2023-02-25 16:13 | 1 | 2:14 | P | PROBLEMA DEL CLIENTE | 2 X 80 EN RISER PROBLEMA DE CLIENTE CONTAMINACION EN GABINETE DEL CLIENETE | B23022500307 | New_Event | Customer-Related Interruption | Include | Include | Public | 134 | 2023-02-25 | 134 | keep | 0 | Feb | 2023 | 9.1267e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-25 13:59 | 2023-02-25 17:21 | 24 | 3:22 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA T-110 A T-111 AVERIA VIEJA T-112 A T-111 1 X 25 EN PROVISIONAL | R23022500072 | New_Event | UG Cable Fault | Include | Include | Equipment | 202 | 2023-02-25 | 4848 | keep | 0 | Feb | 2023 | 0.003302 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-02-25 14:32 | 2023-02-25 18:00 | 10 | 3:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23022500186 | New_Event | Secondary Wire Break | Include | Include | Equipment | 208 | 2023-02-25 | 2080 | keep | 0 | Feb | 2023 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-25 15:07 | 2023-02-25 15:33 | 312 | 0:26 | T | DESGANCHE | SE ESTABLECE GOI SJ-230225-02 PARA REALIZAR DESGANCHE | S23022500189 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 26 | 2023-02-25 | 8112 | keep | 0 | Feb | 2023 | 0.005525 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-02-25 15:11 | 2023-02-25 17:41 | 2 | 2:30 | P | CAUSAS EXTERNAS | 2 X 10 EN TRANSFORMADOR POR IMPACTO DE VEHICULO CON POSTE | M23022500065 | New_Event | Damage From Public | Include | Include | Public | 150 | 2023-02-25 | 300 | keep | 0 | Feb | 2023 | 0.00020433 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-02-25 15:15 | 2023-02-25 15:18 | 520 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23022500130 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-02-25 | 1560 | keep | 0 | Feb | 2023 | 0.0010625 | 0.00035417 | Momentary | FALSE | FALSE | Not_TMED_Event | 520
BAYAMON | 2023-02-25 15:16 | 2023-02-25 22:37 | 288 | 7:21 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN CORTE DE LINEA QUE CRUZA SOTERADO 1 X 80 EN RISER Y SE ENCONTRO AVERIA DEL SU-3A @ T-2 - SE REFIRIO A SOTERRADO QUEDAN 10 CLIENTES POR ENTRAR EN SERVICIO | B23022500334 | New_Event | UG Cable Fault | Include | Include | Equipment | 441 | 2023-02-25 | 127008 | keep | 0 | Feb | 2023 | 0.086505 | 0.00019616 | Sustained | FALSE | FALSE | Not_TMED_Event | 288
MAYAGÃœEZ | 2023-02-25 15:38 | 2023-02-25 18:07 | 500 | 2:29 | P | MAL TIEMPO/RAYOS | 2 X 140 2 X 80 Y 2 X 65 NO SE ENCONTRO CAUSA | M23022500069 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 149 | 2023-02-25 | 74500 | keep | 0 | Feb | 2023 | 0.050742 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
VEGA BAJA | 2023-02-25 15:58 | 2023-02-25 20:00 | 80 | 4:02 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23022500349 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2023-02-25 | 19360 | keep | 0 | Feb | 2023 | 0.013186 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-02-25 16:23 | 2023-02-25 20:25 | 60 | 4:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | A23022500103 | New_Event | Primary Wire Break | Include | Include | Equipment | 242 | 2023-02-25 | 14520 | keep | 0 | Feb | 2023 | 0.0098895 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-02-25 16:26 | 2023-02-25 19:44 | 17 | 3:18 | P | NO SE REPORTO CAUSA | 1 X 12 EN XMR TIPO NX NO CAUSA | B23022500363 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2023-02-25 | 3366 | keep | 0 | Feb | 2023 | 0.0022926 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-02-25 16:32 | 2023-02-25 16:33 | 1491 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23022500090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 1491 | keep | 0 | Feb | 2023 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
CAGUAS | 2023-02-25 16:33 | 2023-02-25 20:04 | 14 | 3:31 | P | PROBLEMA DEL CLIENTE | 1 NX X 20 EN XMR SE DESCONECTO CLIENTE CON TOMA AVERIADA | C23022500140 | New_Event | Customer-Related Interruption | Include | Include | Public | 211 | 2023-02-25 | 2954 | keep | 0 | Feb | 2023 | 0.002012 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-02-25 16:44 | 2023-02-26 09:28 | 40 | 16:44 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR AVE QUE CRUZO LINEAS | M23022500091 | New_Event | Animals | Include | Include | Wildlife | 1004 | 2023-02-25 | 40160 | keep | 0 | Feb | 2023 | 0.027353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-02-25 16:53 | 2023-02-25 16:54 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO SE REPORTO CAUSA | P23022500142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 2113 | keep | 0 | Feb | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
HUMACAO | 2023-02-25 17:16 | 2023-02-25 19:09 | 50 | 1:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REEMPLAZO PORTAFUSIBLE QUEMADO | C23022500147 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2023-02-25 | 5650 | keep | 0 | Feb | 2023 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-02-25 17:21 | 2023-02-26 21:00 | 12 | 27:39 | P | CABLE SOTERRADO AVERIADO | SE INSTALO POSTE PROVISIONAL Y SE REMPLAZO TRANSFORMADOR SOTERRADO75KVA POR 75 KVA AEREO AVERIA NUEVA T-110 A T-111 | R23122500072 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1659 | 2023-02-25 | 19908 | keep | 0 | Feb | 2023 | 0.013559 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-25 17:39 | 2023-02-26 11:46 | 7 | 18:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZARON CONECTORES SULFATADOS | C23022500149 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1087 | 2023-02-25 | 7609 | keep | 0 | Feb | 2023 | 0.0051825 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-02-25 18:21 | 2023-02-26 11:18 | 7 | 16:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR Y SE RETIRO LINEA SECUNDARIA VACANTE OBSTRUYENDO | S23022500211 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1017 | 2023-02-25 | 7119 | keep | 0 | Feb | 2023 | 0.0048487 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-02-25 18:33 | 2023-02-25 19:12 | 10 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BARRAS EN PEDESTAL | C23022500152 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-02-25 | 390 | keep | 0 | Feb | 2023 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-02-25 18:41 | 2023-02-26 09:41 | 7 | 15:00 | P | DESGANCHE | 1 X 10 EN CORTE DE LINEA | C23022500153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 900 | 2023-02-25 | 6300 | keep | 0 | Feb | 2023 | 0.0042909 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-02-25 18:55 | 2023-02-26 12:00 | 150 | 17:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | M23022500113 | New_Event | Primary Wire Break | Include | Include | Equipment | 1025 | 2023-02-25 | 153750 | keep | 0 | Feb | 2023 | 0.10472 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2023-02-25 18:59 | 2023-02-25 22:01 | 9 | 3:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO SECUNDARIA | R23022500092 | New_Event | Secondary Wire Break | Include | Include | Equipment | 182 | 2023-02-25 | 1638 | keep | 0 | Feb | 2023 | 0.0011156 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-02-25 19:02 | 2023-02-26 08:31 | 100 | 13:29 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | R23022500093 | New_Event | Animals | Include | Include | Wildlife | 809 | 2023-02-25 | 80900 | keep | 0 | Feb | 2023 | 0.055101 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-02-25 19:45 | 2023-02-25 19:46 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23022500133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 4304 | keep | 0 | Feb | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
CAGUAS | 2023-02-25 19:54 | 2023-02-25 22:30 | 70 | 2:36 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23022500159 | New_Event | Animals | Include | Include | Wildlife | 156 | 2023-02-25 | 10920 | keep | 0 | Feb | 2023 | 0.0074376 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-02-25 21:38 | 2023-02-25 22:50 | 681 | 1:12 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR EN SERVICIO 60% | S23022500219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-02-25 | 49032 | keep | 0 | Feb | 2023 | 0.033395 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2023-02-25 21:57 | 2023-02-26 11:40 | 7 | 13:43 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN XMR REEMPLAZO PARARRAYO | S23022500227 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 823 | 2023-02-25 | 5761 | keep | 0 | Feb | 2023 | 0.0039238 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-02-25 22:07 | 2023-02-25 23:59 | 50 | 1:52 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23022500166 | New_Event | Animals | Include | Include | Wildlife | 112 | 2023-02-25 | 5600 | keep | 0 | Feb | 2023 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-02-25 22:07 | 2023-02-26 09:17 | 25 | 11:10 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CULEBRA CRUZO FASES | A23022500117 | New_Event | Animals | Include | Include | Wildlife | 670 | 2023-02-25 | 16750 | keep | 0 | Feb | 2023 | 0.011408 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-02-25 22:28 | 2023-02-25 22:29 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S2302250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-25 | 870 | keep | 0 | Feb | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2023-02-25 22:37 | 2023-02-26 14:30 | 10 | 15:53 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DE SU-2 @ T-2 - EN SERVICIO LOS 10 CLIENTES QUE FALABAN POR ENTRAR | B23022500334 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 953 | 2023-02-25 | 9530 | keep | 0 | Feb | 2023 | 0.0064908 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-25 22:50 | 2023-02-26 00:50 | 183 | 2:00 | P | DESGANCHE | SE DESPEJO ARBOL DE LA LINEA Y SE CERRO MACHETES 40% ADICIONAL EN SERVICIO 100% FEEDER EN SERVICIO | S23022500219 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-02-25 | 21960 | keep | 0 | Feb | 2023 | 0.014957 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-02-25 23:45 | 2023-02-26 01:30 | 60 | 1:45 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | B23022500419 | New_Event | Animals | Include | Include | Wildlife | 105 | 2023-02-25 | 6300 | keep | 0 | Feb | 2023 | 0.0042909 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-26 00:40 | 2023-02-26 00:43 | 59 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1117-09 LLEVA 25 % 1119-04 LLEVA 25 % DEL 1119-02 Y LLEVA 50% DEL 1115-02 SE CERRO POR CONTROL | S2302260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-26 | 177 | keep | 0 | Feb | 2023 | 0.00012055 | 4.0185e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 59
SAN JUAN | 2023-02-26 00:40 | 2023-02-26 00:43 | 316 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1117-09 LLEVA 25 % 1119-04 LLEVA 25 % DEL 1119-02 Y LLEVA 50% DEL 1115-02 SE CERRO POR CONTROL | S2302260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-26 | 948 | keep | 0 | Feb | 2023 | 0.00064568 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
SAN JUAN | 2023-02-26 00:40 | 2023-02-26 00:43 | 215 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1117-09 LLEVA 25 % 1119-04 LLEVA 25 % DEL 1119-02 Y LLEVA 50% DEL 1115-02 SE CERRO POR CONTROL | S2302260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-26 | 645 | keep | 0 | Feb | 2023 | 0.00043931 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-02-26 00:40 | 2023-02-26 00:43 | 680 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1117-09 LLEVA 25 % 1119-04 LLEVA 25 % DEL 1119-02 Y LLEVA 50% DEL 1115-02 SE CERRO POR CONTROL | S2302260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-26 | 2040 | keep | 0 | Feb | 2023 | 0.0013894 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
CANOVANAS | 2023-02-26 00:40 | 2023-02-26 10:23 | 100 | 9:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | R23022600003 | New_Event | Cutout Failure | Include | Include | Equipment | 583 | 2023-02-26 | 58300 | keep | 0 | Feb | 2023 | 0.039708 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-02-26 04:35 | 2023-02-26 04:36 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2302260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-26 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-02-26 04:36 | 2023-02-26 11:12 | 118 | 6:36 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 200 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA EN SU | C23022600002 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 396 | 2023-02-26 | 46728 | keep | 0 | Feb | 2023 | 0.031826 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
AGUADILLA | 2023-02-26 05:32 | 2023-02-26 09:31 | 20 | 3:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M23022600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 239 | 2023-02-26 | 4780 | keep | 0 | Feb | 2023 | 0.0032556 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-02-26 06:58 | 2023-02-26 06:59 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23022600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-26 | 3464 | keep | 0 | Feb | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
HUMACAO | 2023-02-26 07:17 | 2023-02-26 07:18 | 1593 | 0:01 | T | ANIMAL | RECIERRE | C2302260000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-02-26 | 1593 | keep | 0 | Feb | 2023 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2023-02-26 07:18 | 2023-02-26 11:59 | 89 | 4:41 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C23022600087 | 1st_after_momentary | Animals | Include | Include | Wildlife | 281 | 2023-02-26 | 25009 | keep | 0 | Feb | 2023 | 0.017034 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
HUMACAO | 2023-02-26 07:41 | 2023-02-26 08:53 | 3833 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600049 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2023-02-26 | 275976 | keep | 0 | Feb | 2023 | 0.18797 | 0.0026106 | Sustained | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2023-02-26 07:41 | 2023-02-26 08:53 | 181 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600049 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2023-02-26 | 13032 | keep | 0 | Feb | 2023 | 0.008876 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
HUMACAO | 2023-02-26 07:41 | 2023-02-26 08:53 | 2299 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600049 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2023-02-26 | 165528 | keep | 0 | Feb | 2023 | 0.11274 | 0.0015658 | Sustained | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2023-02-26 07:41 | 2023-02-26 08:53 | 776 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600049 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2023-02-26 | 55872 | keep | 0 | Feb | 2023 | 0.038054 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
HUMACAO | 2023-02-26 07:41 | 2023-02-26 07:44 | 519 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-02-26 | 1557 | keep | 0 | Feb | 2023 | 0.0010605 | 0.00035349 | Momentary | FALSE | FALSE | Not_TMED_Event | 519
HUMACAO | 2023-02-26 07:41 | 2023-02-26 07:44 | 1117 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-02-26 | 3351 | keep | 0 | Feb | 2023 | 0.0022824 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
HUMACAO | 2023-02-26 07:41 | 2023-02-26 07:44 | 4161 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-02-26 | 12483 | keep | 0 | Feb | 2023 | 0.0085021 | 0.002834 | Momentary | FALSE | FALSE | Not_TMED_Event | 4161
HUMACAO | 2023-02-26 07:41 | 2023-02-26 07:44 | 1891 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-02-26 | 5673 | keep | 0 | Feb | 2023 | 0.0038639 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2023-02-26 07:41 | 2023-02-26 07:44 | 1250 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-02-26 | 3750 | keep | 0 | Feb | 2023 | 0.0025541 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2023-02-26 07:41 | 2023-02-26 07:44 | 2141 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-02-26 | 6423 | keep | 0 | Feb | 2023 | 0.0043747 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2023-02-26 07:41 | 2023-02-26 07:44 | 1827 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO BANCO 115/38KV POR CAUSA DE LA LINEA 12,500 BUSHING AVERIADO EN BKR 12540 HUMACAO SECT. | C23022600054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-02-26 | 5481 | keep | 0 | Feb | 2023 | 0.0037331 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2023-02-26 07:45 | 2023-02-26 08:33 | 922 | 0:48 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1401-08 | S23022600011 | New_Event | Feeder Load Transferred | Include | Include | Other | 48 | 2023-02-26 | 44256 | keep | 0 | Feb | 2023 | 0.030143 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-02-26 07:45 | 2023-02-26 08:33 | 135 | 0:48 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 1401-08 LLEVA CARGA 1346-05 | S23022600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2023-02-26 | 6480 | keep | 0 | Feb | 2023 | 0.0044135 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
VEGA BAJA | 2023-02-26 08:02 | 2023-02-26 11:26 | 120 | 3:24 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | B23022600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2023-02-26 | 24480 | keep | 0 | Feb | 2023 | 0.016673 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
YAUCO | 2023-02-26 08:31 | 2023-02-26 10:58 | 80 | 2:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23022600017 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2023-02-26 | 11760 | keep | 0 | Feb | 2023 | 0.0080097 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-02-26 08:34 | 2023-02-26 11:40 | 23 | 3:06 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P23022600012 | New_Event | Animals | Include | Include | Wildlife | 186 | 2023-02-26 | 4278 | keep | 0 | Feb | 2023 | 0.0029137 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BARRANQUITAS | 2023-02-26 08:50 | 2023-02-26 11:17 | 25 | 2:27 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C23022600079 | New_Event | Animals | Include | Include | Wildlife | 147 | 2023-02-26 | 3675 | keep | 0 | Feb | 2023 | 0.002503 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-02-26 08:53 | 2023-02-26 12:29 | 130 | 3:36 | P | ANIMAL | 1 X 80 Y 1 X 50 EN CORTES DE LINEA CRUCE CON AVE | C23022600080 | New_Event | Animals | Include | Include | Wildlife | 216 | 2023-02-26 | 28080 | keep | 0 | Feb | 2023 | 0.019125 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
VEGA BAJA | 2023-02-26 08:54 | 2023-02-26 14:14 | 50 | 5:20 | P | CONDUCTOR ROTO O ABIERTO | 3 X 65 EN CL SE REPARO LINEA PRIMARIA | A23022600008 | New_Event | Primary Wire Break | Include | Include | Equipment | 320 | 2023-02-26 | 16000 | keep | 0 | Feb | 2023 | 0.010898 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-02-26 09:10 | 2023-02-26 12:45 | 81 | 3:35 | P | NO SE REPORTO CAUSA | SE REPUSO 3 X 80 SMU-20 EN MH 9 (BOVEDA) | S23022600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2023-02-26 | 17415 | keep | 0 | Feb | 2023 | 0.011861 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BARRANQUITAS | 2023-02-26 09:30 | 2023-02-26 13:05 | 6 | 3:35 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | VIA LIBRE XPRESS X2023-241 SE REEMPLAZO POSTE DETERIORADO PROYECTO FIONA | C23022600050 | New_Event | Primary Pole Failure | Include | Include | Equipment | 215 | 2023-02-26 | 1290 | keep | 0 | Feb | 2023 | 0.00087861 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-02-26 10:19 | 2023-02-26 10:21 | 172 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 1620-04 CERRADO POR CONTROL | S23022600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-26 | 344 | keep | 0 | Feb | 2023 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
YAUCO | 2023-02-26 10:27 | 2023-02-26 12:44 | 12 | 2:17 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE SECUNDARIO | M23022600043 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 137 | 2023-02-26 | 1644 | keep | 0 | Feb | 2023 | 0.0011197 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-02-26 11:07 | 2023-02-26 15:17 | 20 | 4:10 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR AVE | M23022600048 | New_Event | Animals | Include | Include | Wildlife | 250 | 2023-02-26 | 5000 | keep | 0 | Feb | 2023 | 0.0034055 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-26 11:18 | 2023-02-26 16:55 | 8 | 5:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 37.5 KVA AVERIADO Y SE REPARARON PUENTES PRIMARIOS Y SECUNDARIOS | S23022600047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 337 | 2023-02-26 | 2696 | keep | 0 | Feb | 2023 | 0.0018362 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-02-26 11:20 | 2023-02-26 11:21 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23022600019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-26 | 3000 | keep | 0 | Feb | 2023 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2023-02-26 11:21 | 2023-02-26 16:55 | 216 | 5:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE INSTALO BRAZO DE AISLACION | B23022600026 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 334 | 2023-02-26 | 72144 | keep | 0 | Feb | 2023 | 0.049137 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
SAN JUAN | 2023-02-26 11:24 | 2023-02-26 13:01 | 1 | 1:37 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE RETIRO CONDUCTOR SECUNDARIO HACIENDO CONTACTO CON BUSHING PRIMARIO | S23022600048 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 97 | 2023-02-26 | 97 | keep | 0 | Feb | 2023 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-26 11:24 | 2023-02-26 11:39 | 7 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA | B23022600020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-02-26 | 105 | keep | 0 | Feb | 2023 | 7.1515e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-02-26 11:53 | 2023-02-26 12:39 | 2 | 0:46 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN TRANSFORMADOR SE RETIRO TOMA PARTIDA EN EL PISO | R23022600034 | New_Event | Customer-Related Interruption | Include | Include | Public | 46 | 2023-02-26 | 92 | keep | 0 | Feb | 2023 | 6.2661e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-02-26 11:55 | 2023-02-26 12:21 | 2 | 0:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23022600055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 26 | 2023-02-26 | 52 | keep | 0 | Feb | 2023 | 3.5417e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-26 11:57 | 2023-02-26 12:31 | 8 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRA SECUNDARIA EN PEDESTAL TIPO MOLE | B23022600027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-02-26 | 272 | keep | 0 | Feb | 2023 | 0.00018526 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-26 12:12 | 2023-02-26 12:13 | 3597 | 0:01 | T | DESGANCHE | RECERRO | B23022600029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-02-26 | 3597 | keep | 0 | Feb | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-02-26 12:13 | 2023-02-26 14:59 | 35 | 2:46 | P | DESGANCHE | 1 X 40 EN C/L SE RETIRO RAMA | B23022600030 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-02-26 | 5810 | keep | 0 | Feb | 2023 | 0.0039572 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-02-26 12:29 | 2023-02-26 15:53 | 556 | 3:24 | P | DESGANCHE | 3 X 80 EN C/L Y 1 X 100 EN C/L SE REALIZO DESGANCHE Y SE LEVANTO CONDUCTOR PRIMARIO | C23022600105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-02-26 | 113424 | keep | 0 | Feb | 2023 | 0.077253 | 0.00037869 | Sustained | FALSE | FALSE | Not_TMED_Event | 556
SAN JUAN | 2023-02-26 12:45 | 2023-02-26 13:45 | 136 | 1:00 | P | NO SE REPORTO CAUSA | SE ABRIO DE SU-2 HACIA MH-9 (BOVEDA) PARA REEMPLAZARA 3 X 80 SMU-20 | S23022600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-02-26 | 8160 | keep | 0 | Feb | 2023 | 0.0055577 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
SAN JUAN | 2023-02-26 13:06 | 2023-02-26 16:16 | 8 | 3:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 37.5 KVA POR 25 KVA | S23022600057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 190 | 2023-02-26 | 1520 | keep | 0 | Feb | 2023 | 0.0010353 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-02-26 13:10 | 2023-02-26 14:30 | 10 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23022600038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-02-26 | 800 | keep | 0 | Feb | 2023 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-26 13:18 | 2023-02-26 16:16 | 100 | 2:58 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23022600061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2023-02-26 | 17800 | keep | 0 | Feb | 2023 | 0.012123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-02-26 13:29 | 2023-02-26 15:50 | 60 | 2:21 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23022600033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-02-26 | 8460 | keep | 0 | Feb | 2023 | 0.0057621 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-26 13:46 | 2023-02-26 13:49 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO X CONTROL | S2302260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-26 | 2610 | keep | 0 | Feb | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-02-26 14:14 | 2023-02-26 14:46 | 13 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REGULAR VOLTAJE DEL 1 AL 3 SE DEJO 125V/FASE Y SE REPARO EL NEUTRAL SECUNDARIO | C23022600144 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2023-02-26 | 416 | keep | 0 | Feb | 2023 | 0.00028334 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-02-26 14:18 | 2023-02-26 17:45 | 1 | 3:27 | P | DESGANCHE | 1 X 30 EN BANCO DE XMR DESGANCHE PRIMARIO | C23022600148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-02-26 | 207 | keep | 0 | Feb | 2023 | 0.00014099 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-26 14:20 | 2023-02-26 14:35 | 12 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZARON CONECTORES | M23022600062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-02-26 | 180 | keep | 0 | Feb | 2023 | 0.0001226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-26 14:21 | 2023-02-26 14:22 | 603 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO LLEVA 9206-09 | B2302260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-26 | 603 | keep | 0 | Feb | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-02-26 14:21 | 2023-02-26 14:22 | 6 | 0:01 | T | PROBLEMA DEL CLIENTE | RECERRO CARGA TRANSFERIDA AL 9206-08 PIZZA HUT CON PROBLEMA INTERNO | B2302260000X | New_Event | Customer-Related Interruption | Include | Include | Public | 1 | 2023-02-26 | 6 | keep | 0 | Feb | 2023 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-02-26 14:27 | 2023-02-26 14:28 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-26 | 2234 | keep | 0 | Feb | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-02-26 14:33 | 2023-02-26 14:34 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-26 | 3511 | keep | 0 | Feb | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
HUMACAO | 2023-02-26 14:45 | 2023-02-26 15:30 | 15 | 0:45 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR PARA REPARAR BUSHING SECUNDARIOS | C23022600129 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2023-02-26 | 675 | keep | 0 | Feb | 2023 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-02-26 14:57 | 2023-02-26 17:30 | 30 | 2:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M23022600068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-02-26 | 4590 | keep | 0 | Feb | 2023 | 0.0031262 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-26 15:26 | 2023-02-26 15:29 | 2720 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1115-01 LLEVANDO CARGA 1119-04 | S2302260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-26 | 8160 | keep | 0 | Feb | 2023 | 0.0055577 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
AGUADILLA | 2023-02-26 15:30 | 2023-02-26 16:50 | 6 | 1:20 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REMPLAZARAR BARRAS SECUNDARIAS | M23022600070 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 80 | 2023-02-26 | 480 | keep | 0 | Feb | 2023 | 0.00032693 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-02-26 16:12 | 2023-02-26 16:35 | 15 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REMPLAZAR CONEXIONES SECUNDARIAS | M23022600021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-02-26 | 345 | keep | 0 | Feb | 2023 | 0.00023498 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-02-26 16:27 | 2023-02-26 17:06 | 7 | 0:39 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR PARA REEMPLAZAR BAJANTES SECUNDARIOS | C23022600154 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 39 | 2023-02-26 | 273 | keep | 0 | Feb | 2023 | 0.00018594 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-02-26 16:57 | 2023-02-26 18:28 | 10 | 1:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA LEVANTAR LINEA SECUNDARIA | S23022600068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 91 | 2023-02-26 | 910 | keep | 0 | Feb | 2023 | 0.0006198 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-26 17:00 | 2023-02-26 21:22 | 25 | 4:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REPARAR SECUNDARIA | M23022600061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 262 | 2023-02-26 | 6550 | keep | 0 | Feb | 2023 | 0.0044612 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-02-26 17:17 | 2023-02-26 18:43 | 132 | 1:26 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | R23022600039 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-02-26 | 11352 | keep | 0 | Feb | 2023 | 0.0077318 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
MAYAGÃœEZ | 2023-02-26 17:22 | 2023-02-26 20:57 | 20 | 3:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | M23022600075 | New_Event | Primary Wire Break | Include | Include | Equipment | 215 | 2023-02-26 | 4300 | keep | 0 | Feb | 2023 | 0.0029287 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-26 17:34 | 2023-02-26 20:40 | 9 | 3:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S23022600086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2023-02-26 | 1674 | keep | 0 | Feb | 2023 | 0.0011402 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2023-02-26 18:14 | 2023-02-26 19:30 | 25 | 1:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CL PORTA FUSIBLE AVERIADO | A23022600045 | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2023-02-26 | 1900 | keep | 0 | Feb | 2023 | 0.0012941 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-02-26 19:08 | 2023-02-27 09:44 | 65 | 14:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M23022600082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 876 | 2023-02-26 | 56940 | keep | 0 | Feb | 2023 | 0.038782 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2023-02-26 19:24 | 2023-02-26 20:50 | 60 | 1:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CL SE REMPLAZO CAJA PRIMARIA | A23022600052 | New_Event | Cutout Failure | Include | Include | Equipment | 86 | 2023-02-26 | 5160 | keep | 0 | Feb | 2023 | 0.0035145 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-02-26 20:16 | 2023-02-27 10:56 | 20 | 14:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | M23022600090 | New_Event | Cutout Failure | Include | Include | Equipment | 880 | 2023-02-26 | 17600 | keep | 0 | Feb | 2023 | 0.011987 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-02-26 21:22 | 2023-02-27 02:34 | 30 | 5:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A23022600059 | New_Event | Primary Wire Break | Include | Include | Equipment | 312 | 2023-02-26 | 9360 | keep | 0 | Feb | 2023 | 0.0063751 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-02-26 22:08 | 2023-02-27 00:31 | 125 | 2:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23022600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2023-02-26 | 17875 | keep | 0 | Feb | 2023 | 0.012175 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-02-26 22:14 | 2023-02-26 22:16 | 4398 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S23022600102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-26 | 8796 | keep | 0 | Feb | 2023 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
GUAYAMA | 2023-02-26 22:46 | 2023-02-27 08:43 | 30 | 9:57 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P23022600054 | New_Event | Animals | Include | Include | Wildlife | 597 | 2023-02-26 | 17910 | keep | 0 | Feb | 2023 | 0.012198 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-02-26 22:55 | 2023-02-27 15:55 | 140 | 17:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE Y SE LEVANTARON LINEAS PRIMARIAS | C23022600065 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1020 | 2023-02-26 | 142800 | keep | 0 | Feb | 2023 | 0.09726 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
AGUADILLA | 2023-02-26 23:06 | 2023-02-27 01:15 | 100 | 2:09 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 140 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | M23022600106 | New_Event | Primary Pole Failure | Include | Include | Equipment | 129 | 2023-02-26 | 12900 | keep | 0 | Feb | 2023 | 0.0087861 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-02-27 00:35 | 2023-02-27 00:36 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2302270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-27 | 2354 | keep | 0 | Feb | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
CAGUAS | 2023-02-27 00:37 | 2023-02-27 00:39 | 1879 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA EL 3006-05 | C23022700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-27 | 3758 | keep | 0 | Feb | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-02-27 00:37 | 2023-02-27 00:39 | 3005 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 3006-02 SE CERRO POR CONTROL CARGA POR EL 3006-02 | C23022700002 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-02-27 | 6010 | keep | 0 | Feb | 2023 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
ARECIBO | 2023-02-27 01:07 | 2023-02-27 09:54 | 1 | 8:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN RISER REEMPLAZO DE CAJAS PRIMARIAS | A23022700001 | New_Event | Cutout Failure | Include | Include | Equipment | 527 | 2023-02-27 | 527 | keep | 0 | Feb | 2023 | 0.00035894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-02-27 01:15 | 2023-02-27 16:30 | 3 | 15:15 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO Y SE CERRO LOS PUENTES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | M23022700003 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 915 | 2023-02-27 | 2745 | keep | 0 | Feb | 2023 | 0.0018696 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-27 01:35 | 2023-02-27 10:19 | 112 | 8:44 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN C/L PARA CERRAR PUENTE PRIMARIO (RADIAL) | S23022700001 | New_Event | Primary Wire Break | Include | Include | Equipment | 524 | 2023-02-27 | 58688 | keep | 0 | Feb | 2023 | 0.039972 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
VEGA BAJA | 2023-02-27 02:23 | 2023-02-27 12:12 | 400 | 9:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REMPLAZO AISLADORES | B23022700006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 589 | 2023-02-27 | 235600 | keep | 0 | Feb | 2023 | 0.16047 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-02-27 02:49 | 2023-02-27 14:24 | 12 | 11:35 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR PARA REMPLAZAR XMR 25KVA X 25 KVA | B23022700013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 695 | 2023-02-27 | 8340 | keep | 0 | Feb | 2023 | 0.0056803 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-02-27 06:24 | 2023-02-27 06:25 | 464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23022700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-27 | 464 | keep | 0 | Feb | 2023 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
ARECIBO | 2023-02-27 06:33 | 2023-02-27 10:27 | 8 | 3:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | A23022700002 | New_Event | Primary Wire Break | Include | Include | Equipment | 234 | 2023-02-27 | 1872 | keep | 0 | Feb | 2023 | 0.001275 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-02-27 06:54 | 2023-02-27 09:26 | 1 | 2:32 | P | SOBRECARGA | 1 X 30 EN CORTE DE LINEA VERIFICADO EN BITACORA ES LA INFORMACION QUE SUMINISTRARON | M23022700006 | New_Event | Trip Due To Overload | Include | Include | Other | 152 | 2023-02-27 | 152 | keep | 0 | Feb | 2023 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-02-27 07:02 | 2023-02-27 13:28 | 8 | 6:26 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASES | M23022700007 | New_Event | Animals | Include | Include | Wildlife | 386 | 2023-02-27 | 3088 | keep | 0 | Feb | 2023 | 0.0021032 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-02-27 07:38 | 2023-02-27 13:05 | 22 | 5:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C23022700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 327 | 2023-02-27 | 7194 | keep | 0 | Feb | 2023 | 0.0048998 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
YAUCO | 2023-02-27 07:40 | 2023-02-27 09:32 | 1 | 1:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P23022700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-02-27 | 112 | keep | 0 | Feb | 2023 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-27 07:45 | 2023-02-27 09:33 | 50 | 1:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R23022700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-02-27 | 5400 | keep | 0 | Feb | 2023 | 0.0036779 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-02-27 08:09 | 2023-02-27 10:34 | 200 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23022700036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-02-27 | 29000 | keep | 0 | Feb | 2023 | 0.019752 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-02-27 08:35 | 2023-02-27 16:48 | 50 | 8:13 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23022700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2023-02-27 | 24650 | keep | 0 | Feb | 2023 | 0.016789 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-02-27 08:36 | 2023-02-27 12:19 | 2 | 3:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN RISER SE REMPLAZO PORTAFUSIBLE | S23022700013 | New_Event | Cutout Failure | Include | Include | Equipment | 223 | 2023-02-27 | 446 | keep | 0 | Feb | 2023 | 0.00030377 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-02-27 08:39 | 2023-02-27 08:44 | 1785 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 90% 1711-04 Y 10% 1717-01 SE VERIFICO PERSONAL DE SUBESTACIONES FUERA DEL AREA | B2302270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-02-27 | 8925 | keep | 0 | Feb | 2023 | 0.0060788 | 0.0012158 | Momentary | FALSE | FALSE | Not_TMED_Event | 1785
BAYAMON | 2023-02-27 08:39 | 2023-02-27 08:44 | 453 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 90% 1711-04 Y 10% 1717-01 SE VERIFICO PERSONAL DE SUBESTACIONES FUERA DEL AREA | B2302270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-02-27 | 2265 | keep | 0 | Feb | 2023 | 0.0015427 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-02-27 08:39 | 2023-02-27 08:44 | 186 | 0:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 90% 1711-04 Y 10% 1717-01 SE VERIFICO PERSONAL DE SUBESTACIONES FUERA DEL AREA | B2302270000X | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 5 | 2023-02-27 | 930 | keep | 0 | Feb | 2023 | 0.00063342 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2023-02-27 08:44 | 2023-02-27 11:27 | 25 | 2:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR SE CERRO PUENTE PRIMARIO Y 1 X 80 EN C/L | B23022700055 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 163 | 2023-02-27 | 4075 | keep | 0 | Feb | 2023 | 0.0027755 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-02-27 08:45 | 2023-02-27 10:22 | 1 | 1:37 | P | ANIMAL | 2 X 15 EN BANCO DE XMRS CRUCE POR AVE | C23022700022 | New_Event | Animals | Include | Include | Wildlife | 97 | 2023-02-27 | 97 | keep | 0 | Feb | 2023 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-27 09:03 | 2023-02-27 15:10 | 1 | 6:07 | P | ANIMAL | 2 X 20 EN BANCO DE XMR SE RETIRO AVE | R23022700010 | New_Event | Animals | Include | Include | Wildlife | 367 | 2023-02-27 | 367 | keep | 0 | Feb | 2023 | 0.00024996 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-02-27 09:13 | 2023-02-27 11:15 | 8 | 2:02 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA POR ANIMAL | P23022700026 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-02-27 | 976 | keep | 0 | Feb | 2023 | 0.00066475 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-02-27 10:04 | 2023-02-27 17:53 | 4 | 7:49 | P | ARBOL SOBRE LINEA | 1 X 40 EN CONVERTIDOR SE RETIRO ARBOL SOBRE LINEA | A23022700022 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 469 | 2023-02-27 | 1876 | keep | 0 | Feb | 2023 | 0.0012777 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-02-27 10:09 | 2023-02-27 11:30 | 12 | 1:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA CON ESCAPE DE ACEITE | M23022700031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 81 | 2023-02-27 | 972 | keep | 0 | Feb | 2023 | 0.00066202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-02-27 10:15 | 2023-02-27 11:58 | 8 | 1:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BARRAS DE PEDESTAL SECUNDARIO SULFATADA | C23022700036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 103 | 2023-02-27 | 824 | keep | 0 | Feb | 2023 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-02-27 10:16 | 2023-02-27 14:05 | 11 | 3:49 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA TRASLADAR LAS LINEAS SECUNDARIAS A POSTE NUEVO | B23022700074 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 229 | 2023-02-27 | 2519 | keep | 0 | Feb | 2023 | 0.0017157 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-02-27 10:27 | 2023-02-27 12:51 | 100 | 2:24 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23022700041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2023-02-27 | 14400 | keep | 0 | Feb | 2023 | 0.0098078 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-02-27 10:35 | 2023-02-27 11:15 | 15 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARA BARRA EN PEDESTAL SOTERRADO | A23022700026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-02-27 | 600 | keep | 0 | Feb | 2023 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-02-27 10:46 | 2023-02-27 12:18 | 45 | 1:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | M23022700036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 92 | 2023-02-27 | 4140 | keep | 0 | Feb | 2023 | 0.0028197 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-02-27 10:50 | 2023-02-27 14:40 | 30 | 3:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L TOTAL PARA REEMPLAZAR POSTE PRIMARIO | B23022700081 | New_Event | Primary Pole Failure | Include | Include | Equipment | 230 | 2023-02-27 | 6900 | keep | 0 | Feb | 2023 | 0.0046996 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-27 11:16 | 2023-02-27 13:53 | 10 | 2:37 | P | CAUSAS EXTERNAS | 1X20 EN XMR SE RETIRO RAMA DERRIBADA POR PERSONAL AJENO A LUMA DESGANCHANDO | S23022700054 | New_Event | Damage From Public | Include | Include | Public | 157 | 2023-02-27 | 1570 | keep | 0 | Feb | 2023 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-27 11:25 | 2023-02-27 13:28 | 38 | 2:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L, 1X65 EN OTRO C/L SE REMPLAZO CAJA PRIMARIA | S23022700061 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2023-02-27 | 4674 | keep | 0 | Feb | 2023 | 0.0031834 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
SAN JUAN | 2023-02-27 11:40 | 2023-02-27 14:34 | 27 | 2:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN RISER SE REEMPLAZO PORTAFUSIBLE | S23022700067 | New_Event | Cutout Failure | Include | Include | Equipment | 174 | 2023-02-27 | 4698 | keep | 0 | Feb | 2023 | 0.0031998 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
FAJARDO | 2023-02-27 11:45 | 2023-02-27 12:24 | 7 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR CONECTOR BAJANTE SECUNDARIO REF. R23022600038 | R23022700045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-02-27 | 273 | keep | 0 | Feb | 2023 | 0.00018594 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-02-27 12:08 | 2023-02-27 14:01 | 10 | 1:53 | P | OTRAS CAUSAS | 1 X 20 EN RISER POR FUSIBLE SULFATADO | A23022700045 | New_Event | Other Causes | Include | Include | Other | 113 | 2023-02-27 | 1130 | keep | 0 | Feb | 2023 | 0.00076964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-02-27 12:17 | 2023-02-27 15:01 | 100 | 2:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN DE AEREO PROVISIONAL @ T-72 SE REMPLAZO CAJA PRIMARIA | S23022700077 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2023-02-27 | 16400 | keep | 0 | Feb | 2023 | 0.01117 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-02-27 12:23 | 2023-02-27 15:11 | 3 | 2:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P23022700072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-02-27 | 504 | keep | 0 | Feb | 2023 | 0.00034327 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-02-27 12:29 | 2023-02-27 13:04 | 20 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022700080 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-02-27 | 700 | keep | 0 | Feb | 2023 | 0.00047677 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-02-27 12:30 | 2023-02-27 16:43 | 125 | 4:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO C/L PARA REEMPLAZO 2 ASILADORES, 2 PIN Y 2 LIGADURAS | C2302270007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 253 | 2023-02-27 | 31625 | keep | 0 | Feb | 2023 | 0.02154 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-02-27 12:38 | 2023-02-27 15:32 | 12 | 2:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA AVERIADA | B23022700087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 174 | 2023-02-27 | 2088 | keep | 0 | Feb | 2023 | 0.0014221 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-02-27 12:42 | 2023-02-27 14:23 | 7 | 1:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONECTORES Y BAJANTE SECUNDARIO | C23022700049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 101 | 2023-02-27 | 707 | keep | 0 | Feb | 2023 | 0.00048153 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-02-27 12:50 | 2023-02-27 14:00 | 25 | 1:10 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | R23022700041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-02-27 | 1750 | keep | 0 | Feb | 2023 | 0.0011919 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-02-27 13:00 | 2023-02-27 17:13 | 100 | 4:13 | P | ARBOL SOBRE LINEA | 1 X 100 EN CORTE DE LINEA POR ARBOL SOBRE LINEA | A23022700068 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 253 | 2023-02-27 | 25300 | keep | 0 | Feb | 2023 | 0.017232 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-02-27 13:05 | 2023-02-27 13:30 | 25 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO LINEA SECUNDARIA | M23022600061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-02-27 | 625 | keep | 0 | Feb | 2023 | 0.00042568 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-02-27 13:21 | 2023-02-27 15:00 | 15 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23022700072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2023-02-27 | 1485 | keep | 0 | Feb | 2023 | 0.0010114 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-02-27 13:27 | 2023-02-27 16:03 | 2 | 2:36 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23022700081 | New_Event | Animals | Include | Include | Wildlife | 156 | 2023-02-27 | 312 | keep | 0 | Feb | 2023 | 0.0002125 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2023-02-27 13:48 | 2023-02-27 16:10 | 6 | 2:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR PARA REPARAR CONEXIONES | A23022700082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 142 | 2023-02-27 | 852 | keep | 0 | Feb | 2023 | 0.00058029 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-02-27 13:54 | 2023-02-27 18:34 | 10 | 4:40 | P | PROBLEMA DEL CLIENTE | 1SMU20X80 DEL MH-9 @ MH-9A POR CONTAMINACION EN FACILIDADES PRIVADAS SE ORIENTO A CLIENTE EN EL LUGAR | S23022700094 | New_Event | Customer-Related Interruption | Include | Include | Public | 280 | 2023-02-27 | 2800 | keep | 0 | Feb | 2023 | 0.0019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-02-27 14:03 | 2023-02-27 16:36 | 9 | 2:33 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN C/L SE REEMPLAZO PARARRAYO AVERIADO | C23022700084 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 153 | 2023-02-27 | 1377 | keep | 0 | Feb | 2023 | 0.00093787 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-02-27 14:07 | 2023-02-27 15:34 | 5 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR CONECTORES EN BAJANTES SECUNDARIO | C23022700085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2023-02-27 | 435 | keep | 0 | Feb | 2023 | 0.00029628 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-02-27 14:11 | 2023-02-27 15:55 | 50 | 1:44 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23022700079 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-02-27 | 5200 | keep | 0 | Feb | 2023 | 0.0035417 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-02-27 14:29 | 2023-02-27 15:25 | 5 | 0:56 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | C23022700087 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 56 | 2023-02-27 | 280 | keep | 0 | Feb | 2023 | 0.00019071 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-02-27 14:35 | 2023-02-27 21:00 | 38 | 6:25 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO | M23022700098 | New_Event | Primary Pole Failure | Include | Include | Equipment | 385 | 2023-02-27 | 14630 | keep | 0 | Feb | 2023 | 0.0099644 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
FAJARDO | 2023-02-27 14:54 | 2023-02-28 01:13 | 15 | 10:19 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN C/L SE CONSTRUYO AEREO PROVICIONAL | R23022700054 | New_Event | UG Cable Fault | Include | Include | Equipment | 619 | 2023-02-27 | 9285 | keep | 0 | Feb | 2023 | 0.006324 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-02-27 15:17 | 2023-02-27 17:45 | 40 | 2:28 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | A23022700099 | New_Event | Animals | Include | Include | Wildlife | 148 | 2023-02-27 | 5920 | keep | 0 | Feb | 2023 | 0.0040321 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-02-27 15:23 | 2023-02-27 22:08 | 10 | 6:45 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | B23022700125 | New_Event | Animals | Include | Include | Wildlife | 405 | 2023-02-27 | 4050 | keep | 0 | Feb | 2023 | 0.0027584 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-02-27 15:36 | 2023-02-27 16:15 | 20 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR Y SECUNDARIA | P23022700113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-02-27 | 780 | keep | 0 | Feb | 2023 | 0.00053125 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-27 15:41 | 2023-02-27 19:49 | 50 | 4:08 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23022700105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-02-27 | 12400 | keep | 0 | Feb | 2023 | 0.0084456 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-02-27 15:52 | 2023-02-27 17:17 | 10 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BARRA EN PEDESTAL | C23022700098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2023-02-27 | 850 | keep | 0 | Feb | 2023 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-02-27 15:53 | 2023-02-27 15:55 | 125 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2302270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-02-27 | 250 | keep | 0 | Feb | 2023 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-02-27 15:54 | 2023-02-27 17:15 | 31 | 1:21 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23022700099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-02-27 | 2511 | keep | 0 | Feb | 2023 | 0.0017102 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CANOVANAS | 2023-02-27 16:35 | 2023-02-27 17:00 | 10 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | R23022700058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-02-27 | 250 | keep | 0 | Feb | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-02-27 16:38 | 2023-02-27 19:29 | 20 | 2:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A23022700104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-02-27 | 3420 | keep | 0 | Feb | 2023 | 0.0023293 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-02-27 16:41 | 2023-02-27 19:51 | 4 | 3:10 | P | NO SE REPORTO CAUSA | 1X20 EN XMR | S23022700112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2023-02-27 | 760 | keep | 0 | Feb | 2023 | 0.00051763 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-02-27 16:50 | 2023-02-27 22:00 | 80 | 5:10 | P | EMPALME SOTERRADO AVERIADO | SE SECCIONALIZO TRAMO SOTERRADO Y SE DEJO ENERGIZADO DEL SU-5 AL T-21 QUEDARON 5 TRANSFORMADORES FUERA DE SERVICIO | S23022700116 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 310 | 2023-02-27 | 24800 | keep | 0 | Feb | 2023 | 0.016891 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-02-27 17:05 | 2023-02-27 18:40 | 80 | 1:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A23022700109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-02-27 | 7600 | keep | 0 | Feb | 2023 | 0.0051763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-27 17:19 | 2023-02-27 19:13 | 8 | 1:54 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR PARA CERAR PUENTE DE CAJA A XMR | B23022700140 | New_Event | Primary Wire Break | Include | Include | Equipment | 114 | 2023-02-27 | 912 | keep | 0 | Feb | 2023 | 0.00062116 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-02-27 17:48 | 2023-02-28 11:10 | 1 | 17:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE CORTE DE LINEA | A23022700112 | New_Event | Primary Wire Break | Include | Include | Equipment | 1042 | 2023-02-27 | 1042 | keep | 0 | Feb | 2023 | 0.0007097 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-27 17:50 | 2023-02-27 19:00 | 40 | 1:10 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | R23022700061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-02-27 | 2800 | keep | 0 | Feb | 2023 | 0.0019071 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-02-27 18:48 | 2023-02-27 20:20 | 527 | 1:32 | T | CAUSAS EXTERNAS | SE ABRE MACHETES Y SE COLOCA TAG FID 10050394 PARA SECCIONALIZAR AVERIA DE POSTE PARTIDO POR ACCIDENTE DE AUTO SE CREA EVENTO P23022700210 | P23022700165 | New_Event | Damage From Public | Include | Include | Public | 92 | 2023-02-27 | 48484 | keep | 0 | Feb | 2023 | 0.033022 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2023-02-27 19:03 | 2023-02-27 20:19 | 100 | 1:16 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P23022700172 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-02-27 | 7600 | keep | 0 | Feb | 2023 | 0.0051763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-02-27 19:06 | 2023-02-27 21:50 | 257 | 2:44 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23022700144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-02-27 | 42148 | keep | 0 | Feb | 2023 | 0.028707 | 0.00017504 | Sustained | FALSE | FALSE | Not_TMED_Event | 257
ARECIBO | 2023-02-27 19:18 | 2023-02-28 10:00 | 14 | 14:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A23022700117 | New_Event | Cutout Failure | Include | Include | Equipment | 882 | 2023-02-27 | 12348 | keep | 0 | Feb | 2023 | 0.0084102 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2023-02-27 20:02 | 2023-02-27 22:20 | 200 | 2:18 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | P23022700197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-02-27 | 27600 | keep | 0 | Feb | 2023 | 0.018798 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2023-02-27 20:20 | 2023-02-27 23:48 | 128 | 3:28 | P | CAUSAS EXTERNAS | SE REMPLAZO POSTE PRIMARIO PARTIDO POR IMPACTO DE VEHICULO DE MOTOR Y SE CERRARON LOS MACHETES | P23022700210 | Partial_restoration | Damage From Public | Include | Include | Public | 208 | 2023-02-27 | 26624 | keep | 0 | Feb | 2023 | 0.018133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-27 20:23 | 2023-02-27 21:34 | 12 | 1:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S23022700151 | New_Event | Secondary Wire Break | Include | Include | Equipment | 71 | 2023-02-27 | 852 | keep | 0 | Feb | 2023 | 0.00058029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-02-27 20:36 | 2023-02-28 11:00 | 8 | 14:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23022700109 | New_Event | Primary Wire Break | Include | Include | Equipment | 864 | 2023-02-27 | 6912 | keep | 0 | Feb | 2023 | 0.0047077 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-02-27 20:38 | 2023-02-27 22:58 | 463 | 2:20 | P | SOBRECARGA | 1 X 100 EN C/L CIRCUITO SOBRE CARGADO POR TRANSFERENCIAS | C23022700133 | New_Event | Trip Due To Overload | Include | Include | Other | 140 | 2023-02-27 | 64820 | keep | 0 | Feb | 2023 | 0.044149 | 0.00031535 | Sustained | FALSE | FALSE | Not_TMED_Event | 463
SAN JUAN | 2023-02-27 21:23 | 2023-02-27 21:26 | 1191 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23022700163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-27 | 3573 | keep | 0 | Feb | 2023 | 0.0024336 | 0.00081118 | Momentary | FALSE | FALSE | Not_TMED_Event | 1191
SAN JUAN | 2023-02-27 21:23 | 2023-02-27 21:26 | 60 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1420-02 LLEVA 10% DE LA CARGA DEL 1420-03 SE CERRO POR CONTROL | S23022700162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-27 | 180 | keep | 0 | Feb | 2023 | 0.0001226 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-02-27 21:23 | 2023-02-27 21:26 | 546 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1420-02 LLEVA 10% DE LA CARGA DEL 1420-03 SE CERRO POR CONTROL | S23022700162 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-02-27 | 1638 | keep | 0 | Feb | 2023 | 0.0011156 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
AGUADILLA | 2023-02-27 21:23 | 2023-02-28 10:30 | 15 | 13:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO PORTA FUSIBLE EN CL | M23022700115 | New_Event | Cutout Failure | Include | Include | Equipment | 787 | 2023-02-27 | 11805 | keep | 0 | Feb | 2023 | 0.0080403 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-27 21:53 | 2023-02-28 02:49 | 30 | 4:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO DE TRANSFORMADOR Y SE REPARO SECUNDARIA | S23022700167 | New_Event | Secondary Wire Break | Include | Include | Equipment | 296 | 2023-02-27 | 8880 | keep | 0 | Feb | 2023 | 0.0060481 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-02-27 22:00 | 2023-02-28 10:00 | 46 | 12:00 | P | EMPALME SOTERRADO AVERIADO | TRAMO SOTERRADO AVERIADO | S23022700116 | Partial_restoration | UG Cable Splice Failure | Include | Include | Equipment | 720 | 2023-02-27 | 33120 | keep | 0 | Feb | 2023 | 0.022558 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-02-27 23:23 | 2023-02-28 07:08 | 14 | 7:45 | P | ANIMAL | 1 X 10 EN XMR AVE | C23022700155 | New_Event | Animals | Include | Include | Wildlife | 465 | 2023-02-27 | 6510 | keep | 0 | Feb | 2023 | 0.0044339 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2023-02-27 23:48 | 2023-02-28 04:26 | 100 | 4:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 Y 1 X 100 EN C/L SE REMPLAZO AISLADOR | B23022700167 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 278 | 2023-02-27 | 27800 | keep | 0 | Feb | 2023 | 0.018934 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-02-28 00:01 | 2023-02-28 00:04 | 1 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S23022800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-02-28 | 3 | keep | 0 | Feb | 2023 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-28 01:16 | 2023-02-28 04:01 | 8 | 2:45 | P | NO SE REPORTO CAUSA | 2 X 200 EN CORTE DE LINEA PRINCIPAL | S23022800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2023-02-28 | 1320 | keep | 0 | Feb | 2023 | 0.00089905 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-02-28 02:05 | 2023-02-28 08:45 | 60 | 6:40 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA PARACAIDAS CRUZANDO LINEAS | A23022800002 | New_Event | Damage From Public | Include | Include | Public | 400 | 2023-02-28 | 24000 | keep | 0 | Feb | 2023 | 0.016346 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-02-28 03:43 | 2023-02-28 12:35 | 5 | 8:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23022800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 532 | 2023-02-28 | 2660 | keep | 0 | Feb | 2023 | 0.0018117 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-02-28 04:01 | 2023-02-28 10:00 | 15 | 5:59 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | S23022800003 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 359 | 2023-02-28 | 5385 | keep | 0 | Feb | 2023 | 0.0036677 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-02-28 04:42 | 2023-02-28 06:59 | 100 | 2:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P23022800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-02-28 | 13700 | keep | 0 | Feb | 2023 | 0.009331 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-02-28 05:18 | 2023-02-28 05:19 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23022800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-28 | 3464 | keep | 0 | Feb | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
VEGA BAJA | 2023-02-28 05:39 | 2023-02-28 10:30 | 50 | 4:51 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA SE RETIRO RANA CRUZANDO FASE A TIERRA | A23022800006 | New_Event | Animals | Include | Include | Wildlife | 291 | 2023-02-28 | 14550 | keep | 0 | Feb | 2023 | 0.0099099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-02-28 06:22 | 2023-02-28 15:15 | 22 | 8:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23022800005 | New_Event | Secondary Wire Break | Include | Include | Equipment | 533 | 2023-02-28 | 11726 | keep | 0 | Feb | 2023 | 0.0079865 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
VEGA BAJA | 2023-02-28 07:27 | 2023-02-28 13:15 | 1 | 5:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SECUNDARIA AVERIADA | A23022800012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 348 | 2023-02-28 | 348 | keep | 0 | Feb | 2023 | 0.00023702 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-28 07:30 | 2023-02-28 12:37 | 15 | 5:07 | P | DESGANCHE | 1X50 EN C/L Y DESGANCHE | R23022800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2023-02-28 | 4605 | keep | 0 | Feb | 2023 | 0.0031364 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-02-28 07:34 | 2023-02-28 07:35 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23022800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-28 | 179 | keep | 0 | Feb | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2023-02-28 07:41 | 2023-02-28 07:42 | 4664 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23022800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-28 | 4664 | keep | 0 | Feb | 2023 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
BAYAMON | 2023-02-28 07:56 | 2023-02-28 11:48 | 12 | 3:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X25 EN C/L SE REMPLAZO AISLADOR PRIMARIO PARTIDO | B23022800010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 232 | 2023-02-28 | 2784 | keep | 0 | Feb | 2023 | 0.0018962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-28 08:02 | 2023-02-28 08:03 | 726 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1346-04 SE CERRO POR SCADA | S2302280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-28 | 726 | keep | 0 | Feb | 2023 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-02-28 08:02 | 2023-02-28 08:03 | 3932 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CARGA POR EL 1303-03 SE CERRO POR SCADA | S2302280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-02-28 | 3932 | keep | 0 | Feb | 2023 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 1225 | 0:36 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO LLEVA 75% 1203-03 | S23022800029 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 44100 | keep | 0 | Feb | 2023 | 0.030036 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 1452 | 0:36 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO | S23022800029 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 52272 | keep | 0 | Feb | 2023 | 0.035602 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 462 | 0:36 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO 75% POR EL 1203-01 Y 25% POR EL 1342-04 | S23022800029 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 16632 | keep | 0 | Feb | 2023 | 0.011328 | 0.00031467 | Sustained | FALSE | FALSE | Not_TMED_Event | 462
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 12:33 | 718 | 4:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO SE REALIZARON OPERACIONES EN EL CAMPO Y SE REALIZO AMARRE CON EL 1330-05 X 1525-03 SJ-230228-01 | S23022800024 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 245 | 2023-02-28 | 175910 | keep | 0 | Feb | 2023 | 0.11981 | 0.00048903 | Sustained | FALSE | FALSE | Not_TMED_Event | 718
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 11:07 | 533 | 2:39 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO SE REALIZARON OPERACIONES EN EL CAMPO Y SE REALIZO AMARRE CON EL 1345-04 SJ-230228-01 | S23022800024 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 159 | 2023-02-28 | 84747 | keep | 0 | Feb | 2023 | 0.057721 | 0.00036302 | Sustained | FALSE | FALSE | Not_TMED_Event | 533
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 11:02 | 844 | 2:34 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO SE REALIZARON OPERACIONES EN EL CAMPO Y SE REALIZO AMARRE CON EL 1345-02 SJ-230228-01 LLEVA 35% DE LA CARGA DEL 1345-05 | S23022800024 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 154 | 2023-02-28 | 129976 | keep | 0 | Feb | 2023 | 0.088526 | 0.00057484 | Sustained | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 790 | 0:36 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO SU CARGA POR EL 1345-03 | S23022800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 28440 | keep | 0 | Feb | 2023 | 0.01937 | 0.00053807 | Sustained | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 312 | 0:36 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO 80% DE SU CARGA POR EL 1345-02 | S23022800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 11232 | keep | 0 | Feb | 2023 | 0.0076501 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 660 | 0:36 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO | S23022800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 23760 | keep | 0 | Feb | 2023 | 0.016183 | 0.00044952 | Sustained | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 435 | 0:36 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO LLEVA 80% DEL 1342-04 | S23022800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 15660 | keep | 0 | Feb | 2023 | 0.010666 | 0.00029628 | Sustained | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 259 | 0:36 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO LLEVA LA CARGA DEL 1342-02 | S23022800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 9324 | keep | 0 | Feb | 2023 | 0.0063505 | 0.0001764 | Sustained | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 686 | 0:36 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO | S23022800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 24696 | keep | 0 | Feb | 2023 | 0.01682 | 0.00046723 | Sustained | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2023-02-28 08:28 | 2023-02-28 09:04 | 619 | 0:36 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO 35% DE SU CARGA POR EL 1330-04 | S23022800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 36 | 2023-02-28 | 22284 | keep | 0 | Feb | 2023 | 0.015178 | 0.0004216 | Sustained | FALSE | FALSE | Not_TMED_Event | 619
BAYAMON | 2023-02-28 08:28 | 2023-02-28 12:33 | 558 | 4:05 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE MONACILLO SE REALIZARON OPERACIONES EN EL CAMPO Y SE REALIZO AMARRE CON EL 1330-05 X 1525-03 SJ-230228-01 LLEVA 90% DE LA CARGA DEL 1901-05 SU CARGA POR 1525-03 | S23022800024 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 245 | 2023-02-28 | 136710 | keep | 0 | Feb | 2023 | 0.093113 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
GUAYAMA | 2023-02-28 08:29 | 2023-02-28 11:38 | 12 | 3:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONCTORES EN SECUNDARIA EN VARIOS PUNTOS | P23022800025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 189 | 2023-02-28 | 2268 | keep | 0 | Feb | 2023 | 0.0015447 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-02-28 08:53 | 2023-02-28 10:37 | 12 | 1:44 | P | PROBLEMA DEL CLIENTE | SE RECONECTO CLIENTES QUE HABIAN SIDO DESCONECTADOS POR TOMA AVERIADA | P23022800031 | New_Event | Customer-Related Interruption | Include | Include | Public | 104 | 2023-02-28 | 1248 | keep | 0 | Feb | 2023 | 0.00085001 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-02-28 09:06 | 2023-02-28 13:00 | 15 | 3:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23022800086 | New_Event | Secondary Wire Break | Include | Include | Equipment | 234 | 2023-02-28 | 3510 | keep | 0 | Feb | 2023 | 0.0023906 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-02-28 09:22 | 2023-02-28 10:42 | 13 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R23022800042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-02-28 | 1040 | keep | 0 | Feb | 2023 | 0.00070834 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2023-02-28 09:30 | 2023-02-28 11:29 | 1 | 1:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REMPLAZO PORTAFUSIBLE AVERIADO | A23022800028 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2023-02-28 | 119 | keep | 0 | Feb | 2023 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-02-28 09:31 | 2023-02-28 10:50 | 35 | 1:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | C23022800023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2023-02-28 | 2765 | keep | 0 | Feb | 2023 | 0.0018832 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2023-02-28 09:33 | 2023-02-28 11:50 | 1 | 2:17 | P | PROBLEMA DEL CLIENTE | SE DEJO ABIERTO RISER POR PROBLEMA INTERNO | P23022800036 | New_Event | Customer-Related Interruption | Include | Include | Public | 137 | 2023-02-28 | 137 | keep | 0 | Feb | 2023 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-28 09:36 | 2023-02-28 14:40 | 9 | 5:04 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE | B23022800021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 304 | 2023-02-28 | 2736 | keep | 0 | Feb | 2023 | 0.0018635 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-02-28 09:48 | 2023-02-28 12:05 | 1 | 2:17 | P | NO SE REPORTO CAUSA | 1 X 25 SMU 20 EN GABINETE | C23022800048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2023-02-28 | 137 | keep | 0 | Feb | 2023 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-28 10:00 | 2023-02-28 16:46 | 183 | 6:46 | P | EMPALME SOTERRADO AVERIADO | SE ABRIO C/L EN FID 31426849 PARA REEMPLAZO EMPALME SOTERRADO EN TRAMO RADIAL | S23022700116 | Additional_clients | UG Cable Splice Failure | Include | Include | Equipment | 406 | 2023-02-28 | 74298 | keep | 0 | Feb | 2023 | 0.050604 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-02-28 10:10 | 2023-02-28 10:16 | 1210 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LUEGO DE CORROBORAR PERSONAL FUERA DE LAS LINEAS | B23022800027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-02-28 | 7260 | keep | 0 | Feb | 2023 | 0.0049448 | 0.00082413 | Sustained | FALSE | FALSE | Not_TMED_Event | 1210
BAYAMON | 2023-02-28 10:14 | 2023-02-28 12:06 | 40 | 1:52 | P | NO SE REPORTO CAUSA | 1X100 EN C/L 1X80 EN OTRO C/L | B23022800028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2023-02-28 | 4480 | keep | 0 | Feb | 2023 | 0.0030513 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-02-28 10:20 | 2023-02-28 11:54 | 1 | 1:34 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 25KVA X 37.5KVA | B23022800029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 94 | 2023-02-28 | 94 | keep | 0 | Feb | 2023 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-28 10:35 | 2023-02-28 12:59 | 4 | 2:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIO Y POSTE SECUNDARIO | S23022800129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 144 | 2023-02-28 | 576 | keep | 0 | Feb | 2023 | 0.00039231 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-02-28 10:39 | 2023-02-28 12:46 | 1 | 2:07 | P | ANIMAL | 1X50 EN C/L 1X40 EN RISER CRUCE POR AVE | B23022800035 | New_Event | Animals | Include | Include | Wildlife | 127 | 2023-02-28 | 127 | keep | 0 | Feb | 2023 | 8.6499e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-02-28 10:58 | 2023-02-28 15:44 | 80 | 4:46 | P | DESGANCHE | 1 X 0 EN C/L Y 1 X 65 SE REALIZO DESGANCHE | S23022800144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2023-02-28 | 22880 | keep | 0 | Feb | 2023 | 0.015583 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-28 10:59 | 2023-02-28 11:11 | 13 | 0:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES SECUNDARIOS QUEMADOS | B23022800038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 12 | 2023-02-28 | 156 | keep | 0 | Feb | 2023 | 0.00010625 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-02-28 11:02 | 2023-02-28 15:10 | 30 | 4:08 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA MAQUINA CRUZO LINEAS | A23022800048 | New_Event | Damage From Public | Include | Include | Public | 248 | 2023-02-28 | 7440 | keep | 0 | Feb | 2023 | 0.0050674 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-02-28 11:17 | 2023-02-28 13:00 | 1 | 1:43 | P | CAUSAS EXTERNAS | SE REMPLAZO 2 X 25 EN C/L DIGGER LE DIO UN GOLPE AL POSTE Y CRUZO LA FASE | R23022800033 | New_Event | Damage From Public | Include | Include | Public | 103 | 2023-02-28 | 103 | keep | 0 | Feb | 2023 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-28 11:18 | 2023-02-28 13:07 | 4085 | 1:49 | T | ALIMENTADOR AMARRADO | LLEVANDO PARTE DE LA CARGA 2404-06 AVERIA SOTERRADA DEL 2404-06 | R23022800035 | New_Event | Feeder Load Transferred | Include | Include | Other | 109 | 2023-02-28 | 445265 | keep | 0 | Feb | 2023 | 0.30327 | 0.0027823 | Sustained | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-02-28 11:18 | 2023-02-28 13:07 | 1905 | 1:49 | P | CABLE SOTERRADO AVERIADO | 25% DE LA CARGA X 2402-03 SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA SOTERRADA ENTRANDO UN 10% DEL 25% AFECTADO | R23022800035 | New_Event | UG Cable Fault | Include | Include | Equipment | 109 | 2023-02-28 | 207645 | keep | 0 | Feb | 2023 | 0.14143 | 0.0012975 | Sustained | FALSE | FALSE | Not_TMED_Event | 1905
ARECIBO | 2023-02-28 11:30 | 2023-02-28 11:50 | 19 | 0:20 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL PRIMARIO AVERIADO | A23022800053 | New_Event | Primary Wire Break | Include | Include | Equipment | 20 | 2023-02-28 | 380 | keep | 0 | Feb | 2023 | 0.00025882 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-02-28 11:36 | 2023-02-28 12:16 | 100 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO MEDIANTE GOI BY-230228-01 SE TRABAJO CON EVENTO DE SITUACION PELIGROSA | B23022600072 | New_Event | Primary Wire Break | Include | Include | Equipment | 40 | 2023-02-28 | 4000 | keep | 0 | Feb | 2023 | 0.0027244 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-02-28 11:55 | 2023-02-28 12:10 | 10 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23022800058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-02-28 | 150 | keep | 0 | Feb | 2023 | 0.00010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-02-28 12:01 | 2023-02-28 12:03 | 3699 | 0:02 | T | CABLE SOTERRADO AVERIADO | DISPARO DEL 2402-04 LLEVANDO LA CARGA 2404-07 PERSONAL TRANSFIRIENDOLE CARGA DEL 2402-03 EL CUAL ESTA LLEVANDO LA CARGA DEL 2404-06 CON AVERIA SOTERADA | R2302280000X | New_Event | UG Cable Fault | Include | Include | Equipment | 2 | 2023-02-28 | 7398 | keep | 0 | Feb | 2023 | 0.0050387 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
SAN JUAN | 2023-02-28 12:10 | 2023-02-28 14:56 | 26 | 2:46 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REPARO BUSHIN PRIMARIO XMR | S23022800165 | New_Event | Service Transformer Failure | Include | Include | Equipment | 166 | 2023-02-28 | 4316 | keep | 0 | Feb | 2023 | 0.0029396 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
HUMACAO | 2023-02-28 12:12 | 2023-02-28 13:06 | 25 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN TRANSFORMADOR Y SE REMPLAZO BARRAS EN PEDESTAL | C23022800047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2023-02-28 | 1350 | keep | 0 | Feb | 2023 | 0.00091948 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-28 12:36 | 2023-02-28 15:00 | 213 | 2:24 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L SE REMPLAZO PARARAYO | B23022800050 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 144 | 2023-02-28 | 30672 | keep | 0 | Feb | 2023 | 0.020891 | 0.00014507 | Sustained | FALSE | FALSE | Not_TMED_Event | 213
UTUADO | 2023-02-28 12:44 | 2023-02-28 15:35 | 4 | 2:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23022800069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-02-28 | 684 | keep | 0 | Feb | 2023 | 0.00046587 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-02-28 13:07 | 2023-02-28 13:25 | 286 | 0:18 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA SOTERRADA Y SE TRANSFIRIO RESTANTE AL 1646-03 CARR 3 INT CARR 874 | R23022800035 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 18 | 2023-02-28 | 5148 | keep | 0 | Feb | 2023 | 0.0035063 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-02-28 13:38 | 2023-02-28 15:55 | 7 | 2:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO LINEA SECUNDARIA | S23022800187 | New_Event | Secondary Wire Break | Include | Include | Equipment | 137 | 2023-02-28 | 959 | keep | 0 | Feb | 2023 | 0.00065317 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-02-28 13:40 | 2023-02-28 14:35 | 10 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23022800055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-02-28 | 550 | keep | 0 | Feb | 2023 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-02-28 14:07 | 2023-02-28 19:31 | 15 | 5:24 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23022800062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 324 | 2023-02-28 | 4860 | keep | 0 | Feb | 2023 | 0.0033101 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-02-28 14:14 | 2023-02-28 16:55 | 200 | 2:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | M23022800066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-02-28 | 32200 | keep | 0 | Feb | 2023 | 0.021931 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-02-28 14:23 | 2023-02-28 14:25 | 2610 | 0:02 | T | PARARRAYOS DEFECTUOSO | DISPARO Y SE CERRO POR CONTROL | B23022800060 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2023-02-28 | 5220 | keep | 0 | Feb | 2023 | 0.0035553 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
ARECIBO | 2023-02-28 14:30 | 2023-02-28 15:00 | 25 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARA CONEXIONES EN BAJANTES SECUNDARIOS | A23022800086 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-02-28 | 750 | keep | 0 | Feb | 2023 | 0.00051082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-02-28 14:44 | 2023-03-01 15:09 | 15 | 24:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 75KVA AVERIADO | B23022800063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1465 | 2023-02-28 | 21975 | keep | 0 | Feb | 2023 | 0.014967 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-02-28 15:05 | 2023-02-28 17:41 | 718 | 2:36 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR PARA REALIZAR OPERACIONES PARA SECCIONALIZAR Y REALIZAR PRUEBA DE CONTACTO AL#5 DE LA SUBESTACION 1330-00 SJ-230228-01 LLEVA 90% DEL 1901-05 | S23022800024 | New_Event | Switch Failure | Include | Include | Equipment | 156 | 2023-02-28 | 112008 | keep | 0 | Feb | 2023 | 0.076288 | 0.00048903 | Sustained | FALSE | FALSE | Not_TMED_Event | 718
BAYAMON | 2023-02-28 15:05 | 2023-02-28 17:41 | 558 | 2:36 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE INTERRUPTOR PARA REALIZAR OPERACIONES PARA SECCIONALIZAR Y REALIZAR PRUEBA DE CONTACTO AL#5 DE LA SUBESTACION 1330-00 SJ-230228-01 90% DE LA CARGA POR EL 1330-01 SU CARGA POR 1525-03 | S23022800024 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 156 | 2023-02-28 | 87048 | keep | 0 | Feb | 2023 | 0.059288 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
CANOVANAS | 2023-02-28 15:08 | 2023-02-28 21:30 | 12 | 6:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 100KVA X 100KVA Y SE REPUSO 1 X 20 PROVISIONAL AEREO Y 1 X 25 SU-C | R23022800123 | New_Event | Service Transformer Failure | Include | Include | Equipment | 382 | 2023-02-28 | 4584 | keep | 0 | Feb | 2023 | 0.0031221 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-02-28 15:14 | 2023-02-28 16:30 | 40 | 1:16 | P | ANIMAL | 1 X 30 EN C/L SE RETIRO AVE | B23022800066 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-02-28 | 3040 | keep | 0 | Feb | 2023 | 0.0020705 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-02-28 15:15 | 2023-02-28 15:57 | 13 | 0:42 | P | CAUSAS EXTERNAS | SE ABRIO XMR Y SE REMPLAZO TOMA AVERIADA POR CAMION | C23022800080 | New_Event | Damage From Public | Include | Include | Public | 42 | 2023-02-28 | 546 | keep | 0 | Feb | 2023 | 0.00037188 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2023-02-28 15:20 | 2023-02-28 17:24 | 187 | 2:04 | P | ANIMAL | I X 100 EN C/L CRUCE X AVE | R23022800125 | New_Event | Animals | Include | Include | Wildlife | 124 | 2023-02-28 | 23188 | keep | 0 | Feb | 2023 | 0.015793 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
BARRANQUITAS | 2023-02-28 15:20 | 2023-02-28 17:20 | 1 | 2:00 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C23022800081 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 120 | 2023-02-28 | 120 | keep | 0 | Feb | 2023 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-28 15:21 | 2023-02-28 16:00 | 10 | 0:39 | P | ERROR HUMANO | PERSONAL DE PODA AVERIO SECUNDARIA REALIZANDO PODA SE ABRIO TRANSFORMADOR PARA REPARAR | B23022800068 | New_Event | Human Error | Include | Include | Other | 39 | 2023-02-28 | 390 | keep | 0 | Feb | 2023 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-02-28 15:30 | 2023-02-28 16:19 | 10 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR REP SECUNDARIA | S23022800200 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-02-28 | 490 | keep | 0 | Feb | 2023 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-02-28 15:47 | 2023-02-28 17:15 | 80 | 1:28 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | B23022800076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-02-28 | 7040 | keep | 0 | Feb | 2023 | 0.0047949 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-02-28 15:55 | 2023-02-28 16:25 | 28 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23022800078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-02-28 | 840 | keep | 0 | Feb | 2023 | 0.00057212 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
GUAYAMA | 2023-02-28 15:57 | 2023-02-28 19:00 | 1 | 3:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23022800091 | New_Event | Primary Wire Break | Include | Include | Equipment | 183 | 2023-02-28 | 183 | keep | 0 | Feb | 2023 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-02-28 16:02 | 2023-02-28 21:05 | 10 | 5:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE SALIDA DE CAJA DE CORTE DE LINEA | A23022800107 | New_Event | Primary Wire Break | Include | Include | Equipment | 303 | 2023-02-28 | 3030 | keep | 0 | Feb | 2023 | 0.0020637 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-02-28 16:15 | 2023-02-28 19:20 | 100 | 3:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CONVERTIDOR POR CAJA QUEMADA | M23022800091 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2023-02-28 | 18500 | keep | 0 | Feb | 2023 | 0.0126 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-02-28 16:19 | 2023-02-28 18:20 | 80 | 2:01 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A23022800109 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 121 | 2023-02-28 | 9680 | keep | 0 | Feb | 2023 | 0.006593 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-02-28 16:30 | 2023-02-28 19:00 | 1 | 2:30 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE | M23022800093 | New_Event | Primary Wire Break | Include | Include | Equipment | 150 | 2023-02-28 | 150 | keep | 0 | Feb | 2023 | 0.00010216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-02-28 16:31 | 2023-02-28 17:46 | 1 | 1:15 | P | DESGANCHE | 1 X 25 EN C/L | R23022800137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-02-28 | 75 | keep | 0 | Feb | 2023 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-28 16:34 | 2023-02-28 19:17 | 14 | 2:43 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | B23022800087 | New_Event | Primary Wire Break | Include | Include | Equipment | 163 | 2023-02-28 | 2282 | keep | 0 | Feb | 2023 | 0.0015543 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-02-28 16:35 | 2023-02-28 22:50 | 254 | 6:15 | P | ALIMENTADOR AMARRADO | DISPARO DE PORTATIL #8 SE REALIZARON OPERACIONES PARA AMARRAR ALIMENTADOR. 20% DE LA CARGA POR EL 1348-08 SJ-230228-02 SE ENCONTRO MACHETE QUEMADO PARTE BAJA PORTATIL #8 | S23022800226 | New_Event | Feeder Load Transferred | Include | Include | Other | 375 | 2023-02-28 | 95250 | keep | 0 | Feb | 2023 | 0.064874 | 0.000173 | Sustained | FALSE | FALSE | Not_TMED_Event | 254
SAN JUAN | 2023-02-28 16:35 | 2023-02-28 22:50 | 1290 | 6:15 | S | DESCONECTIVO DEFECTUOSO | DISPARO DE PORTATIL #8 SE REALIZARON OPERACIONES PARA AMARRAR ALIMENTADOR. LLEVA 20% DEL 1348-06 SJ-230228-02 SE ENCONTRO MACHETE QUEMADO PARTE BAJA PORTATIL#8 | S23022800226 | New_Event | Switch Failure | Include | Include | Equipment | 375 | 2023-02-28 | 483750 | keep | 0 | Feb | 2023 | 0.32948 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
PONCE | 2023-02-28 16:39 | 2023-02-28 19:26 | 40 | 2:47 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEAS | P23022800106 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-02-28 | 6680 | keep | 0 | Feb | 2023 | 0.0045497 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-02-28 16:45 | 2023-02-28 17:20 | 50 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M23022800096 | New_Event | Primary Wire Break | Include | Include | Equipment | 35 | 2023-02-28 | 1750 | keep | 0 | Feb | 2023 | 0.0011919 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-02-28 17:00 | 2023-02-28 18:23 | 20 | 1:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23022800110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 83 | 2023-02-28 | 1660 | keep | 0 | Feb | 2023 | 0.0011306 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-02-28 17:03 | 2023-02-28 18:53 | 1 | 1:50 | P | DESGANCHE | 1 X 50 EN C/L | C23022800095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-02-28 | 110 | keep | 0 | Feb | 2023 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-02-28 17:22 | 2023-02-28 19:24 | 47 | 2:02 | P | ANIMAL | 1 X 40 EN C/L SE RETIRO AVE | B23022800094 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-02-28 | 5734 | keep | 0 | Feb | 2023 | 0.0039054 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2023-02-28 18:13 | 2023-02-28 20:00 | 12 | 1:47 | P | ANIMAL | 1 X 8 EN XMR 1 X 65 EN C/L SE RETIRO AVE | S23022800246 | New_Event | Animals | Include | Include | Wildlife | 107 | 2023-02-28 | 1284 | keep | 0 | Feb | 2023 | 0.00087453 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-02-28 18:17 | 2023-02-28 19:33 | 21 | 1:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BARRA DE PEDESTAL | R23022800146 | New_Event | Secondary Wire Break | Include | Include | Equipment | 76 | 2023-02-28 | 1596 | keep | 0 | Feb | 2023 | 0.001087 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
FAJARDO | 2023-02-28 18:22 | 2023-03-01 09:11 | 15 | 14:49 | P | DESGANCHE | 1X20 EN C/L DESGANCHE PRIMARIO | R23022800147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 889 | 2023-02-28 | 13335 | keep | 0 | Feb | 2023 | 0.0090824 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-02-28 18:52 | 2023-02-28 18:53 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2302280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-02-28 | 4431 | keep | 0 | Feb | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
AGUADILLA | 2023-02-28 19:05 | 2023-02-28 20:50 | 10 | 1:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23022800115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-02-28 | 1050 | keep | 0 | Feb | 2023 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-02-28 19:08 | 2023-02-28 22:31 | 18 | 3:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23022800105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2023-02-28 | 3654 | keep | 0 | Feb | 2023 | 0.0024887 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2023-02-28 19:21 | 2023-03-01 09:40 | 25 | 14:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23022800117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 859 | 2023-02-28 | 21475 | keep | 0 | Feb | 2023 | 0.014627 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-02-28 21:29 | 2023-03-01 11:25 | 50 | 13:56 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA Y SE CIERRA PUENTE | M23022800128 | New_Event | Primary Wire Break | Include | Include | Equipment | 836 | 2023-02-28 | 41800 | keep | 0 | Feb | 2023 | 0.02847 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-03-01 01:03 | 2023-03-01 01:04 | 1879 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA EL 3006-05 CERRADO X CONTROL | C23030100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-01 | 1879 | keep | 0 | Mar | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-03-01 01:03 | 2023-03-01 01:04 | 3005 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 3006-02 | C23030100003 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-01 | 3005 | keep | 0 | Mar | 2023 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
BAYAMON | 2023-03-01 02:22 | 2023-03-01 05:45 | 723 | 3:23 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 203 | 2023-03-01 | 146769 | keep | 0 | Mar | 2023 | 0.099964 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-03-01 02:22 | 2023-03-01 05:45 | 198 | 3:23 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | New_Event | Feeder Load Transferred | Include | Include | Other | 203 | 2023-03-01 | 40194 | keep | 0 | Mar | 2023 | 0.027376 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-03-01 02:22 | 2023-03-01 05:45 | 1976 | 3:23 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | New_Event | Feeder Load Transferred | Include | Include | Other | 203 | 2023-03-01 | 401128 | keep | 0 | Mar | 2023 | 0.27321 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-03-01 02:22 | 2023-03-01 05:45 | 577 | 3:23 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | New_Event | Feeder Load Transferred | Include | Include | Other | 203 | 2023-03-01 | 117131 | keep | 0 | Mar | 2023 | 0.079777 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
MAYAGÃœEZ | 2023-03-01 03:29 | 2023-03-01 03:30 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23040100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-01 | 108 | keep | 0 | Mar | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2023-03-01 03:54 | 2023-03-01 03:55 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23040100006 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-01 | 108 | keep | 0 | Mar | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2023-03-01 05:12 | 2023-03-01 19:00 | 12 | 13:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50KVA | B23030100070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 828 | 2023-03-01 | 9936 | keep | 0 | Mar | 2023 | 0.0067674 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-03-01 05:20 | 2023-03-01 05:21 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-01 | 551 | keep | 0 | Mar | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
MAYAGÃœEZ | 2023-03-01 05:42 | 2023-03-01 11:56 | 50 | 6:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REMPLAZO DE CAJA QUEMADA Y BAJANTE ZAFADO EN CORTE DE LINEA | M23030100001 | New_Event | Cutout Failure | Include | Include | Equipment | 374 | 2023-03-01 | 18700 | keep | 0 | Mar | 2023 | 0.012736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-01 05:43 | 2023-03-01 09:44 | 1 | 4:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y BAJANTE DEL XMR SE REPUSO 1 X 15 EN XMR. | B23030100077 | New_Event | Cutout Failure | Include | Include | Equipment | 241 | 2023-03-01 | 241 | keep | 0 | Mar | 2023 | 0.00016414 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-01 05:45 | 2023-03-01 06:52 | 216 | 1:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | (TRATANDO DE LOCALIZAR AVERIA) DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 67 | 2023-03-01 | 14472 | keep | 0 | Mar | 2023 | 0.0098568 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-03-01 06:18 | 2023-03-01 17:53 | 4 | 11:35 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR T#24 50KVA A 7620VOLTS AVERIADO | P23030100007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 695 | 2023-03-01 | 2780 | keep | 0 | Mar | 2023 | 0.0018934 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-03-01 06:30 | 2023-03-01 06:31 | 1047 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | RECIERRE DE INTERRUPTOR POSTES PARTIDOS | M23030100006 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2023-03-01 | 1047 | keep | 0 | Mar | 2023 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2023-03-01 06:31 | 2023-03-01 10:30 | 20 | 3:59 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 50 EN CORTE DE LINEA SE SECCIONALIZO 2 POSTES PARIDOS | M23030100009 | 1st_after_momentary | Primary Pole Failure | Include | Include | Equipment | 239 | 2023-03-01 | 4780 | keep | 0 | Mar | 2023 | 0.0032556 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-01 06:49 | 2023-03-01 13:20 | 8 | 6:31 | P | ANIMAL | 1 X 15 EN CORTE DE LINEA IGUANA CRUZO LINEAS | A23030100003 | New_Event | Animals | Include | Include | Wildlife | 391 | 2023-03-01 | 3128 | keep | 0 | Mar | 2023 | 0.0021305 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-01 06:52 | 2023-03-01 06:58 | 723 | 0:06 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 6 | 2023-03-01 | 4338 | keep | 0 | Mar | 2023 | 0.0029546 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-01 06:52 | 2023-03-01 06:58 | 198 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 6 | 2023-03-01 | 1188 | keep | 0 | Mar | 2023 | 0.00080914 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-01 06:52 | 2023-03-01 06:58 | 1976 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 6 | 2023-03-01 | 11856 | keep | 0 | Mar | 2023 | 0.0080751 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-01 06:52 | 2023-03-01 06:58 | 1812 | 0:06 | T | ALIMENTADOR AMARRADO | HACIENDO OPERACIONES PARA AMARRAR CARGA SIN LOCALIZAR AVERIA OCASIONARON DISPARO, SE ABRE AMARRE Y SE CIERRA POR SCADA | B23030100096 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-03-01 | 10872 | keep | 0 | Mar | 2023 | 0.0074049 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2023-03-01 06:52 | 2023-03-01 06:58 | 577 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 6 | 2023-03-01 | 3462 | keep | 0 | Mar | 2023 | 0.002358 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-01 06:52 | 2023-03-01 10:04 | 1 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA CERRAR PUENTE PRIMARIO NO FUNDIO | R23030100001 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2023-03-01 | 192 | keep | 0 | Mar | 2023 | 0.00013077 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-01 06:58 | 2023-03-01 10:40 | 216 | 3:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | (TRATANDO DE LOCALIZAR AVERIA) DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 222 | 2023-03-01 | 47952 | keep | 0 | Mar | 2023 | 0.03266 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-01 06:59 | 2023-03-01 09:55 | 30 | 2:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23030100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-03-01 | 5280 | keep | 0 | Mar | 2023 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-03-01 07:09 | 2023-03-01 07:11 | 1475 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23030100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-01 | 2950 | keep | 0 | Mar | 2023 | 0.0020092 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
SAN JUAN | 2023-03-01 08:10 | 2023-03-01 12:55 | 20 | 4:45 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN RISER Y SE CERRO PUENTE DE LINEA A CAJA | S23030100068 | New_Event | Primary Wire Break | Include | Include | Equipment | 285 | 2023-03-01 | 5700 | keep | 0 | Mar | 2023 | 0.0038822 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-03-01 08:10 | 2023-03-01 10:00 | 50 | 1:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-03-01 | 5500 | keep | 0 | Mar | 2023 | 0.003746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-01 08:12 | 2023-03-01 10:40 | 45 | 2:28 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR IGUANA | B23030100117 | New_Event | Animals | Include | Include | Wildlife | 148 | 2023-03-01 | 6660 | keep | 0 | Mar | 2023 | 0.0045361 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-03-01 08:17 | 2023-03-01 10:17 | 100 | 2:00 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23030100119 | New_Event | Animals | Include | Include | Wildlife | 120 | 2023-03-01 | 12000 | keep | 0 | Mar | 2023 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-01 08:25 | 2023-03-01 08:26 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23030100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-01 | 4188 | keep | 0 | Mar | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2023-03-01 08:40 | 2023-03-01 11:26 | 1 | 2:46 | P | DESGANCHE | 2 X 65 EN C/L 1 X 25 EN BANCO DE XMRS DESGANCHE | R23030100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-03-01 | 166 | keep | 0 | Mar | 2023 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-01 08:42 | 2023-03-01 10:30 | 65 | 1:48 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C23030100022 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-03-01 | 7020 | keep | 0 | Mar | 2023 | 0.0047813 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-03-01 09:00 | 2023-03-01 10:13 | 159 | 1:13 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE Y 1 X 65 EN RISER | S23030100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-03-01 | 11607 | keep | 0 | Mar | 2023 | 0.0079055 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
AGUADILLA | 2023-03-01 09:17 | 2023-03-01 10:38 | 35 | 1:21 | P | DESGANCHE | 1 X 50 EN COTE DE LINEA POR DESGANCHE | M23030100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-03-01 | 2835 | keep | 0 | Mar | 2023 | 0.0019309 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-03-01 09:20 | 2023-03-01 18:59 | 43 | 9:39 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZAR POSTE PRIMARIO POR EMERGENCIA SJ-230301-01 | S23030100081 | New_Event | Primary Pole Failure | Include | Include | Equipment | 579 | 2023-03-01 | 24897 | keep | 0 | Mar | 2023 | 0.016957 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
FAJARDO | 2023-03-01 10:10 | 2023-03-01 11:53 | 1 | 1:43 | P | ANIMAL | 1X10 EN XMR CRUCE POR AVE | R23030100014 | New_Event | Animals | Include | Include | Wildlife | 103 | 2023-03-01 | 103 | keep | 0 | Mar | 2023 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-01 10:14 | 2023-03-01 12:49 | 1 | 2:35 | P | SOBRECARGA | 1 X 50 EN RISER POR CARGA TENIA FUSIBLE DE 30AMP | S23030100089 | New_Event | Trip Due To Overload | Include | Include | Other | 155 | 2023-03-01 | 155 | keep | 0 | Mar | 2023 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-01 10:15 | 2023-03-01 11:50 | 11 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23030100045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2023-03-01 | 1045 | keep | 0 | Mar | 2023 | 0.00071174 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-03-01 10:30 | 2023-03-01 19:35 | 7 | 9:05 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO SE CERRO PUENTES | M23030100059 | New_Event | Primary Pole Failure | Include | Include | Equipment | 545 | 2023-03-01 | 3815 | keep | 0 | Mar | 2023 | 0.0025984 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-03-01 10:30 | 2023-03-01 13:35 | 50 | 3:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-03-01 | 9250 | keep | 0 | Mar | 2023 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-01 10:40 | 2023-03-01 10:44 | 723 | 0:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2023-03-01 | 2892 | keep | 0 | Mar | 2023 | 0.0019697 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-03-01 10:40 | 2023-03-01 10:44 | 198 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-03-01 | 792 | keep | 0 | Mar | 2023 | 0.00053943 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-03-01 10:40 | 2023-03-01 10:44 | 1976 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-03-01 | 7904 | keep | 0 | Mar | 2023 | 0.0053834 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-03-01 10:40 | 2023-03-01 10:44 | 1812 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO HACIENDO OPERACIONES CERRADO POR SCADA. | B23030100174 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-03-01 | 7248 | keep | 0 | Mar | 2023 | 0.0049366 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2023-03-01 10:40 | 2023-03-01 10:44 | 577 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-03-01 | 2308 | keep | 0 | Mar | 2023 | 0.001572 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2023-03-01 10:44 | 2023-03-01 12:43 | 216 | 1:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | (TRATANDO DE LOCALIZAR AVERIA) DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 119 | 2023-03-01 | 25704 | keep | 0 | Mar | 2023 | 0.017507 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
MAYAGÃœEZ | 2023-03-01 10:50 | 2023-03-01 16:00 | 50 | 5:10 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN CORTE DE LINEA LINEAS CRUZADAS | M23030100062 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 310 | 2023-03-01 | 15500 | keep | 0 | Mar | 2023 | 0.010557 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-01 10:58 | 2023-03-01 13:25 | 30 | 2:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-03-01 | 4410 | keep | 0 | Mar | 2023 | 0.0030036 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-01 11:14 | 2023-03-01 11:58 | 12 | 0:44 | P | ANIMAL | 2 X 15 EN XMR CULEBRA | B23030100192 | New_Event | Animals | Include | Include | Wildlife | 44 | 2023-03-01 | 528 | keep | 0 | Mar | 2023 | 0.00035962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-01 11:25 | 2023-03-01 13:45 | 237 | 2:20 | P | CONDUCTOR ROTO O ABIERTO | SE CERRARON 2 PUENTES PRIMARIOS SE CERRO CORTE DE LINEA | M23030100070 | New_Event | Primary Wire Break | Include | Include | Equipment | 140 | 2023-03-01 | 33180 | keep | 0 | Mar | 2023 | 0.022599 | 0.00016142 | Sustained | FALSE | FALSE | Not_TMED_Event | 237
YAUCO | 2023-03-01 11:26 | 2023-03-01 11:39 | 3036 | 0:13 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR MANUAL POR RTU DOWN PARA ABRIR MACHETES AVERIADOS EN VIA LIBRE D2023-3084 REV 1 | M23030100058 | New_Event | Switch Failure | Include | Include | Equipment | 13 | 2023-03-01 | 39468 | keep | 0 | Mar | 2023 | 0.026881 | 0.0020678 | Sustained | FALSE | FALSE | Not_TMED_Event | 3036
CAGUAS | 2023-03-01 11:48 | 2023-03-01 15:26 | 25 | 3:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23030100106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2023-03-01 | 5450 | keep | 0 | Mar | 2023 | 0.003712 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-03-01 11:50 | 2023-03-01 13:14 | 8 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | C23030100061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2023-03-01 | 672 | keep | 0 | Mar | 2023 | 0.0004577 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-03-01 12:15 | 2023-03-01 13:27 | 174 | 1:12 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23030100111 | New_Event | Primary Wire Break | Include | Include | Equipment | 72 | 2023-03-01 | 12528 | keep | 0 | Mar | 2023 | 0.0085328 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
HUMACAO | 2023-03-01 12:24 | 2023-03-01 16:10 | 146 | 3:46 | P | CAUSAS EXTERNAS | SE ABRIO C/L PARA REEMPLAZAR POSTE PRIMARIO IMPACTADO POR VEHICULO | C23030100067 | New_Event | Damage From Public | Include | Include | Public | 226 | 2023-03-01 | 32996 | keep | 0 | Mar | 2023 | 0.022473 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
BAYAMON | 2023-03-01 12:43 | 2023-03-01 12:46 | 723 | 0:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2023-03-01 | 2169 | keep | 0 | Mar | 2023 | 0.0014773 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-01 12:43 | 2023-03-01 12:46 | 198 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-01 | 594 | keep | 0 | Mar | 2023 | 0.00040457 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-03-01 12:43 | 2023-03-01 12:46 | 1976 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-01 | 5928 | keep | 0 | Mar | 2023 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-03-01 12:43 | 2023-03-01 12:46 | 577 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-01 | 1731 | keep | 0 | Mar | 2023 | 0.001179 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2023-03-01 12:46 | 2023-03-01 14:25 | 216 | 1:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | (TRATANDO DE LOCALIZAR AVERIA) DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 99 | 2023-03-01 | 21384 | keep | 0 | Mar | 2023 | 0.014565 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
HUMACAO | 2023-03-01 12:56 | 2023-03-01 14:24 | 8 | 1:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA RERPARAR BAJANTE SECUNDARIO | C23030100072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 88 | 2023-03-01 | 704 | keep | 0 | Mar | 2023 | 0.00047949 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-01 13:04 | 2023-03-01 16:24 | 59 | 3:20 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | B23030100235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-03-01 | 11800 | keep | 0 | Mar | 2023 | 0.0080369 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
GUAYAMA | 2023-03-01 13:30 | 2023-03-01 13:46 | 1 | 0:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE 1 X 40 EN CORTE DE LINEA | P23030100023 | New_Event | Primary Wire Break | Include | Include | Equipment | 16 | 2023-03-01 | 16 | keep | 0 | Mar | 2023 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-01 13:42 | 2023-03-01 14:58 | 14 | 1:16 | P | PROBLEMA DEL CLIENTE | ABRIR PM (T-41) POR FUEGO EN BASE DE CONTADOR DEL CLIENTE | R23030100028 | New_Event | Customer-Related Interruption | Include | Include | Public | 76 | 2023-03-01 | 1064 | keep | 0 | Mar | 2023 | 0.00072469 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-03-01 14:05 | 2023-03-01 19:00 | 1 | 4:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23030100067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 295 | 2023-03-01 | 295 | keep | 0 | Mar | 2023 | 0.00020092 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-01 14:20 | 2023-03-01 17:00 | 50 | 2:40 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M23030100098 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 160 | 2023-03-01 | 8000 | keep | 0 | Mar | 2023 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-01 14:25 | 2023-03-01 14:26 | 723 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-03-01 | 723 | keep | 0 | Mar | 2023 | 0.00049243 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-01 14:25 | 2023-03-01 14:26 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-01 | 198 | keep | 0 | Mar | 2023 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-03-01 14:25 | 2023-03-01 14:26 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-01 | 1976 | keep | 0 | Mar | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-03-01 14:25 | 2023-03-01 14:26 | 577 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-01 | 577 | keep | 0 | Mar | 2023 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2023-03-01 14:26 | 2023-03-01 17:02 | 216 | 2:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | (TRATANDO DE LOCALIZAR AVERIA) DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 156 | 2023-03-01 | 33696 | keep | 0 | Mar | 2023 | 0.02295 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
SAN JUAN | 2023-03-01 14:28 | 2023-03-01 17:51 | 8 | 3:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23030100134 | New_Event | Secondary Wire Break | Include | Include | Equipment | 203 | 2023-03-01 | 1624 | keep | 0 | Mar | 2023 | 0.0011061 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-01 14:54 | 2023-03-01 17:55 | 5 | 3:01 | P | DESGANCHE | 1 X 15 EN XMR SE RETIRO RAMA DE PALMA | S23030100138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-03-01 | 905 | keep | 0 | Mar | 2023 | 0.00061639 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-01 14:59 | 2023-03-01 15:00 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23030100032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-01 | 4085 | keep | 0 | Mar | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-03-01 15:32 | 2023-03-02 10:00 | 80 | 18:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L | S23030100145 | New_Event | Cutout Failure | Include | Include | Equipment | 1108 | 2023-03-01 | 88640 | keep | 0 | Mar | 2023 | 0.060372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-03-01 16:08 | 2023-03-01 17:30 | 40 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23030100113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2023-03-01 | 3280 | keep | 0 | Mar | 2023 | 0.002234 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-01 16:14 | 2023-03-01 19:06 | 7 | 2:52 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADO POR LINEA CRUZADA | M23030100114 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 172 | 2023-03-01 | 1204 | keep | 0 | Mar | 2023 | 0.00082004 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-01 17:02 | 2023-03-01 17:08 | 723 | 0:06 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 Y ENTRO 70% EN SERVICIO | B23030100001 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 6 | 2023-03-01 | 4338 | keep | 0 | Mar | 2023 | 0.0029546 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-01 17:02 | 2023-03-01 17:08 | 198 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 6 | 2023-03-01 | 1188 | keep | 0 | Mar | 2023 | 0.00080914 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-03-01 17:02 | 2023-03-01 17:08 | 1976 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 6 | 2023-03-01 | 11856 | keep | 0 | Mar | 2023 | 0.0080751 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-03-01 17:02 | 2023-03-01 17:08 | 577 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 6 | 2023-03-01 | 3462 | keep | 0 | Mar | 2023 | 0.002358 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2023-03-01 17:03 | 2023-03-01 17:07 | 959 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 TRANSFORMADOR AVERIADO SUB. 9860 ESCUELA FRANCISCO LOPEZ | B23030100316 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-01 | 3836 | keep | 0 | Mar | 2023 | 0.0026127 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-03-01 17:03 | 2023-03-01 17:07 | 1382 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 TRANSFORMADOR AVERIADO SUB. 9860 ESCUELA FRANCISCO LOPEZ | B23030100316 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-01 | 5528 | keep | 0 | Mar | 2023 | 0.0037651 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-03-01 17:03 | 2023-03-01 17:07 | 663 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 TRANSFORMADOR AVERIADO SUB. 9860 ESCUELA FRANCISCO LOPEZ | B23030100316 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-01 | 2652 | keep | 0 | Mar | 2023 | 0.0018063 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-03-01 17:03 | 2023-03-01 17:07 | 1514 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 TRANSFORMADOR AVERIADO SUB. 9860 ESCUELA FRANCISCO LOPEZ | B23030100315 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-01 | 6056 | keep | 0 | Mar | 2023 | 0.0041247 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-03-01 17:03 | 2023-03-01 17:07 | 1105 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 TRANSFORMADOR AVERIADO SUB. 9860 ESCUELA FRANCISCO LOPEZ | B23030100315 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-01 | 4420 | keep | 0 | Mar | 2023 | 0.0030104 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-03-01 17:03 | 2023-03-01 17:07 | 4176 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 TRANSFORMADOR AVERIADO SUB. 9860 ESCUELA FRANCISCO LOPEZ | B23030100318 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-01 | 16704 | keep | 0 | Mar | 2023 | 0.011377 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-03-01 17:03 | 2023-03-01 17:07 | 252 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 TRANSFORMADOR AVERIADO SUB. 9860 ESCUELA FRANCISCO LOPEZ | B23030100318 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-01 | 1008 | keep | 0 | Mar | 2023 | 0.00068654 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-03-01 17:03 | 2023-03-01 17:07 | 2147 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 TRANSFORMADOR AVERIADO SUB. 9860 ESCUELA FRANCISCO LOPEZ | B23030100318 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-01 | 8588 | keep | 0 | Mar | 2023 | 0.0058492 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-03-01 17:03 | 2023-03-01 17:07 | 2858 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 TRANSFORMADOR AVERIADO SUB. 9860 ESCUELA FRANCISCO LOPEZ | B23030100320 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-01 | 11432 | keep | 0 | Mar | 2023 | 0.0077863 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-03-01 17:08 | 2023-03-01 18:12 | 216 | 1:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | (TRATANDO DE LOCALIZAR AVERIA) DISPARO DE INTERRUPTOR 1711-02 LLEVA 1711-05 LLEVA 10% 1711-04 Y LLEVA 1912-08 TRABAJOS CON EL GOI BY-23030100001 | B23030100001 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 64 | 2023-03-01 | 13824 | keep | 0 | Mar | 2023 | 0.0094155 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-03-01 17:21 | 2023-03-01 18:51 | 53 | 1:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23030100127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2023-03-01 | 4770 | keep | 0 | Mar | 2023 | 0.0032488 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
CANOVANAS | 2023-03-01 17:26 | 2023-03-01 18:55 | 4 | 1:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R23030100041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 89 | 2023-03-01 | 356 | keep | 0 | Mar | 2023 | 0.00024247 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-03-01 17:29 | 2023-03-01 19:57 | 3 | 2:28 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23030100087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2023-03-01 | 444 | keep | 0 | Mar | 2023 | 0.00030241 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-03-01 17:34 | 2023-03-01 20:27 | 47 | 2:53 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23030100131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-03-01 | 8131 | keep | 0 | Mar | 2023 | 0.005538 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
FAJARDO | 2023-03-01 18:09 | 2023-03-01 18:56 | 3 | 0:47 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XMR DESGANCHE | R23030100042 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 47 | 2023-03-01 | 141 | keep | 0 | Mar | 2023 | 9.6034e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-03-01 18:11 | 2023-03-01 20:25 | 60 | 2:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23030100123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2023-03-01 | 8040 | keep | 0 | Mar | 2023 | 0.005476 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-01 18:12 | 2023-03-01 21:42 | 100 | 3:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZARON JUEGO DE DISCOS PARTIDOS EN VARIOS PUENTOS Y SE AISLO AVERIA VIEJA EN SU-6 | B23030100001 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 210 | 2023-03-01 | 21000 | keep | 0 | Mar | 2023 | 0.014303 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-01 18:51 | 2023-03-01 21:30 | 7 | 2:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23030100093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2023-03-01 | 1113 | keep | 0 | Mar | 2023 | 0.00075806 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-03-01 18:57 | 2023-03-01 20:40 | 15 | 1:43 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-03-01 | 1545 | keep | 0 | Mar | 2023 | 0.0010523 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-03-01 18:57 | 2023-03-01 22:40 | 32 | 3:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A23030100094 | New_Event | Cutout Failure | Include | Include | Equipment | 223 | 2023-03-01 | 7136 | keep | 0 | Mar | 2023 | 0.0048603 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2023-03-01 19:31 | 2023-03-01 19:36 | 1825 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100173 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-01 | 9125 | keep | 0 | Mar | 2023 | 0.006215 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-03-01 19:31 | 2023-03-01 19:36 | 47 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100173 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-01 | 235 | keep | 0 | Mar | 2023 | 0.00016006 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-03-01 19:31 | 2023-03-01 19:36 | 315 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100173 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-01 | 1575 | keep | 0 | Mar | 2023 | 0.0010727 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2023-03-01 19:31 | 2023-03-01 19:36 | 2 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100173 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-01 | 10 | keep | 0 | Mar | 2023 | 6.811e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-03-01 19:31 | 2023-03-01 19:36 | 2391 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100173 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-01 | 11955 | keep | 0 | Mar | 2023 | 0.0081425 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
SAN JUAN | 2023-03-01 19:31 | 2023-03-01 19:36 | 3957 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2303010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-03-01 | 19785 | keep | 0 | Mar | 2023 | 0.013475 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
CAGUAS | 2023-03-01 19:31 | 2023-03-01 21:37 | 1153 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE -LINEA 3000 | C23030100220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-03-01 | 145278 | keep | 0 | Mar | 2023 | 0.098948 | 0.0007853 | Sustained | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2023-03-01 19:31 | 2023-03-01 21:37 | 1709 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE -LINEA 3000 | C23030100220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-03-01 | 215334 | keep | 0 | Mar | 2023 | 0.14666 | 0.001164 | Sustained | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2023-03-01 19:31 | 2023-03-01 21:37 | 1320 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE -LINEA 3000 | C23030100220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-03-01 | 166320 | keep | 0 | Mar | 2023 | 0.11328 | 0.00089905 | Sustained | FALSE | FALSE | Not_TMED_Event | 1320
CAGUAS | 2023-03-01 19:31 | 2023-03-01 21:37 | 2276 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE -LINEA 3000 | C23030100219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-03-01 | 286776 | keep | 0 | Mar | 2023 | 0.19532 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2023-03-01 19:31 | 2023-03-01 21:37 | 777 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE -LINEA 3000 | C23030100219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-03-01 | 97902 | keep | 0 | Mar | 2023 | 0.066681 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2023-03-01 19:31 | 2023-03-01 21:37 | 12 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE -LINEA 3000 | C23030100219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-03-01 | 1512 | keep | 0 | Mar | 2023 | 0.0010298 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-01 19:31 | 2023-03-01 21:37 | 1290 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE -LINEA 3000 | C23030100219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-03-01 | 162540 | keep | 0 | Mar | 2023 | 0.11071 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2023-03-01 21:35 | 2023-03-01 21:37 | 1825 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100225 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-01 | 3650 | keep | 0 | Mar | 2023 | 0.002486 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-01 21:35 | 2023-03-01 21:37 | 47 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100225 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-01 | 94 | keep | 0 | Mar | 2023 | 6.4023e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-01 21:35 | 2023-03-01 21:37 | 315 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100225 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-01 | 630 | keep | 0 | Mar | 2023 | 0.00042909 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-01 21:35 | 2023-03-01 21:37 | 2 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100225 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-01 | 4 | keep | 0 | Mar | 2023 | 2.7244e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-01 21:35 | 2023-03-01 21:37 | 2391 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23030100225 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-01 | 4782 | keep | 0 | Mar | 2023 | 0.003257 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-03-01 22:07 | 2023-03-02 11:15 | 75 | 13:08 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23030100134 | New_Event | Primary Wire Break | Include | Include | Equipment | 788 | 2023-03-01 | 59100 | keep | 0 | Mar | 2023 | 0.040253 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-03-01 22:27 | 2023-03-01 22:28 | 4830 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE | C23030100270 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-01 | 4830 | keep | 0 | Mar | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
BAYAMON | 2023-03-02 00:39 | 2023-03-02 01:34 | 473 | 0:55 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23030200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-03-02 | 26015 | keep | 0 | Mar | 2023 | 0.017719 | 0.00032216 | Sustained | FALSE | FALSE | Not_TMED_Event | 473
BAYAMON | 2023-03-02 02:43 | 2023-03-02 04:34 | 45 | 1:51 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23030200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-03-02 | 4995 | keep | 0 | Mar | 2023 | 0.0034021 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-03-02 03:03 | 2023-03-02 09:22 | 74 | 6:19 | P | DESGANCHE | 1 X 40 EN C/L | R23030200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2023-03-02 | 28046 | keep | 0 | Mar | 2023 | 0.019102 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
CAGUAS | 2023-03-02 03:16 | 2023-03-02 03:17 | 1922 | 0:01 | T | DESGANCHE | RECIERRE | C23030200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-02 | 1922 | keep | 0 | Mar | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2023-03-02 03:17 | 2023-03-02 08:27 | 103 | 5:10 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23030200005 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 310 | 2023-03-02 | 31930 | keep | 0 | Mar | 2023 | 0.021747 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
HUMACAO | 2023-03-02 03:37 | 2023-03-02 03:38 | 4830 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE | C23030200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-02 | 4830 | keep | 0 | Mar | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
ARECIBO | 2023-03-02 04:51 | 2023-03-02 09:50 | 50 | 4:59 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO CRUZANDO CON OTRA FASE | A23030200001 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 299 | 2023-03-02 | 14950 | keep | 0 | Mar | 2023 | 0.010182 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-03-02 06:02 | 2023-03-02 08:26 | 50 | 2:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M2303020007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 144 | 2023-03-02 | 7200 | keep | 0 | Mar | 2023 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-03-02 06:26 | 2023-03-02 06:27 | 4009 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | P23030200028 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-02 | 4009 | keep | 0 | Mar | 2023 | 0.0027305 | 0.0027305 | Momentary | FALSE | FALSE | Not_TMED_Event | 4009
PONCE | 2023-03-02 06:27 | 2023-03-02 08:56 | 200 | 2:29 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | P23030200029 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 149 | 2023-03-02 | 29800 | keep | 0 | Mar | 2023 | 0.020297 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-03-02 06:33 | 2023-03-02 09:08 | 128 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 200 EN C/L | R23030200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2023-03-02 | 19840 | keep | 0 | Mar | 2023 | 0.013513 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
VEGA BAJA | 2023-03-02 07:38 | 2023-03-02 08:10 | 1 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23030200007 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2023-03-02 | 32 | keep | 0 | Mar | 2023 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-03-02 07:39 | 2023-03-02 08:11 | 10 | 0:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REEMPLAZO PORTAFUSIBLE | R23030200020 | New_Event | Cutout Failure | Include | Include | Equipment | 32 | 2023-03-02 | 320 | keep | 0 | Mar | 2023 | 0.00021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-03-02 07:40 | 2023-03-02 10:51 | 30 | 3:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P23030200054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-03-02 | 5730 | keep | 0 | Mar | 2023 | 0.0039027 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-02 07:46 | 2023-03-02 16:27 | 20 | 8:41 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23030200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2023-03-02 | 10420 | keep | 0 | Mar | 2023 | 0.007097 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-03-02 07:49 | 2023-03-02 10:03 | 6 | 2:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE TRANSFORMADOR AVERIADA | M23030200014 | New_Event | Cutout Failure | Include | Include | Equipment | 134 | 2023-03-02 | 804 | keep | 0 | Mar | 2023 | 0.0005476 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-03-02 07:51 | 2023-03-02 07:52 | 4390 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR CARGA POR EL 3301-03 EN SERVICIO | C23030200028 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-02 | 4390 | keep | 0 | Mar | 2023 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2023-03-02 07:51 | 2023-03-02 07:52 | 540 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 3301-01 EN SERVICIO | C23030200028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-02 | 540 | keep | 0 | Mar | 2023 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
PONCE | 2023-03-02 08:00 | 2023-03-02 10:46 | 150 | 2:46 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA DESGANCHE | P23030200059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-03-02 | 24900 | keep | 0 | Mar | 2023 | 0.016959 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-03-02 08:02 | 2023-03-02 08:50 | 293 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | S23030200012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-02 | 14064 | keep | 0 | Mar | 2023 | 0.0095789 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2023-03-02 08:02 | 2023-03-02 08:50 | 315 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | S23030200012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-02 | 15120 | keep | 0 | Mar | 2023 | 0.010298 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2023-03-02 08:02 | 2023-03-02 08:50 | 216 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | S23030200012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-02 | 10368 | keep | 0 | Mar | 2023 | 0.0070616 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2023-03-02 08:02 | 2023-03-02 08:50 | 1310 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 | S23030200012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-02 | 62880 | keep | 0 | Mar | 2023 | 0.042827 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2023-03-02 08:02 | 2023-03-02 08:50 | 212 | 0:48 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 CARGA DE 1924-01 POR 1903-02 | S23030200012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-02 | 10176 | keep | 0 | Mar | 2023 | 0.0069308 | 0.00014439 | Sustained | FALSE | FALSE | Not_TMED_Event | 212
BAYAMON | 2023-03-02 08:02 | 2023-03-02 08:50 | 31 | 0:48 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 70% DE LA CARGA DEL 1924-04 ESTA POR 1903-03 | S23030200012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-02 | 1488 | keep | 0 | Mar | 2023 | 0.0010135 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-03-02 08:02 | 2023-03-02 08:50 | 686 | 0:48 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 CARGA DEL 1924-05 ESTA POR 1903-03 | S23030200012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-02 | 32928 | keep | 0 | Mar | 2023 | 0.022427 | 0.00046723 | Sustained | FALSE | FALSE | Not_TMED_Event | 686
VEGA BAJA | 2023-03-02 08:26 | 2023-03-02 11:51 | 20 | 3:25 | P | ANIMAL | 2 X 65 EN C/L SE RETIRO AVES | B23030200015 | New_Event | Animals | Include | Include | Wildlife | 205 | 2023-03-02 | 4100 | keep | 0 | Mar | 2023 | 0.0027925 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-03-02 09:08 | 2023-03-02 12:10 | 25 | 3:02 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR AVE | P23030200072 | New_Event | Animals | Include | Include | Wildlife | 182 | 2023-03-02 | 4550 | keep | 0 | Mar | 2023 | 0.003099 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-03-02 09:09 | 2023-03-02 09:10 | 181 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S23030200056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-02 | 181 | keep | 0 | Mar | 2023 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
SAN JUAN | 2023-03-02 09:18 | 2023-03-02 09:19 | 271 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2303020000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-02 | 271 | keep | 0 | Mar | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2023-03-02 09:19 | 2023-03-02 14:20 | 1 | 5:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 2 X 50 EN C/L | S23030200069 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 301 | 2023-03-02 | 301 | keep | 0 | Mar | 2023 | 0.00020501 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-02 09:26 | 2023-03-02 12:26 | 291 | 3:00 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23030200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-03-02 | 52380 | keep | 0 | Mar | 2023 | 0.035676 | 0.0001982 | Sustained | FALSE | FALSE | Not_TMED_Event | 291
PONCE | 2023-03-02 09:34 | 2023-03-02 21:00 | 3 | 11:26 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE PRIMARIO PARTIDO | P23030200080 | New_Event | Primary Pole Failure | Include | Include | Equipment | 686 | 2023-03-02 | 2058 | keep | 0 | Mar | 2023 | 0.0014017 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-03-02 09:41 | 2023-03-03 09:11 | 8 | 23:30 | P | TRANSFORMADOR AVERIADO | EVENTO DE CLIENTES SIN SERVICIO SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS OMS DICE SE AJUSTO NEUTRAL SECUNDARIO EN BUSHING DEL TRANSFORMADOR | A23030200083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1410 | 2023-03-02 | 11280 | keep | 0 | Mar | 2023 | 0.0076828 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-03-02 09:44 | 2023-03-02 11:35 | 60 | 1:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M2303020071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-03-02 | 6660 | keep | 0 | Mar | 2023 | 0.0045361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-02 10:01 | 2023-03-02 10:02 | 949 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | B2303020000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-02 | 949 | keep | 0 | Mar | 2023 | 0.00064636 | 0.00064636 | Momentary | FALSE | FALSE | Not_TMED_Event | 949
BAYAMON | 2023-03-02 10:02 | 2023-03-02 15:35 | 313 | 5:33 | P | CONDUCTOR ROTO O ABIERTO | BY-230302-01 SE CERRO AMARRE CONTRA 1715-03 Y SE SECCIONALIZO PARA CERRAR PUENTE ABIERTO | B23030200032 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 333 | 2023-03-02 | 104229 | keep | 0 | Mar | 2023 | 0.07099 | 0.00021318 | Sustained | FALSE | FALSE | Not_TMED_Event | 313
SAN JUAN | 2023-03-02 10:11 | 2023-03-02 15:03 | 30 | 4:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y SE REPARO PUENTE DE LINEA A CAJA | S23030200067 | New_Event | Cutout Failure | Include | Include | Equipment | 292 | 2023-03-02 | 8760 | keep | 0 | Mar | 2023 | 0.0059664 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-02 10:19 | 2023-03-02 14:31 | 4 | 4:12 | P | ANIMAL | 1 X 8 EN XMR CRUCE POR LAGARTIJO | C23030200050 | New_Event | Animals | Include | Include | Wildlife | 252 | 2023-03-02 | 1008 | keep | 0 | Mar | 2023 | 0.00068654 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-03-02 10:19 | 2023-03-02 12:41 | 50 | 2:22 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23030200088 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 142 | 2023-03-02 | 7100 | keep | 0 | Mar | 2023 | 0.0048358 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-03-02 10:20 | 2023-03-02 12:00 | 10 | 1:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE | M2303020102 | New_Event | Service Transformer Failure | Include | Include | Equipment | 100 | 2023-03-02 | 1000 | keep | 0 | Mar | 2023 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-02 10:35 | 2023-03-02 12:35 | 80 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23030200097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2023-03-02 | 9600 | keep | 0 | Mar | 2023 | 0.0065385 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-03-02 10:47 | 2023-03-02 10:48 | 1841 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A23030200022 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-02 | 1841 | keep | 0 | Mar | 2023 | 0.0012539 | 0.0012539 | Momentary | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2023-03-02 10:48 | 2023-03-02 17:10 | 75 | 6:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A23030200027 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 382 | 2023-03-02 | 28650 | keep | 0 | Mar | 2023 | 0.019513 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
GUAYAMA | 2023-03-02 11:06 | 2023-03-02 17:10 | 8 | 6:04 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REEMPLAZO DE POSTE PRIMARIO | P23030200107 | New_Event | Primary Pole Failure | Include | Include | Equipment | 364 | 2023-03-02 | 2912 | keep | 0 | Mar | 2023 | 0.0019833 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-03-02 11:06 | 2023-03-02 17:40 | 200 | 6:34 | P | CONDUCTOR ROTO O ABIERTO | 1 X 140 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M23030200112 | New_Event | Primary Wire Break | Include | Include | Equipment | 394 | 2023-03-02 | 78800 | keep | 0 | Mar | 2023 | 0.05367 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2023-03-02 11:10 | 2023-03-02 12:05 | 7 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA AJUSTAR VOLTAJE SECUNDARIO Y SE REMPLAZO CONEXIONES SECUNDARIAS | A23030200026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-03-02 | 385 | keep | 0 | Mar | 2023 | 0.00026222 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-02 11:56 | 2023-03-02 12:02 | 652 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | B2303020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-03-02 | 3912 | keep | 0 | Mar | 2023 | 0.0026644 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2023-03-02 12:12 | 2023-03-02 12:14 | 2791 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A23030200042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-02 | 5582 | keep | 0 | Mar | 2023 | 0.0038019 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2023-03-02 12:12 | 2023-03-02 12:14 | 1464 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A23030200042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-02 | 2928 | keep | 0 | Mar | 2023 | 0.0019942 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
VEGA BAJA | 2023-03-02 12:12 | 2023-03-02 12:14 | 759 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A23030200042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-02 | 1518 | keep | 0 | Mar | 2023 | 0.0010339 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2023-03-02 12:12 | 2023-03-02 12:14 | 1500 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A23030200042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-02 | 3000 | keep | 0 | Mar | 2023 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
MAYAGÃœEZ | 2023-03-02 12:38 | 2023-03-02 16:28 | 150 | 3:50 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA CAMION IMPACTO POSTE Y CRUZO LINEAS | M23030200142 | New_Event | Damage From Public | Include | Include | Public | 230 | 2023-03-02 | 34500 | keep | 0 | Mar | 2023 | 0.023498 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-03-02 13:01 | 2023-03-02 17:19 | 102 | 4:18 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 Y 1 X 30 EN C/L SE LEVANTO PRIMARIA | B23030200079 | New_Event | Primary Wire Break | Include | Include | Equipment | 258 | 2023-03-02 | 26316 | keep | 0 | Mar | 2023 | 0.017924 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
HUMACAO | 2023-03-02 13:13 | 2023-03-02 14:52 | 12 | 1:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO | C23030200084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 99 | 2023-03-02 | 1188 | keep | 0 | Mar | 2023 | 0.00080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-03-02 13:25 | 2023-03-02 15:32 | 14 | 2:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | R23030200043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 127 | 2023-03-02 | 1778 | keep | 0 | Mar | 2023 | 0.001211 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2023-03-02 13:26 | 2023-03-02 15:10 | 207 | 1:44 | T | DESGANCHE | ALIMENTADOR FUERA DE SERVICIO DEBIDO A RAMA SOBRE LINEA TIENE LA CARGA DEL 5403-02 | P23030200149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-03-02 | 21528 | keep | 0 | Mar | 2023 | 0.014663 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
YAUCO | 2023-03-02 13:26 | 2023-03-02 15:10 | 286 | 1:44 | T | ALIMENTADOR AMARRADO | ALIMENTADOR FUERA DE SERVICIO DEBIDO A RAMA SOBRE LINEA CARGA POR 5403-01 | P23030200149 | New_Event | Feeder Load Transferred | Include | Include | Other | 104 | 2023-03-02 | 29744 | keep | 0 | Mar | 2023 | 0.020259 | 0.00019479 | Sustained | FALSE | FALSE | Not_TMED_Event | 286
MAYAGÃœEZ | 2023-03-02 13:28 | 2023-03-02 13:29 | 1428 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23030200156 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-02 | 1428 | keep | 0 | Mar | 2023 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2023-03-02 13:29 | 2023-03-02 15:23 | 476 | 1:54 | P | CONDUCTOR ROTO O ABIERTO | GOI MY-230302-01A SE ABRE INTERRUPTOR PARA REPARAR LINEA PRIMARIA PARTIDA EN TRONCAL CARR 413 KM 5.7 BO PUNTAS RINCON | M23030200158 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 114 | 2023-03-02 | 54264 | keep | 0 | Mar | 2023 | 0.036959 | 0.0003242 | Sustained | FALSE | FALSE | Not_TMED_Event | 476
AGUADILLA | 2023-03-02 13:30 | 2023-03-02 14:43 | 15 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23030200009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-03-02 | 1095 | keep | 0 | Mar | 2023 | 0.0007458 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-02 13:47 | 2023-03-02 18:05 | 25 | 4:18 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | M23030200166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2023-03-02 | 6450 | keep | 0 | Mar | 2023 | 0.0043931 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-03-02 14:18 | 2023-03-02 18:37 | 50 | 4:19 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23030200179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-03-02 | 12950 | keep | 0 | Mar | 2023 | 0.0088202 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-03-02 14:22 | 2023-03-02 14:23 | 411 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23030200198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-02 | 411 | keep | 0 | Mar | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
HUMACAO | 2023-03-02 14:42 | 2023-03-02 18:30 | 3 | 3:48 | P | DESGANCHE | 1 X 25 EN C/L Y DESGANCHE | C23030200093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-03-02 | 684 | keep | 0 | Mar | 2023 | 0.00046587 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-03-02 14:46 | 2023-03-02 17:15 | 30 | 2:29 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO PALMAS SOBRE LINEAS | A23030200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-03-02 | 4470 | keep | 0 | Mar | 2023 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-03-02 15:10 | 2023-03-02 15:30 | 40 | 0:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M23030200185 | New_Event | Cutout Failure | Include | Include | Equipment | 20 | 2023-03-02 | 800 | keep | 0 | Mar | 2023 | 0.00054488 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-03-02 15:23 | 2023-03-02 20:37 | 1428 | 5:14 | T | CONDUCTOR ROTO O ABIERTO | GOI # MY-230302-01A SE ABRE INTERRUPTOR PARA REPARAR LINEA PRIMARIA PARTIDA EN TRONCAL | M2303020021 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 314 | 2023-03-02 | 448392 | keep | 0 | Mar | 2023 | 0.3054 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-02 15:35 | 2023-03-02 17:20 | 22 | 1:45 | P | CONDUCTOR ROTO O ABIERTO | BY-230302-01 SE CERRO PUENTE ABIERTO Y SE NORMALIZO CARGAS | B23030200032 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 105 | 2023-03-02 | 2310 | keep | 0 | Mar | 2023 | 0.0015733 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-02 15:49 | 2023-03-02 15:50 | 27 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23030200122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-02 | 27 | keep | 0 | Mar | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2023-03-02 16:29 | 2023-03-02 16:36 | 3630 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR RR EN OFF SE VERIFICO PERSONAL FUERA DE LINEAS PRIMARIAS Y SE COLOCO INTERRUPTOR EN SERVICIO | M23030200245 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-03-02 | 25410 | keep | 0 | Mar | 2023 | 0.017307 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2023-03-02 16:35 | 2023-03-02 18:15 | 60 | 1:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA FUERTES VIENTOS | M23030200242 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 100 | 2023-03-02 | 6000 | keep | 0 | Mar | 2023 | 0.0040866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-03-02 16:46 | 2023-03-02 16:47 | 693 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2303020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-02 | 693 | keep | 0 | Mar | 2023 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
PONCE | 2023-03-02 16:57 | 2023-03-02 16:58 | 3744 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | P23030200161 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-02 | 3744 | keep | 0 | Mar | 2023 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2023-03-02 16:58 | 2023-03-02 18:10 | 30 | 1:12 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P23030200163 | 1st_after_momentary | Animals | Include | Include | Wildlife | 72 | 2023-03-02 | 2160 | keep | 0 | Mar | 2023 | 0.0014712 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-02 17:03 | 2023-03-03 11:40 | 150 | 18:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M23030200267 | New_Event | Primary Wire Break | Include | Include | Equipment | 1117 | 2023-03-02 | 167550 | keep | 0 | Mar | 2023 | 0.11412 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2023-03-02 17:08 | 2023-03-02 20:42 | 7 | 3:34 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5 KVA X 37.5 KVA AVERIADO | R23030200051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 214 | 2023-03-02 | 1498 | keep | 0 | Mar | 2023 | 0.0010203 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-03-02 17:35 | 2023-03-02 19:08 | 1 | 1:33 | P | ANIMAL | 1 X 50 EN RISER PAJARO CRUZO FASE | P23030200167 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-03-02 | 93 | keep | 0 | Mar | 2023 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-02 17:41 | 2023-03-02 20:00 | 60 | 2:19 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CL SE REPARO NEUTRAL PRIMARIO | M23030200287 | New_Event | Primary Wire Break | Include | Include | Equipment | 139 | 2023-03-02 | 8340 | keep | 0 | Mar | 2023 | 0.0056803 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-03-02 17:44 | 2023-03-02 18:19 | 25 | 0:35 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L VEHICULO IMPACTO POSTE DE CEMENTO Y PROVOCO QUE SE FUNDIERA C/L | C23030200106 | New_Event | Damage From Public | Include | Include | Public | 35 | 2023-03-02 | 875 | keep | 0 | Mar | 2023 | 0.00059596 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-03-02 18:11 | 2023-03-02 19:05 | 11 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIR XMR Y SE REPARO BAJANTES | B23030200129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2023-03-02 | 594 | keep | 0 | Mar | 2023 | 0.00040457 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
GUAYAMA | 2023-03-02 18:36 | 2023-03-02 18:37 | 464 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | P23030200172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-02 | 464 | keep | 0 | Mar | 2023 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2023-03-02 18:37 | 2023-03-02 20:15 | 25 | 1:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23030200177 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-03-02 | 2450 | keep | 0 | Mar | 2023 | 0.0016687 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-03-02 19:29 | 2023-03-02 23:15 | 300 | 3:46 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN C/L SE ENCONTRO PUENTE ABIERTO | C23030200109 | New_Event | Primary Wire Break | Include | Include | Equipment | 226 | 2023-03-02 | 67800 | keep | 0 | Mar | 2023 | 0.046178 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2023-03-02 20:13 | 2023-03-02 21:52 | 250 | 1:39 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23030200159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-03-02 | 24750 | keep | 0 | Mar | 2023 | 0.016857 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-03-02 20:48 | 2023-03-02 22:55 | 12 | 2:07 | P | DESGANCHE | 1 X 50 EN C/L 1 X 40 EN RISER 1 X 40 EN TRANSCLOSURE A CAUSA DE ENRREDADERA EN EL GABINETE SE QUEDO FUERA WENDYS YA QUE SU TRANSCLOSURE ESTABA CERRADO | B23030200166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-03-02 | 1524 | keep | 0 | Mar | 2023 | 0.001038 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-03-02 21:21 | 2023-03-03 10:48 | 3 | 13:27 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO, SE TRANSFIRIO LAS CARGAS A TRANSFORMADOR CERCANO. | C23030200120 | New_Event | Service Transformer Failure | Include | Include | Equipment | 807 | 2023-03-02 | 2421 | keep | 0 | Mar | 2023 | 0.0016489 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-03-02 23:15 | 2023-03-03 16:00 | 28 | 16:45 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE CERRO PUENTE PRIMARIO DE LINEA A LINEA | C23030300006 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1005 | 2023-03-02 | 28140 | keep | 0 | Mar | 2023 | 0.019166 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-02 23:38 | 2023-03-03 08:23 | 15 | 8:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030200088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 525 | 2023-03-02 | 7875 | keep | 0 | Mar | 2023 | 0.0053636 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-03-03 00:20 | 2023-03-03 00:21 | 1835 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-03 | 1835 | keep | 0 | Mar | 2023 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
VEGA BAJA | 2023-03-03 00:29 | 2023-03-03 06:57 | 30 | 6:28 | P | ANIMAL | 1 X 30 CRUCE POR AVE | B23030300001 | New_Event | Animals | Include | Include | Wildlife | 388 | 2023-03-03 | 11640 | keep | 0 | Mar | 2023 | 0.007928 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-03-03 05:39 | 2023-03-03 09:31 | 25 | 3:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23030300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2023-03-03 | 5800 | keep | 0 | Mar | 2023 | 0.0039504 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-03-03 05:47 | 2023-03-03 11:30 | 10 | 5:43 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23030300005 | New_Event | Primary Wire Break | Include | Include | Equipment | 343 | 2023-03-03 | 3430 | keep | 0 | Mar | 2023 | 0.0023362 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-03 06:56 | 2023-03-03 11:15 | 88 | 4:19 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S23030300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-03-03 | 22792 | keep | 0 | Mar | 2023 | 0.015524 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
CAGUAS | 2023-03-03 07:02 | 2023-03-03 09:23 | 7 | 2:21 | P | DESGANCHE | 1 X 50 DESGANCHE | C23030300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-03-03 | 987 | keep | 0 | Mar | 2023 | 0.00067224 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-03 07:35 | 2023-03-03 09:33 | 101 | 1:58 | P | SOBRECARGA | 1 X 50 EN C/L POR CARGA | B23030300014 | New_Event | Trip Due To Overload | Include | Include | Other | 118 | 2023-03-03 | 11918 | keep | 0 | Mar | 2023 | 0.0081173 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
PONCE | 2023-03-03 07:57 | 2023-03-03 07:58 | 3744 | 0:01 | T | ANIMAL | RECIERRE | P23030300029 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-03 | 3744 | keep | 0 | Mar | 2023 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2023-03-03 07:58 | 2023-03-03 12:29 | 40 | 4:31 | P | ANIMAL | SE CAMBIO PIN Y SE VISTIO 1 X 65 EN CORTE DE LINEA POR AVE | P23030300030 | 1st_after_momentary | Animals | Include | Include | Wildlife | 271 | 2023-03-03 | 10840 | keep | 0 | Mar | 2023 | 0.0073831 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-03-03 08:01 | 2023-03-03 10:56 | 90 | 2:55 | P | DESGANCHE | 1 X 40 C/L 1 X 25 EN C/L DESGANCHE | R23030300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-03-03 | 15750 | keep | 0 | Mar | 2023 | 0.010727 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-03-03 08:04 | 2023-03-03 11:56 | 75 | 3:52 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE PRIMARIO Y SE REEMPLAZO CAJA PRIMARIA | B23030300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-03-03 | 17400 | keep | 0 | Mar | 2023 | 0.011851 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2023-03-03 08:11 | 2023-03-03 11:06 | 53 | 2:55 | P | FUEGO | SE ABRIO PUENTES Y 1 X 50 EN CORTE DE LINEA EN FID 10232241 POR 2 POSTES PRIMARIOS PARTIDOS INTERIOR 47 CLIENTES QUEDAN SIN SERVICIO SE HACE EVENTO P23030300071 | P23030300031 | New_Event | Fire | Include | Include | Public | 175 | 2023-03-03 | 9275 | keep | 0 | Mar | 2023 | 0.0063172 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
FAJARDO | 2023-03-03 08:27 | 2023-03-03 11:57 | 1 | 3:30 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN RISER CLIENTE REPUSO 4 X 80 EN SUBEST, PRIVADA | R23030300005 | New_Event | Primary Wire Break | Include | Include | Equipment | 210 | 2023-03-03 | 210 | keep | 0 | Mar | 2023 | 0.00014303 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-03 08:33 | 2023-03-03 09:30 | 2 | 0:57 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23030300008 | New_Event | Animals | Include | Include | Wildlife | 57 | 2023-03-03 | 114 | keep | 0 | Mar | 2023 | 7.7645e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-03-03 08:37 | 2023-03-03 10:02 | 53 | 1:25 | P | DESGANCHE | 1 X 40 EN C/L Y 1 X 25 EN C/L DESGANCHE | R23030300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-03-03 | 4505 | keep | 0 | Mar | 2023 | 0.0030683 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BAYAMON | 2023-03-03 08:51 | 2023-03-03 10:35 | 68 | 1:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L PORTA FUSIBLE QUEMADO | B23030300024 | New_Event | Cutout Failure | Include | Include | Equipment | 104 | 2023-03-03 | 7072 | keep | 0 | Mar | 2023 | 0.0048167 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
PONCE | 2023-03-03 08:57 | 2023-03-03 08:58 | 2696 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23030300040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-03 | 2696 | keep | 0 | Mar | 2023 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
BAYAMON | 2023-03-03 09:00 | 2023-03-03 10:52 | 2466 | 1:52 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA PARA REPARAR PUENTE ABIERTO BY-230303-01 | S23030300048 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2023-03-03 | 276192 | keep | 0 | Mar | 2023 | 0.18811 | 0.0016796 | Sustained | FALSE | FALSE | Not_TMED_Event | 2466
MAYAGÃœEZ | 2023-03-03 09:02 | 2023-03-03 13:04 | 80 | 4:02 | P | ANIMAL | 1 X 100 Y 1 X 80 EN CORTES DE LINEA IGUANA CRUZO LINEAS | M23030300025 | New_Event | Animals | Include | Include | Wildlife | 242 | 2023-03-03 | 19360 | keep | 0 | Mar | 2023 | 0.013186 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-03-03 09:03 | 2023-03-03 11:44 | 50 | 2:41 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE LEVANTO CONDUCTOR PRIMARIO | B23030300030 | New_Event | Primary Wire Break | Include | Include | Equipment | 161 | 2023-03-03 | 8050 | keep | 0 | Mar | 2023 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-03-03 09:03 | 2023-03-03 12:45 | 15 | 3:42 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 22-003-HC FIONA PARA REEMPLAZO DE POSTE PRIMARIO Y RELOCALIZAR TRANSFORMADOR A POSTE NUEVO. 22-003-HCFIONA | C23030300018 | New_Event | Primary Pole Failure | Include | Include | Equipment | 222 | 2023-03-03 | 3330 | keep | 0 | Mar | 2023 | 0.002268 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-03 09:05 | 2023-03-03 15:18 | 5 | 6:13 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REALIZO DESGANCHE SECUNDARIO. | B23030300026 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 373 | 2023-03-03 | 1865 | keep | 0 | Mar | 2023 | 0.0012702 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-03-03 09:10 | 2023-03-03 12:45 | 10 | 3:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23030300021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 215 | 2023-03-03 | 2150 | keep | 0 | Mar | 2023 | 0.0014644 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-03 09:25 | 2023-03-03 11:35 | 13 | 2:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | S23030300038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-03-03 | 1690 | keep | 0 | Mar | 2023 | 0.0011511 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2023-03-03 09:30 | 2023-03-03 11:35 | 2 | 2:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030300019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-03-03 | 250 | keep | 0 | Mar | 2023 | 0.00017027 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-03-03 09:33 | 2023-03-03 12:37 | 4 | 3:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR CON LIQUEO DE 25KVA POR 25KVA | R23030300016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 184 | 2023-03-03 | 736 | keep | 0 | Mar | 2023 | 0.00050129 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-03-03 09:35 | 2023-03-03 09:37 | 2106 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO 2305-03 Y SE CERRO POR SCADA | R2303030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-03 | 4212 | keep | 0 | Mar | 2023 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CAGUAS | 2023-03-03 09:37 | 2023-03-03 12:06 | 46 | 2:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C23030300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-03-03 | 6854 | keep | 0 | Mar | 2023 | 0.0046682 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
BAYAMON | 2023-03-03 09:40 | 2023-03-03 12:28 | 5 | 2:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23030300038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 168 | 2023-03-03 | 840 | keep | 0 | Mar | 2023 | 0.00057212 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-03 09:47 | 2023-03-03 09:49 | 2891 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | R23030300021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-03 | 5782 | keep | 0 | Mar | 2023 | 0.0039381 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
CANOVANAS | 2023-03-03 09:47 | 2023-03-03 09:50 | 99 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1647-08 | R23030300020 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-03 | 297 | keep | 0 | Mar | 2023 | 0.00020229 | 6.7428e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 99
CANOVANAS | 2023-03-03 09:47 | 2023-03-03 09:50 | 1474 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA LLEVANDO 1647-06 | R23030300020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-03 | 4422 | keep | 0 | Mar | 2023 | 0.0030118 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
CAGUAS | 2023-03-03 09:49 | 2023-03-03 10:10 | 22 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C23030300013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2023-03-03 | 462 | keep | 0 | Mar | 2023 | 0.00031467 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-03-03 10:26 | 2023-03-03 12:13 | 15 | 1:47 | P | PROBLEMA DEL CLIENTE | 1 X 80 EN SU-6 PROBLEMAS CON SUBESTACION DE WENDYS | B23030300049 | New_Event | Customer-Related Interruption | Include | Include | Public | 107 | 2023-03-03 | 1605 | keep | 0 | Mar | 2023 | 0.0010932 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-03-03 10:41 | 2023-03-03 14:27 | 6 | 3:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23030300022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2023-03-03 | 1356 | keep | 0 | Mar | 2023 | 0.00092357 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-03 10:52 | 2023-03-03 11:33 | 848 | 0:41 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO Y SE REPARO PUENTE ABIERTO BY-230303-01 | S23030300048 | New_Event | Primary Wire Break | Include | Include | Equipment | 41 | 2023-03-03 | 34768 | keep | 0 | Mar | 2023 | 0.02368 | 0.00057757 | Sustained | FALSE | FALSE | Not_TMED_Event | 848
PONCE | 2023-03-03 11:06 | 2023-03-04 21:43 | 47 | 34:37 | P | FUEGO | SE REEMPLAZARON DOS POSTES PRIMARIOS PARTIDOS POR FUEGO NATURAL FORESTAL | P23030300071 | New_Event | Fire | Include | Include | Public | 2077 | 2023-03-03 | 97619 | keep | 0 | Mar | 2023 | 0.066488 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
YAUCO | 2023-03-03 11:09 | 2023-03-03 15:14 | 50 | 4:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LINEA | P23030300069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2023-03-03 | 12250 | keep | 0 | Mar | 2023 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-03 11:16 | 2023-03-03 14:23 | 9 | 3:07 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE XMR 37.5KVA X 37.5KVA | B23030300065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 187 | 2023-03-03 | 1683 | keep | 0 | Mar | 2023 | 0.0011463 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-03-03 11:26 | 2023-03-03 12:20 | 6 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23030300027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2023-03-03 | 324 | keep | 0 | Mar | 2023 | 0.00022067 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-03-03 11:30 | 2023-03-03 12:30 | 6 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23030300028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-03-03 | 360 | keep | 0 | Mar | 2023 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-03-03 12:06 | 2023-03-03 12:44 | 14 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23030300039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2023-03-03 | 532 | keep | 0 | Mar | 2023 | 0.00036234 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2023-03-03 12:24 | 2023-03-03 12:25 | 1109 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23030300078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-03 | 1109 | keep | 0 | Mar | 2023 | 0.00075533 | 0.00075533 | Momentary | FALSE | FALSE | Not_TMED_Event | 1109
BAYAMON | 2023-03-03 12:28 | 2023-03-03 14:06 | 35 | 1:38 | P | DESGANCHE | 1 X 25 EN C/L SE REALIZO DESGANCHE | B23030300077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-03-03 | 3430 | keep | 0 | Mar | 2023 | 0.0023362 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-03-03 12:36 | 2023-03-03 16:14 | 80 | 3:38 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO FASE | S23030300098 | New_Event | Animals | Include | Include | Wildlife | 218 | 2023-03-03 | 17440 | keep | 0 | Mar | 2023 | 0.011878 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-03-03 12:40 | 2023-03-03 17:20 | 14 | 4:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR 200 PIES SECUNDARIA | S23030300100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 280 | 2023-03-03 | 3920 | keep | 0 | Mar | 2023 | 0.0026699 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2023-03-03 12:49 | 2023-03-03 12:50 | 1262 | 0:01 | T | DESGANCHE | RECIERRE | P23030300085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-03 | 1262 | keep | 0 | Mar | 2023 | 0.00085954 | 0.00085954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1262
PONCE | 2023-03-03 12:50 | 2023-03-03 17:10 | 350 | 4:20 | P | DESGANCHE | 1 X 40, 3 X 65 EN DISTINTOS CORTES DE LINEA POR DESGANCHE | P23030300092 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 260 | 2023-03-03 | 91000 | keep | 0 | Mar | 2023 | 0.06198 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2023-03-03 12:57 | 2023-03-03 12:58 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-03 | 4533 | keep | 0 | Mar | 2023 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
PONCE | 2023-03-03 12:58 | 2023-03-03 13:53 | 100 | 0:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P23030300087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-03-03 | 5500 | keep | 0 | Mar | 2023 | 0.003746 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-03-03 13:05 | 2023-03-03 16:30 | 25 | 3:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN CORTE DE LINEA | P23030300124 | New_Event | Primary Wire Break | Include | Include | Equipment | 205 | 2023-03-03 | 5125 | keep | 0 | Mar | 2023 | 0.0034906 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-03-03 13:14 | 2023-03-03 15:25 | 35 | 2:11 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | C23030300062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-03-03 | 4585 | keep | 0 | Mar | 2023 | 0.0031228 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-03-03 13:15 | 2023-03-03 18:00 | 60 | 4:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PARTIDA | A23030300042 | New_Event | Primary Wire Break | Include | Include | Equipment | 285 | 2023-03-03 | 17100 | keep | 0 | Mar | 2023 | 0.011647 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-03 13:57 | 2023-03-03 15:21 | 2422 | 1:24 | T | NO SE REPORTO CAUSA | SE ENCONTRO ABIERTO SE PATRULLO Y SE CERRO LOCALMENTE QUEDO EN SERVICIO | S23030300140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2023-03-03 | 203448 | keep | 0 | Mar | 2023 | 0.13857 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
SAN JUAN | 2023-03-03 14:00 | 2023-03-03 15:38 | 10 | 1:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REMPLAZAR CONECTORES Y NEUTRAL SECUNDARIO | S23030300135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 98 | 2023-03-03 | 980 | keep | 0 | Mar | 2023 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-03 14:02 | 2023-03-03 18:40 | 30 | 4:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23030300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2023-03-03 | 8340 | keep | 0 | Mar | 2023 | 0.0056803 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-03-03 14:05 | 2023-03-03 16:47 | 10 | 2:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR CON LIQUEO DE 37.5 KVA X 37.5 KVA | R23030300044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 162 | 2023-03-03 | 1620 | keep | 0 | Mar | 2023 | 0.0011034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-03 14:38 | 2023-03-03 17:55 | 35 | 3:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO BAJANTE DE LINEA A CAJA Y SE REEMPLAZO CAJA PRIMARIA 1 X 100 EN RISER | B23030300095 | New_Event | Cutout Failure | Include | Include | Equipment | 197 | 2023-03-03 | 6895 | keep | 0 | Mar | 2023 | 0.0046962 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-03-03 14:44 | 2023-03-03 19:25 | 3 | 4:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 10 EM XMR Y SE REPARO LINEA SECUNDARIA EVENTO TRANSFERIDO DE ARECIBO | A23030300051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 281 | 2023-03-03 | 843 | keep | 0 | Mar | 2023 | 0.00057416 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-03 14:50 | 2023-03-03 17:10 | 115 | 2:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE CORTE DE LINEA PARA REMPLAZAR 300 PIES DE SECUNDARIA TRAMO CORRE TRAS PATIO Y POR ENCIMA DE TRANSFORMADORES | S23030300112 | New_Event | Secondary Wire Break | Include | Include | Equipment | 140 | 2023-03-03 | 16100 | keep | 0 | Mar | 2023 | 0.010966 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
FAJARDO | 2023-03-03 14:50 | 2023-03-03 16:24 | 28 | 1:34 | P | DESGANCHE | 1 X 40 EN C/L | R23030300050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-03-03 | 2632 | keep | 0 | Mar | 2023 | 0.0017926 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
GUAYAMA | 2023-03-03 14:50 | 2023-03-03 16:02 | 20 | 1:12 | P | ANIMAL | 1 X 30 EN TRANSFORMADOR PAJARO CRUZO FASE | P23030300123 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-03-03 | 1440 | keep | 0 | Mar | 2023 | 0.00098078 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-03-03 14:50 | 2023-03-03 17:47 | 12 | 2:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | M23030300096 | New_Event | Cutout Failure | Include | Include | Equipment | 177 | 2023-03-03 | 2124 | keep | 0 | Mar | 2023 | 0.0014466 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-03 15:15 | 2023-03-03 15:17 | 476 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23030300093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-03 | 952 | keep | 0 | Mar | 2023 | 0.0006484 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-03-03 15:15 | 2023-03-03 15:17 | 1655 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23030300093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-03 | 3310 | keep | 0 | Mar | 2023 | 0.0022544 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-03-03 15:15 | 2023-03-03 15:17 | 361 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23030300093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-03 | 722 | keep | 0 | Mar | 2023 | 0.00049175 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-03-03 15:15 | 2023-03-03 15:17 | 2842 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23030300093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-03 | 5684 | keep | 0 | Mar | 2023 | 0.0038713 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-03-03 15:15 | 2023-03-03 15:17 | 1702 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23030300094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-03 | 3404 | keep | 0 | Mar | 2023 | 0.0023184 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-03-03 15:15 | 2023-03-03 15:17 | 918 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23030300094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-03 | 1836 | keep | 0 | Mar | 2023 | 0.0012505 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-03-03 15:15 | 2023-03-03 15:17 | 1725 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23030300095 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-03 | 3450 | keep | 0 | Mar | 2023 | 0.0023498 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
SAN JUAN | 2023-03-03 15:21 | 2023-03-03 18:06 | 285 | 2:45 | P | NO SE REPORTO CAUSA | 1 X 80 EN PROVISIONAL AEREO NO CAUSA | S230303158 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 165 | 2023-03-03 | 47025 | keep | 0 | Mar | 2023 | 0.032029 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-03 15:41 | 2023-03-03 17:05 | 100 | 1:24 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23030300112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-03-03 | 8400 | keep | 0 | Mar | 2023 | 0.0057212 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-03-03 15:50 | 2023-03-03 16:58 | 6 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23030300113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2023-03-03 | 408 | keep | 0 | Mar | 2023 | 0.00027789 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-03-03 15:57 | 2023-03-03 17:13 | 57 | 1:16 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | C23030300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-03-03 | 4332 | keep | 0 | Mar | 2023 | 0.0029505 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
VEGA BAJA | 2023-03-03 15:58 | 2023-03-03 17:40 | 25 | 1:42 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A23030300061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-03-03 | 2550 | keep | 0 | Mar | 2023 | 0.0017368 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-03-03 16:09 | 2023-03-03 17:05 | 41 | 0:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTE BRISA | P23030300167 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 56 | 2023-03-03 | 2296 | keep | 0 | Mar | 2023 | 0.0015638 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BARRANQUITAS | 2023-03-03 16:10 | 2023-03-03 16:40 | 79 | 0:30 | P | CAUSAS EXTERNAS | SE ABRIO C/L POR EMERGENCIA TENSOR PEGADO DE CAJA. RELACIONADO A EVENTO C23030300084 SECUNDARIA CAMION IMPACTO CABLES Y PARTIO POSTE SECUNDARIO | C23030300104 | New_Event | Damage From Public | Include | Include | Public | 30 | 2023-03-03 | 2370 | keep | 0 | Mar | 2023 | 0.0016142 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
YAUCO | 2023-03-03 16:11 | 2023-03-03 18:34 | 20 | 2:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M23030300108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2023-03-03 | 2860 | keep | 0 | Mar | 2023 | 0.0019479 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-03 16:18 | 2023-03-03 18:08 | 297 | 1:50 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN C/L DESGANCHE | S23030300159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-03-03 | 32670 | keep | 0 | Mar | 2023 | 0.022251 | 0.00020229 | Sustained | FALSE | FALSE | Not_TMED_Event | 297
HUMACAO | 2023-03-03 16:31 | 2023-03-03 18:30 | 2 | 1:59 | P | TRANSFORMADOR AVERIADO | TRTANFORMADOR AVERIADO SE DEJARON LOS CLIENTES A 120 REFERIDO PARA REEMPLAZO DE XMR | C23030300108 | New_Event | Service Transformer Failure | Include | Include | Equipment | 119 | 2023-03-03 | 238 | keep | 0 | Mar | 2023 | 0.0001621 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-03-03 16:40 | 2023-03-03 18:10 | 7 | 1:30 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA RELOCALIZAR SECUNDARIA A POSTE EXISTENTE Y SE REEMPLAZO LINEA SECUNDARIA X CAMION IMPACTO CABLES Y PARTIO POSTE SECUNDARIO | C23030300084 | Partial_restoration | Damage From Public | Include | Include | Public | 90 | 2023-03-03 | 630 | keep | 0 | Mar | 2023 | 0.00042909 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-03 16:51 | 2023-03-03 18:05 | 60 | 1:14 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M23030300112 | New_Event | Animals | Include | Include | Wildlife | 74 | 2023-03-03 | 4440 | keep | 0 | Mar | 2023 | 0.0030241 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-03-03 16:53 | 2023-03-03 18:50 | 391 | 1:57 | P | DESGANCHE | 2 X 140 EN C/L Y DESGANCHE | C23030300113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-03-03 | 45747 | keep | 0 | Mar | 2023 | 0.031158 | 0.00026631 | Sustained | FALSE | FALSE | Not_TMED_Event | 391
GUAYAMA | 2023-03-03 17:00 | 2023-03-03 18:21 | 34 | 1:21 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN CORTE DE LINEA | P23030300168 | New_Event | Primary Wire Break | Include | Include | Equipment | 81 | 2023-03-03 | 2754 | keep | 0 | Mar | 2023 | 0.0018757 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
MAYAGÃœEZ | 2023-03-03 17:27 | 2023-03-03 18:42 | 1337 | 1:15 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE HIZO PRUEBA MANUALMENTE NO DIO INDICACION DE ABIERTO | M23030300131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2023-03-03 | 100275 | keep | 0 | Mar | 2023 | 0.068297 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
CAGUAS | 2023-03-03 17:29 | 2023-03-03 19:08 | 60 | 1:39 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | C23030300126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-03-03 | 5940 | keep | 0 | Mar | 2023 | 0.0040457 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-03 17:31 | 2023-03-03 20:47 | 112 | 3:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON AISLADORES Y 1 X 50 EN C/L | C23030300127 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 196 | 2023-03-03 | 21952 | keep | 0 | Mar | 2023 | 0.014951 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
ARECIBO | 2023-03-03 17:39 | 2023-03-03 21:49 | 10 | 4:10 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO SE REPORTO CAUSA | A23030300072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2023-03-03 | 2500 | keep | 0 | Mar | 2023 | 0.0017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-03 17:45 | 2023-03-03 18:10 | 6 | 0:25 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR PARA REPARAR PEDESTAL SOTERRADO AVERIADO | A23030300071 | New_Event |  |  |  |  | 25 | 2023-03-03 | 150 | keep | 0 | Mar | 2023 | 0.00010216 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-03-03 17:47 | 2023-03-03 19:45 | 10 | 1:58 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO BAMBU | A23030300073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-03-03 | 1180 | keep | 0 | Mar | 2023 | 0.00080369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-03 18:26 | 2023-03-03 21:49 | 5 | 3:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23030300187 | New_Event | Secondary Wire Break | Include | Include | Equipment | 203 | 2023-03-03 | 1015 | keep | 0 | Mar | 2023 | 0.00069131 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-03 18:26 | 2023-03-03 18:27 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-03 | 1362 | keep | 0 | Mar | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
HUMACAO | 2023-03-03 18:30 | 2023-03-03 20:00 | 89 | 1:30 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | C23030300136 | New_Event | Animals | Include | Include | Wildlife | 90 | 2023-03-03 | 8010 | keep | 0 | Mar | 2023 | 0.0054556 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
PONCE | 2023-03-03 18:31 | 2023-03-03 18:35 | 5063 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | P23030300180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-03 | 20252 | keep | 0 | Mar | 2023 | 0.013794 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
PONCE | 2023-03-03 18:35 | 2023-03-03 20:38 | 100 | 2:03 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA 1 X 30 EN SU C , SE ELIMINO PARARRAYO ACTIVADO | P23030300187 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 123 | 2023-03-03 | 12300 | keep | 0 | Mar | 2023 | 0.0083775 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-03 18:42 | 2023-03-03 20:53 | 145 | 2:11 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23030300065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-03-03 | 18995 | keep | 0 | Mar | 2023 | 0.012937 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
ARECIBO | 2023-03-03 18:49 | 2023-03-03 21:35 | 100 | 2:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23030300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-03-03 | 16600 | keep | 0 | Mar | 2023 | 0.011306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-03-03 18:57 | 2023-03-03 21:17 | 10 | 2:20 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | A23030300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2023-03-03 | 1400 | keep | 0 | Mar | 2023 | 0.00095353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-03 19:08 | 2023-03-03 19:09 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-03 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
SAN JUAN | 2023-03-03 19:10 | 2023-03-03 21:26 | 4 | 2:16 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE SECUNDARIO | S23030300189 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 136 | 2023-03-03 | 544 | keep | 0 | Mar | 2023 | 0.00037052 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-03-03 20:46 | 2023-03-04 09:30 | 50 | 12:44 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23030300195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 764 | 2023-03-03 | 38200 | keep | 0 | Mar | 2023 | 0.026018 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-03 22:14 | 2023-03-04 03:29 | 15 | 5:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR Y SE REMPLAZO CAJA PRIMARIA | B23030300128 | New_Event | Cutout Failure | Include | Include | Equipment | 315 | 2023-03-03 | 4725 | keep | 0 | Mar | 2023 | 0.0032182 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-03-03 23:27 | 2023-03-04 09:45 | 50 | 10:18 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23030300076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 618 | 2023-03-03 | 30900 | keep | 0 | Mar | 2023 | 0.021046 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-03-04 00:01 | 2023-03-04 09:35 | 11 | 9:34 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN RISER SE SECCIONALIZAO AVERIA SOTERRADA ABIERTO DE T-11 @ T-13 | A23030400004 | New_Event | UG Cable Fault | Include | Include | Equipment | 574 | 2023-03-04 | 6314 | keep | 0 | Mar | 2023 | 0.0043004 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2023-03-04 03:45 | 2023-03-04 08:38 | 11 | 4:53 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23030400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2023-03-04 | 3223 | keep | 0 | Mar | 2023 | 0.0021952 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2023-03-04 05:51 | 2023-03-04 08:54 | 5 | 3:03 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | R23030400003 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 183 | 2023-03-04 | 915 | keep | 0 | Mar | 2023 | 0.0006232 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-04 06:03 | 2023-03-04 09:18 | 10 | 3:15 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23030400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-03-04 | 1950 | keep | 0 | Mar | 2023 | 0.0013281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-03-04 06:33 | 2023-03-04 11:21 | 40 | 4:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23030400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2023-03-04 | 11520 | keep | 0 | Mar | 2023 | 0.0078462 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-03-04 06:41 | 2023-03-04 12:09 | 5 | 5:28 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA CRUZADA | A23030400007 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 328 | 2023-03-04 | 1640 | keep | 0 | Mar | 2023 | 0.001117 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-03-04 07:24 | 2023-03-04 13:58 | 12 | 6:34 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5KVA POR UNO DE IGUAL CAPACIDAD | R23030400005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 394 | 2023-03-04 | 4728 | keep | 0 | Mar | 2023 | 0.0032202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-03-04 07:35 | 2023-03-04 10:36 | 15 | 3:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN PROVISIONAL | R23030400006 | New_Event | Primary Wire Break | Include | Include | Equipment | 181 | 2023-03-04 | 2715 | keep | 0 | Mar | 2023 | 0.0018492 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-03-04 07:36 | 2023-03-04 07:37 | 800 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 800 CLIENTES POR EL 3205-07 | C23030400006 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-04 | 800 | keep | 0 | Mar | 2023 | 0.00054488 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
CAGUAS | 2023-03-04 07:36 | 2023-03-04 07:37 | 3026 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1608 CLIENTES POR EL 3201-01 Y LLEVA 800 CLIENTES DEL 2603-08 | C23030400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-04 | 3026 | keep | 0 | Mar | 2023 | 0.002061 | 0.002061 | Momentary | FALSE | FALSE | Not_TMED_Event | 3026
CANOVANAS | 2023-03-04 07:50 | 2023-03-04 07:51 | 1380 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23030400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-04 | 1380 | keep | 0 | Mar | 2023 | 0.00093991 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
BARRANQUITAS | 2023-03-04 08:26 | 2023-03-04 13:47 | 36 | 5:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23030400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2023-03-04 | 11556 | keep | 0 | Mar | 2023 | 0.0078707 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-03-04 08:40 | 2023-03-04 08:41 | 1381 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR SU CARGA POR 1204-01 | S23030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-04 | 1381 | keep | 0 | Mar | 2023 | 0.00094059 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2023-03-04 08:42 | 2023-03-04 10:56 | 100 | 2:14 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN PROVISIONAL PUENTE ABIERTO DE LINEA A CAJA DE PROVISIONAL | S23030400007 | New_Event | Primary Wire Break | Include | Include | Equipment | 134 | 2023-03-04 | 13400 | keep | 0 | Mar | 2023 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-04 08:45 | 2023-03-04 11:00 | 100 | 2:15 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | S23030400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-03-04 | 13500 | keep | 0 | Mar | 2023 | 0.0091948 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-03-04 08:45 | 2023-03-04 10:15 | 10 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23030400001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-03-04 | 900 | keep | 0 | Mar | 2023 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-04 09:05 | 2023-03-04 11:27 | 10 | 2:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REMPLAZO 20 PIES DE SECUNDARIA TRAS PATIO Y 2 TOMAS | S23030400012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 142 | 2023-03-04 | 1420 | keep | 0 | Mar | 2023 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-03-04 09:10 | 2023-03-04 11:24 | 28 | 2:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | C23030400011 | New_Event | Cutout Failure | Include | Include | Equipment | 134 | 2023-03-04 | 3752 | keep | 0 | Mar | 2023 | 0.0025555 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
GUAYAMA | 2023-03-04 09:15 | 2023-03-04 10:00 | 2 | 0:45 | P | OTRAS CAUSAS | SE ABRE CORTE DE LINEA PARA CAMBIAR STANDAR EN CORTE DE LINEA ASI EVITAR QUE PAJARO CRUCE FASE | P23030400009 | New_Event | Other Causes | Include | Include | Other | 45 | 2023-03-04 | 90 | keep | 0 | Mar | 2023 | 6.1299e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-04 09:24 | 2023-03-04 13:26 | 41 | 4:02 | P | ANIMAL | 1 X 20 EN PROVISIONAL AVE CRUZO LINEA | B23030400019 | New_Event | Animals | Include | Include | Wildlife | 242 | 2023-03-04 | 9922 | keep | 0 | Mar | 2023 | 0.0067578 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CANOVANAS | 2023-03-04 09:31 | 2023-03-04 12:10 | 50 | 2:39 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L DESGANCHE | R23030400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2023-03-04 | 7950 | keep | 0 | Mar | 2023 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-03-04 09:35 | 2023-03-04 18:20 | 4 | 8:45 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO | A23030400004 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 525 | 2023-03-04 | 2100 | keep | 0 | Mar | 2023 | 0.0014303 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-03-04 09:41 | 2023-03-04 13:23 | 14 | 3:42 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR CRUCE POR AVE | C23030400016 | New_Event | Animals | Include | Include | Wildlife | 222 | 2023-03-04 | 3108 | keep | 0 | Mar | 2023 | 0.0021168 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-03-04 09:46 | 2023-03-04 13:47 | 1 | 4:01 | S | ANIMAL | DISPARO PORTATIL#19 SE FUE A LOCKOUT SE ENCONTRO CULEBRA EN SU-3 PREDIO DE LUMA Y SE CERRO N/O BARRA INSPECCION CON 1346-02 QUE A SU VEZ ESTA POR 1907-04 | S23030400113 | New_Event | Animals | Include | Include | Wildlife | 241 | 2023-03-04 | 241 | keep | 0 | Mar | 2023 | 0.00016414 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-04 09:46 | 2023-03-04 12:14 | 737 | 2:28 | P | ANIMAL | DISPARO PORTATIL#19 SE FUE A LOCKOUT SE ENCONTRO CULEBRA EN SU-3 PREDIO DE LUMA Y SE PASO 40% DE SU CARGA AL 1907-04 | S23030400113 | New_Event | Animals | Include | Include | Wildlife | 148 | 2023-03-04 | 109076 | keep | 0 | Mar | 2023 | 0.074291 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2023-03-04 09:46 | 2023-03-04 12:49 | 2422 | 3:03 | T | ANIMAL | DISPARO PORTATIL#19 SE FUE A LOCKOUT SE ENCONTRO CULEBRA EN SU-3 PREDIO DE LUMA Y SE PASO CARGA AL 1908-03 | S23030400113 | New_Event | Animals | Include | Include | Wildlife | 183 | 2023-03-04 | 443226 | keep | 0 | Mar | 2023 | 0.30188 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
VEGA BAJA | 2023-03-04 10:00 | 2023-03-04 10:40 | 8 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A23030400005 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-03-04 | 320 | keep | 0 | Mar | 2023 | 0.00021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-03-04 10:45 | 2023-03-04 13:24 | 50 | 2:39 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO FASE | P23030400021 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-03-04 | 7950 | keep | 0 | Mar | 2023 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-04 10:54 | 2023-03-04 11:46 | 60 | 0:52 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23030400114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2023-03-04 | 3120 | keep | 0 | Mar | 2023 | 0.002125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-03-04 10:56 | 2023-03-04 16:16 | 25 | 5:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23030400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2023-03-04 | 8000 | keep | 0 | Mar | 2023 | 0.0054488 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-03-04 11:06 | 2023-03-04 12:56 | 28 | 1:50 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23030400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2023-03-04 | 3080 | keep | 0 | Mar | 2023 | 0.0020978 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2023-03-04 11:16 | 2023-03-04 15:35 | 14 | 4:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO NO FUNDIO | S23030400123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 259 | 2023-03-04 | 3626 | keep | 0 | Mar | 2023 | 0.0024697 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2023-03-04 11:23 | 2023-03-04 11:40 | 6 | 0:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C23030400021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 17 | 2023-03-04 | 102 | keep | 0 | Mar | 2023 | 6.9472e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-03-04 11:24 | 2023-03-04 14:59 | 31 | 3:35 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU 22 HACIA T 58 AVERIA NUEVA DE T58 @ T58A | C23030400033 | New_Event | UG Cable Fault | Include | Include | Equipment | 215 | 2023-03-04 | 6665 | keep | 0 | Mar | 2023 | 0.0045395 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
AGUADILLA | 2023-03-04 11:25 | 2023-03-04 11:44 | 9 | 0:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23030400004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 19 | 2023-03-04 | 171 | keep | 0 | Mar | 2023 | 0.00011647 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-03-04 11:30 | 2023-03-04 15:42 | 1 | 4:12 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR SE REPARO BUSHING SECUNDARIO | A23030400025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 252 | 2023-03-04 | 252 | keep | 0 | Mar | 2023 | 0.00017164 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-04 11:32 | 2023-03-04 13:53 | 22 | 2:21 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | R23030400031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-03-04 | 3102 | keep | 0 | Mar | 2023 | 0.0021128 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
FAJARDO | 2023-03-04 11:41 | 2023-03-04 13:05 | 65 | 1:24 | P | ANIMAL | 1 X 50 C/L AVE | R23030400032 | New_Event | Animals | Include | Include | Wildlife | 84 | 2023-03-04 | 5460 | keep | 0 | Mar | 2023 | 0.0037188 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
FAJARDO | 2023-03-04 11:50 | 2023-03-04 13:00 | 2 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23030400034 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-03-04 | 140 | keep | 0 | Mar | 2023 | 9.5353e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-04 11:52 | 2023-03-04 14:23 | 206 | 2:31 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23030400028 | New_Event | Animals | Include | Include | Wildlife | 151 | 2023-03-04 | 31106 | keep | 0 | Mar | 2023 | 0.021186 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
PONCE | 2023-03-04 11:55 | 2023-03-04 13:30 | 10 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | E RECONECTO BAJANTE PRIMARIO | P23030400027 | New_Event | Primary Wire Break | Include | Include | Equipment | 95 | 2023-03-04 | 950 | keep | 0 | Mar | 2023 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-03-04 12:02 | 2023-03-04 12:03 | 1952 | 0:01 | T | PROTECCION DEFECTUOSA | RECIERRE | P23030400029 | New_Event | Protection Miscoordination | Include | Include | Other | 1 | 2023-03-04 | 1952 | keep | 0 | Mar | 2023 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
PONCE | 2023-03-04 12:06 | 2023-03-04 13:21 | 50 | 1:15 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P23030400030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-03-04 | 3750 | keep | 0 | Mar | 2023 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-04 12:12 | 2023-03-04 12:13 | 2106 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | R23030400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-04 | 2106 | keep | 0 | Mar | 2023 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
MAYAGÃœEZ | 2023-03-04 12:13 | 2023-03-04 12:14 | 2530 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6008-05 | M23030400024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-04 | 2530 | keep | 0 | Mar | 2023 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2023-03-04 12:13 | 2023-03-04 12:14 | 199 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL INTERRUPTOR 6008-04 EL CUAL LLEVA LA CARGA DEL 6008-05 | M23030400024 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-04 | 199 | keep | 0 | Mar | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-03-04 13:00 | 2023-03-04 17:05 | 50 | 4:05 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR BAJANTE ZAFADO DE CAJA A LINEA | A23030400043 | New_Event | Primary Wire Break | Include | Include | Equipment | 245 | 2023-03-04 | 12250 | keep | 0 | Mar | 2023 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-04 13:11 | 2023-03-04 14:30 | 50 | 1:19 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B23030400035 | New_Event | Animals | Include | Include | Wildlife | 79 | 2023-03-04 | 3950 | keep | 0 | Mar | 2023 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-04 13:12 | 2023-03-04 18:16 | 137 | 5:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 SE REEMPLAZO AISLADOR ROTO | S23030400139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 304 | 2023-03-04 | 41648 | keep | 0 | Mar | 2023 | 0.028366 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-03-04 13:12 | 2023-03-04 18:16 | 760 | 5:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 SE REEMPLAZO AISLADOR ROTO | S23030400139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 304 | 2023-03-04 | 231040 | keep | 0 | Mar | 2023 | 0.15736 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2023-03-04 13:12 | 2023-03-04 18:16 | 4291 | 5:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 SE REEMPLAZO AISLADOR ROTO | S23030400140 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 304 | 2023-03-04 | 1304464 | keep | 0 | Mar | 2023 | 0.88846 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-03-04 13:12 | 2023-03-04 18:16 | 1381 | 5:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 SE REEMPLAZO AISLADOR ROTO | S23030400140 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 304 | 2023-03-04 | 419824 | keep | 0 | Mar | 2023 | 0.28594 | 0.00094059 | Sustained | FALSE | FALSE | Not_TMED_Event | 1381
MAYAGÃœEZ | 2023-03-04 13:19 | 2023-03-04 14:44 | 150 | 1:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23030400030 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 85 | 2023-03-04 | 12750 | keep | 0 | Mar | 2023 | 0.008684 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2023-03-04 13:22 | 2023-03-04 19:49 | 6 | 6:27 | P | ANIMAL | 1 X 10 EN CORTE DE LINEA AVE CRUZO LINEAS | R23030400047 | New_Event | Animals | Include | Include | Wildlife | 387 | 2023-03-04 | 2322 | keep | 0 | Mar | 2023 | 0.0015815 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-03-04 13:48 | 2023-03-04 15:06 | 50 | 1:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23030400042 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-03-04 | 3900 | keep | 0 | Mar | 2023 | 0.0026563 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-04 13:57 | 2023-03-04 15:57 | 8 | 2:00 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | C23030400055 | New_Event | Animals | Include | Include | Wildlife | 120 | 2023-03-04 | 960 | keep | 0 | Mar | 2023 | 0.00065385 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-03-04 14:20 | 2023-03-04 16:30 | 50 | 2:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23030400062 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 130 | 2023-03-04 | 6500 | keep | 0 | Mar | 2023 | 0.0044271 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-04 14:25 | 2023-03-04 17:05 | 35 | 2:40 | P | ANIMAL | 2 X 100 EN C/L CRUCE POR IGUANA | B23030400042 | New_Event | Animals | Include | Include | Wildlife | 160 | 2023-03-04 | 5600 | keep | 0 | Mar | 2023 | 0.0038141 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2023-03-04 14:25 | 2023-03-04 15:50 | 2 | 1:25 | P | DESGANCHE | 2 X 50 EN RISER POR DESGANCHE | P23030400045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-03-04 | 170 | keep | 0 | Mar | 2023 | 0.00011579 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-04 14:35 | 2023-03-04 14:36 | 13 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-04 | 13 | keep | 0 | Mar | 2023 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2023-03-04 14:37 | 2023-03-04 17:35 | 30 | 2:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23030400041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-03-04 | 5340 | keep | 0 | Mar | 2023 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-04 14:38 | 2023-03-04 14:39 | 13 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303040000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-04 | 13 | keep | 0 | Mar | 2023 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-03-04 14:40 | 2023-03-04 17:06 | 55 | 2:26 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | C23030400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-03-04 | 8030 | keep | 0 | Mar | 2023 | 0.0054692 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
GUAYAMA | 2023-03-04 14:45 | 2023-03-04 15:30 | 12 | 0:45 | P | SECUNDARIA/OTROS | SE ABRE TRANSFORMADOR PARA REEMPLAZO DE BARRAS EN PEDESTAL | P23030400040 | New_Event |  |  |  |  | 45 | 2023-03-04 | 540 | keep | 0 | Mar | 2023 | 0.00036779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-04 14:55 | 2023-03-04 18:00 | 30 | 3:05 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M23030400068 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 185 | 2023-03-04 | 5550 | keep | 0 | Mar | 2023 | 0.0037801 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-03-04 14:59 | 2023-03-05 10:17 | 68 | 19:18 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO ENTRE T-58 @ T-T58A | C23030400033 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1158 | 2023-03-04 | 78744 | keep | 0 | Mar | 2023 | 0.053632 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-03-04 15:15 | 2023-03-04 17:33 | 15 | 2:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23030400066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2023-03-04 | 2070 | keep | 0 | Mar | 2023 | 0.0014099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-04 15:17 | 2023-03-04 18:38 | 40 | 3:21 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B23030400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2023-03-04 | 8040 | keep | 0 | Mar | 2023 | 0.005476 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-03-04 15:48 | 2023-03-04 16:46 | 25 | 0:58 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | R23030400056 | New_Event | Primary Wire Break | Include | Include | Equipment | 58 | 2023-03-04 | 1450 | keep | 0 | Mar | 2023 | 0.00098759 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-03-04 15:58 | 2023-03-04 18:55 | 45 | 2:57 | P | ERROR HUMANO | 1 X 65 EN CORTE DE LINEA COMPAÃ‘IA PRIVADA REALIZANDO DESGANCHE CRUZARON FASE | P23030400065 | New_Event | Human Error | Include | Include | Other | 177 | 2023-03-04 | 7965 | keep | 0 | Mar | 2023 | 0.0054249 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-03-04 16:11 | 2023-03-04 19:51 | 1 | 3:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 30 EN RISER Y SE REPARO BAJUANTE SECUNDARIO | B23030400075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 220 | 2023-03-04 | 220 | keep | 0 | Mar | 2023 | 0.00014984 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-03-04 16:11 | 2023-03-04 18:11 | 10 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23030400078 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2023-03-04 | 1200 | keep | 0 | Mar | 2023 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-03-04 16:14 | 2023-03-04 19:32 | 199 | 3:18 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO LINEA ZAFADA DE AISLADOR | A23030400048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 198 | 2023-03-04 | 39402 | keep | 0 | Mar | 2023 | 0.026837 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
FAJARDO | 2023-03-04 16:15 | 2023-03-04 19:21 | 10 | 3:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN C/L | R23030400057 | New_Event | Cutout Failure | Include | Include | Equipment | 186 | 2023-03-04 | 1860 | keep | 0 | Mar | 2023 | 0.0012668 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-03-04 16:16 | 2023-03-04 21:24 | 68 | 5:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE HIZO DESGANCHE | P23030400070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2023-03-04 | 20944 | keep | 0 | Mar | 2023 | 0.014265 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
PONCE | 2023-03-04 16:25 | 2023-03-05 09:43 | 45 | 17:18 | P | DESGANCHE | 1X65 EN CORTE DE LINEA SE RETIRO BAMBUA | P23030400071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1038 | 2023-03-04 | 46710 | keep | 0 | Mar | 2023 | 0.031814 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2023-03-04 16:27 | 2023-03-04 16:28 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23030400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-04 | 2302 | keep | 0 | Mar | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
GUAYAMA | 2023-03-04 16:31 | 2023-03-04 18:43 | 45 | 2:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO 1 X 25 EN CORTE DE LINEA | P23030400073 | New_Event | Primary Wire Break | Include | Include | Equipment | 132 | 2023-03-04 | 5940 | keep | 0 | Mar | 2023 | 0.0040457 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-03-04 16:37 | 2023-03-04 18:00 | 50 | 1:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR | R23030400058 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 83 | 2023-03-04 | 4150 | keep | 0 | Mar | 2023 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-04 16:47 | 2023-03-04 18:24 | 158 | 1:37 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | B23030400078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-03-04 | 15326 | keep | 0 | Mar | 2023 | 0.010438 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
CAGUAS | 2023-03-04 17:20 | 2023-03-04 19:15 | 150 | 1:55 | P | DESGANCHE | 2 X 140 EN C/L SE REALIZO DESGANCHE | C23030400079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-03-04 | 17250 | keep | 0 | Mar | 2023 | 0.011749 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-03-04 17:22 | 2023-03-04 18:53 | 90 | 1:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23030400089 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 91 | 2023-03-04 | 8190 | keep | 0 | Mar | 2023 | 0.0055782 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-03-04 18:17 | 2023-03-04 21:24 | 1 | 3:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJA PRIMARIAS 2 X 80 EN C/L Y 1 X 100 EN C/L | S23030400520 | New_Event | Cutout Failure | Include | Include | Equipment | 187 | 2023-03-04 | 187 | keep | 0 | Mar | 2023 | 0.00012736 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-03-04 18:28 | 2023-03-05 14:53 | 4 | 20:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS Y SE REALIZO DESGANCHE | A23030400060 | New_Event | Primary Wire Break | Include | Include | Equipment | 1225 | 2023-03-04 | 4900 | keep | 0 | Mar | 2023 | 0.0033374 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2023-03-04 18:30 | 2023-03-05 08:50 | 20 | 14:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES | A23030400061 | New_Event | Cutout Failure | Include | Include | Equipment | 860 | 2023-03-04 | 17200 | keep | 0 | Mar | 2023 | 0.011715 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-03-04 18:40 | 2023-03-05 14:32 | 20 | 19:52 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 30 EN CONVERTIDOR POR POSTE PARTIDO | A23030400062 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1192 | 2023-03-04 | 23840 | keep | 0 | Mar | 2023 | 0.016237 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-03-04 18:48 | 2023-03-04 22:03 | 60 | 3:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030400063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-03-04 | 11700 | keep | 0 | Mar | 2023 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-03-04 19:05 | 2023-03-04 19:26 | 16 | 0:21 | P | ANIMAL | 1 X 10 EN XMR SE RETIRO LAGARTO | C23030400085 | New_Event | Animals | Include | Include | Wildlife | 21 | 2023-03-04 | 336 | keep | 0 | Mar | 2023 | 0.00022885 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-03-04 19:12 | 2023-03-04 21:09 | 80 | 1:57 | P | DESGANCHE | 1 X 80 EN PROVISIONAL AEREO DESGANCHE Y SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | S23030400541 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-03-04 | 9360 | keep | 0 | Mar | 2023 | 0.0063751 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-03-04 19:25 | 2023-03-04 20:29 | 200 | 1:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO PORTAFUSIBLES | R23030400073 | New_Event | Cutout Failure | Include | Include | Equipment | 64 | 2023-03-04 | 12800 | keep | 0 | Mar | 2023 | 0.008718 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-03-04 19:52 | 2023-03-05 09:14 | 20 | 13:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN XMR SE REMPLAZO CAJA PRIMARIA | S23030400553 | New_Event | Cutout Failure | Include | Include | Equipment | 802 | 2023-03-04 | 16040 | keep | 0 | Mar | 2023 | 0.010925 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-03-04 21:28 | 2023-03-05 09:51 | 151 | 12:23 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA GLOBO DE HELIO CRUZO FASE | P23030400108 | New_Event | Damage From Public | Include | Include | Public | 743 | 2023-03-04 | 112193 | keep | 0 | Mar | 2023 | 0.076414 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
CANOVANAS | 2023-03-04 21:31 | 2023-03-05 08:52 | 40 | 11:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN PROVISIONAL AEREO SE REMPLAZO CAJA PRIMARIA | R23030400083 | New_Event | Cutout Failure | Include | Include | Equipment | 681 | 2023-03-04 | 27240 | keep | 0 | Mar | 2023 | 0.018553 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-04 21:49 | 2023-03-04 22:50 | 7 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTES SECUNDARIOS Y CONEXIONES | B23030400086 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2023-03-04 | 427 | keep | 0 | Mar | 2023 | 0.00029083 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-03-04 23:21 | 2023-03-05 06:00 | 8 | 6:39 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | C23030400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 399 | 2023-03-04 | 3192 | keep | 0 | Mar | 2023 | 0.0021741 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-05 00:39 | 2023-03-05 07:53 | 12 | 7:14 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | C23030500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 434 | 2023-03-05 | 5208 | keep | 0 | Mar | 2023 | 0.0035471 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-03-05 00:54 | 2023-03-05 08:18 | 100 | 7:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M23030500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2023-03-05 | 44400 | keep | 0 | Mar | 2023 | 0.030241 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-03-05 01:18 | 2023-03-05 07:45 | 51 | 6:27 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEA | C23030500003 | New_Event | Animals | Include | Include | Wildlife | 387 | 2023-03-05 | 19737 | keep | 0 | Mar | 2023 | 0.013443 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
ARECIBO | 2023-03-05 01:28 | 2023-03-05 03:50 | 100 | 2:22 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | 2 X 65 EN CORTE DE LINEA POSTE SECUNDARIO | A23030500003 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 142 | 2023-03-05 | 14200 | keep | 0 | Mar | 2023 | 0.0096716 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-03-05 01:50 | 2023-03-05 05:45 | 80 | 3:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | A23030500004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 235 | 2023-03-05 | 18800 | keep | 0 | Mar | 2023 | 0.012805 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-03-05 01:52 | 2023-03-05 08:32 | 16 | 6:40 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23030500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2023-03-05 | 6400 | keep | 0 | Mar | 2023 | 0.004359 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-03-05 03:05 | 2023-03-05 04:56 | 3709 | 1:51 | T | PROBLEMA DEL CLIENTE | DISPARO DE BKR SE SECCIONALIZO Y SE CERRO POR CONTROL 20% EN SERVICIO | S23030600006 | New_Event | Customer-Related Interruption | Include | Include | Public | 111 | 2023-03-05 | 411699 | keep | 0 | Mar | 2023 | 0.28041 | 0.0025262 | Sustained | FALSE | FALSE | Not_TMED_Event | 3709
BAYAMON | 2023-03-05 03:53 | 2023-03-05 03:54 | 723 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1912-08 | S2303050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-05 | 723 | keep | 0 | Mar | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-03-05 03:53 | 2023-03-05 03:54 | 198 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1912-08 | S23030500026 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-05 | 198 | keep | 0 | Mar | 2023 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-03-05 03:53 | 2023-03-05 03:54 | 1976 | 0:01 | T | DESGANCHE | RECIERRE DE BKR 1912-08 | S2302050000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-05 | 1976 | keep | 0 | Mar | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-03-05 03:53 | 2023-03-05 03:54 | 577 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1912-08 LLEVA 1711-02 1711-05 Y 10% 1711-04 | S2303050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-05 | 577 | keep | 0 | Mar | 2023 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2023-03-05 03:54 | 2023-03-05 06:00 | 75 | 2:06 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23030500002 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-03-05 | 9450 | keep | 0 | Mar | 2023 | 0.0064364 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-03-05 04:33 | 2023-03-05 08:15 | 30 | 3:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | A23030500011 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2023-03-05 | 6660 | keep | 0 | Mar | 2023 | 0.0045361 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-03-05 04:56 | 2023-03-05 05:35 | 2967 | 0:39 | P | PROBLEMA DEL CLIENTE | SE CERRO MACHETE 100% EN SERVICIO NO SE ENCONTRO CAUSA | S23030600006 | Partial_restoration | Customer-Related Interruption | Include | Include | Public | 39 | 2023-03-05 | 115713 | keep | 0 | Mar | 2023 | 0.078812 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-05 06:08 | 2023-03-05 07:49 | 60 | 1:41 | P | ANIMAL | 1 X 80 EN C/L Y 1 X 65 EN RISER CRUCE X AVE | B23030500003 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-03-05 | 6060 | keep | 0 | Mar | 2023 | 0.0041274 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-03-05 06:50 | 2023-03-05 09:14 | 81 | 2:24 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23030500013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2023-03-05 | 11664 | keep | 0 | Mar | 2023 | 0.0079443 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2023-03-05 06:55 | 2023-03-05 06:56 | 27 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23030500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-05 | 27 | keep | 0 | Mar | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
HUMACAO | 2023-03-05 07:04 | 2023-03-05 09:30 | 69 | 2:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 65 EN C/L MAL TIEMPO LLUVIA | C23030500014 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 146 | 2023-03-05 | 10074 | keep | 0 | Mar | 2023 | 0.0068614 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BARRANQUITAS | 2023-03-05 07:18 | 2023-03-05 11:16 | 36 | 3:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | C23030500016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 238 | 2023-03-05 | 8568 | keep | 0 | Mar | 2023 | 0.0058356 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2023-03-05 07:44 | 2023-03-05 07:45 | 3 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO BKR Y SE CERRO POR SCADA | C2303050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-05 | 3 | keep | 0 | Mar | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-05 08:03 | 2023-03-05 08:04 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1118-10 LLEVA 20% DEL 1111-01 SE CERRO POR CONTROL | S2303050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-05 | 513 | keep | 0 | Mar | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-03-05 08:03 | 2023-03-05 08:04 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVA 20% DEL 1111-01 SE CERRO POR CONTROL | S2303050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-05 | 2782 | keep | 0 | Mar | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CANOVANAS | 2023-03-05 08:11 | 2023-03-05 10:23 | 80 | 2:12 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | R23030500010 | New_Event | Animals | Include | Include | Wildlife | 132 | 2023-03-05 | 10560 | keep | 0 | Mar | 2023 | 0.0071924 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-05 08:30 | 2023-03-05 12:02 | 30 | 3:32 | P | DESGANCHE | 1 X 40 EN C/ Y DESGANCHE | S23030500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2023-03-05 | 6360 | keep | 0 | Mar | 2023 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-03-05 08:32 | 2023-03-05 08:33 | 1569 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030500019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-05 | 1569 | keep | 0 | Mar | 2023 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2023-03-05 08:33 | 2023-03-05 10:40 | 16 | 2:07 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23030500006 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-03-05 | 2032 | keep | 0 | Mar | 2023 | 0.001384 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-03-05 08:51 | 2023-03-05 11:45 | 60 | 2:54 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE | M23030500028 | New_Event | Primary Wire Break | Include | Include | Equipment | 174 | 2023-03-05 | 10440 | keep | 0 | Mar | 2023 | 0.0071106 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-05 08:53 | 2023-03-05 12:47 | 29 | 3:54 | P | SECUNDARIA/DESGANCHE | 1X25 EN XMR DESGANCHE SECUNDARIO | S23030500010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 234 | 2023-03-05 | 6786 | keep | 0 | Mar | 2023 | 0.0046219 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
UTUADO | 2023-03-05 09:02 | 2023-03-05 19:31 | 5 | 10:29 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A23030500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 629 | 2023-03-05 | 3145 | keep | 0 | Mar | 2023 | 0.002142 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-03-05 09:03 | 2023-03-05 10:10 | 70 | 1:07 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23030500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2023-03-05 | 4690 | keep | 0 | Mar | 2023 | 0.0031943 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-03-05 09:53 | 2023-03-05 12:37 | 5 | 2:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE DOS CAJAS PRIMARIAS EN TRANSFORMADOR | P23030500029 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2023-03-05 | 820 | keep | 0 | Mar | 2023 | 0.0005585 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-03-05 09:54 | 2023-03-05 12:47 | 57 | 2:53 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L 1 X 8 EN XMR | C23030500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2023-03-05 | 9861 | keep | 0 | Mar | 2023 | 0.0067163 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2023-03-05 10:09 | 2023-03-05 10:15 | 1 | 0:06 | S | ANIMAL | PORTATIL#19 SE FUE A LOCKOUT SE RETIRO SERPIENTE (CULEBRA) DEL SU-3 (PREDIOS DE LUMA) SUBESTACIONES NO FASEAN, SE ABRIO BKR PARA NORMALIZAR SU CARGA, SE VOLVIO A CERRAR BKR Y SE ABRIO N/O CONTRA 1346-02 EN B/I - CARGA NORMALIZADA | S23030500015 | New_Event | Animals | Include | Include | Wildlife | 6 | 2023-03-05 | 6 | keep | 0 | Mar | 2023 | 4.0866e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-05 10:09 | 2023-03-05 10:15 | 737 | 0:06 | P | ANIMAL | PORTATIL#19 SE FUE A LOCKOUT SE RETIRO SERPIENTE (CULEBRA) DEL SU-3 (PREDIOS DE LUMA) SE ABRIO BKR, SUBESTACIONES NO FASEAN, Y SE VOLVIO A CERRAR PARA NORMALIZAR EL 40% DE SU CARGA QUE SE HABIA TRANSFERIDO AL 1907-04 | S23030500017 | New_Event | Animals | Include | Include | Wildlife | 6 | 2023-03-05 | 4422 | keep | 0 | Mar | 2023 | 0.0030118 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
BAYAMON | 2023-03-05 10:11 | 2023-03-05 12:45 | 1 | 2:34 | P | ANIMAL | 1X40 EN RISER, SE RETIRO IGUANA Y SE REMPLAZO BAJANTE PRIMARIO QUEMADO DE LINEA @ CAJA (RADIAL) | S23030500017 | New_Event | Animals | Include | Include | Wildlife | 154 | 2023-03-05 | 154 | keep | 0 | Mar | 2023 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-05 10:15 | 2023-03-05 11:32 | 150 | 1:17 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE | M23030500044 | New_Event | Primary Wire Break | Include | Include | Equipment | 77 | 2023-03-05 | 11550 | keep | 0 | Mar | 2023 | 0.0078667 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-03-05 10:23 | 2023-03-05 20:30 | 70 | 10:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 100KVA AVERIADO | M23030500045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 607 | 2023-03-05 | 42490 | keep | 0 | Mar | 2023 | 0.02894 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-03-05 10:27 | 2023-03-06 12:25 | 1 | 25:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO LINEA SECUNDARIA | M23030500046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1558 | 2023-03-05 | 1558 | keep | 0 | Mar | 2023 | 0.0010611 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-05 10:51 | 2023-03-05 10:56 | 2422 | 0:05 | S | ANIMAL | DISPARO PORTATIL#19 SE FUE A LOCKOUT SE RETIRO SERPIENTE (CULEBRA) DEL SU-3 (PREDIOS DE LUMA) Y SE NORMALIZO SU CARGA QUE SE HABIA TRANSFERIDO AL 1908-03 | S23030500023 | New_Event | Animals | Include | Include | Wildlife | 5 | 2023-03-05 | 12110 | keep | 0 | Mar | 2023 | 0.0082481 | 0.0016496 | Momentary | FALSE | FALSE | Not_TMED_Event | 2422
CAGUAS | 2023-03-05 10:52 | 2023-03-05 13:40 | 50 | 2:48 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23030500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-03-05 | 8400 | keep | 0 | Mar | 2023 | 0.0057212 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-03-05 10:58 | 2023-03-05 13:47 | 40 | 2:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO HOJA DE PALMA SOBRE LINEA | M23030500053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-03-05 | 6760 | keep | 0 | Mar | 2023 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-03-05 11:13 | 2023-03-05 11:14 | 274 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23030500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-05 | 274 | keep | 0 | Mar | 2023 | 0.00018662 | 0.00018662 | Momentary | FALSE | FALSE | Not_TMED_Event | 274
CAGUAS | 2023-03-05 11:15 | 2023-03-05 11:59 | 210 | 0:44 | P | DESGANCHE | 1 X 80 EN C/L Y 2 X 65 EN C/L DESGANCHE | C23030500040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2023-03-05 | 9240 | keep | 0 | Mar | 2023 | 0.0062933 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
VEGA BAJA | 2023-03-05 11:19 | 2023-03-05 14:40 | 1 | 3:21 | P | DESGANCHE | 1 X 40 Y 1 X 20 EN CORTES DE LINEA SE NECESITA DESGANCHE | A23030500031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2023-03-05 | 201 | keep | 0 | Mar | 2023 | 0.0001369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-05 11:31 | 2023-03-05 11:32 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030500042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-05 | 2302 | keep | 0 | Mar | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
AGUADILLA | 2023-03-05 11:32 | 2023-03-05 11:58 | 300 | 0:26 | P | CONDUCTOR ROTO O ABIERTO | SE CIERRA PUENTE Y CORTE DE LINEA | M23030500044 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 26 | 2023-03-05 | 7800 | keep | 0 | Mar | 2023 | 0.0053125 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-05 11:37 | 2023-03-05 12:44 | 40 | 1:07 | P | DESGANCHE | DISPARO DE INTERRUPTOR LLEVA 10% DE SU CARGA SE REALIZO DESGANCHE (A VARETA) DESDE EL PISO Y SE CERRO POR CONTROL | S23030500024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2023-03-05 | 2680 | keep | 0 | Mar | 2023 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-05 11:38 | 2023-03-05 14:02 | 723 | 2:24 | T | ALIMENTADOR AMARRADO | ALIMENTADOR TRANSFERIDO AL 1912-08 SE ABRIO AMARRE Y SE TRANSFIRIO AL 1709-02 LLEVA 1711-05 Y 10% 1711-04 | B23030500026 | New_Event | Feeder Load Transferred | Include | Include | Other | 144 | 2023-03-05 | 104112 | keep | 0 | Mar | 2023 | 0.07091 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-03-05 11:38 | 2023-03-05 14:02 | 198 | 2:24 | P | ALIMENTADOR AMARRADO | ALIMENTADOR TRANSFERIDO AL 1912-08 SE ABRIO AMARRE Y SE TRANSFIRIO AL 1709-02 LLEVA 1711-05 Y 10% 1711-04 | B23030500026 | New_Event | Feeder Load Transferred | Include | Include | Other | 144 | 2023-03-05 | 28512 | keep | 0 | Mar | 2023 | 0.019419 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-03-05 11:38 | 2023-03-05 14:02 | 1976 | 2:24 | T | ALIMENTADOR AMARRADO | ALIMENTADOR TRANSFERIDO AL 1912-08 SE ABRIO AMARRE Y SE TRANSFIRIO AL 1709-02 LLEVA 1711-05 Y 10% 1711-04 | B23030500026 | New_Event | Feeder Load Transferred | Include | Include | Other | 144 | 2023-03-05 | 284544 | keep | 0 | Mar | 2023 | 0.1938 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-03-05 11:38 | 2023-03-05 15:24 | 577 | 3:46 | T | DESCONECTIVO DEFECTUOSO | MEDIANTE GOI BY-230305-01 SE REMPLAZO MACHETE AVERIADO EVENTO DE SERVICE DE BAYAMON | B23030500026 | New_Event | Switch Failure | Include | Include | Equipment | 226 | 2023-03-05 | 130402 | keep | 0 | Mar | 2023 | 0.088816 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
AGUADILLA | 2023-03-05 11:45 | 2023-03-05 12:30 | 100 | 0:45 | P | CONDUCTOR ROTO O ABIERTO | SE CIERRA PUENTE Y CORTE DE LINEA | M23030500028 | New_Event | Primary Wire Break | Include | Include | Equipment | 45 | 2023-03-05 | 4500 | keep | 0 | Mar | 2023 | 0.0030649 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-03-05 11:47 | 2023-03-05 15:05 | 150 | 3:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M23030500061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2023-03-05 | 29700 | keep | 0 | Mar | 2023 | 0.020229 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-03-05 11:47 | 2023-03-05 17:05 | 30 | 5:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE FIJO AISLADOR PRIMARIO | A23030500033 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 318 | 2023-03-05 | 9540 | keep | 0 | Mar | 2023 | 0.0064977 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-05 12:07 | 2023-03-05 15:28 | 19 | 3:21 | P | NO SE REPORTO CAUSA | 2X80 DEL SU-6 @ SU-E | B23030500069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2023-03-05 | 3819 | keep | 0 | Mar | 2023 | 0.0026011 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-03-05 12:22 | 2023-03-05 12:47 | 10 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO CONECTORES EN LA SALIDA DEL XMR | B23030500085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-03-05 | 250 | keep | 0 | Mar | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-05 12:33 | 2023-03-05 18:52 | 150 | 6:19 | P | CRUCETA DEFECTUOSA O AVERIADA | 2 X 50 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | M23030500072 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 379 | 2023-03-05 | 56850 | keep | 0 | Mar | 2023 | 0.03872 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-03-05 12:45 | 2023-03-05 12:46 | 1180 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23030500109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-05 | 1180 | keep | 0 | Mar | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2023-03-05 13:38 | 2023-03-05 15:42 | 651 | 2:04 | T | CONDUCTOR ARRIADO O CRUZADO | SE RETIRO GUY SOBRE ALIMENTADOR Y SE CERRO POR SCADA | B2303050000X | New_Event | Primary To Primary Contact | Include | Include | Equipment | 124 | 2023-03-05 | 80724 | keep | 0 | Mar | 2023 | 0.054981 | 0.00044339 | Sustained | FALSE | FALSE | Not_TMED_Event | 651
AGUADILLA | 2023-03-05 13:59 | 2023-03-05 17:48 | 30 | 3:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23030500086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2023-03-05 | 6870 | keep | 0 | Mar | 2023 | 0.0046791 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-03-05 14:00 | 2023-03-05 14:50 | 12 | 0:50 | P | SOBRECARGA | SE INSTALA TRANSFORMADOR DE 25KVA A 4160VOLTS PARA DIVIDIR CARGA EN EL SECTOR | P23030500039 | New_Event | Trip Due To Overload | Include | Include | Other | 50 | 2023-03-05 | 600 | keep | 0 | Mar | 2023 | 0.00040866 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-03-05 14:00 | 2023-03-05 15:30 | 14 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON SECUNDARIAS | C23030500047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-03-05 | 1260 | keep | 0 | Mar | 2023 | 0.00085818 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
FAJARDO | 2023-03-05 14:03 | 2023-03-05 15:37 | 50 | 1:34 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL DE LINEA Y 1 X 50 EN C/L | R23030500020 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 94 | 2023-03-05 | 4700 | keep | 0 | Mar | 2023 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-05 14:08 | 2023-03-05 14:09 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2303050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-05 | 3438 | keep | 0 | Mar | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BARRANQUITAS | 2023-03-05 14:40 | 2023-03-05 15:49 | 9 | 1:09 | P | DESGANCHE | 1 X 20 EN C/L 1 X 10 EN XMR DESGANCHE | C23030500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2023-03-05 | 621 | keep | 0 | Mar | 2023 | 0.00042296 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-03-05 14:45 | 2023-03-05 15:27 | 7 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON BARRAS SECUNDARIAS Y TOMAS EN PEDESTAL | R23030500021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2023-03-05 | 294 | keep | 0 | Mar | 2023 | 0.00020024 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-05 14:47 | 2023-03-05 15:31 | 1180 | 0:44 | T | PARARRAYOS DEFECTUOSO | SE RETIRO BAJANTE DE PARARAYO SOBRE CRUCETA | B23030500175 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 44 | 2023-03-05 | 51920 | keep | 0 | Mar | 2023 | 0.035362 | 0.00080369 | Sustained | FALSE | FALSE | Not_TMED_Event | 1180
AGUADILLA | 2023-03-05 15:06 | 2023-03-05 16:45 | 8 | 1:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23030500033 | New_Event | Primary Wire Break | Include | Include | Equipment | 99 | 2023-03-05 | 792 | keep | 0 | Mar | 2023 | 0.00053943 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-05 15:20 | 2023-03-05 16:10 | 10 | 0:50 | P | ANIMAL | 1 X 15 EN XMR SE RETIRO AVE | B23030500196 | New_Event | Animals | Include | Include | Wildlife | 50 | 2023-03-05 | 500 | keep | 0 | Mar | 2023 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-05 15:48 | 2023-03-05 18:13 | 80 | 2:25 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 Y 3 X 50 EN C/L DIFERENTES SE LEVANTO CONDUCTOR PRIMARIO | B23030500191 | New_Event | Primary Wire Break | Include | Include | Equipment | 145 | 2023-03-05 | 11600 | keep | 0 | Mar | 2023 | 0.0079007 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-03-05 15:52 | 2023-03-05 16:41 | 21 | 0:49 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | R23030500024 | New_Event | Animals | Include | Include | Wildlife | 49 | 2023-03-05 | 1029 | keep | 0 | Mar | 2023 | 0.00070085 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
FAJARDO | 2023-03-05 15:56 | 2023-03-05 16:07 | 1 | 0:11 | P | ANIMAL | 1X15 EN C/L CRUCE POR AVE | R23030500026 | New_Event | Animals | Include | Include | Wildlife | 11 | 2023-03-05 | 11 | keep | 0 | Mar | 2023 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-05 15:57 | 2023-03-05 18:38 | 40 | 2:41 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | S23030500053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-03-05 | 6440 | keep | 0 | Mar | 2023 | 0.0043863 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-03-05 16:29 | 2023-03-05 16:32 | 1475 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR | P23030500052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-05 | 4425 | keep | 0 | Mar | 2023 | 0.0030138 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
BAYAMON | 2023-03-05 16:45 | 2023-03-05 18:08 | 12 | 1:23 | P | NO SE REPORTO CAUSA | 1 X 20 EN PROVISIONAL AEREO | B23030500215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2023-03-05 | 996 | keep | 0 | Mar | 2023 | 0.00067837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-03-05 17:09 | 2023-03-05 18:41 | 40 | 1:32 | P | DESGANCHE | 1X30 EN C/L DESGANCHE | R23030500037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-03-05 | 3680 | keep | 0 | Mar | 2023 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-03-05 17:11 | 2023-03-05 17:12 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030500056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-05 | 551 | keep | 0 | Mar | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2023-03-05 17:12 | 2023-03-05 17:28 | 15 | 0:16 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23030500059 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-03-05 | 240 | keep | 0 | Mar | 2023 | 0.00016346 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-03-05 17:27 | 2023-03-05 19:25 | 50 | 1:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA Y SE FIJO LINEA AL AISLADOR | P23030500057 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 118 | 2023-03-05 | 5900 | keep | 0 | Mar | 2023 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-05 17:36 | 2023-03-05 19:42 | 29 | 2:06 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23030500064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-03-05 | 3654 | keep | 0 | Mar | 2023 | 0.0024887 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
ARECIBO | 2023-03-05 18:17 | 2023-03-05 20:08 | 40 | 1:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A23030500072 | New_Event | Cutout Failure | Include | Include | Equipment | 111 | 2023-03-05 | 4440 | keep | 0 | Mar | 2023 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-05 19:40 | 2023-03-06 11:10 | 10 | 15:30 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO QUE ALIMENTA TRANSFORMADOR | M23030500109 | New_Event | Primary Wire Break | Include | Include | Equipment | 930 | 2023-03-05 | 9300 | keep | 0 | Mar | 2023 | 0.0063342 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-05 19:59 | 2023-03-05 23:44 | 89 | 3:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO | B23030500222 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 225 | 2023-03-05 | 20025 | keep | 0 | Mar | 2023 | 0.013639 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
SAN JUAN | 2023-03-05 20:06 | 2023-03-05 21:29 | 33 | 1:23 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR PRIMARIO PARTIDO EN EL SUELO MEDIANTE G.O.I. SJ-230305-01 | S23030500077 | New_Event | Primary Wire Break | Include | Include | Equipment | 83 | 2023-03-05 | 2739 | keep | 0 | Mar | 2023 | 0.0018655 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
AGUADILLA | 2023-03-05 21:15 | 2023-03-05 22:10 | 10 | 0:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR ESCAPE ACEITE DE 75 KVA POR 37.5 KVA | A23030500077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 55 | 2023-03-05 | 550 | keep | 0 | Mar | 2023 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-03-05 21:16 | 2023-03-06 10:08 | 12 | 12:52 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23030500068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 772 | 2023-03-05 | 9264 | keep | 0 | Mar | 2023 | 0.0063097 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-03-05 21:29 | 2023-03-05 22:30 | 100 | 1:01 | P | CONDUCTOR ROTO O ABIERTO | SJ-230305-01 SE CERRO N/O 1301-04 PARA SECCIONALIZAR CONDUCTOR EN EL SUELO SE LE DIO SERVICIO A 50 CLIENTES | S23030500077 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 61 | 2023-03-05 | 6100 | keep | 0 | Mar | 2023 | 0.0041547 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-05 22:01 | 2023-03-05 22:22 | 11 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA EN PEDESTAL | S23030500071 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2023-03-05 | 231 | keep | 0 | Mar | 2023 | 0.00015733 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-03-05 22:30 | 2023-03-05 23:35 | 50 | 1:05 | P | CONDUCTOR ROTO O ABIERTO | SJ-230305-01 SE CERRO MACHETES Y SE RETIRO PELIGRO DE CONDUCTOR EN EL SUELO | S23030500077 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 65 | 2023-03-05 | 3250 | keep | 0 | Mar | 2023 | 0.0022136 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-05 23:19 | 2023-03-06 07:11 | 300 | 7:52 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN C/L DESGANCHE | C23030500071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 472 | 2023-03-05 | 141600 | keep | 0 | Mar | 2023 | 0.096443 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-03-06 01:06 | 2023-03-06 09:21 | 40 | 8:15 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA ANIMAL CRUZO FASE | S23030600003 | New_Event | Animals | Include | Include | Wildlife | 495 | 2023-03-06 | 19800 | keep | 0 | Mar | 2023 | 0.013486 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-03-06 02:24 | 2023-03-06 09:38 | 100 | 7:14 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23030600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2023-03-06 | 43400 | keep | 0 | Mar | 2023 | 0.02956 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-06 03:05 | 2023-03-06 07:12 | 1356 | 4:07 | T | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE CALLE MAGDALENA Y SE CERRO MACHETE CALLE LUCHETE 75% EN SERVICIO | S23030600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2023-03-06 | 334932 | keep | 0 | Mar | 2023 | 0.22812 | 0.00092357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1356
SAN JUAN | 2023-03-06 05:35 | 2023-03-06 19:30 | 82 | 13:55 | P | PROBLEMA DEL CLIENTE | AVERIA SU-1 A SUBEST. PRIVADA SE REMPLAZO 3 X 100 EN RISER Y SE REMPLAZO CAJA PRIMATIA SE DEJO FUERA PISO 4,8,15,16,20,21 | S23030600138 | New_Event | Customer-Related Interruption | Include | Include | Public | 835 | 2023-03-06 | 68470 | keep | 0 | Mar | 2023 | 0.046635 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
BARRANQUITAS | 2023-03-06 06:29 | 2023-03-06 10:16 | 29 | 3:47 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | C23030600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-03-06 | 6583 | keep | 0 | Mar | 2023 | 0.0044837 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2023-03-06 06:38 | 2023-03-06 11:09 | 1 | 4:31 | P | SOBRECARGA | 1 X 40 EN RISER POR CARGA | B23030600004 | New_Event | Trip Due To Overload | Include | Include | Other | 271 | 2023-03-06 | 271 | keep | 0 | Mar | 2023 | 0.00018458 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-06 06:49 | 2023-03-06 06:50 | 990 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23030600002 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-03-06 | 990 | keep | 0 | Mar | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
SAN JUAN | 2023-03-06 07:12 | 2023-03-06 07:22 | 331 | 0:10 | P | NO SE REPORTO CAUSA | SE PATRULLO Y SE CERRO MACHETE CALLE MAGDALENA ESQ. SERRA 100% EN SERVICIO NO SE REPORTO CAUSA | S23030600022 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 10 | 2023-03-06 | 3310 | keep | 0 | Mar | 2023 | 0.0022544 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-06 07:14 | 2023-03-06 12:24 | 1 | 5:10 | P | TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REPARO TERMINACION SOTERRADA | S23030600031 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 310 | 2023-03-06 | 310 | keep | 0 | Mar | 2023 | 0.00021114 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-06 07:35 | 2023-03-06 08:04 | 1 | 0:29 | P | ANIMAL | 1 X 20 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | B23030600007 | New_Event | Animals | Include | Include | Wildlife | 29 | 2023-03-06 | 29 | keep | 0 | Mar | 2023 | 1.9752e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-06 08:02 | 2023-03-06 09:47 | 60 | 1:45 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A23030600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-03-06 | 6300 | keep | 0 | Mar | 2023 | 0.0042909 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-06 08:12 | 2023-03-06 11:34 | 50 | 3:22 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L Y 1 X 100 EN XMR SE REMPLAZO PARARRAYO | C23030600041 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 202 | 2023-03-06 | 10100 | keep | 0 | Mar | 2023 | 0.0068791 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-03-06 08:19 | 2023-03-06 08:20 | 1597 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23030600013 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-06 | 1597 | keep | 0 | Mar | 2023 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
MAYAGÃœEZ | 2023-03-06 08:20 | 2023-03-06 09:30 | 1 | 1:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE | M23030600016 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 70 | 2023-03-06 | 70 | keep | 0 | Mar | 2023 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-06 08:22 | 2023-03-06 10:10 | 12 | 1:48 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | A23030600010 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-03-06 | 1296 | keep | 0 | Mar | 2023 | 0.0008827 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-03-06 08:23 | 2023-03-06 11:48 | 1 | 3:25 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR MAL TIEMPO RAYOS | B23030600008 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 205 | 2023-03-06 | 205 | keep | 0 | Mar | 2023 | 0.00013962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-03-06 08:44 | 2023-03-06 16:08 | 8 | 7:24 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO EN C/L PARA EMPLAZAR POSTE PRIMARIO PARTIDO NO FUNDIO | R23030600029 | New_Event | Primary Pole Failure | Include | Include | Equipment | 444 | 2023-03-06 | 3552 | keep | 0 | Mar | 2023 | 0.0024193 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-03-06 08:48 | 2023-03-06 08:49 | 990 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23030600021 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-03-06 | 990 | keep | 0 | Mar | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
ARECIBO | 2023-03-06 09:05 | 2023-03-06 13:09 | 10 | 4:04 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | A23030600018 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 244 | 2023-03-06 | 2440 | keep | 0 | Mar | 2023 | 0.0016619 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-03-06 09:06 | 2023-03-06 10:49 | 1 | 1:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN SU-1 | C23030600049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2023-03-06 | 103 | keep | 0 | Mar | 2023 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-03-06 09:16 | 2023-03-06 10:22 | 16 | 1:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23030600020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 66 | 2023-03-06 | 1056 | keep | 0 | Mar | 2023 | 0.00071924 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-03-06 09:18 | 2023-03-06 14:13 | 43 | 4:55 | P | NO SE REPORTO CAUSA | 3 X 65 EN RISER NO CAUSA | S23030600049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 295 | 2023-03-06 | 12685 | keep | 0 | Mar | 2023 | 0.0086397 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2023-03-06 09:36 | 2023-03-06 10:53 | 2 | 1:17 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE EVENTO TRANSFERIDO DE PONCE | P23030600022 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-03-06 | 154 | keep | 0 | Mar | 2023 | 0.00010489 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2023-03-06 09:59 | 2023-03-06 10:41 | 20 | 0:42 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23030600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2023-03-06 | 840 | keep | 0 | Mar | 2023 | 0.00057212 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-03-06 10:02 | 2023-03-06 11:40 | 15 | 1:38 | P | ANIMAL | 1 X 15 EN XMR ANIMAL CRUZO LINEAS | P23030600028 | New_Event | Animals | Include | Include | Wildlife | 98 | 2023-03-06 | 1470 | keep | 0 | Mar | 2023 | 0.0010012 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-06 10:04 | 2023-03-06 10:21 | 990 | 0:17 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR MACHETE AVERIADO EN TROCAL PRIMARIO SE ABRIO MACHETES Y SE COLOCA INTERRUPTOR EN SERVICIO | M23030600039 | New_Event | Switch Failure | Include | Include | Equipment | 17 | 2023-03-06 | 16830 | keep | 0 | Mar | 2023 | 0.011463 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
HUMACAO | 2023-03-06 10:17 | 2023-03-06 12:32 | 1 | 2:15 | P | ANIMAL | 1 X 15 EN C/L CRUCE X AVE EVENTO TRANSFERIDO DE PONCE | P23030600032 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-03-06 | 135 | keep | 0 | Mar | 2023 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-06 10:21 | 2023-03-06 17:01 | 14 | 6:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 75 KVA X 75 KVA | S23030600062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 400 | 2023-03-06 | 5600 | keep | 0 | Mar | 2023 | 0.0038141 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-03-06 10:21 | 2023-03-06 10:59 | 70 | 0:38 | P | DESCONECTIVO DEFECTUOSO | SE CERRO N/O CON 6802-05 CON GOI # MY-230306-01A Y SE DEJO SECCIONALIZADO AREA MACHETE AVERIADO Y TODO LOS CLIENTE CON SERVICIO | M23030600066 | Partial_restoration | Switch Failure | Include | Include | Equipment | 38 | 2023-03-06 | 2660 | keep | 0 | Mar | 2023 | 0.0018117 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-06 10:24 | 2023-03-06 10:26 | 1588 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CARGA POR EL 1716-03 | B23030600022 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-06 | 3176 | keep | 0 | Mar | 2023 | 0.0021632 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-06 10:24 | 2023-03-06 10:26 | 1812 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1711-01 | B23030600022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-06 | 3624 | keep | 0 | Mar | 2023 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
AGUADILLA | 2023-03-06 10:26 | 2023-03-06 12:49 | 4 | 2:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23030600054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2023-03-06 | 572 | keep | 0 | Mar | 2023 | 0.00038959 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2023-03-06 11:15 | 2023-03-06 12:02 | 10 | 0:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARA CONEXIONES | A23030600003 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2023-03-06 | 470 | keep | 0 | Mar | 2023 | 0.00032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-06 11:17 | 2023-03-06 14:18 | 80 | 3:01 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | B23030600038 | New_Event | Animals | Include | Include | Wildlife | 181 | 2023-03-06 | 14480 | keep | 0 | Mar | 2023 | 0.0098623 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-03-06 11:35 | 2023-03-06 11:37 | 1879 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 3006-02 QUE LLEVA LA CARGA DEL 3006-05 SE CERRO POR SCADA | C23030600083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-06 | 3758 | keep | 0 | Mar | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-03-06 11:35 | 2023-03-06 11:37 | 3005 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 3006-02 QUE LLEVA LA CARGA DEL 3006-05 SE CERRO POR SCADA | C23030600083 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-06 | 6010 | keep | 0 | Mar | 2023 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CANOVANAS | 2023-03-06 11:50 | 2023-03-06 12:10 | 7 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR BARRAS EN PEDESTAL REDONDO | R23030600040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-03-06 | 140 | keep | 0 | Mar | 2023 | 9.5353e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-03-06 12:00 | 2023-03-06 13:24 | 4 | 1:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | C23030600104 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2023-03-06 | 336 | keep | 0 | Mar | 2023 | 0.00022885 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-03-06 12:18 | 2023-03-06 13:37 | 6 | 1:19 | P | CAUSAS EXTERNAS | SE ABRIO CAJAS EN TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA PARTIDA POR CAMION | M23030600075 | New_Event | Damage From Public | Include | Include | Public | 79 | 2023-03-06 | 474 | keep | 0 | Mar | 2023 | 0.00032284 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-03-06 12:40 | 2023-03-06 17:40 | 15 | 5:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CONVERTIDOR PARA PASAR LINEAS A POSTE NUEVO RELACIONADO A WR-6303964 | A23030600047 | New_Event | Primary Pole Failure | Include | Include | Equipment | 300 | 2023-03-06 | 4500 | keep | 0 | Mar | 2023 | 0.0030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-06 13:18 | 2023-03-06 13:19 | 411 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | M23030600081 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-03-06 | 411 | keep | 0 | Mar | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2023-03-06 13:19 | 2023-03-06 15:08 | 120 | 1:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23030600092 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 109 | 2023-03-06 | 13080 | keep | 0 | Mar | 2023 | 0.0089087 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2023-03-06 13:44 | 2023-03-06 16:11 | 80 | 2:27 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23030600089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-03-06 | 11760 | keep | 0 | Mar | 2023 | 0.0080097 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-03-06 13:50 | 2023-03-06 15:33 | 65 | 1:43 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | C23030600108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-03-06 | 6695 | keep | 0 | Mar | 2023 | 0.0045599 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2023-03-06 13:52 | 2023-03-06 14:50 | 10 | 0:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES | A23030600058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 58 | 2023-03-06 | 580 | keep | 0 | Mar | 2023 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-06 14:15 | 2023-03-06 15:53 | 63 | 1:38 | P | CAUSAS EXTERNAS | SE ABRE SU-1 A T-4 PARA ENDERESAR T-4 Y REPARAR TOMA IMPACTADO POR AUTO | S23030600066 | New_Event | Damage From Public | Include | Include | Public | 98 | 2023-03-06 | 6174 | keep | 0 | Mar | 2023 | 0.0042051 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
CAGUAS | 2023-03-06 14:15 | 2023-03-06 14:17 | 476 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23030600116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-06 | 952 | keep | 0 | Mar | 2023 | 0.0006484 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-03-06 14:15 | 2023-03-06 14:17 | 1655 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23030600116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-06 | 3310 | keep | 0 | Mar | 2023 | 0.0022544 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-03-06 14:15 | 2023-03-06 14:17 | 361 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23030600116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-06 | 722 | keep | 0 | Mar | 2023 | 0.00049175 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-03-06 14:15 | 2023-03-06 14:17 | 2842 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23030600116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-06 | 5684 | keep | 0 | Mar | 2023 | 0.0038713 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-03-06 14:15 | 2023-03-06 14:17 | 1702 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23030600117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-06 | 3404 | keep | 0 | Mar | 2023 | 0.0023184 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-03-06 14:15 | 2023-03-06 14:17 | 918 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23030600117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-06 | 1836 | keep | 0 | Mar | 2023 | 0.0012505 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
BAYAMON | 2023-03-06 14:20 | 2023-03-06 14:22 | 1588 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1716-03 LLEVA CARGA 1711-01 SE CERRO POR SCADA | B23030600058 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-06 | 3176 | keep | 0 | Mar | 2023 | 0.0021632 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-06 14:20 | 2023-03-06 14:22 | 1812 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-03 LLEVA CARGA 1711-01 SE CERRO POR SCADA | B23030600058 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-06 | 3624 | keep | 0 | Mar | 2023 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
SAN JUAN | 2023-03-06 14:21 | 2023-03-06 21:06 | 1 | 6:45 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR SE RETIRO CULEBRA CRUZANDO FASE EVENTO TRANSFERIDO DE CAGUAS A SAN JUAN | C23030600115 | New_Event | Animals | Include | Include | Wildlife | 405 | 2023-03-06 | 405 | keep | 0 | Mar | 2023 | 0.00027584 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-06 14:22 | 2023-03-06 15:18 | 7 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | DESGANCHE EN SECUNDARIA Y SE RETEZO LINEA SECUNDARIA. | S23030600108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2023-03-06 | 392 | keep | 0 | Mar | 2023 | 0.00026699 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-06 14:28 | 2023-03-06 16:41 | 30 | 2:13 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L SE ELIMINO PARARRAYO | S23030600109 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 133 | 2023-03-06 | 3990 | keep | 0 | Mar | 2023 | 0.0027176 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-03-06 15:10 | 2023-03-06 17:02 | 14 | 1:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARO LA SECUNDARIA | R23030600057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 112 | 2023-03-06 | 1568 | keep | 0 | Mar | 2023 | 0.001068 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-03-06 15:17 | 2023-03-06 18:31 | 60 | 3:14 | P | NO SE REPORTO CAUSA | 1 X 65 DE RISER @ T-316 | R23030600058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2023-03-06 | 11640 | keep | 0 | Mar | 2023 | 0.007928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-06 15:17 | 2023-03-06 17:15 | 77 | 1:58 | P | DESGANCHE | 1 X 50 1 X 40 EN C/L SE DESGANCHO | C23030600127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-03-06 | 9086 | keep | 0 | Mar | 2023 | 0.0061884 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
HUMACAO | 2023-03-06 16:00 | 2023-03-06 16:21 | 1 | 0:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE XMR | C23030600146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2023-03-06 | 21 | keep | 0 | Mar | 2023 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-06 16:39 | 2023-03-06 18:41 | 50 | 2:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO ENREDADERA DE LA LINEA | M23030600135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-03-06 | 6100 | keep | 0 | Mar | 2023 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-03-06 17:06 | 2023-03-06 18:02 | 1 | 0:56 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XMR SE REALIZO DESGANCHE SECUNDARIO | R23030600072 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 56 | 2023-03-06 | 56 | keep | 0 | Mar | 2023 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-06 18:04 | 2023-03-06 19:53 | 5 | 1:49 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESPEJO LINEA | S23030600159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2023-03-06 | 545 | keep | 0 | Mar | 2023 | 0.0003712 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-03-06 18:11 | 2023-03-06 19:19 | 30 | 1:08 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23030600077 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-03-06 | 2040 | keep | 0 | Mar | 2023 | 0.0013894 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-03-06 18:16 | 2023-03-06 19:51 | 30 | 1:35 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | R23030600049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2023-03-06 | 2850 | keep | 0 | Mar | 2023 | 0.0019411 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-03-06 18:31 | 2023-03-06 20:43 | 1 | 2:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTES DE TRANSFORMADOR Y SECUNDARIA | P23030600094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 132 | 2023-03-06 | 132 | keep | 0 | Mar | 2023 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-06 18:54 | 2023-03-06 20:32 | 12 | 1:38 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23030600164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2023-03-06 | 1176 | keep | 0 | Mar | 2023 | 0.00080097 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-03-06 19:30 | 2023-03-06 19:33 | 3709 | 0:03 | T | PROBLEMA DEL CLIENTE | DISPARO INTERRUPTOR AL REPONER FUSIBLE EN CORTE DE LINEAN SE DEJO FUERA CLIENTE Y SE VERIFICO PERSONAL FUERA SE CERRO INTERRUPTOR | S23030600167 | New_Event | Customer-Related Interruption | Include | Include | Public | 3 | 2023-03-06 | 11127 | keep | 0 | Mar | 2023 | 0.0075785 | 0.0025262 | Momentary | FALSE | FALSE | Not_TMED_Event | 3709
MAYAGÃœEZ | 2023-03-06 19:32 | 2023-03-07 09:03 | 50 | 13:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA CAJA AVERIADA | M23030600147 | New_Event | Cutout Failure | Include | Include | Equipment | 811 | 2023-03-06 | 40550 | keep | 0 | Mar | 2023 | 0.027618 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-06 19:33 | 2023-03-06 21:10 | 82 | 1:37 | P | PROBLEMA DEL CLIENTE | AVERIA SU-1 A SUBEST. PRIVADA SE REMPLAZO 3 X 100 EN RISER Y SE REMPLAZO CAJA PRIMATIA SE DEJO FUERA PISO 4,8,15,16,20,21 | S23030600138 | 1st_after_momentary | Customer-Related Interruption | Include | Include | Public | 97 | 2023-03-06 | 7954 | keep | 0 | Mar | 2023 | 0.0054174 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
VEGA BAJA | 2023-03-06 21:10 | 2023-03-07 08:12 | 12 | 11:02 | P | DESGANCHE | 2 X 30 EN CL DESGANCHE | A23030600084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 662 | 2023-03-06 | 7944 | keep | 0 | Mar | 2023 | 0.0054106 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-06 21:13 | 2023-03-07 10:38 | 22 | 13:25 | P | DESGANCHE | 1 X 65 EN C/L | C23030600174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 805 | 2023-03-06 | 17710 | keep | 0 | Mar | 2023 | 0.012062 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
HUMACAO | 2023-03-06 21:40 | 2023-03-07 11:00 | 7 | 13:20 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | C23030600103 | New_Event | Service Transformer Failure | Include | Include | Equipment | 800 | 2023-03-06 | 5600 | keep | 0 | Mar | 2023 | 0.0038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-06 21:59 | 2023-03-07 01:41 | 34 | 3:42 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23030600181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-03-06 | 7548 | keep | 0 | Mar | 2023 | 0.0051409 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2023-03-06 22:44 | 2023-03-07 09:57 | 39 | 11:13 | P | DESGANCHE | 1 X 80 EN C/L | C23030600183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 673 | 2023-03-06 | 26247 | keep | 0 | Mar | 2023 | 0.017877 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2023-03-07 00:24 | 2023-03-07 11:50 | 10 | 11:26 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA POR GROUND DE POSTE CRUZO LINEA | M23030700001 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 686 | 2023-03-07 | 6860 | keep | 0 | Mar | 2023 | 0.0046723 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-03-07 00:57 | 2023-03-07 01:10 | 40 | 0:13 | P | CAUSAS EXTERNAS | CAMION IMPACTO POSTE | P23030700001 | New_Event | Damage From Public | Include | Include | Public | 13 | 2023-03-07 | 520 | keep | 0 | Mar | 2023 | 0.00035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-03-07 02:10 | 2023-03-07 06:42 | 50 | 4:32 | P | DESGANCHE | 1 X 50 EN C/L | C23030700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2023-03-07 | 13600 | keep | 0 | Mar | 2023 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-07 03:06 | 2023-03-07 03:07 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23030700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-07 | 1026 | keep | 0 | Mar | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
BAYAMON | 2023-03-07 06:59 | 2023-03-07 07:39 | 293 | 0:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 JUAN DOMINGO INTERRUPTOR 4350 JUAN DOMINGO AVERIADO | S23030700021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-03-07 | 11720 | keep | 0 | Mar | 2023 | 0.0079824 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2023-03-07 06:59 | 2023-03-07 07:39 | 315 | 0:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 JUAN DOMINGO LLEVA LA CARGA DEL 1924-01 INTERRUPTOR 4350 JUAN DOMINGO AVERIADO | S23030700021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-03-07 | 12600 | keep | 0 | Mar | 2023 | 0.0085818 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2023-03-07 06:59 | 2023-03-07 07:39 | 216 | 0:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 JUAN DOMINGO INTERRUPTOR 4350 JUAN DOMINGO AVERIADO | S23030700021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-03-07 | 8640 | keep | 0 | Mar | 2023 | 0.0058847 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2023-03-07 06:59 | 2023-03-07 07:39 | 1310 | 0:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 JUAN DOMINGO INTERRUPTOR 4350 JUAN DOMINGO AVERIADO | S23030700021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-03-07 | 52400 | keep | 0 | Mar | 2023 | 0.035689 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2023-03-07 06:59 | 2023-03-07 07:39 | 212 | 0:40 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 JUAN DOMINGO CARGA TRANSFERIDA AL 1903-02 INTERRUPTOR 4350 JUAN DOMINGO AVERIADO | S23030700021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-03-07 | 8480 | keep | 0 | Mar | 2023 | 0.0057757 | 0.00014439 | Sustained | FALSE | FALSE | Not_TMED_Event | 212
BAYAMON | 2023-03-07 06:59 | 2023-03-07 07:39 | 31 | 0:40 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 JUAN DOMINGO 70% DE SU CARGA TRANSFERIDA AL 1903-03 INTERRUPTOR 4350 JUAN DOMINGO AVERIADO | S23030700021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-03-07 | 1240 | keep | 0 | Mar | 2023 | 0.00084456 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-03-07 06:59 | 2023-03-07 07:39 | 686 | 0:40 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 JUAN DOMINGO CARGA TRANSFERIDA AL 1903-03 INTERRUPTOR 4350 JUAN DOMINGO AVERIADO | S23030700021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-03-07 | 27440 | keep | 0 | Mar | 2023 | 0.018689 | 0.00046723 | Sustained | FALSE | FALSE | Not_TMED_Event | 686
YAUCO | 2023-03-07 07:01 | 2023-03-07 07:24 | 40 | 0:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA QUEMADA 1 X 40 | P23030700002 | New_Event | Cutout Failure | Include | Include | Equipment | 23 | 2023-03-07 | 920 | keep | 0 | Mar | 2023 | 0.00062661 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-03-07 07:18 | 2023-03-07 07:19 | 1475 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23030700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-07 | 1475 | keep | 0 | Mar | 2023 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
CANOVANAS | 2023-03-07 07:20 | 2023-03-07 17:50 | 12 | 10:30 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA Y SE CERRO C/L | R23030700004 | New_Event | Primary Wire Break | Include | Include | Equipment | 630 | 2023-03-07 | 7560 | keep | 0 | Mar | 2023 | 0.0051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-07 07:30 | 2023-03-07 10:30 | 30 | 3:00 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR AVE | M23030700015 | New_Event | Animals | Include | Include | Wildlife | 180 | 2023-03-07 | 5400 | keep | 0 | Mar | 2023 | 0.0036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-03-07 07:37 | 2023-03-07 09:48 | 1 | 2:11 | P | DESGANCHE | 2 X 100 EN RISER A TRANSCLOUSURE DESGANCHE | S23030700037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-03-07 | 131 | keep | 0 | Mar | 2023 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-07 07:47 | 2023-03-07 11:00 | 120 | 3:13 | P | ANIMAL | 1X 80 EN RISER CRUCE X AVE | C23030700011 | New_Event | Animals | Include | Include | Wildlife | 193 | 2023-03-07 | 23160 | keep | 0 | Mar | 2023 | 0.015774 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-03-07 07:55 | 2023-03-07 14:12 | 100 | 6:17 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | B23030700007 | New_Event | Animals | Include | Include | Wildlife | 377 | 2023-03-07 | 37700 | keep | 0 | Mar | 2023 | 0.025677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-03-07 08:09 | 2023-03-07 12:30 | 4 | 4:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA POR VIENTOS | M23030700022 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 261 | 2023-03-07 | 1044 | keep | 0 | Mar | 2023 | 0.00071106 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-03-07 08:28 | 2023-03-07 10:53 | 300 | 2:25 | P | ANIMAL | 2X100 DE RISER @ CONVERTIDOR, 2X65 DE RISER @ SU- 5 CRUCE POR AVE | S23030700044 | New_Event | Animals | Include | Include | Wildlife | 145 | 2023-03-07 | 43500 | keep | 0 | Mar | 2023 | 0.029628 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2023-03-07 08:39 | 2023-03-07 12:17 | 60 | 3:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M23030700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2023-03-07 | 13080 | keep | 0 | Mar | 2023 | 0.0089087 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2023-03-07 08:51 | 2023-03-07 10:47 | 50 | 1:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA Y SE REMPLAZO 2 CAJAS PRIMARIAS | P23030700013 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2023-03-07 | 5800 | keep | 0 | Mar | 2023 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-03-07 08:57 | 2023-03-07 11:06 | 45 | 2:09 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23030700018 | New_Event | Animals | Include | Include | Wildlife | 129 | 2023-03-07 | 5805 | keep | 0 | Mar | 2023 | 0.0039538 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-03-07 09:01 | 2023-03-07 12:00 | 1 | 2:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S23030700049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2023-03-07 | 179 | keep | 0 | Mar | 2023 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-07 09:05 | 2023-03-07 10:52 | 20 | 1:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23030700050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-03-07 | 2140 | keep | 0 | Mar | 2023 | 0.0014575 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-03-07 09:13 | 2023-03-07 18:34 | 22 | 9:21 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN XMR REMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | C23030700021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 561 | 2023-03-07 | 12342 | keep | 0 | Mar | 2023 | 0.0084061 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-03-07 09:16 | 2023-03-07 14:22 | 1 | 5:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO 2 CAJAS PRIMARIA Y BAJANTE DE LINEA A CAJA | S23030700055 | New_Event | Cutout Failure | Include | Include | Equipment | 306 | 2023-03-07 | 306 | keep | 0 | Mar | 2023 | 0.00020842 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-07 09:30 | 2023-03-07 17:49 | 1 | 8:19 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L NO CAUSA EVENTO TRANSFERIDO DE CANOVANAS | R23030700010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 499 | 2023-03-07 | 499 | keep | 0 | Mar | 2023 | 0.00033987 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-03-07 09:36 | 2023-03-07 11:30 | 5 | 1:54 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REMPLAZO POSTE Y RELOCALIZO XMR | C23030700016 | New_Event | Primary Pole Failure | Include | Include | Equipment | 114 | 2023-03-07 | 570 | keep | 0 | Mar | 2023 | 0.00038822 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-03-07 09:38 | 2023-03-07 10:30 | 94 | 0:52 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23030700025 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-03-07 | 4888 | keep | 0 | Mar | 2023 | 0.0033292 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
SAN JUAN | 2023-03-07 09:41 | 2023-03-07 12:40 | 1 | 2:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REEMPLAZO PORTAFUSIBLE | S23030700063 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2023-03-07 | 179 | keep | 0 | Mar | 2023 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-07 09:48 | 2023-03-07 11:00 | 1 | 1:12 | P | PROBLEMA DEL CLIENTE | 1 X 20 EN RISER CONTAMINACION EN TRANSCLOSURE DEL CLIENTE | R23030700013 | New_Event | Customer-Related Interruption | Include | Include | Public | 72 | 2023-03-07 | 72 | keep | 0 | Mar | 2023 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-07 09:55 | 2023-03-07 09:56 | 2092 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-07 | 2092 | keep | 0 | Mar | 2023 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
ARECIBO | 2023-03-07 10:00 | 2023-03-07 11:59 | 75 | 1:59 | P | ERROR HUMANO | 1 X 80 EN CL PERSONAL COMPAÃ‘IA XPERT'S CRUZAN FASE PRIMARIA DURANTE TRABAJOS DE SDESGANCHE EN LINEA 2300 | A23030700034 | New_Event | Human Error | Include | Include | Other | 119 | 2023-03-07 | 8925 | keep | 0 | Mar | 2023 | 0.0060788 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-03-07 10:08 | 2023-03-07 10:09 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVA LA CARGA DEL 1909-09 | S2303070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-07 | 222 | keep | 0 | Mar | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-03-07 10:08 | 2023-03-07 10:09 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1907-03 LLEVA LA CARGA DEL 1909-09 | S2303070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-07 | 4456 | keep | 0 | Mar | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
GUAYAMA | 2023-03-07 10:24 | 2023-03-07 11:35 | 5 | 1:11 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE SE CREO EL EVENTO POR QUE BOMBA DE AAA SE QUEDO SIN SERVICIO DEL EVENTO P23030700026 | P23030700026 | New_Event | Animals | Include | Include | Wildlife | 71 | 2023-03-07 | 355 | keep | 0 | Mar | 2023 | 0.00024179 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-07 10:30 | 2023-03-07 12:24 | 3 | 1:54 | P | ANIMAL | 1X20 EN XMR CRUCE POR AVE | B23030700032 | New_Event | Animals | Include | Include | Wildlife | 114 | 2023-03-07 | 342 | keep | 0 | Mar | 2023 | 0.00023293 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-03-07 10:30 | 2023-03-07 10:31 | 958 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030700037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-07 | 958 | keep | 0 | Mar | 2023 | 0.00065249 | 0.00065249 | Momentary | FALSE | FALSE | Not_TMED_Event | 958
CAGUAS | 2023-03-07 10:30 | 2023-03-07 10:31 | 1378 | 0:01 | T | ANIMAL | RECIERRE | C23030700036 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-07 | 1378 | keep | 0 | Mar | 2023 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
CAGUAS | 2023-03-07 10:31 | 2023-03-07 11:24 | 94 | 0:53 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23030700025 | 1st_after_momentary | Animals | Include | Include | Wildlife | 53 | 2023-03-07 | 4982 | keep | 0 | Mar | 2023 | 0.0033932 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
YAUCO | 2023-03-07 10:35 | 2023-03-07 11:03 | 20 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23030700029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-03-07 | 560 | keep | 0 | Mar | 2023 | 0.00038141 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-03-07 10:40 | 2023-03-07 13:36 | 50 | 2:56 | P | DESGANCHE | 2 X 40 EN CL DESGANCHE | A23030700041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-03-07 | 8800 | keep | 0 | Mar | 2023 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-07 11:03 | 2023-03-07 11:12 | 1588 | 0:09 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1716-03 10% DE SU CARGA TRANSFERIDA AL 1710-01 LLEVA LA CARGA DEL 1711-01 SE CERRO POR CONTROL LUEGO DE CONFIRMAR PERSONAL FUERA DE LAS LINEAS | B23030700040 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-03-07 | 14292 | keep | 0 | Mar | 2023 | 0.0097342 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-07 11:03 | 2023-03-07 11:12 | 1630 | 0:09 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-03 10% DE SU CARGA TRANSFERIDA AL 1710-01 LLEVA LA CARGA DEL 1711-01 SE CERRO POR CONTROL LUEGO DE CONFIRMAR PERSONAL FUERA DE LAS LINEAS | B23030700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-03-07 | 14670 | keep | 0 | Mar | 2023 | 0.0099917 | 0.0011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 1630
SAN JUAN | 2023-03-07 11:05 | 2023-03-07 13:48 | 25 | 2:43 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | S23030700083 | New_Event | Animals | Include | Include | Wildlife | 163 | 2023-03-07 | 4075 | keep | 0 | Mar | 2023 | 0.0027755 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-03-07 11:07 | 2023-03-07 14:06 | 10 | 2:59 | P | ANIMAL | 1 X 20 EN XMR CRUCE POR AVE | B23030700042 | New_Event | Animals | Include | Include | Wildlife | 179 | 2023-03-07 | 1790 | keep | 0 | Mar | 2023 | 0.0012192 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-03-07 11:17 | 2023-03-07 16:39 | 1 | 5:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA DE TRANSFORMADOR 1 X 25 | P23030700041 | New_Event | Cutout Failure | Include | Include | Equipment | 322 | 2023-03-07 | 322 | keep | 0 | Mar | 2023 | 0.00021931 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-07 11:26 | 2023-03-07 14:16 | 52 | 2:50 | P | DESGANCHE | 1 X 80 EN C/L | C23030700046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-03-07 | 8840 | keep | 0 | Mar | 2023 | 0.0060209 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
VEGA BAJA | 2023-03-07 12:02 | 2023-03-07 16:32 | 2 | 4:30 | P | CAUSAS EXTERNAS | 1 X 30 Y 1 X 25 EN CL CRUCE DE FASES PRIMARIAS PROVOCADA POR CONTACTO MAQUINA PESADA CON TENSOR | A23030700055 | New_Event | Damage From Public | Include | Include | Public | 270 | 2023-03-07 | 540 | keep | 0 | Mar | 2023 | 0.00036779 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-03-07 12:03 | 2023-03-07 14:10 | 10 | 2:07 | P | CAUSAS EXTERNAS | 1 X 25 EN TRANSFORMADOR CAMION CRUZO LINEAS | M23030700067 | New_Event | Damage From Public | Include | Include | Public | 127 | 2023-03-07 | 1270 | keep | 0 | Mar | 2023 | 0.00086499 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-07 12:25 | 2023-03-07 14:03 | 16 | 1:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR LINEA SECUNDARIA | S23030700098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 98 | 2023-03-07 | 1568 | keep | 0 | Mar | 2023 | 0.001068 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-03-07 12:56 | 2023-03-07 13:32 | 9 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO BARRA PEDESTAL | C23030700059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2023-03-07 | 324 | keep | 0 | Mar | 2023 | 0.00022067 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-03-07 13:02 | 2023-03-07 13:57 | 1 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMRY SE REMPLAZARON BAJANTES SECUNDARIOS | B23030700078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-03-07 | 55 | keep | 0 | Mar | 2023 | 3.746e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-07 13:30 | 2023-03-07 13:50 | 8 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23030700066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-03-07 | 160 | keep | 0 | Mar | 2023 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-03-07 13:58 | 2023-03-07 17:05 | 80 | 3:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23030700089 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 187 | 2023-03-07 | 14960 | keep | 0 | Mar | 2023 | 0.010189 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-03-07 14:09 | 2023-03-07 15:50 | 17 | 1:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO C/L PARA REMPLAZAR AISLADOR | C23030700067 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 101 | 2023-03-07 | 1717 | keep | 0 | Mar | 2023 | 0.0011694 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-03-07 14:16 | 2023-03-07 16:22 | 4 | 2:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO SECUNDARIA | S23030700112 | New_Event | Secondary Wire Break | Include | Include | Equipment | 126 | 2023-03-07 | 504 | keep | 0 | Mar | 2023 | 0.00034327 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-03-07 14:26 | 2023-03-07 15:26 | 10 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | R23030700023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-03-07 | 600 | keep | 0 | Mar | 2023 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-03-07 14:29 | 2023-03-07 14:54 | 16 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | R23030700024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-03-07 | 400 | keep | 0 | Mar | 2023 | 0.00027244 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-03-07 14:34 | 2023-03-07 16:23 | 40 | 1:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L SE FIJO CONDUCTOR AL AISLADOR | C23030700076 | New_Event | Primary Wire Break | Include | Include | Equipment | 109 | 2023-03-07 | 4360 | keep | 0 | Mar | 2023 | 0.0029696 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-03-07 14:54 | 2023-03-07 14:55 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030700079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-07 | 676 | keep | 0 | Mar | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
CANOVANAS | 2023-03-07 14:57 | 2023-03-07 14:59 | 1615 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2303070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-07 | 3230 | keep | 0 | Mar | 2023 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
AGUADILLA | 2023-03-07 15:00 | 2023-03-08 09:50 | 5 | 18:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN RISER POR MAL TIEMPO | A23030700104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1130 | 2023-03-07 | 5650 | keep | 0 | Mar | 2023 | 0.0038482 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-07 15:06 | 2023-03-07 15:07 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23030700095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-07 | 1362 | keep | 0 | Mar | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
MAYAGÃœEZ | 2023-03-07 15:10 | 2023-03-07 17:45 | 12 | 2:35 | P | OTRAS CAUSAS | CONECTAR TRANSFORMADOR DE 50 KVA QUE SE TRANSFIRIO DEL 6101-02 AL 6101-05 (FID:21251595) CARR 109 KM 2.0, BO. POZO HONDO; AÃ‘ASCO RELACIONADO A VIA LIBRE D2023-3137_REV1 NO CONTEMPLADO EN LA VIA LIBRE | M23030700111 | New_Event | Other Causes | Include | Include | Other | 155 | 2023-03-07 | 1860 | keep | 0 | Mar | 2023 | 0.0012668 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-03-07 15:19 | 2023-03-07 16:30 | 10 | 1:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR CONECTORES | S23030700120 | New_Event | Secondary Wire Break | Include | Include | Equipment | 71 | 2023-03-07 | 710 | keep | 0 | Mar | 2023 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-07 15:20 | 2023-03-07 17:30 | 12 | 2:10 | P | CAUSAS EXTERNAS | SE ABRIO XMR Y SE REPARO LINEA SECUNDARIA AVERIADA POR CAMION | B23030700097 | New_Event | Damage From Public | Include | Include | Public | 130 | 2023-03-07 | 1560 | keep | 0 | Mar | 2023 | 0.0010625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-03-07 15:32 | 2023-03-07 16:04 | 1 | 0:32 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR AVE | P23030700077 | New_Event | Animals | Include | Include | Wildlife | 32 | 2023-03-07 | 32 | keep | 0 | Mar | 2023 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-07 15:34 | 2023-03-07 18:21 | 10 | 2:47 | P | NO SE REPORTO CAUSA | 2 X 25 EN TRANSFORMADOR | S23030700122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2023-03-07 | 1670 | keep | 0 | Mar | 2023 | 0.0011374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-03-07 15:36 | 2023-03-07 15:40 | 1590 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23030700084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-07 | 6360 | keep | 0 | Mar | 2023 | 0.0043318 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
CAGUAS | 2023-03-07 15:36 | 2023-03-07 15:38 | 1116 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23030700083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-07 | 2232 | keep | 0 | Mar | 2023 | 0.0015202 | 0.0007601 | Momentary | FALSE | FALSE | Not_TMED_Event | 1116
AGUADILLA | 2023-03-07 15:39 | 2023-03-07 17:25 | 35 | 1:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23030700102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-03-07 | 3710 | keep | 0 | Mar | 2023 | 0.0025269 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-03-07 15:41 | 2023-03-07 15:42 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23030700103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-07 | 3458 | keep | 0 | Mar | 2023 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
VEGA BAJA | 2023-03-07 15:57 | 2023-03-07 15:58 | 2107 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23030700083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-07 | 2107 | keep | 0 | Mar | 2023 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
PONCE | 2023-03-07 16:48 | 2023-03-07 19:22 | 15 | 2:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | P23030700086 | New_Event | Primary Wire Break | Include | Include | Equipment | 154 | 2023-03-07 | 2310 | keep | 0 | Mar | 2023 | 0.0015733 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-03-07 17:03 | 2023-03-07 19:28 | 30 | 2:25 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO Y CERRO PUENTE | C23030700096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2023-03-07 | 4350 | keep | 0 | Mar | 2023 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-07 17:10 | 2023-03-07 17:11 | 3597 | 0:01 | T | ANIMAL | RECIERRE | B23030700106 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-07 | 3597 | keep | 0 | Mar | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-03-07 17:11 | 2023-03-07 18:55 | 370 | 1:44 | P | ANIMAL | SE REEMPLAZO 1 X 100 EN Y 1 X 65 EN CORTES DE LINEA CRUCE X AVE | B23030700107 | 1st_after_momentary | Animals | Include | Include | Wildlife | 104 | 2023-03-07 | 38480 | keep | 0 | Mar | 2023 | 0.026209 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
YAUCO | 2023-03-07 17:26 | 2023-03-07 17:30 | 12 | 0:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23030700060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 4 | 2023-03-07 | 48 | keep | 0 | Mar | 2023 | 3.2693e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-03-07 18:01 | 2023-03-07 19:10 | 20 | 1:09 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23030700116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2023-03-07 | 1380 | keep | 0 | Mar | 2023 | 0.00093991 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-03-07 18:15 | 2023-03-07 18:16 | 551 | 0:01 | T | ANIMAL | RECIERRE | C23030700107 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-07 | 551 | keep | 0 | Mar | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2023-03-07 18:16 | 2023-03-07 19:17 | 1 | 1:01 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23030700102 | 1st_after_momentary | Animals | Include | Include | Wildlife | 61 | 2023-03-07 | 61 | keep | 0 | Mar | 2023 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-07 18:36 | 2023-03-07 19:47 | 72 | 1:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23030700125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2023-03-07 | 5112 | keep | 0 | Mar | 2023 | 0.0034818 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
CAGUAS | 2023-03-07 19:03 | 2023-03-07 20:53 | 79 | 1:50 | P | DESGANCHE | 1 X 65 EN C/L | C23030700104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-03-07 | 8690 | keep | 0 | Mar | 2023 | 0.0059187 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2023-03-07 19:41 | 2023-03-08 14:18 | 15 | 18:37 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO PISTOLA EN T-1 | B23030700144 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1117 | 2023-03-07 | 16755 | keep | 0 | Mar | 2023 | 0.011412 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-07 19:48 | 2023-03-08 00:15 | 125 | 4:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE | M23030700121 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2023-03-07 | 33375 | keep | 0 | Mar | 2023 | 0.022732 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-03-07 20:34 | 2023-03-07 20:36 | 4291 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | S2303070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-07 | 8582 | keep | 0 | Mar | 2023 | 0.0058452 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
CANOVANAS | 2023-03-07 21:41 | 2023-03-07 23:16 | 328 | 1:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEAMADA | R23030700039 | New_Event | Cutout Failure | Include | Include | Equipment | 95 | 2023-03-07 | 31160 | keep | 0 | Mar | 2023 | 0.021223 | 0.0002234 | Sustained | FALSE | FALSE | Not_TMED_Event | 328
PONCE | 2023-03-07 22:36 | 2023-03-08 06:41 | 2 | 8:05 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR ANIMAL | P23030700097 | New_Event | Animals | Include | Include | Wildlife | 485 | 2023-03-07 | 970 | keep | 0 | Mar | 2023 | 0.00066066 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-03-07 23:03 | 2023-03-08 11:55 | 60 | 12:52 | P | ANIMAL | 1 X 65 EN CL CRUCE DE FASE POR AVE | M23030700144 | New_Event | Animals | Include | Include | Wildlife | 772 | 2023-03-07 | 46320 | keep | 0 | Mar | 2023 | 0.031548 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-03-08 00:38 | 2023-03-08 08:51 | 35 | 8:13 | P | DESGANCHE | 1 X 50 EN C/L | R23030800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2023-03-08 | 17255 | keep | 0 | Mar | 2023 | 0.011752 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-03-08 00:45 | 2023-03-08 01:02 | 1677 | 0:17 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO Y SE CERRO N/O CON EL 1437-02 QUE ESTA POR EL 1437-01 GOISJ-230308-01 | S23030800179 | New_Event | Primary Wire Break | Include | Include | Equipment | 17 | 2023-03-08 | 28509 | keep | 0 | Mar | 2023 | 0.019417 | 0.0011422 | Sustained | FALSE | FALSE | Not_TMED_Event | 1677
SAN JUAN | 2023-03-08 01:02 | 2023-03-08 02:23 | 549 | 1:21 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO 100% EN SERVICIO Y SE NORMALIZO LAS CARGA VER GOI SJ-230308-01 | S23030800179 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 81 | 2023-03-08 | 44469 | keep | 0 | Mar | 2023 | 0.030288 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-08 02:34 | 2023-03-08 02:38 | 601 | 0:04 | T | ERROR HUMANO | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 1437-02, EN OPERACION DE NORMALIZAR LAS CARGAS. ENTENDEMOS QUE NO FASEA CON 1437-03. VER GOI SJ-230308-01 | S23030800017 | New_Event | Human Error | Include | Include | Other | 4 | 2023-03-08 | 2404 | keep | 0 | Mar | 2023 | 0.0016374 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2023-03-08 02:34 | 2023-03-08 02:38 | 640 | 0:04 | T | ERROR HUMANO | DISPARO INTERRUPTOR CARGA POR EL 1437-01, EN OPERACION DE NORMALIZAR LAS CARGAS. ENTENDEMOS QUE NO FASEA CON 1437-03. VER GOI SJ-230308-01 | S23030800017 | New_Event | Human Error | Include | Include | Other | 4 | 2023-03-08 | 2560 | keep | 0 | Mar | 2023 | 0.0017436 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2023-03-08 02:34 | 2023-03-08 02:38 | 1699 | 0:04 | T | ERROR HUMANO | DISPARO INTERRUPTOR EN OPERACION DE NORMALIZAR CARGA, ENTEDEMOS QUE NO FASE CON 1437-01, VER GOI SJ-230308-01 | S23030800016 | New_Event | Human Error | Include | Include | Other | 4 | 2023-03-08 | 6796 | keep | 0 | Mar | 2023 | 0.0046287 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2023-03-08 02:42 | 2023-03-08 06:28 | 7 | 3:46 | P | DESGANCHE | 1 X 25 EN XMR Y SE REALIZO DESGANCHE | S23030800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2023-03-08 | 1582 | keep | 0 | Mar | 2023 | 0.0010775 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-03-08 03:09 | 2023-03-08 17:55 | 30 | 14:46 | P | FUEGO | 3 X 40 EN CORTE DE LINEA SE PASARON LINEAS DE POSTE QUEMADO A POSTE NUEVO FUEGO FORESTAL | M23030800003 | New_Event | Fire | Include | Include | Public | 886 | 2023-03-08 | 26580 | keep | 0 | Mar | 2023 | 0.018104 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-08 03:29 | 2023-03-08 03:30 | 7 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B23030800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-08 | 7 | keep | 0 | Mar | 2023 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-03-08 04:26 | 2023-03-08 04:27 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23030800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-08 | 2126 | keep | 0 | Mar | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2023-03-08 04:41 | 2023-03-08 21:51 | 13 | 17:10 | P | CABLE SOTERRADO AVERIADO | SE CONECTARON CABLE DEL SU- 3 AL T-35 EN SERVICIO BY-230308-02 AVERIA VIEJA EN T36 A T35 CABLES SOTERADOS DESCONECTADOS EN SU3 HACIA T35 SE RECONECTARON Y SE DIO SERVICIO | B23030800003 | New_Event | UG Cable Fault | Include | Include | Equipment | 1030 | 2023-03-08 | 13390 | keep | 0 | Mar | 2023 | 0.0091199 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-03-08 05:34 | 2023-03-08 08:39 | 30 | 3:05 | P | DESGANCHE | 1X40 EN C/L Y 1X25 EN OTRO C/L DESGANCHE | B23030800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-03-08 | 5550 | keep | 0 | Mar | 2023 | 0.0037801 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-03-08 06:10 | 2023-03-08 06:11 | 1381 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1204-03 | S2303080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-08 | 1381 | keep | 0 | Mar | 2023 | 0.00094059 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
BARRANQUITAS | 2023-03-08 06:40 | 2023-03-08 15:32 | 32 | 8:52 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE REMPLAZO PARARAYO | C23030800005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 532 | 2023-03-08 | 17024 | keep | 0 | Mar | 2023 | 0.011595 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2023-03-08 07:02 | 2023-03-08 08:58 | 50 | 1:56 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | B23030800009 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-03-08 | 5800 | keep | 0 | Mar | 2023 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-03-08 07:41 | 2023-03-08 07:46 | 810 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23030800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-08 | 4050 | keep | 0 | Mar | 2023 | 0.0027584 | 0.00055169 | Momentary | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2023-03-08 07:41 | 2023-03-08 07:46 | 1235 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23030800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-08 | 6175 | keep | 0 | Mar | 2023 | 0.0042058 | 0.00084115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2023-03-08 07:41 | 2023-03-08 07:46 | 93 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23030800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-08 | 465 | keep | 0 | Mar | 2023 | 0.00031671 | 6.3342e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2023-03-08 07:41 | 2023-03-08 07:46 | 1825 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23030800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-08 | 9125 | keep | 0 | Mar | 2023 | 0.006215 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2023-03-08 07:41 | 2023-03-08 07:46 | 3230 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23030800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-03-08 | 16150 | keep | 0 | Mar | 2023 | 0.011 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
CAGUAS | 2023-03-08 07:54 | 2023-03-08 11:23 | 10 | 3:29 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | C23030800013 | New_Event | Animals | Include | Include | Wildlife | 209 | 2023-03-08 | 2090 | keep | 0 | Mar | 2023 | 0.0014235 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-03-08 07:56 | 2023-03-08 09:58 | 1 | 2:02 | P | ANIMAL | 2 X 40 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR ANIMAL | P23030800003 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-03-08 | 122 | keep | 0 | Mar | 2023 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-08 08:12 | 2023-03-08 11:48 | 1 | 3:36 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23030800014 | New_Event | Animals | Include | Include | Wildlife | 216 | 2023-03-08 | 216 | keep | 0 | Mar | 2023 | 0.00014712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-08 08:30 | 2023-03-08 09:20 | 8 | 0:50 | P | SECUNDARIA/OTROS | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS EN PEDESTAL SOTERRADO SECUNDARIO | A23030800011 | New_Event |  |  |  |  | 50 | 2023-03-08 | 400 | keep | 0 | Mar | 2023 | 0.00027244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-08 08:33 | 2023-03-08 10:13 | 50 | 1:40 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23030800016 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-03-08 | 5000 | keep | 0 | Mar | 2023 | 0.0034055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-03-08 08:34 | 2023-03-08 12:05 | 122 | 3:31 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | C23030800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2023-03-08 | 25742 | keep | 0 | Mar | 2023 | 0.017533 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
PONCE | 2023-03-08 08:59 | 2023-03-08 09:01 | 5069 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23030800028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-08 | 10138 | keep | 0 | Mar | 2023 | 0.0069049 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
MAYAGÃœEZ | 2023-03-08 09:00 | 2023-03-08 12:44 | 3 | 3:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23030800072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2023-03-08 | 672 | keep | 0 | Mar | 2023 | 0.0004577 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-03-08 09:05 | 2023-03-08 10:19 | 40 | 1:14 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23030800019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-03-08 | 2960 | keep | 0 | Mar | 2023 | 0.002016 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-03-08 09:26 | 2023-03-08 12:42 | 1 | 3:16 | P | ANIMAL | 1 X 15 EN BANCO DE TRANSFORMADOR CRUCE X AVE | C23030800027 | New_Event | Animals | Include | Include | Wildlife | 196 | 2023-03-08 | 196 | keep | 0 | Mar | 2023 | 0.00013349 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-08 09:37 | 2023-03-08 15:20 | 14 | 5:43 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | R23030800005 | New_Event | Animals | Include | Include | Wildlife | 343 | 2023-03-08 | 4802 | keep | 0 | Mar | 2023 | 0.0032706 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-03-08 09:46 | 2023-03-08 14:47 | 6 | 5:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE RELOCALOZI XMR (RADIAL) Y SE REMPLAZO TRAMO SECUNDARIO PARTIDO EN EL SUELO | B23030800023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 301 | 2023-03-08 | 1806 | keep | 0 | Mar | 2023 | 0.0012301 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-03-08 09:51 | 2023-03-08 11:30 | 50 | 1:39 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA POR PARARRAYO CRUZADO | A23030800025 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 99 | 2023-03-08 | 4950 | keep | 0 | Mar | 2023 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-08 09:52 | 2023-03-08 11:01 | 2 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN PM (T-2) PARA AJUSTAR BARRAS SECUNDARIAS EN PEDESTAL | B23030800025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2023-03-08 | 138 | keep | 0 | Mar | 2023 | 9.3991e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-03-08 09:56 | 2023-03-08 12:07 | 25 | 2:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN RISER SE REMPLAZO CAJA PRIMARIA | M23030800038 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2023-03-08 | 3275 | keep | 0 | Mar | 2023 | 0.0022306 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-03-08 10:00 | 2023-03-08 10:50 | 8 | 0:50 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS EN TRANSFORMADOR PARA CORTAR RAMA EN ARBOL Y SE REPARO TRAMO LINEA SECUNDARIA | M23030800037 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 50 | 2023-03-08 | 400 | keep | 0 | Mar | 2023 | 0.00027244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-03-08 10:17 | 2023-03-08 14:06 | 1 | 3:49 | P | DESGANCHE | 1 X 50 EN C/L | R23030800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-03-08 | 229 | keep | 0 | Mar | 2023 | 0.00015597 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-03-08 10:24 | 2023-03-08 11:18 | 31 | 0:54 | P | SOBRECARGA | SE PRUEBA TRANSFORMADOR NO CONECTADO Y AL PROBAR BUENO ABREN TRANSFOMADOR PARA DIVIDIR CARGAS POR FLUCTUACION DE VOLTAJE | P23030800047 | New_Event | Trip Due To Overload | Include | Include | Other | 54 | 2023-03-08 | 1674 | keep | 0 | Mar | 2023 | 0.0011402 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CANOVANAS | 2023-03-08 10:35 | 2023-03-08 13:55 | 1 | 3:20 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23030800025 | New_Event | Animals | Include | Include | Wildlife | 200 | 2023-03-08 | 200 | keep | 0 | Mar | 2023 | 0.00013622 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-08 10:42 | 2023-03-08 11:22 | 10 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR Y SE REPARO SECUNDARIA | S23030800054 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-03-08 | 400 | keep | 0 | Mar | 2023 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-08 10:54 | 2023-03-08 13:06 | 10 | 2:12 | P | DESGANCHE | 1 X 140 EN CL DESGANCHE | M23030800052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-03-08 | 1320 | keep | 0 | Mar | 2023 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-08 10:55 | 2023-03-08 11:15 | 8 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARA CONEXIONES SECUNDARIAS | A23030800002 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-03-08 | 160 | keep | 0 | Mar | 2023 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-03-08 11:01 | 2023-03-08 11:59 | 10 | 0:58 | P | PARARRAYOS DEFECTUOSO | SE REMPLAZO PARARAYO | C23030800031 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 58 | 2023-03-08 | 580 | keep | 0 | Mar | 2023 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-03-08 11:15 | 2023-03-08 13:30 | 30 | 2:15 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | A23030800041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-03-08 | 4050 | keep | 0 | Mar | 2023 | 0.0027584 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-03-08 11:24 | 2023-03-08 14:39 | 12 | 3:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRAS EN PEDESTAL SECUNDARIO | P23030800062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 195 | 2023-03-08 | 2340 | keep | 0 | Mar | 2023 | 0.0015938 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-03-08 11:29 | 2023-03-08 12:03 | 8 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZARON CONECTORES | C23030800050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-03-08 | 272 | keep | 0 | Mar | 2023 | 0.00018526 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-08 11:36 | 2023-03-08 12:00 | 5 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REP SECUNDARIA | C23030800053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-03-08 | 120 | keep | 0 | Mar | 2023 | 8.1731e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-08 11:58 | 2023-03-08 19:23 | 8 | 7:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR TOMA | S23030800060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 445 | 2023-03-08 | 3560 | keep | 0 | Mar | 2023 | 0.0024247 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-08 12:01 | 2023-03-08 12:04 | 1588 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1716-03 10% DE SU CARGA POR EL 1710-01 LLEVA LA CARGA DEL 1711-01 SE CERRO POR CONTROL | B23030800046 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-08 | 4764 | keep | 0 | Mar | 2023 | 0.0032447 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-08 12:01 | 2023-03-08 12:04 | 1630 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-03 10% DE SU CARGA POR EL 1710-01 LLEVA LA CARGA DEL 1711-01 SE CERRO POR CONTROL | B23030800046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-08 | 4890 | keep | 0 | Mar | 2023 | 0.0033306 | 0.0011102 | Momentary | FALSE | FALSE | Not_TMED_Event | 1630
BAYAMON | 2023-03-08 12:19 | 2023-03-08 12:21 | 1588 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1716-03 10% DE SU CARGA POR EL 1710-01 LLEVA LA CARGA DEL 1711-01 SE CERRO POR CONTROL | B23030800048 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-08 | 3176 | keep | 0 | Mar | 2023 | 0.0021632 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-08 12:19 | 2023-03-08 12:21 | 1630 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-03 10% DE SU CARGA POR EL 1710-01 LLEVA LA CARGA DEL 1711-01 SE CERRO POR CONTROL | B23030800048 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-08 | 3260 | keep | 0 | Mar | 2023 | 0.0022204 | 0.0011102 | Momentary | FALSE | FALSE | Not_TMED_Event | 1630
VEGA BAJA | 2023-03-08 12:20 | 2023-03-08 12:50 | 6 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES | A23030800055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-03-08 | 180 | keep | 0 | Mar | 2023 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-08 12:23 | 2023-03-08 14:20 | 12 | 1:57 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B23030800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2023-03-08 | 1404 | keep | 0 | Mar | 2023 | 0.00095626 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-08 12:28 | 2023-03-08 12:29 | 411 | 0:01 | T | FUEGO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23030800068 | New_Event | Fire | Include | Include | Public | 1 | 2023-03-08 | 411 | keep | 0 | Mar | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
CAGUAS | 2023-03-08 12:32 | 2023-03-08 13:30 | 21 | 0:58 | P | ANIMAL | 1 X 65 EN C/L SE RETIRO AVE | C23030800064 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-03-08 | 1218 | keep | 0 | Mar | 2023 | 0.00082957 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
AGUADILLA | 2023-03-08 12:32 | 2023-03-08 16:02 | 12 | 3:30 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23030800054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2023-03-08 | 2520 | keep | 0 | Mar | 2023 | 0.0017164 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-08 12:46 | 2023-03-08 12:47 | 411 | 0:01 | T | FUEGO | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | M23030800074 | 1st_after_momentary | Fire | Include | Include | Public | 1 | 2023-03-08 | 411 | keep | 0 | Mar | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
ARECIBO | 2023-03-08 13:01 | 2023-03-08 17:10 | 75 | 4:09 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23030800058 | New_Event | Primary Wire Break | Include | Include | Equipment | 249 | 2023-03-08 | 18675 | keep | 0 | Mar | 2023 | 0.012719 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-03-08 13:08 | 2023-03-08 15:54 | 411 | 2:46 | T | FUEGO | DISPARO DE INTERRUPTOR REALIZA TRES OPERACIONES Y QUEDA FUERA DE SERVICIO SE EXTINGUIO FUEGO FORESTAL Y SE CERRO INTERRUPTOR | M23030800077 | 1st_after_momentary | Fire | Include | Include | Public | 166 | 2023-03-08 | 68226 | keep | 0 | Mar | 2023 | 0.046468 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
AGUADILLA | 2023-03-08 13:12 | 2023-03-08 18:00 | 50 | 4:48 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | M23030800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2023-03-08 | 14400 | keep | 0 | Mar | 2023 | 0.0098078 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-08 13:17 | 2023-03-08 23:21 | 38 | 10:04 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA PARA REEMPLAZO DE POSTE PRIMARIO Y REPARAR CONDUCTOR PRIMARIO | S23030800066 | New_Event | Primary Pole Failure | Include | Include | Equipment | 604 | 2023-03-08 | 22952 | keep | 0 | Mar | 2023 | 0.015633 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
SAN JUAN | 2023-03-08 13:25 | 2023-03-08 13:34 | 1825 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 POSTE PARTIDO ENTRE MOD 3015 AL ACB 3089B | S23030800070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-08 | 16425 | keep | 0 | Mar | 2023 | 0.011187 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-03-08 13:25 | 2023-03-08 13:34 | 47 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 POSTE PARTIDO ENTRE MOD 3015 AL ACB 3089B | S23030800070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-08 | 423 | keep | 0 | Mar | 2023 | 0.0002881 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-03-08 13:25 | 2023-03-08 13:34 | 315 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 POSTE PARTIDO ENTRE MOD 3015 AL ACB 3089B | S23030800070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-08 | 2835 | keep | 0 | Mar | 2023 | 0.0019309 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2023-03-08 13:25 | 2023-03-08 13:34 | 2 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 POSTE PARTIDO ENTRE MOD 3015 AL ACB 3089B | S23030800070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-08 | 18 | keep | 0 | Mar | 2023 | 1.226e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-03-08 13:25 | 2023-03-08 13:34 | 2391 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 POSTE PARTIDO ENTRE MOD 3015 AL ACB 3089B | S23030800070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-08 | 21519 | keep | 0 | Mar | 2023 | 0.014656 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2023-03-08 13:25 | 2023-03-08 13:34 | 2276 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 POSTE PARTIDO ENTRE MOD 3015 AL ACB 3089B | C23030800075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-08 | 20484 | keep | 0 | Mar | 2023 | 0.013952 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2023-03-08 13:25 | 2023-03-08 13:34 | 777 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 POSTE PARTIDO ENTRE MOD 3015 AL ACB 3089B | C23030800075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-08 | 6993 | keep | 0 | Mar | 2023 | 0.0047629 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2023-03-08 13:25 | 2023-03-08 13:34 | 12 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 POSTE PARTIDO ENTRE MOD 3015 AL ACB 3089B | C23030800075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-08 | 108 | keep | 0 | Mar | 2023 | 7.3558e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-08 13:25 | 2023-03-08 13:34 | 1290 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 POSTE PARTIDO ENTRE MOD 3015 AL ACB 3089B | C23030800075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-08 | 11610 | keep | 0 | Mar | 2023 | 0.0079075 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
AGUADILLA | 2023-03-08 13:38 | 2023-03-08 15:05 | 18 | 1:27 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE Y ABRIO CAJAS EN TRANSFORMADOR PARA REALIZAR CAMBIO SECUNDARIO | A23030800063 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 87 | 2023-03-08 | 1566 | keep | 0 | Mar | 2023 | 0.0010666 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
FAJARDO | 2023-03-08 13:45 | 2023-03-08 15:04 | 30 | 1:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L REEMPLAZO CAJA AVERIADA | R23030800027 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2023-03-08 | 2370 | keep | 0 | Mar | 2023 | 0.0016142 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-03-08 13:45 | 2023-03-08 16:00 | 10 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23030800107 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2023-03-08 | 1350 | keep | 0 | Mar | 2023 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-08 13:50 | 2023-03-08 14:10 | 24 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | M23030800033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-03-08 | 480 | keep | 0 | Mar | 2023 | 0.00032693 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-03-08 13:51 | 2023-03-08 21:10 | 40 | 7:19 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | S23030800112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 439 | 2023-03-08 | 17560 | keep | 0 | Mar | 2023 | 0.01196 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-03-08 13:52 | 2023-03-08 16:51 | 12 | 2:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23030800078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2023-03-08 | 2148 | keep | 0 | Mar | 2023 | 0.001463 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-08 14:02 | 2023-03-08 14:05 | 1588 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1716-03 SOLO LLEVA EL 90% DE SU CARGA Y LLEVA 1711-01 | B23030800069 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-08 | 4764 | keep | 0 | Mar | 2023 | 0.0032447 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-08 14:02 | 2023-03-08 14:05 | 1630 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO DEL 1716-03 SOLO LLEVA EL 90% DE SU CARGA Y LLEVA 1711-01 | B23030800069 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-08 | 4890 | keep | 0 | Mar | 2023 | 0.0033306 | 0.0011102 | Momentary | FALSE | FALSE | Not_TMED_Event | 1630
ARECIBO | 2023-03-08 14:10 | 2023-03-08 14:50 | 12 | 0:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE | A23030800062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 40 | 2023-03-08 | 480 | keep | 0 | Mar | 2023 | 0.00032693 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-08 14:16 | 2023-03-08 16:37 | 37 | 2:21 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | C23030800088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-03-08 | 5217 | keep | 0 | Mar | 2023 | 0.0035533 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
VEGA BAJA | 2023-03-08 14:25 | 2023-03-08 14:55 | 15 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23030800068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-03-08 | 450 | keep | 0 | Mar | 2023 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-03-08 14:38 | 2023-03-08 18:30 | 10 | 3:52 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A23030800069 | New_Event | Primary Wire Break | Include | Include | Equipment | 232 | 2023-03-08 | 2320 | keep | 0 | Mar | 2023 | 0.0015801 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-08 14:47 | 2023-03-08 14:49 | 1588 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DEL BKR 1716-03 SOLO LLEVA EL 90% DE SU CARGA Y LLEVA EL 1711-01 SE CERRO POR CONTROL | B23030800086 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-08 | 3176 | keep | 0 | Mar | 2023 | 0.0021632 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-08 14:47 | 2023-03-08 14:49 | 1630 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DEL BKR 1716-03 SOLO LLEVA EL 90% DE SU CARGA LLEVA EL 1711-01 SE CERRO POR CONTROL | B23030800086 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-08 | 3260 | keep | 0 | Mar | 2023 | 0.0022204 | 0.0011102 | Momentary | FALSE | FALSE | Not_TMED_Event | 1630
ARECIBO | 2023-03-08 15:21 | 2023-03-08 15:57 | 75 | 0:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030800028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2023-03-08 | 2700 | keep | 0 | Mar | 2023 | 0.001839 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-03-08 15:23 | 2023-03-08 20:44 | 77 | 5:21 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | S23030800175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2023-03-08 | 24717 | keep | 0 | Mar | 2023 | 0.016835 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-03-08 15:30 | 2023-03-08 17:02 | 1588 | 1:32 | T | ALIMENTADOR AMARRADO | DISPARO DEL BKR 1716-03 SOLO LLEVA EL 90% DE SU CARGA Y LLEVA EL 1711-01 SE NORMALIZARON LAS CARGAS CON BY-230308-01 | B23030800099 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 92 | 2023-03-08 | 146096 | keep | 0 | Mar | 2023 | 0.099505 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-08 15:30 | 2023-03-08 16:40 | 1630 | 1:10 | P | NO SE REPORTO CAUSA | DISPARO DEL BKR 1716-03 SOLO LLEVA EL 90% DE SU CARGA Y LLEVA EL 1711-01 SE NORMALIZARON LAS CARGAS CON BY-230308-01 | B23030800099 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 70 | 2023-03-08 | 114100 | keep | 0 | Mar | 2023 | 0.077713 | 0.0011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 1630
SAN JUAN | 2023-03-08 15:30 | 2023-03-08 16:10 | 38 | 0:40 | P | CAUSAS EXTERNAS | SWF SJ-230308-05 SE ABRE MACHETE PARA SECCIONALIZAR POSTE IMPACTADO POR CAMION | S23030800230 | New_Event | Damage From Public | Include | Include | Public | 40 | 2023-03-08 | 1520 | keep | 0 | Mar | 2023 | 0.0010353 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
VEGA BAJA | 2023-03-08 15:30 | 2023-03-08 16:40 | 25 | 1:10 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23030800041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-03-08 | 1750 | keep | 0 | Mar | 2023 | 0.0011919 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-03-08 15:36 | 2023-03-08 16:55 | 5 | 1:19 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | M23030800107 | New_Event | Animals | Include | Include | Wildlife | 79 | 2023-03-08 | 395 | keep | 0 | Mar | 2023 | 0.00026903 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-03-08 15:40 | 2023-03-08 17:45 | 40 | 2:05 | P | DESGANCHE | 1 X 40 EN C/L | R23030800033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-03-08 | 5000 | keep | 0 | Mar | 2023 | 0.0034055 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-08 15:45 | 2023-03-08 18:20 | 2 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA, Y 1 SMU 20 DE 40 AMP. | B23030800115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2023-03-08 | 310 | keep | 0 | Mar | 2023 | 0.00021114 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-08 15:50 | 2023-03-08 20:42 | 11 | 4:52 | P | TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO PISTOLA Y 1X 15 EN RISER | B23030800120 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 292 | 2023-03-08 | 3212 | keep | 0 | Mar | 2023 | 0.0021877 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2023-03-08 15:54 | 2023-03-09 08:33 | 1 | 16:39 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | A23030800091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 999 | 2023-03-08 | 999 | keep | 0 | Mar | 2023 | 0.00068041 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-08 16:05 | 2023-03-08 21:20 | 37 | 5:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B23030800131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2023-03-08 | 11655 | keep | 0 | Mar | 2023 | 0.0079382 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-03-08 16:10 | 2023-03-08 18:33 | 345 | 2:23 | P | CAUSAS EXTERNAS | SWF SJ-230308-05 SE ABRIO PUENTE PARA ESTABLECER GOI Y SE CERRO MACHETE | S23030800230 | Additional_clients | Damage From Public | Include | Include | Public | 143 | 2023-03-08 | 49335 | keep | 0 | Mar | 2023 | 0.033602 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-03-08 16:16 | 2023-03-08 17:26 | 10 | 1:10 | P | CAUSAS EXTERNAS | 1 X 20 EN XMR TENSOR SE CRUZO CON BAJANTE PRIMARIO | C23030800107 | New_Event | Damage From Public | Include | Include | Public | 70 | 2023-03-08 | 700 | keep | 0 | Mar | 2023 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-08 16:39 | 2023-03-08 17:10 | 35 | 0:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M23030800121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2023-03-08 | 1085 | keep | 0 | Mar | 2023 | 0.00073899 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-03-08 16:41 | 2023-03-08 18:33 | 179 | 1:52 | P | CAUSAS EXTERNAS | SWF SJ-230308-05 SE ABRIO MACHETE PARA SECCIONALIZAR TRAMO Y REMPLAZAR POSTE IMPACTADO POR CAMION | S23030800230 | New_Event | Damage From Public | Include | Include | Public | 112 | 2023-03-08 | 20048 | keep | 0 | Mar | 2023 | 0.013655 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
BAYAMON | 2023-03-08 17:05 | 2023-03-08 18:00 | 75 | 0:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030800099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-03-08 | 4125 | keep | 0 | Mar | 2023 | 0.0028095 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
YAUCO | 2023-03-08 17:12 | 2023-03-08 18:10 | 8 | 0:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23030800122 | New_Event | Secondary Wire Break | Include | Include | Equipment | 58 | 2023-03-08 | 464 | keep | 0 | Mar | 2023 | 0.00031603 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-08 17:19 | 2023-03-08 18:40 | 92 | 1:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B23030800162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2023-03-08 | 7452 | keep | 0 | Mar | 2023 | 0.0050755 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
VEGA BAJA | 2023-03-08 17:57 | 2023-03-08 18:03 | 3387 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | B23030800169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-03-08 | 20322 | keep | 0 | Mar | 2023 | 0.013841 | 0.0023069 | Sustained | FALSE | FALSE | Not_TMED_Event | 3387
MAYAGÃœEZ | 2023-03-08 18:00 | 2023-03-08 18:37 | 4 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M23030800118 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-03-08 | 148 | keep | 0 | Mar | 2023 | 0.0001008 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-03-08 18:01 | 2023-03-08 18:04 | 1474 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R23030800041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-08 | 4422 | keep | 0 | Mar | 2023 | 0.0030118 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
VEGA BAJA | 2023-03-08 18:44 | 2023-03-08 18:45 | 1310 | 0:01 | T | DESGANCHE | RECERRE | B2303080000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-08 | 1310 | keep | 0 | Mar | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BARRANQUITAS | 2023-03-08 18:45 | 2023-03-08 19:38 | 13 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REP SECUNDARIA | C23030800122 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-03-08 | 689 | keep | 0 | Mar | 2023 | 0.00046927 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-03-08 18:45 | 2023-03-08 20:30 | 203 | 1:45 | P | DESGANCHE | 2 X 50 EN C/L Y 1 X 65 EN C/L DESGANCHE | B23030800197 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-03-08 | 21315 | keep | 0 | Mar | 2023 | 0.014518 | 0.00013826 | Sustained | FALSE | FALSE | Not_TMED_Event | 203
ARECIBO | 2023-03-08 18:55 | 2023-03-08 20:08 | 40 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23030800109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-03-08 | 2920 | keep | 0 | Mar | 2023 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-08 19:27 | 2023-03-09 06:59 | 250 | 11:32 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 Y 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M23030900141 | New_Event | Primary Wire Break | Include | Include | Equipment | 692 | 2023-03-08 | 173000 | keep | 0 | Mar | 2023 | 0.11783 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2023-03-08 19:40 | 2023-03-09 01:20 | 80 | 5:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO | M23030800147 | New_Event | Primary Wire Break | Include | Include | Equipment | 340 | 2023-03-08 | 27200 | keep | 0 | Mar | 2023 | 0.018526 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-03-08 19:43 | 2023-03-08 21:35 | 150 | 1:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L | B23030800205 | New_Event | Cutout Failure | Include | Include | Equipment | 112 | 2023-03-08 | 16800 | keep | 0 | Mar | 2023 | 0.011442 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-03-08 19:54 | 2023-03-09 02:45 | 160 | 6:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA DE 200 AMP | M23030800152 | New_Event | Cutout Failure | Include | Include | Equipment | 411 | 2023-03-08 | 65760 | keep | 0 | Mar | 2023 | 0.044789 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
PONCE | 2023-03-08 21:05 | 2023-03-08 21:45 | 120 | 0:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO VIENTOS | P23030800147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 40 | 2023-03-08 | 4800 | keep | 0 | Mar | 2023 | 0.0032693 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2023-03-08 21:10 | 2023-03-09 00:14 | 93 | 3:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S23030800376 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2023-03-08 | 17112 | keep | 0 | Mar | 2023 | 0.011655 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
BAYAMON | 2023-03-08 21:20 | 2023-03-09 10:37 | 24 | 13:17 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | B23030800229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 797 | 2023-03-08 | 19128 | keep | 0 | Mar | 2023 | 0.013028 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2023-03-08 22:24 | 2023-03-09 11:07 | 40 | 12:43 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR IGUANA | M23030800197 | New_Event | Animals | Include | Include | Wildlife | 763 | 2023-03-08 | 30520 | keep | 0 | Mar | 2023 | 0.020787 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-03-08 22:48 | 2023-03-09 11:48 | 16 | 13:00 | P | DESGANCHE | 1 X40 EN C/L Y DESGANCHE PRIMARIO | R23030800048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 780 | 2023-03-08 | 12480 | keep | 0 | Mar | 2023 | 0.0085001 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-03-09 01:14 | 2023-03-09 01:15 | 3871 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B23030900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 3871 | keep | 0 | Mar | 2023 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
SAN JUAN | 2023-03-09 01:22 | 2023-03-09 17:31 | 10 | 16:09 | P | ANIMAL | 1 X 50 EN C/L AVE | S23030900003 | New_Event | Animals | Include | Include | Wildlife | 969 | 2023-03-09 | 9690 | keep | 0 | Mar | 2023 | 0.0065998 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-09 01:51 | 2023-03-09 19:00 | 15 | 17:09 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN CORTE DE LINEA SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA | A23030900001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1029 | 2023-03-09 | 15435 | keep | 0 | Mar | 2023 | 0.010513 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-03-09 02:09 | 2023-03-09 12:25 | 20 | 10:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | A23030900002 | New_Event | Primary Wire Break | Include | Include | Equipment | 616 | 2023-03-09 | 12320 | keep | 0 | Mar | 2023 | 0.0083911 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-03-09 02:09 | 2023-03-09 07:16 | 6 | 5:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR REPARO SECUNDARIA | C23030900014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 307 | 2023-03-09 | 1842 | keep | 0 | Mar | 2023 | 0.0012546 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-03-09 02:23 | 2023-03-09 04:00 | 47 | 1:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23030900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-03-09 | 4559 | keep | 0 | Mar | 2023 | 0.0031051 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
CANOVANAS | 2023-03-09 03:17 | 2023-03-09 03:19 | 5668 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R23030900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-09 | 11336 | keep | 0 | Mar | 2023 | 0.0077209 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2023-03-09 05:04 | 2023-03-09 05:08 | 1208 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | S23030900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-09 | 4832 | keep | 0 | Mar | 2023 | 0.0032911 | 0.00082276 | Momentary | FALSE | FALSE | Not_TMED_Event | 1208
HUMACAO | 2023-03-09 05:09 | 2023-03-09 07:19 | 271 | 2:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | C23030900004 | New_Event | Cutout Failure | Include | Include | Equipment | 130 | 2023-03-09 | 35230 | keep | 0 | Mar | 2023 | 0.023995 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
BARRANQUITAS | 2023-03-09 05:31 | 2023-03-09 08:57 | 16 | 3:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L REMPLAZO PORTAFUSIBLE | C23030900005 | New_Event | Cutout Failure | Include | Include | Equipment | 206 | 2023-03-09 | 3296 | keep | 0 | Mar | 2023 | 0.0022449 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-03-09 06:19 | 2023-03-09 14:13 | 22 | 7:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU | S23030900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 474 | 2023-03-09 | 10428 | keep | 0 | Mar | 2023 | 0.0071025 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
YAUCO | 2023-03-09 06:26 | 2023-03-09 09:46 | 109 | 3:20 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR DESGANCHE | P23030900011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-03-09 | 21800 | keep | 0 | Mar | 2023 | 0.014848 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
PONCE | 2023-03-09 06:30 | 2023-03-09 07:55 | 12 | 1:25 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO LINEA SECUNDARIA | P23030900012 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 85 | 2023-03-09 | 1020 | keep | 0 | Mar | 2023 | 0.00069472 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-03-09 06:38 | 2023-03-09 11:32 | 40 | 4:54 | P | DESGANCHE | 1 X 40 EN C/L | C23030900009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-03-09 | 11760 | keep | 0 | Mar | 2023 | 0.0080097 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-03-09 07:06 | 2023-03-09 10:56 | 14 | 3:50 | P | CAUSAS EXTERNAS | 1 X 30 EN C/L MAQUINA PESADA IMPACTO EL POSTE Y SACUDIO LAS LINEAS | C23030900016 | New_Event | Damage From Public | Include | Include | Public | 230 | 2023-03-09 | 3220 | keep | 0 | Mar | 2023 | 0.0021931 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-03-09 07:23 | 2023-03-09 10:45 | 20 | 3:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M23030900009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-03-09 | 4040 | keep | 0 | Mar | 2023 | 0.0027516 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-09 07:48 | 2023-03-09 15:30 | 2 | 7:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 2 X 25 EN BANCO DE XMR 2 X 40 EN CL | S23030900025 | New_Event | Cutout Failure | Include | Include | Equipment | 462 | 2023-03-09 | 924 | keep | 0 | Mar | 2023 | 0.00062933 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-09 08:35 | 2023-03-09 08:36 | 1210 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23030900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 1210 | keep | 0 | Mar | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
SAN JUAN | 2023-03-09 08:45 | 2023-03-09 17:22 | 62 | 8:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO 3 CAJAS PRIMARIA Y 3 PARARAYO | S23030900043 | New_Event | Cutout Failure | Include | Include | Equipment | 517 | 2023-03-09 | 32054 | keep | 0 | Mar | 2023 | 0.021832 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-03-09 09:06 | 2023-03-09 09:07 | 1859 | 0:01 | T | CAUSAS EXTERNAS | RECERRO | B23030900015 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-03-09 | 1859 | keep | 0 | Mar | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2023-03-09 09:07 | 2023-03-09 11:51 | 90 | 2:44 | P | CAUSAS EXTERNAS | 1X100 EN C/L POR COMPAÃ‘IA AJENA A LUMA REALIZANDO DESGANCHE | B23030900021 | 1st_after_momentary | Damage From Public | Include | Include | Public | 164 | 2023-03-09 | 14760 | keep | 0 | Mar | 2023 | 0.010053 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2023-03-09 09:17 | 2023-03-09 09:18 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030900031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 1702 | keep | 0 | Mar | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
GUAYAMA | 2023-03-09 09:48 | 2023-03-09 13:20 | 70 | 3:32 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO PUENTE SAFADO EN CORTE DE LINEA | P23030900037 | New_Event | Primary Wire Break | Include | Include | Equipment | 212 | 2023-03-09 | 14840 | keep | 0 | Mar | 2023 | 0.010107 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-03-09 09:52 | 2023-03-09 18:35 | 18 | 8:43 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN SU 2 X 65 EN RISER SE REPARO PUENTE PRIMARIO | S23030900058 | New_Event | Primary Wire Break | Include | Include | Equipment | 523 | 2023-03-09 | 9414 | keep | 0 | Mar | 2023 | 0.0064118 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-03-09 09:54 | 2023-03-09 09:56 | 312 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1345-02 LLEVA 80% DEL 1342-04 SE CERRO POR CONTROL | S23030900060 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-09 | 624 | keep | 0 | Mar | 2023 | 0.000425 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-03-09 09:54 | 2023-03-09 09:56 | 435 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1345-02 LLEVA 80% DEL 1342-04 SE CERRO POR CONTROL | S23030900060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-09 | 870 | keep | 0 | Mar | 2023 | 0.00059255 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-03-09 10:04 | 2023-03-09 14:41 | 10 | 4:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L PORTAFUSIBLES | S23030900062 | New_Event | Cutout Failure | Include | Include | Equipment | 277 | 2023-03-09 | 2770 | keep | 0 | Mar | 2023 | 0.0018866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-09 10:06 | 2023-03-09 15:16 | 312 | 5:10 | P | DESGANCHE | 1 X 65 EN CL 1 X 50 EN C/L DESGANCHE | S23030900066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2023-03-09 | 96720 | keep | 0 | Mar | 2023 | 0.065876 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
CANOVANAS | 2023-03-09 10:13 | 2023-03-09 12:58 | 15 | 2:45 | P | DESGANCHE | 2 X 25 EN BANCO DE XMR Y DESGANCHE PRIMARIO | R23030900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-03-09 | 2475 | keep | 0 | Mar | 2023 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-03-09 10:15 | 2023-03-09 11:45 | 10 | 1:30 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | REMPLAZO DE BARRAS EN PEDESTAL | P23030900048 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 90 | 2023-03-09 | 900 | keep | 0 | Mar | 2023 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-09 10:28 | 2023-03-09 10:29 | 2107 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23030900035 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-09 | 2107 | keep | 0 | Mar | 2023 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2023-03-09 10:29 | 2023-03-09 12:20 | 15 | 1:51 | P | ANIMAL | 1 X 80 EN CL CRUCE DE FASE POR AVE | A23030900039 | 1st_after_momentary | Animals | Include | Include | Wildlife | 111 | 2023-03-09 | 1665 | keep | 0 | Mar | 2023 | 0.001134 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-09 10:47 | 2023-03-09 10:51 | 427 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S23030900091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-09 | 1708 | keep | 0 | Mar | 2023 | 0.0011633 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
PONCE | 2023-03-09 10:50 | 2023-03-09 15:41 | 50 | 4:51 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PALOMA CRUZO FASE | P23030900061 | New_Event | Animals | Include | Include | Wildlife | 291 | 2023-03-09 | 14550 | keep | 0 | Mar | 2023 | 0.0099099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-03-09 10:50 | 2023-03-09 18:24 | 4 | 7:34 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE PRIMARIO PARTIDO | M23030900043 | New_Event | Primary Pole Failure | Include | Include | Equipment | 454 | 2023-03-09 | 1816 | keep | 0 | Mar | 2023 | 0.0012369 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-03-09 10:56 | 2023-03-09 14:18 | 50 | 3:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA QUEMADA | C23030900043 | New_Event | Cutout Failure | Include | Include | Equipment | 202 | 2023-03-09 | 10100 | keep | 0 | Mar | 2023 | 0.0068791 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-09 10:58 | 2023-03-09 10:59 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2303090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 3070 | keep | 0 | Mar | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
GUAYAMA | 2023-03-09 11:01 | 2023-03-09 12:20 | 30 | 1:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA 1 X 80 EN CORTE DE LINEA | P23030900066 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2023-03-09 | 2370 | keep | 0 | Mar | 2023 | 0.0016142 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-03-09 11:01 | 2023-03-09 13:15 | 596 | 2:14 | P | ANIMAL | 2 X 100 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO POR IGUANA | P23030900047 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-03-09 | 79864 | keep | 0 | Mar | 2023 | 0.054395 | 0.00040593 | Sustained | FALSE | FALSE | Not_TMED_Event | 596
MAYAGÃœEZ | 2023-03-09 11:04 | 2023-03-09 12:29 | 60 | 1:25 | P | ANIMAL | 1 X 80 Y 1 X 65 EN CORTE DE LINEA POR AVE | M23030900049 | New_Event | Animals | Include | Include | Wildlife | 85 | 2023-03-09 | 5100 | keep | 0 | Mar | 2023 | 0.0034736 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-03-09 11:08 | 2023-03-09 14:20 | 13 | 3:12 | P | CAUSAS EXTERNAS | 1 X 15 EN XMR REPARO SECUNDARIA AVERIADA X CAMION | C23030900071 | New_Event | Damage From Public | Include | Include | Public | 192 | 2023-03-09 | 2496 | keep | 0 | Mar | 2023 | 0.0017 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-03-09 11:30 | 2023-03-09 11:31 | 312 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1345-02 LLEVA 80% DEL 1342-04 SE CERRO POR CONTROL | S23030900104 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-09 | 312 | keep | 0 | Mar | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-03-09 11:30 | 2023-03-09 11:31 | 435 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1345-02 LLEVA 80% DEL 1342-04 SE CERRO POR CONTROL | S23030900104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 435 | keep | 0 | Mar | 2023 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
BARRANQUITAS | 2023-03-09 11:36 | 2023-03-09 11:37 | 1843 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030900054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 1843 | keep | 0 | Mar | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-03-09 11:40 | 2023-03-09 11:41 | 1843 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22070200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 1843 | keep | 0 | Mar | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
HUMACAO | 2023-03-09 11:48 | 2023-03-09 14:49 | 155 | 3:01 | P | ARBOL SOBRE LINEA | 3 X 50 Y 1 X 65 EN C/L RETIRO ARBOL DE LAS LINEAS Y REMPLAZO AISLADOR | C23030900057 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 181 | 2023-03-09 | 28055 | keep | 0 | Mar | 2023 | 0.019108 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
VEGA BAJA | 2023-03-09 11:51 | 2023-03-09 14:28 | 53 | 2:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B23030900051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-03-09 | 8321 | keep | 0 | Mar | 2023 | 0.0056674 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
GUAYAMA | 2023-03-09 11:54 | 2023-03-09 11:55 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P2.020300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 1945 | keep | 0 | Mar | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
SAN JUAN | 2023-03-09 12:19 | 2023-03-09 12:23 | 427 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S2303090000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-09 | 1708 | keep | 0 | Mar | 2023 | 0.0011633 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
SAN JUAN | 2023-03-09 12:22 | 2023-03-09 16:33 | 95 | 4:11 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | S23030900125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 251 | 2023-03-09 | 23845 | keep | 0 | Mar | 2023 | 0.016241 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
SAN JUAN | 2023-03-09 12:30 | 2023-03-09 15:24 | 31 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23030900130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2023-03-09 | 5394 | keep | 0 | Mar | 2023 | 0.0036738 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
MAYAGÃœEZ | 2023-03-09 12:32 | 2023-03-09 15:40 | 45 | 3:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23030900066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-03-09 | 8460 | keep | 0 | Mar | 2023 | 0.0057621 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-03-09 12:34 | 2023-03-09 12:35 | 1420 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1526-02 LLEVA 1530-06 SE CERRO POR CONTROL | S23030900134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 1420 | keep | 0 | Mar | 2023 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
SAN JUAN | 2023-03-09 12:34 | 2023-03-09 12:35 | 437 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1526-02 LLEVA 1530-06 SE CERRO POR CONTROL | S23030900134 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-09 | 437 | keep | 0 | Mar | 2023 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2023-03-09 12:38 | 2023-03-09 14:40 | 60 | 2:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23030900057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-03-09 | 7320 | keep | 0 | Mar | 2023 | 0.0049856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-09 12:40 | 2023-03-09 14:48 | 411 | 2:08 | T | NO SE REPORTO CAUSA | SWF 230309-01 DISPARO DEL 1530-10 LLEVA 1924-02 LLEVA 1924-03 SE REALIZARON OPERACIONES PARA SECCIONALIZAR 80% EN SERVICO DEL 1530-10 | S23030900137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2023-03-09 | 52608 | keep | 0 | Mar | 2023 | 0.035831 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
BAYAMON | 2023-03-09 12:40 | 2023-03-09 15:00 | 72 | 2:20 | T | ALIMENTADOR AMARRADO | SWF 230309-01 DISPARO DEL 1530-10 SE CERRO AMARRE CONTRA EL 1924-02 | S23030900137 | New_Event | Feeder Load Transferred | Include | Include | Other | 140 | 2023-03-09 | 10080 | keep | 0 | Mar | 2023 | 0.0068654 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2023-03-09 12:40 | 2023-03-09 15:11 | 5 | 2:31 | T | ALIMENTADOR AMARRADO | SWF 230309-01 DISPARO DEL 1530-10 SE CERRO AMARRE CONTRA EL 1924-03 | S23030900137 | New_Event | Feeder Load Transferred | Include | Include | Other | 151 | 2023-03-09 | 755 | keep | 0 | Mar | 2023 | 0.00051423 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-03-09 12:42 | 2023-03-09 14:18 | 140 | 1:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23030900091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-03-09 | 13440 | keep | 0 | Mar | 2023 | 0.0091539 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CANOVANAS | 2023-03-09 12:46 | 2023-03-09 12:47 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2303090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 4981 | keep | 0 | Mar | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
ARECIBO | 2023-03-09 12:49 | 2023-03-09 17:45 | 100 | 4:56 | P | CAUSAS EXTERNAS | 2 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS CAMION DANDO REVERSA TOCO TENSORES | A23030900062 | New_Event | Damage From Public | Include | Include | Public | 296 | 2023-03-09 | 29600 | keep | 0 | Mar | 2023 | 0.02016 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-09 12:56 | 2023-03-09 18:40 | 113 | 5:44 | P | DESGANCHE | 2 X 65 C/L DESGANCHE | S23030900152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2023-03-09 | 38872 | keep | 0 | Mar | 2023 | 0.026476 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
CANOVANAS | 2023-03-09 13:08 | 2023-03-09 15:05 | 10 | 1:57 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | R23030900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-03-09 | 1170 | keep | 0 | Mar | 2023 | 0.00079688 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-03-09 13:25 | 2023-03-09 14:26 | 34 | 1:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO C/L PARA REMPLAZAR AISLADOR | C23030900075 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 61 | 2023-03-09 | 2074 | keep | 0 | Mar | 2023 | 0.0014126 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2023-03-09 13:26 | 2023-03-09 20:11 | 9 | 6:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BARRA EN PEDESTAL | C23030900077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 405 | 2023-03-09 | 3645 | keep | 0 | Mar | 2023 | 0.0024826 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-03-09 13:27 | 2023-03-09 15:36 | 40 | 2:09 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23030900078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-03-09 | 5160 | keep | 0 | Mar | 2023 | 0.0035145 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-03-09 13:30 | 2023-03-09 13:31 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23030900101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 3973 | keep | 0 | Mar | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
SAN JUAN | 2023-03-09 13:42 | 2023-03-09 13:43 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2303090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 4291 | keep | 0 | Mar | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
GUAYAMA | 2023-03-09 13:45 | 2023-03-09 17:20 | 10 | 3:35 | P | SECUNDARIA/OTROS | REEMPLAZO DE BARRAS EN PEDESTAL | P23030900108 | New_Event |  |  |  |  | 215 | 2023-03-09 | 2150 | keep | 0 | Mar | 2023 | 0.0014644 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-09 13:47 | 2023-03-09 16:08 | 1 | 2:21 | P | DESGANCHE | 1 X 25 EN C/L SE REALIZO DESGANCHE | P23030900106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-03-09 | 141 | keep | 0 | Mar | 2023 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-09 13:47 | 2023-03-09 14:27 | 7 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B23030900060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-03-09 | 280 | keep | 0 | Mar | 2023 | 0.00019071 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-03-09 13:55 | 2023-03-09 18:58 | 50 | 5:03 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA RAMA SOBRE LINEA | P23030900109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2023-03-09 | 15150 | keep | 0 | Mar | 2023 | 0.010319 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-03-09 14:05 | 2023-03-09 15:40 | 15 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIAS AVERIADAS | M23030900069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2023-03-09 | 1425 | keep | 0 | Mar | 2023 | 0.00097056 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-03-09 14:08 | 2023-03-09 14:09 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23030900115 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 3973 | keep | 0 | Mar | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
SAN JUAN | 2023-03-09 14:09 | 2023-03-09 19:03 | 20 | 4:54 | P | CONDUCTOR ROTO O ABIERTO | 1 X 25 EN XMR Y SE REPARO BAJANTE PRIMARIO | S23030900202 | New_Event | Primary Wire Break | Include | Include | Equipment | 294 | 2023-03-09 | 5880 | keep | 0 | Mar | 2023 | 0.0040048 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-09 14:25 | 2023-03-09 16:36 | 8 | 2:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR LA SECUNDARIA | B23030900063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 131 | 2023-03-09 | 1048 | keep | 0 | Mar | 2023 | 0.00071379 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-03-09 14:26 | 2023-03-09 16:35 | 45 | 2:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23030900102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-03-09 | 5805 | keep | 0 | Mar | 2023 | 0.0039538 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-03-09 14:31 | 2023-03-09 20:58 | 57 | 6:27 | P | DESGANCHE | 3 X 10 C/L DESGANCHE | S23030900215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 387 | 2023-03-09 | 22059 | keep | 0 | Mar | 2023 | 0.015024 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
YAUCO | 2023-03-09 14:31 | 2023-03-09 14:32 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23030900124 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 3973 | keep | 0 | Mar | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
AGUADILLA | 2023-03-09 14:31 | 2023-03-10 12:25 | 50 | 21:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23030900103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1314 | 2023-03-09 | 65700 | keep | 0 | Mar | 2023 | 0.044748 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-03-09 14:34 | 2023-03-09 14:35 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23030900127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 3973 | keep | 0 | Mar | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
SAN JUAN | 2023-03-09 14:40 | 2023-03-09 16:42 | 150 | 2:02 | P | DESGANCHE | 1 X 100 EN CL Y DESGANCHE | S23030900220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-03-09 | 18300 | keep | 0 | Mar | 2023 | 0.012464 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-03-09 14:46 | 2023-03-09 18:24 | 238 | 3:38 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA SE RETIRO GALLINA DE PALO | B23030900067 | New_Event | Animals | Include | Include | Wildlife | 218 | 2023-03-09 | 51884 | keep | 0 | Mar | 2023 | 0.035338 | 0.0001621 | Sustained | FALSE | FALSE | Not_TMED_Event | 238
BAYAMON | 2023-03-09 14:48 | 2023-03-09 14:58 | 82 | 0:10 | P | NO SE REPORTO CAUSA | SWF 230309-01 LLEVA 1924-02 LLEVA 1924-03 SE ABRIO AMARRE ENTRE 1924-03 Y 02 100% EN SERVICO DEL 1530-10 | S23030900137 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 10 | 2023-03-09 | 820 | keep | 0 | Mar | 2023 | 0.0005585 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-03-09 14:50 | 2023-03-09 14:51 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23030900138 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 3973 | keep | 0 | Mar | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
HUMACAO | 2023-03-09 14:51 | 2023-03-09 15:59 | 56 | 1:08 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23030900094 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-03-09 | 3808 | keep | 0 | Mar | 2023 | 0.0025936 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
YAUCO | 2023-03-09 14:58 | 2023-03-09 14:59 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23030900140 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 3973 | keep | 0 | Mar | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
BAYAMON | 2023-03-09 15:00 | 2023-03-09 19:47 | 47 | 4:47 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S23030900240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2023-03-09 | 13489 | keep | 0 | Mar | 2023 | 0.0091873 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
YAUCO | 2023-03-09 15:02 | 2023-03-09 15:03 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RE3CIERRE | P23030900149 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 3973 | keep | 0 | Mar | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
CANOVANAS | 2023-03-09 15:11 | 2023-03-09 17:44 | 10 | 2:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE CAJA PRIMARIA | R23030900035 | New_Event | Primary Wire Break | Include | Include | Equipment | 153 | 2023-03-09 | 1530 | keep | 0 | Mar | 2023 | 0.0010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-09 15:17 | 2023-03-09 15:37 | 7 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23030900080 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-03-09 | 140 | keep | 0 | Mar | 2023 | 9.5353e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-09 15:20 | 2023-03-09 18:38 | 50 | 3:18 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B23030900071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2023-03-09 | 9900 | keep | 0 | Mar | 2023 | 0.0067428 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-09 15:43 | 2023-03-10 14:49 | 44 | 23:06 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | S23030900262 | New_Event | Primary Wire Break | Include | Include | Equipment | 1386 | 2023-03-09 | 60984 | keep | 0 | Mar | 2023 | 0.041536 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
SAN JUAN | 2023-03-09 15:46 | 2023-03-09 20:46 | 130 | 5:00 | P | CONDUCTOR ROTO O ABIERTO | 3 X 65 EN CORTE DE LINEA SE REPARO CONDUCTOR PRIMARIA TRASPATIO | S23030900264 | New_Event | Primary Wire Break | Include | Include | Equipment | 300 | 2023-03-09 | 39000 | keep | 0 | Mar | 2023 | 0.026563 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2023-03-09 15:48 | 2023-03-09 22:13 | 150 | 6:25 | P | TRANSFORMADOR AVERIADO | 1 X 100 EN C/L SE REMPLAZO CAJA SE DEJO MONTURA DE 167KVA FUERA AVERIADO | S23030900266 | New_Event | Service Transformer Failure | Include | Include | Equipment | 385 | 2023-03-09 | 57750 | keep | 0 | Mar | 2023 | 0.039333 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-03-09 15:52 | 2023-03-09 17:28 | 88 | 1:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B23030900077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-03-09 | 8448 | keep | 0 | Mar | 2023 | 0.0057539 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
SAN JUAN | 2023-03-09 16:01 | 2023-03-09 18:34 | 64 | 2:33 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | S23030900268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-03-09 | 9792 | keep | 0 | Mar | 2023 | 0.0066693 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
ARECIBO | 2023-03-09 16:16 | 2023-03-09 18:35 | 10 | 2:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS Y BAMBUS SOBRE LAS LINEAS | A23030900093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-03-09 | 1390 | keep | 0 | Mar | 2023 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-03-09 16:27 | 2023-03-09 17:23 | 1676 | 0:56 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO INTERRUPTOR Y SE AMARRA CON EL 2 POR ESTAR DEFECTUOSO | P23030900186 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 56 | 2023-03-09 | 93856 | keep | 0 | Mar | 2023 | 0.063925 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
CANOVANAS | 2023-03-09 16:38 | 2023-03-09 19:18 | 15 | 2:40 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23030900039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-03-09 | 2400 | keep | 0 | Mar | 2023 | 0.0016346 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-03-09 16:54 | 2023-03-09 16:55 | 680 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23030900190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 680 | keep | 0 | Mar | 2023 | 0.00046314 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
MAYAGÃœEZ | 2023-03-09 16:58 | 2023-03-10 09:30 | 25 | 16:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN CL FUERTES VIENTOS | M23030900141 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 992 | 2023-03-09 | 24800 | keep | 0 | Mar | 2023 | 0.016891 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-03-09 17:05 | 2023-03-10 13:20 | 25 | 20:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23030900145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1215 | 2023-03-09 | 30375 | keep | 0 | Mar | 2023 | 0.020688 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-03-09 17:20 | 2023-03-09 18:42 | 8 | 1:22 | P | CONDUCTOR ROTO O ABIERTO | ABRIO XMR PARA REMPLAZAR EL NEUTRAL PRIMARIO DEL BAJANTE DEL XMR | C23030900125 | New_Event | Primary Wire Break | Include | Include | Equipment | 82 | 2023-03-09 | 656 | keep | 0 | Mar | 2023 | 0.0004468 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-03-09 17:25 | 2023-03-09 19:08 | 40 | 1:43 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23030900097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-03-09 | 4120 | keep | 0 | Mar | 2023 | 0.0028061 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-03-09 17:49 | 2023-03-09 17:51 | 143 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 80% DEL 1404-07 | S23030900286 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-09 | 286 | keep | 0 | Mar | 2023 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-03-09 17:49 | 2023-03-09 17:51 | 1085 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1404-06 CERRADO POR CONTROL 80% X 1404-06 | S23030900286 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-09 | 2170 | keep | 0 | Mar | 2023 | 0.001478 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2023-03-09 17:57 | 2023-03-09 21:00 | 3 | 3:03 | P | ANIMAL | 1 X 15 EN XMR AVE | B23030900102 | New_Event | Animals | Include | Include | Wildlife | 183 | 2023-03-09 | 549 | keep | 0 | Mar | 2023 | 0.00037392 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2023-03-09 17:58 | 2023-03-09 20:06 | 50 | 2:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23030900154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-03-09 | 6400 | keep | 0 | Mar | 2023 | 0.004359 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-03-09 18:10 | 2023-03-09 18:25 | 20 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23030900153 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-03-09 | 300 | keep | 0 | Mar | 2023 | 0.00020433 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-03-09 18:24 | 2023-03-09 18:50 | 4 | 0:26 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR POR AVE | P23030900233 | New_Event | Animals | Include | Include | Wildlife | 26 | 2023-03-09 | 104 | keep | 0 | Mar | 2023 | 7.0834e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-03-09 18:42 | 2023-03-10 09:26 | 160 | 14:44 | P | CAUSAS EXTERNAS | SE REMPLAZO POSTE CAMION IMPACTO POSTE SJ-230308-50 | S23030900295 | New_Event | Damage From Public | Include | Include | Public | 884 | 2023-03-09 | 141440 | keep | 0 | Mar | 2023 | 0.096334 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
PONCE | 2023-03-09 19:00 | 2023-03-09 19:01 | 2446 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23030900246 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 2446 | keep | 0 | Mar | 2023 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
VEGA BAJA | 2023-03-09 19:00 | 2023-03-10 18:25 | 10 | 23:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA Y BAJANTE DE XMR | B23030900108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1405 | 2023-03-09 | 14050 | keep | 0 | Mar | 2023 | 0.0095694 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-09 19:01 | 2023-03-09 21:03 | 3 | 2:02 | P | DESGANCHE | 1 X 25 EN C/L SE REALIZO DESGANCHE | R23030900045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-03-09 | 366 | keep | 0 | Mar | 2023 | 0.00024928 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2023-03-09 19:04 | 2023-03-10 16:40 | 60 | 21:36 | P | ARBOL SOBRE LINEA | 3 X 40 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO ARBOL SE PARTIO QUEDO SOBRE LINEAS | A23030900110 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1296 | 2023-03-09 | 77760 | keep | 0 | Mar | 2023 | 0.052962 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-03-09 19:04 | 2023-03-10 12:00 | 10 | 16:56 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23030900096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1016 | 2023-03-09 | 10160 | keep | 0 | Mar | 2023 | 0.0069199 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-03-09 19:10 | 2023-03-09 19:28 | 6 | 0:18 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | R23030900046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 18 | 2023-03-09 | 108 | keep | 0 | Mar | 2023 | 7.3558e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-03-09 19:11 | 2023-03-09 20:43 | 9 | 1:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO EL PORTAFUSIBLE | C23030900127 | New_Event | Cutout Failure | Include | Include | Equipment | 92 | 2023-03-09 | 828 | keep | 0 | Mar | 2023 | 0.00056395 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2023-03-09 19:30 | 2023-03-10 06:55 | 117 | 11:25 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE | P23030900248 | New_Event | Animals | Include | Include | Wildlife | 685 | 2023-03-09 | 80145 | keep | 0 | Mar | 2023 | 0.054586 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
MAYAGÃœEZ | 2023-03-09 19:30 | 2023-03-09 20:20 | 4 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23030900143 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-03-09 | 200 | keep | 0 | Mar | 2023 | 0.00013622 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-03-09 19:34 | 2023-03-09 20:28 | 207 | 0:54 | T | NO SE REPORTO CAUSA | SE ENCONTRO INTERRUPTOR ABIERTO SE CERRO MANUALMENTE LUEGO DE PATRULLAR | P23030900250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2023-03-09 | 11178 | keep | 0 | Mar | 2023 | 0.0076133 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
YAUCO | 2023-03-09 19:34 | 2023-03-09 20:28 | 286 | 0:54 | T | NO SE REPORTO CAUSA | SE ENCONYTRO INTERRUPTOR 1 ABIERTO SE CERRO MANUALMENTE | P23030900250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2023-03-09 | 15444 | keep | 0 | Mar | 2023 | 0.010519 | 0.00019479 | Sustained | FALSE | FALSE | Not_TMED_Event | 286
MAYAGÃœEZ | 2023-03-09 19:34 | 2023-03-09 21:20 | 50 | 1:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23030900181 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2023-03-09 | 5300 | keep | 0 | Mar | 2023 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-09 19:43 | 2023-03-09 21:53 | 140 | 2:10 | P | DESGANCHE | 1 SMU 20 DE 80 AMP. SU-4 Y 1 X 65 EN RISER SE REALIZO DESGANCHE EN RISER | B23030900111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-03-09 | 18200 | keep | 0 | Mar | 2023 | 0.012396 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CAGUAS | 2023-03-09 19:55 | 2023-03-09 19:56 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23030900128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 2178 | keep | 0 | Mar | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CANOVANAS | 2023-03-09 20:01 | 2023-03-09 21:53 | 1644 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE ABIERTO EN LA SALIDA DEL BKR | R23030900048 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2023-03-09 | 184128 | keep | 0 | Mar | 2023 | 0.12541 | 0.0011197 | Sustained | FALSE | FALSE | Not_TMED_Event | 1644
MAYAGÃœEZ | 2023-03-09 20:06 | 2023-03-10 11:19 | 30 | 15:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M23030900185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 913 | 2023-03-09 | 27390 | keep | 0 | Mar | 2023 | 0.018655 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-03-09 20:20 | 2023-03-09 21:54 | 10 | 1:34 | P | ANIMAL | 1 X 25 EN C/L CRUCE X IGUANA | R23030900104 | New_Event | Animals | Include | Include | Wildlife | 94 | 2023-03-09 | 940 | keep | 0 | Mar | 2023 | 0.00064023 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-03-09 20:43 | 2023-03-10 08:05 | 4 | 11:22 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | M23030900191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 682 | 2023-03-09 | 2728 | keep | 0 | Mar | 2023 | 0.001858 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-03-09 20:52 | 2023-03-10 09:31 | 1 | 12:39 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23030900214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 759 | 2023-03-09 | 759 | keep | 0 | Mar | 2023 | 0.00051695 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-09 21:11 | 2023-03-10 10:42 | 30 | 13:31 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA DESGANCHE | S23030900316 | New_Event | Vegetation Contact | Include | Include | Vegetation | 811 | 2023-03-09 | 24330 | keep | 0 | Mar | 2023 | 0.016571 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-03-09 21:13 | 2023-03-09 21:14 | 143 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 80% DEL 1404-07 | S23030900318 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 143 | keep | 0 | Mar | 2023 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-03-09 21:13 | 2023-03-09 21:14 | 1085 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1404-06 CERRADO POR CONTROL 80% POR 1404-06 | S23030900318 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-09 | 1085 | keep | 0 | Mar | 2023 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2023-03-09 21:20 | 2023-03-09 21:21 | 1647 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B23030900112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 1647 | keep | 0 | Mar | 2023 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
YAUCO | 2023-03-09 21:25 | 2023-03-09 23:00 | 43 | 1:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23030900276 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-03-09 | 4085 | keep | 0 | Mar | 2023 | 0.0027823 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2023-03-09 21:53 | 2023-03-09 21:56 | 4312 | 0:03 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA DIVIDIR LA CARGA DEL 1336-06 Y SE CERRO CONTRA EL 1619-02. ENTRANDO APROX 87% EN SERVICIO | R23030900048 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 3 | 2023-03-09 | 12936 | keep | 0 | Mar | 2023 | 0.0088107 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-09 21:56 | 2023-03-09 22:15 | 669 | 0:19 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO AMARRE CONTRA EL 1620-04 ENTRANDO 100% EN SERVICIO. SE DEJO ABIERTO Y TAG EL RISER DE SALIDA DEL 1336-06. | R23030900048 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 19 | 2023-03-09 | 12711 | keep | 0 | Mar | 2023 | 0.0086574 | 0.00045565 | Sustained | FALSE | FALSE | Not_TMED_Event | 669
YAUCO | 2023-03-09 22:12 | 2023-03-10 20:12 | 200 | 22:00 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTARON 2 FASES PRIMARIAS Y DESGANCHE 1 X 80 EN CORTE DE LINEA 1 X 40 EN DIFERENTE CORTE DE LINEA | P23030900291 | New_Event | Primary Wire Break | Include | Include | Equipment | 1320 | 2023-03-09 | 264000 | keep | 0 | Mar | 2023 | 0.17981 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-03-09 22:13 | 2023-03-10 17:21 | 8 | 19:08 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 167 KVA X 167 KVA EN LA PARALELA | S23030900266 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1148 | 2023-03-09 | 9184 | keep | 0 | Mar | 2023 | 0.0062552 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-03-09 22:19 | 2023-03-10 11:06 | 36 | 12:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23030900293 | New_Event | Vegetation Contact | Include | Include | Vegetation | 767 | 2023-03-09 | 27612 | keep | 0 | Mar | 2023 | 0.018806 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
YAUCO | 2023-03-09 22:22 | 2023-03-10 09:07 | 30 | 10:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23030900191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 645 | 2023-03-09 | 19350 | keep | 0 | Mar | 2023 | 0.013179 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-09 22:54 | 2023-03-09 22:55 | 2362 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C23030900137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-09 | 2362 | keep | 0 | Mar | 2023 | 0.0016087 | 0.0016087 | Momentary | FALSE | FALSE | Not_TMED_Event | 2362
BARRANQUITAS | 2023-03-09 22:55 | 2023-03-10 07:32 | 66 | 8:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23030900138 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 517 | 2023-03-09 | 34122 | keep | 0 | Mar | 2023 | 0.02324 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
SAN JUAN | 2023-03-09 23:02 | 2023-03-10 13:12 | 5 | 14:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA 1 X 50 EN RISER NO CAUSA | S23030900330 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 850 | 2023-03-09 | 4250 | keep | 0 | Mar | 2023 | 0.0028947 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-03-09 23:44 | 2023-03-10 01:39 | 115 | 1:55 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23030900113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-03-09 | 13225 | keep | 0 | Mar | 2023 | 0.0090075 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
CANOVANAS | 2023-03-09 23:45 | 2023-03-10 11:00 | 10 | 11:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE CON "SHOTGUN" TRASPATIO Y SE CERRO CORTE DE LINEA. | R23030900315 | New_Event | Primary Wire Break | Include | Include | Equipment | 675 | 2023-03-09 | 6750 | keep | 0 | Mar | 2023 | 0.0045974 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-10 04:00 | 2023-03-10 18:41 | 2 | 14:41 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | B23031000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 881 | 2023-03-10 | 1762 | keep | 0 | Mar | 2023 | 0.0012001 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-03-10 04:01 | 2023-03-10 07:55 | 135 | 3:54 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | P23031000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2023-03-10 | 31590 | keep | 0 | Mar | 2023 | 0.021516 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2023-03-10 04:27 | 2023-03-10 04:28 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23031000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-10 | 1026 | keep | 0 | Mar | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-03-10 04:27 | 2023-03-10 13:15 | 2 | 8:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | R23031000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 528 | 2023-03-10 | 1056 | keep | 0 | Mar | 2023 | 0.00071924 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-03-10 04:37 | 2023-03-10 04:39 | 1565 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23031000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-10 | 3130 | keep | 0 | Mar | 2023 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2023-03-10 05:17 | 2023-03-10 05:18 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P2303100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-10 | 4132 | keep | 0 | Mar | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
AGUADILLA | 2023-03-10 05:34 | 2023-03-10 12:07 | 20 | 6:33 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23031000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2023-03-10 | 7860 | keep | 0 | Mar | 2023 | 0.0053534 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-03-10 06:27 | 2023-03-10 06:38 | 1945 | 0:11 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | P23031000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2023-03-10 | 21395 | keep | 0 | Mar | 2023 | 0.014572 | 0.0013247 | Sustained | FALSE | FALSE | Not_TMED_Event | 1945
GUAYAMA | 2023-03-10 06:27 | 2023-03-10 06:29 | 1945 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | P23031000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-10 | 3890 | keep | 0 | Mar | 2023 | 0.0026495 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
CANOVANAS | 2023-03-10 07:44 | 2023-03-10 11:24 | 11 | 3:40 | P | ANIMAL | 3 X 40 EN CORTE DE LINEA Y 1 X 30 EN RISER CRUCE POR GATO | R23031000010 | New_Event | Animals | Include | Include | Wildlife | 220 | 2023-03-10 | 2420 | keep | 0 | Mar | 2023 | 0.0016483 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2023-03-10 07:45 | 2023-03-10 08:34 | 2343 | 0:49 | T | ARBOL SOBRE LINEA | SE ABRIO BKR POR EMERGENCIA PARA SE SECCIONALIZAR AVERIA DE ARBOL SOBRE LINEA QUE TUMBO POSTE PRIMARIO FRENTE A ESCUELA SE CERRO BKR POR CONTROL DESPUES DE ABRIR CORTE DE LINEA CG-230310-01 | C23031000006 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 49 | 2023-03-10 | 114807 | keep | 0 | Mar | 2023 | 0.078195 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
AGUADILLA | 2023-03-10 07:49 | 2023-03-10 10:40 | 3041 | 2:51 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR SE REPARO LINEA PRIMARIA CON GOI MY-230310-01A Y SE COLOCO INTERRUPTOR EN SERVICIO | M23031000010 | New_Event | Primary Wire Break | Include | Include | Equipment | 171 | 2023-03-10 | 520011 | keep | 0 | Mar | 2023 | 0.35418 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
FAJARDO | 2023-03-10 07:59 | 2023-03-10 10:40 | 50 | 2:41 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | R23031000012 | New_Event | Primary Wire Break | Include | Include | Equipment | 161 | 2023-03-10 | 8050 | keep | 0 | Mar | 2023 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-10 08:20 | 2023-03-10 10:20 | 40 | 2:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-03-10 | 4800 | keep | 0 | Mar | 2023 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-10 08:25 | 2023-03-10 16:03 | 10 | 7:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23031000013 | New_Event | Primary Wire Break | Include | Include | Equipment | 458 | 2023-03-10 | 4580 | keep | 0 | Mar | 2023 | 0.0031194 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-10 08:30 | 2023-03-10 08:31 | 74 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE LLEVA CARGA DEL 1912-07 | S2303100000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-10 | 74 | keep | 0 | Mar | 2023 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2023-03-10 08:30 | 2023-03-10 08:31 | 57 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE CARGA POR EL 1521-02 | S2303100000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-10 | 57 | keep | 0 | Mar | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-03-10 08:31 | 2023-03-10 13:18 | 3 | 4:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 20 EN RISER SE REEMPLAZO CAJA PRIMARIA DE 100 AMP | S23031000020 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 287 | 2023-03-10 | 861 | keep | 0 | Mar | 2023 | 0.00058642 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-03-10 08:34 | 2023-03-10 21:03 | 587 | 12:29 | P | ARBOL SOBRE LINEA | SE REEMPLAZO POSTE PRIMARIO, 2 POSTES SECUNDARIOS Y XMR DE 25 KVA X 37.5KVA Y SE RETIRO ARBOL SOBRE LINEA | C23031000019 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 749 | 2023-03-10 | 439663 | keep | 0 | Mar | 2023 | 0.29945 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-03-10 08:51 | 2023-03-10 12:08 | 1 | 3:17 | P | ANIMAL | 1 X 40 EN RISER CRUCE POR RATON | C23031000023 | New_Event | Animals | Include | Include | Wildlife | 197 | 2023-03-10 | 197 | keep | 0 | Mar | 2023 | 0.00013418 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-03-10 08:59 | 2023-03-10 12:15 | 105 | 3:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23031000048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-03-10 | 20580 | keep | 0 | Mar | 2023 | 0.014017 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
BAYAMON | 2023-03-10 09:03 | 2023-03-10 13:00 | 150 | 3:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA 1 X 65 EN CORTE DE LINEA | S23031000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2023-03-10 | 35550 | keep | 0 | Mar | 2023 | 0.024213 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-03-10 09:05 | 2023-03-10 10:17 | 385 | 1:12 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION CHARCO HONDO POR PUENTE ABIERTO EN LINEA 2300 DE 2 DOCAS A SUB CHARCO HONDO PUENTE ABIERTO BKR 2360 - ACB 2327. LINEA ESTABA RADIAL AL MOMENTO DEL DISPARO (BKR 2350 EN MANTENIMIENTO) | A23031000011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2023-03-10 | 27720 | keep | 0 | Mar | 2023 | 0.01888 | 0.00026222 | Sustained | FALSE | FALSE | Not_TMED_Event | 385
ARECIBO | 2023-03-10 09:05 | 2023-03-10 10:17 | 264 | 1:12 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION CHARCO HONDO POR PUENTE ABIERTO EN LINEA 2300 DE 2 DOCAS A SUB CHARCO HONDO PUENTE ABIERTO BKR 2360 - ACB 2327. LINEA ESTABA RADIAL AL MOMENTO DEL DISPARO (BKR 2350 EN MANTENIMIENTO) | A23031000011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2023-03-10 | 19008 | keep | 0 | Mar | 2023 | 0.012946 | 0.00017981 | Sustained | FALSE | FALSE | Not_TMED_Event | 264
CAGUAS | 2023-03-10 09:13 | 2023-03-10 14:14 | 10 | 5:01 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE SECUNDARIO | C23031000027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 301 | 2023-03-10 | 3010 | keep | 0 | Mar | 2023 | 0.0020501 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-03-10 09:17 | 2023-03-10 11:36 | 1 | 2:19 | P | ANIMAL | 2 X 10 BANCO EN XMR Y 2 X 20 EN RISER CRUCE POR AVE | C23031000032 | New_Event | Animals | Include | Include | Wildlife | 139 | 2023-03-10 | 139 | keep | 0 | Mar | 2023 | 9.4672e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-10 09:26 | 2023-03-10 09:27 | 3957 | 0:01 | T | DESGANCHE | DISPARO, SE PROBO POR CONTROL QUEDO EN SERVICIO | S23031000027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-10 | 3957 | keep | 0 | Mar | 2023 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2023-03-10 09:27 | 2023-03-10 10:00 | 160 | 0:33 | P | CAUSAS EXTERNAS | SE REMPLAZO POSTE Y SE NORMALIZARON LAS CARGAS CAMION IMPACTO POSTE. SJ-230308-50 | S23030900295 | New_Event | Damage From Public | Include | Include | Public | 33 | 2023-03-10 | 5280 | keep | 0 | Mar | 2023 | 0.0035962 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
SAN JUAN | 2023-03-10 09:27 | 2023-03-10 11:50 | 1 | 2:23 | P | DESGANCHE | DESPEJE DE LINEA 1 X 40 EN RISER EVENTO TRANSFERIDO | P23031000074 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-03-10 | 143 | keep | 0 | Mar | 2023 | 9.7397e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-10 09:31 | 2023-03-10 12:50 | 1 | 3:19 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23031000035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2023-03-10 | 199 | keep | 0 | Mar | 2023 | 0.00013554 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-10 09:49 | 2023-03-10 15:05 | 10 | 5:16 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R23031000023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2023-03-10 | 3160 | keep | 0 | Mar | 2023 | 0.0021523 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-10 10:00 | 2023-03-10 13:50 | 330 | 3:50 | P | CAUSAS EXTERNAS | SE ABRIO MACHETE PARA CERRAR PUENTE REMPLAZO POSTE Y SE NORMALIZARON LAS CARGAS CAMION IMPACTO POSTE. SJ-230308-50 | S23030900295 | New_Event | Damage From Public | Include | Include | Public | 230 | 2023-03-10 | 75900 | keep | 0 | Mar | 2023 | 0.051695 | 0.00022476 | Sustained | FALSE | FALSE | Not_TMED_Event | 330
MAYAGÃœEZ | 2023-03-10 10:05 | 2023-03-10 10:27 | 10 | 0:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | M23031000026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 22 | 2023-03-10 | 220 | keep | 0 | Mar | 2023 | 0.00014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-03-10 10:21 | 2023-03-10 13:47 | 374 | 3:26 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | C23031000045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-03-10 | 77044 | keep | 0 | Mar | 2023 | 0.052474 | 0.00025473 | Sustained | FALSE | FALSE | Not_TMED_Event | 374
CANOVANAS | 2023-03-10 10:23 | 2023-03-10 20:06 | 693 | 9:43 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | ABRIO C/L PARA REMPLAZAR POSTE PRIMARIO A PUNTO DE CAERSE SJ-230310-50 | R23031000027 | New_Event | Primary Pole Failure | Include | Include | Equipment | 583 | 2023-03-10 | 404019 | keep | 0 | Mar | 2023 | 0.27518 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
PONCE | 2023-03-10 10:29 | 2023-03-10 13:20 | 1 | 2:51 | P | ANIMAL | 1 X 100 EN RISER POR AVE | P23031000072 | New_Event | Animals | Include | Include | Wildlife | 171 | 2023-03-10 | 171 | keep | 0 | Mar | 2023 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-03-10 10:30 | 2023-03-10 12:38 | 8 | 2:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | LINEA SECUNDARIA AVERIADA | P23031000073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 128 | 2023-03-10 | 1024 | keep | 0 | Mar | 2023 | 0.00069744 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-03-10 10:31 | 2023-03-10 11:45 | 15 | 1:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIA | B23031000002 | New_Event | Secondary Wire Break | Include | Include | Equipment | 74 | 2023-03-10 | 1110 | keep | 0 | Mar | 2023 | 0.00075602 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-03-10 10:53 | 2023-03-10 10:54 | 2725 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DE SANTA ISABEL A CAYEY | C23031000056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-10 | 2725 | keep | 0 | Mar | 2023 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2023-03-10 10:53 | 2023-03-10 10:54 | 1834 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DE SANTA ISABEL A CAYEY | C23031000056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-10 | 1834 | keep | 0 | Mar | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2023-03-10 10:53 | 2023-03-10 10:54 | 1437 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DE SANTA ISABEL A CAYEY | C23031000056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-10 | 1437 | keep | 0 | Mar | 2023 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2023-03-10 10:53 | 2023-03-10 10:54 | 2565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C23031000058 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-10 | 2565 | keep | 0 | Mar | 2023 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2023-03-10 10:53 | 2023-03-10 10:54 | 3565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DE SANTA ISABEL A CAYEY | C23031000058 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-10 | 3565 | keep | 0 | Mar | 2023 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
BARRANQUITAS | 2023-03-10 10:53 | 2023-03-10 10:54 | 282 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 DE SANTA ISABEL A CAYEY BKR 3502-01 LLEVA EL 11% DEL 9601-01 | C23031000058 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-10 | 282 | keep | 0 | Mar | 2023 | 0.00019207 | 0.00019207 | Momentary | FALSE | FALSE | Not_TMED_Event | 282
MAYAGÃœEZ | 2023-03-10 10:56 | 2023-03-10 12:50 | 20 | 1:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CAJA CORTE LINEA | M23031000040 | New_Event | Primary Wire Break | Include | Include | Equipment | 114 | 2023-03-10 | 2280 | keep | 0 | Mar | 2023 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-03-10 11:01 | 2023-03-10 13:00 | 54 | 1:59 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 EN RISER CONTAMINACION EN BOVEDA | C23031000062 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 119 | 2023-03-10 | 6426 | keep | 0 | Mar | 2023 | 0.0043767 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
FAJARDO | 2023-03-10 11:03 | 2023-03-10 11:54 | 15 | 0:51 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23031000033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2023-03-10 | 765 | keep | 0 | Mar | 2023 | 0.00052104 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-03-10 11:16 | 2023-03-10 14:29 | 8 | 3:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23031000065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 193 | 2023-03-10 | 1544 | keep | 0 | Mar | 2023 | 0.0010516 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-03-10 11:32 | 2023-03-10 13:36 | 1 | 2:04 | P | DESGANCHE | 1 X 50 EN RISER DESGANCHE | M23031000052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-03-10 | 124 | keep | 0 | Mar | 2023 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-10 11:42 | 2023-03-10 16:27 | 17 | 4:45 | P | NO SE REPORTO CAUSA | 1 SMU20 X 20 EN SU-5 @ T-11 | C23031000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2023-03-10 | 4845 | keep | 0 | Mar | 2023 | 0.0032999 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2023-03-10 11:45 | 2023-03-10 17:36 | 15 | 5:51 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23031000072 | New_Event | Animals | Include | Include | Wildlife | 351 | 2023-03-10 | 5265 | keep | 0 | Mar | 2023 | 0.003586 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-10 11:55 | 2023-03-11 16:13 | 3 | 28:18 | P | DESGANCHE | SE RALIZO DESGANCHE Y LEVANTO LINEA PRIMARIA | S23031000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1698 | 2023-03-10 | 5094 | keep | 0 | Mar | 2023 | 0.0034695 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-10 11:55 | 2023-03-10 20:03 | 3 | 8:08 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTE Y SE RETIRO PELIGRO ALAMBRE EN EL PISO Y SE PASO CARGA DE CLIENTE A OTRA FASE | S23031000085 | New_Event | Primary Wire Break | Include | Include | Equipment | 488 | 2023-03-10 | 1464 | keep | 0 | Mar | 2023 | 0.00099712 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-10 12:00 | 2023-03-10 12:05 | 8 | 0:05 | P | PROBLEMA DEL CLIENTE | SE ABRIO TRANSFORMADOR T-5 PARA DESCONECTAR TOMA DE CLIENTE AVERIADA | S23031000068 | New_Event | Customer-Related Interruption | Include | Include | Public | 5 | 2023-03-10 | 40 | keep | 0 | Mar | 2023 | 2.7244e-05 | 5.4488e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-03-10 12:13 | 2023-03-10 14:14 | 1825 | 2:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR SE PATRULLO Y NO SE ENCONTRO CAUSA | M23031000062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2023-03-10 | 220825 | keep | 0 | Mar | 2023 | 0.1504 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
AGUADILLA | 2023-03-10 12:36 | 2023-03-10 13:40 | 1 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZAR BAJANTES SECUNDARIOS | M23031000064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2023-03-10 | 64 | keep | 0 | Mar | 2023 | 4.359e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-10 12:43 | 2023-03-10 12:45 | 1420 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1530-06 SE PROBO POR CONTROL QUEDO EN SERVICIO | S23031000121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-10 | 2840 | keep | 0 | Mar | 2023 | 0.0019343 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
SAN JUAN | 2023-03-10 12:43 | 2023-03-10 12:45 | 437 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO SU CARGA POR 1526-02 SE PROBO POR CONTROL QUEDO EN SERVICIO | S23031000121 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-10 | 874 | keep | 0 | Mar | 2023 | 0.00059528 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CAGUAS | 2023-03-10 12:45 | 2023-03-10 14:21 | 8 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C23031000079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2023-03-10 | 768 | keep | 0 | Mar | 2023 | 0.00052308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-03-10 13:08 | 2023-03-10 13:32 | 11 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR CONECTOR EN NEUTRAL DEL BAJANTE SECUNDARIO | R23031000043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-03-10 | 264 | keep | 0 | Mar | 2023 | 0.00017981 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-03-10 13:09 | 2023-03-10 16:54 | 15 | 3:45 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | C23031000084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2023-03-10 | 3375 | keep | 0 | Mar | 2023 | 0.0022987 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-10 13:16 | 2023-03-10 14:50 | 2 | 1:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031000075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 94 | 2023-03-10 | 188 | keep | 0 | Mar | 2023 | 0.00012805 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-03-10 13:21 | 2023-03-10 15:11 | 10 | 1:50 | P | ARBOL SOBRE LINEA | SE REPARO SECUNDARIA ARBOL SOBRE LA LINEA | B23031000051 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 110 | 2023-03-10 | 1100 | keep | 0 | Mar | 2023 | 0.0007492 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-10 13:23 | 2023-03-10 16:41 | 42 | 3:18 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN C/L RETEZO CONDUCTOR | R23031000047 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 198 | 2023-03-10 | 8316 | keep | 0 | Mar | 2023 | 0.005664 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
MAYAGÃœEZ | 2023-03-10 13:27 | 2023-03-10 17:00 | 60 | 3:33 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M23031000082 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 213 | 2023-03-10 | 12780 | keep | 0 | Mar | 2023 | 0.0087044 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-03-10 13:39 | 2023-03-10 15:57 | 100 | 2:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23031000120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-03-10 | 13800 | keep | 0 | Mar | 2023 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-03-10 13:49 | 2023-03-10 17:00 | 40 | 3:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031000090 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 191 | 2023-03-10 | 7640 | keep | 0 | Mar | 2023 | 0.0052036 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-10 13:50 | 2023-03-10 20:46 | 50 | 6:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23031000092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2023-03-10 | 20800 | keep | 0 | Mar | 2023 | 0.014167 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-03-10 13:51 | 2023-03-10 19:05 | 1 | 5:14 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR Y 1 X 30 EN C/L SE REEMPLAZO XMR DE 75KVA X 25KVA | C23031000088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 314 | 2023-03-10 | 314 | keep | 0 | Mar | 2023 | 0.00021386 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-03-10 13:59 | 2023-03-10 17:18 | 12 | 3:19 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L Y SE ELIMINO PARRARYO QUEMADO | C23031000091 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 199 | 2023-03-10 | 2388 | keep | 0 | Mar | 2023 | 0.0016265 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-03-10 14:11 | 2023-03-10 17:30 | 6 | 3:19 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A23031000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2023-03-10 | 1194 | keep | 0 | Mar | 2023 | 0.00081323 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-03-10 14:14 | 2023-03-10 18:07 | 100 | 3:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23031000036 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 233 | 2023-03-10 | 23300 | keep | 0 | Mar | 2023 | 0.01587 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-03-10 14:22 | 2023-03-10 14:57 | 1 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | SE CAMBIO HOT CLAMP Y SE CERRO CL | P23031000135 | New_Event | Primary Wire Break | Include | Include | Equipment | 35 | 2023-03-10 | 35 | keep | 0 | Mar | 2023 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-10 14:42 | 2023-03-10 16:40 | 4 | 1:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESPEJE DE LINEA | S2303100154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-03-10 | 472 | keep | 0 | Mar | 2023 | 0.00032148 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-03-10 15:00 | 2023-03-10 16:13 | 20 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | R23031000059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-03-10 | 1460 | keep | 0 | Mar | 2023 | 0.0009944 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-10 15:08 | 2023-03-10 16:56 | 721 | 1:48 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DEL INTERRUPTOR LINEA PRIMARIA ROTA SE SECCIONALIZO | M23031000124 | New_Event | Primary Wire Break | Include | Include | Equipment | 108 | 2023-03-10 | 77868 | keep | 0 | Mar | 2023 | 0.053036 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
PONCE | 2023-03-10 15:13 | 2023-03-10 17:31 | 80 | 2:18 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P23031000155 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-03-10 | 11040 | keep | 0 | Mar | 2023 | 0.0075193 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-03-10 15:44 | 2023-03-10 19:26 | 25 | 3:42 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23031000135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-03-10 | 5550 | keep | 0 | Mar | 2023 | 0.0037801 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-03-10 15:56 | 2023-03-10 18:24 | 50 | 2:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23031000164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-03-10 | 7400 | keep | 0 | Mar | 2023 | 0.0050401 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-10 16:00 | 2023-03-10 17:43 | 8 | 1:43 | P | DESGANCHE | 1 X 15 Y DESGANCHE | B23031000071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-03-10 | 824 | keep | 0 | Mar | 2023 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-03-10 16:12 | 2023-03-10 19:10 | 30 | 2:58 | P | DESGANCHE | 1 X 30 Y 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031000104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-03-10 | 5340 | keep | 0 | Mar | 2023 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-10 16:18 | 2023-03-10 17:00 | 5 | 0:42 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA REPARAR SECUNDARIA IMPACTADA POR CAMION | C23031000111 | New_Event | Damage From Public | Include | Include | Public | 42 | 2023-03-10 | 210 | keep | 0 | Mar | 2023 | 0.00014303 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-03-10 16:56 | 2023-03-10 18:30 | 450 | 1:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA | M23031000164 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 94 | 2023-03-10 | 42300 | keep | 0 | Mar | 2023 | 0.02881 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-03-10 17:01 | 2023-03-10 17:02 | 1834 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE DE INTERRUPTOR | C23031000116 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-03-10 | 1834 | keep | 0 | Mar | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2023-03-10 17:02 | 2023-03-10 23:10 | 90 | 6:08 | P | CAUSAS EXTERNAS | SE RETIRO GLOBO ENREDADO EN MACHETE Y SE CERRO EL MACHETE | C23031000122 | 1st_after_momentary | Damage From Public | Include | Include | Public | 368 | 2023-03-10 | 33120 | keep | 0 | Mar | 2023 | 0.022558 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2023-03-10 17:11 | 2023-03-10 18:21 | 900 | 1:10 | T | ANIMAL | DISPARO INTERRUPTOR SE RETIRO VARIAS IGUANAS DE LINEA Y PEGO PUENTE PRIMARIO A TENSOR Y SE CERRO INTERRUPTOR | P23031000176 | New_Event | Animals | Include | Include | Wildlife | 70 | 2023-03-10 | 63000 | keep | 0 | Mar | 2023 | 0.042909 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
SAN JUAN | 2023-03-10 17:24 | 2023-03-10 21:35 | 62 | 4:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23031000194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2023-03-10 | 15562 | keep | 0 | Mar | 2023 | 0.010599 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
SAN JUAN | 2023-03-10 17:30 | 2023-03-10 19:35 | 7 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN TRANSFORMADOR Y SE LEVANTO SECUNDARIA | S23031000028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2023-03-10 | 875 | keep | 0 | Mar | 2023 | 0.00059596 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-10 17:36 | 2023-03-10 17:37 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | B2303100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-10 | 2956 | keep | 0 | Mar | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BARRANQUITAS | 2023-03-10 18:07 | 2023-03-11 17:36 | 15 | 23:29 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO Y SECUNDARIO Y LEVANTANDO LINEA PRIMARIAS | C23031000124 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1409 | 2023-03-10 | 21135 | keep | 0 | Mar | 2023 | 0.014395 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-10 18:36 | 2023-03-10 21:13 | 12 | 2:37 | P | CAUSAS EXTERNAS | 1 X 15 EN XMR CAMION SE LLEVO TOMA DE CLIENTE | B23031000081 | New_Event | Damage From Public | Include | Include | Public | 157 | 2023-03-10 | 1884 | keep | 0 | Mar | 2023 | 0.0012832 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-10 18:39 | 2023-03-11 09:36 | 10 | 14:57 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23031000181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 897 | 2023-03-10 | 8970 | keep | 0 | Mar | 2023 | 0.0061094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-10 18:51 | 2023-03-11 10:50 | 6 | 15:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | M23031000183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 959 | 2023-03-10 | 5754 | keep | 0 | Mar | 2023 | 0.003919 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-03-10 19:10 | 2023-03-10 20:41 | 30 | 1:31 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23031000132 | New_Event | Animals | Include | Include | Wildlife | 91 | 2023-03-10 | 2730 | keep | 0 | Mar | 2023 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-03-10 19:24 | 2023-03-10 19:47 | 15 | 0:23 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23031000135 | New_Event | Animals | Include | Include | Wildlife | 23 | 2023-03-10 | 345 | keep | 0 | Mar | 2023 | 0.00023498 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-03-10 20:07 | 2023-03-11 12:50 | 60 | 16:43 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA ARRIADA | M23031000186 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1003 | 2023-03-10 | 60180 | keep | 0 | Mar | 2023 | 0.040988 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-10 20:17 | 2023-03-11 09:45 | 50 | 13:28 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | S23031000219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 808 | 2023-03-10 | 40400 | keep | 0 | Mar | 2023 | 0.027516 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-10 20:55 | 2023-03-10 22:17 | 1 | 1:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO PORTAFUSIBLES | B23031000084 | New_Event | Cutout Failure | Include | Include | Equipment | 82 | 2023-03-10 | 82 | keep | 0 | Mar | 2023 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-10 20:59 | 2023-03-11 12:05 | 6 | 15:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 50KVA X 50KVA | M23031000188 | New_Event | Service Transformer Failure | Include | Include | Equipment | 906 | 2023-03-10 | 5436 | keep | 0 | Mar | 2023 | 0.0037024 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-03-10 21:38 | 2023-03-11 10:10 | 100 | 12:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031000118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 752 | 2023-03-10 | 75200 | keep | 0 | Mar | 2023 | 0.051218 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-03-10 22:10 | 2023-03-10 22:11 | 989 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23031000149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-10 | 989 | keep | 0 | Mar | 2023 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
AGUADILLA | 2023-03-10 22:22 | 2023-03-11 14:43 | 15 | 16:21 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO CON TRANSFORMADOR | M23031000193 | New_Event | Primary Pole Failure | Include | Include | Equipment | 981 | 2023-03-10 | 14715 | keep | 0 | Mar | 2023 | 0.010022 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-03-10 22:31 | 2023-03-11 11:55 | 10 | 13:24 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | M23031000194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 804 | 2023-03-10 | 8040 | keep | 0 | Mar | 2023 | 0.005476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-11 00:02 | 2023-03-11 02:37 | 80 | 2:35 | P | ANIMAL | 1 X 100 EN C/L AVE | B23031100002 | New_Event | Animals | Include | Include | Wildlife | 155 | 2023-03-11 | 12400 | keep | 0 | Mar | 2023 | 0.0084456 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-11 01:10 | 2023-03-11 09:48 | 46 | 8:38 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23031100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 518 | 2023-03-11 | 23828 | keep | 0 | Mar | 2023 | 0.016229 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
SAN JUAN | 2023-03-11 03:14 | 2023-03-11 11:05 | 100 | 7:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER 2 X 80 EN C/L | S23031100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 471 | 2023-03-11 | 47100 | keep | 0 | Mar | 2023 | 0.03208 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-03-11 05:16 | 2023-03-11 12:05 | 60 | 6:49 | P | FUEGO | 1 X 65 EN CL SE ABRIO PUENTES HACIA AVERIA POSTE QUEMADO Y ALAMBRE PARTIDO | P23031100009 | New_Event | Fire | Include | Include | Public | 409 | 2023-03-11 | 24540 | keep | 0 | Mar | 2023 | 0.016714 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-03-11 07:27 | 2023-03-11 08:30 | 2 | 1:03 | P | DESGANCHE | 1 X 20 EN RISER SE RETIRO ENREDADERA SOBRE RISER | M23031100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-03-11 | 126 | keep | 0 | Mar | 2023 | 8.5818e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-03-11 07:47 | 2023-03-11 10:34 | 3 | 2:47 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23031100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-03-11 | 501 | keep | 0 | Mar | 2023 | 0.00034123 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2023-03-11 07:56 | 2023-03-11 07:57 | 1173 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO CAUSAS | P23031100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-11 | 1173 | keep | 0 | Mar | 2023 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
CAGUAS | 2023-03-11 08:00 | 2023-03-11 14:30 | 15 | 6:30 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHE SECUNDARIO | C23031100004 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 390 | 2023-03-11 | 5850 | keep | 0 | Mar | 2023 | 0.0039844 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-03-11 08:01 | 2023-03-11 08:02 | 1722 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23031100002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-03-11 | 1722 | keep | 0 | Mar | 2023 | 0.0011728 | 0.0011728 | Momentary | FALSE | FALSE | Not_TMED_Event | 1722
HUMACAO | 2023-03-11 08:16 | 2023-03-11 10:06 | 97 | 1:50 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23031100008 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-03-11 | 10670 | keep | 0 | Mar | 2023 | 0.0072673 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
BAYAMON | 2023-03-11 08:20 | 2023-03-11 08:46 | 12 | 0:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | B23031100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2023-03-11 | 312 | keep | 0 | Mar | 2023 | 0.0002125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-03-11 08:30 | 2023-03-11 13:27 | 71 | 4:57 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | CG-230311-01 SE RETEZO LINEA Y SE ELIMINO POSTE PRIMARIO Y 1 80 EN C/L | C23031100010 | New_Event | Primary Pole Failure | Include | Include | Equipment | 297 | 2023-03-11 | 21087 | keep | 0 | Mar | 2023 | 0.014362 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
YAUCO | 2023-03-11 08:51 | 2023-03-11 12:48 | 50 | 3:57 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23031100016 | New_Event | Animals | Include | Include | Wildlife | 237 | 2023-03-11 | 11850 | keep | 0 | Mar | 2023 | 0.008071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-03-11 09:06 | 2023-03-11 11:46 | 10 | 2:40 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23031100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2023-03-11 | 1600 | keep | 0 | Mar | 2023 | 0.0010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-11 09:08 | 2023-03-11 19:00 | 10 | 9:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23031100041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 592 | 2023-03-11 | 5920 | keep | 0 | Mar | 2023 | 0.0040321 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-11 09:12 | 2023-03-11 11:36 | 60 | 2:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA 1 X 40 EN CORTE DE LINEA DESGANCHE | R23031100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2023-03-11 | 8640 | keep | 0 | Mar | 2023 | 0.0058847 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-03-11 09:15 | 2023-03-11 14:35 | 30 | 5:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031100012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 320 | 2023-03-11 | 9600 | keep | 0 | Mar | 2023 | 0.0065385 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-11 09:16 | 2023-03-11 09:19 | 723 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR CONTROL LLEVA 1912-08 1711-02 -03 LLEVA 10% 1711-04 | B2303110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-11 | 2169 | keep | 0 | Mar | 2023 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-03-11 09:16 | 2023-03-11 09:19 | 13 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR CERRADO POR CONTROL CARGA POR 1711-02 | B2303110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-11 | 39 | keep | 0 | Mar | 2023 | 2.6563e-05 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-03-11 09:16 | 2023-03-11 09:19 | 198 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR CERRADO POR CONTROL CARGA POR 1711-02 | B2303110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-11 | 594 | keep | 0 | Mar | 2023 | 0.00040457 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-03-11 09:16 | 2023-03-11 09:19 | 577 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR CERRADO POR CONTROL CARGA POR 1711-02 | B2303110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-11 | 1731 | keep | 0 | Mar | 2023 | 0.001179 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
CAGUAS | 2023-03-11 09:25 | 2023-03-11 09:26 | 125 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C2303110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-11 | 125 | keep | 0 | Mar | 2023 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2023-03-11 09:25 | 2023-03-11 11:58 | 25 | 2:33 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-03-11 | 3825 | keep | 0 | Mar | 2023 | 0.0026052 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-03-11 09:34 | 2023-03-11 11:00 | 11 | 1:26 | P | REGULADOR DEFECTUOSO O AVERIADO | SE REMPLAZO XMR LIQUEANDO ACEITE 37.5 KVA 2400 VOLT | P23031100021 | New_Event | Regulator Failure | Include | Include | Equipment | 86 | 2023-03-11 | 946 | keep | 0 | Mar | 2023 | 0.00064432 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-03-11 09:36 | 2023-03-11 12:32 | 15 | 2:56 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA REEMPLAZAR PEDESTAL | B23031100030 | New_Event |  |  |  |  | 176 | 2023-03-11 | 2640 | keep | 0 | Mar | 2023 | 0.0017981 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-11 09:41 | 2023-03-11 21:14 | 5 | 11:33 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23031100045 | New_Event | Primary Wire Break | Include | Include | Equipment | 693 | 2023-03-11 | 3465 | keep | 0 | Mar | 2023 | 0.00236 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-11 09:49 | 2023-03-11 11:56 | 100 | 2:07 | P | ANIMAL | 1 X 50 Y 1 X 65 EN C/L CRUCE POR AVE | B23031100033 | New_Event | Animals | Include | Include | Wildlife | 127 | 2023-03-11 | 12700 | keep | 0 | Mar | 2023 | 0.0086499 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-03-11 10:44 | 2023-03-11 13:27 | 27 | 2:43 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR IGUANA | B23031100049 | New_Event | Animals | Include | Include | Wildlife | 163 | 2023-03-11 | 4401 | keep | 0 | Mar | 2023 | 0.0029975 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2023-03-11 10:50 | 2023-03-11 17:05 | 15 | 6:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | S23031100051 | New_Event | Primary Wire Break | Include | Include | Equipment | 375 | 2023-03-11 | 5625 | keep | 0 | Mar | 2023 | 0.0038312 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-11 10:50 | 2023-03-11 12:06 | 15 | 1:16 | P | ANIMAL | 1 X 20 EN XMR CRUCE POR AVE | B23031100050 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-03-11 | 1140 | keep | 0 | Mar | 2023 | 0.00077645 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-11 10:54 | 2023-03-11 16:47 | 115 | 5:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 1 X 15 C/L EVENTO TRANFERIDO BAYAMON GUAYNABO | B23031100061 | New_Event | Cutout Failure | Include | Include | Equipment | 353 | 2023-03-11 | 40595 | keep | 0 | Mar | 2023 | 0.027649 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
BAYAMON | 2023-03-11 11:00 | 2023-03-11 11:01 | 326 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 9202-03 LEVA 50% 9201-01 | B2303110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-11 | 326 | keep | 0 | Mar | 2023 | 0.00022204 | 0.00022204 | Momentary | FALSE | FALSE | Not_TMED_Event | 326
BAYAMON | 2023-03-11 11:00 | 2023-03-11 11:01 | 51 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 9202-03 LLEVA 17% 9202-02 Y 50% 9201-01 | 2303110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-11 | 51 | keep | 0 | Mar | 2023 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
BAYAMON | 2023-03-11 11:00 | 2023-03-11 11:01 | 1159 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE BKR 9202-03 LLEVA 17% 9202-02 Y 50% 9201-01 | B2303110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-11 | 1159 | keep | 0 | Mar | 2023 | 0.00078939 | 0.00078939 | Momentary | FALSE | FALSE | Not_TMED_Event | 1159
BAYAMON | 2023-03-11 11:00 | 2023-03-11 11:01 | 2926 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 9202-04 | B2303110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-11 | 2926 | keep | 0 | Mar | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
MAYAGÃœEZ | 2023-03-11 11:37 | 2023-03-11 12:25 | 1 | 0:48 | P | CAUSAS EXTERNAS | 1 X 5 EN TRANSFORMADOR CAMION CRUZO TOMA | M23031100022 | New_Event | Damage From Public | Include | Include | Public | 48 | 2023-03-11 | 48 | keep | 0 | Mar | 2023 | 3.2693e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-03-11 11:46 | 2023-03-11 12:33 | 10 | 0:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN XMR | P23031100033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2023-03-11 | 470 | keep | 0 | Mar | 2023 | 0.00032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-11 11:57 | 2023-03-11 13:35 | 78 | 1:38 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y 1 X 100 EN C/L | S23031100064 | New_Event | Primary Wire Break | Include | Include | Equipment | 98 | 2023-03-11 | 7644 | keep | 0 | Mar | 2023 | 0.0052063 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
BARRANQUITAS | 2023-03-11 12:08 | 2023-03-11 15:54 | 1 | 3:46 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | C23031100093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2023-03-11 | 226 | keep | 0 | Mar | 2023 | 0.00015393 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-03-11 12:17 | 2023-03-12 20:17 | 40 | 31:60 | P | FUEGO | SE REMPLAZO POSTE PRIMARIO PARTIDO Y ALAMBRES PRIMARIOS PARTIDOS SE CERRARON PUENTES ABIERTOS EL DIA ANTERIOR | P23031100037 | New_Event | Fire | Include | Include | Public | 1920 | 2023-03-11 | 76800 | keep | 0 | Mar | 2023 | 0.052308 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-03-11 12:22 | 2023-03-11 14:56 | 14 | 2:34 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23031100107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-03-11 | 2156 | keep | 0 | Mar | 2023 | 0.0014684 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-03-11 12:39 | 2023-03-11 12:40 | 2435 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1909-08 | B2303110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-11 | 2435 | keep | 0 | Mar | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-03-11 12:39 | 2023-03-11 12:40 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 1907-05 | B2303110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-11 | 2956 | keep | 0 | Mar | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-03-11 12:42 | 2023-03-11 15:12 | 10 | 2:30 | P | NO SE REPORTO CAUSA | 1 X 80 RISER 1 X 80 C/L | B23031100064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2023-03-11 | 1500 | keep | 0 | Mar | 2023 | 0.0010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-03-11 12:46 | 2023-03-11 18:30 | 80 | 5:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23031100034 | New_Event | Cutout Failure | Include | Include | Equipment | 344 | 2023-03-11 | 27520 | keep | 0 | Mar | 2023 | 0.018744 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-03-11 12:53 | 2023-03-11 14:33 | 60 | 1:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R23031100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-03-11 | 6000 | keep | 0 | Mar | 2023 | 0.0040866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-11 12:59 | 2023-03-11 13:00 | 125 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL BKR SE CERRO POR CONTROL | C2303110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-11 | 125 | keep | 0 | Mar | 2023 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-03-11 13:27 | 2023-03-11 15:37 | 1 | 2:10 | P | ANIMAL | 1 X 20 XMR AVE CRUZO LINEA | B23031100079 | New_Event | Animals | Include | Include | Wildlife | 130 | 2023-03-11 | 130 | keep | 0 | Mar | 2023 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-11 13:31 | 2023-03-11 13:39 | 80 | 0:08 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23031100082 | New_Event | Animals | Include | Include | Wildlife | 8 | 2023-03-11 | 640 | keep | 0 | Mar | 2023 | 0.0004359 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-03-11 13:59 | 2023-03-11 16:08 | 12 | 2:09 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR AVE CRUZO LINEA A TIERRA | A23031100040 | New_Event | Animals | Include | Include | Wildlife | 129 | 2023-03-11 | 1548 | keep | 0 | Mar | 2023 | 0.0010543 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-03-11 14:03 | 2023-03-11 17:10 | 8 | 3:07 | P | ANIMAL | 1 X 30 EN C/L Y SE REPARO NEUTRAL CRUCE X AVE | C23031100127 | New_Event | Animals | Include | Include | Wildlife | 187 | 2023-03-11 | 1496 | keep | 0 | Mar | 2023 | 0.0010189 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-11 15:03 | 2023-03-11 15:04 | 2926 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2303110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-11 | 2926 | keep | 0 | Mar | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
FAJARDO | 2023-03-11 15:06 | 2023-03-11 17:32 | 1 | 2:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | R23031100015 | New_Event | Cutout Failure | Include | Include | Equipment | 146 | 2023-03-11 | 146 | keep | 0 | Mar | 2023 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-11 15:23 | 2023-03-11 16:23 | 252 | 1:00 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | R23031100020 | New_Event | Animals | Include | Include | Wildlife | 60 | 2023-03-11 | 15120 | keep | 0 | Mar | 2023 | 0.010298 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
AGUADILLA | 2023-03-11 15:42 | 2023-03-11 18:50 | 50 | 3:08 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23031100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-03-11 | 9400 | keep | 0 | Mar | 2023 | 0.0064023 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-03-11 15:46 | 2023-03-12 09:07 | 10 | 17:21 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SECUNDARIO | C23031100134 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1041 | 2023-03-11 | 10410 | keep | 0 | Mar | 2023 | 0.0070902 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-11 16:07 | 2023-03-11 17:34 | 25 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23031100100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-03-11 | 2175 | keep | 0 | Mar | 2023 | 0.0014814 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-03-11 16:11 | 2023-03-12 10:32 | 40 | 18:21 | P | PROBLEMA DEL CLIENTE | 1 X 80 EN RISER SE DEJO EDIFICIO 3 FUERA PROBLEMA INTERNO | S23031100079 | New_Event | Customer-Related Interruption | Include | Include | Public | 1101 | 2023-03-11 | 44040 | keep | 0 | Mar | 2023 | 0.029995 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-03-11 16:18 | 2023-03-11 19:33 | 87 | 3:15 | P | CAUSAS EXTERNAS | 1 X 50 Y 1 X 65 EN C/L SE REALIZO DESGANCHE PERSONA AJENA A LUMA RETIRANDO RAMA CRUZO FASE | C23031100137 | New_Event | Damage From Public | Include | Include | Public | 195 | 2023-03-11 | 16965 | keep | 0 | Mar | 2023 | 0.011555 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
UTUADO | 2023-03-11 16:30 | 2023-03-12 10:13 | 6 | 17:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | A23031100047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1063 | 2023-03-11 | 6378 | keep | 0 | Mar | 2023 | 0.004344 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:32 | 1225 | 0:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 LLEVA 75% DEL 1203-03 ANIMAL - IGUANA | S23031100097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2023-03-11 | 25725 | keep | 0 | Mar | 2023 | 0.017521 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:32 | 1452 | 0:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 ANIMAL - IGUANA | S23031100097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2023-03-11 | 30492 | keep | 0 | Mar | 2023 | 0.020768 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:32 | 462 | 0:21 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 75% DE SU CARGA ESTA POR EL 1203-01 Y 25% POR EL 1342-04 ANIMAL - IGUANA | S23031100097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2023-03-11 | 9702 | keep | 0 | Mar | 2023 | 0.006608 | 0.00031467 | Sustained | FALSE | FALSE | Not_TMED_Event | 462
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:59 | 790 | 0:48 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 ANIMAL - IGUANA | S23031100098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-11 | 37920 | keep | 0 | Mar | 2023 | 0.025827 | 0.00053807 | Sustained | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:59 | 312 | 0:48 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 80% DE SU CARGA POR EL 1345-02 ANIMAL - IGUANA | S23031100098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-11 | 14976 | keep | 0 | Mar | 2023 | 0.0102 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:59 | 660 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 ANIMAL - IGUANA | S23031100098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-11 | 31680 | keep | 0 | Mar | 2023 | 0.021577 | 0.00044952 | Sustained | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:59 | 435 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 LLEVA 80% DEL 1342-04 ANIMAL - IGUANA | S23031100098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-11 | 20880 | keep | 0 | Mar | 2023 | 0.014221 | 0.00029628 | Sustained | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:59 | 259 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 LLEVA LA CARGA DEL 1342-02 ANIMAL - IGUANA | S23031100098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-11 | 12432 | keep | 0 | Mar | 2023 | 0.0084674 | 0.0001764 | Sustained | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:59 | 686 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 ANIMAL - IGUANA | S23031100098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-11 | 32928 | keep | 0 | Mar | 2023 | 0.022427 | 0.00046723 | Sustained | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2023-03-11 17:11 | 2023-03-11 17:59 | 953 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 ANIMAL - IGUANA | S23031100098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2023-03-11 | 45744 | keep | 0 | Mar | 2023 | 0.031156 | 0.00064908 | Sustained | FALSE | FALSE | Not_TMED_Event | 953
BARRANQUITAS | 2023-03-11 17:12 | 2023-03-12 10:29 | 4 | 17:17 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | C23031100144 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1037 | 2023-03-11 | 4148 | keep | 0 | Mar | 2023 | 0.0028252 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-03-11 17:38 | 2023-03-12 10:59 | 3 | 17:21 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REEMPLAZO EL MISMO | B23031100102 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1041 | 2023-03-11 | 3123 | keep | 0 | Mar | 2023 | 0.0021271 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-11 17:50 | 2023-03-11 17:51 | 271 | 0:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2303110000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-11 | 271 | keep | 0 | Mar | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2023-03-11 18:14 | 2023-03-11 18:17 | 271 | 0:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2303110000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-03-11 | 813 | keep | 0 | Mar | 2023 | 0.00055373 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
GUAYAMA | 2023-03-11 18:41 | 2023-03-11 20:10 | 20 | 1:29 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE | P23031100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-03-11 | 1780 | keep | 0 | Mar | 2023 | 0.0012123 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-11 19:00 | 2023-03-11 19:30 | 271 | 0:30 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO Y SE CERRO POR SCADA | S23031100163 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 30 | 2023-03-11 | 8130 | keep | 0 | Mar | 2023 | 0.0055373 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
VEGA BAJA | 2023-03-11 19:15 | 2023-03-11 20:05 | 7 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A23031100049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-03-11 | 350 | keep | 0 | Mar | 2023 | 0.00023838 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-11 19:30 | 2023-03-11 19:32 | 189 | 0:02 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO SE RETIRO RAMA DE LINEA Y SE CERRO POR SCADA | S23031100163 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-03-11 | 378 | keep | 0 | Mar | 2023 | 0.00025745 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-11 19:32 | 2023-03-11 21:12 | 271 | 1:40 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO Y SE CERRO POR SCADA | S23031100163 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-03-11 | 27100 | keep | 0 | Mar | 2023 | 0.018458 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
HUMACAO | 2023-03-11 20:31 | 2023-03-11 20:32 | 2873 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2303110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-11 | 2873 | keep | 0 | Mar | 2023 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
SAN JUAN | 2023-03-11 21:12 | 2023-03-11 21:15 | 189 | 0:03 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO Y SE CERRO POR SCADA | S23031100163 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-03-11 | 567 | keep | 0 | Mar | 2023 | 0.00038618 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-11 21:15 | 2023-03-11 22:07 | 271 | 0:52 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO Y SE CERRO POR SCADA | S23031100163 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 52 | 2023-03-11 | 14092 | keep | 0 | Mar | 2023 | 0.009598 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2023-03-11 21:24 | 2023-03-12 03:50 | 750 | 6:26 | P | CAUSAS EXTERNAS | 3 X 100 EN C/L SE INSTALO POSTE Y SE LEVANTO PRIMARIA DEBIDO A IMPACTO DE AUTO | S23031100182 | New_Event | Damage From Public | Include | Include | Public | 386 | 2023-03-11 | 289500 | keep | 0 | Mar | 2023 | 0.19718 | 0.00051082 | Sustained | FALSE | FALSE | Not_TMED_Event | 750
SAN JUAN | 2023-03-11 22:07 | 2023-03-11 22:58 | 110 | 0:51 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO Y SE CERRO POR SCADA | S23031100163 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 51 | 2023-03-11 | 5610 | keep | 0 | Mar | 2023 | 0.0038209 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-11 22:58 | 2023-03-11 23:27 | 80 | 0:29 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA CERRAR TRAMO Y DEJAR TODO EN SERVICIO | S23031100163 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 29 | 2023-03-11 | 2320 | keep | 0 | Mar | 2023 | 0.0015801 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-11 22:58 | 2023-03-12 08:04 | 12 | 9:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REMPLAZO CAJA PRIMARIA | R23031100025 | New_Event | Cutout Failure | Include | Include | Equipment | 546 | 2023-03-11 | 6552 | keep | 0 | Mar | 2023 | 0.0044625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-11 23:32 | 2023-03-11 23:34 | 4381 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23031100053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-11 | 8762 | keep | 0 | Mar | 2023 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
CAGUAS | 2023-03-12 03:00 | 2023-03-12 03:01 | 725 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C23031200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-12 | 725 | keep | 0 | Mar | 2023 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
CAGUAS | 2023-03-12 03:01 | 2023-03-12 11:53 | 63 | 8:52 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23031200015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 532 | 2023-03-12 | 33516 | keep | 0 | Mar | 2023 | 0.022828 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
BAYAMON | 2023-03-12 03:08 | 2023-03-12 03:09 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 959 | keep | 0 | Mar | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-03-12 03:08 | 2023-03-12 03:09 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 1382 | keep | 0 | Mar | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-03-12 03:08 | 2023-03-12 03:09 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 663 | keep | 0 | Mar | 2023 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-03-12 03:08 | 2023-03-12 03:09 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 1514 | keep | 0 | Mar | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-03-12 03:08 | 2023-03-12 03:09 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 1105 | keep | 0 | Mar | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-03-12 03:08 | 2023-03-12 03:09 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 4176 | keep | 0 | Mar | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-03-12 03:08 | 2023-03-12 03:09 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 252 | keep | 0 | Mar | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-03-12 03:08 | 2023-03-12 03:09 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 2147 | keep | 0 | Mar | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-03-12 03:08 | 2023-03-12 03:09 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 2858 | keep | 0 | Mar | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
SAN JUAN | 2023-03-12 03:50 | 2023-03-12 20:00 | 10 | 16:10 | P | CAUSAS EXTERNAS | SE REMPLAZO POSTE PRIMARIO Y SE INSTALO TRANSFORMADOR 37.5 DEBIDO A IMPACTO DE AUTO | S23031100182 | Partial_restoration | Damage From Public | Include | Include | Public | 970 | 2023-03-12 | 9700 | keep | 0 | Mar | 2023 | 0.0066066 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-12 04:17 | 2023-03-12 10:25 | 30 | 6:08 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C23031200002 | New_Event | Animals | Include | Include | Wildlife | 368 | 2023-03-12 | 11040 | keep | 0 | Mar | 2023 | 0.0075193 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-12 04:38 | 2023-03-12 11:30 | 492 | 6:52 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO CONECTOR AVERIADO EN MACHETE FID-17410134 Y SE PASO POLE BREAKER 6704-03A A TRAVES DEL BY-PASS YA QUE INFORMA ANGEL LAMBERTY QUE EL POLE BREAKER 6704-03A CUANDO LLEGARON TENIA 2 FASES ABIERTAS Y UNA CERRADA | M23031200002 | New_Event | Switch Failure | Include | Include | Equipment | 412 | 2023-03-12 | 202704 | keep | 0 | Mar | 2023 | 0.13806 | 0.0003351 | Sustained | FALSE | FALSE | Not_TMED_Event | 492
BARRANQUITAS | 2023-03-12 05:41 | 2023-03-12 05:42 | 2937 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2303120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-12 | 2937 | keep | 0 | Mar | 2023 | 0.0020004 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
BARRANQUITAS | 2023-03-12 05:42 | 2023-03-12 08:08 | 15 | 2:26 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23031200004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 146 | 2023-03-12 | 2190 | keep | 0 | Mar | 2023 | 0.0014916 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-12 05:45 | 2023-03-12 08:44 | 55 | 2:59 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | B23031200005 | New_Event | Animals | Include | Include | Wildlife | 179 | 2023-03-12 | 9845 | keep | 0 | Mar | 2023 | 0.0067054 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2023-03-12 06:05 | 2023-03-12 10:54 | 63 | 4:49 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA SE RETIRO GLOBO CRUZANDO FASE | S23031200008 | New_Event | Damage From Public | Include | Include | Public | 289 | 2023-03-12 | 18207 | keep | 0 | Mar | 2023 | 0.012401 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
CAGUAS | 2023-03-12 06:55 | 2023-03-12 06:56 | 1879 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 3006-05 SE CERRO POR SCADA | C2303120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-12 | 1879 | keep | 0 | Mar | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-03-12 06:55 | 2023-03-12 06:56 | 3005 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 3006-02 | C2303120000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-12 | 3005 | keep | 0 | Mar | 2023 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
GUAYAMA | 2023-03-12 07:36 | 2023-03-12 11:00 | 9 | 3:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23031200015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 204 | 2023-03-12 | 1836 | keep | 0 | Mar | 2023 | 0.0012505 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-03-12 08:08 | 2023-03-12 10:07 | 3000 | 1:59 | T | AISLADOR ROTO, PARTIDO O SAFADO | BY-230312-01 SE REEMPLAZO AISLADOR DEFECTUOSO | B23031200012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 119 | 2023-03-12 | 357000 | keep | 0 | Mar | 2023 | 0.24315 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
HUMACAO | 2023-03-12 08:17 | 2023-03-12 08:42 | 5 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REEMPLAZO SECUNDARIA | C23031200012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-03-12 | 125 | keep | 0 | Mar | 2023 | 8.5137e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-12 08:23 | 2023-03-12 11:24 | 53 | 3:01 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23031200016 | New_Event | Animals | Include | Include | Wildlife | 181 | 2023-03-12 | 9593 | keep | 0 | Mar | 2023 | 0.0065337 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2023-03-12 08:30 | 2023-03-12 10:10 | 10 | 1:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS Y LINEAS SECUNDARIAS AVERIADAS | M23031200001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2023-03-12 | 1000 | keep | 0 | Mar | 2023 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-12 08:36 | 2023-03-12 10:30 | 120 | 1:54 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | S23031200006 | New_Event | Animals | Include | Include | Wildlife | 114 | 2023-03-12 | 13680 | keep | 0 | Mar | 2023 | 0.0093174 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-03-12 08:58 | 2023-03-12 13:16 | 117 | 4:18 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23031200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2023-03-12 | 30186 | keep | 0 | Mar | 2023 | 0.02056 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
BAYAMON | 2023-03-12 09:08 | 2023-03-12 10:11 | 15 | 1:03 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REPARO BUSHING SECUNDARIO | B23031200028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 63 | 2023-03-12 | 945 | keep | 0 | Mar | 2023 | 0.00064364 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-12 09:09 | 2023-03-12 13:45 | 10 | 4:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | S23031200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2023-03-12 | 2760 | keep | 0 | Mar | 2023 | 0.0018798 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-12 10:00 | 2023-03-12 15:00 | 1 | 5:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE POSTE | A23031200004 | New_Event | Primary Pole Failure | Include | Include | Equipment | 300 | 2023-03-12 | 300 | keep | 0 | Mar | 2023 | 0.00020433 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-12 10:23 | 2023-03-12 10:24 | 2608 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2303120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-12 | 2608 | keep | 0 | Mar | 2023 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CANOVANAS | 2023-03-12 10:30 | 2023-03-12 12:03 | 2 | 1:33 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA AVE CRUZO FASE | R23031200008 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-03-12 | 186 | keep | 0 | Mar | 2023 | 0.00012668 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-03-12 10:47 | 2023-03-12 14:00 | 12 | 3:13 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO EN CAJA DE XMR | P23031200038 | New_Event | Primary Wire Break | Include | Include | Equipment | 193 | 2023-03-12 | 2316 | keep | 0 | Mar | 2023 | 0.0015774 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-03-12 11:03 | 2023-03-12 11:05 | 1106 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 60% POR 1529-15 | S23031200000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-12 | 2212 | keep | 0 | Mar | 2023 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-03-12 11:03 | 2023-03-12 11:05 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 60% DEL 1346-02 | S23031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-12 | 3604 | keep | 0 | Mar | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
UTUADO | 2023-03-12 11:26 | 2023-03-12 14:11 | 32 | 2:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23031200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-03-12 | 5280 | keep | 0 | Mar | 2023 | 0.0035962 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2023-03-12 11:32 | 2023-03-13 11:14 | 18 | 23:42 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL AEREO DE EXISTENTE AL T7. | C23031200022 | New_Event | UG Cable Fault | Include | Include | Equipment | 1422 | 2023-03-12 | 25596 | keep | 0 | Mar | 2023 | 0.017433 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2023-03-12 11:38 | 2023-03-12 13:49 | 20 | 2:11 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | C23031200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-03-12 | 2620 | keep | 0 | Mar | 2023 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-12 11:49 | 2023-03-12 11:50 | 2926 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-12 | 2926 | keep | 0 | Mar | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
CAGUAS | 2023-03-12 12:02 | 2023-03-12 21:26 | 1444 | 9:24 | P | DESGANCHE | DISPARO DE INTELLIRRUPTER 3015-05A SE REALIZO DESGANCHE MASIVO DE BAMBUAS CON VARETA DESDE EL SUELO Y SE ENERGIZO | C23031200025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 564 | 2023-03-12 | 814416 | keep | 0 | Mar | 2023 | 0.5547 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
AGUADILLA | 2023-03-12 12:13 | 2023-03-12 13:06 | 2 | 0:53 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DE TRANSFORMADOR AVERIADO 50 KVA X 25 KVA | M23031200161 | New_Event | Service Transformer Failure | Include | Include | Equipment | 53 | 2023-03-12 | 106 | keep | 0 | Mar | 2023 | 7.2196e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-03-12 12:27 | 2023-03-13 08:50 | 1 | 20:23 | P | ANIMAL | 1 X 50 EN RISER CRUCE CON AVE | C23031200037 | New_Event | Animals | Include | Include | Wildlife | 1223 | 2023-03-12 | 1223 | keep | 0 | Mar | 2023 | 0.00083298 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-12 12:42 | 2023-03-12 13:10 | 30 | 0:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R23031200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2023-03-12 | 840 | keep | 0 | Mar | 2023 | 0.00057212 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-03-12 13:02 | 2023-03-12 15:13 | 10 | 2:11 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23031200168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2023-03-12 | 1310 | keep | 0 | Mar | 2023 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-12 13:34 | 2023-03-12 16:03 | 30 | 2:29 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23031200064 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-03-12 | 4470 | keep | 0 | Mar | 2023 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-12 13:37 | 2023-03-12 15:06 | 3 | 1:29 | P | TRANSFORMADOR AVERIADO | TRANFORMADOR AVERIADO SE PASARON CLIENTES A TRANSFORMADOR MAS CERCANO | B23031200066 | New_Event | Service Transformer Failure | Include | Include | Equipment | 89 | 2023-03-12 | 267 | keep | 0 | Mar | 2023 | 0.00018185 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-03-12 13:43 | 2023-03-12 17:08 | 6 | 3:25 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y DESGANCHE SECUNDARIO | B23031200067 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 205 | 2023-03-12 | 1230 | keep | 0 | Mar | 2023 | 0.00083775 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-12 14:01 | 2023-03-12 14:02 | 2926 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23031200068 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-12 | 2926 | keep | 0 | Mar | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
BAYAMON | 2023-03-12 14:10 | 2023-03-12 14:11 | 2926 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23031200069 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-12 | 2926 | keep | 0 | Mar | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
AGUADILLA | 2023-03-12 14:20 | 2023-03-12 14:44 | 6 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23031200171 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-03-12 | 144 | keep | 0 | Mar | 2023 | 9.8078e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-12 14:23 | 2023-03-12 14:24 | 2926 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23031200070 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-12 | 2926 | keep | 0 | Mar | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
BAYAMON | 2023-03-12 14:24 | 2023-03-12 14:25 | 2926 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23031200071 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-12 | 2926 | keep | 0 | Mar | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
YAUCO | 2023-03-12 14:41 | 2023-03-12 17:00 | 10 | 2:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO 300 PIES DE SECUNDARIA | P23031200055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 139 | 2023-03-12 | 1390 | keep | 0 | Mar | 2023 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-03-12 14:46 | 2023-03-12 17:20 | 75 | 2:34 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO RAMA SOBRE LINEA | C23031200057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-03-12 | 11550 | keep | 0 | Mar | 2023 | 0.0078667 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
FAJARDO | 2023-03-12 15:00 | 2023-03-12 16:05 | 12 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO Y BARRA EN PEDESTAL | R23031200015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-03-12 | 780 | keep | 0 | Mar | 2023 | 0.00053125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-03-12 15:11 | 2023-03-12 15:12 | 4702 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23031200089 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-03-12 | 4702 | keep | 0 | Mar | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
UTUADO | 2023-03-12 15:14 | 2023-03-12 18:15 | 3 | 3:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A23031200020 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 181 | 2023-03-12 | 543 | keep | 0 | Mar | 2023 | 0.00036983 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-03-12 15:29 | 2023-03-12 15:30 | 4702 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23031200091 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-03-12 | 4702 | keep | 0 | Mar | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-03-12 15:40 | 2023-03-12 16:58 | 4702 | 1:18 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA MEDIANTE GOI BY-230312-02 ENTRO 10% EN SERVICIO MACHTE QUEMADO | B23031200096 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 78 | 2023-03-12 | 366756 | keep | 0 | Mar | 2023 | 0.2498 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
BAYAMON | 2023-03-12 15:47 | 2023-03-12 17:05 | 837 | 1:18 | P | DESGANCHE | 1 X 80 EN C/L Y X 50 EN C/L DESGANCHE | S23031200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-03-12 | 65286 | keep | 0 | Mar | 2023 | 0.044466 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-03-12 15:53 | 2023-03-12 16:26 | 140 | 0:33 | P | ARBOL SOBRE LINEA | SE ABRE CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA QUEMANDO SITUACION PELIGROSA REF. S23031200038 | S23031200054 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 33 | 2023-03-12 | 4620 | keep | 0 | Mar | 2023 | 0.0031467 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
FAJARDO | 2023-03-12 16:17 | 2023-03-12 17:16 | 200 | 0:59 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R23031200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-03-12 | 11800 | keep | 0 | Mar | 2023 | 0.0080369 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-03-12 16:26 | 2023-03-12 16:32 | 137 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23031200056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-03-12 | 822 | keep | 0 | Mar | 2023 | 0.00055986 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-03-12 16:26 | 2023-03-12 16:32 | 760 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23031200056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-03-12 | 4560 | keep | 0 | Mar | 2023 | 0.0031058 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2023-03-12 16:26 | 2023-03-12 16:32 | 4291 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23031200056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-03-12 | 25746 | keep | 0 | Mar | 2023 | 0.017535 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-03-12 16:26 | 2023-03-12 16:32 | 1242 | 0:06 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 LLEVA 90% POR 1204-01 | S23031200056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-03-12 | 7452 | keep | 0 | Mar | 2023 | 0.0050755 | 0.00084592 | Sustained | FALSE | FALSE | Not_TMED_Event | 1242
CANOVANAS | 2023-03-12 16:28 | 2023-03-12 18:18 | 4085 | 1:50 | T | LINEA DE TRANSMISION 38KV | DISPARO SE VERIFICO TRAMO LINEA 3100 CAYO ENCIMA ALIMENTADOR SE RETIRO CON VARETA Y SE CERRO INTERRUPTOR | R23031200022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2023-03-12 | 449350 | keep | 0 | Mar | 2023 | 0.30605 | 0.0027823 | Sustained | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-03-12 16:30 | 2023-03-12 19:00 | 3984 | 2:30 | P | ALIMENTADOR AMARRADO | DISPARO 0050 TIRO BANDERA IAC-52 GROUND Y SE AUTORIZO ENERGIZAR CARGAS 80% DE SU CARGA POR 1619-02 | R23031200324 | New_Event | Feeder Load Transferred | Include | Include | Other | 150 | 2023-03-12 | 597600 | keep | 0 | Mar | 2023 | 0.40702 | 0.0027135 | Sustained | FALSE | FALSE | Not_TMED_Event | 3984
SAN JUAN | 2023-03-12 16:30 | 2023-03-12 16:32 | 790 | 0:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 SU CARGA POR 1345-03 | S23031200084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-12 | 1580 | keep | 0 | Mar | 2023 | 0.0010761 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2023-03-12 16:30 | 2023-03-12 16:32 | 312 | 0:02 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 SU CARGA POR 1345-02 | S23031200084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-12 | 624 | keep | 0 | Mar | 2023 | 0.000425 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-03-12 16:30 | 2023-03-12 16:32 | 660 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23031200084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-12 | 1320 | keep | 0 | Mar | 2023 | 0.00089905 | 0.00044952 | Momentary | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2023-03-12 16:30 | 2023-03-12 16:32 | 435 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 LLEVA 80% DEL 1342-04 | S23031200084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-12 | 870 | keep | 0 | Mar | 2023 | 0.00059255 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-03-12 16:30 | 2023-03-12 16:32 | 259 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 LLEVA 1342-02 | S23031200084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-12 | 518 | keep | 0 | Mar | 2023 | 0.00035281 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2023-03-12 16:30 | 2023-03-12 16:32 | 686 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23031200084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-12 | 1372 | keep | 0 | Mar | 2023 | 0.00093446 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2023-03-12 16:30 | 2023-03-12 16:32 | 667 | 0:02 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 30% POR 1330-04 | S23031200084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-12 | 1334 | keep | 0 | Mar | 2023 | 0.00090858 | 0.00045429 | Momentary | FALSE | FALSE | Not_TMED_Event | 667
CANOVANAS | 2023-03-12 16:30 | 2023-03-12 16:31 | 9 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R23031200385 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 9 | keep | 0 | Mar | 2023 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-03-12 16:30 | 2023-03-12 16:31 | 6 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R23031200385 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 6 | keep | 0 | Mar | 2023 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-03-12 16:30 | 2023-03-12 16:31 | 1 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R23031200385 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 1 | keep | 0 | Mar | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-12 16:30 | 2023-03-12 16:31 | 12 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R23031200385 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-12 | 12 | keep | 0 | Mar | 2023 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-03-12 16:30 | 2023-03-12 19:00 | 2179 | 2:30 | S | NO SE REPORTO CAUSA | DISPARO 0050 SE VERIFICO TIRO RELE AIC-52 GROUND Y SE AUTORIZO ENERGIZAR CARGAS | R23031200324 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2023-03-12 | 326850 | keep | 0 | Mar | 2023 | 0.22262 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2023-03-12 16:30 | 2023-03-12 19:00 | 5062 | 2:30 | S | NO SE REPORTO CAUSA | DISPARO 0050 SE VERIFICO TIRO RELE AIC-52 GROUND Y SE AUTORIZO ENERGIZAR CARGAS | R23031200325 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2023-03-12 | 759300 | keep | 0 | Mar | 2023 | 0.51716 | 0.0034477 | Sustained | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2023-03-12 16:32 | 2023-03-12 16:52 | 140 | 0:20 | P | ARBOL SOBRE LINEA | SE ABRE CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA QUEMANDO SITUACION PELIGROSA REF. S23031200038 | S23031200054 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 20 | 2023-03-12 | 2800 | keep | 0 | Mar | 2023 | 0.0019071 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-12 16:58 | 2023-03-12 17:06 | 4231 | 0:08 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA MEDIANTE GOI BY-230312-02 MACHETE QUEMADO | B23031200096 | Partial_restoration | Switch Failure | Include | Include | Equipment | 8 | 2023-03-12 | 33848 | keep | 0 | Mar | 2023 | 0.023054 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-12 17:06 | 2023-03-12 18:12 | 4702 | 1:06 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA MEDIANTE GOI BY-230312-02 SE RETIRO RAMAS SOBRE LAS LINEAS 100% EN SERVICIO | B23031200096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2023-03-12 | 310332 | keep | 0 | Mar | 2023 | 0.21137 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
UTUADO | 2023-03-12 17:10 | 2023-03-12 20:03 | 50 | 2:53 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A23031200029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-03-12 | 8650 | keep | 0 | Mar | 2023 | 0.0058915 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-12 17:11 | 2023-03-12 18:31 | 837 | 1:20 | T | ALIMENTADOR AMARRADO | DISPARO SU CARGA POR 1401-07 SE CERRO LOCALMENTE | S23031200069 | New_Event | Feeder Load Transferred | Include | Include | Other | 80 | 2023-03-12 | 66960 | keep | 0 | Mar | 2023 | 0.045606 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-03-12 17:11 | 2023-03-12 18:31 | 908 | 1:20 | T | NO SE REPORTO CAUSA | DISPARO LLEVA CARGA 1401-06 SE CERRO LOCALMENTE | S23031200069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2023-03-12 | 72640 | keep | 0 | Mar | 2023 | 0.049475 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
CAGUAS | 2023-03-12 17:28 | 2023-03-13 08:02 | 1 | 14:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BARRA SUELTA EN PEDESTAL | C23031200079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 874 | 2023-03-12 | 874 | keep | 0 | Mar | 2023 | 0.00059528 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-03-12 19:02 | 2023-03-13 11:06 | 19 | 16:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 30 EN AEREO PROVISIONAL HACIA T-1 Y SE CERRO N/O EN T-12 QUEDANDO TADO EL MUNDO EN SERVICIO | R23031200490 | New_Event | Secondary Wire Break | Include | Include | Equipment | 964 | 2023-03-12 | 18316 | keep | 0 | Mar | 2023 | 0.012475 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-03-12 19:13 | 2023-03-12 19:22 | 1715 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-12 | 15435 | keep | 0 | Mar | 2023 | 0.010513 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-03-12 19:13 | 2023-03-12 19:22 | 1498 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-12 | 13482 | keep | 0 | Mar | 2023 | 0.0091825 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-03-12 19:13 | 2023-03-12 19:22 | 1221 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-12 | 10989 | keep | 0 | Mar | 2023 | 0.0074846 | 0.00083162 | Sustained | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-03-12 19:13 | 2023-03-12 19:22 | 1100 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-03-12 | 9900 | keep | 0 | Mar | 2023 | 0.0067428 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-03-12 19:14 | 2023-03-12 19:22 | 1399 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-03-12 | 11192 | keep | 0 | Mar | 2023 | 0.0076228 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2023-03-12 19:14 | 2023-03-12 19:22 | 302 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-03-12 | 2416 | keep | 0 | Mar | 2023 | 0.0016455 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2023-03-12 19:14 | 2023-03-12 19:22 | 1048 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-03-12 | 8384 | keep | 0 | Mar | 2023 | 0.0057103 | 0.00071379 | Sustained | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2023-03-12 19:14 | 2023-03-12 19:22 | 573 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-03-12 | 4584 | keep | 0 | Mar | 2023 | 0.0031221 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2023-03-12 19:14 | 2023-03-12 19:22 | 1313 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23031200172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-03-12 | 10504 | keep | 0 | Mar | 2023 | 0.0071542 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
BARRANQUITAS | 2023-03-12 19:31 | 2023-03-13 11:02 | 23 | 15:31 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA, CRUCE POR AVE. | C23031200008 | New_Event | Animals | Include | Include | Wildlife | 931 | 2023-03-12 | 21413 | keep | 0 | Mar | 2023 | 0.014584 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
AGUADILLA | 2023-03-12 19:50 | 2023-03-13 09:55 | 8 | 14:05 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO RAMA | M23031200188 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 845 | 2023-03-12 | 6760 | keep | 0 | Mar | 2023 | 0.0046042 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-12 19:57 | 2023-03-13 01:12 | 250 | 5:15 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23031200102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2023-03-12 | 78750 | keep | 0 | Mar | 2023 | 0.053636 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2023-03-12 20:02 | 2023-03-12 23:07 | 52 | 3:05 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN RISER EL T-2 ESTA AVERIADO Y SE DEJO FUERA 8 CLIENTES AFECTADOS | R23031200541 | New_Event | Service Transformer Failure | Include | Include | Equipment | 185 | 2023-03-12 | 9620 | keep | 0 | Mar | 2023 | 0.0065521 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CANOVANAS | 2023-03-12 20:34 | 2023-03-13 12:45 | 20 | 16:11 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REMPLAZO EL MISMO POR UNO DE LA MISMA CAPACIDAD 50 KVA | R23031200547 | New_Event | Service Transformer Failure | Include | Include | Equipment | 971 | 2023-03-12 | 19420 | keep | 0 | Mar | 2023 | 0.013227 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-03-12 21:12 | 2023-03-12 21:15 | 4702 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23031200284 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-12 | 14106 | keep | 0 | Mar | 2023 | 0.0096075 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-03-12 22:10 | 2023-03-12 22:12 | 4702 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23031200304 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-12 | 9404 | keep | 0 | Mar | 2023 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
BAYAMON | 2023-03-12 22:40 | 2023-03-12 23:02 | 4431 | 0:22 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR POR ERROR DEL PERSONAL DE CAMPO AL REALIZAR OPERACIONES PARA LEVANTAR CONDUCTOR PRIMARIO DEL SUELO BY-230312-03 | B23031200283 | New_Event | Human Error | Include | Include | Other | 22 | 2023-03-12 | 97482 | keep | 0 | Mar | 2023 | 0.066395 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
VEGA BAJA | 2023-03-12 23:06 | 2023-03-12 23:08 | 4702 | 0:02 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA PODER ABRIR EL MACHETE QUE ESTABA QUEMANDO QUE AUN TENIAN SERVICIO Y POSTERIORMENTE REMPLAZAR EL MISMO - QUEDAN 50 CLIENTES SIN SERVICIO | B23031200421 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2023-03-12 | 9404 | keep | 0 | Mar | 2023 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
CANOVANAS | 2023-03-12 23:07 | 2023-03-13 15:40 | 8 | 16:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 100 KVA AVERIADO | R23031200541 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 993 | 2023-03-12 | 7944 | keep | 0 | Mar | 2023 | 0.0054106 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-12 23:08 | 2023-03-13 07:20 | 50 | 8:12 | P | DESCONECTIVO DEFECTUOSO | SE DEJO ABIERTO EL MACHETE QUEMADO PARA SER REEMPLAZADO EN LA MANANA BY-230312-04 | B23031200421 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 492 | 2023-03-12 | 24600 | keep | 0 | Mar | 2023 | 0.016755 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-12 23:09 | 2023-03-12 23:10 | 1834 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23031200402 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-12 | 1834 | keep | 0 | Mar | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
FAJARDO | 2023-03-12 23:21 | 2023-03-13 08:39 | 10 | 9:18 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23031200565 | New_Event | Vegetation Contact | Include | Include | Vegetation | 558 | 2023-03-12 | 5580 | keep | 0 | Mar | 2023 | 0.0038005 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-12 23:43 | 2023-03-12 23:50 | 2657 | 0:07 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA PODER ABRIR C/L INOPERANTE PARA REPARAR/LEVANTAR CONDUCTOR VIVO QUEMANDO EN EL SUELO LLEVA PARTE DEL 1717-03 | B23031200283 | New_Event | Primary Wire Break | Include | Include | Equipment | 7 | 2023-03-12 | 18599 | keep | 0 | Mar | 2023 | 0.012668 | 0.0018097 | Sustained | FALSE | FALSE | Not_TMED_Event | 2657
BAYAMON | 2023-03-12 23:43 | 2023-03-12 23:50 | 2617 | 0:07 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA PODER ABRIR C/L INOPERANTE PARA REPARAR/LEVANTAR CONDUCTOR VIVO QUEMANDO EN EL SUELO LLEVA PARTE DEL 1717-03 | B23031200283 | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-03-12 | 18319 | keep | 0 | Mar | 2023 | 0.012477 | 0.0017824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2023-03-12 23:50 | 2023-03-13 01:42 | 300 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. BY-230312-03 | B23031200283 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 112 | 2023-03-12 | 33600 | keep | 0 | Mar | 2023 | 0.022885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-13 00:05 | 2023-03-13 06:25 | 9 | 6:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C23031300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 380 | 2023-03-13 | 3420 | keep | 0 | Mar | 2023 | 0.0023293 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-03-13 00:42 | 2023-03-13 00:43 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23031300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-13 | 4085 | keep | 0 | Mar | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
BARRANQUITAS | 2023-03-13 01:07 | 2023-03-13 01:09 | 3296 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | C2303130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-13 | 6592 | keep | 0 | Mar | 2023 | 0.0044898 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2023-03-13 01:09 | 2023-03-13 06:53 | 21 | 5:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23031300004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 344 | 2023-03-13 | 7224 | keep | 0 | Mar | 2023 | 0.0049202 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
HUMACAO | 2023-03-13 01:49 | 2023-03-13 01:50 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2303130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-13 | 2354 | keep | 0 | Mar | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-03-13 02:21 | 2023-03-13 08:22 | 130 | 6:01 | P | NO SE REPORTO CAUSA | 1 X 200 EN SU11 | C23031300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 361 | 2023-03-13 | 46930 | keep | 0 | Mar | 2023 | 0.031964 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
YAUCO | 2023-03-13 06:28 | 2023-03-13 06:29 | 1339 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 1339 | keep | 0 | Mar | 2023 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-03-13 06:28 | 2023-03-13 06:29 | 470 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 470 | keep | 0 | Mar | 2023 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2023-03-13 06:28 | 2023-03-13 06:29 | 2483 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 2483 | keep | 0 | Mar | 2023 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2023-03-13 06:28 | 2023-03-13 06:29 | 2190 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 2190 | keep | 0 | Mar | 2023 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2023-03-13 06:28 | 2023-03-13 06:29 | 3006 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 3006 | keep | 0 | Mar | 2023 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2023-03-13 06:28 | 2023-03-13 06:29 | 179 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 179 | keep | 0 | Mar | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2023-03-13 06:28 | 2023-03-13 06:29 | 107 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 107 | keep | 0 | Mar | 2023 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2023-03-13 06:28 | 2023-03-13 06:29 | 1666 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 1666 | keep | 0 | Mar | 2023 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2023-03-13 06:28 | 2023-03-13 06:29 | 4387 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 4387 | keep | 0 | Mar | 2023 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2023-03-13 06:28 | 2023-03-13 06:29 | 3147 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 3147 | keep | 0 | Mar | 2023 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2023-03-13 06:28 | 2023-03-13 06:29 | 4304 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23031300010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 4304 | keep | 0 | Mar | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2023-03-13 06:50 | 2023-03-13 09:50 | 150 | 3:00 | P | CAPACITOR DEFECTUOSO O AVERIADO | 2 X 100 EN CORTE DE LINEA AVERIA DE CAPACITORES | M23031300014 | New_Event | Capacitor Failure | Include | Include | Equipment | 180 | 2023-03-13 | 27000 | keep | 0 | Mar | 2023 | 0.01839 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-03-13 06:59 | 2023-03-13 10:38 | 837 | 3:39 | T | ALIMENTADOR AMARRADO | DISPARO SE PATRULLO NO SE ENCONTRO CAUSA Y SE CERRO INTERRUPTOR LOCALMENTE SU CARGA POR 1401-07 | S23031300010 | New_Event | Feeder Load Transferred | Include | Include | Other | 219 | 2023-03-13 | 183303 | keep | 0 | Mar | 2023 | 0.12485 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-03-13 06:59 | 2023-03-13 10:38 | 908 | 3:39 | T | NO SE REPORTO CAUSA | DISPARO SE PATRULLO NO SE ENCONTRO CAUSA Y SE CERRO INTERRUPTOR LOCALMENTE LLEVA 1401-6 | S23031300010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2023-03-13 | 198852 | keep | 0 | Mar | 2023 | 0.13544 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
BARRANQUITAS | 2023-03-13 07:16 | 2023-03-13 08:42 | 20 | 1:26 | P | NO SE REPORTO CAUSA | SE PATRULLO 1 X 30 EN CORTE DE LINEA | C23031300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2023-03-13 | 1720 | keep | 0 | Mar | 2023 | 0.0011715 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-03-13 07:20 | 2023-03-13 15:32 | 303 | 8:12 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO MEDIANTE GOI BY-230312-04 | B23031200421 | Additional_clients | Switch Failure | Include | Include | Equipment | 492 | 2023-03-13 | 149076 | keep | 0 | Mar | 2023 | 0.10153 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-13 07:31 | 2023-03-13 09:27 | 627 | 1:56 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE | B23031300037 | New_Event | Primary Wire Break | Include | Include | Equipment | 116 | 2023-03-13 | 72732 | keep | 0 | Mar | 2023 | 0.049537 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
MAYAGÃœEZ | 2023-03-13 07:34 | 2023-03-13 11:20 | 30 | 3:46 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M23031300018 | New_Event | Animals | Include | Include | Wildlife | 226 | 2023-03-13 | 6780 | keep | 0 | Mar | 2023 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-13 07:42 | 2023-03-13 09:28 | 10 | 1:46 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | B23031300039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 106 | 2023-03-13 | 1060 | keep | 0 | Mar | 2023 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-13 07:59 | 2023-03-13 08:00 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2303130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-13 | 2234 | keep | 0 | Mar | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2023-03-13 08:13 | 2023-03-13 09:59 | 271 | 1:46 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE REALIZAN OPERACIONES PAR SECCIONALIZAR ALIMENTADOR SE CERRO POR SCADA 5% EN SERVICIO SJ-230313-01 | S23031300023 | New_Event | Switch Failure | Include | Include | Equipment | 106 | 2023-03-13 | 28726 | keep | 0 | Mar | 2023 | 0.019565 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
MAYAGÃœEZ | 2023-03-13 08:21 | 2023-03-13 13:24 | 1 | 5:03 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE SECUNDARIO Y SE HACE CAMBIO SECUNDARIO | M23031300024 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 303 | 2023-03-13 | 303 | keep | 0 | Mar | 2023 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-13 08:27 | 2023-03-13 11:47 | 60 | 3:20 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23031300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-03-13 | 12000 | keep | 0 | Mar | 2023 | 0.0081731 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-13 08:35 | 2023-03-13 09:36 | 1 | 1:01 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE X AVE | C23031300028 | New_Event | Animals | Include | Include | Wildlife | 61 | 2023-03-13 | 61 | keep | 0 | Mar | 2023 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-13 08:35 | 2023-03-13 09:43 | 80 | 1:08 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23031300052 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-03-13 | 5440 | keep | 0 | Mar | 2023 | 0.0037052 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-03-13 08:39 | 2023-03-13 08:41 | 996 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 20% POR 1620-04 SE PROBO POR CONTROL QUEDO EN SERVICIO | R23031300042 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-13 | 1992 | keep | 0 | Mar | 2023 | 0.0013567 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
CANOVANAS | 2023-03-13 08:39 | 2023-03-13 08:41 | 172 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA 20% DEL 1336-06 SE PROBO POR CONTROL QUEDO EN SERVICIO | R23031300042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-13 | 344 | keep | 0 | Mar | 2023 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
VEGA BAJA | 2023-03-13 08:45 | 2023-03-13 18:25 | 40 | 9:40 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | A23031300007 | New_Event | Animals | Include | Include | Wildlife | 580 | 2023-03-13 | 23200 | keep | 0 | Mar | 2023 | 0.015801 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-03-13 08:47 | 2023-03-13 14:08 | 15 | 5:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA QUEMADA DE XMR | C23031300032 | New_Event | Cutout Failure | Include | Include | Equipment | 321 | 2023-03-13 | 4815 | keep | 0 | Mar | 2023 | 0.0032795 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-03-13 09:04 | 2023-03-13 14:40 | 28 | 5:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L Y SE INSTALO AISLADOR | R23031300038 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 336 | 2023-03-13 | 9408 | keep | 0 | Mar | 2023 | 0.0064077 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
FAJARDO | 2023-03-13 09:06 | 2023-03-13 12:31 | 1 | 3:25 | P | DESGANCHE | 1 X 20 EN XMR SE REALIZO DESGANCHE PRIMARIO | R23031300040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-03-13 | 205 | keep | 0 | Mar | 2023 | 0.00013962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-03-13 09:15 | 2023-03-13 13:00 | 10 | 3:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN XMR SE REMPLAZO 2 CAJAS QUEMADAS EN XMR | P23031300044 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2023-03-13 | 2250 | keep | 0 | Mar | 2023 | 0.0015325 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-13 09:46 | 2023-03-13 10:00 | 10 | 0:14 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE PRIMARIO DE LINEA A CAJA DE TRANSFORMADOR | S23031200052 | New_Event | Primary Wire Break | Include | Include | Equipment | 14 | 2023-03-13 | 140 | keep | 0 | Mar | 2023 | 9.5353e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-13 09:53 | 2023-03-13 16:00 | 13 | 6:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN TRANSFOMADOR SE REPARO LINEA SECUNDARIA | M23031300077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 367 | 2023-03-13 | 4771 | keep | 0 | Mar | 2023 | 0.0032495 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-03-13 09:59 | 2023-03-13 10:09 | 257 | 0:10 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR REALIZANDO OPERACIONES PARA SECCIONALIZAR ALIMENTADOR SJ-230313-01 | S23031300023 | Partial_restoration | Switch Failure | Include | Include | Equipment | 10 | 2023-03-13 | 2570 | keep | 0 | Mar | 2023 | 0.0017504 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-13 10:04 | 2023-03-13 23:35 | 200 | 13:31 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZARON (2) POSTES PRIMARIOS CON XMR | C23031300045 | New_Event | Primary Pole Failure | Include | Include | Equipment | 811 | 2023-03-13 | 162200 | keep | 0 | Mar | 2023 | 0.11047 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-03-13 10:09 | 2023-03-13 10:55 | 271 | 0:46 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 5% EN SERVICIO SE CERRO POR SCADA SJ-230313-01 | S23031300023 | New_Event | Switch Failure | Include | Include | Equipment | 46 | 2023-03-13 | 12466 | keep | 0 | Mar | 2023 | 0.0084905 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
HUMACAO | 2023-03-13 10:12 | 2023-03-13 15:54 | 10 | 5:42 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C23031300046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 342 | 2023-03-13 | 3420 | keep | 0 | Mar | 2023 | 0.0023293 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-03-13 10:32 | 2023-03-13 12:29 | 15 | 1:57 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CL DESGANCHE | R23031300058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-03-13 | 1755 | keep | 0 | Mar | 2023 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-03-13 10:40 | 2023-03-13 10:55 | 8 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARA CONECIONES EN BUSHING DEL TRANSFORMADOR | A23031300023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-03-13 | 120 | keep | 0 | Mar | 2023 | 8.1731e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-13 10:51 | 2023-03-13 15:35 | 1 | 4:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L SE REEMPLAZO CAJA PRIMARIA | R23031300059 | New_Event | Cutout Failure | Include | Include | Equipment | 284 | 2023-03-13 | 284 | keep | 0 | Mar | 2023 | 0.00019343 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-13 10:55 | 2023-03-13 12:25 | 257 | 1:30 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 20% EN SERVICIO SE CERRO POR SCADA SJ-230313-01 | S23031300023 | Partial_restoration | Switch Failure | Include | Include | Equipment | 90 | 2023-03-13 | 23130 | keep | 0 | Mar | 2023 | 0.015754 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-13 11:10 | 2023-03-13 18:10 | 30 | 7:00 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA POR IMPACTOR DE VEHICULO | A23031300034 | New_Event | Damage From Public | Include | Include | Public | 420 | 2023-03-13 | 12600 | keep | 0 | Mar | 2023 | 0.0085818 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-13 11:11 | 2023-03-13 11:42 | 10 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B23031300080 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2023-03-13 | 310 | keep | 0 | Mar | 2023 | 0.00021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-03-13 11:15 | 2023-03-13 15:30 | 7 | 4:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REEMPLAZA SECUNDARIAS AVERIADAS | A23031300033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 255 | 2023-03-13 | 1785 | keep | 0 | Mar | 2023 | 0.0012158 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-13 11:23 | 2023-03-13 11:24 | 1362 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | B2303130000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-13 | 1362 | keep | 0 | Mar | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2023-03-13 11:24 | 2023-03-13 16:29 | 166 | 5:05 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L Y SE LEVANTO CONDUCTOR DEL SUELO | B23031300085 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 305 | 2023-03-13 | 50630 | keep | 0 | Mar | 2023 | 0.034484 | 0.00011306 | Sustained | FALSE | FALSE | Not_TMED_Event | 166
FAJARDO | 2023-03-13 11:57 | 2023-03-13 14:05 | 1 | 2:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO TRAMO SECUNDARIO | R23031300064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 128 | 2023-03-13 | 128 | keep | 0 | Mar | 2023 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-13 12:10 | 2023-03-13 15:55 | 8 | 3:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARAN CONEXIONES | A23031300013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 225 | 2023-03-13 | 1800 | keep | 0 | Mar | 2023 | 0.001226 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-13 12:14 | 2023-03-13 12:35 | 7 | 0:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO C/L PARA REMPLAZAR AISLADOR | C23031300070 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 21 | 2023-03-13 | 147 | keep | 0 | Mar | 2023 | 0.00010012 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-03-13 12:15 | 2023-03-13 12:35 | 4 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE LINEA SECUNDARIA | M23031300074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-03-13 | 80 | keep | 0 | Mar | 2023 | 5.4488e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-03-13 12:15 | 2023-03-13 14:40 | 6 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARA CONEXIONES | M23031300073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-03-13 | 870 | keep | 0 | Mar | 2023 | 0.00059255 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-03-13 12:25 | 2023-03-13 12:43 | 217 | 0:18 | P | DESCONECTIVO DEFECTUOSO | SE REALIZO OPERACIONES PARA SECCIONALIZAR ALIMENTADOR 85% EN SERVICIO SJ-230313-01 | S23031300023 | Partial_restoration | Switch Failure | Include | Include | Equipment | 18 | 2023-03-13 | 3906 | keep | 0 | Mar | 2023 | 0.0026604 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-13 12:25 | 2023-03-13 13:47 | 478 | 1:22 | T | DESGANCHE | DISPARO DE BKR SE RETIRO RAMA DESDE EL SUELO A VARETA Y SE CERRO POR CONTROL | B23031300097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2023-03-13 | 39196 | keep | 0 | Mar | 2023 | 0.026696 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
YAUCO | 2023-03-13 12:25 | 2023-03-13 15:26 | 2 | 3:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P23031300070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-03-13 | 362 | keep | 0 | Mar | 2023 | 0.00024656 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-13 12:26 | 2023-03-13 13:37 | 60 | 1:11 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23031300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-03-13 | 4260 | keep | 0 | Mar | 2023 | 0.0029015 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-13 12:30 | 2023-03-13 13:00 | 10 | 0:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5KVA X 37.5KVA | B23031300083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 30 | 2023-03-13 | 300 | keep | 0 | Mar | 2023 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-13 12:43 | 2023-03-13 13:31 | 41 | 0:48 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO SJ-230313-01 | S23031300023 | Partial_restoration | Switch Failure | Include | Include | Equipment | 48 | 2023-03-13 | 1968 | keep | 0 | Mar | 2023 | 0.0013404 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-13 12:43 | 2023-03-14 15:18 | 6 | 26:35 | P | FUEGO | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE SE REMPLAZO 2 POSTES PRIMARIOS ROTOS Y SE REPARO LINEA PRIMARIA VERIFICADO EN BITACORA Y OMS | M23031300081 | New_Event | Fire | Include | Include | Public | 1595 | 2023-03-13 | 9570 | keep | 0 | Mar | 2023 | 0.0065181 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-03-13 12:48 | 2023-03-13 16:40 | 50 | 3:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CL FUERTE VIENTOS | M23031300083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 232 | 2023-03-13 | 11600 | keep | 0 | Mar | 2023 | 0.0079007 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-13 14:12 | 2023-03-13 15:34 | 2402 | 1:22 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR SE SECIONALIZO INTERRUPTOR MEDIANTE GOI BY-230313-02 Y ENTRO 80% EN SERVICIO | S23031300127 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 82 | 2023-03-13 | 196964 | keep | 0 | Mar | 2023 | 0.13415 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
CAGUAS | 2023-03-13 14:21 | 2023-03-13 14:38 | 1 | 0:17 | P | ANIMAL | 2 X 10 EN BANCO DE XMRS CRUCE X AVE | C23031300100 | New_Event | Animals | Include | Include | Wildlife | 17 | 2023-03-13 | 17 | keep | 0 | Mar | 2023 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-13 14:21 | 2023-03-13 18:40 | 80 | 4:19 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23031300106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-03-13 | 20720 | keep | 0 | Mar | 2023 | 0.014112 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-03-13 14:31 | 2023-03-13 14:32 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-13 | 2178 | keep | 0 | Mar | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
VEGA BAJA | 2023-03-13 14:46 | 2023-03-13 16:49 | 80 | 2:03 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | B23031300131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-03-13 | 9840 | keep | 0 | Mar | 2023 | 0.006702 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-13 15:06 | 2023-03-13 15:07 | 766 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1909-07 LLEVA 50% 1709-03 | B2303130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-13 | 766 | keep | 0 | Mar | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-03-13 15:06 | 2023-03-13 15:07 | 1139 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE DE INTERRUPTOR 1909-07 LLEVA 50% 1709-03 | B2303130000X | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-03-13 | 1139 | keep | 0 | Mar | 2023 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2023-03-13 15:07 | 2023-03-13 21:16 | 90 | 6:09 | P | CAUSAS EXTERNAS | 1 X 80 EN C/L PRINCIPAL Y 1 X 40 EN OTRO C/L CRUCE X GLOBO | S23031300220 | 1st_after_momentary | Damage From Public | Include | Include | Public | 369 | 2023-03-13 | 33210 | keep | 0 | Mar | 2023 | 0.022619 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-03-13 15:23 | 2023-03-13 15:47 | 1 | 0:24 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | S23031300148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2023-03-13 | 24 | keep | 0 | Mar | 2023 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-13 15:25 | 2023-03-13 18:24 | 150 | 2:59 | P | ANIMAL | 1 X 100 EN CL CRUCE DE FASE POR IGUANA | M23031300134 | New_Event | Animals | Include | Include | Wildlife | 179 | 2023-03-13 | 26850 | keep | 0 | Mar | 2023 | 0.018287 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-03-13 15:29 | 2023-03-13 17:00 | 60 | 1:31 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE | M23031300139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-03-13 | 5460 | keep | 0 | Mar | 2023 | 0.0037188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-13 15:34 | 2023-03-13 16:52 | 480 | 1:18 | P | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR SE SECIONALIZO INTERRUPTOR MEDIANTE GOI BY-230313-02 Y ENTRO 98% EN SERVICIO | S23031300127 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 78 | 2023-03-13 | 37440 | keep | 0 | Mar | 2023 | 0.0255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-13 15:35 | 2023-03-14 15:17 | 100 | 23:42 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 3 X 15 EN CORTE DE LINEA POR POSTE PARTIDO | M23031400141 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1422 | 2023-03-13 | 142200 | keep | 0 | Mar | 2023 | 0.096852 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-03-13 15:37 | 2023-03-13 21:52 | 7 | 6:15 | P | FUEGO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA QUEMADA POR FUEGO EN PASTO | M23031300143 | New_Event | Fire | Include | Include | Public | 375 | 2023-03-13 | 2625 | keep | 0 | Mar | 2023 | 0.0017879 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-13 15:48 | 2023-03-13 16:04 | 1 | 0:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO EL PORTAFUSIBLE Y 1 X 50 EN C/L | B23031300147 | New_Event | Cutout Failure | Include | Include | Equipment | 16 | 2023-03-13 | 16 | keep | 0 | Mar | 2023 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-13 15:52 | 2023-03-13 18:30 | 4 | 2:38 | P | PROBLEMA DEL CLIENTE | SE ABRIO BANCO DE XMR SE REEMPLAZO SECUNDARIA Y CONECTORES SE DEJO FUERA 1 CLIENTE A CAUSA DE FUEGO POR CONTADOR QUEMADO | S23031300158 | New_Event | Customer-Related Interruption | Include | Include | Public | 158 | 2023-03-13 | 632 | keep | 0 | Mar | 2023 | 0.00043045 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-03-13 16:20 | 2023-03-13 16:21 | 1320 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C23031300126 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-03-13 | 1320 | keep | 0 | Mar | 2023 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
VEGA BAJA | 2023-03-13 16:20 | 2023-03-13 18:46 | 70 | 2:26 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A23031300069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-03-13 | 10220 | keep | 0 | Mar | 2023 | 0.0069608 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-03-13 16:21 | 2023-03-13 21:28 | 700 | 5:07 | P | DESCONECTIVO DEFECTUOSO | 3 X 200 EN C/L REMPLAZO 3 MACHETES QUEMADOS | C23031300127 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 307 | 2023-03-13 | 214900 | keep | 0 | Mar | 2023 | 0.14637 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
CANOVANAS | 2023-03-13 16:33 | 2023-03-14 08:26 | 1 | 15:53 | P | TRANSFORMADOR AVERIADO | SE TRANSFIRIO LINEA SECUNDARIA A OTRO TRANSFORMADOR QUE ESTABA VACANTE | R23031300081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 953 | 2023-03-13 | 953 | keep | 0 | Mar | 2023 | 0.00064908 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-03-13 16:37 | 2023-03-13 18:34 | 1 | 1:57 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA PARA COMPLETAR TRIFASICA | P23031300105 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-03-13 | 117 | keep | 0 | Mar | 2023 | 7.9688e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-03-13 16:47 | 2023-03-13 18:31 | 60 | 1:44 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTARON ALAMBRES PRIMARIA Y SE CERRO CORTE DE LINEA | P23031300106 | New_Event | Primary Wire Break | Include | Include | Equipment | 104 | 2023-03-13 | 6240 | keep | 0 | Mar | 2023 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-03-13 16:50 | 2023-03-13 18:51 | 4 | 2:01 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XMR DESGANCHE | C23031300137 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 121 | 2023-03-13 | 484 | keep | 0 | Mar | 2023 | 0.00032965 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-03-13 16:52 | 2023-03-13 19:25 | 48 | 2:33 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETEZO LINEA ARRIADA TRAS PATIO MEDIANTE GOI BY-230313-02 100% EN SERVICIO | S23031300127 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 153 | 2023-03-13 | 7344 | keep | 0 | Mar | 2023 | 0.005002 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-13 17:16 | 2023-03-13 20:17 | 80 | 3:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REMPLAZO POERTAFUSIBLE | B23031300163 | New_Event | Cutout Failure | Include | Include | Equipment | 181 | 2023-03-13 | 14480 | keep | 0 | Mar | 2023 | 0.0098623 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-03-13 17:35 | 2023-03-17 23:40 | 1 | 102:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJAS QUEMADAS EN TRANSFORMADOR SE CREO EVENTO NUEVO M23031700291 8:31 PERO ESTABAN SIN SERVICIO DESDE EL 13 DE MARZO | M23031300208 | New_Event | Cutout Failure | Include | Include | Equipment | 6125 | 2023-03-13 | 6125 | keep | 0 | Mar | 2023 | 0.0041717 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-13 17:52 | 2023-03-13 22:33 | 150 | 4:41 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | C23031300156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 281 | 2023-03-13 | 42150 | keep | 0 | Mar | 2023 | 0.028708 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-03-13 18:11 | 2023-03-14 09:59 | 2 | 15:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 8 EN MONTURA TRIFASICA FUERTE VIENTOS | A23031300079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 948 | 2023-03-13 | 1896 | keep | 0 | Mar | 2023 | 0.0012914 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-03-13 18:20 | 2023-03-13 19:30 | 18 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARAN CONEXIONES | A23031300016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-03-13 | 1260 | keep | 0 | Mar | 2023 | 0.00085818 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-03-13 18:27 | 2023-03-13 18:28 | 2999 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23031300225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-13 | 2999 | keep | 0 | Mar | 2023 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
VEGA BAJA | 2023-03-13 19:02 | 2023-03-13 21:22 | 70 | 2:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA LINEA PRIMARIA PARTIDA | A23031300084 | New_Event | Primary Wire Break | Include | Include | Equipment | 140 | 2023-03-13 | 9800 | keep | 0 | Mar | 2023 | 0.0066747 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-03-13 19:26 | 2023-03-13 19:27 | 1834 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-13 | 1834 | keep | 0 | Mar | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
AGUADILLA | 2023-03-13 19:43 | 2023-03-13 21:14 | 80 | 1:31 | P | DESGANCHE | 2 X 100 EN CL DESGANCHE | M23031300235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-03-13 | 7280 | keep | 0 | Mar | 2023 | 0.0049584 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-03-13 19:52 | 2023-03-14 09:35 | 60 | 13:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23031300238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 823 | 2023-03-13 | 49380 | keep | 0 | Mar | 2023 | 0.033632 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-03-13 20:06 | 2023-03-13 20:07 | 1827 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO LINEA 6000 SOBRE ALIMENTADOR | M23031300243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-13 | 1827 | keep | 0 | Mar | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2023-03-13 20:13 | 2023-03-14 01:43 | 1827 | 5:30 | T | LINEA DE TRANSMISION 38KV | LINEA 6000 SOBRE ALIMENTADOR 7011-01 | M23031300247 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 330 | 2023-03-13 | 602910 | keep | 0 | Mar | 2023 | 0.41064 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2023-03-13 20:13 | 2023-03-14 01:34 | 1047 | 5:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6000 | M23031300252 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 321 | 2023-03-13 | 336087 | keep | 0 | Mar | 2023 | 0.22891 | 0.00071311 | Sustained | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2023-03-13 20:13 | 2023-03-14 01:34 | 4882 | 5:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6000 | M23031300252 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 321 | 2023-03-13 | 1567122 | keep | 0 | Mar | 2023 | 1.0674 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
BARRANQUITAS | 2023-03-13 20:24 | 2023-03-14 18:57 | 8 | 22:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 10 KVA X 10 KVA | C23031300174 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1353 | 2023-03-13 | 10824 | keep | 0 | Mar | 2023 | 0.0073722 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-13 20:47 | 2023-03-14 11:21 | 37 | 14:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA | B23031300206 | New_Event | Secondary Wire Break | Include | Include | Equipment | 874 | 2023-03-13 | 32338 | keep | 0 | Mar | 2023 | 0.022025 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BARRANQUITAS | 2023-03-13 21:16 | 2023-03-14 01:24 | 226 | 4:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO NO FUNDIO | C23031300176 | New_Event | Primary Wire Break | Include | Include | Equipment | 248 | 2023-03-13 | 56048 | keep | 0 | Mar | 2023 | 0.038174 | 0.00015393 | Sustained | FALSE | FALSE | Not_TMED_Event | 226
CANOVANAS | 2023-03-13 21:43 | 2023-03-13 22:08 | 76 | 0:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN RISER SE REMPLAZO CAJA PRIMARIA | R23031300091 | New_Event | Cutout Failure | Include | Include | Equipment | 25 | 2023-03-13 | 1900 | keep | 0 | Mar | 2023 | 0.0012941 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
BAYAMON | 2023-03-13 22:12 | 2023-03-14 02:03 | 134 | 3:51 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23031300218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2023-03-13 | 30954 | keep | 0 | Mar | 2023 | 0.021083 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2023-03-13 22:20 | 2023-03-14 10:39 | 1 | 12:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO Y SE RETEZO LINEA | B23031300022 | New_Event | Primary Wire Break | Include | Include | Equipment | 739 | 2023-03-13 | 739 | keep | 0 | Mar | 2023 | 0.00050333 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-13 22:32 | 2023-03-14 09:58 | 52 | 11:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | C23031300182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 686 | 2023-03-13 | 35672 | keep | 0 | Mar | 2023 | 0.024296 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
VEGA BAJA | 2023-03-13 22:51 | 2023-03-14 08:29 | 11 | 9:38 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO SAFADO EN CAJA DE TRANSFORMADOR | A23031300095 | New_Event | Primary Wire Break | Include | Include | Equipment | 578 | 2023-03-13 | 6358 | keep | 0 | Mar | 2023 | 0.0043304 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-03-13 23:15 | 2023-03-14 03:25 | 8 | 4:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO DE LINEA A CAJA | B23031300226 | New_Event | Primary Wire Break | Include | Include | Equipment | 250 | 2023-03-13 | 2000 | keep | 0 | Mar | 2023 | 0.0013622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-03-13 23:27 | 2023-03-14 08:00 | 5 | 8:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO SE REPORTO CAUSA | B23031300229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 513 | 2023-03-13 | 2565 | keep | 0 | Mar | 2023 | 0.001747 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-14 00:12 | 2023-03-14 09:28 | 35 | 9:16 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | R23031400001 | New_Event | Animals | Include | Include | Wildlife | 556 | 2023-03-14 | 19460 | keep | 0 | Mar | 2023 | 0.013254 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-03-14 00:50 | 2023-03-14 07:28 | 12 | 6:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23031400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 398 | 2023-03-14 | 4776 | keep | 0 | Mar | 2023 | 0.0032529 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-14 01:30 | 2023-03-14 01:31 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-14 | 1922 | keep | 0 | Mar | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2023-03-14 02:15 | 2023-03-14 13:18 | 101 | 11:03 | P | ANIMAL | 1 X 100 Y 1 X 80 EN CORTES DE LINEA CRUCE POR AVE | C23031400002 | New_Event | Animals | Include | Include | Wildlife | 663 | 2023-03-14 | 66963 | keep | 0 | Mar | 2023 | 0.045608 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
AGUADILLA | 2023-03-14 02:19 | 2023-03-14 02:20 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23031400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-14 | 1827 | keep | 0 | Mar | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BAYAMON | 2023-03-14 03:19 | 2023-03-14 04:40 | 80 | 1:21 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L TOTAL PARA REALIZAR DESGANCHE, LEVANTAR CONDUCTOR PRIMARIO DEL SUELO | B23031400007 | New_Event | Primary Wire Break | Include | Include | Equipment | 81 | 2023-03-14 | 6480 | keep | 0 | Mar | 2023 | 0.0044135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-03-14 03:19 | 2023-03-14 12:20 | 52 | 9:01 | P | DESGANCHE | 2 X 65 Y 1 X 80 EN CORTES DE LINEA DESGANCHE | C23031400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 541 | 2023-03-14 | 28132 | keep | 0 | Mar | 2023 | 0.019161 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
YAUCO | 2023-03-14 03:19 | 2023-03-14 09:27 | 200 | 6:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | M23031400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 368 | 2023-03-14 | 73600 | keep | 0 | Mar | 2023 | 0.050129 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-03-14 03:34 | 2023-03-14 07:05 | 1261 | 3:31 | S | AVERIA EN BARRA DE DISTRIBUCION | DISPARO DE MAIN BREAKER SE TRANSFIRIO LA CARGA CG-230314-01 SE REEMPLAZO PARARRAYO AVERIADO EN BARRA DE DISTRIBUCION | C23031400029 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 211 | 2023-03-14 | 266071 | keep | 0 | Mar | 2023 | 0.18122 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
CAGUAS | 2023-03-14 03:34 | 2023-03-14 07:05 | 1922 | 3:31 | S | AVERIA EN BARRA DE DISTRIBUCION | DISPARO DE MAIN BREAKER SE TRANSFIRIO LA CARGA CG-230314-01 SE REEMPLAZO PARARRAYO AVERIADO EN BARRA DE DISTRIBUCION | C23031400029 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 211 | 2023-03-14 | 405542 | keep | 0 | Mar | 2023 | 0.27621 | 0.0013091 | Sustained | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2023-03-14 03:34 | 2023-03-14 07:23 | 853 | 3:49 | S | AVERIA EN BARRA DE DISTRIBUCION | DISPARO DE MAIN BREAKER SE TRANSFIRIO LA CARGA CG-230314-01 SE REEMPLAZO PARARRAYO AVERIADO EN BARRA DE DISTRIBUCION | C23031400029 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 229 | 2023-03-14 | 195337 | keep | 0 | Mar | 2023 | 0.13304 | 0.00058097 | Sustained | FALSE | FALSE | Not_TMED_Event | 853
CAGUAS | 2023-03-14 03:34 | 2023-03-14 07:26 | 2900 | 3:52 | S | AVERIA EN BARRA DE DISTRIBUCION | DISPARO DE MAIN BREAKER SE TRANSFIRIO LA CARGA CG-230314-01 SE REEMPLAZO PARARRAYO AVERIADO EN BARRA DE DISTRIBUCION | C23031400029 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 232 | 2023-03-14 | 672800 | keep | 0 | Mar | 2023 | 0.45824 | 0.0019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 2900
CAGUAS | 2023-03-14 03:34 | 2023-03-14 06:33 | 2178 | 2:59 | S | AVERIA EN BARRA DE DISTRIBUCION | DISPARO DE MAIN BREAKER SE TRANSFIRIO LA CARGA CG-230314-01 SE REEMPLAZO PARARRAYO AVERIADO EN BARRA DE DISTRIBUCION | C23031400029 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 179 | 2023-03-14 | 389862 | keep | 0 | Mar | 2023 | 0.26553 | 0.0014834 | Sustained | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2023-03-14 04:40 | 2023-03-14 04:41 | 1105 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR A PETICION DE JUAN CARRASQUILLLO POR ALAMBRE EN EL SUELO PARA ABRIR CAJAS DEL C/L TOTAL QUE ESTABAN MUY INCOMODAS Y SE CERRO POR CONTROL | B23031400011 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-14 | 1105 | keep | 0 | Mar | 2023 | 0.00075261 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-14 04:41 | 2023-03-14 06:03 | 342 | 1:22 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L TOTAL Y SE LEVANTO ALAMBRE EN EL SUELO | B23031400011 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 82 | 2023-03-14 | 28044 | keep | 0 | Mar | 2023 | 0.019101 | 0.00023293 | Sustained | FALSE | FALSE | Not_TMED_Event | 342
VEGA BAJA | 2023-03-14 05:29 | 2023-03-14 08:25 | 5 | 2:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23031400012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2023-03-14 | 880 | keep | 0 | Mar | 2023 | 0.00059936 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-03-14 06:59 | 2023-03-14 13:44 | 1 | 6:45 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE ENCONTRO CAUSA | A23031400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 405 | 2023-03-14 | 405 | keep | 0 | Mar | 2023 | 0.00027584 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-14 07:05 | 2023-03-14 08:27 | 82 | 1:22 | P | ANIMAL | 1 X 65 Y 1 X 40 EN CORTES DE LINEA CRUCE POR AVE | C23031400006 | New_Event | Animals | Include | Include | Wildlife | 82 | 2023-03-14 | 6724 | keep | 0 | Mar | 2023 | 0.0045797 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
BAYAMON | 2023-03-14 07:47 | 2023-03-14 07:48 | 1397 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B23031400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-14 | 1397 | keep | 0 | Mar | 2023 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
HUMACAO | 2023-03-14 08:18 | 2023-03-14 10:53 | 138 | 2:35 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE CERRO PUENTE DE LINEA A CAJA | C23031400105 | New_Event | Primary Wire Break | Include | Include | Equipment | 155 | 2023-03-14 | 21390 | keep | 0 | Mar | 2023 | 0.014569 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
CANOVANAS | 2023-03-14 08:26 | 2023-03-14 08:27 | 3838 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23031400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-14 | 3838 | keep | 0 | Mar | 2023 | 0.002614 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
CANOVANAS | 2023-03-14 08:27 | 2023-03-14 15:57 | 1 | 7:30 | P | TRANSFORMADOR AVERIADO | SE TRANSFIRIO LINEA SECUNDARIA A OTRO TRANSFORMADOR QUE ESTABA VACANTE | R23031300081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 450 | 2023-03-14 | 450 | keep | 0 | Mar | 2023 | 0.00030649 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-14 08:30 | 2023-03-14 10:16 | 3 | 1:46 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | A23031400007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 106 | 2023-03-14 | 318 | keep | 0 | Mar | 2023 | 0.00021659 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-03-14 09:05 | 2023-03-14 11:22 | 23 | 2:17 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN C/L SE RETEZO PRIMARIA | B23031400030 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 137 | 2023-03-14 | 3151 | keep | 0 | Mar | 2023 | 0.0021461 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
PONCE | 2023-03-14 09:20 | 2023-03-14 12:10 | 8 | 2:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRAS EN PEDESTAL SECUNDARIO | P23031400042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 170 | 2023-03-14 | 1360 | keep | 0 | Mar | 2023 | 0.00092629 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-03-14 09:25 | 2023-03-14 09:39 | 1 | 0:14 | P | ANIMAL | 1 X 15 EN BANCO DE TRANSFORMADORES CRUCE POR CHANGO | C23031400132 | New_Event | Animals | Include | Include | Wildlife | 14 | 2023-03-14 | 14 | keep | 0 | Mar | 2023 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-14 09:33 | 2023-03-14 09:36 | 476 | 0:03 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA REPARAR NEUTRAL FLOTANTE TRAS PATIO EN TRANSFORMADOR REF. S2303100032 | S23031400059 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-03-14 | 1428 | keep | 0 | Mar | 2023 | 0.0009726 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
SAN JUAN | 2023-03-14 09:38 | 2023-03-14 10:40 | 45 | 1:02 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | S23031400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-03-14 | 2790 | keep | 0 | Mar | 2023 | 0.0019003 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-03-14 09:50 | 2023-03-14 12:18 | 1 | 2:28 | P | CRUCETA DEFECTUOSA O AVERIADA | 3 X 20 EN MONTURA Y SE LLEVO CAJA PRIMARIA A CRCETA | B23031400029 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 148 | 2023-03-14 | 148 | keep | 0 | Mar | 2023 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-14 09:55 | 2023-03-14 10:55 | 13 | 1:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | R23031400018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 60 | 2023-03-14 | 780 | keep | 0 | Mar | 2023 | 0.00053125 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2023-03-14 10:38 | 2023-03-14 13:41 | 1 | 3:03 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE | A23031400027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-03-14 | 183 | keep | 0 | Mar | 2023 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-03-14 10:43 | 2023-03-14 11:36 | 10 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23031400061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-03-14 | 530 | keep | 0 | Mar | 2023 | 0.00036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-14 11:07 | 2023-03-14 13:07 | 13 | 2:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | R23031400018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 120 | 2023-03-14 | 1560 | keep | 0 | Mar | 2023 | 0.0010625 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-03-14 11:29 | 2023-03-14 19:30 | 60 | 8:01 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | A23031400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 481 | 2023-03-14 | 28860 | keep | 0 | Mar | 2023 | 0.019656 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-14 12:15 | 2023-03-14 14:00 | 5 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIO TRAS PATIO | S23031400173 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2023-03-14 | 525 | keep | 0 | Mar | 2023 | 0.00035758 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-14 12:20 | 2023-03-14 12:23 | 643 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23031400197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-14 | 1929 | keep | 0 | Mar | 2023 | 0.0013138 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
SAN JUAN | 2023-03-14 12:21 | 2023-03-15 17:36 | 11 | 29:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S23031400196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1755 | 2023-03-14 | 19305 | keep | 0 | Mar | 2023 | 0.013149 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2023-03-14 12:26 | 2023-03-14 12:50 | 12 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONECTORES DEL XMR | B23031400092 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-03-14 | 288 | keep | 0 | Mar | 2023 | 0.00019616 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-03-14 12:29 | 2023-03-14 16:50 | 80 | 4:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER SE REMPLAZO CAJA PRIMARIA | S23031400206 | New_Event | Cutout Failure | Include | Include | Equipment | 261 | 2023-03-14 | 20880 | keep | 0 | Mar | 2023 | 0.014221 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-03-14 12:40 | 2023-03-14 14:26 | 20 | 1:46 | P | PROBLEMA DEL CLIENTE | ABRIR CAJA PRIMARIA DEL TRANSFORMADOR PARA DESCONECTAR TOMA QUEMADA DE CLIENTE SE DEJO FUERA | C23031300169 | New_Event | Customer-Related Interruption | Include | Include | Public | 106 | 2023-03-14 | 2120 | keep | 0 | Mar | 2023 | 0.0014439 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-14 12:42 | 2023-03-14 14:25 | 80 | 1:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M23031400089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-03-14 | 8240 | keep | 0 | Mar | 2023 | 0.0056122 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-14 12:54 | 2023-03-14 12:57 | 723 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR 1711-02 LLEVA 1711-05 Y 1912-08 | B2303140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-14 | 2169 | keep | 0 | Mar | 2023 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-03-14 12:54 | 2023-03-14 12:57 | 1976 | 0:03 | T | ALIMENTADOR AMARRADO | CERRADO POR CONTROL DISPARO DE ALIMENTADOR 1711-02 | B2303140000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-14 | 5928 | keep | 0 | Mar | 2023 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-03-14 12:54 | 2023-03-14 12:57 | 577 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE ALIMENTADOR CARGA POR 1711-02 | B2303140000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-14 | 1731 | keep | 0 | Mar | 2023 | 0.001179 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
VEGA BAJA | 2023-03-14 12:55 | 2023-03-14 12:56 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-14 | 1310 | keep | 0 | Mar | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2023-03-14 13:02 | 2023-03-14 13:05 | 723 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR 1711-02 LLEVA 1711-05 Y 1912-08 | B2303140000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-14 | 2169 | keep | 0 | Mar | 2023 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-03-14 13:02 | 2023-03-14 13:05 | 1976 | 0:03 | T | ALIMENTADOR AMARRADO | CERRADO POR CONTROL DISPARO DE ALIMENTADOR 1711-02 | B2303140000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-14 | 5928 | keep | 0 | Mar | 2023 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2023-03-14 13:20 | 2023-03-14 17:46 | 20 | 4:26 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO SE ABRE CL PARA REPARAR | A23031400060 | New_Event | Primary Wire Break | Include | Include | Equipment | 266 | 2023-03-14 | 5320 | keep | 0 | Mar | 2023 | 0.0036234 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-14 13:30 | 2023-03-14 15:50 | 30 | 2:20 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B23031400119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-03-14 | 4200 | keep | 0 | Mar | 2023 | 0.0028606 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-14 13:36 | 2023-03-14 15:50 | 16 | 2:14 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE ELIMINO PARARRAYO AVERIADO | C23031400546 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 134 | 2023-03-14 | 2144 | keep | 0 | Mar | 2023 | 0.0014603 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-03-14 13:41 | 2023-03-14 15:59 | 87 | 2:18 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | B23031400122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-03-14 | 12006 | keep | 0 | Mar | 2023 | 0.0081772 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
FAJARDO | 2023-03-14 13:43 | 2023-03-14 15:29 | 3 | 1:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R23031400107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-03-14 | 318 | keep | 0 | Mar | 2023 | 0.00021659 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-14 13:56 | 2023-03-14 15:05 | 1242 | 1:09 | P | NO SE REPORTO CAUSA | RECERRO 3 VECES QUEDO FUERA SE PATRULLO NO SE ENCONTRO CAUSA Y SE CERRO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1204-01 LLEVA 90% DE SU CARGA | S23031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2023-03-14 | 85698 | keep | 0 | Mar | 2023 | 0.058369 | 0.00084592 | Sustained | FALSE | FALSE | Not_TMED_Event | 1242
VEGA BAJA | 2023-03-14 13:56 | 2023-03-14 18:08 | 130 | 4:12 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN CORTE DE LINEA POR BAJANTE PEGANDO A ESTRUCTURA | A23031400066 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 252 | 2023-03-14 | 32760 | keep | 0 | Mar | 2023 | 0.022313 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
GUAYAMA | 2023-03-14 13:57 | 2023-03-14 15:17 | 40 | 1:20 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEAS | P23031400131 | New_Event | Animals | Include | Include | Wildlife | 80 | 2023-03-14 | 3200 | keep | 0 | Mar | 2023 | 0.0021795 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-03-14 13:58 | 2023-03-14 14:34 | 13 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE CONECTORES QUEMADOS EN LINEA SECUNDARIAS | R23031400110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2023-03-14 | 468 | keep | 0 | Mar | 2023 | 0.00031875 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2023-03-14 14:01 | 2023-03-14 16:22 | 80 | 2:21 | P | ANIMAL | 1 X 65 EN CL CRUCE DE FASE PRIMARIA POR AVE | A23031400069 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-03-14 | 11280 | keep | 0 | Mar | 2023 | 0.0076828 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-14 14:04 | 2023-03-14 14:34 | 50 | 0:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L SE REMPLAZO POSTAFUSIBLE QUEMADO | B23031400148 | New_Event | Cutout Failure | Include | Include | Equipment | 30 | 2023-03-14 | 1500 | keep | 0 | Mar | 2023 | 0.0010216 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-14 14:04 | 2023-03-14 16:36 | 1 | 2:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN RISER Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | B23031400127 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 152 | 2023-03-14 | 152 | keep | 0 | Mar | 2023 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-14 14:09 | 2023-03-14 16:30 | 15 | 2:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23031400111 | New_Event | Secondary Wire Break | Include | Include | Equipment | 141 | 2023-03-14 | 2115 | keep | 0 | Mar | 2023 | 0.0014405 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-03-14 14:10 | 2023-03-14 15:24 | 103 | 1:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C23031400578 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2023-03-14 | 7622 | keep | 0 | Mar | 2023 | 0.0051913 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
BAYAMON | 2023-03-14 14:13 | 2023-03-14 17:23 | 62 | 3:10 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L Y SE ENDEREZO PUENTE PEGADO A CRUCETA | B23031400146 | New_Event | Primary Wire Break | Include | Include | Equipment | 190 | 2023-03-14 | 11780 | keep | 0 | Mar | 2023 | 0.0080233 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-03-14 14:27 | 2023-03-14 18:18 | 7 | 3:51 | P | CAUSAS EXTERNAS | 1 X 15 EN XMR SE RETIRO GLOBO | B23031400132 | New_Event | Damage From Public | Include | Include | Public | 231 | 2023-03-14 | 1617 | keep | 0 | Mar | 2023 | 0.0011013 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-03-14 14:29 | 2023-03-14 14:30 | 4830 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 800 DE LOS CLIENTES POR EL 3205-07 PARA MEJORAR VOLTAJE EN SERVICIO | C23031400598 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-14 | 4830 | keep | 0 | Mar | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
BAYAMON | 2023-03-14 14:30 | 2023-03-14 14:31 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23031400135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-14 | 2402 | keep | 0 | Mar | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
HUMACAO | 2023-03-14 14:31 | 2023-03-14 15:34 | 676 | 1:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 5300 INFORMO EL ING. JESUS LOPEZ | C23031400609 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2023-03-14 | 42588 | keep | 0 | Mar | 2023 | 0.029006 | 0.00046042 | Sustained | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2023-03-14 14:31 | 2023-03-14 15:34 | 2873 | 1:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 5300 INFORMO EL ING. JESUS LOPEZ | C23031400609 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2023-03-14 | 180999 | keep | 0 | Mar | 2023 | 0.12328 | 0.0019568 | Sustained | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2023-03-14 14:31 | 2023-03-14 15:34 | 3902 | 1:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 5300 INFORMO EL ING. JESUS LOPEZ | C23031400609 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2023-03-14 | 245826 | keep | 0 | Mar | 2023 | 0.16743 | 0.0026576 | Sustained | FALSE | FALSE | Not_TMED_Event | 3902
BAYAMON | 2023-03-14 14:34 | 2023-03-14 14:37 | 911 | 0:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO POR CONTROL | B23031400137 | Additional_clients | Cutout Failure | Include | Include | Equipment | 3 | 2023-03-14 | 2733 | keep | 0 | Mar | 2023 | 0.0018614 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-14 14:35 | 2023-03-14 15:07 | 29 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S23031400199 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2023-03-14 | 928 | keep | 0 | Mar | 2023 | 0.00063206 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2023-03-14 14:37 | 2023-03-14 18:49 | 50 | 4:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L SE REMPLAZO POSTAFUSIBLE QUEMADO | B23031400148 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 252 | 2023-03-14 | 12600 | keep | 0 | Mar | 2023 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-03-14 14:42 | 2023-03-14 18:00 | 8 | 3:18 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R23031400118 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 198 | 2023-03-14 | 1584 | keep | 0 | Mar | 2023 | 0.0010789 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-03-14 14:48 | 2023-03-14 18:42 | 13 | 3:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C23031400613 | New_Event | Cutout Failure | Include | Include | Equipment | 234 | 2023-03-14 | 3042 | keep | 0 | Mar | 2023 | 0.0020719 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2023-03-14 14:50 | 2023-03-14 17:10 | 15 | 2:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | M23031400117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-03-14 | 2100 | keep | 0 | Mar | 2023 | 0.0014303 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-14 14:54 | 2023-03-14 19:39 | 70 | 4:45 | P | DESGANCHE | 1 X 50 EN C/L Y 1 X 10 EN XMR Y DESGANCHE | B23031400157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2023-03-14 | 19950 | keep | 0 | Mar | 2023 | 0.013588 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-03-14 15:03 | 2023-03-14 17:24 | 27 | 2:21 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | R23031400130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2023-03-14 | 3807 | keep | 0 | Mar | 2023 | 0.0025929 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-03-14 15:08 | 2023-03-15 01:01 | 40 | 9:53 | P | ANIMAL | 1SMU20X20AMPS DEL SU-4A @ T-28 Y SE RETIRO ROEDOR (RATON) | B23031400163 | New_Event | Animals | Include | Include | Wildlife | 593 | 2023-03-14 | 23720 | keep | 0 | Mar | 2023 | 0.016156 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-03-14 15:14 | 2023-03-14 16:37 | 50 | 1:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CL FUERTE LLUVIA | A23031400084 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 83 | 2023-03-14 | 4150 | keep | 0 | Mar | 2023 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-03-14 15:22 | 2023-03-14 18:39 | 45 | 3:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN CL NO SE ENCONTRO CAUSA | A23031400087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2023-03-14 | 8865 | keep | 0 | Mar | 2023 | 0.0060379 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-03-14 15:23 | 2023-03-14 15:40 | 5 | 0:17 | P | CAUSAS EXTERNAS | 1 X 25 EN TRANSFORMADO POR IMPACTO DE VEHICULO | M23031400124 | New_Event | Damage From Public | Include | Include | Public | 17 | 2023-03-14 | 85 | keep | 0 | Mar | 2023 | 5.7893e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-03-14 15:24 | 2023-03-14 15:57 | 60 | 0:33 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23031400089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2023-03-14 | 1980 | keep | 0 | Mar | 2023 | 0.0013486 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-14 15:27 | 2023-03-14 15:29 | 513 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 20% POR 1118-10 SE PROBO POR CONTROL QUEDO EN SERVICIO | S23031400000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-14 | 1026 | keep | 0 | Mar | 2023 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-03-14 15:27 | 2023-03-14 15:29 | 2782 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 20% DEL 1111-01 SE PROBO POR CONTROL QUEDO EN SERVICIO | S23031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-14 | 5564 | keep | 0 | Mar | 2023 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
AGUADILLA | 2023-03-14 15:34 | 2023-03-14 18:14 | 15 | 2:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REQUIERE DESGANCHE | M23031400127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-03-14 | 2400 | keep | 0 | Mar | 2023 | 0.0016346 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-03-14 15:38 | 2023-03-14 16:54 | 16 | 1:16 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION SOTERRADA EN PADMONTED | P23031400075 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 76 | 2023-03-14 | 1216 | keep | 0 | Mar | 2023 | 0.00082821 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-03-14 15:40 | 2023-03-14 16:20 | 6 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S23031400225 | New_Event | Primary Wire Break | Include | Include | Equipment | 40 | 2023-03-14 | 240 | keep | 0 | Mar | 2023 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-03-14 15:46 | 2023-03-14 18:07 | 21 | 2:21 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | R23031400129 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-03-14 | 2961 | keep | 0 | Mar | 2023 | 0.0020167 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
UTUADO | 2023-03-14 15:58 | 2023-03-14 21:46 | 3 | 5:48 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23021400161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2023-03-14 | 1044 | keep | 0 | Mar | 2023 | 0.00071106 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-03-14 15:59 | 2023-03-14 21:20 | 9 | 5:21 | P | SECUNDARIA/DESGANCHE | SE ABRE CAJAS EN TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA POR RAMA | A23031400105 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 321 | 2023-03-14 | 2889 | keep | 0 | Mar | 2023 | 0.0019677 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-03-14 16:03 | 2023-03-14 18:08 | 20 | 2:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA PRINCIPAL Y DESGANCHE | S23031400296 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-03-14 | 2500 | keep | 0 | Mar | 2023 | 0.0017027 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-14 16:04 | 2023-03-14 23:03 | 160 | 6:59 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO, SE REPARO NEUTRAL DEL SISTEMA CRUZADO Y SE CERRO PB MEDIANTE G.O.I. BY-230314-04 | B23031400176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 419 | 2023-03-14 | 67040 | keep | 0 | Mar | 2023 | 0.045661 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2023-03-14 16:08 | 2023-03-14 17:14 | 1 | 1:06 | P | ANIMAL | 1 X 15 EN EN BANCO DE XMR Y 1X 40 EN C/L CRUCE X IGUANA | B23031400183 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-03-14 | 66 | keep | 0 | Mar | 2023 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-14 16:20 | 2023-03-14 18:30 | 5 | 2:10 | P | CAUSAS EXTERNAS | SE ABRIO CAJAS EN TRANSFORMADOR DEBIDO A POSTE SECUNDARIO PARTIDO POR IMPACTO DE VEHICULO PESADO AL TENSOR | A23031400072 | New_Event | Damage From Public | Include | Include | Public | 130 | 2023-03-14 | 650 | keep | 0 | Mar | 2023 | 0.00044271 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-14 16:25 | 2023-03-14 16:43 | 9 | 0:18 | P | PROBLEMA DEL CLIENTE | 1 X 50 EN CORTE DE LINEA PROBLEMA INTERNO BOMBA AAA | R23031400137 | New_Event | Customer-Related Interruption | Include | Include | Public | 18 | 2023-03-14 | 162 | keep | 0 | Mar | 2023 | 0.00011034 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-03-14 16:28 | 2023-03-14 19:56 | 100 | 3:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CL FUERTE LLUVIA | A23031400118 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 208 | 2023-03-14 | 20800 | keep | 0 | Mar | 2023 | 0.014167 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-14 16:56 | 2023-03-14 19:08 | 143 | 2:12 | T | NO SE REPORTO CAUSA | DISPARO SE LIMPIARON BANDERAS Y SE ABRIO N/O CONTRA 1404-07 SE CERRO POR CONTROL 100% 1404-06 | S23031400312 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2023-03-14 | 18876 | keep | 0 | Mar | 2023 | 0.012856 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-03-14 16:56 | 2023-03-14 19:10 | 1085 | 2:14 | P | ALIMENTADOR AMARRADO | DISPARO SE LIMPIARON BANDERAS Y SE CERRO N/O 80% DE SU CARGA POR 1404-06 NO SE REPORTO CAUSA | S23031400312 | New_Event | Feeder Load Transferred | Include | Include | Other | 134 | 2023-03-14 | 145390 | keep | 0 | Mar | 2023 | 0.099024 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
CAGUAS | 2023-03-14 17:02 | 2023-03-15 05:57 | 2 | 12:55 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | C23031400064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 775 | 2023-03-14 | 1550 | keep | 0 | Mar | 2023 | 0.0010557 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-03-14 17:25 | 2023-03-14 19:25 | 70 | 2:00 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P23031400183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-03-14 | 8400 | keep | 0 | Mar | 2023 | 0.0057212 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-03-14 17:28 | 2023-03-14 18:03 | 186 | 0:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23031400654 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2023-03-14 | 6510 | keep | 0 | Mar | 2023 | 0.0044339 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
PONCE | 2023-03-14 17:33 | 2023-03-14 20:00 | 30 | 2:27 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE ELIMINO PARARAYO DEFECTUOSO | P23031400188 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 147 | 2023-03-14 | 4410 | keep | 0 | Mar | 2023 | 0.0030036 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-03-14 17:46 | 2023-03-14 18:16 | 80 | 0:30 | P | CONDUCTOR ROTO O ABIERTO | SE CIERRA PUENTE PRIMARIO Y SE CERRO CL | A23031400060 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 30 | 2023-03-14 | 2400 | keep | 0 | Mar | 2023 | 0.0016346 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-14 17:46 | 2023-03-14 22:12 | 34 | 4:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X200 EN C/L SE REMPLAZO CAJA PRIMARIA | B23031400261 | New_Event | Cutout Failure | Include | Include | Equipment | 266 | 2023-03-14 | 9044 | keep | 0 | Mar | 2023 | 0.0061598 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
VEGA BAJA | 2023-03-14 17:48 | 2023-03-14 20:41 | 100 | 2:53 | P | DESGANCHE | 1 X 65 EN C/L SE RETIRO RAMA | B23031400264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-03-14 | 17300 | keep | 0 | Mar | 2023 | 0.011783 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-03-14 17:55 | 2023-03-14 19:51 | 15 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIA | B23031400280 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2023-03-14 | 1740 | keep | 0 | Mar | 2023 | 0.0011851 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-03-14 18:09 | 2023-03-14 20:38 | 80 | 2:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M23031400163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-03-14 | 11920 | keep | 0 | Mar | 2023 | 0.0081187 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-03-14 18:14 | 2023-03-14 21:19 | 5 | 3:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X30 C/L POR VIENTO FUERTE | B23031400310 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 185 | 2023-03-14 | 925 | keep | 0 | Mar | 2023 | 0.00063001 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-03-14 18:17 | 2023-03-15 17:00 | 250 | 22:43 | P | CAUSAS EXTERNAS | 2 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO PARTIDO CAMION PRIVADO DE ALIMENTOS AVERIO POSTE DE TEL Y A SU VEZ POSTES DE LUMA | A23031400133 | New_Event | Damage From Public | Include | Include | Public | 1363 | 2023-03-14 | 340750 | keep | 0 | Mar | 2023 | 0.23208 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2023-03-14 18:17 | 2023-03-14 20:54 | 10 | 2:37 | P | CAUSAS EXTERNAS | 1 X 40 EN CL TENSOR PARTIDO CRUZA FASE PRIMARIA | A23031400146 | New_Event | Damage From Public | Include | Include | Public | 157 | 2023-03-14 | 1570 | keep | 0 | Mar | 2023 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-14 18:22 | 2023-03-14 19:45 | 100 | 1:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M23031400164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-03-14 | 8300 | keep | 0 | Mar | 2023 | 0.0056531 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-03-14 18:49 | 2023-03-14 22:10 | 6 | 3:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEAMAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23031400141 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 201 | 2023-03-14 | 1206 | keep | 0 | Mar | 2023 | 0.0008214 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-03-14 19:04 | 2023-03-14 20:58 | 80 | 1:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C23031400673 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-03-14 | 9120 | keep | 0 | Mar | 2023 | 0.0062116 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-03-14 19:10 | 2023-03-14 19:11 | 1 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23031400163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-14 | 1 | keep | 0 | Mar | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-14 19:15 | 2023-03-15 07:25 | 12 | 12:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23031400123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 730 | 2023-03-14 | 8760 | keep | 0 | Mar | 2023 | 0.0059664 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-03-14 19:17 | 2023-03-14 21:04 | 4 | 1:47 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | B23031400368 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-03-14 | 428 | keep | 0 | Mar | 2023 | 0.00029151 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-03-14 19:20 | 2023-03-14 19:38 | 12 | 0:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | C23031400475 | New_Event | Cutout Failure | Include | Include | Equipment | 18 | 2023-03-14 | 216 | keep | 0 | Mar | 2023 | 0.00014712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-03-14 19:27 | 2023-03-14 20:19 | 30 | 0:52 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23031400219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2023-03-14 | 1560 | keep | 0 | Mar | 2023 | 0.0010625 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-03-14 19:39 | 2023-03-14 22:44 | 350 | 3:05 | P | TRANSFORMADOR AVERIADO | SE RETIRO PELIGRO SE DEJO FUERA EL PM T-3 SE REPUSO 1 X 65 EN C/L | C23031400676 | New_Event | Service Transformer Failure | Include | Include | Equipment | 185 | 2023-03-14 | 64750 | keep | 0 | Mar | 2023 | 0.044101 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
UTUADO | 2023-03-14 19:39 | 2023-03-15 10:20 | 25 | 14:41 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031400155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 881 | 2023-03-14 | 22025 | keep | 0 | Mar | 2023 | 0.015001 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-03-14 19:39 | 2023-03-15 07:36 | 25 | 11:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C23031400667 | New_Event | Vegetation Contact | Include | Include | Vegetation | 717 | 2023-03-14 | 17925 | keep | 0 | Mar | 2023 | 0.012209 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-03-14 19:47 | 2023-03-14 22:20 | 400 | 2:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | A23031400178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-03-14 | 61200 | keep | 0 | Mar | 2023 | 0.041683 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
VEGA BAJA | 2023-03-14 19:49 | 2023-03-14 22:00 | 6 | 2:11 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23031400157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2023-03-14 | 786 | keep | 0 | Mar | 2023 | 0.00053534 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-03-14 20:09 | 2023-03-15 10:03 | 30 | 13:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23031400442 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 834 | 2023-03-14 | 25020 | keep | 0 | Mar | 2023 | 0.017041 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-03-14 20:11 | 2023-03-15 02:22 | 5 | 6:11 | P | DESGANCHE | 1X20 EN XMR DESGANCHE PRIMARIO | S23031400446 | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2023-03-14 | 1855 | keep | 0 | Mar | 2023 | 0.0012634 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-14 20:19 | 2023-03-15 09:42 | 56 | 13:23 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | S23031400452 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 803 | 2023-03-14 | 44968 | keep | 0 | Mar | 2023 | 0.030628 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2023-03-14 20:25 | 2023-03-15 01:33 | 40 | 5:08 | P | DESGANCHE | 1 X 100 EN LA ENTRADA DEL RISER & 1X65 EN LA SALIDA DEL RISER @ TRAMO AEREO - DESGANCHE | B23031400435 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2023-03-14 | 12320 | keep | 0 | Mar | 2023 | 0.0083911 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-14 20:54 | 2023-03-15 08:10 | 70 | 11:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23031400191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 676 | 2023-03-14 | 47320 | keep | 0 | Mar | 2023 | 0.032229 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2023-03-14 21:08 | 2023-03-15 10:10 | 79 | 13:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23031400693 | New_Event | Vegetation Contact | Include | Include | Vegetation | 782 | 2023-03-14 | 61778 | keep | 0 | Mar | 2023 | 0.042077 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
ARECIBO | 2023-03-14 22:16 | 2023-03-15 16:00 | 40 | 17:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23031400171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1064 | 2023-03-14 | 42560 | keep | 0 | Mar | 2023 | 0.028987 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-03-14 22:44 | 2023-03-15 20:07 | 25 | 21:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50 X 75KVA | C23031400676 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1283 | 2023-03-14 | 32075 | keep | 0 | Mar | 2023 | 0.021846 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-14 22:56 | 2023-03-15 09:17 | 5 | 10:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR EVENTRO TRANSFERIDO | P23031400235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 621 | 2023-03-14 | 3105 | keep | 0 | Mar | 2023 | 0.0021148 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-14 23:28 | 2023-03-15 09:46 | 20 | 10:18 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 25A EN SU - 2A NO CAUSA | R23031400172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 618 | 2023-03-14 | 12360 | keep | 0 | Mar | 2023 | 0.0084183 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-03-14 23:29 | 2023-03-14 23:30 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031400703 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-14 | 1702 | keep | 0 | Mar | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
FAJARDO | 2023-03-14 23:36 | 2023-03-15 08:57 | 75 | 9:21 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO CAUSA | R23031400176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 561 | 2023-03-14 | 42075 | keep | 0 | Mar | 2023 | 0.028657 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-03-14 23:53 | 2023-03-14 23:55 | 320 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23031400509 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-14 | 640 | keep | 0 | Mar | 2023 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
CANOVANAS | 2023-03-15 00:12 | 2023-03-15 09:00 | 50 | 8:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REMPLAZO AISLADOR | R23031500002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 528 | 2023-03-15 | 26400 | keep | 0 | Mar | 2023 | 0.017981 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-15 00:34 | 2023-03-15 00:35 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23031500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 325 | keep | 0 | Mar | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
MAYAGÃœEZ | 2023-03-15 00:40 | 2023-03-15 11:30 | 25 | 10:50 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | M23031500001 | New_Event | Animals | Include | Include | Wildlife | 650 | 2023-03-15 | 16250 | keep | 0 | Mar | 2023 | 0.011068 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-03-15 01:23 | 2023-03-15 01:24 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE IDENTIFICA CAUSA | M23031500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 2067 | keep | 0 | Mar | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
ARECIBO | 2023-03-15 01:57 | 2023-03-15 03:21 | 2407 | 1:24 | T | CAUSAS EXTERNAS | SE RETIRO TENSOR CRUZANDO EL ALIMENTADOR Y AISLACION SE CERRO INTERRUPTOR | A23031500001 | New_Event | Damage From Public | Include | Include | Public | 84 | 2023-03-15 | 202188 | keep | 0 | Mar | 2023 | 0.13771 | 0.0016394 | Sustained | FALSE | FALSE | Not_TMED_Event | 2407
SAN JUAN | 2023-03-15 03:30 | 2023-03-15 16:19 | 34 | 12:49 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S23031500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 769 | 2023-03-15 | 26146 | keep | 0 | Mar | 2023 | 0.017808 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BARRANQUITAS | 2023-03-15 04:18 | 2023-03-15 10:05 | 10 | 5:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C23031500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2023-03-15 | 3470 | keep | 0 | Mar | 2023 | 0.0023634 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-15 04:38 | 2023-03-15 04:39 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23031500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 2402 | keep | 0 | Mar | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
CAGUAS | 2023-03-15 04:54 | 2023-03-15 07:41 | 60 | 2:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C23031500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2023-03-15 | 10020 | keep | 0 | Mar | 2023 | 0.0068246 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-03-15 04:57 | 2023-03-15 04:58 | 2179 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO X CONTROL | R23031500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 2179 | keep | 0 | Mar | 2023 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
VEGA BAJA | 2023-03-15 05:08 | 2023-03-15 07:38 | 40 | 2:30 | P | NO SE REPORTO CAUSA | 1 X 40 C/L | B23031500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2023-03-15 | 6000 | keep | 0 | Mar | 2023 | 0.0040866 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-03-15 05:37 | 2023-03-15 15:32 | 108 | 9:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C23031500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 595 | 2023-03-15 | 64260 | keep | 0 | Mar | 2023 | 0.043767 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
BARRANQUITAS | 2023-03-15 06:34 | 2023-03-15 09:33 | 3 | 2:59 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C23031500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-03-15 | 537 | keep | 0 | Mar | 2023 | 0.00036575 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-03-15 06:50 | 2023-03-15 09:02 | 15 | 2:12 | P | CAUSAS EXTERNAS | SE REMPLAZO TRANSFORMADOR T-53 DE 50KVA X 75KVA IMPACTADO POR VEHICULO MEDIANTE GOY BY-230315-02 | B23031500048 | New_Event | Damage From Public | Include | Include | Public | 132 | 2023-03-15 | 1980 | keep | 0 | Mar | 2023 | 0.0013486 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-03-15 06:56 | 2023-03-15 16:09 | 2 | 9:13 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA AVERIADO | R23031500012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 553 | 2023-03-15 | 1106 | keep | 0 | Mar | 2023 | 0.00075329 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-15 07:23 | 2023-03-15 09:07 | 20 | 1:44 | P | DESGANCHE | 1 X 20 EN RISER DESGANCHE | B23031500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-03-15 | 2080 | keep | 0 | Mar | 2023 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-03-15 07:42 | 2023-03-15 11:00 | 40 | 3:18 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CREO AVERIA | A23031500006 | New_Event | Animals | Include | Include | Wildlife | 198 | 2023-03-15 | 7920 | keep | 0 | Mar | 2023 | 0.0053943 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-03-15 07:50 | 2023-03-15 07:51 | 598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 3405-03 SE CERRO POR CONTROL | C23031500036 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-15 | 598 | keep | 0 | Mar | 2023 | 0.0004073 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2023-03-15 07:50 | 2023-03-15 07:51 | 1001 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO LA CARGA DEL 3403-01 | C23031500036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 1001 | keep | 0 | Mar | 2023 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
YAUCO | 2023-03-15 08:10 | 2023-03-15 11:16 | 20 | 3:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23031500020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 186 | 2023-03-15 | 3720 | keep | 0 | Mar | 2023 | 0.0025337 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-15 08:28 | 2023-03-15 12:19 | 9 | 3:51 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1 X 50 EN CORTES DE LINEA SE ELIMINO PARARRAYO | S23031500031 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 231 | 2023-03-15 | 2079 | keep | 0 | Mar | 2023 | 0.001416 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-03-15 08:28 | 2023-03-15 08:29 | 3315 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M2303150009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 3315 | keep | 0 | Mar | 2023 | 0.0022578 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
SAN JUAN | 2023-03-15 08:36 | 2023-03-15 14:25 | 15 | 5:49 | P | DESGANCHE | 1 X 60 EN C/L DESGANCHE PRIMARIO | S23031500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2023-03-15 | 5235 | keep | 0 | Mar | 2023 | 0.0035655 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-15 08:39 | 2023-03-15 11:30 | 40 | 2:51 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | B23031500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-03-15 | 6840 | keep | 0 | Mar | 2023 | 0.0046587 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-03-15 08:41 | 2023-03-15 09:19 | 1 | 0:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER A TRANSCLOSURE REMPLAZO CAJA QUEMADA | R23031500026 | New_Event | Cutout Failure | Include | Include | Equipment | 38 | 2023-03-15 | 38 | keep | 0 | Mar | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-15 08:57 | 2023-03-15 10:25 | 8 | 1:28 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS CRUZADAS | M23031500015 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 88 | 2023-03-15 | 704 | keep | 0 | Mar | 2023 | 0.00047949 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-15 09:00 | 2023-03-15 09:01 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031500054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 2302 | keep | 0 | Mar | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 09:03 | 4027 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA A CAUSA DE AVES QUE CRUZARON MACHETES DE MEDICION REMOTA DE LA SUBESTACION 9105-00 BKR 0050 VEGA ALTA DAÃ‘ADO | B23031500043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-15 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 09:03 | 2468 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA A CAUSA DE AVES QUE CRUZARON MACHETES DE MEDICION REMOTA DE LA SUBESTACION 9105-00 BKR 0050 VEGA ALTA DAÃ‘ADO | B23031500043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-15 | 2468 | keep | 0 | Mar | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 09:03 | 1494 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA A CAUSA DE AVES QUE CRUZARON MACHETES DE MEDICION REMOTA DE LA SUBESTACION 9105-00 BKR 0050 VEGA ALTA DAÃ‘ADO | B23031500043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-15 | 1494 | keep | 0 | Mar | 2023 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 09:03 | 2368 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 7800 OCASIONO BARRA DE VEGA ALTA QUEDARA SIN VOLTAJE MOMENTANEAMENTE BKR 0050 VEGA ALTA DAÃ‘ADO | B23031500042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-15 | 2368 | keep | 0 | Mar | 2023 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 09:03 | 538 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 7800 OCASIONO BARRA DE VEGA ALTA QUEDARA SIN VOLTAJE MOMENTANEAMENTE BKR 0050 VEGA ALTA DAÃ‘ADO | B23031500042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-15 | 538 | keep | 0 | Mar | 2023 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 09:03 | 1284 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 7800 OCASIONO BARRA DE VEGA ALTA QUEDARA SIN VOLTAJE MOMENTANEAMENTE BKR 0050 VEGA ALTA DAÃ‘ADO | B23031500042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-15 | 1284 | keep | 0 | Mar | 2023 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 10:58 | 1310 | 1:56 | S | ANIMAL | BY-230315-01 SE CONFIRMO AVERIA EN MACHETES DE MED. REMOTA POR CHANGOS. SE AISLARON, SE REMONTO LOCK OUT Y SE NORMALIZO LA CARGA | B23031500024 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-03-15 | 151960 | keep | 0 | Mar | 2023 | 0.1035 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 10:58 | 215 | 1:56 | S | ANIMAL | BY-230315-01 SE CONFIRMO AVERIA EN MACHETES DE MED. REMOTA POR CHANGOS. SE AISLARON, SE REMONTO LOCK OUT Y SE NORMALIZO LA CARGA | B23031500024 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-03-15 | 24940 | keep | 0 | Mar | 2023 | 0.016987 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 10:58 | 1 | 1:56 | S | ANIMAL | BY-230315-01 SE CONFIRMO AVERIA EN MACHETES DE MED. REMOTA POR CHANGOS. SE AISLARON, SE REMONTO LOCK OUT Y SE NORMALIZO LA CARGA | B23031500024 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-03-15 | 116 | keep | 0 | Mar | 2023 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-15 09:02 | 2023-03-15 09:03 | 652 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 7800 | B23031500039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-15 | 652 | keep | 0 | Mar | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2023-03-15 09:02 | 2023-03-15 09:03 | 2704 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 7800 BKR 0050 VEGA ALTA DAÃ‘ADO | B23031500039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-15 | 2704 | keep | 0 | Mar | 2023 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
CANOVANAS | 2023-03-15 09:05 | 2023-03-15 09:07 | 234 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R23031500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-15 | 468 | keep | 0 | Mar | 2023 | 0.00031875 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
CAGUAS | 2023-03-15 09:17 | 2023-03-15 13:10 | 70 | 3:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23031500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2023-03-15 | 16310 | keep | 0 | Mar | 2023 | 0.011109 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-03-15 09:20 | 2023-03-15 10:03 | 1 | 0:43 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN RISER SE CERRO PUENTE DE LINEA A CAJA | R23031500034 | New_Event | Primary Wire Break | Include | Include | Equipment | 43 | 2023-03-15 | 43 | keep | 0 | Mar | 2023 | 2.9287e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-03-15 09:20 | 2023-03-15 11:48 | 12 | 2:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23031500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2023-03-15 | 1776 | keep | 0 | Mar | 2023 | 0.0012096 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-15 09:22 | 2023-03-15 10:00 | 40 | 0:38 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23031500013 | New_Event | Animals | Include | Include | Wildlife | 38 | 2023-03-15 | 1520 | keep | 0 | Mar | 2023 | 0.0010353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-03-15 09:25 | 2023-03-15 11:01 | 1 | 1:36 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | C23031500068 | New_Event | Primary Wire Break | Include | Include | Equipment | 96 | 2023-03-15 | 96 | keep | 0 | Mar | 2023 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-15 09:28 | 2023-03-15 11:37 | 1 | 2:09 | P | NO SE REPORTO CAUSA | 3 X 25 EN SU HACIA TRANSCLOSURE | C23031500070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2023-03-15 | 129 | keep | 0 | Mar | 2023 | 8.7861e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-15 09:30 | 2023-03-15 09:31 | 2675 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23031500038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 2675 | keep | 0 | Mar | 2023 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2023-03-15 09:32 | 2023-03-15 13:08 | 120 | 3:36 | P | DESGANCHE | 1 X 80 EN C/L | R23031500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2023-03-15 | 25920 | keep | 0 | Mar | 2023 | 0.017654 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BARRANQUITAS | 2023-03-15 10:02 | 2023-03-15 10:44 | 36 | 0:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REEMPLAZO DE AISLADORES EN POSTES | C23031500059 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 42 | 2023-03-15 | 1512 | keep | 0 | Mar | 2023 | 0.0010298 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CANOVANAS | 2023-03-15 10:03 | 2023-03-15 10:50 | 2179 | 0:47 | T | ANIMAL | DISPARO INTERRUPTOR SE SECCIONALIZO EL ALIMENTADOR SJ-230315-50 | R23031500044 | New_Event | Animals | Include | Include | Wildlife | 47 | 2023-03-15 | 102413 | keep | 0 | Mar | 2023 | 0.069753 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
FAJARDO | 2023-03-15 10:35 | 2023-03-15 12:47 | 100 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | R23031500067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2023-03-15 | 13200 | keep | 0 | Mar | 2023 | 0.0089905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-03-15 10:37 | 2023-03-15 14:56 | 100 | 4:19 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA POR AVE | M23031500060 | New_Event | Animals | Include | Include | Wildlife | 259 | 2023-03-15 | 25900 | keep | 0 | Mar | 2023 | 0.01764 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-15 10:39 | 2023-03-15 12:15 | 6 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BAJANTES SECUNDARIOS | R23031500031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2023-03-15 | 576 | keep | 0 | Mar | 2023 | 0.00039231 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-15 10:40 | 2023-03-15 23:30 | 48 | 12:50 | P | DESGANCHE | 2X40 EN C/L DESGANCHE | S23031501085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 770 | 2023-03-15 | 36960 | keep | 0 | Mar | 2023 | 0.025173 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
AGUADILLA | 2023-03-15 10:45 | 2023-03-15 13:15 | 7 | 2:30 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23031500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-03-15 | 1050 | keep | 0 | Mar | 2023 | 0.00071515 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-03-15 10:50 | 2023-03-15 12:02 | 327 | 1:12 | P | ANIMAL | SE RETIRO PALOMA Y REMPLAZO PIN POLE TOP SJ-230315-50 | R23031500044 | Partial_restoration | Animals | Include | Include | Wildlife | 72 | 2023-03-15 | 23544 | keep | 0 | Mar | 2023 | 0.016036 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-03-15 10:50 | 2023-03-15 11:07 | 2 | 0:17 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23031500046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2023-03-15 | 34 | keep | 0 | Mar | 2023 | 2.3157e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-03-15 10:57 | 2023-03-15 14:59 | 50 | 4:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C23031500100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2023-03-15 | 12100 | keep | 0 | Mar | 2023 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-15 10:58 | 2023-03-16 14:15 | 15 | 27:17 | P | CAUSAS EXTERNAS | SE REMPLAZO TRANSFORMADOR T-53 DE 50KVA X 75KVA IMPACTADO POR VEHICULO MEDIANTE GOI BY-230315-02 | B23031500048 | New_Event | Damage From Public | Include | Include | Public | 1637 | 2023-03-15 | 24555 | keep | 0 | Mar | 2023 | 0.016724 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-15 11:14 | 2023-03-15 12:14 | 353 | 1:00 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR GLOBO CRUZO LINEAS SE RETIRO GLOBO Y SE CERRO POR SCADA | S23031500127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-03-15 | 21180 | keep | 0 | Mar | 2023 | 0.014426 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
SAN JUAN | 2023-03-15 11:17 | 2023-03-15 16:38 | 244 | 5:21 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN RISER DE SALIDA | S23031500125 | New_Event | Primary Wire Break | Include | Include | Equipment | 321 | 2023-03-15 | 78324 | keep | 0 | Mar | 2023 | 0.053346 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
BARRANQUITAS | 2023-03-15 11:17 | 2023-03-15 13:42 | 15 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO TOMA SECUNDARIA DETERIORADO | C23031500110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-03-15 | 2175 | keep | 0 | Mar | 2023 | 0.0014814 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-15 11:32 | 2023-03-15 13:02 | 2402 | 1:30 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA Y ENTRO 80% EN SERVICIO MEDIANTE GOI BY-230315-03 | B23031500061 | New_Event | Primary Wire Break | Include | Include | Equipment | 90 | 2023-03-15 | 216180 | keep | 0 | Mar | 2023 | 0.14724 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
MAYAGÃœEZ | 2023-03-15 11:32 | 2023-03-15 13:44 | 80 | 2:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031500082 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 132 | 2023-03-15 | 10560 | keep | 0 | Mar | 2023 | 0.0071924 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-03-15 11:34 | 2023-03-15 11:36 | 5931 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 5% DE SU CARGA POR EL 1336-08 SE CERRO POR SCADA | S23031500136 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-15 | 11862 | keep | 0 | Mar | 2023 | 0.0080792 | 0.0040396 | Momentary | FALSE | FALSE | Not_TMED_Event | 5931
YAUCO | 2023-03-15 12:00 | 2023-03-15 12:30 | 10 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23031500056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-03-15 | 300 | keep | 0 | Mar | 2023 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-03-15 12:10 | 2023-03-15 12:11 | 1843 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 1843 | keep | 0 | Mar | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BAYAMON | 2023-03-15 12:26 | 2023-03-15 12:27 | 1984 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPCION SE CERRO POR SCADA | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 1984 | keep | 0 | Mar | 2023 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
VEGA BAJA | 2023-03-15 12:26 | 2023-03-15 12:27 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
BARRANQUITAS | 2023-03-15 12:30 | 2023-03-15 12:40 | 37 | 0:10 | P | OTRAS CAUSAS | SE ABRIO CORTE DE LINEA PARA VERIFICAR COORDINACION DE FUSIBLES EN EL ALIMENTADOR | C23031500118 | New_Event | Other Causes | Include | Include | Other | 10 | 2023-03-15 | 370 | keep | 0 | Mar | 2023 | 0.00025201 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-03-15 12:33 | 2023-03-15 14:53 | 5 | 2:20 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23031500216 | New_Event | Primary Wire Break | Include | Include | Equipment | 140 | 2023-03-15 | 700 | keep | 0 | Mar | 2023 | 0.00047677 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-15 12:34 | 2023-03-15 12:35 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1909-09 | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 222 | keep | 0 | Mar | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-03-15 12:34 | 2023-03-15 12:35 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 1907-07 CARGA X 1907-07 | S2303150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-15 | 4456 | keep | 0 | Mar | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
AGUADILLA | 2023-03-15 12:34 | 2023-03-15 15:06 | 80 | 2:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23031500096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2023-03-15 | 12160 | keep | 0 | Mar | 2023 | 0.0082821 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-03-15 12:48 | 2023-03-15 15:47 | 60 | 2:59 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C23031500133 | New_Event | Animals | Include | Include | Wildlife | 179 | 2023-03-15 | 10740 | keep | 0 | Mar | 2023 | 0.007315 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-15 12:49 | 2023-03-15 15:55 | 71 | 3:06 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L SE REMPLAZO PARARRAYO | B23031500074 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 186 | 2023-03-15 | 13206 | keep | 0 | Mar | 2023 | 0.0089945 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
SAN JUAN | 2023-03-15 12:50 | 2023-03-15 12:54 | 143 | 0:04 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 80% DEL 1404-07 | S23031500244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-15 | 572 | keep | 0 | Mar | 2023 | 0.00038959 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-03-15 12:50 | 2023-03-15 12:54 | 1085 | 0:04 | P | ALIMENTADOR AMARRADO | SE CERRO POR SCADA 80% DE SU CARGA POR EL 1404-07 | S23031500244 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-03-15 | 4340 | keep | 0 | Mar | 2023 | 0.002956 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2023-03-15 12:50 | 2023-03-15 12:51 | 1368 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 1368 | keep | 0 | Mar | 2023 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
BAYAMON | 2023-03-15 12:55 | 2023-03-15 12:56 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23031500077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 3438 | keep | 0 | Mar | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
VEGA BAJA | 2023-03-15 12:56 | 2023-03-15 15:23 | 15 | 2:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L SE RETIRO RAMA | B23031500076 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2023-03-15 | 2205 | keep | 0 | Mar | 2023 | 0.0015018 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-15 12:57 | 2023-03-15 15:53 | 212 | 2:56 | P | DESGANCHE | SE REEMPLAZO 1X65 EN C/L | S23031500257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-03-15 | 37312 | keep | 0 | Mar | 2023 | 0.025413 | 0.00014439 | Sustained | FALSE | FALSE | Not_TMED_Event | 212
BAYAMON | 2023-03-15 12:57 | 2023-03-15 12:58 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23031500077 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 3438 | keep | 0 | Mar | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
SAN JUAN | 2023-03-15 12:58 | 2023-03-15 13:00 | 4398 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23031500263 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-15 | 8796 | keep | 0 | Mar | 2023 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
BAYAMON | 2023-03-15 13:00 | 2023-03-15 13:16 | 216 | 0:16 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 70% DE 1924-04 LLEVA 1924-05 | S23031500281 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-03-15 | 3456 | keep | 0 | Mar | 2023 | 0.0023539 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2023-03-15 13:00 | 2023-03-15 13:16 | 31 | 0:16 | P | ALIMENTADOR AMARRADO | DISPARO 1903-03 LLEVA 70% 1924-04 | S23031500281 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-03-15 | 496 | keep | 0 | Mar | 2023 | 0.00033782 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-03-15 13:00 | 2023-03-15 13:16 | 686 | 0:16 | T | ALIMENTADOR AMARRADO | DISPARO 1903-03 Y LLEVA 1924-05 | S23031500281 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-03-15 | 10976 | keep | 0 | Mar | 2023 | 0.0074757 | 0.00046723 | Sustained | FALSE | FALSE | Not_TMED_Event | 686
BAYAMON | 2023-03-15 13:02 | 2023-03-15 21:30 | 480 | 8:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO PARTIDO EN EL SUELO MEDIANTE GOI BY-230315-03 EN SERVICIO EL 20% QUE FALTABA | B23031500061 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 508 | 2023-03-15 | 243840 | keep | 0 | Mar | 2023 | 0.16608 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-15 13:02 | 2023-03-15 13:40 | 2090 | 0:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR 2090 CLIENTES POR EL 2403-02 SE ABRIO MACHETES PARA SECCIONALIZAR AISLADOR ROTO SJ-230315-51 | R23031500118 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 38 | 2023-03-15 | 79420 | keep | 0 | Mar | 2023 | 0.054093 | 0.0014235 | Sustained | FALSE | FALSE | Not_TMED_Event | 2090
CANOVANAS | 2023-03-15 13:02 | 2023-03-15 13:40 | 500 | 0:38 | T | ALIMENTADOR AMARRADO | DISPARRO INTERRUPTOR LLEVA LA CARGA DEL 2403-01 SE SECCIONALIZO AISLADOR ROTO EN EL 2403-01 SJ-230315-51 | R23031500110 | New_Event | Feeder Load Transferred | Include | Include | Other | 38 | 2023-03-15 | 19000 | keep | 0 | Mar | 2023 | 0.012941 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2023-03-15 13:05 | 2023-03-15 13:11 | 577 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-03-15 | 3462 | keep | 0 | Mar | 2023 | 0.002358 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
SAN JUAN | 2023-03-15 13:08 | 2023-03-15 13:09 | 362 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 90% DE LA CARGA X EL 1620-01 | S2303150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-15 | 362 | keep | 0 | Mar | 2023 | 0.00024656 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-03-15 13:08 | 2023-03-15 13:09 | 36 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 90% DEL 1336-10 | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 36 | keep | 0 | Mar | 2023 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2023-03-15 13:10 | 2023-03-15 23:16 | 100 | 10:06 | P | CONDUCTOR ROTO O ABIERTO | 2X65 EN C/L SE LEVANTO TRAMO PRIMARIO (RADIAL) DEL SUELO | B23031500080 | New_Event | Primary Wire Break | Include | Include | Equipment | 606 | 2023-03-15 | 60600 | keep | 0 | Mar | 2023 | 0.041274 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-03-15 13:11 | 2023-03-15 13:12 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 57 | keep | 0 | Mar | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-03-15 13:14 | 2023-03-15 17:06 | 30 | 3:52 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23031500081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-03-15 | 6960 | keep | 0 | Mar | 2023 | 0.0047404 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-15 13:15 | 2023-03-15 20:15 | 5 | 7:00 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO CABLE SOTERRADO AVERIADO SE CERRO N/O TODO EN SERVICIO | B23031500082 | New_Event | UG Cable Fault | Include | Include | Equipment | 420 | 2023-03-15 | 2100 | keep | 0 | Mar | 2023 | 0.0014303 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-15 13:16 | 2023-03-15 13:19 | 3709 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23031500308 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-15 | 11127 | keep | 0 | Mar | 2023 | 0.0075785 | 0.0025262 | Momentary | FALSE | FALSE | Not_TMED_Event | 3709
SAN JUAN | 2023-03-15 13:16 | 2023-03-15 13:17 | 1381 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1204-03 | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 1381 | keep | 0 | Mar | 2023 | 0.00094059 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
BAYAMON | 2023-03-15 13:17 | 2023-03-15 14:52 | 6136 | 1:35 | T | PARARRAYOS DEFECTUOSO | SE ELEMINARON PARRARAYOS HACIA LA ESCUELA ERMINIA RIVERA MEDIANTE SW-230315-04 | B23031500084 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 95 | 2023-03-15 | 582920 | keep | 0 | Mar | 2023 | 0.39702 | 0.0041792 | Sustained | FALSE | FALSE | Not_TMED_Event | 6136
SAN JUAN | 2023-03-15 13:21 | 2023-03-15 13:23 | 362 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 90% DE LA CARGA X EL 1620-01 | S2303150000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-15 | 724 | keep | 0 | Mar | 2023 | 0.00049311 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-03-15 13:21 | 2023-03-15 13:23 | 36 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 90% DEL 1336-10 | S2303150000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-15 | 72 | keep | 0 | Mar | 2023 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-03-15 13:25 | 2023-03-15 13:27 | 169 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23031500323 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-15 | 338 | keep | 0 | Mar | 2023 | 0.00023021 | 0.00011511 | Momentary | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2023-03-15 13:26 | 2023-03-15 13:27 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIEERE | S2303150000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 57 | keep | 0 | Mar | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
CANOVANAS | 2023-03-15 13:27 | 2023-03-15 17:34 | 9 | 4:07 | P | DESGANCHE | 1 X 10 EN AEREO PROVISIONAL HACIA T-44 SE RETIRO ENREDADERA DEL PM | R23031500114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2023-03-15 | 2223 | keep | 0 | Mar | 2023 | 0.0015141 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-03-15 13:33 | 2023-03-15 13:37 | 7658 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 85% DE SU CARGA POR EL 1206-03 SE CERRO POR SCADA | S2303150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-03-15 | 30632 | keep | 0 | Mar | 2023 | 0.020863 | 0.0052158 | Momentary | FALSE | FALSE | Not_TMED_Event | 7658
SAN JUAN | 2023-03-15 13:33 | 2023-03-15 13:37 | 4133 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 85% DEL 1204-05 SE CERRO POR SCADA | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-15 | 16532 | keep | 0 | Mar | 2023 | 0.01126 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2023-03-15 13:38 | 2023-03-15 15:08 | 105 | 1:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L Y 1 X 140 EN C/L | B23031500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2023-03-15 | 9450 | keep | 0 | Mar | 2023 | 0.0064364 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
CAGUAS | 2023-03-15 13:39 | 2023-03-15 13:41 | 1879 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 3006-05 | C23031500155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-15 | 3758 | keep | 0 | Mar | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-03-15 13:39 | 2023-03-15 13:41 | 3005 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL DEL 3006-05 | C23031500155 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-15 | 6010 | keep | 0 | Mar | 2023 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CANOVANAS | 2023-03-15 13:40 | 2023-03-15 14:31 | 718 | 0:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR ROTO Y SE CERRO MACHETES SJ-230315-51 | R23031500118 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 51 | 2023-03-15 | 36618 | keep | 0 | Mar | 2023 | 0.02494 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-15 13:46 | 2023-03-15 15:26 | 60 | 1:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | A23031500070 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 100 | 2023-03-15 | 6000 | keep | 0 | Mar | 2023 | 0.0040866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-15 13:52 | 2023-03-15 13:56 | 7658 | 0:04 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVA 85% DEL 1204-05 SE CERRO POR SCADA | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-15 | 30632 | keep | 0 | Mar | 2023 | 0.020863 | 0.0052158 | Momentary | FALSE | FALSE | Not_TMED_Event | 7658
SAN JUAN | 2023-03-15 13:52 | 2023-03-15 13:56 | 4133 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVA 85% DEL 1204-05 SE CERRO POR SCADA | S2303150000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-15 | 16532 | keep | 0 | Mar | 2023 | 0.01126 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2023-03-15 13:55 | 2023-03-15 14:43 | 71 | 0:48 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23031500106 | New_Event | Animals | Include | Include | Wildlife | 48 | 2023-03-15 | 3408 | keep | 0 | Mar | 2023 | 0.0023212 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
ARECIBO | 2023-03-15 14:00 | 2023-03-15 14:59 | 2228 | 0:59 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 8007-05 QUE ES SPARE ESTA LLEVANDO LA CARGA DEL 8007-03 SE CERRO EN LA SUBESTACION Y QUEDO EN SERVICIO ESTE NO CIERRA POR SCADA | A23031500075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2023-03-15 | 131452 | keep | 0 | Mar | 2023 | 0.089531 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2023-03-15 14:00 | 2023-03-15 14:59 | 438 | 0:59 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 8007-05 QUE ES SPARE ESTA LLEVANDO LA CARGA DEL 8007-04 SE CERRO EN LA SUBESTACION Y QUEDO EN SERVICIO ESTE NO CIERRA POR SCADA | A23031500075 | New_Event | Feeder Load Transferred | Include | Include | Other | 59 | 2023-03-15 | 25842 | keep | 0 | Mar | 2023 | 0.017601 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
CANOVANAS | 2023-03-15 14:06 | 2023-03-15 16:07 | 51 | 2:01 | P | DESGANCHE | 1 RVA DE 50 EN SU-2 SE RETIRO ENREDADERA | R23031500120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-03-15 | 6171 | keep | 0 | Mar | 2023 | 0.004203 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
CANOVANAS | 2023-03-15 14:08 | 2023-03-15 16:28 | 25 | 2:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23031500121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-03-15 | 3500 | keep | 0 | Mar | 2023 | 0.0023838 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-03-15 14:16 | 2023-03-15 14:17 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 2234 | keep | 0 | Mar | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
CAGUAS | 2023-03-15 14:17 | 2023-03-15 17:41 | 60 | 3:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C23031500169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-03-15 | 12240 | keep | 0 | Mar | 2023 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-15 14:28 | 2023-03-15 18:55 | 2644 | 4:27 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PB Y SE REPUSO 1 X 65 EN RISER Y SE CERRO PUENTE DE LINEA A CAJA | S23031500437 | New_Event | Primary Wire Break | Include | Include | Equipment | 267 | 2023-03-15 | 705948 | keep | 0 | Mar | 2023 | 0.48082 | 0.0018008 | Sustained | FALSE | FALSE | Not_TMED_Event | 2644
MAYAGÃœEZ | 2023-03-15 14:32 | 2023-03-15 16:44 | 12 | 2:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR BAMBUA | M23031500120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-03-15 | 1584 | keep | 0 | Mar | 2023 | 0.0010789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-03-15 14:36 | 2023-03-15 17:36 | 80 | 3:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | R23031500131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-03-15 | 14400 | keep | 0 | Mar | 2023 | 0.0098078 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2023-03-15 14:36 | 2023-03-15 16:20 | 8 | 1:44 | P | SECUNDARIA/DESGANCHE | SE ABREN CAJAS EN TRANSFORMADOR PARA REALIZAR DESGANCHE Y SE REPARA LINEA SECUNDARIA | P23031500083 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 104 | 2023-03-15 | 832 | keep | 0 | Mar | 2023 | 0.00056667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-15 14:37 | 2023-03-15 14:39 | 331 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R23031500132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-15 | 662 | keep | 0 | Mar | 2023 | 0.00045089 | 0.00022544 | Momentary | FALSE | FALSE | Not_TMED_Event | 331
AGUADILLA | 2023-03-15 14:42 | 2023-03-15 15:05 | 7 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REMPLAZO DE CONECTORES | M23031500123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-03-15 | 161 | keep | 0 | Mar | 2023 | 0.00010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-15 14:48 | 2023-03-15 17:04 | 7 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR BARRAS EN PEDESTAL | S23031500460 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2023-03-15 | 952 | keep | 0 | Mar | 2023 | 0.0006484 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-15 14:52 | 2023-03-15 15:08 | 3068 | 0:16 | P | PARARRAYOS DEFECTUOSO | SE ELEMINARON PARRARAYOS HACIA LA ESCUELA ERMINIA RIVERAY SE CERRO PB INTELIRRUPTER MEDIANTE SW-230315-04 | B23031500084 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 16 | 2023-03-15 | 49088 | keep | 0 | Mar | 2023 | 0.033434 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-03-15 14:54 | 2023-03-15 16:58 | 1830 | 2:04 | T | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO MACHETES PARA SECCIONALIZAR CRUCETA DESPRENDIDA POR PERNOS PODRIDOS CON CONDUCTOR PRIMARIO EN EL SUELO 40% EN SERVICIO SJ-230315-52 | R23031500137 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 124 | 2023-03-15 | 226920 | keep | 0 | Mar | 2023 | 0.15455 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-03-15 14:54 | 2023-03-15 15:28 | 1197 | 0:34 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR SE ABRIO AMARRE DEL 2201-04 CON 2201-02 SJ-230315-52 SE CONTINUA PATRULLANDO 2201-02 | R23031500137 | New_Event | Feeder Load Transferred | Include | Include | Other | 34 | 2023-03-15 | 40698 | keep | 0 | Mar | 2023 | 0.027719 | 0.00081527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1197
BAYAMON | 2023-03-15 15:34 | 2023-03-15 16:46 | 50 | 1:12 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B23031500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-03-15 | 3600 | keep | 0 | Mar | 2023 | 0.0024519 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-15 16:00 | 2023-03-15 17:24 | 30 | 1:24 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23031500135 | New_Event | Animals | Include | Include | Wildlife | 84 | 2023-03-15 | 2520 | keep | 0 | Mar | 2023 | 0.0017164 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-03-15 16:02 | 2023-03-15 17:27 | 360 | 1:25 | P | DESGANCHE | 2 X 80 EN C/L Y DESGANCHE | S23031500552 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-03-15 | 30600 | keep | 0 | Mar | 2023 | 0.020842 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
UTUADO | 2023-03-15 16:05 | 2023-03-15 16:50 | 9 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23031500103 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-03-15 | 405 | keep | 0 | Mar | 2023 | 0.00027584 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-03-15 16:16 | 2023-03-15 17:11 | 382 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE SECCIONALIZA LINEA 5600 Y SE COLOCA EN SERVICIO TRAMO AÃ‘ASCO TC HASTA PUNTA DEL MAR OHGW SOBRE LA LINEA | M23031500157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2023-03-15 | 21010 | keep | 0 | Mar | 2023 | 0.01431 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-03-15 16:16 | 2023-03-15 17:11 | 39 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE SECCIONALIZA LINEA 5600 Y SE COLOCA EN SERVICIO TRAMO AÃ‘ASCO TC HASTA PUNTA DEL MAR OHGW SOBRE LA LINEA | M23031500157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2023-03-15 | 2145 | keep | 0 | Mar | 2023 | 0.0014609 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2023-03-15 16:16 | 2023-03-15 17:11 | 2366 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE SECCIONALIZA LINEA 5600 Y SE COLOCA EN SERVICIO TRAMO AÃ‘ASCO TC HASTA PUNTA DEL MAR OHGW SOBRE LA LINEA | M23031500158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2023-03-15 | 130130 | keep | 0 | Mar | 2023 | 0.088631 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2023-03-15 16:16 | 2023-03-15 17:11 | 1337 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE SECCIONALIZA LINEA 5600 Y SE COLOCA EN SERVICIO TRAMO AÃ‘ASCO TC HASTA PUNTA DEL MAR OHGW SOBRE LA LINEA | M23031500158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2023-03-15 | 73535 | keep | 0 | Mar | 2023 | 0.050084 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-03-15 16:16 | 2023-03-15 17:11 | 709 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE SECCIONALIZA LINEA 5600 Y SE COLOCA EN SERVICIO TRAMO AÃ‘ASCO TC HASTA PUNTA DEL MAR OHGW SOBRE LA LINEA | M23031500158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2023-03-15 | 38995 | keep | 0 | Mar | 2023 | 0.026559 | 0.0004829 | Sustained | FALSE | FALSE | Not_TMED_Event | 709
AGUADILLA | 2023-03-15 16:16 | 2023-03-16 09:45 | 20 | 17:29 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23031500102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1049 | 2023-03-15 | 20980 | keep | 0 | Mar | 2023 | 0.014289 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-03-15 16:18 | 2023-03-15 17:17 | 126 | 0:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTO | R23031500177 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 59 | 2023-03-15 | 7434 | keep | 0 | Mar | 2023 | 0.0050633 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
ARECIBO | 2023-03-15 16:35 | 2023-03-15 18:50 | 90 | 2:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A23031500105 | New_Event | Primary Wire Break | Include | Include | Equipment | 135 | 2023-03-15 | 12150 | keep | 0 | Mar | 2023 | 0.0082753 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2023-03-15 16:36 | 2023-03-15 16:37 | 889 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C2303150000X | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-03-15 | 889 | keep | 0 | Mar | 2023 | 0.00060549 | 0.00060549 | Momentary | FALSE | FALSE | Not_TMED_Event | 889
BARRANQUITAS | 2023-03-15 16:37 | 2023-03-15 19:13 | 7 | 2:36 | P | PARARRAYOS DEFECTUOSO | PARARRAYO AVERIADO EN EL SU1 SE CERRO N/O SU3 Y SE ABRIO EN SU1 | C23031500226 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 156 | 2023-03-15 | 1092 | keep | 0 | Mar | 2023 | 0.00074376 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-03-15 16:38 | 2023-03-15 19:44 | 205 | 3:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23031500185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-03-15 | 38130 | keep | 0 | Mar | 2023 | 0.02597 | 0.00013962 | Sustained | FALSE | FALSE | Not_TMED_Event | 205
SAN JUAN | 2023-03-15 16:39 | 2023-03-15 18:08 | 333 | 1:29 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO MANUAL EN EL CAMPO 35 % DE SU CARGA 1330-04 | S23031500581 | New_Event | Feeder Load Transferred | Include | Include | Other | 89 | 2023-03-15 | 29637 | keep | 0 | Mar | 2023 | 0.020186 | 0.0002268 | Sustained | FALSE | FALSE | Not_TMED_Event | 333
AGUADILLA | 2023-03-15 16:47 | 2023-03-15 19:15 | 7 | 2:28 | P | FUEGO | 1 X 50 EN CORTE DE LINEA FUEGO FORESTAL | M23031500186 | New_Event | Fire | Include | Include | Public | 148 | 2023-03-15 | 1036 | keep | 0 | Mar | 2023 | 0.00070561 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-03-15 16:48 | 2023-03-15 17:56 | 30 | 1:08 | P | CONDUCTOR ROTO O ABIERTO | 2 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23031500076 | New_Event | Primary Wire Break | Include | Include | Equipment | 68 | 2023-03-15 | 2040 | keep | 0 | Mar | 2023 | 0.0013894 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-03-15 16:51 | 2023-03-15 17:04 | 8 | 0:13 | P | DESGANCHE | 1 X 35 EN C/L DESGANCHE | B23031500143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 13 | 2023-03-15 | 104 | keep | 0 | Mar | 2023 | 7.0834e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-03-15 16:58 | 2023-03-15 21:00 | 1098 | 4:02 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REEMPLAZO CRUCETA Y SE LEVANTO CONDUCTOR PRIMARIO, SE CERRO MACHETES 100% EN SERVICIO SJ-230315-52 | R23031500137 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 242 | 2023-03-15 | 265716 | keep | 0 | Mar | 2023 | 0.18098 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-15 17:11 | 2023-03-15 19:11 | 70 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINE POR VIENTOS | M23031500234 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2023-03-15 | 8400 | keep | 0 | Mar | 2023 | 0.0057212 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-03-15 17:12 | 2023-03-15 18:25 | 35 | 1:13 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | R23031500195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-03-15 | 2555 | keep | 0 | Mar | 2023 | 0.0017402 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-03-15 17:13 | 2023-03-15 17:14 | 271 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 271 | keep | 0 | Mar | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2023-03-15 17:13 | 2023-03-15 17:14 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23031500197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 4085 | keep | 0 | Mar | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-03-15 17:16 | 2023-03-15 18:36 | 643 | 1:20 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES Y SE ENCONTRO AVERIA SOTERRADA DE BKR A RISER DE SALIDA SE TRANFIRIO CARGA AL 1530-09 | S23031500611 | New_Event | UG Cable Fault | Include | Include | Equipment | 80 | 2023-03-15 | 51440 | keep | 0 | Mar | 2023 | 0.035036 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
CANOVANAS | 2023-03-15 17:17 | 2023-03-15 17:52 | 40 | 0:35 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE ELIMINO PARARRAYO | R23031500198 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 35 | 2023-03-15 | 1400 | keep | 0 | Mar | 2023 | 0.00095353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2023-03-15 17:22 | 2023-03-15 19:20 | 25 | 1:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23031500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-03-15 | 2950 | keep | 0 | Mar | 2023 | 0.0020092 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-03-15 18:08 | 2023-03-15 18:09 | 3257 | 0:01 | P | DESGANCHE | RECERRO INTERRUPTOR TIENE 931 CLIENTES POR EL 2302-03 SJ-221005-50 | R23031500208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-15 | 3257 | keep | 0 | Mar | 2023 | 0.0022183 | 0.0022183 | Momentary | FALSE | FALSE | Not_TMED_Event | 3257
SAN JUAN | 2023-03-15 18:09 | 2023-03-16 02:49 | 90 | 8:40 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | S23031500643 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 520 | 2023-03-15 | 46800 | keep | 0 | Mar | 2023 | 0.031875 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2023-03-15 18:09 | 2023-03-15 19:33 | 99 | 1:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ENREDADERA | R23031500212 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-03-15 | 8316 | keep | 0 | Mar | 2023 | 0.005664 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
BAYAMON | 2023-03-15 18:11 | 2023-03-16 12:56 | 20 | 18:45 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | B23031500152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1125 | 2023-03-15 | 22500 | keep | 0 | Mar | 2023 | 0.015325 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-15 18:11 | 2023-03-15 18:29 | 293 | 0:18 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR A PETICION DE GIONANNIE RIVERA POR CONDUCTOR EN EL SUELO SE TRABAJO MEDIANTE GOI BY-230315-06 | S23031500292 | New_Event | Primary Wire Break | Include | Include | Equipment | 18 | 2023-03-15 | 5274 | keep | 0 | Mar | 2023 | 0.0035921 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
ARECIBO | 2023-03-15 18:11 | 2023-03-15 19:05 | 15 | 0:54 | P | ANIMAL | 1 X 20 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23031500113 | New_Event | Animals | Include | Include | Wildlife | 54 | 2023-03-15 | 810 | keep | 0 | Mar | 2023 | 0.00055169 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-15 18:36 | 2023-03-16 04:50 | 20 | 10:14 | P | NO SE REPORTO CAUSA | 2X65 DE RISER @ SUBESTACION PRIVADA | S23031500674 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 614 | 2023-03-15 | 12280 | keep | 0 | Mar | 2023 | 0.0083639 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-15 18:43 | 2023-03-16 16:13 | 25 | 21:30 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23031500704 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1290 | 2023-03-15 | 32250 | keep | 0 | Mar | 2023 | 0.021965 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2023-03-15 18:57 | 2023-03-15 21:40 | 60 | 2:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23031500114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-03-15 | 9780 | keep | 0 | Mar | 2023 | 0.0066611 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-03-15 19:04 | 2023-03-15 20:47 | 18 | 1:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 SMU 20 DE 25 AMP. EN SU-3 SE REEMPLAZO BASE DE PORTAFUSIBLE | R23031500224 | New_Event | Cutout Failure | Include | Include | Equipment | 103 | 2023-03-15 | 1854 | keep | 0 | Mar | 2023 | 0.0012628 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-03-15 19:05 | 2023-03-15 20:00 | 271 | 0:55 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PB EN EL CAMPO | S23031500826 | New_Event | Primary Wire Break | Include | Include | Equipment | 55 | 2023-03-15 | 14905 | keep | 0 | Mar | 2023 | 0.010152 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
AGUADILLA | 2023-03-15 19:15 | 2023-03-16 19:03 | 17 | 23:48 | P | FUEGO | 1 X 40 EN CORTE DE LINEA FUEGO FORESTAL SE REPARO LINEA PRIMARIA ROTA. DENTRO DE FINCA SE LEVANTO 3000 PIES DE ALAMBRE PRIMARIO SE REPUSO NEUTRAL , SE REPARO EN VARIOS PUNTOS Y SE DESGANCHO | M23031500186 | Additional_clients | Fire | Include | Include | Public | 1428 | 2023-03-15 | 24276 | keep | 0 | Mar | 2023 | 0.016534 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-15 19:20 | 2023-03-15 19:21 | 1984 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2303150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 1984 | keep | 0 | Mar | 2023 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
SAN JUAN | 2023-03-15 20:00 | 2023-03-16 02:01 | 60 | 6:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO MEDIANTE GOI SJ-230316-01 | S23031500937 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 361 | 2023-03-15 | 21660 | keep | 0 | Mar | 2023 | 0.014753 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-03-15 20:11 | 2023-03-16 07:05 | 24 | 10:54 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA LINEA PARTIDA | P23031500127 | New_Event | Primary Wire Break | Include | Include | Equipment | 654 | 2023-03-15 | 15696 | keep | 0 | Mar | 2023 | 0.01069 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
AGUADILLA | 2023-03-15 20:31 | 2023-03-15 21:10 | 861 | 0:39 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA EN TRONCAL PARTIDA SE ABRE INTERRUPTOR | M23031500254 | New_Event | Primary Wire Break | Include | Include | Equipment | 39 | 2023-03-15 | 33579 | keep | 0 | Mar | 2023 | 0.022871 | 0.00058642 | Sustained | FALSE | FALSE | Not_TMED_Event | 861
CAGUAS | 2023-03-15 21:02 | 2023-03-15 21:03 | 1510 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031500278 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 1510 | keep | 0 | Mar | 2023 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
BAYAMON | 2023-03-15 21:09 | 2023-03-16 11:32 | 6 | 14:23 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTES DE LINEA | B23031500161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 863 | 2023-03-15 | 5178 | keep | 0 | Mar | 2023 | 0.0035267 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-03-15 21:10 | 2023-03-16 01:54 | 997 | 4:44 | T | ALIMENTADOR AMARRADO | CARGA POR 7201-05 | M23031500254 | New_Event | Feeder Load Transferred | Include | Include | Other | 284 | 2023-03-15 | 283148 | keep | 0 | Mar | 2023 | 0.19285 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2023-03-15 21:10 | 2023-03-16 01:54 | 1497 | 4:44 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA AVERIADA SE CERRO INTERRUPTOR CON LA CARGA DEL 7201-04 | M23031500254 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 284 | 2023-03-15 | 425148 | keep | 0 | Mar | 2023 | 0.28957 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-15 21:31 | 2023-03-15 21:33 | 996 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 20% DE SU CARGA POR EL 1620-04 | S23031501045 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-15 | 1992 | keep | 0 | Mar | 2023 | 0.0013567 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
CANOVANAS | 2023-03-15 21:31 | 2023-03-15 21:33 | 172 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 20% DEL 1336-06 | S23031501045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-15 | 344 | keep | 0 | Mar | 2023 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2023-03-15 21:59 | 2023-03-16 10:25 | 9 | 12:26 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE HACIA CAJA. | B23031500169 | New_Event | Primary Wire Break | Include | Include | Equipment | 746 | 2023-03-15 | 6714 | keep | 0 | Mar | 2023 | 0.0045729 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-03-15 22:05 | 2023-03-15 22:13 | 3438 | 0:08 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23031500170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2023-03-15 | 27504 | keep | 0 | Mar | 2023 | 0.018733 | 0.0023416 | Sustained | FALSE | FALSE | Not_TMED_Event | 3438
SAN JUAN | 2023-03-15 22:51 | 2023-03-16 11:00 | 6 | 12:09 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE DE CAJA A XMR | S23031501095 | New_Event | Primary Wire Break | Include | Include | Equipment | 729 | 2023-03-15 | 4374 | keep | 0 | Mar | 2023 | 0.0029791 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-03-15 23:07 | 2023-03-15 23:08 | 99 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR CARGA POR EL 1647-07 CERRADO POR CONTROL | R23031500237 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-15 | 99 | keep | 0 | Mar | 2023 | 6.7428e-05 | 6.7428e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 99
CANOVANAS | 2023-03-15 23:07 | 2023-03-15 23:08 | 31 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 1647-06 CERRADO POR CONTROL | R23031500237 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-15 | 31 | keep | 0 | Mar | 2023 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
CANOVANAS | 2023-03-15 23:15 | 2023-03-16 09:00 | 1 | 9:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L 1 X 50 EN RISER | R23031500238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 585 | 2023-03-15 | 585 | keep | 0 | Mar | 2023 | 0.00039844 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-15 23:48 | 2023-03-16 00:13 | 15 | 0:25 | P | NO SE REPORTO CAUSA | 1X20 DE RISER @ T-3 | B23031500199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2023-03-15 | 375 | keep | 0 | Mar | 2023 | 0.00025541 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-03-15 23:50 | 2023-03-16 07:41 | 63 | 7:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA QUEMADA | C23031500284 | New_Event | Cutout Failure | Include | Include | Equipment | 471 | 2023-03-15 | 29673 | keep | 0 | Mar | 2023 | 0.02021 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
SAN JUAN | 2023-03-15 23:57 | 2023-03-16 | 4291 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23031501129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-15 | 12873 | keep | 0 | Mar | 2023 | 0.0087677 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
BAYAMON | 2023-03-16 00:15 | 2023-03-16 04:15 | 40 | 4:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L SE REMPLAZO PORTAFUSIBLE | B23031600001 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2023-03-16 | 9600 | keep | 0 | Mar | 2023 | 0.0065385 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-16 01:38 | 2023-03-16 02:34 | 216 | 0:56 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR 1903-03 A PETICION DEL PERSONAL DE CAMPO PARA REPARAR/CERRAR PUENTE PRIMARIO MEDIANTE GOI BY-230316-01 LLEVA 70% DE LA CARGA DEL 1924-04 | S23031600069 | New_Event | Primary Wire Break | Include | Include | Equipment | 56 | 2023-03-16 | 12096 | keep | 0 | Mar | 2023 | 0.0082385 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2023-03-16 01:38 | 2023-03-16 02:34 | 31 | 0:56 | P | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR 1903-03 A PETICION DEL PERSONAL DE CAMPO PARA REPARAR/CERRAR PUENTE PRIMARIO MEDIANTE GOI BY-230316-01 LLEVA 70% DE LA CARGA DEL 1924-04 | S23031600069 | New_Event | Feeder Load Transferred | Include | Include | Other | 56 | 2023-03-16 | 1736 | keep | 0 | Mar | 2023 | 0.0011824 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-03-16 01:51 | 2023-03-16 06:21 | 87 | 4:30 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | S23031600078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2023-03-16 | 23490 | keep | 0 | Mar | 2023 | 0.015999 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
BAYAMON | 2023-03-16 01:55 | 2023-03-16 10:02 | 100 | 8:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | B23031600006 | New_Event | Cutout Failure | Include | Include | Equipment | 487 | 2023-03-16 | 48700 | keep | 0 | Mar | 2023 | 0.033169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-03-16 02:58 | 2023-03-16 03:26 | 12 | 0:28 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | B23031600007 | New_Event | Animals | Include | Include | Wildlife | 28 | 2023-03-16 | 336 | keep | 0 | Mar | 2023 | 0.00022885 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-16 04:10 | 2023-03-16 06:33 | 104 | 2:23 | P | DESGANCHE | 1 X 65 EN C/L | C23031600011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-03-16 | 14872 | keep | 0 | Mar | 2023 | 0.010129 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
PONCE | 2023-03-16 04:10 | 2023-03-16 07:30 | 150 | 3:20 | P | ANIMAL | 1 X 80 EN SU D PAJARO CRUZO FASE | P23031600010 | New_Event | Animals | Include | Include | Wildlife | 200 | 2023-03-16 | 30000 | keep | 0 | Mar | 2023 | 0.020433 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-03-16 04:24 | 2023-03-16 08:59 | 20 | 4:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2023-03-16 | 5500 | keep | 0 | Mar | 2023 | 0.003746 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-03-16 04:46 | 2023-03-16 04:47 | 6197 | 0:01 | T | DESGANCHE | RECIERRE | C2303160000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-16 | 6197 | keep | 0 | Mar | 2023 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2023-03-16 04:47 | 2023-03-16 07:50 | 208 | 3:03 | P | DESGANCHE | 1 X 140 EN C/L | C23031600020 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-03-16 | 38064 | keep | 0 | Mar | 2023 | 0.025925 | 0.00014167 | Sustained | FALSE | FALSE | Not_TMED_Event | 208
BARRANQUITAS | 2023-03-16 05:07 | 2023-03-16 08:15 | 42 | 3:08 | P | CONDUCTOR ROTO O ABIERTO | ABRIO C/L PARA LEVANTAR CONDUCTOR NO FUNDIO | C23031600019 | New_Event | Primary Wire Break | Include | Include | Equipment | 188 | 2023-03-16 | 7896 | keep | 0 | Mar | 2023 | 0.0053779 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
HUMACAO | 2023-03-16 05:10 | 2023-03-16 09:04 | 92 | 3:54 | P | DESGANCHE | 1 X 100 EN C/L | C23031600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2023-03-16 | 21528 | keep | 0 | Mar | 2023 | 0.014663 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
GUAYAMA | 2023-03-16 06:15 | 2023-03-16 06:16 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23031600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 4132 | keep | 0 | Mar | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
VEGA BAJA | 2023-03-16 06:18 | 2023-03-16 13:05 | 30 | 6:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2023-03-16 | 12210 | keep | 0 | Mar | 2023 | 0.0083162 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-03-16 06:53 | 2023-03-16 10:31 | 7 | 3:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO QUEMADO | C23031600035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 218 | 2023-03-16 | 1526 | keep | 0 | Mar | 2023 | 0.0010394 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-03-16 07:02 | 2023-03-16 10:03 | 25 | 3:01 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L SE CERRO PUENTE ABIERTO | R23031600003 | New_Event | Primary Wire Break | Include | Include | Equipment | 181 | 2023-03-16 | 4525 | keep | 0 | Mar | 2023 | 0.003082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-03-16 07:23 | 2023-03-16 09:40 | 40 | 2:17 | P | DESGANCHE | 1 X 40 EN C/L | C23031600047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-03-16 | 5480 | keep | 0 | Mar | 2023 | 0.0037324 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-16 07:27 | 2023-03-16 19:00 | 210 | 11:33 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO 40' DE MADERA X POSTE DE 45' GALVANIZADO NO FUNDIO | B23031600018 | New_Event | Primary Pole Failure | Include | Include | Equipment | 693 | 2023-03-16 | 145530 | keep | 0 | Mar | 2023 | 0.09912 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
MAYAGÃœEZ | 2023-03-16 07:30 | 2023-03-16 07:31 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23031600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 990 | keep | 0 | Mar | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
HUMACAO | 2023-03-16 07:37 | 2023-03-16 12:48 | 20 | 5:11 | P | ANIMAL | 1 X 40 EN C/L CRUCE X REPTIL | C23031600049 | New_Event | Animals | Include | Include | Wildlife | 311 | 2023-03-16 | 6220 | keep | 0 | Mar | 2023 | 0.0042364 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-03-16 07:44 | 2023-03-16 07:45 | 996 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE 1620-04 20% POR 1620-04 | S23031600102 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-16 | 996 | keep | 0 | Mar | 2023 | 0.00067837 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
CANOVANAS | 2023-03-16 07:44 | 2023-03-16 07:45 | 172 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 20% 1336-06 | S23031600102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 172 | keep | 0 | Mar | 2023 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2023-03-16 08:10 | 2023-03-16 11:54 | 150 | 3:44 | P | DESGANCHE | 1 X 80 EN C/L Y 1 X100 EN C/L SE REALIZO DESGANCHE | S23031600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-03-16 | 33600 | keep | 0 | Mar | 2023 | 0.022885 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2023-03-16 08:16 | 2023-03-16 09:06 | 1633 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 81650 | keep | 0 | Mar | 2023 | 0.055611 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2023-03-16 08:16 | 2023-03-16 09:06 | 1624 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 81200 | keep | 0 | Mar | 2023 | 0.055305 | 0.0011061 | Sustained | FALSE | FALSE | Not_TMED_Event | 1624
UTUADO | 2023-03-16 08:17 | 2023-03-16 09:07 | 1405 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 70250 | keep | 0 | Mar | 2023 | 0.047847 | 0.00095694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2023-03-16 08:17 | 2023-03-16 09:07 | 669 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 33450 | keep | 0 | Mar | 2023 | 0.022783 | 0.00045565 | Sustained | FALSE | FALSE | Not_TMED_Event | 669
UTUADO | 2023-03-16 08:17 | 2023-03-16 09:07 | 1527 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 76350 | keep | 0 | Mar | 2023 | 0.052002 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2023-03-16 08:17 | 2023-03-16 09:07 | 1054 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 52700 | keep | 0 | Mar | 2023 | 0.035894 | 0.00071787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2023-03-16 08:17 | 2023-03-16 09:07 | 932 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 46600 | keep | 0 | Mar | 2023 | 0.031739 | 0.00063478 | Sustained | FALSE | FALSE | Not_TMED_Event | 932
UTUADO | 2023-03-16 08:17 | 2023-03-16 09:07 | 705 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 35250 | keep | 0 | Mar | 2023 | 0.024009 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2023-03-16 08:17 | 2023-03-16 09:07 | 1521 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 76050 | keep | 0 | Mar | 2023 | 0.051797 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2023-03-16 08:17 | 2023-03-16 09:07 | 882 | 0:50 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 CAMION IMPACTO POSTES Y CRUZO LINEAS | A23031600032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2023-03-16 | 44100 | keep | 0 | Mar | 2023 | 0.030036 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
CANOVANAS | 2023-03-16 08:19 | 2023-03-16 15:00 | 10 | 6:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | R23031600008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 401 | 2023-03-16 | 4010 | keep | 0 | Mar | 2023 | 0.0027312 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-03-16 08:21 | 2023-03-16 14:57 | 6 | 6:36 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA SECUNDARIA Y REEMPLAZO DE CAJA PRIMARIA EN TRANSFORMADOR | P23031600027 | New_Event | Primary Wire Break | Include | Include | Equipment | 396 | 2023-03-16 | 2376 | keep | 0 | Mar | 2023 | 0.0016183 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-03-16 08:26 | 2023-03-16 13:00 | 161 | 4:34 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23031600064 | New_Event | Animals | Include | Include | Wildlife | 274 | 2023-03-16 | 44114 | keep | 0 | Mar | 2023 | 0.030046 | 0.00010966 | Sustained | FALSE | FALSE | Not_TMED_Event | 161
FAJARDO | 2023-03-16 08:32 | 2023-03-16 10:44 | 20 | 2:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN RISER SE REMPLAZO PORTAFUSIBLE QUEMADO | R23031600009 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2023-03-16 | 2640 | keep | 0 | Mar | 2023 | 0.0017981 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-16 08:42 | 2023-03-16 10:42 | 1483 | 2:00 | T | CAUSAS EXTERNAS | CAMION IMPACTO LINEAS Y LAS CRUZO MOMENTANEAMENTE Y CAUSO DISPARO DEL INTERRUPTOR | A23031600078 | New_Event | Damage From Public | Include | Include | Public | 120 | 2023-03-16 | 177960 | keep | 0 | Mar | 2023 | 0.12121 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-03-16 08:44 | 2023-03-16 16:51 | 30 | 8:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR 37.5KVA | S23031600131 | New_Event | Service Transformer Failure | Include | Include | Equipment | 487 | 2023-03-16 | 14610 | keep | 0 | Mar | 2023 | 0.0099508 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-03-16 08:47 | 2023-03-16 08:48 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2303160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 4291 | keep | 0 | Mar | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
HUMACAO | 2023-03-16 08:48 | 2023-03-16 11:09 | 5 | 2:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | C23031600071 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2023-03-16 | 705 | keep | 0 | Mar | 2023 | 0.00048017 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-16 08:55 | 2023-03-16 10:39 | 4 | 1:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO CONECTORES QUEMADOS EN TOMAS SECUNDARIAS | B23031600028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 104 | 2023-03-16 | 416 | keep | 0 | Mar | 2023 | 0.00028334 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-03-16 09:07 | 2023-03-16 09:24 | 1521 | 0:17 | T | CAUSAS EXTERNAS | DISPARO DEL INTERRUPTOR CAMION IMPACTO POSTES Y CRUZO LINEAS SE CERRO INTERRUPTOR MANUAL EN LA SUBESTACION | A23031600036 | New_Event | Damage From Public | Include | Include | Public | 17 | 2023-03-16 | 25857 | keep | 0 | Mar | 2023 | 0.017611 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
CANOVANAS | 2023-03-16 09:08 | 2023-03-16 12:38 | 1 | 3:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 3 EN BANCO DE XMR | R23031600014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 210 | 2023-03-16 | 210 | keep | 0 | Mar | 2023 | 0.00014303 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-16 09:09 | 2023-03-16 11:20 | 5 | 2:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23031600031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-03-16 | 655 | keep | 0 | Mar | 2023 | 0.00044612 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-03-16 09:24 | 2023-03-16 10:24 | 61 | 1:00 | P | CAUSAS EXTERNAS | 3 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA CAMION IMPACTO LINEAS | A23031600064 | Partial_restoration | Damage From Public | Include | Include | Public | 60 | 2023-03-16 | 3660 | keep | 0 | Mar | 2023 | 0.0024928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-16 09:30 | 2023-03-16 12:09 | 1 | 2:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN CL Y SE REMPLAZO CAJA PRIMARIA | S23031600206 | New_Event | Cutout Failure | Include | Include | Equipment | 159 | 2023-03-16 | 159 | keep | 0 | Mar | 2023 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-16 09:40 | 2023-03-16 10:56 | 45 | 1:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23031600161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2023-03-16 | 3420 | keep | 0 | Mar | 2023 | 0.0023293 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-03-16 09:41 | 2023-03-16 09:42 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERCION Y QUEDA EN SERVICIO | M23031600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 1192 | keep | 0 | Mar | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
YAUCO | 2023-03-16 09:48 | 2023-03-16 09:52 | 1475 | 0:04 | T | ANIMAL | DISPARO DE ALIMENTADOR SE CERRO POR CONTROL | P23031600052 | New_Event | Animals | Include | Include | Wildlife | 4 | 2023-03-16 | 5900 | keep | 0 | Mar | 2023 | 0.0040185 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
GUAYAMA | 2023-03-16 09:49 | 2023-03-16 12:00 | 12 | 2:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA Y SE REGULO VOLTAJE | P23031600051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 131 | 2023-03-16 | 1572 | keep | 0 | Mar | 2023 | 0.0010707 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-03-16 09:52 | 2023-03-16 11:29 | 190 | 1:37 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P23031600058 | 1st_after_momentary | Animals | Include | Include | Wildlife | 97 | 2023-03-16 | 18430 | keep | 0 | Mar | 2023 | 0.012553 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
MAYAGÃœEZ | 2023-03-16 09:56 | 2023-03-16 09:57 | 637 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23031600054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 637 | keep | 0 | Mar | 2023 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
CANOVANAS | 2023-03-16 10:08 | 2023-03-16 10:37 | 50 | 0:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA NO FUNDIO | R23031600019 | New_Event | Cutout Failure | Include | Include | Equipment | 29 | 2023-03-16 | 1450 | keep | 0 | Mar | 2023 | 0.00098759 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-03-16 10:08 | 2023-03-16 16:50 | 7 | 6:42 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | C23031600087 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 402 | 2023-03-16 | 2814 | keep | 0 | Mar | 2023 | 0.0019166 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-16 10:10 | 2023-03-16 10:11 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2303160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 733 | keep | 0 | Mar | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
AGUADILLA | 2023-03-16 10:19 | 2023-03-16 14:38 | 40 | 4:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA | A23031600080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-03-16 | 10360 | keep | 0 | Mar | 2023 | 0.0070561 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-03-16 10:36 | 2023-03-16 13:03 | 6 | 2:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BARRA EN PEDESTAL | R23031600023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 147 | 2023-03-16 | 882 | keep | 0 | Mar | 2023 | 0.00060073 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-03-16 10:37 | 2023-03-16 11:10 | 1 | 0:33 | P | ANIMAL | 1 X 40 EN RISER CRUCE POR AVE | R23031600024 | New_Event | Animals | Include | Include | Wildlife | 33 | 2023-03-16 | 33 | keep | 0 | Mar | 2023 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-16 10:38 | 2023-03-16 16:09 | 2 | 5:31 | P | PROBLEMA DEL CLIENTE | 3 X 100 EN RISER PARARRAYO PRIVADO | S23031600182 | New_Event | Customer-Related Interruption | Include | Include | Public | 331 | 2023-03-16 | 662 | keep | 0 | Mar | 2023 | 0.00045089 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-03-16 10:47 | 2023-03-16 14:15 | 60 | 3:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA NO FUNDIO | C23031600091 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2023-03-16 | 12480 | keep | 0 | Mar | 2023 | 0.0085001 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-03-16 11:06 | 2023-03-16 12:12 | 2286 | 1:06 | S | PROTECCION DEFECTUOSA | DISPARO A LOCK OUT DE LA SUBESTACION SE TRANSFIRIO LAS CARGAS AL 2005-09 PARA REPARA SUDDEN PREASSURE DEL TRANSFORMADOR. SJ-230316-50 | R23031600026 | New_Event | Protection Miscoordination | Include | Include | Other | 66 | 2023-03-16 | 150876 | keep | 0 | Mar | 2023 | 0.10276 | 0.001557 | Sustained | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2023-03-16 11:06 | 2023-03-16 12:12 | 693 | 1:06 | S | PROTECCION DEFECTUOSA | DISPARO A LOCK OUT DE LA SUBESTACION SE TRANSFIRIO LAS CARGAS AL 2005-09 PARA REPARA SUDDEN PREASSURE DEL TRANSFORMADOR. SJ-230316-50 | R23031600026 | New_Event | Protection Miscoordination | Include | Include | Other | 66 | 2023-03-16 | 45738 | keep | 0 | Mar | 2023 | 0.031152 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
UTUADO | 2023-03-16 11:08 | 2023-03-16 12:05 | 652 | 0:57 | P | CAUSAS EXTERNAS | SE ABRIO MACHETES PARA REMPLAZAR AISLADORES CAMION IMPACTO POSTES Y CRUZO LINEAS AVERIANDO LOS AISLADORES | A23031600085 | New_Event | Damage From Public | Include | Include | Public | 57 | 2023-03-16 | 37164 | keep | 0 | Mar | 2023 | 0.025312 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
BAYAMON | 2023-03-16 11:12 | 2023-03-16 15:08 | 1 | 3:56 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR Y SE REPARO SECUNDARIA Y DEJO CLIENTE SIN SERVICIO POR AVERIA INTERNA | B23031600024 | New_Event | Customer-Related Interruption | Include | Include | Public | 236 | 2023-03-16 | 236 | keep | 0 | Mar | 2023 | 0.00016074 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-16 11:25 | 2023-03-16 16:10 | 180 | 4:45 | P | ANIMAL | 1 X 65 EN CL CRUCE DE FASE POR IGUANA | M23031600075 | New_Event | Animals | Include | Include | Wildlife | 285 | 2023-03-16 | 51300 | keep | 0 | Mar | 2023 | 0.03494 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
FAJARDO | 2023-03-16 11:29 | 2023-03-16 11:33 | 1778 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | R23031600037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-16 | 7112 | keep | 0 | Mar | 2023 | 0.004844 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2023-03-16 11:36 | 2023-03-16 12:16 | 1778 | 0:40 | T | CAUSAS EXTERNAS | SE ENCONTRO CORTE DE LINEA ABIERTO SE CERRO INTERRUPTOR Y QUEDO EN SERVICIO 90% | R23031600037 | New_Event | Damage From Public | Include | Include | Public | 40 | 2023-03-16 | 71120 | keep | 0 | Mar | 2023 | 0.04844 | 0.001211 | Sustained | FALSE | FALSE | Not_TMED_Event | 1778
CANOVANAS | 2023-03-16 11:37 | 2023-03-16 13:51 | 60 | 2:14 | P | DESGANCHE | 1 X 40, 1 X 30 Y 1 X 20 EN CORTE DE LINEA DESGANCHE | R23031600036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-03-16 | 8040 | keep | 0 | Mar | 2023 | 0.005476 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-03-16 11:46 | 2023-03-16 18:00 | 30 | 6:14 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CL SE REPARO LINEA PRIMARIA | M23031600080 | New_Event | Primary Wire Break | Include | Include | Equipment | 374 | 2023-03-16 | 11220 | keep | 0 | Mar | 2023 | 0.0076419 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-16 11:52 | 2023-03-16 11:56 | 2617 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | B2303160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-16 | 10468 | keep | 0 | Mar | 2023 | 0.0071297 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
SAN JUAN | 2023-03-16 11:54 | 2023-03-16 12:01 | 3957 | 0:07 | T | DESGANCHE | DISPARO CERRADO POR CONTROL | S23031600212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 7 | 2023-03-16 | 27699 | keep | 0 | Mar | 2023 | 0.018866 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2023-03-16 12:01 | 2023-03-16 16:18 | 150 | 4:17 | P | DESGANCHE | 1 X 80 EN C/L Y 1 X100 EN C/L SE REALIZO DESGANCHE | S23031600010 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 257 | 2023-03-16 | 38550 | keep | 0 | Mar | 2023 | 0.026256 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-16 12:01 | 2023-03-16 15:40 | 199 | 3:39 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES MEDIANTE SJ-230316-02 | S23031600284 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2023-03-16 | 43581 | keep | 0 | Mar | 2023 | 0.029683 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-03-16 12:05 | 2023-03-16 12:30 | 1 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23031600099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-03-16 | 25 | keep | 0 | Mar | 2023 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-16 12:11 | 2023-03-16 15:10 | 6 | 2:59 | P | ANIMAL | 1 X 30 EN CL CRUCE DE FASE PRIMARIA POR AVE | M23031600082 | New_Event | Animals | Include | Include | Wildlife | 179 | 2023-03-16 | 1074 | keep | 0 | Mar | 2023 | 0.0007315 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-03-16 12:16 | 2023-03-16 12:41 | 170 | 0:25 | P | CAUSAS EXTERNAS | 1 X 140 EN C/L CAMION IMPACTO POSTE Y SE CRUZARON LAS LINEAS CON EL MOVIMIENTO | R23031600037 | Partial_restoration | Damage From Public | Include | Include | Public | 25 | 2023-03-16 | 4250 | keep | 0 | Mar | 2023 | 0.0028947 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-16 12:35 | 2023-03-16 15:42 | 35 | 3:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L SE REMPLAZARON 2 CAJAS PRIMARIAS MEDIANTE SJ-230316-03 | S23031600296 | New_Event | Cutout Failure | Include | Include | Equipment | 187 | 2023-03-16 | 6545 | keep | 0 | Mar | 2023 | 0.0044578 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-03-16 12:35 | 2023-03-16 14:00 | 9 | 1:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA A 13.2KV CON L/A | M23031600088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 85 | 2023-03-16 | 765 | keep | 0 | Mar | 2023 | 0.00052104 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-03-16 12:43 | 2023-03-16 13:00 | 1 | 0:17 | P | NO SE REPORTO CAUSA | 2 X 50 C/L 1 X 25 RISER | S23031600315 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2023-03-16 | 17 | keep | 0 | Mar | 2023 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-16 12:56 | 2023-03-16 15:39 | 30 | 2:43 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23031600120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-03-16 | 4890 | keep | 0 | Mar | 2023 | 0.0033306 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-03-16 13:11 | 2023-03-16 14:16 | 69 | 1:05 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23031600122 | New_Event | Animals | Include | Include | Wildlife | 65 | 2023-03-16 | 4485 | keep | 0 | Mar | 2023 | 0.0030547 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
PONCE | 2023-03-16 13:26 | 2023-03-16 14:20 | 185 | 0:54 | P | CAUSAS EXTERNAS | 2 X 100 1 X 80 EN CORTE DE LINEA CLIENTE PODANDO ARBOL CRUZO FASES | P23031600092 | New_Event | Damage From Public | Include | Include | Public | 54 | 2023-03-16 | 9990 | keep | 0 | Mar | 2023 | 0.0068041 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2023-03-16 13:31 | 2023-03-16 15:40 | 40 | 2:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23031600117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-03-16 | 5160 | keep | 0 | Mar | 2023 | 0.0035145 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-03-16 13:32 | 2023-03-16 14:40 | 1 | 1:08 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | R23031600056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2023-03-16 | 68 | keep | 0 | Mar | 2023 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-16 13:32 | 2023-03-16 17:10 | 20 | 3:38 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | A23031600118 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 218 | 2023-03-16 | 4360 | keep | 0 | Mar | 2023 | 0.0029696 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-03-16 13:37 | 2023-03-16 15:38 | 70 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR VIENTO | A23031600119 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2023-03-16 | 8470 | keep | 0 | Mar | 2023 | 0.0057689 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-03-16 13:40 | 2023-03-16 13:59 | 1 | 0:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S23031600391 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-03-16 | 19 | keep | 0 | Mar | 2023 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-16 13:40 | 2023-03-16 14:15 | 10 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | M23031600097 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-03-16 | 350 | keep | 0 | Mar | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-16 13:58 | 2023-03-17 15:32 | 16 | 25:34 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO CAUSA | S23031600405 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1534 | 2023-03-16 | 24544 | keep | 0 | Mar | 2023 | 0.016717 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-03-16 13:59 | 2023-03-16 14:26 | 19 | 0:27 | T | NO SE REPORTO CAUSA | DISPARO DE 1512-05 QUE LLEVA 1910-01, SE CERRO EN SUBESTACION. SUB. NO TIENE CONTROL POR SCADA | S2303160000X | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 27 | 2023-03-16 | 513 | keep | 0 | Mar | 2023 | 0.0003494 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-16 13:59 | 2023-03-16 14:26 | 37 | 0:27 | T | ALIMENTADOR AMARRADO | DISPARO DE 1512-05 QUE LLEVA 1910-01, SE CERRO EN SUBESTACION. SUB. NO TIENE CONTROL POR SCADA | S2303160000X | New_Event | Feeder Load Transferred | Include | Include | Other | 27 | 2023-03-16 | 999 | keep | 0 | Mar | 2023 | 0.00068041 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2023-03-16 14:01 | 2023-03-16 18:50 | 409 | 4:49 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETA PARTIDA ENCIMA DE SPACER MEDIANTE GOI BY-230316-02 | S23031600407 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 289 | 2023-03-16 | 118201 | keep | 0 | Mar | 2023 | 0.080506 | 0.00027857 | Sustained | FALSE | FALSE | Not_TMED_Event | 409
VEGA BAJA | 2023-03-16 14:02 | 2023-03-16 18:55 | 30 | 4:53 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A23031600122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2023-03-16 | 8790 | keep | 0 | Mar | 2023 | 0.0059868 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-16 14:03 | 2023-03-16 14:22 | 15 | 0:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | C23031600135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 19 | 2023-03-16 | 285 | keep | 0 | Mar | 2023 | 0.00019411 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-16 14:04 | 2023-03-16 15:56 | 1 | 1:52 | P | DESGANCHE | 1 X 50 EN RISER DESGANCHE | S23031600409 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-03-16 | 112 | keep | 0 | Mar | 2023 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-16 14:04 | 2023-03-16 17:08 | 377 | 3:04 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DEJO SECCIONALIZADO EN CAJAS SECAS DEL MH-2-VS SE QUEDARON FUERAS 2 CLIENTES QUE SIRVEN DEL MH-2-VS Y ENTRO 99% EN SERVICIO SE TRABAJO MEDIANTE SW-230316-01 | B23031600008 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 184 | 2023-03-16 | 69368 | keep | 0 | Mar | 2023 | 0.047246 | 0.00025677 | Sustained | FALSE | FALSE | Not_TMED_Event | 377
BARRANQUITAS | 2023-03-16 14:10 | 2023-03-16 14:56 | 30 | 0:46 | P | ERROR HUMANO | 1 X 30 EN C/L PERSONAL DE CONSTRUCCION DESGANCHANDO | C23031600113 | New_Event | Human Error | Include | Include | Other | 46 | 2023-03-16 | 1380 | keep | 0 | Mar | 2023 | 0.00093991 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-03-16 14:10 | 2023-03-16 14:12 | 2833 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A23031600123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-16 | 5666 | keep | 0 | Mar | 2023 | 0.0038591 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
BARRANQUITAS | 2023-03-16 14:13 | 2023-03-16 14:45 | 5 | 0:32 | P | ANIMAL | 1 X 10 EN XMR CRUCE X RATA | C23031600114 | New_Event | Animals | Include | Include | Wildlife | 32 | 2023-03-16 | 160 | keep | 0 | Mar | 2023 | 0.00010898 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-03-16 14:30 | 2023-03-16 15:00 | 15 | 0:30 | P | TRANSFORMADOR AVERIADO | BUSHING AVERIADO | A23031600127 | New_Event | Service Transformer Failure | Include | Include | Equipment | 30 | 2023-03-16 | 450 | keep | 0 | Mar | 2023 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-03-16 14:48 | 2023-03-16 16:27 | 20 | 1:39 | P | PROBLEMA DEL CLIENTE | SE ELIMINO TOMA Y SE LE DIO RESET A TRANSFORMADOR AUTOPROTEJIDO | P23031600108 | New_Event | Customer-Related Interruption | Include | Include | Public | 99 | 2023-03-16 | 1980 | keep | 0 | Mar | 2023 | 0.0013486 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-16 15:00 | 2023-03-16 17:30 | 10 | 2:30 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR LIQUEANDO 50KVA X 50 KVA | A23031600131 | New_Event | Service Transformer Failure | Include | Include | Equipment | 150 | 2023-03-16 | 1500 | keep | 0 | Mar | 2023 | 0.0010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-03-16 15:06 | 2023-03-16 15:07 | 3902 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031600145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 3902 | keep | 0 | Mar | 2023 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
CAGUAS | 2023-03-16 15:13 | 2023-03-16 17:09 | 85 | 1:56 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23031600147 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-03-16 | 9860 | keep | 0 | Mar | 2023 | 0.0067156 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
ARECIBO | 2023-03-16 15:17 | 2023-03-16 16:50 | 40 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 2 X 30 EN CORTE DE LINEA POR FUERTES VIENTO | A23031600134 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2023-03-16 | 3720 | keep | 0 | Mar | 2023 | 0.0025337 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-03-16 15:22 | 2023-03-16 17:13 | 54 | 1:51 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L CAMION HALO LINEAS DEL TELEFONO | C23031600150 | New_Event | Damage From Public | Include | Include | Public | 111 | 2023-03-16 | 5994 | keep | 0 | Mar | 2023 | 0.0040825 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
ARECIBO | 2023-03-16 15:30 | 2023-03-16 17:45 | 75 | 2:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA | A23031600137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-03-16 | 10125 | keep | 0 | Mar | 2023 | 0.0068961 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2023-03-16 15:30 | 2023-03-16 18:56 | 50 | 3:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR VIENTOS | A23031600234 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 206 | 2023-03-16 | 10300 | keep | 0 | Mar | 2023 | 0.0070153 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-03-16 15:38 | 2023-03-16 16:24 | 2873 | 0:46 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO, SE SECCIONALIZO CONDUCTOR EN EL SUELO. TRAMO RADIAL | C23031600156 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 46 | 2023-03-16 | 132158 | keep | 0 | Mar | 2023 | 0.090012 | 0.0019568 | Sustained | FALSE | FALSE | Not_TMED_Event | 2873
ARECIBO | 2023-03-16 15:43 | 2023-03-16 18:20 | 25 | 2:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR VIENTO | A23031600145 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 157 | 2023-03-16 | 3925 | keep | 0 | Mar | 2023 | 0.0026733 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-03-16 15:44 | 2023-03-16 21:15 | 150 | 5:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR VIENTOS | A23031600146 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 331 | 2023-03-16 | 49650 | keep | 0 | Mar | 2023 | 0.033816 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-03-16 15:58 | 2023-03-16 19:05 | 80 | 3:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L FUERTES LLUVIAS | C23031600162 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 187 | 2023-03-16 | 14960 | keep | 0 | Mar | 2023 | 0.010189 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-03-16 16:16 | 2023-03-16 17:50 | 50 | 1:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23031600216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-03-16 | 4700 | keep | 0 | Mar | 2023 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-16 16:17 | 2023-03-16 18:15 | 80 | 1:58 | P | DESGANCHE | 1 X 100 Y 1 X 40 EN CORTE DE LINEA RAMA CRUZADA | A23031600180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-03-16 | 9440 | keep | 0 | Mar | 2023 | 0.0064295 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-03-16 16:18 | 2023-03-16 20:20 | 50 | 4:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CL FUERTE LLUVIA | M23031600124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 242 | 2023-03-16 | 12100 | keep | 0 | Mar | 2023 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-03-16 16:24 | 2023-03-16 18:30 | 715 | 2:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE LE REEMPLAZO 2 AISLADORES, 2 PIN SHORT, SE REPARO Y LEVANTO CONDUCTOR | C23031600156 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 126 | 2023-03-16 | 90090 | keep | 0 | Mar | 2023 | 0.06136 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-16 16:25 | 2023-03-16 16:30 | 427 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23031600486 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-03-16 | 2135 | keep | 0 | Mar | 2023 | 0.0014541 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
BARRANQUITAS | 2023-03-16 16:30 | 2023-03-16 19:32 | 25 | 3:02 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO Y REMPLAZO CAJA AVERIADA | C23031600178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-03-16 | 4550 | keep | 0 | Mar | 2023 | 0.003099 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-03-16 16:38 | 2023-03-16 18:22 | 20 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | C23031600182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-03-16 | 2080 | keep | 0 | Mar | 2023 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-03-16 16:38 | 2023-03-16 16:39 | 2281 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031600183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 2281 | keep | 0 | Mar | 2023 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
GUAYAMA | 2023-03-16 16:38 | 2023-03-16 17:45 | 55 | 1:07 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PALOMA CRUZO FASE | P23031600114 | New_Event | Animals | Include | Include | Wildlife | 67 | 2023-03-16 | 3685 | keep | 0 | Mar | 2023 | 0.0025098 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
HUMACAO | 2023-03-16 16:41 | 2023-03-16 16:42 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031600185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 3 | keep | 0 | Mar | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-03-16 16:42 | 2023-03-16 16:43 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031600185 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 3 | keep | 0 | Mar | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-03-16 16:45 | 2023-03-16 16:46 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031600185 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 3 | keep | 0 | Mar | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-03-16 16:49 | 2023-03-16 19:13 | 54 | 2:24 | P | ARBOL SOBRE LINEA | 1 X 30 EN C/L SE RETIRO ARBOL SOBRE LA LINEA | B23031600161 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 144 | 2023-03-16 | 7776 | keep | 0 | Mar | 2023 | 0.0052962 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
ARECIBO | 2023-03-16 16:59 | 2023-03-16 21:27 | 60 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR VIENTO | A23031600189 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2023-03-16 | 16080 | keep | 0 | Mar | 2023 | 0.010952 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-03-16 17:08 | 2023-03-17 13:39 | 2 | 20:31 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DEJO SECCIONALIZADO EN CAJAS SECAS DEL MH-2-VS | B23031600008 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 1231 | 2023-03-16 | 2462 | keep | 0 | Mar | 2023 | 0.0016769 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-16 17:09 | 2023-03-16 17:10 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23031600171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 3438 | keep | 0 | Mar | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
SAN JUAN | 2023-03-16 17:12 | 2023-03-16 17:15 | 427 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2303160000X | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-16 | 1281 | keep | 0 | Mar | 2023 | 0.00087248 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-03-16 17:16 | 2023-03-16 19:46 | 16 | 2:30 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23031600196 | New_Event | Animals | Include | Include | Wildlife | 150 | 2023-03-16 | 2400 | keep | 0 | Mar | 2023 | 0.0016346 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-03-16 17:47 | 2023-03-16 19:07 | 25 | 1:20 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | B23031600203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2023-03-16 | 2000 | keep | 0 | Mar | 2023 | 0.0013622 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-03-16 17:50 | 2023-03-16 20:39 | 50 | 2:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA | B23031600206 | New_Event | Cutout Failure | Include | Include | Equipment | 169 | 2023-03-16 | 8450 | keep | 0 | Mar | 2023 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-16 17:50 | 2023-03-16 17:51 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23031600068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 3699 | keep | 0 | Mar | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
PONCE | 2023-03-16 17:50 | 2023-03-16 19:11 | 8 | 1:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA PRIMARIA EN TRANSFORMADOR 1 X 20 AMP EN TRANSFORMADOR | P23031600138 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2023-03-16 | 648 | keep | 0 | Mar | 2023 | 0.00044135 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-16 17:51 | 2023-03-16 20:18 | 173 | 2:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA AVERIADA | R23031600067 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2023-03-16 | 25431 | keep | 0 | Mar | 2023 | 0.017321 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
ARECIBO | 2023-03-16 17:51 | 2023-03-16 22:00 | 60 | 4:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031600226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2023-03-16 | 14940 | keep | 0 | Mar | 2023 | 0.010176 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-03-16 18:01 | 2023-03-17 01:25 | 75 | 7:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23031600231 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 444 | 2023-03-16 | 33300 | keep | 0 | Mar | 2023 | 0.02268 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-03-16 18:03 | 2023-03-16 18:54 | 70 | 0:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 Y 1 X 80 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA Y SE RECONECTO AL CLIENTE | R23031600072 | New_Event | Cutout Failure | Include | Include | Equipment | 51 | 2023-03-16 | 3570 | keep | 0 | Mar | 2023 | 0.0024315 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2023-03-16 18:07 | 2023-03-17 08:30 | 1 | 14:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L MAL TIEMPO | C23031600209 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 863 | 2023-03-16 | 863 | keep | 0 | Mar | 2023 | 0.00058779 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-16 18:17 | 2023-03-16 20:10 | 126 | 1:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ENREDADERA | R23031600076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-03-16 | 14238 | keep | 0 | Mar | 2023 | 0.0096974 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
VEGA BAJA | 2023-03-16 18:18 | 2023-03-16 19:57 | 82 | 1:39 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23031600214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-03-16 | 8118 | keep | 0 | Mar | 2023 | 0.0055291 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
VEGA BAJA | 2023-03-16 18:19 | 2023-03-16 18:42 | 4 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRAS SECUNDARIAS | B23031600215 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-03-16 | 92 | keep | 0 | Mar | 2023 | 6.2661e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-03-16 18:24 | 2023-03-16 21:15 | 45 | 2:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23031600522 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2023-03-16 | 7695 | keep | 0 | Mar | 2023 | 0.005241 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-03-16 18:31 | 2023-03-16 21:02 | 45 | 2:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L FUERTES LLUVIAS | C23031600217 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 151 | 2023-03-16 | 6795 | keep | 0 | Mar | 2023 | 0.004628 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2023-03-16 18:34 | 2023-03-16 22:10 | 2302 | 3:36 | T | AISLADOR ROTO, PARTIDO O SAFADO | CG-230316-01 SE SECCIONALIZO AVERIA DE AISLADORES QUEMADOS SE REEMPLAZARON AISLADORES QUEMADOS ENTRO UN 60% EN SERVICIO | C23031600219 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 216 | 2023-03-16 | 497232 | keep | 0 | Mar | 2023 | 0.33866 | 0.0015679 | Sustained | FALSE | FALSE | Not_TMED_Event | 2302
ARECIBO | 2023-03-16 18:35 | 2023-03-16 21:39 | 40 | 3:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA | A23031600245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2023-03-16 | 7360 | keep | 0 | Mar | 2023 | 0.0050129 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-03-16 18:39 | 2023-03-17 07:12 | 60 | 12:33 | P | DESGANCHE | 1 X 80 EN C/L | C23031600220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 753 | 2023-03-16 | 45180 | keep | 0 | Mar | 2023 | 0.030772 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-16 18:49 | 2023-03-16 18:50 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2303160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 870 | keep | 0 | Mar | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
HUMACAO | 2023-03-16 18:56 | 2023-03-17 09:15 | 20 | 14:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L REMPLAZO CAJA QUEMADA | C23031600243 | New_Event | Cutout Failure | Include | Include | Equipment | 859 | 2023-03-16 | 17180 | keep | 0 | Mar | 2023 | 0.011701 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-03-16 19:01 | 2023-03-16 19:03 | 548 | 0:02 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO CERRADO X CONTROL | C23031600253 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 2 | 2023-03-16 | 1096 | keep | 0 | Mar | 2023 | 0.00074648 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
SAN JUAN | 2023-03-16 19:03 | 2023-03-16 19:23 | 12 | 0:20 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REPARO BUSHING SECUNDARIO | S23031600546 | New_Event | Service Transformer Failure | Include | Include | Equipment | 20 | 2023-03-16 | 240 | keep | 0 | Mar | 2023 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-03-16 19:04 | 2023-03-16 20:51 | 548 | 1:47 | T | CONDUCTOR ARRIADO O CRUZADO | CG-230316-02 SE SECCIONALIZO EL ALIMENTADOR ENTRO UN 30% EN SERVICIO | C23031600253 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 107 | 2023-03-16 | 58636 | keep | 0 | Mar | 2023 | 0.039937 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
GUAYAMA | 2023-03-16 19:07 | 2023-03-16 19:08 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23031600133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 4132 | keep | 0 | Mar | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
ARECIBO | 2023-03-16 19:15 | 2023-03-16 21:56 | 20 | 2:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR VIENTOS | A23031600264 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 161 | 2023-03-16 | 3220 | keep | 0 | Mar | 2023 | 0.0021931 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-03-16 19:27 | 2023-03-16 22:38 | 7 | 3:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR MAL TIEMPO | C23031600272 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 191 | 2023-03-16 | 1337 | keep | 0 | Mar | 2023 | 0.00091062 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-03-16 19:40 | 2023-03-16 21:19 | 150 | 1:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA POR VIENTOS | A23031600284 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 99 | 2023-03-16 | 14850 | keep | 0 | Mar | 2023 | 0.010114 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-03-16 19:43 | 2023-03-17 08:43 | 40 | 13:00 | P | DESGANCHE | 1 X 40 EN C/L | C23031600288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 780 | 2023-03-16 | 31200 | keep | 0 | Mar | 2023 | 0.02125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-03-16 19:46 | 2023-03-16 21:04 | 150 | 1:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | A23031600236 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2023-03-16 | 11700 | keep | 0 | Mar | 2023 | 0.0079688 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-03-16 19:48 | 2023-03-16 21:04 | 400 | 1:16 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | B23031600244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2023-03-16 | 30400 | keep | 0 | Mar | 2023 | 0.020705 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BARRANQUITAS | 2023-03-16 20:16 | 2023-03-17 10:18 | 8 | 14:02 | P | DESGANCHE | SE ENERGIZO XMR AUTOPROTEGIDO. Y SE REALIZO DESGANCHE DE LINEA A CAJA | C23031600333 | New_Event | Vegetation Contact | Include | Include | Vegetation | 842 | 2023-03-16 | 6736 | keep | 0 | Mar | 2023 | 0.0045879 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-03-16 20:16 | 2023-03-17 07:55 | 400 | 11:39 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23031600160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 699 | 2023-03-16 | 279600 | keep | 0 | Mar | 2023 | 0.19043 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2023-03-16 20:31 | 2023-03-16 21:25 | 998 | 0:54 | T | DESGANCHE | SE ABRIO MACHETE PARA SECCIONALIZAR AVERIA POR DESGANCHE MEDIANTE SWITCHING-FORM SJ-230316-04 ENTRO 30% EN SERVICIO | S23031600584 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2023-03-16 | 53892 | keep | 0 | Mar | 2023 | 0.036706 | 0.00067973 | Sustained | FALSE | FALSE | Not_TMED_Event | 998
SAN JUAN | 2023-03-16 20:42 | 2023-03-16 20:43 | 1420 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1526-02 LLEVA 1530-06 CERRADO POR SCADA | S23031600589 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 1420 | keep | 0 | Mar | 2023 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
SAN JUAN | 2023-03-16 20:42 | 2023-03-16 20:43 | 437 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO 1526-02 LLEVA 1530-06 CERRADO POR SCADA | S23031600589 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-16 | 437 | keep | 0 | Mar | 2023 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2023-03-16 20:47 | 2023-03-17 09:30 | 30 | 12:43 | P | ARBOL SOBRE LINEA | 1 X 30 Y 1 X 40 EN C/L SE RETIRO ARBOL SOBRE LINEA | B23031600252 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 763 | 2023-03-16 | 22890 | keep | 0 | Mar | 2023 | 0.01559 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-16 20:51 | 2023-03-16 22:00 | 384 | 1:09 | P | CONDUCTOR ARRIADO O CRUZADO | CG-230316-02 SE DESPEGO BAJANTE DE LINEA A CAJA DE XMR CON VARETA DESDE EL PISO. ENTRO EL 70% QUE FALTABA. 100% EN SERVICIO | C23031600253 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 69 | 2023-03-16 | 26496 | keep | 0 | Mar | 2023 | 0.018046 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-16 20:55 | 2023-03-17 10:55 | 10 | 14:00 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE | S23031600593 | New_Event | Vegetation Contact | Include | Include | Vegetation | 840 | 2023-03-16 | 8400 | keep | 0 | Mar | 2023 | 0.0057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-16 20:57 | 2023-03-16 22:30 | 100 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23031600327 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2023-03-16 | 9300 | keep | 0 | Mar | 2023 | 0.0063342 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-16 21:02 | 2023-03-16 22:55 | 150 | 1:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTO | R23031600092 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 113 | 2023-03-16 | 16950 | keep | 0 | Mar | 2023 | 0.011545 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-03-16 21:04 | 2023-03-16 21:05 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031600317 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 853 | keep | 0 | Mar | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
SAN JUAN | 2023-03-16 21:06 | 2023-03-16 21:07 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2303160000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 870 | keep | 0 | Mar | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CANOVANAS | 2023-03-16 21:17 | 2023-03-16 22:00 | 70 | 0:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTO | R23031600106 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 43 | 2023-03-16 | 3010 | keep | 0 | Mar | 2023 | 0.0020501 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-03-16 21:18 | 2023-03-17 10:08 | 53 | 12:50 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE PRIMARIO | S23031600600 | New_Event | Primary Wire Break | Include | Include | Equipment | 770 | 2023-03-16 | 40810 | keep | 0 | Mar | 2023 | 0.027796 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
AGUADILLA | 2023-03-16 21:19 | 2023-03-16 23:50 | 50 | 2:31 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23031600173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-03-16 | 7550 | keep | 0 | Mar | 2023 | 0.0051423 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-16 21:25 | 2023-03-16 22:31 | 742 | 1:06 | P | DESGANCHE | SE REALIZO DESGANCHE MEDIANTE SWITCHING-FORM SJ-230316-04 EN SERVICIO EL 70% QUE FALTABA | S23031600584 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 66 | 2023-03-16 | 48972 | keep | 0 | Mar | 2023 | 0.033355 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-03-16 21:29 | 2023-03-17 01:30 | 19 | 4:01 | P | ARBOL SOBRE LINEA | SE ABRIO XMR PARA RETIRAR ARBOL DE LINEA SECUNDARIA POR MANEJO DE EMERGENCIA, SE REPARO SECUNDARIA | R23031600087 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 241 | 2023-03-16 | 4579 | keep | 0 | Mar | 2023 | 0.0031187 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
AGUADILLA | 2023-03-16 21:35 | 2023-03-16 23:15 | 100 | 1:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | A23031600345 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2023-03-16 | 10000 | keep | 0 | Mar | 2023 | 0.006811 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-16 21:44 | 2023-03-17 12:28 | 20 | 14:44 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23031600118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 884 | 2023-03-16 | 17680 | keep | 0 | Mar | 2023 | 0.012042 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-03-16 21:44 | 2023-03-17 11:12 | 16 | 13:28 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESPEJE DE ENREDADERA | R23031600115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 808 | 2023-03-16 | 12928 | keep | 0 | Mar | 2023 | 0.0088052 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-03-16 21:51 | 2023-03-16 22:50 | 85 | 0:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTO | R23031600119 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 59 | 2023-03-16 | 5015 | keep | 0 | Mar | 2023 | 0.0034157 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2023-03-16 21:54 | 2023-03-17 12:19 | 17 | 14:25 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23031600329 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 865 | 2023-03-16 | 14705 | keep | 0 | Mar | 2023 | 0.010016 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2023-03-16 22:10 | 2023-03-16 22:25 | 920 | 0:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | CG-230316-01 SE REEMPLAZARON AISLADORES QUEMADOS ENTRO UN 40% QUE FALTABA. 100% EN SERVICIO | C23031600219 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 15 | 2023-03-16 | 13800 | keep | 0 | Mar | 2023 | 0.0093991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-03-16 22:19 | 2023-03-17 09:15 | 1 | 10:56 | P | ANIMAL | 1 X 30 EN C/L EN EQUIPO DE MEDICION. CRUCE POR AVE | R23031600125 | New_Event | Animals | Include | Include | Wildlife | 656 | 2023-03-16 | 656 | keep | 0 | Mar | 2023 | 0.0004468 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-16 22:21 | 2023-03-17 08:21 | 23 | 10:00 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN C/L. XMR AVERIADO | C23031600336 | New_Event | Service Transformer Failure | Include | Include | Equipment | 600 | 2023-03-16 | 13800 | keep | 0 | Mar | 2023 | 0.0093991 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
ARECIBO | 2023-03-16 22:22 | 2023-03-16 23:40 | 60 | 1:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23031600360 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 78 | 2023-03-16 | 4680 | keep | 0 | Mar | 2023 | 0.0031875 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-16 22:31 | 2023-03-17 06:25 | 100 | 7:54 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23031600627 | New_Event | Vegetation Contact | Include | Include | Vegetation | 474 | 2023-03-16 | 47400 | keep | 0 | Mar | 2023 | 0.032284 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-03-16 22:49 | 2023-03-17 11:06 | 15 | 12:17 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031700365 | New_Event | Vegetation Contact | Include | Include | Vegetation | 737 | 2023-03-16 | 11055 | keep | 0 | Mar | 2023 | 0.0075295 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-03-16 23:04 | 2023-03-17 09:05 | 15 | 10:01 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR PUENTE PRIMARIO CRUZADO | P23031600157 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 601 | 2023-03-16 | 9015 | keep | 0 | Mar | 2023 | 0.0061401 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-16 23:05 | 2023-03-17 11:34 | 75 | 12:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER Y 1 X 65 EN OTRO RISER NO CAUSA | S23031600632 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 749 | 2023-03-16 | 56175 | keep | 0 | Mar | 2023 | 0.038261 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-03-16 23:12 | 2023-03-17 02:00 | 39 | 2:48 | T | DESGANCHE | SE RETIRO RAMA SOBRE LAS LINEAS Y SE CERRO INTERRUPTOR 7302-02 | M23031600189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-03-16 | 6552 | keep | 0 | Mar | 2023 | 0.0044625 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2023-03-16 23:26 | 2023-03-16 23:27 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23031600263 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-16 | 3438 | keep | 0 | Mar | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2023-03-16 23:28 | 2023-03-17 00:42 | 3438 | 1:14 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AVERIA POR AISLADOR PARTIDO MEDIANTE GOI BY-230316-03 ENTRO UN 30% EN SERVICIO | B23031600264 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 74 | 2023-03-16 | 254412 | keep | 0 | Mar | 2023 | 0.17328 | 0.0023416 | Sustained | FALSE | FALSE | Not_TMED_Event | 3438
ARECIBO | 2023-03-16 23:28 | 2023-03-17 15:31 | 12 | 16:03 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA CRUZADA | A23031600368 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 963 | 2023-03-16 | 11556 | keep | 0 | Mar | 2023 | 0.0078707 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-03-16 23:39 | 2023-03-17 08:14 | 2 | 8:35 | P | NO SE REPORTO CAUSA | 1 X 40 CORTE DE LINEA | S23031600638 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 515 | 2023-03-16 | 1030 | keep | 0 | Mar | 2023 | 0.00070153 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-03-16 23:52 | 2023-03-17 10:08 | 46 | 10:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIA FUERTE | R23031600129 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 616 | 2023-03-16 | 28336 | keep | 0 | Mar | 2023 | 0.0193 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
VEGA BAJA | 2023-03-17 00:02 | 2023-03-17 10:05 | 74 | 10:03 | P | PROBLEMA DEL CLIENTE | 1 X 65 EN CORTE DE LINEA PROBLEMA INTERNO DE BOMBAS DE AAA | A23031700001 | New_Event | Customer-Related Interruption | Include | Include | Public | 603 | 2023-03-17 | 44622 | keep | 0 | Mar | 2023 | 0.030392 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
MAYAGÃœEZ | 2023-03-17 00:10 | 2023-03-17 02:40 | 60 | 2:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23031700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-03-17 | 9000 | keep | 0 | Mar | 2023 | 0.0061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-17 00:14 | 2023-03-17 00:16 | 1681 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-01 LLEVA LA CARGA DEL 1346-06 SE CERRO POR CONTROL | S23031700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-17 | 3362 | keep | 0 | Mar | 2023 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-03-17 00:14 | 2023-03-17 00:16 | 1598 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-01 LLEVA LA CARGA DEL 1346-06 SE CERRO POR CONTROL | S23031700004 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-17 | 3196 | keep | 0 | Mar | 2023 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
HUMACAO | 2023-03-17 00:26 | 2023-03-17 00:27 | 4830 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO. 800 CLIENTES X 3205-07 | C23031700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 4830 | keep | 0 | Mar | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
CANOVANAS | 2023-03-17 00:28 | 2023-03-17 00:29 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23031700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 3699 | keep | 0 | Mar | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
BAYAMON | 2023-03-17 00:42 | 2023-03-17 02:29 | 2406 | 1:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO MEDIANTE GOI BY-230316-03 EN SERVICIO EL 70% QUE FALTABA POR ENTRAR | B23031600264 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 107 | 2023-03-17 | 257442 | keep | 0 | Mar | 2023 | 0.17534 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-17 01:27 | 2023-03-17 01:28 | 853 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23031700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 853 | keep | 0 | Mar | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
AGUADILLA | 2023-03-17 01:36 | 2023-03-17 09:15 | 60 | 7:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031700010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 459 | 2023-03-17 | 27540 | keep | 0 | Mar | 2023 | 0.018757 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-17 01:59 | 2023-03-17 02:00 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23031700028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 733 | keep | 0 | Mar | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BARRANQUITAS | 2023-03-17 02:39 | 2023-03-17 08:43 | 35 | 6:04 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE Y REEMPLAZO DE AISLADOR | C23031700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 364 | 2023-03-17 | 12740 | keep | 0 | Mar | 2023 | 0.0086772 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-03-17 03:08 | 2023-03-17 10:36 | 1541 | 7:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENCONTRO PUNTO CALIENTE EN FUSIBLE Y FUSIBLE FUNDIDO EN LA ALTA DE TRANSFORMADOR 7503-00 | A23031700026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 448 | 2023-03-17 | 690368 | keep | 0 | Mar | 2023 | 0.47021 | 0.0010496 | Sustained | FALSE | FALSE | Not_TMED_Event | 1541
AGUADILLA | 2023-03-17 03:08 | 2023-03-17 10:36 | 307 | 7:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENCONTRO PUNTO CALIENTE EN FUSIBLE Y FUSIBLE FUNDIDO EN LA ALTA DE TRANSFORMADOR 7503-00 | A23031700026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 448 | 2023-03-17 | 137536 | keep | 0 | Mar | 2023 | 0.093675 | 0.0002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 307
AGUADILLA | 2023-03-17 03:08 | 2023-03-17 10:36 | 1277 | 7:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENCONTRO PUNTO CALIENTE EN FUSIBLE Y FUSIBLE FUNDIDO EN LA ALTA DE TRANSFORMADOR 7503-00 | A23031700026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 448 | 2023-03-17 | 572096 | keep | 0 | Mar | 2023 | 0.38965 | 0.00086976 | Sustained | FALSE | FALSE | Not_TMED_Event | 1277
AGUADILLA | 2023-03-17 03:08 | 2023-03-17 10:36 | 1644 | 7:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENCONTRO PUNTO CALIENTE EN FUSIBLE Y FUSIBLE FUNDIDO EN LA ALTA DE TRANSFORMADOR 7503-00 | A23031700026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 448 | 2023-03-17 | 736512 | keep | 0 | Mar | 2023 | 0.50163 | 0.0011197 | Sustained | FALSE | FALSE | Not_TMED_Event | 1644
AGUADILLA | 2023-03-17 03:08 | 2023-03-17 10:36 | 1831 | 7:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENCONTRO PUNTO CALIENTE EN FUSIBLE Y FUSIBLE FUNDIDO EN LA ALTA DE TRANSFORMADOR 7503-00 | A23031700026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 448 | 2023-03-17 | 820288 | keep | 0 | Mar | 2023 | 0.55869 | 0.0012471 | Sustained | FALSE | FALSE | Not_TMED_Event | 1831
YAUCO | 2023-03-17 03:32 | 2023-03-17 07:45 | 97 | 4:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P23031700026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2023-03-17 | 24541 | keep | 0 | Mar | 2023 | 0.016715 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
CAGUAS | 2023-03-17 03:35 | 2023-03-17 11:34 | 8 | 7:59 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | C23031700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 479 | 2023-03-17 | 3832 | keep | 0 | Mar | 2023 | 0.00261 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-17 03:54 | 2023-03-17 03:55 | 4089 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23031700056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 4089 | keep | 0 | Mar | 2023 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
GUAYAMA | 2023-03-17 03:55 | 2023-03-17 08:10 | 81 | 4:15 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA PALOMA CRUZO FASE | P23031700028 | New_Event | Animals | Include | Include | Wildlife | 255 | 2023-03-17 | 20655 | keep | 0 | Mar | 2023 | 0.014068 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
VEGA BAJA | 2023-03-17 03:58 | 2023-03-17 03:59 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2303170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
GUAYAMA | 2023-03-17 04:00 | 2023-03-17 11:40 | 5 | 7:40 | P | CONDUCTOR ROTO O ABIERTO | TRABAJANDO LEVANTANDO LINEA PRMARIA | P23031700029 | New_Event | Primary Wire Break | Include | Include | Equipment | 460 | 2023-03-17 | 2300 | keep | 0 | Mar | 2023 | 0.0015665 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-03-17 04:00 | 2023-03-17 04:01 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2303170000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
ARECIBO | 2023-03-17 04:19 | 2023-03-17 15:20 | 50 | 11:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23031700041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 661 | 2023-03-17 | 33050 | keep | 0 | Mar | 2023 | 0.02251 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-17 05:09 | 2023-03-17 13:22 | 51 | 8:13 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 25 EN AEREO PROVISIONAL SE INSTALO POSTE PARA LEVANTAR AEREO PROVISIONAL | R23031700010 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 493 | 2023-03-17 | 25143 | keep | 0 | Mar | 2023 | 0.017125 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
CAGUAS | 2023-03-17 05:09 | 2023-03-17 13:10 | 20 | 8:01 | P | TERMINACION SOTERRADA AVERIADA | 1 X 30 EN RISER SE REMPLAZO TERMINACION EN RISER | C23031700016 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 481 | 2023-03-17 | 9620 | keep | 0 | Mar | 2023 | 0.0065521 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-17 05:25 | 2023-03-17 05:26 | 320 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23031700057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 320 | keep | 0 | Mar | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
CANOVANAS | 2023-03-17 05:33 | 2023-03-17 09:43 | 419 | 4:10 | P | ANIMAL | 1 X 30 EN RISER HACIA SU1 Y 1 X 100 EN C/L. CRUCE POR RATON | R23031700012 | New_Event | Animals | Include | Include | Wildlife | 250 | 2023-03-17 | 104750 | keep | 0 | Mar | 2023 | 0.071345 | 0.00028538 | Sustained | FALSE | FALSE | Not_TMED_Event | 419
AGUADILLA | 2023-03-17 05:35 | 2023-03-17 11:00 | 1485 | 5:25 | S | ANIMAL | SE RETIRO NIDOS DE AVES CRUZANDO BUSHINGS EN LA ALTA DEL TRANSFORMADOR SE REMPLAZO DOS FUSIBLES 80E SLOW | M23031700038 | New_Event | Animals | Include | Include | Wildlife | 325 | 2023-03-17 | 482625 | keep | 0 | Mar | 2023 | 0.32871 | 0.0010114 | Sustained | FALSE | FALSE | Not_TMED_Event | 1485
AGUADILLA | 2023-03-17 05:35 | 2023-03-17 11:00 | 543 | 5:25 | S | ANIMAL | SE RETIRO NIDOS DE AVES CRUZANDO BUSHINGS EN LA ALTA DEL TRANSFORMADOR SE REMPLAZO DOS FUSIBLES 80E SLOW | M23031700038 | New_Event | Animals | Include | Include | Wildlife | 325 | 2023-03-17 | 176475 | keep | 0 | Mar | 2023 | 0.1202 | 0.00036983 | Sustained | FALSE | FALSE | Not_TMED_Event | 543
VEGA BAJA | 2023-03-17 05:39 | 2023-03-17 11:30 | 30 | 5:51 | P | DESGANCHE | SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | A23031700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2023-03-17 | 10530 | keep | 0 | Mar | 2023 | 0.0071719 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-03-17 05:55 | 2023-03-17 05:57 | 948 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2303170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-17 | 1896 | keep | 0 | Mar | 2023 | 0.0012914 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
VEGA BAJA | 2023-03-17 05:56 | 2023-03-17 05:57 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23031700057 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
AGUADILLA | 2023-03-17 06:00 | 2023-03-17 11:25 | 50 | 5:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23031700041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2023-03-17 | 16250 | keep | 0 | Mar | 2023 | 0.011068 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-03-17 06:32 | 2023-03-17 13:52 | 30 | 7:20 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23031700024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2023-03-17 | 13200 | keep | 0 | Mar | 2023 | 0.0089905 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-17 06:41 | 2023-03-17 11:16 | 939 | 4:35 | P | DESCONECTIVO DEFECTUOSO | SE ENCONTRARON 2 FASES FUERA DEL ALIMENTADOR CARGA POR 1714-03 | B23031700063 | New_Event | Switch Failure | Include | Include | Equipment | 275 | 2023-03-17 | 258225 | keep | 0 | Mar | 2023 | 0.17588 | 0.00063955 | Sustained | FALSE | FALSE | Not_TMED_Event | 939
BAYAMON | 2023-03-17 06:41 | 2023-03-17 11:24 | 303 | 4:43 | P | ALIMENTADOR AMARRADO | SE ENCONTRARON 2 FASES FUERA DEL ALIMENTADOR LLEVA EL 1714-02 | B23031700063 | New_Event | Feeder Load Transferred | Include | Include | Other | 283 | 2023-03-17 | 85749 | keep | 0 | Mar | 2023 | 0.058403 | 0.00020637 | Sustained | FALSE | FALSE | Not_TMED_Event | 303
CAGUAS | 2023-03-17 06:44 | 2023-03-17 10:00 | 20 | 3:16 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23031700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-03-17 | 3920 | keep | 0 | Mar | 2023 | 0.0026699 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-17 06:59 | 2023-03-17 07:00 | 51 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1118-10 20% POR 1118-10 | S2303170000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-17 | 51 | keep | 0 | Mar | 2023 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
SAN JUAN | 2023-03-17 06:59 | 2023-03-17 07:00 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 20% DEL 1111-01 | S2303170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 2782 | keep | 0 | Mar | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2023-03-17 07:03 | 2023-03-17 07:04 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1206-03 85% X 1206-03 | S2303170000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-17 | 8679 | keep | 0 | Mar | 2023 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-03-17 07:03 | 2023-03-17 07:04 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 85% DEL 1204-05 | S2303170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 4133 | keep | 0 | Mar | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
PONCE | 2023-03-17 07:04 | 2023-03-17 09:47 | 111 | 2:43 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P23031700048 | New_Event | Animals | Include | Include | Wildlife | 163 | 2023-03-17 | 18093 | keep | 0 | Mar | 2023 | 0.012323 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
HUMACAO | 2023-03-17 07:07 | 2023-03-17 15:09 | 15 | 8:02 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y 1 X 15 EN XMR | C23031700029 | New_Event | Primary Wire Break | Include | Include | Equipment | 482 | 2023-03-17 | 7230 | keep | 0 | Mar | 2023 | 0.0049243 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-03-17 07:09 | 2023-03-17 08:48 | 1 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R23031700016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2023-03-17 | 99 | keep | 0 | Mar | 2023 | 6.7428e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-03-17 07:10 | 2023-03-17 07:11 | 508 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO SE ENCONTRO CAUSA | P23031700049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 508 | keep | 0 | Mar | 2023 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-03-17 07:10 | 2023-03-17 07:11 | 64 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23031700049 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-17 | 64 | keep | 0 | Mar | 2023 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
BAYAMON | 2023-03-17 07:15 | 2023-03-17 10:50 | 1 | 3:35 | P | DESGANCHE | 1 X 30 EN RISER DESGANCHE | S23031700043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2023-03-17 | 215 | keep | 0 | Mar | 2023 | 0.00014644 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-03-17 07:31 | 2023-03-17 16:11 | 32 | 8:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO Y SE LEVANTO CONDUCTOR PRIMARIO Y 1 X 30 EN C/L | C23031700035 | New_Event | Primary Wire Break | Include | Include | Equipment | 520 | 2023-03-17 | 16640 | keep | 0 | Mar | 2023 | 0.011333 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CANOVANAS | 2023-03-17 07:34 | 2023-03-17 10:05 | 287 | 2:31 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 80 EN C/L SE RETEZO LINEA PRIMARIA | R23031700020 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 151 | 2023-03-17 | 43337 | keep | 0 | Mar | 2023 | 0.029517 | 0.00019547 | Sustained | FALSE | FALSE | Not_TMED_Event | 287
AGUADILLA | 2023-03-17 07:35 | 2023-03-17 14:50 | 200 | 7:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | M23031700056 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 435 | 2023-03-17 | 87000 | keep | 0 | Mar | 2023 | 0.059255 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-03-17 07:40 | 2023-03-18 04:54 | 1 | 21:14 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | S23031700051 | New_Event | Animals | Include | Include | Wildlife | 1274 | 2023-03-17 | 1274 | keep | 0 | Mar | 2023 | 0.00086772 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-03-17 07:42 | 2023-03-17 13:45 | 20 | 6:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | A23031700075 | New_Event | Primary Wire Break | Include | Include | Equipment | 363 | 2023-03-17 | 7260 | keep | 0 | Mar | 2023 | 0.0049448 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-03-17 07:44 | 2023-03-17 10:15 | 20 | 2:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23031700077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-03-17 | 3020 | keep | 0 | Mar | 2023 | 0.0020569 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-17 07:54 | 2023-03-18 12:31 | 4 | 28:37 | P | CRUCETA DEFECTUOSA O AVERIADA | SE SECCIONALIZO POR CRUCETA PARTIDA Y SE CERRO C/L | B23031700128 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 1717 | 2023-03-17 | 6868 | keep | 0 | Mar | 2023 | 0.0046778 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-03-17 07:55 | 2023-03-17 07:56 | 2225 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23031700060 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-17 | 2225 | keep | 0 | Mar | 2023 | 0.0015154 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-03-17 07:56 | 2023-03-17 16:00 | 400 | 8:04 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23031600160 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 484 | 2023-03-17 | 193600 | keep | 0 | Mar | 2023 | 0.13186 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-03-17 08:08 | 2023-03-17 08:09 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23031700140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 2402 | keep | 0 | Mar | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
SAN JUAN | 2023-03-17 08:14 | 2023-03-17 10:51 | 137 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S23031700066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-03-17 | 21509 | keep | 0 | Mar | 2023 | 0.01465 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-03-17 08:14 | 2023-03-17 10:51 | 760 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S23031700066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-03-17 | 119320 | keep | 0 | Mar | 2023 | 0.081268 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2023-03-17 08:14 | 2023-03-17 10:51 | 4291 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S23031700066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-03-17 | 673687 | keep | 0 | Mar | 2023 | 0.45885 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-03-17 08:14 | 2023-03-17 10:51 | 1381 | 2:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 CARGA X 1204-01 | S23031700066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 157 | 2023-03-17 | 216817 | keep | 0 | Mar | 2023 | 0.14767 | 0.00094059 | Sustained | FALSE | FALSE | Not_TMED_Event | 1381
CANOVANAS | 2023-03-17 08:17 | 2023-03-17 12:25 | 18 | 4:08 | P | TRANSFORMADOR AVERIADO | SE CERRO DE SU-4 A T-9 Y T-8 | R23031700026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 248 | 2023-03-17 | 4464 | keep | 0 | Mar | 2023 | 0.0030404 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
HUMACAO | 2023-03-17 08:21 | 2023-03-17 12:32 | 10 | 4:11 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE XMR 37.5 X 50KVA | C23031600336 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 251 | 2023-03-17 | 2510 | keep | 0 | Mar | 2023 | 0.0017095 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-17 08:22 | 2023-03-17 13:30 | 5 | 5:08 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE NECESITA DESGANCHE | A23031700089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2023-03-17 | 1540 | keep | 0 | Mar | 2023 | 0.0010489 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-03-17 08:31 | 2023-03-17 10:33 | 30 | 2:02 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23031700047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-03-17 | 3660 | keep | 0 | Mar | 2023 | 0.0024928 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-17 08:46 | 2023-03-17 11:19 | 50 | 2:33 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M23031700071 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 153 | 2023-03-17 | 7650 | keep | 0 | Mar | 2023 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-03-17 08:49 | 2023-03-17 17:44 | 28 | 8:55 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN C/L Y SE RETEZO LINEA | C23031700051 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 535 | 2023-03-17 | 14980 | keep | 0 | Mar | 2023 | 0.010203 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
CAGUAS | 2023-03-17 08:50 | 2023-03-17 18:31 | 15 | 9:41 | P | NO SE REPORTO CAUSA | 1 X 10 EN T-16 | C23031700052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 581 | 2023-03-17 | 8715 | keep | 0 | Mar | 2023 | 0.0059357 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-17 08:53 | 2023-03-17 15:15 | 60 | 6:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23031700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2023-03-17 | 22920 | keep | 0 | Mar | 2023 | 0.015611 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-03-17 08:59 | 2023-03-17 09:00 | 1843 | 0:01 | T | DESGANCHE | RECIERRE | C23031700058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-17 | 1843 | keep | 0 | Mar | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-03-17 09:00 | 2023-03-17 12:17 | 129 | 3:17 | P | DESGANCHE | 3 X 100 EN C/L DESGANCHE | C23031700064 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-03-17 | 25413 | keep | 0 | Mar | 2023 | 0.017309 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
UTUADO | 2023-03-17 09:01 | 2023-03-17 15:45 | 25 | 6:44 | P | ARBOL SOBRE LINEA | 1 X 30 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A23031700110 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 404 | 2023-03-17 | 10100 | keep | 0 | Mar | 2023 | 0.0068791 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-03-17 09:02 | 2023-03-17 15:00 | 20 | 5:58 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031700112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 358 | 2023-03-17 | 7160 | keep | 0 | Mar | 2023 | 0.0048766 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-17 09:06 | 2023-03-17 19:25 | 1 | 10:19 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO NEUTRAL PRIMARIO SE INSTALO C/L MONOFASICO Y SE CERRARON LOS PUENTES ABIERTOS | B23031700184 | New_Event | Primary Wire Break | Include | Include | Equipment | 619 | 2023-03-17 | 619 | keep | 0 | Mar | 2023 | 0.0004216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-17 09:36 | 2023-03-17 12:53 | 100 | 3:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | M23031700133 | New_Event | Primary Wire Break | Include | Include | Equipment | 197 | 2023-03-17 | 19700 | keep | 0 | Mar | 2023 | 0.013418 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-17 09:52 | 2023-03-17 11:52 | 20 | 2:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 50 EN RISER | R23031700038 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2023-03-17 | 2400 | keep | 0 | Mar | 2023 | 0.0016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-03-17 09:53 | 2023-03-17 14:03 | 65 | 4:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23031700076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2023-03-17 | 16250 | keep | 0 | Mar | 2023 | 0.011068 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2023-03-17 09:59 | 2023-03-17 10:34 | 8 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y SE REMPLAZARON 2 PARARRAYOS | C23031700078 | New_Event | Primary Wire Break | Include | Include | Equipment | 35 | 2023-03-17 | 280 | keep | 0 | Mar | 2023 | 0.00019071 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-03-17 10:00 | 2023-03-17 15:00 | 10 | 5:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA CON ESCAPE DE ACEITE | M23031700067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 300 | 2023-03-17 | 3000 | keep | 0 | Mar | 2023 | 0.0020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-17 10:02 | 2023-03-17 10:05 | 302 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | B2303170000X | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-03-17 | 906 | keep | 0 | Mar | 2023 | 0.00061707 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2023-03-17 10:02 | 2023-03-17 15:31 | 1 | 5:29 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23031700217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 329 | 2023-03-17 | 329 | keep | 0 | Mar | 2023 | 0.00022408 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-17 10:03 | 2023-03-17 10:04 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23031700219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 2402 | keep | 0 | Mar | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
MAYAGÃœEZ | 2023-03-17 10:03 | 2023-03-18 15:30 | 10 | 29:27 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23031700105 | New_Event | Primary Wire Break | Include | Include | Equipment | 1767 | 2023-03-17 | 17670 | keep | 0 | Mar | 2023 | 0.012035 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-17 10:03 | 2023-03-17 17:29 | 10 | 7:26 | P | SECUNDARIA/OTROS | SE HABIA ABIERTO TRANSFORMADOR PARA REPARAR SECUNDARIA AL CERRARLO FUNDIO CORTE DE LINEA PRINCIPAL SE DEJO TRANSFORMADOR ABIERTO | M23031700247 | New_Event |  |  |  |  | 446 | 2023-03-17 | 4460 | keep | 0 | Mar | 2023 | 0.0030377 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-17 10:05 | 2023-03-17 12:15 | 25 | 2:10 | P | CONDUCTOR ROTO O ABIERTO | LEVANTAR NEUTRAL PRIMARIO Y REEMPLAZAR 2 DISCOS QUEMADOS | B23031700218 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 130 | 2023-03-17 | 3250 | keep | 0 | Mar | 2023 | 0.0022136 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-03-17 10:08 | 2023-03-17 12:52 | 7 | 2:44 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | R23031700043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-03-17 | 1148 | keep | 0 | Mar | 2023 | 0.0007819 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-17 10:15 | 2023-03-17 10:16 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2303170000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 2402 | keep | 0 | Mar | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
SAN JUAN | 2023-03-17 10:21 | 2023-03-17 10:35 | 418 | 0:14 | T | PROBLEMA DEL CLIENTE | HACIENDO PRUEBA EN RISER DEL CLIENTE PROBO MALO Y PROVOCO EL DISPARO DEL ALIMENTADOR | S2303170000X | New_Event | Customer-Related Interruption | Include | Include | Public | 14 | 2023-03-17 | 5852 | keep | 0 | Mar | 2023 | 0.0039858 | 0.0002847 | Sustained | FALSE | FALSE | Not_TMED_Event | 418
CAGUAS | 2023-03-17 10:23 | 2023-03-17 10:24 | 1320 | 0:01 | T | CRUCETA DEFECTUOSA O AVERIADA | RECIERRE | C23031700089 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 1 | 2023-03-17 | 1320 | keep | 0 | Mar | 2023 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
CAGUAS | 2023-03-17 10:24 | 2023-03-17 17:34 | 144 | 7:10 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REEMPLAZO CRUCETA PARTIDA CG-230317-02 | C23031700096 | 1st_after_momentary | Primary Crossarm Failure | Include | Include | Equipment | 430 | 2023-03-17 | 61920 | keep | 0 | Mar | 2023 | 0.042173 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
BAYAMON | 2023-03-17 10:28 | 2023-03-17 12:37 | 30 | 2:09 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23031700246 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-03-17 | 3870 | keep | 0 | Mar | 2023 | 0.0026358 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-03-17 10:34 | 2023-03-17 10:38 | 3902 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C23031700091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-17 | 15608 | keep | 0 | Mar | 2023 | 0.010631 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
ARECIBO | 2023-03-17 10:36 | 2023-03-17 11:20 | 20 | 0:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23031700006 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 44 | 2023-03-17 | 880 | keep | 0 | Mar | 2023 | 0.00059936 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-03-17 10:38 | 2023-03-17 13:09 | 8 | 2:31 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y SE REMPLAZARON 2 PARARRAYOS | C23031700078 | New_Event | Primary Wire Break | Include | Include | Equipment | 151 | 2023-03-17 | 1208 | keep | 0 | Mar | 2023 | 0.00082276 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-03-17 10:49 | 2023-03-17 10:50 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23031700104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 3 | keep | 0 | Mar | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-17 10:51 | 2023-03-17 15:41 | 2 | 4:50 | P | NO SE REPORTO CAUSA | 1 X 40 CORTE DE LINEA | S23031600638 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 290 | 2023-03-17 | 580 | keep | 0 | Mar | 2023 | 0.00039504 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-17 11:00 | 2023-03-17 14:52 | 8 | 3:52 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO PARTIDO | B23031700263 | New_Event | Primary Wire Break | Include | Include | Equipment | 232 | 2023-03-17 | 1856 | keep | 0 | Mar | 2023 | 0.0012641 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-17 11:02 | 2023-03-17 14:40 | 38 | 3:38 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23031700054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2023-03-17 | 8284 | keep | 0 | Mar | 2023 | 0.0056422 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
MAYAGÃœEZ | 2023-03-17 11:02 | 2023-03-18 10:09 | 30 | 23:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031700147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1387 | 2023-03-17 | 41610 | keep | 0 | Mar | 2023 | 0.02834 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-03-17 11:02 | 2023-03-17 11:20 | 20 | 0:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23031700146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2023-03-17 | 360 | keep | 0 | Mar | 2023 | 0.00024519 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-03-17 11:06 | 2023-03-17 12:38 | 1 | 1:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23031700149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 92 | 2023-03-17 | 92 | keep | 0 | Mar | 2023 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-03-17 11:06 | 2023-03-17 12:38 | 2266 | 1:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23031700149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 92 | 2023-03-17 | 208472 | keep | 0 | Mar | 2023 | 0.14199 | 0.0015434 | Sustained | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2023-03-17 11:06 | 2023-03-17 12:38 | 1399 | 1:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A23031700149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 92 | 2023-03-17 | 128708 | keep | 0 | Mar | 2023 | 0.087662 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
CANOVANAS | 2023-03-17 11:14 | 2023-03-17 17:27 | 5 | 6:13 | P | DESGANCHE | SE REEMPLAZO XMR DE 15 KVA Y DESGANCHE | R23031700057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2023-03-17 | 1865 | keep | 0 | Mar | 2023 | 0.0012702 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-17 11:16 | 2023-03-17 11:24 | 1096 | 0:08 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO LINEAS CRUZADAS, 5 MACHETES QUEMADOS Y 2 PUENTES ABIERTOS | B23031700063 | New_Event | Switch Failure | Include | Include | Equipment | 8 | 2023-03-17 | 8768 | keep | 0 | Mar | 2023 | 0.0059718 | 0.00074648 | Sustained | FALSE | FALSE | Not_TMED_Event | 1096
SAN JUAN | 2023-03-17 11:22 | 2023-03-17 13:29 | 35 | 2:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23031700215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2023-03-17 | 4445 | keep | 0 | Mar | 2023 | 0.0030275 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-03-17 11:24 | 2023-03-17 15:31 | 986 | 4:07 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON 5 MACHETES QUEMADOS , SE REPARO 2 PUENTES ABIERTOS Y SE DESCRUZARON LINEAS | B23031700063 | Partial_restoration | Switch Failure | Include | Include | Equipment | 247 | 2023-03-17 | 243542 | keep | 0 | Mar | 2023 | 0.16588 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-17 11:30 | 2023-03-17 16:52 | 40 | 5:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23031700155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2023-03-17 | 12880 | keep | 0 | Mar | 2023 | 0.0087725 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-03-17 12:04 | 2023-03-17 13:45 | 40 | 1:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23031700167 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 101 | 2023-03-17 | 4040 | keep | 0 | Mar | 2023 | 0.0027516 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-03-17 12:05 | 2023-03-17 16:25 | 7 | 4:20 | P | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO TRANSFORMADOR Y SE REMPLAZO CRUCETA | S23031700213 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 260 | 2023-03-17 | 1820 | keep | 0 | Mar | 2023 | 0.0012396 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-03-17 12:05 | 2023-03-17 15:37 | 10 | 3:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | M23031700168 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 212 | 2023-03-17 | 2120 | keep | 0 | Mar | 2023 | 0.0014439 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-17 12:15 | 2023-03-17 15:40 | 300 | 3:25 | P | CONDUCTOR ROTO O ABIERTO | LEVANTAR NEUTRAL PRIMARIO Y REEMPLAZAR 2 DISCOS QUEMADOS | B23031700218 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 205 | 2023-03-17 | 61500 | keep | 0 | Mar | 2023 | 0.041887 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-17 12:19 | 2023-03-17 14:24 | 13 | 2:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23031700227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-03-17 | 1625 | keep | 0 | Mar | 2023 | 0.0011068 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2023-03-17 12:25 | 2023-03-17 15:39 | 6 | 3:14 | P | TRANSFORMADOR AVERIADO | SE REPUSO 1 X 35 EN SU-3 Y SE REEMPLAZO XMR DE 100KVA POR 100 KVA | R23031700026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 194 | 2023-03-17 | 1164 | keep | 0 | Mar | 2023 | 0.0007928 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-17 12:28 | 2023-03-17 18:22 | 50 | 5:54 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN MACHETE | S23031700230 | New_Event | Primary Wire Break | Include | Include | Equipment | 354 | 2023-03-17 | 17700 | keep | 0 | Mar | 2023 | 0.012055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-03-17 12:38 | 2023-03-17 13:00 | 15 | 0:22 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031700365 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-03-17 | 330 | keep | 0 | Mar | 2023 | 0.00022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-17 12:43 | 2023-03-18 11:30 | 1 | 22:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23031700185 | New_Event | Primary Wire Break | Include | Include | Equipment | 1367 | 2023-03-17 | 1367 | keep | 0 | Mar | 2023 | 0.00093106 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-17 12:59 | 2023-03-17 18:18 | 20 | 5:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L 2 X 10 EN XMR Y SE REEMPLAZO CAJA PRIMARIA | C23031700138 | New_Event | Cutout Failure | Include | Include | Equipment | 319 | 2023-03-17 | 6380 | keep | 0 | Mar | 2023 | 0.0043454 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-17 13:00 | 2023-03-17 14:15 | 50 | 1:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23031700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-03-17 | 3750 | keep | 0 | Mar | 2023 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-17 13:00 | 2023-03-17 14:45 | 9 | 1:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S23031700257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2023-03-17 | 945 | keep | 0 | Mar | 2023 | 0.00064364 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2023-03-17 13:17 | 2023-03-17 20:19 | 37 | 7:02 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23031700145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 422 | 2023-03-17 | 15614 | keep | 0 | Mar | 2023 | 0.010635 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2023-03-17 13:30 | 2023-03-17 18:09 | 1633 | 4:39 | T | DESGANCHE | DISPARO DE BKR 1703-01 SE SECCIONALIZO Y SE CERRO POR CONTROL LLEVA EL 80% DEL 1703-05 | B23031700309 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2023-03-17 | 455607 | keep | 0 | Mar | 2023 | 0.31031 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
BAYAMON | 2023-03-17 13:30 | 2023-03-17 18:09 | 33 | 4:39 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1703-01 SE SECCIONALIZO Y SE CERRO POR CONTROL ENTRO UN 70% DEL 1703-01. LLEVA EL 80% DEL 1703-05. | B23031700309 | New_Event | Feeder Load Transferred | Include | Include | Other | 279 | 2023-03-17 | 9207 | keep | 0 | Mar | 2023 | 0.0062708 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
AGUADILLA | 2023-03-17 13:32 | 2023-03-17 15:00 | 8 | 1:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | M23031700199 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2023-03-17 | 704 | keep | 0 | Mar | 2023 | 0.00047949 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-03-17 13:39 | 2023-03-17 15:50 | 377 | 2:11 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO BKR A PETICION DE VICTOR QUINONEZ PARA TRABAJAR CON AVERIA DE VS-2 @ CAJAS SECAS EN EL MH-2. | B23031700315 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 131 | 2023-03-17 | 49387 | keep | 0 | Mar | 2023 | 0.033637 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-17 13:50 | 2023-03-17 22:09 | 38 | 8:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | S23031700253 | New_Event | Primary Wire Break | Include | Include | Equipment | 499 | 2023-03-17 | 18962 | keep | 0 | Mar | 2023 | 0.012915 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2023-03-17 13:50 | 2023-03-17 23:43 | 30 | 9:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | B23031700248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 593 | 2023-03-17 | 17790 | keep | 0 | Mar | 2023 | 0.012117 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-17 13:54 | 2023-03-17 18:43 | 45 | 4:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23031700152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 289 | 2023-03-17 | 13005 | keep | 0 | Mar | 2023 | 0.0088576 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-03-17 13:58 | 2023-03-18 06:10 | 40 | 16:12 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23031700254 | New_Event | Vegetation Contact | Include | Include | Vegetation | 972 | 2023-03-17 | 38880 | keep | 0 | Mar | 2023 | 0.026481 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2023-03-17 14:12 | 2023-03-17 16:45 | 40 | 2:33 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LA LINEA | A23031700192 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 153 | 2023-03-17 | 6120 | keep | 0 | Mar | 2023 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-03-17 14:18 | 2023-03-18 09:45 | 11 | 19:27 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23031700259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1167 | 2023-03-17 | 12837 | keep | 0 | Mar | 2023 | 0.0087432 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-03-17 14:25 | 2023-03-17 16:02 | 1 | 1:37 | P | DESGANCHE | 2 X 65 EN RISER DESGANCHE | R23031700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-03-17 | 97 | keep | 0 | Mar | 2023 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-17 14:33 | 2023-03-17 16:06 | 8 | 1:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25KVA | A23031700198 | New_Event | Service Transformer Failure | Include | Include | Equipment | 93 | 2023-03-17 | 744 | keep | 0 | Mar | 2023 | 0.00050674 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-03-17 14:36 | 2023-03-17 16:55 | 78 | 2:19 | P | DESGANCHE | DESGANCHE Y 1 X 50 EN C/L | C23031700161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-03-17 | 10842 | keep | 0 | Mar | 2023 | 0.0073844 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
GUAYAMA | 2023-03-17 14:45 | 2023-03-17 15:10 | 7 | 0:25 | P | PARARRAYOS DEFECTUOSO | SE ABRE TRANSFORMADOR PARA RETIRAR PARARRAYO | P23031700160 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 25 | 2023-03-17 | 175 | keep | 0 | Mar | 2023 | 0.00011919 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-03-17 14:59 | 2023-03-17 20:20 | 15 | 5:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA FUERTES VIENTOS | M23031700222 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 321 | 2023-03-17 | 4815 | keep | 0 | Mar | 2023 | 0.0032795 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-17 15:12 | 2023-03-18 16:42 | 1 | 25:30 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTO Y SE CERRO PUENTE ABIERTO | S23031700270 | New_Event | Primary Wire Break | Include | Include | Equipment | 1530 | 2023-03-17 | 1530 | keep | 0 | Mar | 2023 | 0.0010421 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-17 15:20 | 2023-03-17 16:06 | 20 | 0:46 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA Y SE RETESO LINEA | S23031700267 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 46 | 2023-03-17 | 920 | keep | 0 | Mar | 2023 | 0.00062661 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-17 15:37 | 2023-03-17 15:58 | 4 | 0:21 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR SE REFIERE A LOW VOLTAJE SE REMOVIERON 3 TOMAS CLIENTES CONECTADOS SIN CONTADOR | S23031700246 | New_Event | Other Causes | Include | Include | Other | 21 | 2023-03-17 | 84 | keep | 0 | Mar | 2023 | 5.7212e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-03-17 15:38 | 2023-03-17 16:30 | 12 | 0:52 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y SE REPARO PEDESTAL | C23031700176 | New_Event |  |  |  |  | 52 | 2023-03-17 | 624 | keep | 0 | Mar | 2023 | 0.000425 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-17 15:39 | 2023-03-17 18:17 | 1 | 2:38 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23031700229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2023-03-17 | 158 | keep | 0 | Mar | 2023 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-17 15:50 | 2023-03-17 15:52 | 2 | 0:02 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DEJO SECCIONALIZADO EN CAJAS SECAS DEL MH-2-VS | B23031600008 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2023-03-17 | 4 | keep | 0 | Mar | 2023 | 2.7244e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-17 15:51 | 2023-03-17 23:39 | 60 | 7:48 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA LEVANTAR PROVISIONAL EN EL PISO | B23031700369 | New_Event | Primary Wire Break | Include | Include | Equipment | 468 | 2023-03-17 | 28080 | keep | 0 | Mar | 2023 | 0.019125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-03-17 15:52 | 2023-03-17 18:35 | 377 | 2:43 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE BKR SE INSTALO EXTENCIONES PARA CONECTAR 2 ELBOW T. TIENE 2 VIAS AVERIADAS EN EL VS-2. | B23031700315 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 163 | 2023-03-17 | 61451 | keep | 0 | Mar | 2023 | 0.041854 | 0.00025677 | Sustained | FALSE | FALSE | Not_TMED_Event | 377
PONCE | 2023-03-17 15:53 | 2023-03-17 15:56 | 3114 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | P23031700179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-17 | 9342 | keep | 0 | Mar | 2023 | 0.0063628 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
VEGA BAJA | 2023-03-17 16:12 | 2023-03-17 16:14 | 3076 | 0:02 | T | ERROR HUMANO | DISPARO DE INTERRUPTOR PERSONAL DE CAMPO (VICTOR QUINONEZ) INTENTADO ABRIR EL RISER DEL 9004-11 OPERO EL BKR. SE VERIFICO PERSONAL FUERA Y SE CERO POR CONTROL | B23031700378 | New_Event | Human Error | Include | Include | Other | 2 | 2023-03-17 | 6152 | keep | 0 | Mar | 2023 | 0.0041901 | 0.002095 | Momentary | FALSE | FALSE | Not_TMED_Event | 3076
PONCE | 2023-03-17 16:26 | 2023-03-17 18:15 | 85 | 1:49 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA 1 X 100 EN SU PAJARO CRUZO FASE | P23031700191 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-03-17 | 9265 | keep | 0 | Mar | 2023 | 0.0063103 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CANOVANAS | 2023-03-17 16:28 | 2023-03-17 16:32 | 1 | 0:04 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | R23031700081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-17 | 4 | keep | 0 | Mar | 2023 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-03-17 16:30 | 2023-03-17 17:42 | 232 | 1:12 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA REPARAR LINEA PRIMARIA | P23031700147 | New_Event | Primary Wire Break | Include | Include | Equipment | 72 | 2023-03-17 | 16704 | keep | 0 | Mar | 2023 | 0.011377 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
AGUADILLA | 2023-03-17 16:35 | 2023-03-18 13:40 | 30 | 21:05 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23031700237 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1265 | 2023-03-17 | 37950 | keep | 0 | Mar | 2023 | 0.025848 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-03-17 16:37 | 2023-03-18 10:25 | 100 | 17:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A23031700223 | New_Event | Cutout Failure | Include | Include | Equipment | 1068 | 2023-03-17 | 106800 | keep | 0 | Mar | 2023 | 0.072741 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-03-17 16:40 | 2023-03-18 11:35 | 12 | 18:55 | P | TERMINACION SOTERRADA AVERIADA | 1 X 15 EN XMR SE REPARO TERMINACIONES EN RISER | C23031700191 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1135 | 2023-03-17 | 13620 | keep | 0 | Mar | 2023 | 0.0092765 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-17 16:41 | 2023-03-18 07:12 | 8 | 14:31 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23031700192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 871 | 2023-03-17 | 6968 | keep | 0 | Mar | 2023 | 0.0047459 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-03-17 17:02 | 2023-03-18 13:43 | 2 | 20:41 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMA | A23031700231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1241 | 2023-03-17 | 2482 | keep | 0 | Mar | 2023 | 0.0016905 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-03-17 17:04 | 2023-03-18 10:20 | 15 | 17:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23031700242 | New_Event | Primary Wire Break | Include | Include | Equipment | 1036 | 2023-03-17 | 15540 | keep | 0 | Mar | 2023 | 0.010584 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-03-17 17:15 | 2023-03-17 19:44 | 15 | 2:29 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE RETIRO POSTE DE MADERA SECUNDARIO PODRIDO, SE REPUSO 1X10 EN XMR Y SE SUBIERON LINEAS SECUNDARIAS | C23031700202 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 149 | 2023-03-17 | 2235 | keep | 0 | Mar | 2023 | 0.0015222 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-03-17 17:23 | 2023-03-17 19:28 | 1 | 2:05 | P | NO SE REPORTO CAUSA | 3 X 140 EN RISER | R23031700083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2023-03-17 | 125 | keep | 0 | Mar | 2023 | 8.5137e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-17 17:29 | 2023-03-18 08:34 | 100 | 15:05 | P | SECUNDARIA/OTROS | 1 X 65 EN CORTE DE LINEA SE HABIA ABIERTO TRANSFORMADOR PARA REPARAR SECUNDARIA AL CERRARLO FUNDIO CORTE DE LINEA PRINCIPAL SE DEJO TRANSFORMADOR ABIERTO | M23031700247 | Additional_clients |  |  |  |  | 905 | 2023-03-17 | 90500 | keep | 0 | Mar | 2023 | 0.061639 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-03-17 17:55 | 2023-03-17 18:15 | 12 | 0:20 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | P23031700202 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 20 | 2023-03-17 | 240 | keep | 0 | Mar | 2023 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-17 18:04 | 2023-03-17 19:51 | 12 | 1:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO SECUNDARIA | C23031700213 | New_Event | Secondary Wire Break | Include | Include | Equipment | 107 | 2023-03-17 | 1284 | keep | 0 | Mar | 2023 | 0.00087453 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-17 18:09 | 2023-03-17 18:39 | 490 | 0:30 | P | DESGANCHE | 100% EN SERVICIO SE REALIZO DESGANCHE CON BARETA DESDE EL SUELO | B23031700309 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 30 | 2023-03-17 | 14700 | keep | 0 | Mar | 2023 | 0.010012 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-17 18:17 | 2023-03-17 20:15 | 233 | 1:58 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | R23031700088 | New_Event | Animals | Include | Include | Wildlife | 118 | 2023-03-17 | 27494 | keep | 0 | Mar | 2023 | 0.018726 | 0.0001587 | Sustained | FALSE | FALSE | Not_TMED_Event | 233
YAUCO | 2023-03-17 18:27 | 2023-03-17 20:40 | 300 | 2:13 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTES PARA SECCIONALIZAR ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | M23031700258 | New_Event | Primary Wire Break | Include | Include | Equipment | 133 | 2023-03-17 | 39900 | keep | 0 | Mar | 2023 | 0.027176 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2023-03-17 18:32 | 2023-03-18 10:00 | 35 | 15:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23031700261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 928 | 2023-03-17 | 32480 | keep | 0 | Mar | 2023 | 0.022122 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-03-17 18:35 | 2023-03-18 10:41 | 2 | 16:06 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DEJO SECCIONALIZADO EN CAJAS SECAS DEL MH-2-VS | B23031600008 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 966 | 2023-03-17 | 1932 | keep | 0 | Mar | 2023 | 0.0013159 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-03-17 19:00 | 2023-03-17 19:45 | 12 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P23031700201 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-03-17 | 540 | keep | 0 | Mar | 2023 | 0.00036779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-03-17 19:03 | 2023-03-17 19:06 | 3114 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR CONTROL DE SCADA | P23031700209 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-17 | 9342 | keep | 0 | Mar | 2023 | 0.0063628 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2023-03-17 19:21 | 2023-03-18 09:23 | 30 | 14:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23031700281 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 842 | 2023-03-17 | 25260 | keep | 0 | Mar | 2023 | 0.017204 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-17 20:33 | 2023-03-18 10:15 | 40 | 13:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23031700292 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 822 | 2023-03-17 | 32880 | keep | 0 | Mar | 2023 | 0.022394 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-03-17 20:40 | 2023-03-18 18:00 | 30 | 21:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO PUENTES | M23031700258 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1280 | 2023-03-17 | 38400 | keep | 0 | Mar | 2023 | 0.026154 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-17 20:48 | 2023-03-17 20:49 | 411 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23031700297 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 411 | keep | 0 | Mar | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
BAYAMON | 2023-03-17 20:50 | 2023-03-18 01:51 | 20 | 5:01 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN PROVISIONAL AEREO Y 1 SMU 12 AMP. AVERIA T50-A AL T 49 SE QUEDARON FUERA 12 CLIENTES | B23031700428 | New_Event | UG Cable Fault | Include | Include | Equipment | 301 | 2023-03-17 | 6020 | keep | 0 | Mar | 2023 | 0.0041002 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-17 20:53 | 2023-03-17 20:54 | 650 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23031700299 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-17 | 650 | keep | 0 | Mar | 2023 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
MAYAGÃœEZ | 2023-03-17 22:43 | 2023-03-18 12:42 | 30 | 13:59 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23031700310 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 839 | 2023-03-17 | 25170 | keep | 0 | Mar | 2023 | 0.017143 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-03-17 23:46 | 2023-03-18 09:55 | 30 | 10:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO CAJA PRIMARIA | R23031700090 | New_Event | Cutout Failure | Include | Include | Equipment | 609 | 2023-03-17 | 18270 | keep | 0 | Mar | 2023 | 0.012444 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-03-18 00:02 | 2023-03-18 08:48 | 50 | 8:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 Y 10 EN TRNSFORMADOR NO SE IDENTIFICO CAUSA | M23031800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 526 | 2023-03-18 | 26300 | keep | 0 | Mar | 2023 | 0.017913 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-03-18 00:20 | 2023-03-18 07:56 | 59 | 7:36 | P | ANIMAL | 1 X 40 EN C/L Y 2 X 10 EN XMR CRUCE X AVE | R23031800001 | New_Event | Animals | Include | Include | Wildlife | 456 | 2023-03-18 | 26904 | keep | 0 | Mar | 2023 | 0.018324 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BAYAMON | 2023-03-18 00:43 | 2023-03-18 18:26 | 8 | 17:43 | P | DESGANCHE | SE HIZO DESGANCHE Y 1X10 EN XMR | B23031800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1063 | 2023-03-18 | 8504 | keep | 0 | Mar | 2023 | 0.005792 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-03-18 00:44 | 2023-03-18 00:45 | 1902 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23031800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-18 | 1902 | keep | 0 | Mar | 2023 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
VEGA BAJA | 2023-03-18 00:47 | 2023-03-18 07:37 | 25 | 6:50 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE CAJA A LINEA EN C/L | B23031800002 | New_Event | Primary Wire Break | Include | Include | Equipment | 410 | 2023-03-18 | 10250 | keep | 0 | Mar | 2023 | 0.0069812 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-03-18 01:40 | 2023-03-18 09:36 | 8 | 7:56 | P | TRANSFORMADOR AVERIADO | SE TRANSFIRIO CARGAS DEL XMR FID 8369399 A XMR FID 8369432 | C23031800002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 476 | 2023-03-18 | 3808 | keep | 0 | Mar | 2023 | 0.0025936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-18 01:51 | 2023-03-18 19:00 | 12 | 17:09 | P | CABLE SOTERRADO AVERIADO | SE INSTALO UN POSTE DE 45 PARA AEREO PROVICIONAL A T-49 | B23031700428 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1029 | 2023-03-18 | 12348 | keep | 0 | Mar | 2023 | 0.0084102 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-18 02:32 | 2023-03-18 14:46 | 227 | 12:14 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE LEVANTO CONDUCTOR PRIMARIO | S23031800002 | New_Event | Primary Wire Break | Include | Include | Equipment | 734 | 2023-03-18 | 166618 | keep | 0 | Mar | 2023 | 0.11348 | 0.00015461 | Sustained | FALSE | FALSE | Not_TMED_Event | 227
BAYAMON | 2023-03-18 04:03 | 2023-03-18 08:46 | 1 | 4:43 | P | DESGANCHE | 1 X 30 EN C/L SE RETIRO RAMA CRUZANDO LINEAS | B23031800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2023-03-18 | 283 | keep | 0 | Mar | 2023 | 0.00019275 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-18 05:30 | 2023-03-18 08:59 | 4 | 3:29 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y SE REALIZO DESGANCHE SECUNDARIO | B23031800005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 209 | 2023-03-18 | 836 | keep | 0 | Mar | 2023 | 0.0005694 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-03-18 06:57 | 2023-03-18 12:04 | 15 | 5:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P23031800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2023-03-18 | 4605 | keep | 0 | Mar | 2023 | 0.0031364 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-18 07:13 | 2023-03-18 09:56 | 142 | 2:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | S23031800010 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2023-03-18 | 23146 | keep | 0 | Mar | 2023 | 0.015765 | 9.6716e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 142
MAYAGÃœEZ | 2023-03-18 07:13 | 2023-03-18 14:18 | 6 | 7:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M23031800008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 425 | 2023-03-18 | 2550 | keep | 0 | Mar | 2023 | 0.0017368 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-03-18 07:26 | 2023-03-18 16:00 | 18 | 8:34 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23031800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 514 | 2023-03-18 | 9252 | keep | 0 | Mar | 2023 | 0.0063015 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2023-03-18 07:30 | 2023-03-18 11:52 | 60 | 4:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | A23031800030 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 262 | 2023-03-18 | 15720 | keep | 0 | Mar | 2023 | 0.010707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-03-18 07:41 | 2023-03-18 12:20 | 50 | 4:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031800012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 279 | 2023-03-18 | 13950 | keep | 0 | Mar | 2023 | 0.0095013 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-18 08:14 | 2023-03-18 15:51 | 6 | 7:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON BARRAS SECUNDARIAS EN PEDESTAL | S23031800017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 457 | 2023-03-18 | 2742 | keep | 0 | Mar | 2023 | 0.0018676 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-18 08:25 | 2023-03-18 10:07 | 18 | 1:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B23031700387 | New_Event | Secondary Wire Break | Include | Include | Equipment | 102 | 2023-03-18 | 1836 | keep | 0 | Mar | 2023 | 0.0012505 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-03-18 08:34 | 2023-03-18 15:37 | 10 | 7:03 | P | SECUNDARIA/OTROS | SE HABIA ABIERTO TRANSFORMADOR PARA REPARAR SECUNDARIA AL CERRARLO FUNDIO CORTE DE LINEA PRINCIPAL SE DEJO TRANSFORMADOR ABIERTO | M23031700247 | Partial_restoration |  |  |  |  | 423 | 2023-03-18 | 4230 | keep | 0 | Mar | 2023 | 0.002881 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-03-18 08:34 | 2023-03-18 13:15 | 200 | 4:41 | P | ARBOL SOBRE LINEA | 1 X 140 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | M23031800030 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 281 | 2023-03-18 | 56200 | keep | 0 | Mar | 2023 | 0.038278 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-03-18 08:39 | 2023-03-18 12:10 | 67 | 3:31 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P23031800033 | New_Event | Animals | Include | Include | Wildlife | 211 | 2023-03-18 | 14137 | keep | 0 | Mar | 2023 | 0.0096286 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
HUMACAO | 2023-03-18 08:47 | 2023-03-18 08:48 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2303180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-18 | 2354 | keep | 0 | Mar | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
UTUADO | 2023-03-18 09:00 | 2023-03-18 17:10 | 15 | 8:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A23031800067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 490 | 2023-03-18 | 7350 | keep | 0 | Mar | 2023 | 0.0050061 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-03-18 09:10 | 2023-03-18 10:35 | 12 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES SECUNDARIAS | P23031700140 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2023-03-18 | 1020 | keep | 0 | Mar | 2023 | 0.00069472 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-18 09:23 | 2023-03-18 09:24 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23031800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-18 | 2402 | keep | 0 | Mar | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
HUMACAO | 2023-03-18 09:23 | 2023-03-18 11:33 | 20 | 2:10 | P | ANIMAL | 1 X 20 EN C/L CRUCE X AVE | C23031800026 | New_Event | Animals | Include | Include | Wildlife | 130 | 2023-03-18 | 2600 | keep | 0 | Mar | 2023 | 0.0017708 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-03-18 09:23 | 2023-03-18 11:49 | 26 | 2:26 | P | DESGANCHE | 1 X 50 EN C/L | C23031800032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-03-18 | 3796 | keep | 0 | Mar | 2023 | 0.0025854 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
AGUADILLA | 2023-03-18 09:45 | 2023-03-18 11:08 | 40 | 1:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031800047 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 83 | 2023-03-18 | 3320 | keep | 0 | Mar | 2023 | 0.0022612 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-03-18 10:04 | 2023-03-18 11:30 | 277 | 1:26 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23031800035 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-03-18 | 23822 | keep | 0 | Mar | 2023 | 0.016225 | 0.00018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 277
MAYAGÃœEZ | 2023-03-18 10:09 | 2023-03-18 15:15 | 50 | 5:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031800057 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 306 | 2023-03-18 | 15300 | keep | 0 | Mar | 2023 | 0.010421 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-03-18 10:12 | 2023-03-18 10:35 | 3 | 0:23 | P | CAUSAS EXTERNAS | 1 X 15 EN XMR A CAUSA DE SALITRE | R23031800009 | New_Event | Damage From Public | Include | Include | Public | 23 | 2023-03-18 | 69 | keep | 0 | Mar | 2023 | 4.6996e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-03-18 10:14 | 2023-03-18 11:31 | 2402 | 1:17 | T | CONDUCTOR ARRIADO O CRUZADO | BY-230318-01 SE SECCIONALIZO ALIMENTADOR SE CERRO BKR 10% EN SERVICIO | B23031800019 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 77 | 2023-03-18 | 184954 | keep | 0 | Mar | 2023 | 0.12597 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
VEGA BAJA | 2023-03-18 10:41 | 2023-03-18 18:37 | 377 | 7:56 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE HIZO BYPASS A VACUUM SWITCH Y SE CERRO BKR POR CONTROL | B23031800021 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 476 | 2023-03-18 | 179452 | keep | 0 | Mar | 2023 | 0.12222 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-18 10:41 | 2023-03-18 11:27 | 2 | 0:46 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR SECUNDARIA | B23031700402 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 46 | 2023-03-18 | 92 | keep | 0 | Mar | 2023 | 6.2661e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2023-03-18 10:47 | 2023-03-18 15:16 | 20 | 4:29 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DESENREDO LINEAS | A23031800040 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 269 | 2023-03-18 | 5380 | keep | 0 | Mar | 2023 | 0.0036643 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-03-18 10:50 | 2023-03-18 14:29 | 1 | 3:39 | P | CONDUCTOR ROTO O ABIERTO | 3 X 15 EN RISER 3 X 10 EN BANCO DE XMR SE FIJO BAJANTES PRIMARIOS | C23031800040 | New_Event | Primary Wire Break | Include | Include | Equipment | 219 | 2023-03-18 | 219 | keep | 0 | Mar | 2023 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-03-18 11:16 | 2023-03-18 14:10 | 12 | 2:54 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 2 X 15 EN TRANSFORMADOR SE REMPLAZO SECUNDARIA CRUZADA | A23031800043 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 174 | 2023-03-18 | 2088 | keep | 0 | Mar | 2023 | 0.0014221 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-18 11:20 | 2023-03-18 12:58 | 30 | 1:38 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L CAMION IMPACTO LINEAS SECUNDARIAS | C23031800048 | New_Event | Damage From Public | Include | Include | Public | 98 | 2023-03-18 | 2940 | keep | 0 | Mar | 2023 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-18 11:22 | 2023-03-18 12:27 | 4 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIR XMR PARA REEMPLAZAR CONECTORES EN BAJANTES SECUNDARIOS | C23031700173 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-03-18 | 260 | keep | 0 | Mar | 2023 | 0.00017708 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-03-18 11:24 | 2023-03-18 14:48 | 106 | 3:24 | P | DESGANCHE | SE REALIZO DEGANCHE 2 X 65 Y 1 X 80 EN CORTES DE LINEA | S23031800051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-03-18 | 21624 | keep | 0 | Mar | 2023 | 0.014728 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
CAGUAS | 2023-03-18 11:24 | 2023-03-18 13:54 | 20 | 2:30 | P | ANIMAL | 2 X 80 EN C/L CRUCE X AVE | C23031800050 | New_Event | Animals | Include | Include | Wildlife | 150 | 2023-03-18 | 3000 | keep | 0 | Mar | 2023 | 0.0020433 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-03-18 11:24 | 2023-03-18 15:32 | 80 | 4:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A23031800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-03-18 | 19840 | keep | 0 | Mar | 2023 | 0.013513 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-18 11:31 | 2023-03-18 11:33 | 2162 | 0:02 | P | CONDUCTOR ARRIADO O CRUZADO | BY-230318-01 DISPARO DE BKR AL HACER OPERACIONES PARA SECCIONALIZAR ALIMENTADOR | B23031800019 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 2 | 2023-03-18 | 4324 | keep | 0 | Mar | 2023 | 0.0029451 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-18 11:33 | 2023-03-18 11:45 | 2402 | 0:12 | T | CONDUCTOR ARRIADO O CRUZADO | BY-230318-01 SE SECCIONALIZO ALIMENTADOR SE CERRO POR SCADA 10% EN SERVICIO | B23031800019 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 12 | 2023-03-18 | 28824 | keep | 0 | Mar | 2023 | 0.019632 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2023-03-18 11:33 | 2023-03-18 17:07 | 60 | 5:34 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23031800031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2023-03-18 | 20040 | keep | 0 | Mar | 2023 | 0.013649 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-03-18 11:45 | 2023-03-18 12:48 | 25 | 1:03 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 SMU 20 DE 40 AMP EN EL SU 2A CONTAMINACION | R23031800012 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 63 | 2023-03-18 | 1575 | keep | 0 | Mar | 2023 | 0.0010727 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-03-18 11:45 | 2023-03-18 12:55 | 2162 | 1:10 | P | CONDUCTOR ARRIADO O CRUZADO | BY-230318-01 SE SECCIONALIZO ALIMENTADOR ENTRO EN SERVICIO 30% | B23031800019 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 70 | 2023-03-18 | 151340 | keep | 0 | Mar | 2023 | 0.10308 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-03-18 11:47 | 2023-03-18 13:23 | 6 | 1:36 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA REPARAR SECUNDARIA POR IMPACTO DE CAMION | C23031800053 | New_Event | Damage From Public | Include | Include | Public | 96 | 2023-03-18 | 576 | keep | 0 | Mar | 2023 | 0.00039231 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-03-18 12:00 | 2023-03-19 09:40 | 200 | 21:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO DOS CAJAS QUEMADAS DE CORTE DE LINEA | M23031800104 | New_Event | Cutout Failure | Include | Include | Equipment | 1300 | 2023-03-18 | 260000 | keep | 0 | Mar | 2023 | 0.17708 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2023-03-18 12:04 | 2023-03-18 12:37 | 2 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REPARO SECUNDARIA Y SE BAJO TAP 5 AL 1 124V/248V | C23031800025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-03-18 | 66 | keep | 0 | Mar | 2023 | 4.4952e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-03-18 12:17 | 2023-03-18 14:50 | 70 | 2:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | M23031800089 | New_Event | Primary Wire Break | Include | Include | Equipment | 153 | 2023-03-18 | 10710 | keep | 0 | Mar | 2023 | 0.0072945 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-03-18 12:29 | 2023-03-18 14:26 | 10 | 1:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23031800008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 117 | 2023-03-18 | 1170 | keep | 0 | Mar | 2023 | 0.00079688 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-18 12:31 | 2023-03-18 23:44 | 2 | 11:13 | P | CRUCETA DEFECTUOSA O AVERIADA | SE SECCIONALIZO TRAMO Y SE REMPLAZO CRUCETA PARTIDA Y SE CERRO PUENTES ABIERTOS BY-230318-03 | B23031700128 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 673 | 2023-03-18 | 1346 | keep | 0 | Mar | 2023 | 0.00091675 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-18 12:32 | 2023-03-18 12:33 | 1648 | 0:01 | T | DESGANCHE | RECIERRE | R23031800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-18 | 1648 | keep | 0 | Mar | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-03-18 12:33 | 2023-03-18 14:22 | 150 | 1:49 | P | DESGANCHE | 1 X 100 EN C/L 1 X 40 EN RISER Y 1 X 15 EN BANCO DE XMRS | R23031800015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 109 | 2023-03-18 | 16350 | keep | 0 | Mar | 2023 | 0.011136 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-03-18 12:39 | 2023-03-18 14:03 | 10 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23031700421 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2023-03-18 | 840 | keep | 0 | Mar | 2023 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-18 12:42 | 2023-03-18 14:55 | 10 | 2:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO DEL XMR | B23031800043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 133 | 2023-03-18 | 1330 | keep | 0 | Mar | 2023 | 0.00090586 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-03-18 12:54 | 2023-03-18 16:10 | 1 | 3:16 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23031800061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-03-18 | 196 | keep | 0 | Mar | 2023 | 0.00013349 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-18 12:55 | 2023-03-18 13:47 | 1681 | 0:52 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR ENTRO EN SERVICIO 35% | B23031800019 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 52 | 2023-03-18 | 87412 | keep | 0 | Mar | 2023 | 0.059536 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-18 12:57 | 2023-03-18 12:58 | 4089 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23031800048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-18 | 4089 | keep | 0 | Mar | 2023 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BAYAMON | 2023-03-18 12:58 | 2023-03-18 19:39 | 106 | 6:41 | P | TERMINACION SOTERRADA AVERIADA | 1 X80 EN SU 4 SE LLEVO PISTOLA A SU LLUGAR EN T-46 | B23031800058 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 401 | 2023-03-18 | 42506 | keep | 0 | Mar | 2023 | 0.028951 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
SAN JUAN | 2023-03-18 13:03 | 2023-03-18 15:29 | 17 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | S23031800094 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2023-03-18 | 2482 | keep | 0 | Mar | 2023 | 0.0016905 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2023-03-18 13:07 | 2023-03-18 17:51 | 82 | 4:44 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L CRUCE X GLOBO | C23031800069 | New_Event | Damage From Public | Include | Include | Public | 284 | 2023-03-18 | 23288 | keep | 0 | Mar | 2023 | 0.015861 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
MAYAGÃœEZ | 2023-03-18 13:39 | 2023-03-18 15:30 | 60 | 1:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23031800106 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 111 | 2023-03-18 | 6660 | keep | 0 | Mar | 2023 | 0.0045361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-18 13:40 | 2023-03-18 17:51 | 8 | 4:11 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO SE ENERGIZO T20 | C23031800081 | New_Event | UG Cable Fault | Include | Include | Equipment | 251 | 2023-03-18 | 2008 | keep | 0 | Mar | 2023 | 0.0013676 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-18 13:41 | 2023-03-18 15:34 | 6 | 1:53 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR BAJANTE SECUNDARIO | R23031700068 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 113 | 2023-03-18 | 678 | keep | 0 | Mar | 2023 | 0.00046178 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-18 13:47 | 2023-03-18 14:07 | 1561 | 0:20 | P | CONDUCTOR ARRIADO O CRUZADO | BY-230318-01 SE SECCIONALIZO ALIMENTADOR ENTRO EN SERVICIO 60% | B23031800019 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 20 | 2023-03-18 | 31220 | keep | 0 | Mar | 2023 | 0.021264 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-18 13:53 | 2023-03-18 14:35 | 11 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIAS DEL XMR | B23031800056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2023-03-18 | 462 | keep | 0 | Mar | 2023 | 0.00031467 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-03-18 13:57 | 2023-03-18 13:58 | 643 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1530-09 | S2303180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-18 | 643 | keep | 0 | Mar | 2023 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
SAN JUAN | 2023-03-18 13:57 | 2023-03-18 13:58 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1530-07 | S2303180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-18 | 1310 | keep | 0 | Mar | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CAGUAS | 2023-03-18 13:58 | 2023-03-19 11:50 | 50 | 21:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C23031800084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1312 | 2023-03-18 | 65600 | keep | 0 | Mar | 2023 | 0.04468 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-03-18 14:00 | 2023-03-18 17:20 | 60 | 3:20 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23031800118 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 200 | 2023-03-18 | 12000 | keep | 0 | Mar | 2023 | 0.0081731 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-03-18 14:00 | 2023-03-18 14:45 | 8 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23031800126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-03-18 | 360 | keep | 0 | Mar | 2023 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-18 14:07 | 2023-03-18 15:52 | 960 | 1:45 | P | CONDUCTOR ARRIADO O CRUZADO | BY-230318-01 SE DESENREDO NEUTRAL PRIMARIO DE LINEA PRIMARIA A VARETA 100% EN SERVICIO | B23031800019 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 105 | 2023-03-18 | 100800 | keep | 0 | Mar | 2023 | 0.068654 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-18 14:15 | 2023-03-18 17:51 | 96 | 3:36 | P | CAUSAS EXTERNAS | 2 X 100 EN C/L CRUCE X GLOBO | C23031800086 | New_Event | Damage From Public | Include | Include | Public | 216 | 2023-03-18 | 20736 | keep | 0 | Mar | 2023 | 0.014123 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
MAYAGÃœEZ | 2023-03-18 14:18 | 2023-03-18 15:00 | 50 | 0:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CORTE DE LINEA HUBO DESGANCHE, HACER CAMINO PARA ACCESO AL AREA | M23031800122 | New_Event | Primary Wire Break | Include | Include | Equipment | 42 | 2023-03-18 | 2100 | keep | 0 | Mar | 2023 | 0.0014303 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-18 14:47 | 2023-03-18 14:48 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2303180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-18 | 4533 | keep | 0 | Mar | 2023 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2023-03-18 14:52 | 2023-03-19 09:18 | 91 | 18:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REEMPLAZO CAJA QUEMADA | B23031800061 | New_Event | Cutout Failure | Include | Include | Equipment | 1106 | 2023-03-18 | 100646 | keep | 0 | Mar | 2023 | 0.06855 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
HUMACAO | 2023-03-18 14:53 | 2023-03-18 17:39 | 88 | 2:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23031800093 | New_Event | Cutout Failure | Include | Include | Equipment | 166 | 2023-03-18 | 14608 | keep | 0 | Mar | 2023 | 0.0099494 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
MAYAGÃœEZ | 2023-03-18 15:00 | 2023-03-18 15:01 | 574 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 574 | keep | 0 | Mar | 2023 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2023-03-18 15:00 | 2023-03-18 15:01 | 2493 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 2493 | keep | 0 | Mar | 2023 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2023-03-18 15:00 | 2023-03-18 15:01 | 1415 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 1415 | keep | 0 | Mar | 2023 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2023-03-18 15:00 | 2023-03-18 15:01 | 1428 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 1428 | keep | 0 | Mar | 2023 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2023-03-18 15:00 | 2023-03-18 15:01 | 1036 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 1036 | keep | 0 | Mar | 2023 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2023-03-18 15:00 | 2023-03-18 15:01 | 382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800145 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 382 | keep | 0 | Mar | 2023 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-03-18 15:00 | 2023-03-18 15:01 | 39 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800145 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 39 | keep | 0 | Mar | 2023 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2023-03-18 15:00 | 2023-03-18 15:01 | 2366 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 2366 | keep | 0 | Mar | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2023-03-18 15:00 | 2023-03-18 15:01 | 1337 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 1337 | keep | 0 | Mar | 2023 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-03-18 15:00 | 2023-03-18 15:01 | 709 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23031800146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-18 | 709 | keep | 0 | Mar | 2023 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
MAYAGÃœEZ | 2023-03-18 15:01 | 2023-03-19 15:43 | 50 | 24:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CORTE DE LINEA HUBO DESGANCHE, HACER CAMINO PARA ACCESO AL AREA | M23031800122 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1482 | 2023-03-18 | 74100 | keep | 0 | Mar | 2023 | 0.050469 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-18 15:25 | 2023-03-18 16:30 | 6 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTORES SECUNDARIO | S23031800114 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-03-18 | 390 | keep | 0 | Mar | 2023 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-03-18 15:27 | 2023-03-18 16:27 | 100 | 1:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23031800147 | New_Event | Primary Wire Break | Include | Include | Equipment | 60 | 2023-03-18 | 6000 | keep | 0 | Mar | 2023 | 0.0040866 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-03-18 15:27 | 2023-03-18 18:15 | 60 | 2:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23031800068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-03-18 | 10080 | keep | 0 | Mar | 2023 | 0.0068654 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-03-18 15:31 | 2023-03-19 08:11 | 5 | 16:40 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR LINEA SECUNDARIA CRUZADA | C23031800103 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 1000 | 2023-03-18 | 5000 | keep | 0 | Mar | 2023 | 0.0034055 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-18 15:56 | 2023-03-19 11:03 | 30 | 19:07 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S23031800116 | New_Event | Primary Wire Break | Include | Include | Equipment | 1147 | 2023-03-18 | 34410 | keep | 0 | Mar | 2023 | 0.023436 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-03-18 16:08 | 2023-03-18 16:09 | 1702 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | C23031800117 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-18 | 1702 | keep | 0 | Mar | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-03-18 16:09 | 2023-03-18 18:15 | 65 | 2:06 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23031800119 | 1st_after_momentary | Animals | Include | Include | Wildlife | 126 | 2023-03-18 | 8190 | keep | 0 | Mar | 2023 | 0.0055782 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
YAUCO | 2023-03-18 16:10 | 2023-03-18 17:51 | 40 | 1:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23031800162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-03-18 | 4040 | keep | 0 | Mar | 2023 | 0.0027516 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-03-18 16:32 | 2023-03-18 21:57 | 35 | 5:25 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S23031800118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2023-03-18 | 11375 | keep | 0 | Mar | 2023 | 0.0077475 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-03-18 16:33 | 2023-03-18 16:35 | 996 | 0:02 | T | ANIMAL | DISPARO INTERRUPTOR SE PROBO POR CONTROL QUEDO EN SERVICIO | S23031800119 | New_Event | Animals | Include | Include | Wildlife | 2 | 2023-03-18 | 1992 | keep | 0 | Mar | 2023 | 0.0013567 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
SAN JUAN | 2023-03-18 16:35 | 2023-03-18 18:22 | 156 | 1:47 | P | ANIMAL | 1 X 80 Y 2 X 65 EN C/L CRUCE POR AVE | S23031800120 | 1st_after_momentary | Animals | Include | Include | Wildlife | 107 | 2023-03-18 | 16692 | keep | 0 | Mar | 2023 | 0.011369 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
SAN JUAN | 2023-03-18 16:42 | 2023-03-18 19:11 | 150 | 2:29 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | S23031800121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-03-18 | 22350 | keep | 0 | Mar | 2023 | 0.015222 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-03-18 16:45 | 2023-03-18 18:30 | 30 | 1:45 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23031800173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2023-03-18 | 3150 | keep | 0 | Mar | 2023 | 0.0021455 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-03-18 17:33 | 2023-03-18 19:20 | 50 | 1:47 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 80 EN C/L SE FIJO LINEA A AISLADOR | P23031800080 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 107 | 2023-03-18 | 5350 | keep | 0 | Mar | 2023 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-18 17:37 | 2023-03-18 23:26 | 177 | 5:49 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23031800076 | New_Event | Animals | Include | Include | Wildlife | 349 | 2023-03-18 | 61773 | keep | 0 | Mar | 2023 | 0.042073 | 0.00012055 | Sustained | FALSE | FALSE | Not_TMED_Event | 177
ARECIBO | 2023-03-18 17:38 | 2023-03-18 19:26 | 75 | 1:48 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23031800077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-03-18 | 8100 | keep | 0 | Mar | 2023 | 0.0055169 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2023-03-18 17:51 | 2023-03-18 17:53 | 6197 | 0:02 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | C2303180000X | Additional_clients | UG Cable Fault | Include | Include | Equipment | 2 | 2023-03-18 | 12394 | keep | 0 | Mar | 2023 | 0.0084415 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-18 17:53 | 2023-03-18 22:05 | 8 | 4:12 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO SE ENERGIZO T20 | C23031800081 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 252 | 2023-03-18 | 2016 | keep | 0 | Mar | 2023 | 0.0013731 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-18 17:53 | 2023-03-18 18:23 | 96 | 0:30 | P | CAUSAS EXTERNAS | 2 X 100 EN C/L CRUCE X GLOBO | C23031800086 | Partial_restoration | Damage From Public | Include | Include | Public | 30 | 2023-03-18 | 2880 | keep | 0 | Mar | 2023 | 0.0019616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-18 18:12 | 2023-03-18 20:27 | 35 | 2:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031800080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-03-18 | 4725 | keep | 0 | Mar | 2023 | 0.0032182 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-03-18 18:26 | 2023-03-18 20:31 | 120 | 2:05 | P | ANIMAL | 1 X 100 EN C/L SE REEMPLAZO PORTAFUSIBLE CRUCE X AVE | C23031800144 | New_Event | Animals | Include | Include | Wildlife | 125 | 2023-03-18 | 15000 | keep | 0 | Mar | 2023 | 0.010216 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-03-18 18:49 | 2023-03-19 08:55 | 7 | 14:06 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23031800080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 846 | 2023-03-18 | 5922 | keep | 0 | Mar | 2023 | 0.0040334 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-18 19:39 | 2023-03-18 19:40 | 4089 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2303180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-18 | 4089 | keep | 0 | Mar | 2023 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BAYAMON | 2023-03-18 19:40 | 2023-03-18 22:12 | 106 | 2:32 | P | TERMINACION SOTERRADA AVERIADA | 1 X80 EN SU 4 SE LLEVO PISTOLA A SU LLUGAR EN T-46 | B23031800058 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 152 | 2023-03-18 | 16112 | keep | 0 | Mar | 2023 | 0.010974 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-03-18 19:46 | 2023-03-19 11:55 | 7 | 16:09 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23031800085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 969 | 2023-03-18 | 6783 | keep | 0 | Mar | 2023 | 0.0046199 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-03-18 19:51 | 2023-03-18 23:45 | 100 | 3:54 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA EN EL PISO | P23031800103 | New_Event | Primary Wire Break | Include | Include | Equipment | 234 | 2023-03-18 | 23400 | keep | 0 | Mar | 2023 | 0.015938 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-03-18 20:05 | 2023-03-19 11:32 | 3 | 15:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE CONECTORES QUEMADOS | C23031800160 | New_Event | Secondary Wire Break | Include | Include | Equipment | 927 | 2023-03-18 | 2781 | keep | 0 | Mar | 2023 | 0.0018941 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-03-18 21:18 | 2023-03-19 10:15 | 8 | 12:57 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | M23031800204 | New_Event | Primary Wire Break | Include | Include | Equipment | 777 | 2023-03-18 | 6216 | keep | 0 | Mar | 2023 | 0.0042337 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-18 22:06 | 2023-03-19 14:53 | 75 | 16:47 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23031800167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1007 | 2023-03-18 | 75525 | keep | 0 | Mar | 2023 | 0.05144 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2023-03-18 22:17 | 2023-03-19 08:29 | 35 | 10:12 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23031800087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 612 | 2023-03-18 | 21420 | keep | 0 | Mar | 2023 | 0.014589 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2023-03-18 22:36 | 2023-03-19 04:32 | 214 | 5:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO DE PORTAFUSIBLE | C23031800169 | New_Event | Cutout Failure | Include | Include | Equipment | 356 | 2023-03-18 | 76184 | keep | 0 | Mar | 2023 | 0.051889 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
BAYAMON | 2023-03-18 22:43 | 2023-03-18 22:44 | 492 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-18 | 492 | keep | 0 | Mar | 2023 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
CAGUAS | 2023-03-18 23:14 | 2023-03-19 14:48 | 1 | 15:34 | P | ANIMAL | 2 X 10 EN BANCO DE XMR NIDO DE AVE | C23031800173 | New_Event | Animals | Include | Include | Wildlife | 934 | 2023-03-18 | 934 | keep | 0 | Mar | 2023 | 0.00063614 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-19 00:06 | 2023-03-19 12:00 | 175 | 11:54 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23031900018 | New_Event | Primary Wire Break | Include | Include | Equipment | 714 | 2023-03-19 | 124950 | keep | 0 | Mar | 2023 | 0.085103 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
VEGA BAJA | 2023-03-19 00:50 | 2023-03-19 07:30 | 6 | 6:40 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23031900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 400 | 2023-03-19 | 2400 | keep | 0 | Mar | 2023 | 0.0016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-03-19 01:00 | 2023-03-19 10:03 | 15 | 9:03 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO PUENTE DE LINEA A CAJA, EVENTO TRANSFERIDO DE PONCE | P23031900003 | New_Event | Primary Wire Break | Include | Include | Equipment | 543 | 2023-03-19 | 8145 | keep | 0 | Mar | 2023 | 0.0055475 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-03-19 01:30 | 2023-03-19 02:39 | 2531 | 1:09 | P | CABLE SOTERRADO AVERIADO | 50% SU CARGA TRANSFERIDA AL 1619-02 CON SJ-230319-50 SE ABRIO EN SU 1-E Y SE CERRO BKR 98% EN SERVICIO ALAMBRE QUEMADO #2 | R23031900002 | New_Event | UG Cable Fault | Include | Include | Equipment | 69 | 2023-03-19 | 174639 | keep | 0 | Mar | 2023 | 0.11895 | 0.0017239 | Sustained | FALSE | FALSE | Not_TMED_Event | 2531
CANOVANAS | 2023-03-19 02:39 | 2023-03-19 12:35 | 51 | 9:56 | P | CABLE SOTERRADO AVERIADO | SWF SJ-230319-50 SE REMPLAZO PROVICIONAL AEREO 100% EN SERVICIO | R23031900002 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 596 | 2023-03-19 | 30396 | keep | 0 | Mar | 2023 | 0.020703 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-19 02:40 | 2023-03-19 09:32 | 22 | 6:52 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN C/L | S23031900003 | New_Event | Primary Wire Break | Include | Include | Equipment | 412 | 2023-03-19 | 9064 | keep | 0 | Mar | 2023 | 0.0061734 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2023-03-19 03:00 | 2023-03-19 08:24 | 1336 | 5:24 | T | ARBOL SOBRE LINEA | ARBOL CRUZO FASES INTERRUPTOR CERRADO MANUAL ELECTRICO (RTU DOWN) | M23031900008 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 324 | 2023-03-19 | 432864 | keep | 0 | Mar | 2023 | 0.29482 | 0.00090994 | Sustained | FALSE | FALSE | Not_TMED_Event | 1336
BARRANQUITAS | 2023-03-19 05:30 | 2023-03-19 08:00 | 100 | 2:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C23031900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-03-19 | 15000 | keep | 0 | Mar | 2023 | 0.010216 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-03-19 05:37 | 2023-03-19 17:23 | 5 | 11:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PRIMARIO Y SE CERRO PUENTES ABIERTOS HACIA AVERIA | P23031900006 | New_Event | Primary Wire Break | Include | Include | Equipment | 706 | 2023-03-19 | 3530 | keep | 0 | Mar | 2023 | 0.0024043 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-03-19 05:48 | 2023-03-19 08:35 | 1 | 2:47 | P | NO SE REPORTO CAUSA | 1 X 15 EN C/L | R23031900039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2023-03-19 | 167 | keep | 0 | Mar | 2023 | 0.00011374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-19 07:00 | 2023-03-19 11:35 | 40 | 4:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR REQUIERE DESGANCHE | M23031900078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2023-03-19 | 11000 | keep | 0 | Mar | 2023 | 0.007492 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-03-19 07:28 | 2023-03-19 09:55 | 50 | 2:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M23031900033 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 147 | 2023-03-19 | 7350 | keep | 0 | Mar | 2023 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-19 07:32 | 2023-03-19 11:28 | 3 | 3:56 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | R23031900046 | New_Event | Primary Wire Break | Include | Include | Equipment | 236 | 2023-03-19 | 708 | keep | 0 | Mar | 2023 | 0.00048222 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-03-19 07:37 | 2023-03-19 10:31 | 12 | 2:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN XMR | B23031800004 | New_Event | Cutout Failure | Include | Include | Equipment | 174 | 2023-03-19 | 2088 | keep | 0 | Mar | 2023 | 0.0014221 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-03-19 07:41 | 2023-03-19 09:06 | 30 | 1:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23031900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-03-19 | 2550 | keep | 0 | Mar | 2023 | 0.0017368 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-03-19 07:47 | 2023-03-19 09:48 | 18 | 2:01 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE HACIA TRANSFORMADOR SULFATADO | C23031900013 | New_Event | Primary Wire Break | Include | Include | Equipment | 121 | 2023-03-19 | 2178 | keep | 0 | Mar | 2023 | 0.0014834 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2023-03-19 07:49 | 2023-03-19 07:55 | 6 | 0:06 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23031900008 | New_Event | Animals | Include | Include | Wildlife | 6 | 2023-03-19 | 36 | keep | 0 | Mar | 2023 | 2.4519e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-19 08:13 | 2023-03-19 10:51 | 18 | 2:38 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEAS | B23031900006 | New_Event | Animals | Include | Include | Wildlife | 158 | 2023-03-19 | 2844 | keep | 0 | Mar | 2023 | 0.001937 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2023-03-19 08:28 | 2023-03-19 08:29 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23031900009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-19 | 1945 | keep | 0 | Mar | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
AGUADILLA | 2023-03-19 08:36 | 2023-03-19 12:55 | 30 | 4:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | M23031900056 | New_Event | Primary Wire Break | Include | Include | Equipment | 259 | 2023-03-19 | 7770 | keep | 0 | Mar | 2023 | 0.0052921 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-19 09:05 | 2023-03-19 14:10 | 2 | 5:05 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | C23031900026 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 305 | 2023-03-19 | 610 | keep | 0 | Mar | 2023 | 0.00041547 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-03-19 09:37 | 2023-03-19 15:52 | 60 | 6:15 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23031900034 | New_Event | Animals | Include | Include | Wildlife | 375 | 2023-03-19 | 22500 | keep | 0 | Mar | 2023 | 0.015325 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-19 09:37 | 2023-03-19 12:48 | 6 | 3:11 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO CONDUCOR DEL SUELO | C23031900022 | New_Event | Primary Wire Break | Include | Include | Equipment | 191 | 2023-03-19 | 1146 | keep | 0 | Mar | 2023 | 0.00078054 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-03-19 09:40 | 2023-03-19 11:30 | 8 | 1:50 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M23031900099 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 110 | 2023-03-19 | 880 | keep | 0 | Mar | 2023 | 0.00059936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-03-19 10:01 | 2023-03-19 12:55 | 20 | 2:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M23031900067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2023-03-19 | 3480 | keep | 0 | Mar | 2023 | 0.0023702 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-03-19 10:15 | 2023-03-19 11:25 | 10 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A23031900011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-03-19 | 700 | keep | 0 | Mar | 2023 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-03-19 10:26 | 2023-03-19 12:25 | 207 | 1:59 | T | CONDUCTOR ARRIADO O CRUZADO | SE ENCONTRO CRUCE DE LINEAS PRIMARIAS CON SECUNDARIA LLEVA LA CARGA DEL 5403-02 | P23031900030 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 119 | 2023-03-19 | 24633 | keep | 0 | Mar | 2023 | 0.016777 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
YAUCO | 2023-03-19 10:26 | 2023-03-19 12:25 | 286 | 1:59 | T | ALIMENTADOR AMARRADO | SE ENCONTRO CRUCE DE LINEAS PRIMARIA DEL 5403-01 CON SECUNDARIA | P23031900030 | New_Event | Feeder Load Transferred | Include | Include | Other | 119 | 2023-03-19 | 34034 | keep | 0 | Mar | 2023 | 0.02318 | 0.00019479 | Sustained | FALSE | FALSE | Not_TMED_Event | 286
BAYAMON | 2023-03-19 10:40 | 2023-03-20 00:47 | 15 | 14:07 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO T-651 SE DEJO PENDIENTE AVERIA T-652 A T-658 | B23031900033 | New_Event | UG Cable Fault | Include | Include | Equipment | 847 | 2023-03-19 | 12705 | keep | 0 | Mar | 2023 | 0.0086533 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-03-19 10:48 | 2023-03-19 12:30 | 60 | 1:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031900016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-03-19 | 6120 | keep | 0 | Mar | 2023 | 0.0041683 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-03-19 10:58 | 2023-03-19 12:19 | 41 | 1:21 | P | CAUSAS EXTERNAS | SE RETIRO GLOBO METALICO Y 1 X 65 EN C/L | B23031900035 | New_Event | Damage From Public | Include | Include | Public | 81 | 2023-03-19 | 3321 | keep | 0 | Mar | 2023 | 0.0022619 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2023-03-19 11:00 | 2023-03-19 18:22 | 40 | 7:22 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23031900037 | New_Event | Animals | Include | Include | Wildlife | 442 | 2023-03-19 | 17680 | keep | 0 | Mar | 2023 | 0.012042 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-19 11:03 | 2023-03-19 11:04 | 766 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1909-07 LLEVANDO 50% 1709-03 | S23031900017 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-19 | 766 | keep | 0 | Mar | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-03-19 11:03 | 2023-03-19 11:04 | 1139 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR 1909-07 LLEVANDO 50% 1709-03 | S23031900017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-19 | 1139 | keep | 0 | Mar | 2023 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2023-03-19 11:04 | 2023-03-19 18:26 | 839 | 7:22 | P | DESGANCHE | 1 X 80 C/L DESGANCHE | S23031900019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 442 | 2023-03-19 | 370838 | keep | 0 | Mar | 2023 | 0.25258 | 0.00057144 | Sustained | FALSE | FALSE | Not_TMED_Event | 839
HUMACAO | 2023-03-19 11:51 | 2023-03-19 13:42 | 90 | 1:51 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C23031900050 | New_Event | Animals | Include | Include | Wildlife | 111 | 2023-03-19 | 9990 | keep | 0 | Mar | 2023 | 0.0068041 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2023-03-19 11:59 | 2023-03-19 14:30 | 20 | 2:31 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-03-19 | 3020 | keep | 0 | Mar | 2023 | 0.0020569 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-19 12:00 | 2023-03-19 19:38 | 36 | 7:38 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | B23031900057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 458 | 2023-03-19 | 16488 | keep | 0 | Mar | 2023 | 0.01123 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2023-03-19 12:05 | 2023-03-19 12:06 | 638 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2303190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-19 | 638 | keep | 0 | Mar | 2023 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
GUAYAMA | 2023-03-19 12:19 | 2023-03-19 13:55 | 73 | 1:36 | P | CAUSAS EXTERNAS | CAMION IMPACTO NEUTRAL COMUN Y CRUZARON FASES 1 X 80 EN CORTE DE LINEA | P23031900031 | New_Event | Damage From Public | Include | Include | Public | 96 | 2023-03-19 | 7008 | keep | 0 | Mar | 2023 | 0.0047731 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
PONCE | 2023-03-19 12:29 | 2023-03-19 13:31 | 1157 | 1:02 | T | DESGANCHE | ALIMENTADOR FUERA DEBIDO A DESGANCHE | P23031900032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-03-19 | 71734 | keep | 0 | Mar | 2023 | 0.048858 | 0.00078803 | Sustained | FALSE | FALSE | Not_TMED_Event | 1157
SAN JUAN | 2023-03-19 12:45 | 2023-03-19 15:31 | 60 | 2:46 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | S23031900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-03-19 | 9960 | keep | 0 | Mar | 2023 | 0.0067837 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-19 12:48 | 2023-03-20 14:08 | 4 | 25:20 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C23031900033 | New_Event | Primary Wire Break | Include | Include | Equipment | 1520 | 2023-03-19 | 6080 | keep | 0 | Mar | 2023 | 0.0041411 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-03-19 12:52 | 2023-03-19 13:12 | 6 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23031900031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-03-19 | 120 | keep | 0 | Mar | 2023 | 8.1731e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-03-19 13:32 | 2023-03-19 16:35 | 15 | 3:03 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | R23031900106 | New_Event | Primary Wire Break | Include | Include | Equipment | 183 | 2023-03-19 | 2745 | keep | 0 | Mar | 2023 | 0.0018696 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-03-19 13:36 | 2023-03-19 13:37 | 1952 | 0:01 | T | DESGANCHE | RECIERRE | P23031900039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-19 | 1952 | keep | 0 | Mar | 2023 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
YAUCO | 2023-03-19 13:42 | 2023-03-19 19:55 | 80 | 6:13 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEAS PRIMARIAS | M23031900096 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 373 | 2023-03-19 | 29840 | keep | 0 | Mar | 2023 | 0.020324 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-03-19 13:49 | 2023-03-19 16:45 | 50 | 2:56 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P23031900043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-03-19 | 8800 | keep | 0 | Mar | 2023 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-03-19 13:54 | 2023-03-19 14:13 | 50 | 0:19 | P | DESGANCHE | SE ABRE C/L PARA RETIRAR RAMA SOBRE LINEAS | P23031900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 19 | 2023-03-19 | 950 | keep | 0 | Mar | 2023 | 0.00064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-03-19 13:55 | 2023-03-19 15:24 | 1952 | 1:29 | T | DESGANCHE | SE CERO BKR DISPARO POR DESGANCHE EN VARIOS PUNTOS Y FUERTES VIENTOS | P23031900045 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-03-19 | 173728 | keep | 0 | Mar | 2023 | 0.11833 | 0.0013295 | Sustained | FALSE | FALSE | Not_TMED_Event | 1952
BAYAMON | 2023-03-19 14:05 | 2023-03-19 17:34 | 177 | 3:29 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23031900072 | New_Event | Animals | Include | Include | Wildlife | 209 | 2023-03-19 | 36993 | keep | 0 | Mar | 2023 | 0.025196 | 0.00012055 | Sustained | FALSE | FALSE | Not_TMED_Event | 177
BARRANQUITAS | 2023-03-19 14:05 | 2023-03-19 15:12 | 25 | 1:07 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23031900058 | New_Event | Animals | Include | Include | Wildlife | 67 | 2023-03-19 | 1675 | keep | 0 | Mar | 2023 | 0.0011408 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-03-19 14:13 | 2023-03-19 18:53 | 30 | 4:40 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23031900059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2023-03-19 | 8400 | keep | 0 | Mar | 2023 | 0.0057212 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-03-19 14:19 | 2023-03-19 14:20 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO CAUSA | P23031900054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-19 | 2039 | keep | 0 | Mar | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
BAYAMON | 2023-03-19 14:21 | 2023-03-19 20:41 | 15 | 6:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23031900074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 380 | 2023-03-19 | 5700 | keep | 0 | Mar | 2023 | 0.0038822 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-03-19 14:24 | 2023-03-19 15:50 | 75 | 1:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23031900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-03-19 | 6450 | keep | 0 | Mar | 2023 | 0.0043931 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-03-19 14:33 | 2023-03-19 16:26 | 3 | 1:53 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23031900067 | New_Event | Animals | Include | Include | Wildlife | 113 | 2023-03-19 | 339 | keep | 0 | Mar | 2023 | 0.00023089 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-19 14:35 | 2023-03-19 14:36 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2303190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-19 | 870 | keep | 0 | Mar | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2023-03-19 14:36 | 2023-03-19 14:37 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2303190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-19 | 652 | keep | 0 | Mar | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
SAN JUAN | 2023-03-19 14:49 | 2023-03-19 19:19 | 23 | 4:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S23031900037 | New_Event | Cutout Failure | Include | Include | Equipment | 270 | 2023-03-19 | 6210 | keep | 0 | Mar | 2023 | 0.0042296 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
MAYAGÃœEZ | 2023-03-19 14:50 | 2023-03-19 15:10 | 10 | 0:20 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO | M23031900073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 20 | 2023-03-19 | 200 | keep | 0 | Mar | 2023 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-03-19 15:13 | 2023-03-19 15:56 | 36 | 0:43 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23031900074 | Additional_clients | Animals | Include | Include | Wildlife | 43 | 2023-03-19 | 1548 | keep | 0 | Mar | 2023 | 0.0010543 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-19 15:25 | 2023-03-19 16:50 | 7 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTES SECUNDARIOS DEL XMR | B23031900081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2023-03-19 | 595 | keep | 0 | Mar | 2023 | 0.00040525 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-19 15:39 | 2023-03-19 17:06 | 12 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO PUENTE ABIERTO SECUNDARIO | S23031900039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2023-03-19 | 1044 | keep | 0 | Mar | 2023 | 0.00071106 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-19 15:39 | 2023-03-19 17:14 | 60 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | C23031900076 | New_Event | Primary Wire Break | Include | Include | Equipment | 95 | 2023-03-19 | 5700 | keep | 0 | Mar | 2023 | 0.0038822 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-03-19 15:39 | 2023-03-20 09:45 | 100 | 18:06 | P | FUEGO | 2 X 50 EN CORTE DE LINEA POR FUEGO FORRESTAL | M23031900109 | New_Event | Fire | Include | Include | Public | 1086 | 2023-03-19 | 108600 | keep | 0 | Mar | 2023 | 0.073967 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-19 16:05 | 2023-03-19 21:46 | 281 | 5:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER 1 X 20 EN SU 6 | S23031900041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 341 | 2023-03-19 | 95821 | keep | 0 | Mar | 2023 | 0.065263 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
YAUCO | 2023-03-19 16:08 | 2023-03-19 17:24 | 100 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN C/L MAL TIEMPO VIENTOS | P23031900064 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2023-03-19 | 7600 | keep | 0 | Mar | 2023 | 0.0051763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-03-19 16:17 | 2023-03-19 18:13 | 4 | 1:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | M23031900113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2023-03-19 | 464 | keep | 0 | Mar | 2023 | 0.00031603 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-03-19 16:47 | 2023-03-19 19:16 | 20 | 2:29 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | R23031900108 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-03-19 | 2980 | keep | 0 | Mar | 2023 | 0.0020297 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-03-19 16:56 | 2023-03-19 19:28 | 54 | 2:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | R23031900109 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2023-03-19 | 8208 | keep | 0 | Mar | 2023 | 0.0055904 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
AGUADILLA | 2023-03-19 17:22 | 2023-03-20 09:07 | 3 | 15:45 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR FUSIBLE PODRIDO | M23031900117 | New_Event | Other Causes | Include | Include | Other | 945 | 2023-03-19 | 2835 | keep | 0 | Mar | 2023 | 0.0019309 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-03-19 17:31 | 2023-03-19 18:32 | 15 | 1:01 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1 X 30 EN CORTES DE LINEA SE REEMPLAZO PARARRAYO | R23031900117 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 61 | 2023-03-19 | 915 | keep | 0 | Mar | 2023 | 0.0006232 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-03-19 17:40 | 2023-03-19 18:22 | 8 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA AVERIADA | M23031900108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2023-03-19 | 336 | keep | 0 | Mar | 2023 | 0.00022885 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-03-19 18:00 | 2023-03-20 07:39 | 25 | 13:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P23031900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 819 | 2023-03-19 | 20475 | keep | 0 | Mar | 2023 | 0.013945 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-03-19 18:32 | 2023-03-19 20:50 | 15 | 2:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | M23031900123 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2023-03-19 | 2070 | keep | 0 | Mar | 2023 | 0.0014099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-19 19:12 | 2023-03-19 21:57 | 15 | 2:45 | P | ANIMAL | 1 X 15 TRANSFORMADOR AVE CRUZO FASE | B23031900116 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-03-19 | 2475 | keep | 0 | Mar | 2023 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-03-19 19:22 | 2023-03-20 09:28 | 1 | 14:06 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN RISER Y 3 X 20 EN GABINETE PROBLEMA INTERNO EN LAS BOMBAS | R23031900122 | New_Event | Customer-Related Interruption | Include | Include | Public | 846 | 2023-03-19 | 846 | keep | 0 | Mar | 2023 | 0.00057621 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-19 19:39 | 2023-03-19 19:40 | 4830 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 800 CLIENTES X 3205-07 | C23031900098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-19 | 4830 | keep | 0 | Mar | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
CANOVANAS | 2023-03-19 20:02 | 2023-03-20 09:37 | 14 | 13:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 2 X 65 EN C/L | R23031900123 | New_Event | Cutout Failure | Include | Include | Equipment | 815 | 2023-03-19 | 11410 | keep | 0 | Mar | 2023 | 0.0077713 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2023-03-19 20:10 | 2023-03-20 10:44 | 34 | 14:34 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23031900099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 874 | 2023-03-19 | 29716 | keep | 0 | Mar | 2023 | 0.020239 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
VEGA BAJA | 2023-03-19 21:15 | 2023-03-20 11:01 | 8 | 13:46 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN C/L TOMA CRUZADA DEL CLIENTE SE DEJO FUERA PARA QUE REPAREN | B23031900126 | New_Event | Customer-Related Interruption | Include | Include | Public | 826 | 2023-03-19 | 6608 | keep | 0 | Mar | 2023 | 0.0045007 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-19 21:23 | 2023-03-19 21:24 | 679 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 85% 1705-05 | B2303190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-19 | 679 | keep | 0 | Mar | 2023 | 0.00046246 | 0.00046246 | Momentary | FALSE | FALSE | Not_TMED_Event | 679
BAYAMON | 2023-03-19 21:23 | 2023-03-19 21:24 | 637 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1705-02 | B2303190000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-19 | 637 | keep | 0 | Mar | 2023 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
GUAYAMA | 2023-03-19 21:41 | 2023-03-20 08:10 | 10 | 10:29 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR ANIMAL | P23031900083 | New_Event | Animals | Include | Include | Wildlife | 629 | 2023-03-19 | 6290 | keep | 0 | Mar | 2023 | 0.0042841 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-19 21:59 | 2023-03-20 02:13 | 15 | 4:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE EVENTO TRANSFERIDO CAGUAS A TOA BAJA | C23031900103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2023-03-19 | 3810 | keep | 0 | Mar | 2023 | 0.002595 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-03-19 22:07 | 2023-03-19 22:08 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 800 CLIENTES DEL 2402-02 | R23031900131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-19 | 1648 | keep | 0 | Mar | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-03-19 22:07 | 2023-03-19 22:08 | 800 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 2302-03 LLEVA 800 CLIENTES DEL 2402-02 | R23031900131 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-19 | 800 | keep | 0 | Mar | 2023 | 0.00054488 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2023-03-19 22:57 | 2023-03-20 00:19 | 40 | 1:22 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA 1 X 30 EN CORTE DE LINEA SE ELIMINO PARARRAYO REF. B23031900113 | B23032000001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 82 | 2023-03-19 | 3280 | keep | 0 | Mar | 2023 | 0.002234 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-19 23:10 | 2023-03-20 10:16 | 20 | 11:06 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEA | M23031900145 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 666 | 2023-03-19 | 13320 | keep | 0 | Mar | 2023 | 0.0090722 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-19 23:49 | 2023-03-20 03:11 | 30 | 3:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | B23031900140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-03-19 | 6060 | keep | 0 | Mar | 2023 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-20 00:47 | 2023-03-20 19:15 | 80 | 18:28 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO @ T-651 | B23031900033 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1108 | 2023-03-20 | 88640 | keep | 0 | Mar | 2023 | 0.060372 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-03-20 00:54 | 2023-03-20 04:35 | 390 | 3:41 | T | PROTECCION DEFECTUOSA | AC DE CARGA DEL INTERRUPTOR TRIPEADO | M23032000002 | New_Event | Protection Miscoordination | Include | Include | Other | 221 | 2023-03-20 | 86190 | keep | 0 | Mar | 2023 | 0.058704 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
CANOVANAS | 2023-03-20 01:28 | 2023-03-20 08:21 | 25 | 6:53 | P | TRANSFORMADOR AVERIADO | SE LIMPIO AISLACION EN T 39 Y 1X 30 EN AEREO PROVISIONAL | R23032000002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 413 | 2023-03-20 | 10325 | keep | 0 | Mar | 2023 | 0.0070323 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-03-20 01:46 | 2023-03-20 09:40 | 50 | 7:54 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE ELIMINO PARARRAYO CRUZADO | M23032000005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 474 | 2023-03-20 | 23700 | keep | 0 | Mar | 2023 | 0.016142 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-03-20 03:02 | 2023-03-20 08:40 | 50 | 5:38 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE DESENREDO LINEAS | M23032000008 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 338 | 2023-03-20 | 16900 | keep | 0 | Mar | 2023 | 0.011511 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-20 03:18 | 2023-03-20 08:59 | 8 | 5:41 | P | CONDUCTOR ARRIADO O CRUZADO | SE DESPEGO PUENTE PRIMARIO A NEUTRAL EN C/L Y SE REPUSO 1 X 20 EN C/L | R23032000003 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 341 | 2023-03-20 | 2728 | keep | 0 | Mar | 2023 | 0.001858 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-03-20 04:40 | 2023-03-20 10:54 | 66 | 6:14 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C23032000002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 374 | 2023-03-20 | 24684 | keep | 0 | Mar | 2023 | 0.016812 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2023-03-20 05:08 | 2023-03-20 16:37 | 15 | 11:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REPARO SECUNDARIA | B23032000005 | New_Event | Secondary Wire Break | Include | Include | Equipment | 689 | 2023-03-20 | 10335 | keep | 0 | Mar | 2023 | 0.0070391 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-03-20 05:32 | 2023-03-20 18:34 | 498 | 13:02 | P | CAUSAS EXTERNAS | SE REMPLAZO POSTE Y SE CERRO CL POSTE PARTIDO POR IMPACTO DE VEHICULO PESADO | A23032000005 | New_Event | Damage From Public | Include | Include | Public | 782 | 2023-03-20 | 389436 | keep | 0 | Mar | 2023 | 0.26524 | 0.00033919 | Sustained | FALSE | FALSE | Not_TMED_Event | 498
MAYAGÃœEZ | 2023-03-20 06:07 | 2023-03-20 09:10 | 30 | 3:03 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M23032000011 | New_Event | Animals | Include | Include | Wildlife | 183 | 2023-03-20 | 5490 | keep | 0 | Mar | 2023 | 0.0037392 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-20 06:30 | 2023-03-20 13:01 | 15 | 6:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | M23032000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 391 | 2023-03-20 | 5865 | keep | 0 | Mar | 2023 | 0.0039946 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-03-20 06:41 | 2023-03-20 08:41 | 50 | 2:00 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO CONECTOR QUEMADO EN PUENTE PRIMARIO 1 X 50 EN CORTE DE LINEA | P23032000009 | New_Event | Primary Wire Break | Include | Include | Equipment | 120 | 2023-03-20 | 6000 | keep | 0 | Mar | 2023 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-03-20 07:02 | 2023-03-20 13:16 | 5 | 6:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA FUERTES VIENTOS | M23032000013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 374 | 2023-03-20 | 1870 | keep | 0 | Mar | 2023 | 0.0012736 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-03-20 07:18 | 2023-03-20 09:25 | 50 | 2:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23032000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-03-20 | 6350 | keep | 0 | Mar | 2023 | 0.004325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-20 07:26 | 2023-03-20 13:39 | 1 | 6:13 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER 1 X 25 EN TRANSCLOSURE | B23032000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 373 | 2023-03-20 | 373 | keep | 0 | Mar | 2023 | 0.00025405 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-20 07:37 | 2023-03-20 11:28 | 60 | 3:51 | P | ANIMAL | 1X80 EN C/L, 1X40 EN OTRO C/L CRUCE POR AVE | S23032000008 | New_Event | Animals | Include | Include | Wildlife | 231 | 2023-03-20 | 13860 | keep | 0 | Mar | 2023 | 0.00944 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-20 07:38 | 2023-03-20 14:13 | 47 | 6:35 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C23032000008 | New_Event | Animals | Include | Include | Wildlife | 395 | 2023-03-20 | 18565 | keep | 0 | Mar | 2023 | 0.012645 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-03-20 07:55 | 2023-03-20 13:19 | 10 | 5:24 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23032000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2023-03-20 | 3240 | keep | 0 | Mar | 2023 | 0.0022067 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-20 08:14 | 2023-03-20 12:37 | 2 | 4:23 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR POR SALITRE | A23032000033 | New_Event | Other Causes | Include | Include | Other | 263 | 2023-03-20 | 526 | keep | 0 | Mar | 2023 | 0.00035826 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-03-20 08:23 | 2023-03-20 10:55 | 1339 | 2:32 | T | ALIMENTADOR AMARRADO | CARGA POR 6601-02 | M23032000026 | New_Event | Feeder Load Transferred | Include | Include | Other | 152 | 2023-03-20 | 203528 | keep | 0 | Mar | 2023 | 0.13862 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-03-20 08:23 | 2023-03-20 10:55 | 470 | 2:32 | T | PARARRAYOS DEFECTUOSO | SE RETIRO PARARRAYOS CRUZADO | M23032000026 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 152 | 2023-03-20 | 71440 | keep | 0 | Mar | 2023 | 0.048657 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
BAYAMON | 2023-03-20 08:27 | 2023-03-20 16:41 | 10 | 8:14 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO DE LINEA A CAJA | B23032000014 | New_Event | Primary Wire Break | Include | Include | Equipment | 494 | 2023-03-20 | 4940 | keep | 0 | Mar | 2023 | 0.0033646 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-20 08:31 | 2023-03-20 12:18 | 2 | 3:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REPARO SECUNDARIA | B23032000015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 227 | 2023-03-20 | 454 | keep | 0 | Mar | 2023 | 0.00030922 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-03-20 08:38 | 2023-03-20 15:25 | 30 | 6:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO VIENTOS | P23032000016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 407 | 2023-03-20 | 12210 | keep | 0 | Mar | 2023 | 0.0083162 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-20 08:44 | 2023-03-20 12:49 | 7 | 4:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23032000017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 245 | 2023-03-20 | 1715 | keep | 0 | Mar | 2023 | 0.0011681 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-03-20 08:49 | 2023-03-20 12:27 | 7 | 3:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CERRO PUENTE ABIERTO EN LINEA SECUNDARIA | C23032000019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 218 | 2023-03-20 | 1526 | keep | 0 | Mar | 2023 | 0.0010394 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-03-20 09:04 | 2023-03-20 10:22 | 40 | 1:18 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA POR AVE | P23032000020 | New_Event | Animals | Include | Include | Wildlife | 78 | 2023-03-20 | 3120 | keep | 0 | Mar | 2023 | 0.002125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-20 09:48 | 2023-03-20 10:34 | 1 | 0:46 | P | ANIMAL | 1 X 25 EN C/L Y SE REMPLAZO PORTAFUSIBLE CRUCE X AVE | B23032000031 | New_Event | Animals | Include | Include | Wildlife | 46 | 2023-03-20 | 46 | keep | 0 | Mar | 2023 | 3.133e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-20 09:53 | 2023-03-20 15:24 | 1 | 5:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S23032000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 331 | 2023-03-20 | 331 | keep | 0 | Mar | 2023 | 0.00022544 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-20 10:01 | 2023-03-20 13:35 | 1 | 3:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23032000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2023-03-20 | 214 | keep | 0 | Mar | 2023 | 0.00014575 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-20 10:02 | 2023-03-20 10:14 | 652 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 POSTE PARTIDO EN TRAMO 7805-7867B | B23032000040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-03-20 | 7824 | keep | 0 | Mar | 2023 | 0.0053289 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2023-03-20 10:02 | 2023-03-20 10:14 | 2704 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 POSTE PARTIDO EN TRAMO 7805-7867B | B23032000040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-03-20 | 32448 | keep | 0 | Mar | 2023 | 0.0221 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
BAYAMON | 2023-03-20 10:02 | 2023-03-20 10:03 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23032000037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-20 | 325 | keep | 0 | Mar | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-03-20 10:04 | 2023-03-20 15:41 | 8 | 5:37 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO DE CAJA A TRANSFORMADOR | S23032000024 | New_Event | Primary Wire Break | Include | Include | Equipment | 337 | 2023-03-20 | 2696 | keep | 0 | Mar | 2023 | 0.0018362 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-03-20 10:21 | 2023-03-20 13:36 | 10 | 3:15 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR PARA LOCALIZAR PEDESTAL ENTERRADO. NO SE ENCONTRO PEDESTAL, PENDIENTE A LOCALIZAR. | C23032000031 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 195 | 2023-03-20 | 1950 | keep | 0 | Mar | 2023 | 0.0013281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-03-20 10:37 | 2023-03-20 14:00 | 50 | 3:23 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C23032000039 | New_Event | Animals | Include | Include | Wildlife | 203 | 2023-03-20 | 10150 | keep | 0 | Mar | 2023 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-03-20 10:44 | 2023-03-20 13:21 | 1 | 2:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A23032000064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-03-20 | 157 | keep | 0 | Mar | 2023 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-03-20 11:02 | 2023-03-20 15:00 | 115 | 3:58 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | P23032000043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-03-20 | 27370 | keep | 0 | Mar | 2023 | 0.018642 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
SAN JUAN | 2023-03-20 11:03 | 2023-03-20 12:29 | 10 | 1:26 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO/REPARAR TRONCAL SECUNDARIO NO FUNDIO | S23031900068 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 86 | 2023-03-20 | 860 | keep | 0 | Mar | 2023 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-20 11:11 | 2023-03-20 13:36 | 1588 | 2:25 | S | POWER TRANSFORMER AVERIADO | SE ENCONTRO PARARAYO EN POWER XMR AVERIADO SE TRANSFIRIERON LAS CARGAS | B23032000067 | New_Event | Power Transformer Failure | Include | Include | Equipment | 145 | 2023-03-20 | 230260 | keep | 0 | Mar | 2023 | 0.15683 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-20 11:11 | 2023-03-20 12:59 | 723 | 1:48 | S | POWER TRANSFORMER AVERIADO | SE ENCONTRO PARARAYO EN POWER XMR AVERIADO SE TRANSFIRIERON LAS CARGAS | B23032000067 | New_Event | Power Transformer Failure | Include | Include | Equipment | 108 | 2023-03-20 | 78084 | keep | 0 | Mar | 2023 | 0.053183 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-03-20 11:11 | 2023-03-20 13:36 | 13 | 2:25 | S | POWER TRANSFORMER AVERIADO | SE ENCONTRO PARARAYO EN POWER XMR AVERIADO SE TRANSFIRIERON LAS CARGAS | B23032000067 | New_Event | Power Transformer Failure | Include | Include | Equipment | 145 | 2023-03-20 | 1885 | keep | 0 | Mar | 2023 | 0.0012839 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-03-20 11:11 | 2023-03-20 12:59 | 198 | 1:48 | T | ALIMENTADOR AMARRADO | SE ENCONTRO PARARAYO EN POWER XMR AVERIADO SE TRANSFIRIERON LAS CARGAS SU CARGA ESTA POR 1711-02 | B23030200067 | New_Event | Feeder Load Transferred | Include | Include | Other | 108 | 2023-03-20 | 21384 | keep | 0 | Mar | 2023 | 0.014565 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-03-20 11:11 | 2023-03-20 12:59 | 1976 | 1:48 | S | POWER TRANSFORMER AVERIADO | SE ENCONTRO PARARAYO EN POWER XMR AVERIADO SE TRANSFIRIERON LAS CARGAS | B23032000067 | New_Event | Power Transformer Failure | Include | Include | Equipment | 108 | 2023-03-20 | 213408 | keep | 0 | Mar | 2023 | 0.14535 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
MAYAGÃœEZ | 2023-03-20 11:26 | 2023-03-20 14:55 | 10 | 3:29 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23032000067 | New_Event | Animals | Include | Include | Wildlife | 209 | 2023-03-20 | 2090 | keep | 0 | Mar | 2023 | 0.0014235 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-20 11:37 | 2023-03-20 14:48 | 10 | 3:11 | P | ANIMAL | 1 X 15 TRANSFORMADOR CRUCE DE FASE POR AVE | A23032000070 | New_Event | Animals | Include | Include | Wildlife | 191 | 2023-03-20 | 1910 | keep | 0 | Mar | 2023 | 0.0013009 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-03-20 11:38 | 2023-03-20 16:51 | 30 | 5:13 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23032000051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2023-03-20 | 9390 | keep | 0 | Mar | 2023 | 0.0063955 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-20 11:44 | 2023-03-20 11:45 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2303200000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-20 | 325 | keep | 0 | Mar | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-03-20 11:46 | 2023-03-20 15:06 | 946 | 3:20 | T | DESGANCHE | DISPARO DE BKR 1525-05 LLEVA LA CARGA DEL 1525-02 ENTRO 95% EN SERVICIO | S23032000040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-03-20 | 189200 | keep | 0 | Mar | 2023 | 0.12886 | 0.00064432 | Sustained | FALSE | FALSE | Not_TMED_Event | 946
SAN JUAN | 2023-03-20 11:46 | 2023-03-20 13:44 | 937 | 1:58 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1525-05 - PROBO MALO - LLEVA LA CARGA DEL 1525-02 SE ABRIO AMARRE Y LA CARGA DEL 1525-05 ENTRO EN SERVICIO | S23032000040 | New_Event | Feeder Load Transferred | Include | Include | Other | 118 | 2023-03-20 | 110566 | keep | 0 | Mar | 2023 | 0.075306 | 0.00063819 | Sustained | FALSE | FALSE | Not_TMED_Event | 937
MAYAGÃœEZ | 2023-03-20 11:48 | 2023-03-20 14:04 | 30 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR FUERTE VIENTO | M23032000072 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2023-03-20 | 4080 | keep | 0 | Mar | 2023 | 0.0027789 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-20 11:56 | 2023-03-20 15:39 | 8 | 3:43 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE POSTE SECUNDARIO | C23032000020 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 223 | 2023-03-20 | 1784 | keep | 0 | Mar | 2023 | 0.0012151 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-03-20 12:10 | 2023-03-20 15:25 | 60 | 3:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032000080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-03-20 | 11700 | keep | 0 | Mar | 2023 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-03-20 12:13 | 2023-03-20 13:10 | 6 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTE SECUNDARIO QUEMADO | C23032000075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-03-20 | 342 | keep | 0 | Mar | 2023 | 0.00023293 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-03-20 12:26 | 2023-03-20 19:00 | 13 | 6:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | M23032000205 | New_Event | Cutout Failure | Include | Include | Equipment | 394 | 2023-03-20 | 5122 | keep | 0 | Mar | 2023 | 0.0034886 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2023-03-20 12:46 | 2023-03-20 13:34 | 6 | 0:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIOS | R23032000032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 48 | 2023-03-20 | 288 | keep | 0 | Mar | 2023 | 0.00019616 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-03-20 12:51 | 2023-03-20 17:44 | 50 | 4:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO VIENTOS | P23032000062 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 293 | 2023-03-20 | 14650 | keep | 0 | Mar | 2023 | 0.009978 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-20 12:55 | 2023-03-21 09:08 | 15 | 20:13 | P | DESGANCHE | 1X25 EN C/L DESGANCHE | S23032000061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1213 | 2023-03-20 | 18195 | keep | 0 | Mar | 2023 | 0.012393 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-03-20 12:57 | 2023-03-20 14:44 | 10 | 1:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO VARIOS TRAMOS DE LINEA SECUNDARIA QUEMADA. | C23032000070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 107 | 2023-03-20 | 1070 | keep | 0 | Mar | 2023 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-20 13:07 | 2023-03-20 14:03 | 10 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA Y BAJANTE SECUNDARIO | R23032000035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2023-03-20 | 560 | keep | 0 | Mar | 2023 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-03-20 13:07 | 2023-03-20 13:09 | 3502 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A23032000085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-20 | 7004 | keep | 0 | Mar | 2023 | 0.0047704 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
BARRANQUITAS | 2023-03-20 13:08 | 2023-03-20 16:16 | 55 | 3:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C23032000074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-03-20 | 10340 | keep | 0 | Mar | 2023 | 0.0070425 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2023-03-20 13:14 | 2023-03-20 15:46 | 10 | 2:32 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | S23032000067 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 152 | 2023-03-20 | 1520 | keep | 0 | Mar | 2023 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-20 13:18 | 2023-03-20 15:25 | 80 | 2:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR FUERTE VIENTO | M23032000101 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 127 | 2023-03-20 | 10160 | keep | 0 | Mar | 2023 | 0.0069199 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-03-20 13:21 | 2023-03-20 16:15 | 80 | 2:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L Y SE REEMPLAZO AISLADOR PARTIDO | R23032000038 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 174 | 2023-03-20 | 13920 | keep | 0 | Mar | 2023 | 0.0094808 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-20 13:22 | 2023-03-20 13:23 | 3070 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECERRO LINEA 36100 | B23032000206 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-20 | 3070 | keep | 0 | Mar | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-03-20 13:22 | 2023-03-20 13:23 | 2735 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECERRO LINEA 36100 | B23032000206 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-20 | 2735 | keep | 0 | Mar | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2023-03-20 13:22 | 2023-03-20 13:23 | 1070 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECERRO LINEA 36100 | B23032000206 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-20 | 1070 | keep | 0 | Mar | 2023 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2023-03-20 13:22 | 2023-03-20 13:23 | 1647 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B23032000207 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-20 | 1647 | keep | 0 | Mar | 2023 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-03-20 13:22 | 2023-03-20 13:23 | 3295 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B23032000207 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-20 | 3295 | keep | 0 | Mar | 2023 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-03-20 13:22 | 2023-03-20 13:23 | 1180 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B23032000207 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-20 | 1180 | keep | 0 | Mar | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2023-03-20 13:22 | 2023-03-20 13:23 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B23032000208 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-20 | 320 | keep | 0 | Mar | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-03-20 13:22 | 2023-03-20 13:23 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B23032000208 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-20 | 2234 | keep | 0 | Mar | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2023-03-20 13:25 | 2023-03-20 13:27 | 922 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 LLEVA LA CARGA DEL 1346-05 SE CERRO POR CONTROL | S23032000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-20 | 1844 | keep | 0 | Mar | 2023 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-03-20 13:25 | 2023-03-20 13:27 | 135 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 LLEVA LA CARGA DEL 1346-05 SE CERRO POR CONTROL | S23032000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-20 | 270 | keep | 0 | Mar | 2023 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2023-03-20 13:40 | 2023-03-21 12:08 | 1 | 22:28 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | S23032000076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1348 | 2023-03-20 | 1348 | keep | 0 | Mar | 2023 | 0.00091812 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-20 13:42 | 2023-03-20 14:20 | 10 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | A23032000090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2023-03-20 | 380 | keep | 0 | Mar | 2023 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-20 13:45 | 2023-03-20 14:27 | 3 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON BAJANTES SECUNDARIOS | R23032000041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2023-03-20 | 126 | keep | 0 | Mar | 2023 | 8.5818e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-20 13:49 | 2023-03-21 14:31 | 1 | 24:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S23032000079 | New_Event | Cutout Failure | Include | Include | Equipment | 1482 | 2023-03-20 | 1482 | keep | 0 | Mar | 2023 | 0.0010094 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-03-20 14:00 | 2023-03-20 18:08 | 67 | 4:08 | P | DESGANCHE | 2 X 40 EN CORTES DE LINEA | C23032000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-03-20 | 16616 | keep | 0 | Mar | 2023 | 0.011317 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2023-03-20 14:02 | 2023-03-20 17:02 | 480 | 3:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23032000218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2023-03-20 | 86400 | keep | 0 | Mar | 2023 | 0.058847 | 0.00032693 | Sustained | FALSE | FALSE | Not_TMED_Event | 480
MAYAGÃœEZ | 2023-03-20 14:04 | 2023-03-20 14:05 | 1117 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTORES | M23032000115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-20 | 1117 | keep | 0 | Mar | 2023 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2023-03-20 14:04 | 2023-03-20 14:05 | 1671 | 0:01 | T | ALIMENTADOR AMARRADO | SU CARGA POR 6404-01 | M23032000115 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-20 | 1671 | keep | 0 | Mar | 2023 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
MAYAGÃœEZ | 2023-03-20 14:04 | 2023-03-20 14:06 | 527 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE INTERRUPTOR | M23032000114 | Additional_clients | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2023-03-20 | 1054 | keep | 0 | Mar | 2023 | 0.00071787 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-20 14:06 | 2023-03-20 14:53 | 30 | 0:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR FUERTE VIENTO | M23032000072 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 47 | 2023-03-20 | 1410 | keep | 0 | Mar | 2023 | 0.00096034 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-03-20 14:07 | 2023-03-20 17:47 | 12 | 3:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23032000219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2023-03-20 | 2640 | keep | 0 | Mar | 2023 | 0.0017981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-20 14:08 | 2023-03-20 16:25 | 60 | 2:17 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | B23032000221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-03-20 | 8220 | keep | 0 | Mar | 2023 | 0.0055986 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-20 14:19 | 2023-03-21 10:27 | 16 | 20:08 | P | DESGANCHE | 1X30 EN C/L DESGANCHE | S23032000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1208 | 2023-03-20 | 19328 | keep | 0 | Mar | 2023 | 0.013164 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2023-03-20 14:28 | 2023-03-20 17:28 | 40 | 3:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L SE REMPLAZO AISLADOR | P23032000072 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 180 | 2023-03-20 | 7200 | keep | 0 | Mar | 2023 | 0.0049039 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-03-20 14:38 | 2023-03-21 12:04 | 15 | 21:26 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23032000087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1286 | 2023-03-20 | 19290 | keep | 0 | Mar | 2023 | 0.013138 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-20 14:38 | 2023-03-20 16:00 | 30 | 1:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032000127 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 82 | 2023-03-20 | 2460 | keep | 0 | Mar | 2023 | 0.0016755 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-20 14:43 | 2023-03-20 17:45 | 3 | 3:02 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032000130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-03-20 | 546 | keep | 0 | Mar | 2023 | 0.00037188 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-03-20 14:51 | 2023-03-20 19:20 | 4 | 4:29 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA ROTA Y SE REPARO PUENTES ABIERTOS | M23032000137 | New_Event | Primary Wire Break | Include | Include | Equipment | 269 | 2023-03-20 | 1076 | keep | 0 | Mar | 2023 | 0.00073286 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-03-20 14:55 | 2023-03-20 16:53 | 2 | 1:58 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P23032000082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2023-03-20 | 236 | keep | 0 | Mar | 2023 | 0.00016074 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-03-20 15:06 | 2023-03-20 18:10 | 48 | 3:04 | P | DESGANCHE | SE REALIZO DESGANCHE 100% EN SERVICIO | S23032000040 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 184 | 2023-03-20 | 8832 | keep | 0 | Mar | 2023 | 0.0060154 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-03-20 15:28 | 2023-03-20 17:10 | 7 | 1:42 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN TRANSFORMADOR SE RETIRO SERVICIO A CLIENTE CON TOMA CRUZADA. TOMA AEREA ES DEL LUMA | M23032000151 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 102 | 2023-03-20 | 714 | keep | 0 | Mar | 2023 | 0.0004863 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-03-20 15:31 | 2023-03-20 18:54 | 200 | 3:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR FUERTE VIENTO | M23032000153 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 203 | 2023-03-20 | 40600 | keep | 0 | Mar | 2023 | 0.027652 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-03-20 15:35 | 2023-03-20 16:54 | 50 | 1:19 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C23032000099 | New_Event | Animals | Include | Include | Wildlife | 79 | 2023-03-20 | 3950 | keep | 0 | Mar | 2023 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-03-20 15:43 | 2023-03-21 10:15 | 60 | 18:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES VERIFCADO EN BITACORA EVENTO AGUADILLA | M23032000164 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1112 | 2023-03-20 | 66720 | keep | 0 | Mar | 2023 | 0.045443 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-20 15:47 | 2023-03-20 17:29 | 4 | 1:42 | P | DESGANCHE | 1 X 20 EN XMR SE REALIZO DESGANCHE | B23032000238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-03-20 | 408 | keep | 0 | Mar | 2023 | 0.00027789 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-03-20 15:53 | 2023-03-20 20:22 | 39 | 4:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE LEVANTO LINEA PRIMARIA | B23032000239 | New_Event | Primary Wire Break | Include | Include | Equipment | 269 | 2023-03-20 | 10491 | keep | 0 | Mar | 2023 | 0.0071454 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
VEGA BAJA | 2023-03-20 16:19 | 2023-03-20 16:20 | 2107 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23032000108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-20 | 2107 | keep | 0 | Mar | 2023 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
YAUCO | 2023-03-20 16:42 | 2023-03-20 20:00 | 10 | 3:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23032000097 | New_Event | Primary Wire Break | Include | Include | Equipment | 198 | 2023-03-20 | 1980 | keep | 0 | Mar | 2023 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-20 17:32 | 2023-03-21 14:10 | 18 | 20:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | S23032000124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1238 | 2023-03-20 | 22284 | keep | 0 | Mar | 2023 | 0.015178 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
HUMACAO | 2023-03-20 17:37 | 2023-03-20 18:09 | 23 | 0:32 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA DESENREDAR LINEA SECUNDARIA | C23032000113 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 32 | 2023-03-20 | 736 | keep | 0 | Mar | 2023 | 0.00050129 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
GUAYAMA | 2023-03-20 17:38 | 2023-03-20 17:39 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO CAUSA | P23032000108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-20 | 4132 | keep | 0 | Mar | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
AGUADILLA | 2023-03-20 17:44 | 2023-03-21 12:49 | 12 | 19:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REMPLAZARON CONECTORES SECUNDARIOS | A23032000207 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1145 | 2023-03-20 | 13740 | keep | 0 | Mar | 2023 | 0.0093583 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-03-20 17:52 | 2023-03-20 18:22 | 10 | 0:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23032000110 | New_Event | Primary Wire Break | Include | Include | Equipment | 30 | 2023-03-20 | 300 | keep | 0 | Mar | 2023 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-03-20 18:14 | 2023-03-20 22:23 | 60 | 4:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M23032000213 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 249 | 2023-03-20 | 14940 | keep | 0 | Mar | 2023 | 0.010176 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-20 18:20 | 2023-03-20 20:20 | 14 | 2:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032000215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-03-20 | 1680 | keep | 0 | Mar | 2023 | 0.0011442 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-03-20 18:26 | 2023-03-20 19:50 | 150 | 1:24 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A23032000121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-03-20 | 12600 | keep | 0 | Mar | 2023 | 0.0085818 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-03-20 18:34 | 2023-03-20 20:30 | 10 | 1:56 | P | CAUSAS EXTERNAS | SE ATACHARON LINEAS SECUNDARIAS Y SE CERRO CAJAS EN TRANSFORMADOR POSTE PARTIDO POR IMPACTO DE VEHICULO PESADO | A23032000005 | New_Event | Damage From Public | Include | Include | Public | 116 | 2023-03-20 | 1160 | keep | 0 | Mar | 2023 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-20 19:01 | 2023-03-21 10:43 | 15 | 15:42 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR IGUANA | M23032000221 | New_Event | Animals | Include | Include | Wildlife | 942 | 2023-03-20 | 14130 | keep | 0 | Mar | 2023 | 0.0096239 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-20 19:07 | 2023-03-20 20:50 | 70 | 1:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032000225 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 103 | 2023-03-20 | 7210 | keep | 0 | Mar | 2023 | 0.0049107 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-03-20 19:12 | 2023-03-20 19:13 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23032000227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-20 | 1192 | keep | 0 | Mar | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
SAN JUAN | 2023-03-20 19:24 | 2023-03-20 20:38 | 65 | 1:14 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN RISER PRINCIPAL Y 1 X 80 EN SU-3 FUNDIO AL PROBAR MALO DE SU-2 @ SHOPPING CENTER | S23032000144 | New_Event | UG Cable Fault | Include | Include | Equipment | 74 | 2023-03-20 | 4810 | keep | 0 | Mar | 2023 | 0.0032761 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
AGUADILLA | 2023-03-20 19:30 | 2023-03-21 17:00 | 40 | 21:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M23032000235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1290 | 2023-03-20 | 51600 | keep | 0 | Mar | 2023 | 0.035145 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-20 19:41 | 2023-03-21 10:25 | 150 | 14:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | M23032000236 | New_Event | Primary Wire Break | Include | Include | Equipment | 884 | 2023-03-20 | 132600 | keep | 0 | Mar | 2023 | 0.090313 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-03-20 19:43 | 2023-03-21 10:12 | 495 | 14:29 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA TRABAJAR CON GOI MY230321-01 | M23032000240 | New_Event | Primary Wire Break | Include | Include | Equipment | 869 | 2023-03-20 | 430155 | keep | 0 | Mar | 2023 | 0.29298 | 0.00033714 | Sustained | FALSE | FALSE | Not_TMED_Event | 495
ARECIBO | 2023-03-20 20:31 | 2023-03-20 21:44 | 80 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN CL NO SE ENCONTRO CAUSA | A23032000125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-03-20 | 5840 | keep | 0 | Mar | 2023 | 0.0039776 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-03-20 20:38 | 2023-03-22 12:22 | 13 | 39:44 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DEL T-21 @ SU-2 | S23032000133 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 2384 | 2023-03-20 | 30992 | keep | 0 | Mar | 2023 | 0.021109 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-20 20:42 | 2023-03-21 13:21 | 5 | 16:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23032000126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 999 | 2023-03-20 | 4995 | keep | 0 | Mar | 2023 | 0.0034021 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-20 21:20 | 2023-03-20 22:10 | 44 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23032000026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-03-20 | 2200 | keep | 0 | Mar | 2023 | 0.0014984 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
AGUADILLA | 2023-03-20 23:23 | 2023-03-21 00:52 | 125 | 1:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M23032000309 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 89 | 2023-03-20 | 11125 | keep | 0 | Mar | 2023 | 0.0075772 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BARRANQUITAS | 2023-03-21 00:21 | 2023-03-21 00:23 | 1403 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | C23032100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-21 | 2806 | keep | 0 | Mar | 2023 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
GUAYAMA | 2023-03-21 00:34 | 2023-03-21 08:11 | 12 | 7:37 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA POR LINEA ARRIADA | P23032100007 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 457 | 2023-03-21 | 5484 | keep | 0 | Mar | 2023 | 0.0037351 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-21 03:39 | 2023-03-21 04:41 | 1 | 1:02 | P | ANIMAL | 1 X 20 EN XMR CRUCE X AVE | B23032100003 | New_Event | Animals | Include | Include | Wildlife | 62 | 2023-03-21 | 62 | keep | 0 | Mar | 2023 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-21 03:55 | 2023-03-21 07:56 | 40 | 4:01 | P | DESGANCHE | 1 X 65 EN C/L SE RETIRO RAMA | B23032100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2023-03-21 | 9640 | keep | 0 | Mar | 2023 | 0.0065658 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-21 04:05 | 2023-03-21 06:06 | 50 | 2:01 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23032100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-03-21 | 6050 | keep | 0 | Mar | 2023 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-21 04:49 | 2023-03-21 12:27 | 17 | 7:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23032100010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 458 | 2023-03-21 | 7786 | keep | 0 | Mar | 2023 | 0.005303 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2023-03-21 04:51 | 2023-03-21 04:52 | 1922 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | C23032100004 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-21 | 1922 | keep | 0 | Mar | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2023-03-21 04:52 | 2023-03-21 10:25 | 4 | 5:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | C23032100005 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 333 | 2023-03-21 | 1332 | keep | 0 | Mar | 2023 | 0.00090722 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-03-21 05:05 | 2023-03-21 05:07 | 844 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 35% 1345-05 | S23032100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-21 | 1688 | keep | 0 | Mar | 2023 | 0.0011497 | 0.00057484 | Momentary | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2023-03-21 05:05 | 2023-03-21 05:07 | 334 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1330-04 SE CERRO POR CONTROL LLEVA 35% 1345-05 | S23032100004 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-21 | 668 | keep | 0 | Mar | 2023 | 0.00045497 | 0.00022749 | Momentary | FALSE | FALSE | Not_TMED_Event | 334
SAN JUAN | 2023-03-21 05:12 | 2023-03-21 05:14 | 844 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 35% 1345-05 | S23032100004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-21 | 1688 | keep | 0 | Mar | 2023 | 0.0011497 | 0.00057484 | Momentary | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2023-03-21 05:12 | 2023-03-21 05:14 | 334 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1330-04 SE CERRO POR CONTROL LLEVA 35% 1345-05 | S23032100004 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-21 | 668 | keep | 0 | Mar | 2023 | 0.00045497 | 0.00022749 | Momentary | FALSE | FALSE | Not_TMED_Event | 334
HUMACAO | 2023-03-21 05:49 | 2023-03-21 08:29 | 9 | 2:40 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | C23032100006 | New_Event | Animals | Include | Include | Wildlife | 160 | 2023-03-21 | 1440 | keep | 0 | Mar | 2023 | 0.00098078 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2023-03-21 06:36 | 2023-03-21 06:37 | 3431 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | A23032100004 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-21 | 3431 | keep | 0 | Mar | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-03-21 06:37 | 2023-03-21 09:10 | 50 | 2:33 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASES | A23032100005 | 1st_after_momentary | Animals | Include | Include | Wildlife | 153 | 2023-03-21 | 7650 | keep | 0 | Mar | 2023 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-21 06:43 | 2023-03-21 11:26 | 15 | 4:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R23032100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2023-03-21 | 4245 | keep | 0 | Mar | 2023 | 0.0028913 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-03-21 06:57 | 2023-03-21 12:10 | 1 | 5:13 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER NO CAUSA | M23032100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2023-03-21 | 313 | keep | 0 | Mar | 2023 | 0.00021318 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-21 07:27 | 2023-03-21 07:28 | 3941 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2303210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 3941 | keep | 0 | Mar | 2023 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
CAGUAS | 2023-03-21 07:33 | 2023-03-21 11:17 | 10 | 3:44 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23032100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-03-21 | 2240 | keep | 0 | Mar | 2023 | 0.0015257 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-03-21 07:39 | 2023-03-21 11:41 | 10 | 4:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO 2 CAJAS PRIMARIAS DE TRANASFORMADOR | P23032100022 | New_Event | Cutout Failure | Include | Include | Equipment | 242 | 2023-03-21 | 2420 | keep | 0 | Mar | 2023 | 0.0016483 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-21 07:39 | 2023-03-21 10:30 | 100 | 2:51 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO | A23032100014 | New_Event | Primary Wire Break | Include | Include | Equipment | 171 | 2023-03-21 | 17100 | keep | 0 | Mar | 2023 | 0.011647 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-03-21 08:14 | 2023-03-21 08:15 | 4369 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2303210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 4369 | keep | 0 | Mar | 2023 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
HUMACAO | 2023-03-21 08:26 | 2023-03-21 08:27 | 3701 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23032100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 3701 | keep | 0 | Mar | 2023 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
SAN JUAN | 2023-03-21 08:28 | 2023-03-21 08:29 | 601 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1437-01 LLEVA LA CARGA DEL 1437-02 | S23032100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 601 | keep | 0 | Mar | 2023 | 0.00040934 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2023-03-21 08:28 | 2023-03-21 08:29 | 640 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1437-01 LLEVA LA CARGA DEL 1437-02 | S23032100017 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-21 | 640 | keep | 0 | Mar | 2023 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
MAYAGÃœEZ | 2023-03-21 08:30 | 2023-03-21 15:35 | 200 | 7:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA | M23032100044 | New_Event | Primary Wire Break | Include | Include | Equipment | 425 | 2023-03-21 | 85000 | keep | 0 | Mar | 2023 | 0.057893 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-03-21 08:30 | 2023-03-21 08:50 | 8 | 0:20 | P | PROBLEMA DEL CLIENTE | SE ABRIO TRANSFORMADOR PARA DESCONECTAR PEDESTAL PARA QUE CLIENTE REPARE | A23032100023 | New_Event | Customer-Related Interruption | Include | Include | Public | 20 | 2023-03-21 | 160 | keep | 0 | Mar | 2023 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-03-21 08:35 | 2023-03-21 14:59 | 60 | 6:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN RISER 1 X 65 EN RISER | S23032100018 | New_Event | Cutout Failure | Include | Include | Equipment | 384 | 2023-03-21 | 23040 | keep | 0 | Mar | 2023 | 0.015692 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-21 08:35 | 2023-03-21 08:36 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23032100023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 325 | keep | 0 | Mar | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
AGUADILLA | 2023-03-21 09:21 | 2023-03-21 13:20 | 30 | 3:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032100090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2023-03-21 | 7170 | keep | 0 | Mar | 2023 | 0.0048835 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-21 09:33 | 2023-03-21 10:33 | 7 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BARRA EN PEDESTAL | B23032100029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-03-21 | 420 | keep | 0 | Mar | 2023 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-21 09:35 | 2023-03-21 10:54 | 1 | 1:19 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23032100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-03-21 | 79 | keep | 0 | Mar | 2023 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-21 09:54 | 2023-03-21 14:11 | 1 | 4:17 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23032100039 | New_Event | Animals | Include | Include | Wildlife | 257 | 2023-03-21 | 257 | keep | 0 | Mar | 2023 | 0.00017504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-21 10:10 | 2023-03-21 11:50 | 40 | 1:40 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA CAMION PRIVADO DERRIBO CONDUCTORES DE COMUNICACIONES | C23032100047 | New_Event | Damage From Public | Include | Include | Public | 100 | 2023-03-21 | 4000 | keep | 0 | Mar | 2023 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-21 10:12 | 2023-03-21 13:41 | 1485 | 3:29 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE ABIERTO EN TRONCAL CON GOI MY230321-01 | M23032100163 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 209 | 2023-03-21 | 310365 | keep | 0 | Mar | 2023 | 0.21139 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-03-21 10:13 | 2023-03-21 14:25 | 18 | 4:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | A23032100049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 252 | 2023-03-21 | 4536 | keep | 0 | Mar | 2023 | 0.0030894 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2023-03-21 10:15 | 2023-03-21 11:35 | 6 | 1:20 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y SE REMPLAZO PEDESTAL | S23032100037 | New_Event |  |  |  |  | 80 | 2023-03-21 | 480 | keep | 0 | Mar | 2023 | 0.00032693 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-03-21 10:21 | 2023-03-21 10:22 | 3025 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2303210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 3025 | keep | 0 | Mar | 2023 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
AGUADILLA | 2023-03-21 10:30 | 2023-03-21 11:25 | 200 | 0:55 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE ABIERTO | A23032100014 | New_Event | Primary Wire Break | Include | Include | Equipment | 55 | 2023-03-21 | 11000 | keep | 0 | Mar | 2023 | 0.007492 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-03-21 10:44 | 2023-03-21 20:29 | 271 | 9:45 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR POR ERROR. SE CERRO POR CONTROL. | S23032100000 | New_Event | Human Error | Include | Include | Other | 585 | 2023-03-21 | 158535 | keep | 0 | Mar | 2023 | 0.10798 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
BARRANQUITAS | 2023-03-21 10:45 | 2023-03-21 12:58 | 130 | 2:13 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C23032100050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-03-21 | 17290 | keep | 0 | Mar | 2023 | 0.011776 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
FAJARDO | 2023-03-21 10:54 | 2023-03-21 13:03 | 15 | 2:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR Y SE REPARO TOMA SOTERRADA | R23032100011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 129 | 2023-03-21 | 1935 | keep | 0 | Mar | 2023 | 0.0013179 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-21 11:09 | 2023-03-21 13:51 | 514 | 2:42 | T | DESGANCHE | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR 75% EN SERVICIO SU CARGA POR 1520-05 | S23032100064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-03-21 | 83268 | keep | 0 | Mar | 2023 | 0.056713 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2023-03-21 11:09 | 2023-03-21 13:31 | 752 | 2:22 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE ENCONTRO SE REALIZO DESGANCHE A VARETA DE PISO SE ABRIO MACHETE N/O CONTRA 1520-01 PARA SECCIONALIZAR LLEVA 1520-04 | S23032100064 | New_Event | Feeder Load Transferred | Include | Include | Other | 142 | 2023-03-21 | 106784 | keep | 0 | Mar | 2023 | 0.07273 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2023-03-21 11:09 | 2023-03-21 13:31 | 68 | 2:22 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE ENCONTRO SE REALIZO DESGANCHE A VARETA DE PISO SE ABRIO MACHETE N/O CONTRA 1520-01 PARA SECCIONALIZAR LLEVA 1520-04 | S23032100064 | New_Event | Feeder Load Transferred | Include | Include | Other | 142 | 2023-03-21 | 9656 | keep | 0 | Mar | 2023 | 0.0065767 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
CAGUAS | 2023-03-21 11:10 | 2023-03-21 17:32 | 45 | 6:22 | P | TERMINACION SOTERRADA AVERIADA | 1 X 40 Y SE REPARO PISTOLA Y BUSHING EN PM TRAMO RADIAL | C23032100061 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 382 | 2023-03-21 | 17190 | keep | 0 | Mar | 2023 | 0.011708 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-03-21 11:12 | 2023-03-21 23:52 | 8 | 12:40 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | S23032100069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 760 | 2023-03-21 | 6080 | keep | 0 | Mar | 2023 | 0.0041411 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-03-21 11:16 | 2023-03-21 12:13 | 25 | 0:57 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23032100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2023-03-21 | 1425 | keep | 0 | Mar | 2023 | 0.00097056 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-03-21 11:29 | 2023-03-21 15:29 | 313 | 4:00 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO AREA DEL ALIMENTADOR 6702-03 PARA PODER TRABAJAR REPARANDO LINEA PRIMARIA ROTA DEL ALIMENTADOR 6704-03 | M23032100158 | New_Event | Primary Wire Break | Include | Include | Equipment | 240 | 2023-03-21 | 75120 | keep | 0 | Mar | 2023 | 0.051164 | 0.00021318 | Sustained | FALSE | FALSE | Not_TMED_Event | 313
CANOVANAS | 2023-03-21 11:35 | 2023-03-21 13:10 | 10 | 1:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO PORTAFUSIBLE Y 1 X 8 EN XMR | R23032100013 | New_Event | Cutout Failure | Include | Include | Equipment | 95 | 2023-03-21 | 950 | keep | 0 | Mar | 2023 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-21 11:38 | 2023-03-21 15:33 | 7 | 3:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO SECUNDARIA SE REMPLAZO 3 TOMAS. | S23032100083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 235 | 2023-03-21 | 1645 | keep | 0 | Mar | 2023 | 0.0011204 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-21 11:40 | 2023-03-22 13:39 | 40 | 25:59 | P | CABLE SOTERRADO AVERIADO | SE HABILITO BACKUP AL SU-2 QUE TENIA PUENTES ABIERTOS ANTES DEL RISER | S23032100085 | New_Event | UG Cable Fault | Include | Include | Equipment | 1559 | 2023-03-21 | 62360 | keep | 0 | Mar | 2023 | 0.042473 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-03-21 11:46 | 2023-03-21 13:30 | 1 | 1:44 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23032100175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-03-21 | 104 | keep | 0 | Mar | 2023 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-03-21 12:08 | 2023-03-21 12:09 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23032100071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 2379 | keep | 0 | Mar | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
VEGA BAJA | 2023-03-21 12:15 | 2023-03-21 12:45 | 45 | 0:30 | P | ERROR HUMANO | 2 X 40 EN CORTE DE LINEA EN TRABAJOS EN VIA LIBRE X2023-378 SE CRUZO NEUTRAL CON FASES | A23032100070 | New_Event | Human Error | Include | Include | Other | 30 | 2023-03-21 | 1350 | keep | 0 | Mar | 2023 | 0.00091948 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2023-03-21 12:22 | 2023-03-21 14:25 | 80 | 2:03 | P | CAUSAS EXTERNAS | 1 X 80 EN C/L SE RETIRO GLOBO SOBRE LINEAS | P23032100076 | New_Event | Damage From Public | Include | Include | Public | 123 | 2023-03-21 | 9840 | keep | 0 | Mar | 2023 | 0.006702 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-03-21 12:35 | 2023-03-21 13:05 | 321 | 0:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REEMPLAZO AISLADOR | R23032100030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 30 | 2023-03-21 | 9630 | keep | 0 | Mar | 2023 | 0.0065589 | 0.00021863 | Sustained | FALSE | FALSE | Not_TMED_Event | 321
MAYAGÃœEZ | 2023-03-21 12:35 | 2023-03-21 18:58 | 5 | 6:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL PRIMARIO ROTO Y SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | M23032100193 | New_Event | Secondary Wire Break | Include | Include | Equipment | 383 | 2023-03-21 | 1915 | keep | 0 | Mar | 2023 | 0.0013043 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-03-21 12:37 | 2023-03-21 17:30 | 25 | 4:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23032100073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2023-03-21 | 7325 | keep | 0 | Mar | 2023 | 0.004989 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-03-21 12:50 | 2023-03-21 14:06 | 10 | 1:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO XMR Y SE REPARO CAJA PRIMARIA | R23032100026 | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2023-03-21 | 760 | keep | 0 | Mar | 2023 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-21 12:52 | 2023-03-21 17:18 | 1061 | 4:26 | S | LINEA DE TRANSMISION 38KV | AL DISPARAR LINEA 12300 POR CRUCE EN GOAB 12340 FUNDIO 3 FUSIBLES 38KV, SE VAN A TRANSFERIR LAS CARGAS SE PASO AL 1652-03 | S23032100292 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 266 | 2023-03-21 | 282226 | keep | 0 | Mar | 2023 | 0.19222 | 0.00072264 | Sustained | FALSE | FALSE | Not_TMED_Event | 1061
SAN JUAN | 2023-03-21 12:52 | 2023-03-21 16:35 | 742 | 3:43 | S | LINEA DE TRANSMISION 38KV | AL DISPARAR LINEA 12300 POR CRUCE EN GOAB 12340 FUNDIO 3 FUSIBLES 38KV, SE VAN A TRANSFERIR LAS CARGAS SU CARGAS 1437-04 | S23032100293 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 223 | 2023-03-21 | 165466 | keep | 0 | Mar | 2023 | 0.1127 | 0.00050537 | Sustained | FALSE | FALSE | Not_TMED_Event | 742
SAN JUAN | 2023-03-21 12:52 | 2023-03-21 16:35 | 998 | 3:43 | S | LINEA DE TRANSMISION 38KV | AL DISPARAR LINEA 12300 POR CRUCE EN GOAB 12340 FUNDIO 3 FUSIBLES 38KV, SE VAN A TRANSFERIR LAS CARGAS SU CARGA POR 1652-05 | S23032100292 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 223 | 2023-03-21 | 222554 | keep | 0 | Mar | 2023 | 0.15158 | 0.00067973 | Sustained | FALSE | FALSE | Not_TMED_Event | 998
SAN JUAN | 2023-03-21 12:52 | 2023-03-21 16:35 | 1397 | 3:43 | S | LINEA DE TRANSMISION 38KV | AL DISPARAR LINEA 12300 POR CRUCE EN GOAB 12340 FUNDIO 3 FUSIBLES 38KV, SE VAN A TRANSFERIR LAS CARGAS SU CARGA POR 1335-04 | S23032100324 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 223 | 2023-03-21 | 311531 | keep | 0 | Mar | 2023 | 0.21218 | 0.00095149 | Sustained | FALSE | FALSE | Not_TMED_Event | 1397
FAJARDO | 2023-03-21 13:13 | 2023-03-21 14:22 | 15 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR Y SE REPARO TOMA SOTERRADA | R23032100011 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 69 | 2023-03-21 | 1035 | keep | 0 | Mar | 2023 | 0.00070493 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-03-21 13:13 | 2023-03-21 15:38 | 321 | 2:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REEMPLAZO AISLADOR | R23032100030 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 145 | 2023-03-21 | 46545 | keep | 0 | Mar | 2023 | 0.031702 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-21 13:17 | 2023-03-21 15:40 | 10 | 2:23 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | A23032100061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2023-03-21 | 1430 | keep | 0 | Mar | 2023 | 0.00097397 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-03-21 13:19 | 2023-03-21 13:20 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23032100100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 449 | keep | 0 | Mar | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
SAN JUAN | 2023-03-21 13:35 | 2023-03-21 17:04 | 100 | 3:29 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA T-5 A T-4 AVERIA VIEJA T-3 A T-4 1 X 80 EN PROVISIONAL | S23032100183 | New_Event | UG Cable Fault | Include | Include | Equipment | 209 | 2023-03-21 | 20900 | keep | 0 | Mar | 2023 | 0.014235 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-21 13:39 | 2023-03-21 19:06 | 20 | 5:27 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23032100047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2023-03-21 | 6540 | keep | 0 | Mar | 2023 | 0.0044544 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-03-21 13:43 | 2023-03-21 14:50 | 632 | 1:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO DISCOS PARTIDOS CG-230321-01 | C23032100168 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 67 | 2023-03-21 | 42344 | keep | 0 | Mar | 2023 | 0.02884 | 0.00043045 | Sustained | FALSE | FALSE | Not_TMED_Event | 632
CANOVANAS | 2023-03-21 13:44 | 2023-03-21 15:42 | 253 | 1:58 | P | CAUSAS EXTERNAS | 1 X 65 C/L Y 1 X 10 EN XMR SE RETIRO GLOBO CRUZO FASE | R23032100053 | New_Event | Damage From Public | Include | Include | Public | 118 | 2023-03-21 | 29854 | keep | 0 | Mar | 2023 | 0.020333 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
SAN JUAN | 2023-03-21 13:51 | 2023-03-21 14:30 | 128 | 0:39 | P | DESGANCHE | SE REALIZO DESGANCHE A VARETA DE PISO Y SE CERRO MACHETE 100% EN SERVICIO SU CARGA POR 1520-05 | S23032100064 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 39 | 2023-03-21 | 4992 | keep | 0 | Mar | 2023 | 0.0034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-21 14:03 | 2023-03-22 10:18 | 9 | 20:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA A CAJA | S23032100220 | New_Event | Primary Wire Break | Include | Include | Equipment | 1215 | 2023-03-21 | 10935 | keep | 0 | Mar | 2023 | 0.0074478 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2023-03-21 14:07 | 2023-03-21 14:45 | 10 | 0:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 10 EN TRANSFORMADOR SE REPARO NEUTRAL PRIMARIO PARTIDO | A23032100094 | New_Event | Primary Wire Break | Include | Include | Equipment | 38 | 2023-03-21 | 380 | keep | 0 | Mar | 2023 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-03-21 14:09 | 2023-03-21 18:27 | 8 | 4:18 | P | ANIMAL | SE REPARO BAJANTE PRIMARIO CRUCE X AVE | C23032100175 | New_Event | Animals | Include | Include | Wildlife | 258 | 2023-03-21 | 2064 | keep | 0 | Mar | 2023 | 0.0014058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-03-21 14:23 | 2023-03-21 14:46 | 2791 | 0:23 | S | LINEA DE TRANSMISION 115KV | PERSONAL DE CONSERVACION TRABAJANDO Y OPERO EL 36104 | A23032100111 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 23 | 2023-03-21 | 64193 | keep | 0 | Mar | 2023 | 0.043722 | 0.0019009 | Sustained | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2023-03-21 14:23 | 2023-03-21 14:46 | 1464 | 0:23 | S | LINEA DE TRANSMISION 115KV | PERSONAL DE CONSERVACION TRABAJANDO Y OPERO EL 36104 | A23032100111 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 23 | 2023-03-21 | 33672 | keep | 0 | Mar | 2023 | 0.022934 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
VEGA BAJA | 2023-03-21 14:23 | 2023-03-21 14:46 | 759 | 0:23 | S | LINEA DE TRANSMISION 115KV | PERSONAL DE CONSERVACION TRABAJANDO Y OPERO EL 36104 | A23032100111 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 23 | 2023-03-21 | 17457 | keep | 0 | Mar | 2023 | 0.01189 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2023-03-21 14:23 | 2023-03-21 14:46 | 1500 | 0:23 | S | LINEA DE TRANSMISION 115KV | PERSONAL DE CONSERVACION TRABAJANDO Y OPERO EL 36104 | A23032100111 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 23 | 2023-03-21 | 34500 | keep | 0 | Mar | 2023 | 0.023498 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
UTUADO | 2023-03-21 14:26 | 2023-03-21 18:30 | 45 | 4:04 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23032100112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2023-03-21 | 10980 | keep | 0 | Mar | 2023 | 0.0074784 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-03-21 14:32 | 2023-03-21 14:34 | 172 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23032100257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-21 | 344 | keep | 0 | Mar | 2023 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
ARECIBO | 2023-03-21 14:40 | 2023-03-21 15:20 | 2 | 0:40 | P | PROBLEMA DEL CLIENTE | SE ABRIO CAJAS DE TRANSFORMADOR PARA RECONECTAR SERVICIO A 2 CLIENTES | P23032100079 | New_Event | Customer-Related Interruption | Include | Include | Public | 40 | 2023-03-21 | 80 | keep | 0 | Mar | 2023 | 5.4488e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-03-21 14:42 | 2023-03-21 17:00 | 80 | 2:18 | P | ANIMAL | 1 X 65, 1 X 80 Y 1 X 100 EN C/L CRUCE X AVE | C23032100198 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-03-21 | 11040 | keep | 0 | Mar | 2023 | 0.0075193 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-03-21 14:53 | 2023-03-21 14:54 | 1952 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | P23032100123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-21 | 1952 | keep | 0 | Mar | 2023 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
PONCE | 2023-03-21 14:54 | 2023-03-21 18:20 | 50 | 3:26 | P | DESGANCHE | 2 X 65 EN CL DESGANCHE | P23032100170 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-03-21 | 10300 | keep | 0 | Mar | 2023 | 0.0070153 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-03-21 14:57 | 2023-03-21 17:49 | 278 | 2:52 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L NO CAUSA | R23032100079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2023-03-21 | 47816 | keep | 0 | Mar | 2023 | 0.032567 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
FAJARDO | 2023-03-21 14:57 | 2023-03-21 17:35 | 278 | 2:38 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23032100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-03-21 | 43924 | keep | 0 | Mar | 2023 | 0.029916 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
CANOVANAS | 2023-03-21 15:21 | 2023-03-21 18:37 | 80 | 3:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO | R23032100081 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 196 | 2023-03-21 | 15680 | keep | 0 | Mar | 2023 | 0.01068 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-03-21 15:22 | 2023-03-21 15:25 | 362 | 0:03 | P | ALIMENTADOR AMARRADO | SE PROBO POR CONTROL QUEDO EN SERVICIO 90% DE SU CARGA POR 1620-01 | S2303210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-21 | 1086 | keep | 0 | Mar | 2023 | 0.00073967 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-03-21 15:22 | 2023-03-21 15:25 | 36 | 0:03 | T | NO SE REPORTO CAUSA | SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 90% DEL 1336-10 | S2303210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-21 | 108 | keep | 0 | Mar | 2023 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-03-21 15:32 | 2023-03-21 18:00 | 80 | 2:28 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S23032100322 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-03-21 | 11840 | keep | 0 | Mar | 2023 | 0.0080642 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-03-21 15:35 | 2023-03-21 23:08 | 200 | 7:33 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE CONVERTIDOR Y SE REPARO LINEA PARTIDA 15:35 | M23032100044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 453 | 2023-03-21 | 90600 | keep | 0 | Mar | 2023 | 0.061707 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-03-21 15:40 | 2023-03-21 19:43 | 79 | 4:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23032100331 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-03-21 | 19197 | keep | 0 | Mar | 2023 | 0.013075 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2023-03-21 15:40 | 2023-03-21 19:15 | 190 | 3:35 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MACHETE PARA SECCIONALIZAR PUENTE ABIERTO Y CAJA COLGANDO | S23032100330 | New_Event | Primary Wire Break | Include | Include | Equipment | 215 | 2023-03-21 | 40850 | keep | 0 | Mar | 2023 | 0.027823 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
VEGA BAJA | 2023-03-21 15:43 | 2023-03-21 17:05 | 300 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23032100136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2023-03-21 | 24600 | keep | 0 | Mar | 2023 | 0.016755 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-03-21 15:44 | 2023-03-21 19:00 | 150 | 3:16 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | B23032100137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-03-21 | 29400 | keep | 0 | Mar | 2023 | 0.020024 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-03-21 15:51 | 2023-03-21 19:03 | 13 | 3:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO PORTA FUSIBLE | M23032100288 | New_Event | Cutout Failure | Include | Include | Equipment | 192 | 2023-03-21 | 2496 | keep | 0 | Mar | 2023 | 0.0017 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-03-21 15:53 | 2023-03-21 15:54 | 776 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23032100139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 776 | keep | 0 | Mar | 2023 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2023-03-21 15:54 | 2023-03-21 20:42 | 50 | 4:48 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | B23032100156 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 288 | 2023-03-21 | 14400 | keep | 0 | Mar | 2023 | 0.0098078 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-03-21 16:06 | 2023-03-21 18:22 | 50 | 2:16 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23032100100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-03-21 | 6800 | keep | 0 | Mar | 2023 | 0.0046314 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-03-21 16:10 | 2023-03-21 16:40 | 50 | 0:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO | P23032100150 | New_Event | Primary Wire Break | Include | Include | Equipment | 30 | 2023-03-21 | 1500 | keep | 0 | Mar | 2023 | 0.0010216 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-21 16:26 | 2023-03-21 16:27 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2303210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 45 | keep | 0 | Mar | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-03-21 16:28 | 2023-03-21 18:50 | 5 | 2:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23032100139 | New_Event | Primary Wire Break | Include | Include | Equipment | 142 | 2023-03-21 | 710 | keep | 0 | Mar | 2023 | 0.00048358 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-03-21 16:35 | 2023-03-21 20:10 | 150 | 3:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23032100140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2023-03-21 | 32250 | keep | 0 | Mar | 2023 | 0.021965 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-03-21 16:39 | 2023-03-21 19:48 | 40 | 3:09 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | B23032100157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2023-03-21 | 7560 | keep | 0 | Mar | 2023 | 0.0051491 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-03-21 16:46 | 2023-03-21 16:47 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23032100219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 1606 | keep | 0 | Mar | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2023-03-21 16:47 | 2023-03-21 18:58 | 130 | 2:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | C23032100221 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 131 | 2023-03-21 | 17030 | keep | 0 | Mar | 2023 | 0.011599 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
VEGA BAJA | 2023-03-21 16:48 | 2023-03-21 20:00 | 60 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA | A23032100142 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2023-03-21 | 11520 | keep | 0 | Mar | 2023 | 0.0078462 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-03-21 16:56 | 2023-03-21 19:12 | 1 | 2:16 | P | PARARRAYOS DEFECTUOSO | 3 X 25 EN RISER | C23032100222 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 136 | 2023-03-21 | 136 | keep | 0 | Mar | 2023 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-21 16:57 | 2023-03-21 18:33 | 60 | 1:36 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L SE LEVANTO ALAMBRE PRIMARIO | R23032100108 | New_Event | Primary Wire Break | Include | Include | Equipment | 96 | 2023-03-21 | 5760 | keep | 0 | Mar | 2023 | 0.0039231 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-21 17:04 | 2023-03-21 20:23 | 40 | 3:19 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA T-5 A T-4 | S23032100183 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 199 | 2023-03-21 | 7960 | keep | 0 | Mar | 2023 | 0.0054215 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-21 17:07 | 2023-03-21 17:08 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23032100317 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 2067 | keep | 0 | Mar | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2023-03-21 17:09 | 2023-03-21 17:10 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23032100318 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 2067 | keep | 0 | Mar | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
HUMACAO | 2023-03-21 17:11 | 2023-03-21 17:38 | 1008 | 0:27 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN RISER DE SALIDA | C23032100225 | New_Event | Primary Wire Break | Include | Include | Equipment | 27 | 2023-03-21 | 27216 | keep | 0 | Mar | 2023 | 0.018537 | 0.00068654 | Sustained | FALSE | FALSE | Not_TMED_Event | 1008
MAYAGÃœEZ | 2023-03-21 17:11 | 2023-03-21 17:12 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23032100319 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 2067 | keep | 0 | Mar | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
SAN JUAN | 2023-03-21 17:15 | 2023-03-21 17:25 | 922 | 0:10 | T | ALIMENTADOR AMARRADO | DISPARO NTERRUPTOR SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1401-08 | S23032100000 | New_Event | Feeder Load Transferred | Include | Include | Other | 10 | 2023-03-21 | 9220 | keep | 0 | Mar | 2023 | 0.0062797 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-03-21 17:15 | 2023-03-21 17:25 | 135 | 0:10 | T | NO SE REPORTO CAUSA | DISPARO NTERRUPTOR SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-05 | S23032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2023-03-21 | 1350 | keep | 0 | Mar | 2023 | 0.00091948 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2023-03-21 17:20 | 2023-03-21 17:30 | 7 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO T-9 Y SE REPARO BARRA PEDESTAL REF. S23031300040 | S23032100361 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-03-21 | 70 | keep | 0 | Mar | 2023 | 4.7677e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-21 17:27 | 2023-03-21 21:43 | 2 | 4:16 | P | NO SE REPORTO CAUSA | 1 X 20 EN MONTURA Y 1 X 30 EN RISER | S23032100400 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 256 | 2023-03-21 | 512 | keep | 0 | Mar | 2023 | 0.00034872 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-03-21 17:34 | 2023-03-21 17:59 | 10 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23032100207 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-03-21 | 250 | keep | 0 | Mar | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-21 17:36 | 2023-03-21 17:39 | 922 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO NTERRUPTOR SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1401-08 | S23032100000 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-21 | 2766 | keep | 0 | Mar | 2023 | 0.0018839 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-21 17:36 | 2023-03-21 17:39 | 135 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO NTERRUPTOR SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-05 | S23032100000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-21 | 405 | keep | 0 | Mar | 2023 | 0.00027584 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-21 17:55 | 2023-03-21 17:56 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23032100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 45 | keep | 0 | Mar | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-03-21 17:57 | 2023-03-21 20:35 | 75 | 2:38 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | A23032100154 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2023-03-21 | 11850 | keep | 0 | Mar | 2023 | 0.008071 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-03-21 18:08 | 2023-03-21 18:09 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23032100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 45 | keep | 0 | Mar | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-03-21 18:26 | 2023-03-21 19:27 | 80 | 1:01 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23032100122 | New_Event | Animals | Include | Include | Wildlife | 61 | 2023-03-21 | 4880 | keep | 0 | Mar | 2023 | 0.0033237 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-21 18:35 | 2023-03-21 19:45 | 15 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23032100198 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-03-21 | 1050 | keep | 0 | Mar | 2023 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-03-21 18:48 | 2023-03-21 20:12 | 17 | 1:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR MAL TIEMPO | R23032100124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 84 | 2023-03-21 | 1428 | keep | 0 | Mar | 2023 | 0.0009726 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
PONCE | 2023-03-21 18:51 | 2023-03-22 19:30 | 118 | 24:39 | P | LINEA DE TRANSMISION 38KV | 2 X 65 EN CORTE DE LINEA LINEA PRIMARIA PARTIDA DEBIDO A TRAMO DE LINEA 11200 QUE CAYO SOBRE LA MISMA | P23032100199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1479 | 2023-03-21 | 174522 | keep | 0 | Mar | 2023 | 0.11887 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
BAYAMON | 2023-03-21 18:53 | 2023-03-22 12:16 | 1 | 17:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO XMR | B23032100043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1043 | 2023-03-21 | 1043 | keep | 0 | Mar | 2023 | 0.00071038 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-21 18:53 | 2023-03-22 12:55 | 150 | 18:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CORTE DE LINEA Y SE REPARO ALAMBRE EN EL SUELO RADIAL | B23032100201 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1082 | 2023-03-21 | 162300 | keep | 0 | Mar | 2023 | 0.11054 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-03-21 18:56 | 2023-03-21 20:32 | 15 | 1:36 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | R23032100126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-03-21 | 1440 | keep | 0 | Mar | 2023 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-03-21 19:01 | 2023-03-21 21:14 | 8 | 2:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A23032100166 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2023-03-21 | 1064 | keep | 0 | Mar | 2023 | 0.00072469 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-03-21 19:15 | 2023-03-21 20:00 | 312 | 0:45 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MACHETE PARA SECCIONALIZAR PUENTE ABIERTO Y CAJA COLGANDO | S23032100330 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 45 | 2023-03-21 | 14040 | keep | 0 | Mar | 2023 | 0.0095626 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-21 19:33 | 2023-03-21 20:28 | 45 | 0:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L Y 1 X 65 EN C/MAL TIEMPO LLUVIA | C23032100248 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 55 | 2023-03-21 | 2475 | keep | 0 | Mar | 2023 | 0.0016857 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
FAJARDO | 2023-03-21 19:40 | 2023-03-22 03:15 | 40 | 7:35 | P | CABLE SOTERRADO AVERIADO | 2 SMU 20 DE 40 EN SU - 9 AVERIA DEL T-16 @ T-15 | R23032100129 | New_Event | UG Cable Fault | Include | Include | Equipment | 455 | 2023-03-21 | 18200 | keep | 0 | Mar | 2023 | 0.012396 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-03-21 20:01 | 2023-03-21 20:03 | 1590 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2303210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-21 | 3180 | keep | 0 | Mar | 2023 | 0.0021659 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
CAGUAS | 2023-03-21 20:03 | 2023-03-21 21:06 | 59 | 1:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23032100252 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2023-03-21 | 3717 | keep | 0 | Mar | 2023 | 0.0025316 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
HUMACAO | 2023-03-21 20:11 | 2023-03-22 07:57 | 20 | 11:46 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23032100268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 706 | 2023-03-21 | 14120 | keep | 0 | Mar | 2023 | 0.0096171 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-03-21 20:28 | 2023-03-22 09:35 | 20 | 13:07 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23032100368 | New_Event | Vegetation Contact | Include | Include | Vegetation | 787 | 2023-03-21 | 15740 | keep | 0 | Mar | 2023 | 0.01072 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-21 20:39 | 2023-03-21 23:00 | 164 | 2:21 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA CORTE DE LINEA Y A CAJA DE TRANSFORMADOR | B23032100214 | New_Event | Primary Wire Break | Include | Include | Equipment | 141 | 2023-03-21 | 23124 | keep | 0 | Mar | 2023 | 0.01575 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
VEGA BAJA | 2023-03-21 20:43 | 2023-03-21 23:05 | 150 | 2:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CONVERTIDOR NO SE ENCONTRO CAUSA | A23032100174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2023-03-21 | 21300 | keep | 0 | Mar | 2023 | 0.014507 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-03-21 20:55 | 2023-03-21 22:18 | 976 | 1:23 | T | DESGANCHE | SE SECCIONALIZO CONDUCTOR EN EL SUELO POR DESGANCHE | C23032100312 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-03-21 | 81008 | keep | 0 | Mar | 2023 | 0.055174 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
SAN JUAN | 2023-03-21 21:36 | 2023-03-21 21:42 | 169 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-03-21 | 1014 | keep | 0 | Mar | 2023 | 0.00069063 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
SAN JUAN | 2023-03-21 21:36 | 2023-03-21 21:42 | 1356 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-03-21 | 8136 | keep | 0 | Mar | 2023 | 0.0055414 | 0.00092357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1356
SAN JUAN | 2023-03-21 21:43 | 2023-03-21 21:48 | 948 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23032100000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-03-21 | 4740 | keep | 0 | Mar | 2023 | 0.0032284 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-21 21:48 | 2023-03-22 14:36 | 2 | 16:48 | P | NO SE REPORTO CAUSA | 1 X 20 EN MONTURA Y 1 X 30 EN RISER | S23032100400 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1008 | 2023-03-21 | 2016 | keep | 0 | Mar | 2023 | 0.0013731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-03-21 21:48 | 2023-03-22 00:15 | 70 | 2:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R23032100139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2023-03-21 | 10290 | keep | 0 | Mar | 2023 | 0.0070085 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-03-21 21:54 | 2023-03-22 13:00 | 14 | 15:06 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M23032100378 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 906 | 2023-03-21 | 12684 | keep | 0 | Mar | 2023 | 0.008639 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-03-21 22:04 | 2023-03-22 10:08 | 98 | 12:04 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23032100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 724 | 2023-03-21 | 70952 | keep | 0 | Mar | 2023 | 0.048325 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
BAYAMON | 2023-03-21 22:13 | 2023-03-22 01:36 | 93 | 3:23 | P | ANIMAL | 1 X 65 EN PROVISIONAL AVE CRUZO FASE | B23032100224 | New_Event | Animals | Include | Include | Wildlife | 203 | 2023-03-21 | 18879 | keep | 0 | Mar | 2023 | 0.012858 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
BARRANQUITAS | 2023-03-21 22:18 | 2023-03-22 | 195 | 1:42 | P | DESGANCHE | ABRIO PUENTES Y RETIRO CONDUCTOR, TRAMO SIN CARGA SE REALIZO DESGANCHE | C23032100312 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-03-21 | 19890 | keep | 0 | Mar | 2023 | 0.013547 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-21 22:18 | 2023-03-22 09:10 | 24 | 10:52 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN TRANSFORMADOR SECUNDARIA CRUZADA | A23032100179 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 652 | 2023-03-21 | 15648 | keep | 0 | Mar | 2023 | 0.010658 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CAGUAS | 2023-03-21 22:22 | 2023-03-21 22:23 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23032100334 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 918 | keep | 0 | Mar | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-03-21 22:31 | 2023-03-22 01:35 | 230 | 3:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L FUERTES LLUVIAS | C23032100335 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 184 | 2023-03-21 | 42320 | keep | 0 | Mar | 2023 | 0.028824 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
CANOVANAS | 2023-03-21 22:52 | 2023-03-21 22:53 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032100144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 3699 | keep | 0 | Mar | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
SAN JUAN | 2023-03-21 23:21 | 2023-03-21 23:22 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-21 | 4291 | keep | 0 | Mar | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
BARRANQUITAS | 2023-03-22 | 2023-03-22 17:15 | 89 | 17:15 | P | DESGANCHE | CG-230322-01 SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | C23032200028 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1035 | 2023-03-22 | 92115 | keep | 0 | Mar | 2023 | 0.062739 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-22 00:02 | 2023-03-22 00:04 | 143 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 80% DEL 1404-07 | S23032200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-22 | 286 | keep | 0 | Mar | 2023 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-03-22 00:02 | 2023-03-22 00:04 | 1085 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 80% POR 1404-06 | S23032200002 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-22 | 2170 | keep | 0 | Mar | 2023 | 0.001478 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2023-03-22 00:02 | 2023-03-22 04:40 | 75 | 4:38 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA ARBOL SOBRE LINEA | B23032200001 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 278 | 2023-03-22 | 20850 | keep | 0 | Mar | 2023 | 0.014201 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-03-22 00:37 | 2023-03-22 00:38 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032200007 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 3699 | keep | 0 | Mar | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2023-03-22 00:43 | 2023-03-22 00:44 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032200007 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 3699 | keep | 0 | Mar | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
FAJARDO | 2023-03-22 00:47 | 2023-03-22 06:00 | 35 | 5:13 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR DE PROVICIONAL AEREO NO FUNDIO | R23032200019 | New_Event | Primary Wire Break | Include | Include | Equipment | 313 | 2023-03-22 | 10955 | keep | 0 | Mar | 2023 | 0.0074614 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-03-22 00:54 | 2023-03-22 10:58 | 38 | 10:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REMPLAZO AISLADOR | R23032200013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 604 | 2023-03-22 | 22952 | keep | 0 | Mar | 2023 | 0.015633 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
VEGA BAJA | 2023-03-22 01:12 | 2023-03-22 12:05 | 10 | 10:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23032200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2023-03-22 | 6530 | keep | 0 | Mar | 2023 | 0.0044476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-22 02:24 | 2023-03-22 02:25 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 308 | keep | 0 | Mar | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2023-03-22 02:41 | 2023-03-22 08:10 | 30 | 5:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23032200002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 329 | 2023-03-22 | 9870 | keep | 0 | Mar | 2023 | 0.0067224 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-22 03:11 | 2023-03-22 12:00 | 80 | 8:49 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 529 | 2023-03-22 | 42320 | keep | 0 | Mar | 2023 | 0.028824 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-03-22 03:15 | 2023-03-22 17:33 | 10 | 14:18 | P | CABLE SOTERRADO AVERIADO | 1 X 15 EN PROVICIONAL AERERO DE SU-10 A T15 TRABAJAR INSTALANADO PROVISIONAL DE EXISTENTE HACIA T-15 SJ-230322-50 | R23032100129 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 858 | 2023-03-22 | 8580 | keep | 0 | Mar | 2023 | 0.0058438 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-22 03:48 | 2023-03-22 03:52 | 362 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 90% POR 1620-01 | S23032200000 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-03-22 | 1448 | keep | 0 | Mar | 2023 | 0.00098623 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-03-22 03:48 | 2023-03-22 03:52 | 36 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 90% DEL 1336-10 | S23032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-22 | 144 | keep | 0 | Mar | 2023 | 9.8078e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
VEGA BAJA | 2023-03-22 04:18 | 2023-03-22 04:19 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 3332 | keep | 0 | Mar | 2023 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
CANOVANAS | 2023-03-22 04:55 | 2023-03-22 04:56 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032200023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 3464 | keep | 0 | Mar | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2023-03-22 05:26 | 2023-03-22 08:29 | 99 | 3:03 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | R23032200028 | New_Event | Animals | Include | Include | Wildlife | 183 | 2023-03-22 | 18117 | keep | 0 | Mar | 2023 | 0.012339 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
AGUADILLA | 2023-03-22 06:17 | 2023-03-22 09:10 | 300 | 2:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23032200004 | New_Event | Cutout Failure | Include | Include | Equipment | 173 | 2023-03-22 | 51900 | keep | 0 | Mar | 2023 | 0.035349 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-03-22 06:30 | 2023-03-22 12:00 | 250 | 5:30 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | S23032200042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 330 | 2023-03-22 | 82500 | keep | 0 | Mar | 2023 | 0.05619 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2023-03-22 06:46 | 2023-03-22 06:47 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23032200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 1227 | keep | 0 | Mar | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
GUAYAMA | 2023-03-22 06:48 | 2023-03-22 11:06 | 80 | 4:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO AISLACION 1 X 50 EN CORTE DE LINEA | P23032200020 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 258 | 2023-03-22 | 20640 | keep | 0 | Mar | 2023 | 0.014058 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-03-22 06:54 | 2023-03-22 06:55 | 4279 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | P23032200021 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-22 | 4279 | keep | 0 | Mar | 2023 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2023-03-22 06:55 | 2023-03-22 12:44 | 1 | 5:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIARON 2 CAJAS PRIMARIAS DE CORTE DE LINEA Y 2 X 50 Y 1 X 10 EN TRANSFORMADOR | P23032200045 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 349 | 2023-03-22 | 349 | keep | 0 | Mar | 2023 | 0.0002377 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-22 07:00 | 2023-03-22 15:42 | 33 | 8:42 | P | DESGANCHE | 1 X 50 Y 1 X 60 EN C/L | S23032200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 522 | 2023-03-22 | 17226 | keep | 0 | Mar | 2023 | 0.011733 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
ARECIBO | 2023-03-22 07:08 | 2023-03-22 09:35 | 6 | 2:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A23032200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-03-22 | 882 | keep | 0 | Mar | 2023 | 0.00060073 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-03-22 07:12 | 2023-03-22 11:30 | 1 | 4:18 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO SE ENCONTRO CAUSA | M23032200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2023-03-22 | 258 | keep | 0 | Mar | 2023 | 0.00017572 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-22 07:21 | 2023-03-22 12:20 | 8 | 4:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23032200042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 299 | 2023-03-22 | 2392 | keep | 0 | Mar | 2023 | 0.0016292 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-22 07:22 | 2023-03-22 07:23 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C23032200008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 476 | keep | 0 | Mar | 2023 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-03-22 07:22 | 2023-03-22 07:23 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C23032200008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 1655 | keep | 0 | Mar | 2023 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-03-22 07:22 | 2023-03-22 07:23 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C23032200008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 361 | keep | 0 | Mar | 2023 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-03-22 07:22 | 2023-03-22 07:23 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C23032200008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 2842 | keep | 0 | Mar | 2023 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-03-22 07:22 | 2023-03-22 07:23 | 1702 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C23032200009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 1702 | keep | 0 | Mar | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-03-22 07:22 | 2023-03-22 07:23 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C23032200009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 918 | keep | 0 | Mar | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-03-22 07:22 | 2023-03-22 07:23 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 | C23032200011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 1725 | keep | 0 | Mar | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
CANOVANAS | 2023-03-22 07:24 | 2023-03-22 10:37 | 86 | 3:13 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23032200060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2023-03-22 | 16598 | keep | 0 | Mar | 2023 | 0.011305 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
CAGUAS | 2023-03-22 07:24 | 2023-03-22 12:49 | 20 | 5:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C23032200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2023-03-22 | 6500 | keep | 0 | Mar | 2023 | 0.0044271 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-03-22 07:24 | 2023-03-22 13:00 | 1 | 5:36 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23032200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 336 | 2023-03-22 | 336 | keep | 0 | Mar | 2023 | 0.00022885 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-03-22 07:38 | 2023-03-22 07:39 | 2457 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23032200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 2457 | keep | 0 | Mar | 2023 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
CANOVANAS | 2023-03-22 07:42 | 2023-03-22 10:45 | 86 | 3:03 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23032200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-03-22 | 15738 | keep | 0 | Mar | 2023 | 0.010719 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
MAYAGÃœEZ | 2023-03-22 07:48 | 2023-03-22 10:00 | 10 | 2:12 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR SE REPARO NEUTRAL PRIMARIO ROTO | M23032200015 | New_Event | Primary Wire Break | Include | Include | Equipment | 132 | 2023-03-22 | 1320 | keep | 0 | Mar | 2023 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-22 07:50 | 2023-03-22 13:33 | 80 | 5:43 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23032200018 | New_Event | Animals | Include | Include | Wildlife | 343 | 2023-03-22 | 27440 | keep | 0 | Mar | 2023 | 0.018689 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-03-22 07:51 | 2023-03-22 07:52 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23032200010 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 1227 | keep | 0 | Mar | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
YAUCO | 2023-03-22 08:14 | 2023-03-22 10:29 | 1 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO SECUNDARIA 1 X 5 EN TRANSFORMADOR | P23032200029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2023-03-22 | 135 | keep | 0 | Mar | 2023 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-03-22 08:27 | 2023-03-22 12:50 | 4 | 4:23 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23032200022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2023-03-22 | 1052 | keep | 0 | Mar | 2023 | 0.00071651 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-03-22 08:29 | 2023-03-22 14:58 | 6 | 6:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 Y 1 X 40 EN C/L SE REPARO LINEA PRIMARIA | B23032200025 | New_Event | Primary Wire Break | Include | Include | Equipment | 389 | 2023-03-22 | 2334 | keep | 0 | Mar | 2023 | 0.0015897 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-03-22 08:36 | 2023-03-22 12:05 | 3 | 3:29 | P | NO SE REPORTO CAUSA | 1X100 EN RISER | S23032200075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2023-03-22 | 627 | keep | 0 | Mar | 2023 | 0.00042705 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2023-03-22 08:51 | 2023-03-22 13:45 | 75 | 4:54 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | P23032200038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-03-22 | 22050 | keep | 0 | Mar | 2023 | 0.015018 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-03-22 08:55 | 2023-03-22 09:47 | 10 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23032200025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-03-22 | 520 | keep | 0 | Mar | 2023 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-22 08:57 | 2023-03-22 09:01 | 2493 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23032200033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-22 | 9972 | keep | 0 | Mar | 2023 | 0.0067919 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
UTUADO | 2023-03-22 09:13 | 2023-03-22 10:50 | 40 | 1:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23032200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-03-22 | 3880 | keep | 0 | Mar | 2023 | 0.0026427 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-22 09:35 | 2023-03-22 17:25 | 80 | 7:50 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L SE DESCRUZARON LINEAS | B23032200041 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 470 | 2023-03-22 | 37600 | keep | 0 | Mar | 2023 | 0.025609 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-22 09:55 | 2023-03-22 18:29 | 9 | 8:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR Y SE REPARO SECUNDARIA | S23032200126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 514 | 2023-03-22 | 4626 | keep | 0 | Mar | 2023 | 0.0031507 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-03-22 10:06 | 2023-03-22 14:50 | 100 | 4:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA, NO FUNDIO FUSIBLE | B23032200050 | New_Event | Primary Wire Break | Include | Include | Equipment | 284 | 2023-03-22 | 28400 | keep | 0 | Mar | 2023 | 0.019343 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-03-22 10:11 | 2023-03-22 12:29 | 14 | 2:18 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE X AVE | C23032200036 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-03-22 | 1932 | keep | 0 | Mar | 2023 | 0.0013159 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-03-22 10:29 | 2023-03-22 14:37 | 188 | 4:08 | P | DESGANCHE | 2 X 80 EN C/L Y DESGANCHE | S23032200140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-03-22 | 46624 | keep | 0 | Mar | 2023 | 0.031755 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
GUAYAMA | 2023-03-22 10:34 | 2023-03-22 13:01 | 12 | 2:27 | P | PROBLEMA DEL CLIENTE | SE REMPLAZO PEDESTAL PRIVADO HAY AVERIA DEL PEDESTAL AL METER BANK PROBLEMA INTERNO | P23032200062 | New_Event | Customer-Related Interruption | Include | Include | Public | 147 | 2023-03-22 | 1764 | keep | 0 | Mar | 2023 | 0.0012015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-22 10:42 | 2023-03-22 13:40 | 40 | 2:58 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23032200059 | New_Event | Animals | Include | Include | Wildlife | 178 | 2023-03-22 | 7120 | keep | 0 | Mar | 2023 | 0.0048494 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-03-22 10:54 | 2023-03-22 10:58 | 922 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1401-08 LLEVA LA CARGA DEL 1346-05 SE CERRO POR CONTROL | S23032200159 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-03-22 | 3688 | keep | 0 | Mar | 2023 | 0.0025119 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-03-22 10:54 | 2023-03-22 10:58 | 135 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 LLEVA LA CARGA DEL 1346-05 SE CERRO POR CONTROL | S23032200159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-22 | 540 | keep | 0 | Mar | 2023 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2023-03-22 11:03 | 2023-03-22 13:27 | 922 | 2:24 | T | ALIMENTADOR AMARRADO | CARGA TRANSFERIDA AL 1401-08 PERSONAL DE CAMPO NO ENCONTRO NADA DURANTE EL PATRULLAJE Y SE VOVLIO A CERRAR EL AMARRE ENTRE AMBOS INTERRUPTORES - EN SERVICIO TOTAL | S23032200242 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 144 | 2023-03-22 | 132768 | keep | 0 | Mar | 2023 | 0.090428 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-03-22 11:03 | 2023-03-22 12:52 | 135 | 1:49 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1346-05 SE ABRIO EL AMARRE ENTRE AMBOS INTERRUPTORES PARA SECCIONALIZAR POR POSIBLE AVERIA - PROBO BUENO | S23032200242 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 109 | 2023-03-22 | 14715 | keep | 0 | Mar | 2023 | 0.010022 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2023-03-22 11:11 | 2023-03-22 17:30 | 15 | 6:19 | P | CAUSAS EXTERNAS | PERSONAL PRIVADO HACIENDO PODA CRUZO SECUNDARIA | B23032200060 | New_Event | Damage From Public | Include | Include | Public | 379 | 2023-03-22 | 5685 | keep | 0 | Mar | 2023 | 0.003872 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-03-22 11:13 | 2023-03-22 11:47 | 8 | 0:34 | P | CONDUCTOR ROTO O ABIERTO | SE RERPARO CONECTOR SULFATADO | P23032200068 | New_Event | Primary Wire Break | Include | Include | Equipment | 34 | 2023-03-22 | 272 | keep | 0 | Mar | 2023 | 0.00018526 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-03-22 11:18 | 2023-03-22 11:19 | 2231 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23032200037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 2231 | keep | 0 | Mar | 2023 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
FAJARDO | 2023-03-22 11:35 | 2023-03-22 12:05 | 2 | 0:30 | P | OTRAS CAUSAS | SE ABRIO C/L PARA DESCONECTAR CLIENTE POR FALTA DE PAGO SE AFECTARON 2 CASAS | R23032200087 | New_Event | Other Causes | Include | Include | Other | 30 | 2023-03-22 | 60 | keep | 0 | Mar | 2023 | 4.0866e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-03-22 11:36 | 2023-03-22 20:05 | 6 | 8:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REMPLAZO SECUNDARIA AVERIADA Y SE RELOCALIZO POSTE | A23032200038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 509 | 2023-03-22 | 3054 | keep | 0 | Mar | 2023 | 0.0020801 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-03-22 11:41 | 2023-03-22 14:10 | 7 | 2:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23032200039 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 149 | 2023-03-22 | 1043 | keep | 0 | Mar | 2023 | 0.00071038 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-22 12:00 | 2023-03-22 21:10 | 280 | 9:10 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | REEMPLAZAR DESCONECTIVO DEL SU-04 SJ-230322-02 | S23032200042 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 550 | 2023-03-22 | 154000 | keep | 0 | Mar | 2023 | 0.10489 | 0.00019071 | Sustained | FALSE | FALSE | Not_TMED_Event | 280
AGUADILLA | 2023-03-22 12:00 | 2023-03-22 13:00 | 16 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23032200076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-03-22 | 960 | keep | 0 | Mar | 2023 | 0.00065385 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
VEGA BAJA | 2023-03-22 12:00 | 2023-03-22 15:58 | 60 | 3:58 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 65 EN C/L SE RETEZO PRIMARIA | B23032200067 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 238 | 2023-03-22 | 14280 | keep | 0 | Mar | 2023 | 0.009726 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-03-22 12:26 | 2023-03-22 14:53 | 10 | 2:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO ALAMBRE SECUNDARIO SE REPARO CONECTORES SECUNDARIAOS | C23032200063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 147 | 2023-03-22 | 1470 | keep | 0 | Mar | 2023 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-22 12:35 | 2023-03-22 18:46 | 15 | 6:11 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23032200235 | New_Event | Primary Wire Break | Include | Include | Equipment | 371 | 2023-03-22 | 5565 | keep | 0 | Mar | 2023 | 0.0037903 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-03-22 12:38 | 2023-03-22 15:38 | 357 | 3:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L VIENTOS MAL TIEMPO | C23032200065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 180 | 2023-03-22 | 64260 | keep | 0 | Mar | 2023 | 0.043767 | 0.00024315 | Sustained | FALSE | FALSE | Not_TMED_Event | 357
VEGA BAJA | 2023-03-22 12:53 | 2023-03-22 12:54 | 2231 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23032200044 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 2231 | keep | 0 | Mar | 2023 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
HUMACAO | 2023-03-22 12:58 | 2023-03-22 15:57 | 50 | 2:59 | P | DESGANCHE | SE REEMPLAZO CAJA Y 1 X 50 EN C/L SE REALIZO DESGANCHE | C23032200070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-03-22 | 8950 | keep | 0 | Mar | 2023 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-22 13:01 | 2023-03-22 13:02 | 2231 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23032200045 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 2231 | keep | 0 | Mar | 2023 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
SAN JUAN | 2023-03-22 13:04 | 2023-03-22 16:21 | 11 | 3:17 | P | NO SE REPORTO CAUSA | 1 X 140 EN RISER TRASPATIO | S23032200257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2023-03-22 | 2167 | keep | 0 | Mar | 2023 | 0.0014759 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-03-22 13:04 | 2023-03-22 16:21 | 11 | 3:17 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S23032200257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2023-03-22 | 2167 | keep | 0 | Mar | 2023 | 0.0014759 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2023-03-22 13:29 | 2023-03-22 16:15 | 8 | 2:46 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS | M23032200104 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 166 | 2023-03-22 | 1328 | keep | 0 | Mar | 2023 | 0.00090449 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-03-22 13:30 | 2023-03-22 14:45 | 70 | 1:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032200105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-03-22 | 5250 | keep | 0 | Mar | 2023 | 0.0035758 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-03-22 13:40 | 2023-03-22 14:18 | 2 | 0:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S23032200267 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2023-03-22 | 76 | keep | 0 | Mar | 2023 | 5.1763e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-03-22 13:51 | 2023-03-22 17:30 | 71 | 3:39 | P | ARBOL SOBRE LINEA | 1 X 80 EN C/L Y SE REMOVIO ARBOL SOBRE LINEA | S23032200270 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 219 | 2023-03-22 | 15549 | keep | 0 | Mar | 2023 | 0.01059 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
MAYAGÃœEZ | 2023-03-22 13:56 | 2023-03-22 13:57 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23032200113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 312 | keep | 0 | Mar | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
BAYAMON | 2023-03-22 14:00 | 2023-03-22 16:58 | 140 | 2:58 | P | DESGANCHE | 1 X 65 EN C/L | B23032200084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-03-22 | 24920 | keep | 0 | Mar | 2023 | 0.016973 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
MAYAGÃœEZ | 2023-03-22 14:12 | 2023-03-22 19:50 | 103 | 5:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032200115 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 338 | 2023-03-22 | 34814 | keep | 0 | Mar | 2023 | 0.023712 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
CAGUAS | 2023-03-22 14:13 | 2023-03-22 14:14 | 718 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23032200085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 718 | keep | 0 | Mar | 2023 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
FAJARDO | 2023-03-22 14:15 | 2023-03-22 15:23 | 120 | 1:08 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | R23032200101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-03-22 | 8160 | keep | 0 | Mar | 2023 | 0.0055577 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2023-03-22 14:16 | 2023-03-22 15:00 | 5 | 0:44 | P | DESGANCHE | 1 X 10 EN XMR Y DESGANCHE | R23032200102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2023-03-22 | 220 | keep | 0 | Mar | 2023 | 0.00014984 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-22 14:23 | 2023-03-22 14:57 | 10 | 0:34 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO Y SE RELAIZO DESGANCHE SECUNDARIO | S23032200285 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 34 | 2023-03-22 | 340 | keep | 0 | Mar | 2023 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-22 14:23 | 2023-03-22 14:24 | 2231 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23032200066 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 2231 | keep | 0 | Mar | 2023 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
HUMACAO | 2023-03-22 14:24 | 2023-03-22 16:27 | 15 | 2:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO 125 PIES DE SECUNDARIA | C23032200088 | New_Event | Secondary Wire Break | Include | Include | Equipment | 123 | 2023-03-22 | 1845 | keep | 0 | Mar | 2023 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-03-22 14:25 | 2023-03-22 17:20 | 20 | 2:55 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032200122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-03-22 | 3500 | keep | 0 | Mar | 2023 | 0.0023838 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-03-22 14:28 | 2023-03-22 16:50 | 75 | 2:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA AREA REQUIERE DESGANCHE | M23032200123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-03-22 | 10650 | keep | 0 | Mar | 2023 | 0.0072537 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-03-22 14:41 | 2023-03-22 15:36 | 1 | 0:55 | P | NO SE REPORTO CAUSA | SE ENCONTRO GANGA DEL SU-22 AL T22 ABIERTA Y FUE CERRADA. | R23032200106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2023-03-22 | 55 | keep | 0 | Mar | 2023 | 3.746e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-03-22 14:46 | 2023-03-22 22:04 | 50 | 7:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGACHE | A23032200072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 438 | 2023-03-22 | 21900 | keep | 0 | Mar | 2023 | 0.014916 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-22 14:48 | 2023-03-22 16:50 | 18 | 2:02 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO POSTE SECUNDARIO | S23032200290 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 122 | 2023-03-22 | 2196 | keep | 0 | Mar | 2023 | 0.0014957 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2023-03-22 14:48 | 2023-03-22 14:49 | 449 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | P23032200104 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-22 | 449 | keep | 0 | Mar | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
BARRANQUITAS | 2023-03-22 14:49 | 2023-03-22 17:28 | 85 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO | C23032200094 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2023-03-22 | 13515 | keep | 0 | Mar | 2023 | 0.009205 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
GUAYAMA | 2023-03-22 14:49 | 2023-03-22 19:47 | 129 | 4:58 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO 1 X 100 ENTRADA CONVERTIDOR 1 X 140 EN SALIDA DEL CONVERTIDOR | P23032200108 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 298 | 2023-03-22 | 38442 | keep | 0 | Mar | 2023 | 0.026183 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
VEGA BAJA | 2023-03-22 14:57 | 2023-03-22 20:24 | 124 | 5:27 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L SE CERRO PUENTE ABIERTO | B23032200098 | New_Event | Primary Wire Break | Include | Include | Equipment | 327 | 2023-03-22 | 40548 | keep | 0 | Mar | 2023 | 0.027617 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
PONCE | 2023-03-22 15:00 | 2023-03-22 15:28 | 13 | 0:28 | P | CONDUCTOR ROTO O ABIERTO | SE RETIRA CARGA A TRANSFORMADOR PARA CERRAR NEUTRAL PRIMARIO | P23032200109 | New_Event | Primary Wire Break | Include | Include | Equipment | 28 | 2023-03-22 | 364 | keep | 0 | Mar | 2023 | 0.00024792 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2023-03-22 15:03 | 2023-03-22 17:05 | 2 | 2:02 | P | PARARRAYOS DEFECTUOSO | 2 X 100 EN RISER PARARRAYOS DEFECTUOSO | M23032200138 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 122 | 2023-03-22 | 244 | keep | 0 | Mar | 2023 | 0.00016619 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-03-22 15:11 | 2023-03-22 15:12 | 1843 | 0:01 | T | DESGANCHE | RECIERRE | C23032200102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-22 | 1843 | keep | 0 | Mar | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
GUAYAMA | 2023-03-22 15:11 | 2023-03-22 17:59 | 19 | 2:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA 1 X 30 EN TRANSFORMADOR | P23032200115 | New_Event | Cutout Failure | Include | Include | Equipment | 168 | 2023-03-22 | 3192 | keep | 0 | Mar | 2023 | 0.0021741 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BARRANQUITAS | 2023-03-22 15:12 | 2023-03-22 17:08 | 80 | 1:56 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23032200118 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-03-22 | 9280 | keep | 0 | Mar | 2023 | 0.0063206 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-03-22 15:15 | 2023-03-22 16:11 | 199 | 0:56 | P | PARARRAYOS DEFECTUOSO | CG-230322-02 SE REEMPLAZO PARARRAYO Y SE CORRIGIO PUNTO CALIENTE EN RISER DE LA GIS SERVICE STATION DE AGUAS BUENAS | C23032200095 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 56 | 2023-03-22 | 11144 | keep | 0 | Mar | 2023 | 0.0075901 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BARRANQUITAS | 2023-03-22 15:29 | 2023-03-22 18:38 | 1 | 3:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO | C23032200107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2023-03-22 | 189 | keep | 0 | Mar | 2023 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-22 15:33 | 2023-03-22 16:04 | 2 | 0:31 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN RISER DESGANCHE PRIMARIO | S23032200308 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2023-03-22 | 62 | keep | 0 | Mar | 2023 | 4.2228e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-03-22 15:38 | 2023-03-22 17:53 | 2 | 2:15 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINE 1 X 15 EN TRANSFORMADOR BAJANTE PRIMARIO CRUZADO | P23032200131 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 135 | 2023-03-22 | 270 | keep | 0 | Mar | 2023 | 0.0001839 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2023-03-22 15:41 | 2023-03-22 15:42 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23032200134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 1945 | keep | 0 | Mar | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
YAUCO | 2023-03-22 15:42 | 2023-03-23 01:30 | 20 | 9:48 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | P23032200133 | New_Event | Primary Wire Break | Include | Include | Equipment | 588 | 2023-03-22 | 11760 | keep | 0 | Mar | 2023 | 0.0080097 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-22 15:57 | 2023-03-22 18:40 | 50 | 2:43 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23032200152 | New_Event | Primary Wire Break | Include | Include | Equipment | 163 | 2023-03-22 | 8150 | keep | 0 | Mar | 2023 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-22 16:10 | 2023-03-22 17:19 | 12 | 1:09 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE XMR | B23032200105 | New_Event | Primary Wire Break | Include | Include | Equipment | 69 | 2023-03-22 | 828 | keep | 0 | Mar | 2023 | 0.00056395 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-03-22 16:20 | 2023-03-22 20:19 | 20 | 3:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23032200092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2023-03-22 | 4780 | keep | 0 | Mar | 2023 | 0.0032556 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-03-22 16:30 | 2023-03-22 18:00 | 40 | 1:30 | P | PARARRAYOS DEFECTUOSO | 2 X 80 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M23032200167 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 90 | 2023-03-22 | 3600 | keep | 0 | Mar | 2023 | 0.0024519 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-03-22 16:40 | 2023-03-22 20:36 | 3 | 3:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON DOS CAJAS PRIMARIAS Y 2 X 15 EN TRANSFORMADOR | P23032200141 | New_Event | Cutout Failure | Include | Include | Equipment | 236 | 2023-03-22 | 708 | keep | 0 | Mar | 2023 | 0.00048222 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2023-03-22 16:42 | 2023-03-23 11:30 | 40 | 18:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23032200094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1128 | 2023-03-22 | 45120 | keep | 0 | Mar | 2023 | 0.030731 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-22 16:46 | 2023-03-22 19:35 | 50 | 2:49 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | B23032200109 | New_Event | Primary Wire Break | Include | Include | Equipment | 169 | 2023-03-22 | 8450 | keep | 0 | Mar | 2023 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-22 16:54 | 2023-03-23 11:50 | 70 | 18:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23032300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1136 | 2023-03-22 | 79520 | keep | 0 | Mar | 2023 | 0.054161 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-03-22 17:07 | 2023-03-22 19:45 | 80 | 2:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M23032200181 | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2023-03-22 | 12640 | keep | 0 | Mar | 2023 | 0.008609 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-03-22 17:19 | 2023-03-23 09:10 | 2 | 15:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23032200102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 951 | 2023-03-22 | 1902 | keep | 0 | Mar | 2023 | 0.0012954 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-03-22 17:32 | 2023-03-22 18:46 | 125 | 1:14 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23032200112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2023-03-22 | 9250 | keep | 0 | Mar | 2023 | 0.0063001 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-03-22 17:48 | 2023-03-22 17:49 | 1702 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | C23032200128 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-03-22 | 1702 | keep | 0 | Mar | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-03-22 17:49 | 2023-03-22 19:26 | 77 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO | C23032200131 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2023-03-22 | 7469 | keep | 0 | Mar | 2023 | 0.0050871 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
VEGA BAJA | 2023-03-22 17:52 | 2023-03-23 13:22 | 6 | 19:30 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR LINEAS CRUZADAS | A23032200109 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 1170 | 2023-03-22 | 7020 | keep | 0 | Mar | 2023 | 0.0047813 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-03-22 17:53 | 2023-03-22 18:45 | 8 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23032200129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-03-22 | 416 | keep | 0 | Mar | 2023 | 0.00028334 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-22 17:58 | 2023-03-22 19:38 | 206 | 1:40 | P | ANIMAL | 2 X 100 EN C/L Y 1 X 15 EN XMR CRUCE POR AVE | C23032200132 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-03-22 | 20600 | keep | 0 | Mar | 2023 | 0.014031 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
BAYAMON | 2023-03-22 18:32 | 2023-03-22 22:20 | 15 | 3:48 | P | DESGANCHE | SE REALIZO DESGANCHE Y 1 X 20 EN RISER | B23032200122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-03-22 | 3420 | keep | 0 | Mar | 2023 | 0.0023293 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-22 18:35 | 2023-03-23 11:06 | 100 | 16:31 | P | NO SE REPORTO CAUSA | 2X80 EN C/L | S23032200369 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 991 | 2023-03-22 | 99100 | keep | 0 | Mar | 2023 | 0.067497 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-22 18:49 | 2023-03-22 20:52 | 61 | 2:03 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L 1 X50 EN RISER | R23032200121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2023-03-22 | 7503 | keep | 0 | Mar | 2023 | 0.0051103 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
MAYAGÃœEZ | 2023-03-22 18:57 | 2023-03-23 09:49 | 80 | 14:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M23032200203 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 892 | 2023-03-22 | 71360 | keep | 0 | Mar | 2023 | 0.048603 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-03-22 18:59 | 2023-03-22 19:00 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23032200139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-22 | 2126 | keep | 0 | Mar | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
YAUCO | 2023-03-22 19:10 | 2023-03-22 19:11 | 1339 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 1339 | keep | 0 | Mar | 2023 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-03-22 19:10 | 2023-03-22 19:11 | 470 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 470 | keep | 0 | Mar | 2023 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2023-03-22 19:10 | 2023-03-22 19:11 | 2483 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 2483 | keep | 0 | Mar | 2023 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2023-03-22 19:10 | 2023-03-22 19:11 | 2190 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 2190 | keep | 0 | Mar | 2023 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2023-03-22 19:10 | 2023-03-22 19:11 | 3006 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200211 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 3006 | keep | 0 | Mar | 2023 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2023-03-22 19:10 | 2023-03-22 19:11 | 179 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200211 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 179 | keep | 0 | Mar | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2023-03-22 19:10 | 2023-03-22 19:11 | 107 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 107 | keep | 0 | Mar | 2023 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2023-03-22 19:10 | 2023-03-22 19:11 | 1666 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 1666 | keep | 0 | Mar | 2023 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2023-03-22 19:10 | 2023-03-22 19:11 | 4387 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 4387 | keep | 0 | Mar | 2023 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2023-03-22 19:10 | 2023-03-22 19:11 | 3147 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200214 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 3147 | keep | 0 | Mar | 2023 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2023-03-22 19:10 | 2023-03-22 19:11 | 4304 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23032200214 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-22 | 4304 | keep | 0 | Mar | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2023-03-22 19:19 | 2023-03-22 23:18 | 580 | 3:59 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y 1 X 140 EN C/L | B23032200131 | New_Event | Primary Wire Break | Include | Include | Equipment | 239 | 2023-03-22 | 138620 | keep | 0 | Mar | 2023 | 0.094413 | 0.00039504 | Sustained | FALSE | FALSE | Not_TMED_Event | 580
CANOVANAS | 2023-03-22 19:30 | 2023-03-22 20:15 | 61 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR TOMA Y REMPLAZAR CONECTORES | R23032200124 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-03-22 | 2745 | keep | 0 | Mar | 2023 | 0.0018696 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
VEGA BAJA | 2023-03-22 19:33 | 2023-03-22 23:48 | 80 | 4:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A23032200140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2023-03-22 | 20400 | keep | 0 | Mar | 2023 | 0.013894 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-03-22 19:35 | 2023-03-23 08:50 | 14 | 13:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C23032200143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 795 | 2023-03-22 | 11130 | keep | 0 | Mar | 2023 | 0.0075806 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-03-22 20:09 | 2023-03-23 09:15 | 15 | 13:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | A23032200150 | New_Event | Cutout Failure | Include | Include | Equipment | 786 | 2023-03-22 | 11790 | keep | 0 | Mar | 2023 | 0.0080301 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-22 20:15 | 2023-03-22 23:21 | 100 | 3:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M23032200236 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-03-22 | 18600 | keep | 0 | Mar | 2023 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-22 20:40 | 2023-03-22 22:11 | 17 | 1:31 | P | DESGANCHE | 1 X 100 EN RISER | S23032200383 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-03-22 | 1547 | keep | 0 | Mar | 2023 | 0.0010537 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-03-22 20:40 | 2023-03-23 09:40 | 50 | 13:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23032200153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 780 | 2023-03-22 | 39000 | keep | 0 | Mar | 2023 | 0.026563 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-22 20:43 | 2023-03-22 20:47 | 959 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S23032200391 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-22 | 3836 | keep | 0 | Mar | 2023 | 0.0026127 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-03-22 20:43 | 2023-03-22 20:47 | 1297 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S23032200391 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-22 | 5188 | keep | 0 | Mar | 2023 | 0.0035335 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2023-03-22 20:43 | 2023-03-22 20:47 | 451 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S23032200391 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-22 | 1804 | keep | 0 | Mar | 2023 | 0.0012287 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2023-03-22 20:43 | 2023-03-22 20:47 | 1264 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S23032200391 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-22 | 5056 | keep | 0 | Mar | 2023 | 0.0034436 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-03-22 20:43 | 2023-03-22 20:47 | 620 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S23032200391 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-22 | 2480 | keep | 0 | Mar | 2023 | 0.0016891 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
SAN JUAN | 2023-03-22 20:53 | 2023-03-23 10:46 | 80 | 13:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA NO FUNDIO | S23032200396 | New_Event | Cutout Failure | Include | Include | Equipment | 833 | 2023-03-22 | 66640 | keep | 0 | Mar | 2023 | 0.045388 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-03-22 21:08 | 2023-03-23 08:01 | 150 | 10:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA SIN FUSIBLE | P23032200227 | New_Event | Cutout Failure | Include | Include | Equipment | 653 | 2023-03-22 | 97950 | keep | 0 | Mar | 2023 | 0.066713 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-03-22 22:01 | 2023-03-23 12:14 | 25 | 14:13 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | B23032200150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 853 | 2023-03-22 | 21325 | keep | 0 | Mar | 2023 | 0.014524 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-03-22 22:15 | 2023-03-23 09:00 | 25 | 10:45 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M23032200242 | New_Event | Vegetation Contact | Include | Include | Vegetation | 645 | 2023-03-22 | 16125 | keep | 0 | Mar | 2023 | 0.010983 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2023-03-22 22:41 | 2023-03-23 10:40 | 100 | 11:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23032200167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 719 | 2023-03-22 | 71900 | keep | 0 | Mar | 2023 | 0.048971 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-03-22 23:39 | 2023-03-23 08:29 | 35 | 8:50 | P | PARARRAYOS DEFECTUOSO | 2 X 65 EN CORTE DE LINEA POR PARARRAYOS ACTIVADO | P23032200242 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 530 | 2023-03-22 | 18550 | keep | 0 | Mar | 2023 | 0.012634 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-03-23 01:06 | 2023-03-23 05:03 | 3108 | 3:57 | T | CAUSAS EXTERNAS | DISPARO DE BKR Y 2 X 200 EN C/L SE SECCIONALIZO PARA ABRIR PUENTES 80% EN SERVICIO | C23032300003 | New_Event | Damage From Public | Include | Include | Public | 237 | 2023-03-23 | 736596 | keep | 0 | Mar | 2023 | 0.50169 | 0.0021168 | Sustained | FALSE | FALSE | Not_TMED_Event | 3108
CANOVANAS | 2023-03-23 03:47 | 2023-03-23 03:48 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-23 | 3699 | keep | 0 | Mar | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
PONCE | 2023-03-23 04:51 | 2023-03-23 08:46 | 60 | 3:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE 100AMP NO FUNDIO FUSIBLE | P23032300001 | New_Event | Cutout Failure | Include | Include | Equipment | 235 | 2023-03-23 | 14100 | keep | 0 | Mar | 2023 | 0.0096034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-03-23 05:03 | 2023-03-24 04:40 | 622 | 23:37 | P | CAUSAS EXTERNAS | SE SECCIONALIZO POSTE PARTIDO POR IMPACTO DE AUTO Y SE ABRIO MACHETES PARA CERRAR LOS PUENTES 70% EN SERVICIO | C23032300003 | Partial_restoration | Damage From Public | Include | Include | Public | 1417 | 2023-03-23 | 881374 | keep | 0 | Mar | 2023 | 0.6003 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-23 06:09 | 2023-03-23 09:38 | 10 | 3:29 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | B23032300002 | New_Event | Animals | Include | Include | Wildlife | 209 | 2023-03-23 | 2090 | keep | 0 | Mar | 2023 | 0.0014235 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-03-23 06:15 | 2023-03-23 08:09 | 103 | 1:54 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | R23032300003 | New_Event | Animals | Include | Include | Wildlife | 114 | 2023-03-23 | 11742 | keep | 0 | Mar | 2023 | 0.0079974 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 873 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300012 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 3492 | keep | 0 | Mar | 2023 | 0.0023784 | 0.0005946 | Momentary | FALSE | FALSE | Not_TMED_Event | 873
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 1261 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300012 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 5044 | keep | 0 | Mar | 2023 | 0.0034354 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 2713 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300012 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 10852 | keep | 0 | Mar | 2023 | 0.0073912 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 51 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300012 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 204 | keep | 0 | Mar | 2023 | 0.00013894 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 285 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300012 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 1140 | keep | 0 | Mar | 2023 | 0.00077645 | 0.00019411 | Momentary | FALSE | FALSE | Not_TMED_Event | 285
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 1253 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300013 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 5012 | keep | 0 | Mar | 2023 | 0.0034137 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 1266 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300013 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 5064 | keep | 0 | Mar | 2023 | 0.0034491 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 411 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300013 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 1644 | keep | 0 | Mar | 2023 | 0.0011197 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 1444 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300014 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 5776 | keep | 0 | Mar | 2023 | 0.003934 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 3630 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300014 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 14520 | keep | 0 | Mar | 2023 | 0.0098895 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 871 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300014 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 3484 | keep | 0 | Mar | 2023 | 0.0023729 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2023-03-23 06:36 | 2023-03-23 06:40 | 108 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 2000 INTERRUPTOR 2030 CON FLASHOVER Y NO ABRIÃ“ EN AVERÃA | M23032300015 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-03-23 | 432 | keep | 0 | Mar | 2023 | 0.00029423 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BARRANQUITAS | 2023-03-23 07:02 | 2023-03-23 07:40 | 7 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO QUEMADO NO FUNDIO | C23032300019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2023-03-23 | 266 | keep | 0 | Mar | 2023 | 0.00018117 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-23 07:05 | 2023-03-23 16:18 | 90 | 9:13 | P | DESGANCHE | 1X80 EN C/L 2X65 EN OTRO C/L DESGANCHE | S23032300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 553 | 2023-03-23 | 49770 | keep | 0 | Mar | 2023 | 0.033898 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-03-23 07:16 | 2023-03-23 07:18 | 271 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S2303230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-23 | 542 | keep | 0 | Mar | 2023 | 0.00036915 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
HUMACAO | 2023-03-23 07:43 | 2023-03-23 14:08 | 18 | 6:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C23032300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2023-03-23 | 6930 | keep | 0 | Mar | 2023 | 0.00472 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2023-03-23 07:49 | 2023-03-23 15:43 | 117 | 7:54 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | R23032300014 | New_Event | Primary Wire Break | Include | Include | Equipment | 474 | 2023-03-23 | 55458 | keep | 0 | Mar | 2023 | 0.037772 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
BAYAMON | 2023-03-23 07:55 | 2023-03-23 11:50 | 12 | 3:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23032300014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 235 | 2023-03-23 | 2820 | keep | 0 | Mar | 2023 | 0.0019207 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-03-23 08:09 | 2023-03-23 09:40 | 15 | 1:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23032300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-03-23 | 1365 | keep | 0 | Mar | 2023 | 0.0009297 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-23 08:16 | 2023-03-23 14:29 | 40 | 6:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23032300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 373 | 2023-03-23 | 14920 | keep | 0 | Mar | 2023 | 0.010162 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-03-23 08:30 | 2023-03-23 10:25 | 17 | 1:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTES DE LINEA SE REEMPLAZARON DISCOS QUEMADOS | C23032300039 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 115 | 2023-03-23 | 1955 | keep | 0 | Mar | 2023 | 0.0013315 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-03-23 08:37 | 2023-03-23 08:40 | 1483 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30 % DEL 1204-04 SE CERRO POR CONTROL | S2303230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-23 | 4449 | keep | 0 | Mar | 2023 | 0.0030302 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-03-23 08:37 | 2023-03-23 08:40 | 1531 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 15% DEL 1204-05 SE CERRO POR CONTROL | S2303230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-23 | 4593 | keep | 0 | Mar | 2023 | 0.0031283 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-03-23 08:37 | 2023-03-23 08:40 | 5290 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVA 15% DEL 1204-05 Y 30% DEL 1204-04 SE CERRO POR CONTROL | S2303230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-23 | 15870 | keep | 0 | Mar | 2023 | 0.010809 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
CANOVANAS | 2023-03-23 08:49 | 2023-03-23 19:42 | 10 | 10:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 Y SE REMPLAZO CAJA PRIMARIA | R23032300019 | New_Event | Cutout Failure | Include | Include | Equipment | 653 | 2023-03-23 | 6530 | keep | 0 | Mar | 2023 | 0.0044476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-03-23 08:50 | 2023-03-23 08:51 | 1952 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23032300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-23 | 1952 | keep | 0 | Mar | 2023 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
YAUCO | 2023-03-23 08:54 | 2023-03-23 10:43 | 1 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE REPORTO CAUSA | P23032300024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2023-03-23 | 109 | keep | 0 | Mar | 2023 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-23 09:06 | 2023-03-23 10:00 | 9 | 0:54 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA CRUAZADA | M23032300037 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 54 | 2023-03-23 | 486 | keep | 0 | Mar | 2023 | 0.00033101 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-03-23 09:10 | 2023-03-23 14:33 | 124 | 5:23 | P | NO SE REPORTO CAUSA | 1 X 10 XMR 1 X 25 EN CL | R23032300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 323 | 2023-03-23 | 40052 | keep | 0 | Mar | 2023 | 0.027279 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
CAGUAS | 2023-03-23 09:23 | 2023-03-23 12:36 | 3 | 3:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA | C23032300050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2023-03-23 | 579 | keep | 0 | Mar | 2023 | 0.00039435 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-03-23 09:48 | 2023-03-23 19:04 | 8 | 9:16 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L Y SE REEMPLAZO POSTE PRIMARIO | B23032300030 | New_Event | Primary Pole Failure | Include | Include | Equipment | 556 | 2023-03-23 | 4448 | keep | 0 | Mar | 2023 | 0.0030295 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-23 10:32 | 2023-03-23 11:45 | 239 | 1:13 | P | CAUSAS EXTERNAS | SJ-230323-50 SE SECCIONALIZO 5 POSTES PRIMARIOS PARTIDOS POR CAMION QUE SE ENREDO EN CABLE DE COMUNICACIONES | R23032300005 | New_Event | Damage From Public | Include | Include | Public | 73 | 2023-03-23 | 17447 | keep | 0 | Mar | 2023 | 0.011883 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
BAYAMON | 2023-03-23 10:40 | 2023-03-23 13:25 | 12 | 2:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN C/L Y SE REPARO SECUNDARIA | B23032300043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 165 | 2023-03-23 | 1980 | keep | 0 | Mar | 2023 | 0.0013486 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-23 10:45 | 2023-03-23 11:27 | 3 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23032300045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2023-03-23 | 126 | keep | 0 | Mar | 2023 | 8.5818e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-23 10:48 | 2023-03-23 13:41 | 15 | 2:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X20 EN XMR SE REPARO/LEVANTO SECUNDARIA PARTIDA DEL SUELO | S23032300063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 173 | 2023-03-23 | 2595 | keep | 0 | Mar | 2023 | 0.0017674 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-23 10:55 | 2023-03-23 14:23 | 6 | 3:28 | P | TERMINACION SOTERRADA AVERIADA | 1X20 EN AEREO PROVISIONAL SE REMPLAZO TERMINACION SOTERRADA QUEMADA | S23032300064 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 208 | 2023-03-23 | 1248 | keep | 0 | Mar | 2023 | 0.00085001 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-03-23 10:56 | 2023-03-23 14:28 | 20 | 3:32 | P | CAUSAS EXTERNAS | 2X65 EN C/L 1X50 EN OTRO C/L POR PERSONAL AJENO A LUMA DESGANCHANDO | S23032300066 | New_Event | Damage From Public | Include | Include | Public | 212 | 2023-03-23 | 4240 | keep | 0 | Mar | 2023 | 0.0028878 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-03-23 11:29 | 2023-03-23 12:55 | 40 | 1:26 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE X AVE | B23032300050 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-03-23 | 3440 | keep | 0 | Mar | 2023 | 0.002343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-03-23 11:30 | 2023-03-23 12:32 | 12 | 1:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M23032300061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 62 | 2023-03-23 | 744 | keep | 0 | Mar | 2023 | 0.00050674 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-03-23 11:40 | 2023-03-23 14:38 | 50 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032300075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-03-23 | 8900 | keep | 0 | Mar | 2023 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-23 11:45 | 2023-03-24 10:02 | 179 | 22:17 | P | CAUSAS EXTERNAS | SE CERRO C/L DE AMARRE CONTRA EL MISMO INTERRUPTOR, SECCIONALIZADO CON PUENTES ABIERTOS SE SIGUE TRABAJANDO EN AVERIA POR POSTES PARTIDOS POR CAMION QUE SE ENREDO EN CABLE DE COMUNICACIONES MEDIANTE GOI SJ-230323-50 | R23032300005 | Partial_restoration | Damage From Public | Include | Include | Public | 1337 | 2023-03-23 | 239323 | keep | 0 | Mar | 2023 | 0.163 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-23 11:46 | 2023-03-23 12:37 | 8 | 0:51 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | S23032300074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2023-03-23 | 408 | keep | 0 | Mar | 2023 | 0.00027789 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-23 11:47 | 2023-03-23 12:34 | 3 | 0:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R23032300043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2023-03-23 | 141 | keep | 0 | Mar | 2023 | 9.6034e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-03-23 11:55 | 2023-03-23 14:35 | 10 | 2:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA CON ESCAPE DE ACEITE | M23032300078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 160 | 2023-03-23 | 1600 | keep | 0 | Mar | 2023 | 0.0010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-03-23 12:14 | 2023-03-23 12:16 | 752 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR | P23032300053 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-23 | 1504 | keep | 0 | Mar | 2023 | 0.0010244 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2023-03-23 12:14 | 2023-03-23 12:16 | 2696 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 5011-04 | P23032300053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-23 | 5392 | keep | 0 | Mar | 2023 | 0.0036725 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
BAYAMON | 2023-03-23 12:30 | 2023-03-23 13:12 | 14 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23032300059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2023-03-23 | 588 | keep | 0 | Mar | 2023 | 0.00040048 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-03-23 12:31 | 2023-03-23 14:30 | 40 | 1:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23032300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-03-23 | 4760 | keep | 0 | Mar | 2023 | 0.003242 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-03-23 12:31 | 2023-03-23 16:15 | 80 | 3:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23032300109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-03-23 | 17920 | keep | 0 | Mar | 2023 | 0.012205 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-23 12:46 | 2023-03-23 21:51 | 1 | 9:05 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER HACIA MONTURA DE XMR | S23032300090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 545 | 2023-03-23 | 545 | keep | 0 | Mar | 2023 | 0.0003712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-23 12:52 | 2023-03-23 17:19 | 16 | 4:27 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA ELIMINAR POSTE SECUNDARIO PARTIDO SE RELOCALIZARON LINEAS SECUNDARIAS A POSTE PRIMARIO EXISTENTE | C23032300089 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 267 | 2023-03-23 | 4272 | keep | 0 | Mar | 2023 | 0.0029096 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-03-23 12:54 | 2023-03-23 12:55 | 2999 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23032300093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-23 | 2999 | keep | 0 | Mar | 2023 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
SAN JUAN | 2023-03-23 12:56 | 2023-03-23 16:04 | 12 | 3:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR BAJANTE SECUNDARIO | S23032300091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 188 | 2023-03-23 | 2256 | keep | 0 | Mar | 2023 | 0.0015366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-03-23 13:00 | 2023-03-23 14:30 | 17 | 1:30 | P | PROBLEMA DEL CLIENTE | SE DEJO FUERA UN CLIENTE PARA QUE REPARE AVERIA INTERNA CRUZO FASE | R23032300048 | New_Event | Customer-Related Interruption | Include | Include | Public | 90 | 2023-03-23 | 1530 | keep | 0 | Mar | 2023 | 0.0010421 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2023-03-23 13:11 | 2023-03-23 14:37 | 1 | 1:26 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23032300098 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-03-23 | 86 | keep | 0 | Mar | 2023 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-23 13:13 | 2023-03-23 13:14 | 2450 | 0:01 | T | ANIMAL | RECIERRE | C2303230000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-23 | 2450 | keep | 0 | Mar | 2023 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-03-23 13:14 | 2023-03-23 15:27 | 216 | 2:13 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23032300101 | 1st_after_momentary | Animals | Include | Include | Wildlife | 133 | 2023-03-23 | 28728 | keep | 0 | Mar | 2023 | 0.019567 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
SAN JUAN | 2023-03-23 13:18 | 2023-03-23 18:24 | 8 | 5:06 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | S23032300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2023-03-23 | 2448 | keep | 0 | Mar | 2023 | 0.0016673 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-03-23 13:18 | 2023-03-23 16:35 | 5 | 3:17 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M23032300097 | New_Event | Animals | Include | Include | Wildlife | 197 | 2023-03-23 | 985 | keep | 0 | Mar | 2023 | 0.00067088 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-23 13:22 | 2023-03-23 15:51 | 9 | 2:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23032300100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 149 | 2023-03-23 | 1341 | keep | 0 | Mar | 2023 | 0.00091335 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2023-03-23 13:25 | 2023-03-23 14:35 | 120 | 1:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23032300107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-03-23 | 8400 | keep | 0 | Mar | 2023 | 0.0057212 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2023-03-23 13:33 | 2023-03-23 20:10 | 9 | 6:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA | M23032300100 | New_Event | Service Transformer Failure | Include | Include | Equipment | 397 | 2023-03-23 | 3573 | keep | 0 | Mar | 2023 | 0.0024336 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-03-23 13:40 | 2023-03-23 16:13 | 5 | 2:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR Y SE REPARO SECUNDARIA | B23032300067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 153 | 2023-03-23 | 765 | keep | 0 | Mar | 2023 | 0.00052104 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-23 13:50 | 2023-03-23 17:00 | 21 | 3:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE Y SECUNDARIA | R23032300052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 190 | 2023-03-23 | 3990 | keep | 0 | Mar | 2023 | 0.0027176 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
AGUADILLA | 2023-03-23 14:02 | 2023-03-23 16:20 | 3 | 2:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23032300107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2023-03-23 | 414 | keep | 0 | Mar | 2023 | 0.00028197 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2023-03-23 14:21 | 2023-03-23 20:42 | 1 | 6:21 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23032300171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 381 | 2023-03-23 | 381 | keep | 0 | Mar | 2023 | 0.0002595 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-03-23 14:30 | 2023-03-23 16:58 | 67 | 2:28 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | C23032300135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-03-23 | 9916 | keep | 0 | Mar | 2023 | 0.0067537 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2023-03-23 14:32 | 2023-03-23 14:49 | 2067 | 0:17 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23032300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2023-03-23 | 35139 | keep | 0 | Mar | 2023 | 0.023933 | 0.0014078 | Sustained | FALSE | FALSE | Not_TMED_Event | 2067
SAN JUAN | 2023-03-23 14:33 | 2023-03-23 15:17 | 10 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONEXIONES EN BAJANTE SECUNDARIO DEL XMR | S23032300113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-03-23 | 440 | keep | 0 | Mar | 2023 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-23 15:15 | 2023-03-23 17:00 | 144 | 1:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230323-51 SE REMPLAZO POSTE PRIMARIO PARTIDO | R23032300062 | New_Event | Primary Pole Failure | Include | Include | Equipment | 105 | 2023-03-23 | 15120 | keep | 0 | Mar | 2023 | 0.010298 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
UTUADO | 2023-03-23 15:36 | 2023-03-23 19:10 | 50 | 3:34 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS | A23032300121 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 214 | 2023-03-23 | 10700 | keep | 0 | Mar | 2023 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-03-23 15:47 | 2023-03-23 21:55 | 79 | 6:08 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23032300153 | New_Event | Animals | Include | Include | Wildlife | 368 | 2023-03-23 | 29072 | keep | 0 | Mar | 2023 | 0.019801 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2023-03-23 16:18 | 2023-03-23 19:18 | 2435 | 3:00 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO ALIMENTADOR POR PARTES Y SE QUEDO EN SERVICIO BY-230323-01 CARGA POR EL 1909-08 | S23032300171 | New_Event | Feeder Load Transferred | Include | Include | Other | 180 | 2023-03-23 | 438300 | keep | 0 | Mar | 2023 | 0.29852 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-03-23 16:18 | 2023-03-23 18:59 | 2956 | 2:41 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE ABRIO AMARRE CO 1907-05 Y SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 1907-05 | S23032300171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2023-03-23 | 475916 | keep | 0 | Mar | 2023 | 0.32414 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
ARECIBO | 2023-03-23 16:47 | 2023-03-23 17:40 | 70 | 0:53 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA LINEAS CRUZADAS | A23032300130 | New_Event | Primary Wire Break | Include | Include | Equipment | 53 | 2023-03-23 | 3710 | keep | 0 | Mar | 2023 | 0.0025269 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-03-23 16:49 | 2023-03-23 18:30 | 50 | 1:41 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE | A23032300132 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-03-23 | 5050 | keep | 0 | Mar | 2023 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-23 16:55 | 2023-03-23 23:09 | 20 | 6:14 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN C/L Y 1 X 15 EN XMR SE ELIMINO PARARRAYO | B23032300087 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 374 | 2023-03-23 | 7480 | keep | 0 | Mar | 2023 | 0.0050946 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-03-23 17:00 | 2023-03-23 23:17 | 20 | 6:17 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230323-51 SE REMPLAZO POSTE PRIMARIO PARTIDO | R23032300062 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 377 | 2023-03-23 | 7540 | keep | 0 | Mar | 2023 | 0.0051355 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-23 17:49 | 2023-03-23 18:41 | 52 | 0:52 | P | DESGANCHE | 1X 80 CAJA PRIMARIA Y DESGANCHE | R23032300074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2023-03-23 | 2704 | keep | 0 | Mar | 2023 | 0.0018417 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2023-03-23 17:52 | 2023-03-23 20:06 | 24 | 2:14 | P | DESGANCHE | 1X65 EN C/L SE REFIRIO PARA DESGANCHE | S23032300196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-03-23 | 3216 | keep | 0 | Mar | 2023 | 0.0021904 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2023-03-23 17:55 | 2023-03-23 23:20 | 70 | 5:25 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 100 EN CL Y 1 X 20 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIAS CRUZADAS | M23032300147 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 325 | 2023-03-23 | 22750 | keep | 0 | Mar | 2023 | 0.015495 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-03-23 18:00 | 2023-03-23 19:45 | 54 | 1:45 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO SAFADO EN C/L | P23032300095 | New_Event | Primary Wire Break | Include | Include | Equipment | 105 | 2023-03-23 | 5670 | keep | 0 | Mar | 2023 | 0.0038618 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BARRANQUITAS | 2023-03-23 18:04 | 2023-03-23 20:02 | 5 | 1:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA Y 1 X10 EN XMR | C23032300177 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2023-03-23 | 590 | keep | 0 | Mar | 2023 | 0.00040185 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-23 18:27 | 2023-03-23 19:26 | 1 | 0:59 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO EN FUEGO SE ABRE INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA SECCIONALIZAR LA AVERIA MEDIANTE SWITCHING-FORM BY-230323-02 | S23032300332 | New_Event | Primary Wire Break | Include | Include | Equipment | 59 | 2023-03-23 | 59 | keep | 0 | Mar | 2023 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-23 18:45 | 2023-03-23 18:46 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23032300297 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-23 | 45 | keep | 0 | Mar | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-03-23 19:02 | 2023-03-23 19:03 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23032300319 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-23 | 45 | keep | 0 | Mar | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-03-23 19:07 | 2023-03-23 19:09 | 4304 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE COLOCA RR EN OFF Y SE REALIZA PRUEBA QUEDANDO EN SERVICIO | M23032300156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-23 | 8608 | keep | 0 | Mar | 2023 | 0.0058629 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2023-03-23 19:18 | 2023-03-23 19:49 | 400 | 0:31 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO ALIMENTADOR POR PARTES Y SE QUEDO EN SERVICIO BY-230323-01 CARGA POR EL 1909-08 | S23032300171 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 31 | 2023-03-23 | 12400 | keep | 0 | Mar | 2023 | 0.0084456 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-23 19:26 | 2023-03-23 19:59 | 6136 | 0:33 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR A PETICION DE WILFREDO VALLESCORBO PARA SECCIONALIZAR TRAMO BY-230323-02 | B23032300103 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 33 | 2023-03-23 | 202488 | keep | 0 | Mar | 2023 | 0.13791 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-23 19:59 | 2023-03-24 01:24 | 1 | 5:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE SWITCHING-FORM BY-230323-02 | S23032300332 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 325 | 2023-03-23 | 325 | keep | 0 | Mar | 2023 | 0.00022136 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-23 19:59 | 2023-03-24 10:17 | 1 | 14:18 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR SE REPARO PRIMARIA Y 1 X 30 EN C/L | S23032300332 | New_Event | Primary Wire Break | Include | Include | Equipment | 858 | 2023-03-23 | 858 | keep | 0 | Mar | 2023 | 0.00058438 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-03-23 20:00 | 2023-03-24 09:24 | 40 | 13:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA @ CAJA NO FUNDIO | R23032300088 | New_Event | Primary Wire Break | Include | Include | Equipment | 804 | 2023-03-23 | 32160 | keep | 0 | Mar | 2023 | 0.021904 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-03-23 20:02 | 2023-03-23 22:03 | 4 | 2:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S23032300335 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2023-03-23 | 484 | keep | 0 | Mar | 2023 | 0.00032965 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-03-23 20:53 | 2023-03-24 09:18 | 1 | 12:25 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23032300188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 745 | 2023-03-23 | 745 | keep | 0 | Mar | 2023 | 0.00050742 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-23 21:43 | 2023-03-24 14:17 | 15 | 16:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA AVERIADA | M23032300178 | New_Event | Secondary Wire Break | Include | Include | Equipment | 994 | 2023-03-23 | 14910 | keep | 0 | Mar | 2023 | 0.010155 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-23 22:11 | 2023-03-24 00:32 | 60 | 2:21 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | S23032300348 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-03-23 | 8460 | keep | 0 | Mar | 2023 | 0.0057621 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-23 23:30 | 2023-03-24 09:27 | 241 | 9:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L Y 1 X 100 EN C/L MAL TIEMPO LLUVIAS | B23032300149 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 597 | 2023-03-23 | 143877 | keep | 0 | Mar | 2023 | 0.097994 | 0.00016414 | Sustained | FALSE | FALSE | Not_TMED_Event | 241
FAJARDO | 2023-03-23 23:56 | 2023-03-24 01:09 | 50 | 1:13 | P | DESGANCHE | 1 X 50 EN C/L | R23032300097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-03-23 | 3650 | keep | 0 | Mar | 2023 | 0.002486 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-24 01:08 | 2023-03-24 01:09 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2303240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-24 | 1746 | keep | 0 | Mar | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
HUMACAO | 2023-03-24 02:00 | 2023-03-24 07:42 | 150 | 5:42 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE ELIMINO PARARRAYO | C23032400002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 342 | 2023-03-24 | 51300 | keep | 0 | Mar | 2023 | 0.03494 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-03-24 02:30 | 2023-03-24 10:56 | 5 | 8:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23032400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 506 | 2023-03-24 | 2530 | keep | 0 | Mar | 2023 | 0.0017232 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-24 02:35 | 2023-03-24 13:42 | 8 | 11:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN XMR SE REMPLAZO CAJA Y PARARAYOS | S23032400003 | New_Event | Cutout Failure | Include | Include | Equipment | 667 | 2023-03-24 | 5336 | keep | 0 | Mar | 2023 | 0.0036343 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-03-24 04:38 | 2023-03-24 13:47 | 118 | 9:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 50 EN C/L MAL TIEMPO VIENTOS | C23032400005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 549 | 2023-03-24 | 64782 | keep | 0 | Mar | 2023 | 0.044123 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
CAGUAS | 2023-03-24 04:40 | 2023-03-24 05:25 | 933 | 0:45 | P | CAUSAS EXTERNAS | SE REALIZARON OPERACIONES 80% EN SERVICIO | C23032300003 | Additional_clients | Damage From Public | Include | Include | Public | 45 | 2023-03-24 | 41985 | keep | 0 | Mar | 2023 | 0.028596 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-24 05:16 | 2023-03-24 09:45 | 45 | 4:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A23032400002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 269 | 2023-03-24 | 12105 | keep | 0 | Mar | 2023 | 0.0082447 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2023-03-24 05:25 | 2023-03-24 05:43 | 622 | 0:18 | P | CAUSAS EXTERNAS | SE REALIZARON OPERACIONES 100% EN SERVICIO | C23032300003 | Partial_restoration | Damage From Public | Include | Include | Public | 18 | 2023-03-24 | 11196 | keep | 0 | Mar | 2023 | 0.0076255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-24 06:05 | 2023-03-24 09:28 | 53 | 3:23 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | R23032400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2023-03-24 | 10759 | keep | 0 | Mar | 2023 | 0.0073279 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BARRANQUITAS | 2023-03-24 07:18 | 2023-03-24 11:37 | 25 | 4:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23032400009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 259 | 2023-03-24 | 6475 | keep | 0 | Mar | 2023 | 0.0044101 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-03-24 07:26 | 2023-03-24 07:27 | 1746 | 0:01 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR | B23032400018 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-03-24 | 1746 | keep | 0 | Mar | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2023-03-24 07:27 | 2023-03-24 10:01 | 100 | 2:34 | P | PARARRAYOS DEFECTUOSO | 1 X 150 EN SU-13 1 X 80 EN SU-10 Y 1 X 20 EN RISER SE REMPLAZO PARARRAYO QUEMDO | B23032400020 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 154 | 2023-03-24 | 15400 | keep | 0 | Mar | 2023 | 0.010489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-24 07:30 | 2023-03-24 07:31 | 1681 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTRO LLEVA 1346-06 | S23032400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-24 | 1681 | keep | 0 | Mar | 2023 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-03-24 07:30 | 2023-03-24 07:31 | 1598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1303-01 QUE LLEVA LA CARGA DEL 1346-06 | S23032400010 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-24 | 1598 | keep | 0 | Mar | 2023 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2023-03-24 07:49 | 2023-03-24 11:15 | 209 | 3:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | B23032400029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 206 | 2023-03-24 | 43054 | keep | 0 | Mar | 2023 | 0.029324 | 0.00014235 | Sustained | FALSE | FALSE | Not_TMED_Event | 209
MAYAGÃœEZ | 2023-03-24 07:52 | 2023-03-24 17:20 | 50 | 9:28 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23032400007 | New_Event | Primary Wire Break | Include | Include | Equipment | 568 | 2023-03-24 | 28400 | keep | 0 | Mar | 2023 | 0.019343 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-24 07:54 | 2023-03-24 12:00 | 35 | 4:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 30 EN C/L Y 1 X 15 EN XMR Y SE REMPLAZO BARRAS EN PEDESTAL | B23032400031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 246 | 2023-03-24 | 8610 | keep | 0 | Mar | 2023 | 0.0058642 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-03-24 07:58 | 2023-03-24 13:21 | 5 | 5:23 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO PUENTE DE LINEA A CAJA | S23032400016 | New_Event | Primary Wire Break | Include | Include | Equipment | 323 | 2023-03-24 | 1615 | keep | 0 | Mar | 2023 | 0.0011 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-03-24 08:03 | 2023-03-24 08:04 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-24 | 4431 | keep | 0 | Mar | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
CANOVANAS | 2023-03-24 08:10 | 2023-03-24 12:27 | 1 | 4:17 | P | NO SE REPORTO CAUSA | 1X30 EN RISER | R23032400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 257 | 2023-03-24 | 257 | keep | 0 | Mar | 2023 | 0.00017504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-03-24 08:10 | 2023-03-24 09:26 | 100 | 1:16 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P23032400009 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-03-24 | 7600 | keep | 0 | Mar | 2023 | 0.0051763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-03-24 08:11 | 2023-03-24 16:40 | 15 | 8:29 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA IGUANA CRUZO FASES | M23032400011 | New_Event | Animals | Include | Include | Wildlife | 509 | 2023-03-24 | 7635 | keep | 0 | Mar | 2023 | 0.0052002 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-03-24 08:33 | 2023-03-24 09:18 | 12 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23032400038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-03-24 | 540 | keep | 0 | Mar | 2023 | 0.00036779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-24 08:36 | 2023-03-24 08:37 | 1362 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | B23032400040 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-24 | 1362 | keep | 0 | Mar | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2023-03-24 08:37 | 2023-03-24 19:08 | 4 | 10:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA REPUSO 2X80 EN C/L. | B23032400040 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 631 | 2023-03-24 | 2524 | keep | 0 | Mar | 2023 | 0.0017191 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-03-24 09:00 | 2023-03-24 11:42 | 1 | 2:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO EN XMR Y SE REPARARON CONECTORES EN TOMA | S23032400009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 162 | 2023-03-24 | 162 | keep | 0 | Mar | 2023 | 0.00011034 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-24 09:02 | 2023-03-24 09:03 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23032400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-24 | 4085 | keep | 0 | Mar | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
HUMACAO | 2023-03-24 09:06 | 2023-03-24 09:09 | 327 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 2603-06 SE CERRO POR CONTROL LLEVA 2603-07 | C23032400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-24 | 981 | keep | 0 | Mar | 2023 | 0.00066815 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
SAN JUAN | 2023-03-24 09:20 | 2023-03-24 09:22 | 922 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1401-08 LLEVA 1346-05 | S2303240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-24 | 1844 | keep | 0 | Mar | 2023 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-03-24 09:20 | 2023-03-24 09:22 | 135 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE 1401-08 LLEVA 1346-05 | S2303240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-24 | 270 | keep | 0 | Mar | 2023 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
HUMACAO | 2023-03-24 09:20 | 2023-03-24 18:32 | 1 | 9:12 | P | OTRAS CAUSAS | SE REEMPLAZO CT Y PT | C23032400023 | New_Event | Other Causes | Include | Include | Other | 552 | 2023-03-24 | 552 | keep | 0 | Mar | 2023 | 0.00037596 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-03-24 09:21 | 2023-03-24 10:42 | 6 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZAR CONEXIONES EN SECUNDARIA | R23032400018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2023-03-24 | 486 | keep | 0 | Mar | 2023 | 0.00033101 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-03-24 09:46 | 2023-03-24 10:57 | 12 | 1:11 | P | SECUNDARIA/OTROS | SE CAMBIO PEDESTAL SECUNDARIO | P23032400026 | New_Event |  |  |  |  | 71 | 2023-03-24 | 852 | keep | 0 | Mar | 2023 | 0.00058029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-03-24 09:53 | 2023-03-24 12:18 | 100 | 2:25 | P | ANIMAL | 1 X 80 EN C/L Y 1 X 15 EN XMR CRUCE X AVE | C23032400034 | New_Event | Animals | Include | Include | Wildlife | 145 | 2023-03-24 | 14500 | keep | 0 | Mar | 2023 | 0.0098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-03-24 10:00 | 2023-03-24 10:01 | 234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2 | P23032400031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-24 | 234 | keep | 0 | Mar | 2023 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2023-03-24 10:00 | 2023-03-24 10:01 | 2468 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23032400031 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-24 | 2468 | keep | 0 | Mar | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
CANOVANAS | 2023-03-24 10:16 | 2023-03-24 12:45 | 6 | 2:29 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | R23032400025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-03-24 | 894 | keep | 0 | Mar | 2023 | 0.0006089 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-03-24 10:31 | 2023-03-24 11:54 | 2 | 1:23 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN XMR Y 1 X 40 EN C/L SE ELIMINO PARARRAYO | C23032400048 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 83 | 2023-03-24 | 166 | keep | 0 | Mar | 2023 | 0.00011306 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-24 10:52 | 2023-03-24 17:05 | 8 | 6:13 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARARON SECUNDARIAS Y DESGANCHE | B23032400058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 373 | 2023-03-24 | 2984 | keep | 0 | Mar | 2023 | 0.0020324 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-24 11:11 | 2023-03-24 13:01 | 180 | 1:50 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | B23032400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-03-24 | 19800 | keep | 0 | Mar | 2023 | 0.013486 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
SAN JUAN | 2023-03-24 11:20 | 2023-03-24 13:20 | 115 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23032400057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2023-03-24 | 13800 | keep | 0 | Mar | 2023 | 0.0093991 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
SAN JUAN | 2023-03-24 11:42 | 2023-03-24 12:19 | 1085 | 0:37 | T | DESGANCHE | SE RETIRO RAMA FRENTE Y SE CERRO POR SCADA | S23032400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2023-03-24 | 40145 | keep | 0 | Mar | 2023 | 0.027343 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
VEGA BAJA | 2023-03-24 11:50 | 2023-03-24 13:00 | 7 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A23032400025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-03-24 | 490 | keep | 0 | Mar | 2023 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-03-24 12:00 | 2023-03-24 13:05 | 4 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23032400042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-03-24 | 260 | keep | 0 | Mar | 2023 | 0.00017708 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-03-24 12:21 | 2023-03-25 17:15 | 8 | 28:54 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 25 EN CORTE DE LINEA REMPLAZO DE POSTE CON TRANSFORMADOR REALCIONADO A EVENTO M23032400051 | M23032500145 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1734 | 2023-03-24 | 13872 | keep | 0 | Mar | 2023 | 0.0094482 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-03-24 12:21 | 2023-03-24 12:22 | 759 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23032400033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-24 | 759 | keep | 0 | Mar | 2023 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
BARRANQUITAS | 2023-03-24 12:56 | 2023-03-24 14:50 | 4 | 1:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO | C23032400019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 114 | 2023-03-24 | 456 | keep | 0 | Mar | 2023 | 0.00031058 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-03-24 13:01 | 2023-03-24 15:10 | 17 | 2:09 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B23032400083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-03-24 | 2193 | keep | 0 | Mar | 2023 | 0.0014936 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-03-24 13:06 | 2023-03-24 13:07 | 1066 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23032400037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-24 | 1066 | keep | 0 | Mar | 2023 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
SAN JUAN | 2023-03-24 13:14 | 2023-03-24 13:15 | 386 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | S23032400095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-24 | 386 | keep | 0 | Mar | 2023 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
SAN JUAN | 2023-03-24 13:15 | 2023-03-24 13:19 | 271 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO POR CONTROL | S2303240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-24 | 1084 | keep | 0 | Mar | 2023 | 0.00073831 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2023-03-24 13:22 | 2023-03-24 15:46 | 7 | 2:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONECTORES SECUNDARIOS | B23032400087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 144 | 2023-03-24 | 1008 | keep | 0 | Mar | 2023 | 0.00068654 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-03-24 13:22 | 2023-03-24 15:04 | 10 | 1:42 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA REPARAR PEDESTAL SECUNDARIO | C23032400073 | New_Event |  |  |  |  | 102 | 2023-03-24 | 1020 | keep | 0 | Mar | 2023 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-24 13:30 | 2023-03-24 16:30 | 11 | 3:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 75KVA X 50KVA | B23032400090 | New_Event | Service Transformer Failure | Include | Include | Equipment | 180 | 2023-03-24 | 1980 | keep | 0 | Mar | 2023 | 0.0013486 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2023-03-24 13:35 | 2023-03-24 15:43 | 1 | 2:08 | P | ANIMAL | 1 X 15 EN BANCO DE XMRS CRUCE POR AVE (EVENTO TRANSFERIDO DE PONCE) | P23032400059 | New_Event | Animals | Include | Include | Wildlife | 128 | 2023-03-24 | 128 | keep | 0 | Mar | 2023 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-24 14:00 | 2023-03-24 14:49 | 12 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON BARRAS EN PEDESTAL | R23032400042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-03-24 | 588 | keep | 0 | Mar | 2023 | 0.00040048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-03-24 14:05 | 2023-03-24 15:04 | 20 | 0:59 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | R23032400047 | New_Event | Animals | Include | Include | Wildlife | 59 | 2023-03-24 | 1180 | keep | 0 | Mar | 2023 | 0.00080369 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-03-24 14:07 | 2023-03-24 16:14 | 45 | 2:07 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | R23032400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-03-24 | 5715 | keep | 0 | Mar | 2023 | 0.0038925 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2023-03-24 14:13 | 2023-03-24 20:55 | 16 | 6:42 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | C23032400080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 402 | 2023-03-24 | 6432 | keep | 0 | Mar | 2023 | 0.0043808 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2023-03-24 14:14 | 2023-03-24 16:36 | 200 | 2:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CORTE DE LINEA FUERTES VIENTOS | M23032400067 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 142 | 2023-03-24 | 28400 | keep | 0 | Mar | 2023 | 0.019343 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2023-03-24 14:23 | 2023-03-24 17:13 | 50 | 2:50 | P | CAUSAS EXTERNAS | 1 X 80 EN CORTE DE LINEA CAMION IMPACTO POSTE | P23032400070 | New_Event | Damage From Public | Include | Include | Public | 170 | 2023-03-24 | 8500 | keep | 0 | Mar | 2023 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-24 14:32 | 2023-03-24 18:16 | 73 | 3:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23032400100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2023-03-24 | 16352 | keep | 0 | Mar | 2023 | 0.011137 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2023-03-24 14:52 | 2023-03-24 16:30 | 141 | 1:38 | P | DESGANCHE | 2 X 100 EN C/L Y DESGANCHE | B23032400108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-03-24 | 13818 | keep | 0 | Mar | 2023 | 0.0094114 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
VEGA BAJA | 2023-03-24 15:03 | 2023-03-24 15:35 | 4 | 0:32 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A23032400064 | New_Event | Animals | Include | Include | Wildlife | 32 | 2023-03-24 | 128 | keep | 0 | Mar | 2023 | 8.718e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-03-24 15:13 | 2023-03-24 16:39 | 10 | 1:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23032400091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 86 | 2023-03-24 | 860 | keep | 0 | Mar | 2023 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-03-24 15:20 | 2023-03-24 15:53 | 10 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES SECUNDARIAS | P23032400046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-03-24 | 330 | keep | 0 | Mar | 2023 | 0.00022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-03-24 15:34 | 2023-03-24 15:49 | 5 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA RELOCALIZAR LINEA SECUNDARIA | C23032400079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-03-24 | 75 | keep | 0 | Mar | 2023 | 5.1082e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-24 15:44 | 2023-03-24 18:22 | 40 | 2:38 | P | CONDUCTOR ROTO O ABIERTO | 1X50 EN C/L SE REPARO/SUBIO CONDUCTOR PRIMARIO DEL SUELO (RADIAL) | R23032400054 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2023-03-24 | 6320 | keep | 0 | Mar | 2023 | 0.0043045 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-03-24 15:45 | 2023-03-24 20:39 | 120 | 4:54 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23032400095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-03-24 | 35280 | keep | 0 | Mar | 2023 | 0.024029 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
YAUCO | 2023-03-24 16:01 | 2023-03-24 17:03 | 1 | 1:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON CONEXIONES EN BAJANTES PRIMARIOS | P23032400083 | New_Event | Primary Wire Break | Include | Include | Equipment | 62 | 2023-03-24 | 62 | keep | 0 | Mar | 2023 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-24 16:28 | 2023-03-24 21:33 | 25 | 5:05 | P | DESGANCHE | 1 X 40 EN C/L SE DEJO FUERA BANCO DE XMR POR 2 XMR AVERIADOS | S23032400125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2023-03-24 | 7625 | keep | 0 | Mar | 2023 | 0.0051934 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-03-24 16:55 | 2023-03-24 17:39 | 5 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE CERRO BAJANTE SECUNDARIO | S23032400129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-03-24 | 220 | keep | 0 | Mar | 2023 | 0.00014984 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-03-24 17:13 | 2023-03-24 18:26 | 234 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO POR GLOBO DE HELIO ENREDADO EN LINEA | P23032400009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2023-03-24 | 17082 | keep | 0 | Mar | 2023 | 0.011634 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2023-03-24 17:13 | 2023-03-24 18:26 | 2468 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO POR GLOBO DE HELIO ENREDADO EN LINEA | P23032400009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2023-03-24 | 180164 | keep | 0 | Mar | 2023 | 0.12271 | 0.0016809 | Sustained | FALSE | FALSE | Not_TMED_Event | 2468
CAGUAS | 2023-03-24 17:26 | 2023-03-24 20:54 | 10 | 3:28 | P | ARBOL SOBRE LINEA | 1 X 30 EN C/L SE RETIRO ARBOL SOBRE LINEA Y SE REPARO SECUNDARIA | C23032400112 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 208 | 2023-03-24 | 2080 | keep | 0 | Mar | 2023 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-24 17:27 | 2023-03-24 19:00 | 25 | 1:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ROTO | A23032400080 | New_Event | Primary Wire Break | Include | Include | Equipment | 93 | 2023-03-24 | 2325 | keep | 0 | Mar | 2023 | 0.0015835 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-03-24 17:34 | 2023-03-24 18:34 | 6 | 1:00 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | S23032400135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2023-03-24 | 360 | keep | 0 | Mar | 2023 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-03-24 18:21 | 2023-03-25 10:15 | 15 | 15:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032400102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 954 | 2023-03-24 | 14310 | keep | 0 | Mar | 2023 | 0.0097465 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-03-24 19:01 | 2023-03-25 09:08 | 16 | 14:07 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO DE LINEA A CAJA | C23032400114 | New_Event | Primary Wire Break | Include | Include | Equipment | 847 | 2023-03-24 | 13552 | keep | 0 | Mar | 2023 | 0.0092302 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2023-03-24 19:07 | 2023-03-24 21:00 | 125 | 1:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23032400102 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2023-03-24 | 14125 | keep | 0 | Mar | 2023 | 0.0096205 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
AGUADILLA | 2023-03-24 19:30 | 2023-03-25 10:45 | 80 | 15:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032400108 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 915 | 2023-03-24 | 73200 | keep | 0 | Mar | 2023 | 0.049856 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-03-24 19:56 | 2023-03-24 21:00 | 239 | 1:04 | P | CAUSAS EXTERNAS | SE VOLVIO A ABRIR C/L DE AMARRE CON EL MISMO INTERRUPTOR, PARA CERRAR LOS PUENTES ABIERTOS POR POSTES PARTIDOS MEDIANTE POR CAMION QUE SE ENREDO EN CABLE DE COMUNICACIONES GOI SJ-230323-50 | R23032300005 | New_Event | Damage From Public | Include | Include | Public | 64 | 2023-03-24 | 15296 | keep | 0 | Mar | 2023 | 0.010418 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
PONCE | 2023-03-24 20:02 | 2023-03-25 11:20 | 15 | 15:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SECUNDARIA AVERIADA | P23032400105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 918 | 2023-03-24 | 13770 | keep | 0 | Mar | 2023 | 0.0093787 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-03-24 20:42 | 2023-03-25 09:44 | 21 | 13:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C23032400126 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 782 | 2023-03-24 | 16422 | keep | 0 | Mar | 2023 | 0.011185 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
HUMACAO | 2023-03-24 21:23 | 2023-03-25 09:04 | 70 | 11:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23032400128 | New_Event | Cutout Failure | Include | Include | Equipment | 701 | 2023-03-24 | 49070 | keep | 0 | Mar | 2023 | 0.033421 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-03-24 21:33 | 2023-03-25 17:51 | 2 | 20:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO 2 TRANSFORMADORES 25KVA POR 25KVA | S23032400125 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1218 | 2023-03-24 | 2436 | keep | 0 | Mar | 2023 | 0.0016591 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-24 22:00 | 2023-03-25 17:17 | 4 | 19:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B23032400151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1157 | 2023-03-24 | 4628 | keep | 0 | Mar | 2023 | 0.0031521 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-03-24 22:07 | 2023-03-24 22:08 | 603 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-24 | 603 | keep | 0 | Mar | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
HUMACAO | 2023-03-24 23:55 | 2023-03-24 23:57 | 640 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23032400135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-24 | 1280 | keep | 0 | Mar | 2023 | 0.0008718 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
BAYAMON | 2023-03-25 00:27 | 2023-03-25 03:07 | 30 | 2:40 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B23032500001 | New_Event | Animals | Include | Include | Wildlife | 160 | 2023-03-25 | 4800 | keep | 0 | Mar | 2023 | 0.0032693 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-03-25 01:51 | 2023-03-25 09:00 | 50 | 7:09 | P | DESGANCHE | 1 X 100 EN C/L | R23032500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2023-03-25 | 21450 | keep | 0 | Mar | 2023 | 0.014609 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-03-25 02:14 | 2023-03-25 11:54 | 70 | 9:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | C23032500003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 580 | 2023-03-25 | 40600 | keep | 0 | Mar | 2023 | 0.027652 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 1222 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1222 | keep | 0 | Mar | 2023 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 2756 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2756 | keep | 0 | Mar | 2023 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 2833 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2833 | keep | 0 | Mar | 2023 | 0.0019295 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 1218 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1218 | keep | 0 | Mar | 2023 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 1345 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1345 | keep | 0 | Mar | 2023 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 1265 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1265 | keep | 0 | Mar | 2023 | 0.00086159 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 2071 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2071 | keep | 0 | Mar | 2023 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 760 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 760 | keep | 0 | Mar | 2023 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 509 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 509 | keep | 0 | Mar | 2023 | 0.00034668 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 2620 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2620 | keep | 0 | Mar | 2023 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2023-03-25 02:45 | 2023-03-25 02:46 | 1916 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2100 SUB 7774 AAA FUNDIÃ“ UN FUSIBLE | A23032500007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1916 | keep | 0 | Mar | 2023 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
MAYAGÃœEZ | 2023-03-25 03:33 | 2023-03-25 09:40 | 382 | 6:07 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE CARGO MECANISMO PARA CERRAR Y SE CERRO INTERRUPTOR | M23032500008 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 367 | 2023-03-25 | 140194 | keep | 0 | Mar | 2023 | 0.095485 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
AGUADILLA | 2023-03-25 03:46 | 2023-03-25 08:10 | 500 | 4:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23032500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 264 | 2023-03-25 | 132000 | keep | 0 | Mar | 2023 | 0.089905 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2023-03-25 04:02 | 2023-03-25 04:03 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2303250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 4431 | keep | 0 | Mar | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2023-03-25 04:22 | 2023-03-25 06:49 | 25 | 2:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN RISER MAL TIEMPO LLUVIA | B23032500003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 147 | 2023-03-25 | 3675 | keep | 0 | Mar | 2023 | 0.002503 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-03-25 04:54 | 2023-03-25 07:20 | 20 | 2:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | A23032500024 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 146 | 2023-03-25 | 2920 | keep | 0 | Mar | 2023 | 0.0019888 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-03-25 05:00 | 2023-03-25 06:00 | 30 | 1:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | A23032500264 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 60 | 2023-03-25 | 1800 | keep | 0 | Mar | 2023 | 0.001226 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-03-25 06:00 | 2023-03-25 06:01 | 2201 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2201 | keep | 0 | Mar | 2023 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-03-25 06:00 | 2023-03-25 06:01 | 1986 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1986 | keep | 0 | Mar | 2023 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2023-03-25 06:00 | 2023-03-25 06:01 | 199 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 199 | keep | 0 | Mar | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-03-25 06:00 | 2023-03-25 06:01 | 24 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 24 | keep | 0 | Mar | 2023 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2023-03-25 06:01 | 2023-03-25 06:30 | 30 | 0:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | A23032500264 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 29 | 2023-03-25 | 870 | keep | 0 | Mar | 2023 | 0.00059255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-25 06:06 | 2023-03-25 06:09 | 2124 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1658-12 QUE LLEVA EL 1118-07 SE CERRO X CONTROL | R2303250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-25 | 6372 | keep | 0 | Mar | 2023 | 0.0043399 | 0.0014466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2124
CANOVANAS | 2023-03-25 06:06 | 2023-03-25 06:09 | 775 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1658-12 LLEVA EL 60% DEL 1657-02 SE CERRO X CONTROL | R2303250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-25 | 2325 | keep | 0 | Mar | 2023 | 0.0015835 | 0.00052785 | Momentary | FALSE | FALSE | Not_TMED_Event | 775
CANOVANAS | 2023-03-25 06:06 | 2023-03-25 06:09 | 363 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1658-12 LLEVA EL 1657-03 SE CERRO X CONTROL | R2303250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-25 | 1089 | keep | 0 | Mar | 2023 | 0.00074171 | 0.00024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 363
CANOVANAS | 2023-03-25 06:06 | 2023-03-25 06:09 | 14 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1658-12 LLEVA EL 1657-04 SE CERRO POR CONTROL | R2303250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-25 | 42 | keep | 0 | Mar | 2023 | 2.8606e-05 | 9.5353e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-03-25 06:07 | 2023-03-25 06:08 | 922 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1401-08 | S23032500000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-25 | 922 | keep | 0 | Mar | 2023 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-03-25 06:07 | 2023-03-25 06:08 | 135 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-05 | S23032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 135 | keep | 0 | Mar | 2023 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2023-03-25 06:07 | 2023-03-25 08:25 | 399 | 2:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN RISER MAL TIEMPO LLUVIA | B23032500005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 138 | 2023-03-25 | 55062 | keep | 0 | Mar | 2023 | 0.037502 | 0.00027176 | Sustained | FALSE | FALSE | Not_TMED_Event | 399
SAN JUAN | 2023-03-25 06:10 | 2023-03-25 09:45 | 80 | 3:35 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN CORTE DE LINEA SE CERRO PUENTE PRIMARIO | S23032500018 | New_Event | Primary Wire Break | Include | Include | Equipment | 215 | 2023-03-25 | 17200 | keep | 0 | Mar | 2023 | 0.011715 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-03-25 06:10 | 2023-03-25 07:24 | 771 | 1:14 | T | DESGANCHE | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO ALIMENTADOR LOCALMENTE 10% EN SERVICIO AL PROBAR ALIMENTADOR POR CONTROL DABA FAIL TO OPERATE | S23032500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-03-25 | 57054 | keep | 0 | Mar | 2023 | 0.038859 | 0.00052512 | Sustained | FALSE | FALSE | Not_TMED_Event | 771
CANOVANAS | 2023-03-25 06:14 | 2023-03-25 13:35 | 40 | 7:21 | P | DESGANCHE | 1 X 80 EN C/L | R23032500023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2023-03-25 | 17640 | keep | 0 | Mar | 2023 | 0.012015 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-25 06:19 | 2023-03-25 11:01 | 227 | 4:42 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23032500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2023-03-25 | 64014 | keep | 0 | Mar | 2023 | 0.0436 | 0.00015461 | Sustained | FALSE | FALSE | Not_TMED_Event | 227
ARECIBO | 2023-03-25 06:30 | 2023-03-25 06:31 | 2201 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500041 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2201 | keep | 0 | Mar | 2023 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-03-25 06:30 | 2023-03-25 06:31 | 1986 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500041 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1986 | keep | 0 | Mar | 2023 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2023-03-25 06:30 | 2023-03-25 06:31 | 199 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500041 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 199 | keep | 0 | Mar | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-03-25 06:30 | 2023-03-25 06:31 | 24 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500041 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 24 | keep | 0 | Mar | 2023 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2023-03-25 06:38 | 2023-03-25 09:20 | 200 | 2:42 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PARTIDO | A23032500042 | New_Event | Primary Wire Break | Include | Include | Equipment | 162 | 2023-03-25 | 32400 | keep | 0 | Mar | 2023 | 0.022067 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-03-25 06:42 | 2023-03-25 09:46 | 55 | 3:04 | P | DESGANCHE | 1 X 100 EN C/L | R23032500027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2023-03-25 | 10120 | keep | 0 | Mar | 2023 | 0.0068927 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2023-03-25 06:43 | 2023-03-25 09:50 | 55 | 3:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S23032500019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 187 | 2023-03-25 | 10285 | keep | 0 | Mar | 2023 | 0.0070051 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2023-03-25 06:47 | 2023-03-25 08:49 | 325 | 2:02 | T | NO SE REPORTO CAUSA | BY-230325-01 SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 50% EN SERVICIO | B23032500011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2023-03-25 | 39650 | keep | 0 | Mar | 2023 | 0.027005 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
PONCE | 2023-03-25 06:48 | 2023-03-25 09:28 | 15 | 2:40 | P | ANIMAL | 1 X 100 EN CL CRUCE DE FASE POR IGUANA | P23032500009 | New_Event | Animals | Include | Include | Wildlife | 160 | 2023-03-25 | 2400 | keep | 0 | Mar | 2023 | 0.0016346 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-03-25 06:48 | 2023-03-25 08:35 | 30 | 1:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A23032500046 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 107 | 2023-03-25 | 3210 | keep | 0 | Mar | 2023 | 0.0021863 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-25 06:49 | 2023-03-25 10:17 | 277 | 3:28 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23032500012 | New_Event | Animals | Include | Include | Wildlife | 208 | 2023-03-25 | 57616 | keep | 0 | Mar | 2023 | 0.039242 | 0.00018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 277
ARECIBO | 2023-03-25 06:50 | 2023-03-25 06:51 | 1227 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | A23032500048 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-03-25 | 1227 | keep | 0 | Mar | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-03-25 06:51 | 2023-03-25 06:52 | 3431 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | A23032500049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-03-25 | 3431 | keep | 0 | Mar | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-03-25 06:52 | 2023-03-25 19:40 | 30 | 12:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 40 EN CORTES DE LINEA FUERTES VIENTOS | A23032500189 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 768 | 2023-03-25 | 23040 | keep | 0 | Mar | 2023 | 0.015692 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-03-25 07:14 | 2023-03-25 09:11 | 4882 | 1:57 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO BAJANTE DE LINEA A CAJA DE CORTE DE LINEA Y SE CERRO INTERRUPTOR | M23032500032 | New_Event | Primary Wire Break | Include | Include | Equipment | 117 | 2023-03-25 | 571194 | keep | 0 | Mar | 2023 | 0.38904 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
VEGA BAJA | 2023-03-25 07:17 | 2023-03-25 07:18 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23032500057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 308 | keep | 0 | Mar | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2023-03-25 07:17 | 2023-03-25 07:18 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23032500058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 2697 | keep | 0 | Mar | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-03-25 07:20 | 2023-03-25 12:47 | 25 | 5:27 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASES | A23032500059 | New_Event | Animals | Include | Include | Wildlife | 327 | 2023-03-25 | 8175 | keep | 0 | Mar | 2023 | 0.005568 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-03-25 07:24 | 2023-03-25 07:43 | 700 | 0:19 | P | DESGANCHE | SE RETIRO GANCHO CRUZANDO FASE CON VARETA DE PISO Y SE CERRO MACHETE 100% EN SERVICIO | S23032500015 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 19 | 2023-03-25 | 13300 | keep | 0 | Mar | 2023 | 0.0090586 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-25 07:24 | 2023-03-25 07:26 | 3766 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R2303250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-25 | 7532 | keep | 0 | Mar | 2023 | 0.00513 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
ARECIBO | 2023-03-25 07:33 | 2023-03-25 09:56 | 50 | 2:23 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE RETIRO PARARRAYO CRUZADO | A23032500063 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 143 | 2023-03-25 | 7150 | keep | 0 | Mar | 2023 | 0.0048698 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-25 07:49 | 2023-03-25 10:21 | 5961 | 2:32 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE BKR SE CERRO N/O ENTRE 1717-02 Y 1713-05 80% EN SERVICIO SE SECCIONALIZO AISLADOR ROTO Y CONDUCTOR | B23032500016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 152 | 2023-03-25 | 906072 | keep | 0 | Mar | 2023 | 0.61712 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
VEGA BAJA | 2023-03-25 07:52 | 2023-03-25 10:15 | 16 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A23032500070 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2023-03-25 | 2288 | keep | 0 | Mar | 2023 | 0.0015583 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-03-25 08:06 | 2023-03-25 12:05 | 10 | 3:59 | P | ANIMAL | 1 X 20 EN C/L CRUCE X REPTIL | R23032500057 | New_Event | Animals | Include | Include | Wildlife | 239 | 2023-03-25 | 2390 | keep | 0 | Mar | 2023 | 0.0016278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-03-25 08:13 | 2023-03-25 08:14 | 1702 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | C23032500013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-03-25 | 1702 | keep | 0 | Mar | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-03-25 08:14 | 2023-03-25 18:13 | 80 | 9:59 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN C/L AVERIA DEL PROVISIONAL AEREO @ T-39 | C23032500014 | New_Event | UG Cable Fault | Include | Include | Equipment | 599 | 2023-03-25 | 47920 | keep | 0 | Mar | 2023 | 0.032638 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-03-25 08:14 | 2023-03-25 12:53 | 27 | 4:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C23032500016 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 279 | 2023-03-25 | 7533 | keep | 0 | Mar | 2023 | 0.0051307 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2023-03-25 08:14 | 2023-03-25 08:15 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23032500079 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 308 | keep | 0 | Mar | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2023-03-25 08:18 | 2023-03-25 08:24 | 143 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 80% DEL 1404-07 | S23032500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-03-25 | 858 | keep | 0 | Mar | 2023 | 0.00058438 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-03-25 08:18 | 2023-03-25 08:24 | 1085 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 80% POR 1404-06 | S23032500044 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-03-25 | 6510 | keep | 0 | Mar | 2023 | 0.0044339 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2023-03-25 08:31 | 2023-03-25 15:29 | 6 | 6:58 | P | DESGANCHE | 1 X 15 EN XMR Y DESGANCHE | B23032500073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 418 | 2023-03-25 | 2508 | keep | 0 | Mar | 2023 | 0.0017082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-03-25 08:38 | 2023-03-25 08:39 | 232 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 232 | keep | 0 | Mar | 2023 | 0.00015801 | 0.00015801 | Momentary | FALSE | FALSE | Not_TMED_Event | 232
BAYAMON | 2023-03-25 08:49 | 2023-03-25 09:47 | 162 | 0:58 | P | NO SE REPORTO CAUSA | BY-230325-01 REALIZANDO OPERACIONES EN EL CAMPO SE DISPARO ALIMENTADOR | B23032500011 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 58 | 2023-03-25 | 9396 | keep | 0 | Mar | 2023 | 0.0063996 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-25 08:50 | 2023-03-25 08:53 | 2201 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500140 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-25 | 6603 | keep | 0 | Mar | 2023 | 0.0044973 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-03-25 08:50 | 2023-03-25 08:53 | 1986 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500140 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-25 | 5958 | keep | 0 | Mar | 2023 | 0.004058 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2023-03-25 08:50 | 2023-03-25 08:53 | 199 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500140 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-25 | 597 | keep | 0 | Mar | 2023 | 0.00040661 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-03-25 08:50 | 2023-03-25 08:53 | 24 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500140 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-25 | 72 | keep | 0 | Mar | 2023 | 4.9039e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2023-03-25 08:53 | 2023-03-25 08:59 | 30 | 0:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | A23032500264 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 6 | 2023-03-25 | 180 | keep | 0 | Mar | 2023 | 0.0001226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-03-25 08:58 | 2023-03-25 08:59 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23032500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 1827 | keep | 0 | Mar | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2023-03-25 08:59 | 2023-03-25 11:55 | 50 | 2:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23032500055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-03-25 | 8800 | keep | 0 | Mar | 2023 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-25 08:59 | 2023-03-25 11:25 | 72 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE ABIERTO TRAS PATIO | S23032500041 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2023-03-25 | 10512 | keep | 0 | Mar | 2023 | 0.0071597 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
ARECIBO | 2023-03-25 08:59 | 2023-03-25 10:47 | 2201 | 1:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500143 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2023-03-25 | 237708 | keep | 0 | Mar | 2023 | 0.1619 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-03-25 08:59 | 2023-03-25 10:47 | 1986 | 1:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500143 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2023-03-25 | 214488 | keep | 0 | Mar | 2023 | 0.14609 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2023-03-25 08:59 | 2023-03-25 10:47 | 199 | 1:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500143 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2023-03-25 | 21492 | keep | 0 | Mar | 2023 | 0.014638 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-03-25 08:59 | 2023-03-25 10:47 | 24 | 1:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FUSIBLE FUNDIDO EN SUB 8067 PLAZA DEL NORTE Y FUSIBLE FUNDIDO EN SUB 7779 HOME DEPOT | A23032500143 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2023-03-25 | 2592 | keep | 0 | Mar | 2023 | 0.0017654 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-03-25 09:04 | 2023-03-25 09:06 | 178 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-25 | 356 | keep | 0 | Mar | 2023 | 0.00024247 | 0.00012123 | Momentary | FALSE | FALSE | Not_TMED_Event | 178
AGUADILLA | 2023-03-25 09:11 | 2023-03-25 11:50 | 2800 | 2:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA SE CERRO MACHETES | M23032500076 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 159 | 2023-03-25 | 445200 | keep | 0 | Mar | 2023 | 0.30322 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-25 09:20 | 2023-03-25 09:21 | 2071 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | A23032500144 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-25 | 2071 | keep | 0 | Mar | 2023 | 0.0014105 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-25 09:21 | 2023-03-25 09:23 | 200 | 0:02 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PARTIDO | A23032500042 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2023-03-25 | 400 | keep | 0 | Mar | 2023 | 0.00027244 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 1222 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1222 | keep | 0 | Mar | 2023 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 2756 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2756 | keep | 0 | Mar | 2023 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 2833 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2833 | keep | 0 | Mar | 2023 | 0.0019295 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 1218 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1218 | keep | 0 | Mar | 2023 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 1345 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500150 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1345 | keep | 0 | Mar | 2023 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 1265 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500150 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1265 | keep | 0 | Mar | 2023 | 0.00086159 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 2071 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500150 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2071 | keep | 0 | Mar | 2023 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 760 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500150 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 760 | keep | 0 | Mar | 2023 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 509 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500152 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 509 | keep | 0 | Mar | 2023 | 0.00034668 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 2620 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500152 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 2620 | keep | 0 | Mar | 2023 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2023-03-25 09:23 | 2023-03-25 09:24 | 1916 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A23032500152 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-03-25 | 1916 | keep | 0 | Mar | 2023 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2023-03-25 09:24 | 2023-03-25 12:40 | 200 | 3:16 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PARTIDO | A23032500042 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 196 | 2023-03-25 | 39200 | keep | 0 | Mar | 2023 | 0.026699 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-03-25 09:30 | 2023-03-25 14:10 | 25 | 4:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23032500297 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2023-03-25 | 7000 | keep | 0 | Mar | 2023 | 0.0047677 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-03-25 09:43 | 2023-03-25 14:13 | 53 | 4:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER 1 X 40 EN SU-1 | S23032500067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2023-03-25 | 14310 | keep | 0 | Mar | 2023 | 0.0097465 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BAYAMON | 2023-03-25 09:47 | 2023-03-25 09:50 | 325 | 0:03 | T | NO SE REPORTO CAUSA | BY-230325-01 SE VOLVIO A SECCIONALIZAR A LIMENTADOR 50% EN SERVICIO | B23032500011 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-25 | 975 | keep | 0 | Mar | 2023 | 0.00066407 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-25 09:49 | 2023-03-25 17:14 | 150 | 7:25 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN C/L DESGANCHE | C23032500030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 445 | 2023-03-25 | 66750 | keep | 0 | Mar | 2023 | 0.045463 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-03-25 09:50 | 2023-03-25 11:32 | 162 | 1:42 | P | NO SE REPORTO CAUSA | BY-230325-01 SE SECCIONALIZO ALIMENTADOR EN SERVICIO 90% | B23032500011 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 102 | 2023-03-25 | 16524 | keep | 0 | Mar | 2023 | 0.011254 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
AGUADILLA | 2023-03-25 09:51 | 2023-03-25 11:40 | 200 | 1:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23032500086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2023-03-25 | 21800 | keep | 0 | Mar | 2023 | 0.014848 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-03-25 10:05 | 2023-03-25 10:20 | 30 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA AVERIADA | B23032500004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-03-25 | 450 | keep | 0 | Mar | 2023 | 0.00030649 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-03-25 10:19 | 2023-03-25 14:45 | 70 | 4:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR ROTO Y 1 X 100 EN C/L | R23032500083 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 266 | 2023-03-25 | 18620 | keep | 0 | Mar | 2023 | 0.012682 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-03-25 10:20 | 2023-03-25 13:31 | 399 | 3:11 | P | NO SE REPORTO CAUSA | 1 X 65 1 X 40 NO SE REPORTO CAUSA | B23032500282 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2023-03-25 | 76209 | keep | 0 | Mar | 2023 | 0.051906 | 0.00027176 | Sustained | FALSE | FALSE | Not_TMED_Event | 399
BAYAMON | 2023-03-25 10:21 | 2023-03-25 13:20 | 1192 | 2:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y SE LEVANTO CONDUCTOR SE PASO EL 20% RESTANTE AL 1717-02 POR BRK 1713-05 PROBANDO MALO SIN CARGA | B23032500016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 179 | 2023-03-25 | 213368 | keep | 0 | Mar | 2023 | 0.14532 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
FAJARDO | 2023-03-25 10:40 | 2023-03-25 13:04 | 5 | 2:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | R23032500082 | New_Event | Service Transformer Failure | Include | Include | Equipment | 144 | 2023-03-25 | 720 | keep | 0 | Mar | 2023 | 0.00049039 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-25 10:42 | 2023-03-25 13:48 | 81 | 3:06 | P | OTRAS CAUSAS | SE CORRIGIO FASEO EN N/O CONTRA EL MISMO FEEDER | R2303250000X | New_Event | Other Causes | Include | Include | Other | 186 | 2023-03-25 | 15066 | keep | 0 | Mar | 2023 | 0.010261 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
CAGUAS | 2023-03-25 10:42 | 2023-03-25 10:43 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23032500038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 918 | keep | 0 | Mar | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
ARECIBO | 2023-03-25 10:47 | 2023-03-25 15:45 | 30 | 4:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | A23032500264 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 298 | 2023-03-25 | 8940 | keep | 0 | Mar | 2023 | 0.006089 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-25 10:48 | 2023-03-25 12:20 | 80 | 1:32 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M23032500101 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-03-25 | 7360 | keep | 0 | Mar | 2023 | 0.0050129 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-25 10:50 | 2023-03-25 15:50 | 200 | 5:00 | P | NO SE REPORTO CAUSA | 1 X 140 C/L | B23032500310 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 300 | 2023-03-25 | 60000 | keep | 0 | Mar | 2023 | 0.040866 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-03-25 10:52 | 2023-03-25 17:11 | 165 | 6:19 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN C/L Y SE REMOVIO PARARRAYO | B23032500311 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 379 | 2023-03-25 | 62535 | keep | 0 | Mar | 2023 | 0.042592 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
CANOVANAS | 2023-03-25 11:08 | 2023-03-25 14:10 | 30 | 3:02 | P | DESGANCHE | 1 X 40 EN AEREO PROVISIONAL SE REALIZO DESGANCHE | R23032500090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-03-25 | 5460 | keep | 0 | Mar | 2023 | 0.0037188 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-03-25 11:20 | 2023-03-25 15:39 | 9 | 4:19 | P | DESGANCHE | 1 X 30 EN C/L | R23032500095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-03-25 | 2331 | keep | 0 | Mar | 2023 | 0.0015876 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-03-25 11:25 | 2023-03-25 12:23 | 229 | 0:58 | P | CONDUCTOR ROTO O ABIERTO | SE ESTABLECIO GOI PARA CERRAR PUENTE TRAS PATIO | S23032500041 | New_Event | Primary Wire Break | Include | Include | Equipment | 58 | 2023-03-25 | 13282 | keep | 0 | Mar | 2023 | 0.0090463 | 0.00015597 | Sustained | FALSE | FALSE | Not_TMED_Event | 229
SAN JUAN | 2023-03-25 11:28 | 2023-03-25 13:57 | 8 | 2:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S23032500082 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 149 | 2023-03-25 | 1192 | keep | 0 | Mar | 2023 | 0.00081187 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-03-25 11:32 | 2023-03-25 20:35 | 38 | 9:03 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L PARA REEMPLAZO DE POSTE PRIMARIO PARTIDO | R23032500098 | New_Event | Primary Pole Failure | Include | Include | Equipment | 543 | 2023-03-25 | 20634 | keep | 0 | Mar | 2023 | 0.014054 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2023-03-25 11:32 | 2023-03-25 12:43 | 293 | 1:11 | P | NO SE REPORTO CAUSA | BY-230325-01 SE CERRO MACHETES 100% EN SERVICIO NO SE ENCONTRO CAUSA | B23032500011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2023-03-25 | 20803 | keep | 0 | Mar | 2023 | 0.014169 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
GUAYAMA | 2023-03-25 11:50 | 2023-03-25 12:10 | 6 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | P23032500044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-03-25 | 120 | keep | 0 | Mar | 2023 | 8.1731e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-03-25 11:53 | 2023-03-25 14:06 | 100 | 2:13 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA Y SE LEVANTO LINEA PRIMARIA | S23032500102 | New_Event | Primary Wire Break | Include | Include | Equipment | 133 | 2023-03-25 | 13300 | keep | 0 | Mar | 2023 | 0.0090586 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-03-25 12:04 | 2023-03-25 14:32 | 30 | 2:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C23032500046 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 148 | 2023-03-25 | 4440 | keep | 0 | Mar | 2023 | 0.0030241 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-03-25 12:15 | 2023-03-25 12:16 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P23032500046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 1746 | keep | 0 | Mar | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
AGUADILLA | 2023-03-25 12:22 | 2023-03-25 20:53 | 60 | 8:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032500122 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 511 | 2023-03-25 | 30660 | keep | 0 | Mar | 2023 | 0.020882 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-03-25 12:30 | 2023-03-25 14:20 | 450 | 1:50 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA APAGAR FUEGO EN POSTE Y SE REMPLAZO BAJANTES PRIMARIOS QUEMADOS | M23032500122 | New_Event | Primary Wire Break | Include | Include | Equipment | 110 | 2023-03-25 | 49500 | keep | 0 | Mar | 2023 | 0.033714 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
YAUCO | 2023-03-25 12:33 | 2023-03-25 16:25 | 25 | 3:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REEMPLAZO DE LINEA SECUNDARIA 1 X 10 EN TRANSFORMADOR | P23032500051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 232 | 2023-03-25 | 5800 | keep | 0 | Mar | 2023 | 0.0039504 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-03-25 12:40 | 2023-03-25 16:00 | 1200 | 3:20 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES Y SE REPARO LINEA PARTIDA | A23032500042 | New_Event | Primary Wire Break | Include | Include | Equipment | 200 | 2023-03-25 | 240000 | keep | 0 | Mar | 2023 | 0.16346 | 0.00081731 | Sustained | FALSE | FALSE | Not_TMED_Event | 1200
VEGA BAJA | 2023-03-25 12:41 | 2023-03-25 12:42 | 759 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23032500284 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 759 | keep | 0 | Mar | 2023 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2023-03-25 13:00 | 2023-03-25 18:40 | 3 | 5:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A23032500403 | New_Event | Cutout Failure | Include | Include | Equipment | 340 | 2023-03-25 | 1020 | keep | 0 | Mar | 2023 | 0.00069472 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-03-25 13:15 | 2023-03-25 15:21 | 70 | 2:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23032500396 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2023-03-25 | 8820 | keep | 0 | Mar | 2023 | 0.0060073 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-03-25 13:36 | 2023-03-25 17:15 | 32 | 3:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23032500401 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2023-03-25 | 7008 | keep | 0 | Mar | 2023 | 0.0047731 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2023-03-25 13:38 | 2023-03-25 14:11 | 20 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23032500402 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-03-25 | 660 | keep | 0 | Mar | 2023 | 0.00044952 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-25 13:50 | 2023-03-25 15:50 | 50 | 2:00 | P | DESGANCHE | 1 X 40 Y 1 X 80 EN CORTE DE LINEA DESGANCHE | S23032500129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-03-25 | 6000 | keep | 0 | Mar | 2023 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-25 13:51 | 2023-03-25 15:10 | 45 | 1:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | B23032500412 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-03-25 | 3555 | keep | 0 | Mar | 2023 | 0.0024213 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2023-03-25 13:53 | 2023-03-25 13:54 | 1131 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23032500054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 1131 | keep | 0 | Mar | 2023 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
PONCE | 2023-03-25 13:54 | 2023-03-25 17:45 | 144 | 3:51 | P | DESGANCHE | 1 X 100 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P23032500072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2023-03-25 | 33264 | keep | 0 | Mar | 2023 | 0.022656 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
GUAYAMA | 2023-03-25 14:02 | 2023-03-25 15:13 | 130 | 1:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA FUERTE BRISA | P23032500075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2023-03-25 | 9230 | keep | 0 | Mar | 2023 | 0.0062865 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
ARECIBO | 2023-03-25 14:25 | 2023-03-26 13:50 | 30 | 23:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23032500338 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1405 | 2023-03-25 | 42150 | keep | 0 | Mar | 2023 | 0.028708 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-03-25 14:28 | 2023-03-25 14:29 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032500110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 4085 | keep | 0 | Mar | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
ARECIBO | 2023-03-25 14:36 | 2023-03-25 16:21 | 314 | 1:45 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE EN MALAS CONDICIONES | A23032500344 | New_Event | Switch Failure | Include | Include | Equipment | 105 | 2023-03-25 | 32970 | keep | 0 | Mar | 2023 | 0.022456 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
AGUADILLA | 2023-03-25 14:52 | 2023-03-25 22:40 | 50 | 7:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M23032500154 | New_Event | Cutout Failure | Include | Include | Equipment | 468 | 2023-03-25 | 23400 | keep | 0 | Mar | 2023 | 0.015938 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-25 14:55 | 2023-03-25 15:07 | 19 | 0:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BARRA EN PEDESTAL | B23032500434 | New_Event | Secondary Wire Break | Include | Include | Equipment | 12 | 2023-03-25 | 228 | keep | 0 | Mar | 2023 | 0.00015529 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
ARECIBO | 2023-03-25 14:59 | 2023-03-25 15:00 | 316 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | A23032500360 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-25 | 316 | keep | 0 | Mar | 2023 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2023-03-25 15:00 | 2023-03-25 18:20 | 60 | 3:20 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A23032500361 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 200 | 2023-03-25 | 12000 | keep | 0 | Mar | 2023 | 0.0081731 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-03-25 15:00 | 2023-03-25 18:56 | 15 | 3:56 | P | DESGANCHE | 3 X 80 Y DESGANCHE | B23032500343 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2023-03-25 | 3540 | keep | 0 | Mar | 2023 | 0.0024111 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-25 15:10 | 2023-03-25 16:26 | 28 | 1:16 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA LEVANTAR PRIMARIA | S23032500114 | New_Event | Primary Wire Break | Include | Include | Equipment | 76 | 2023-03-25 | 2128 | keep | 0 | Mar | 2023 | 0.0014494 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
HUMACAO | 2023-03-25 15:11 | 2023-03-25 17:07 | 10 | 1:56 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C23032500060 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 116 | 2023-03-25 | 1160 | keep | 0 | Mar | 2023 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-03-25 15:19 | 2023-03-25 15:49 | 15 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BAJANTES SECUNDARIOS | C23032500008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-03-25 | 450 | keep | 0 | Mar | 2023 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-03-25 15:33 | 2023-03-25 16:38 | 50 | 1:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN CORTE DE LINEA FUERTES VIENTOS | A23032500372 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 65 | 2023-03-25 | 3250 | keep | 0 | Mar | 2023 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-03-25 15:53 | 2023-03-25 19:20 | 15 | 3:27 | P | ANIMAL | 1 X 40 EN C/L CURCE X AVE | C23032500065 | New_Event | Animals | Include | Include | Wildlife | 207 | 2023-03-25 | 3105 | keep | 0 | Mar | 2023 | 0.0021148 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-25 16:04 | 2023-03-25 16:05 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23032500166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-25 | 2067 | keep | 0 | Mar | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
FAJARDO | 2023-03-25 16:09 | 2023-03-25 16:57 | 86 | 0:48 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE LEVANTO CONDUCTOR PRIMARIO RADIAL NO HABIA FUNDIDO | R23032500115 | New_Event | Primary Wire Break | Include | Include | Equipment | 48 | 2023-03-25 | 4128 | keep | 0 | Mar | 2023 | 0.0028116 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
MAYAGÃœEZ | 2023-03-25 16:29 | 2023-03-25 19:01 | 80 | 2:32 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23032500167 | New_Event | Animals | Include | Include | Wildlife | 152 | 2023-03-25 | 12160 | keep | 0 | Mar | 2023 | 0.0082821 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-03-25 16:43 | 2023-03-25 18:01 | 14 | 1:18 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | B23032500467 | New_Event | Animals | Include | Include | Wildlife | 78 | 2023-03-25 | 1092 | keep | 0 | Mar | 2023 | 0.00074376 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-03-25 17:10 | 2023-03-25 17:20 | 15 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23032500147 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-03-25 | 150 | keep | 0 | Mar | 2023 | 0.00010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-25 17:11 | 2023-03-25 21:35 | 56 | 4:24 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PARA CERRAR PUENTE PRIMARIO | S23032500149 | New_Event | Primary Wire Break | Include | Include | Equipment | 264 | 2023-03-25 | 14784 | keep | 0 | Mar | 2023 | 0.010069 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
GUAYAMA | 2023-03-25 17:23 | 2023-03-25 20:30 | 1 | 3:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN MONTURA TRIFASICA Y 1 X 10 AMP. | P23032500120 | New_Event | Cutout Failure | Include | Include | Equipment | 187 | 2023-03-25 | 187 | keep | 0 | Mar | 2023 | 0.00012736 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-03-25 17:30 | 2023-03-26 08:55 | 25 | 15:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | A23032500400 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 925 | 2023-03-25 | 23125 | keep | 0 | Mar | 2023 | 0.01575 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-03-25 17:31 | 2023-03-26 07:20 | 15 | 13:49 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | A23032500401 | New_Event | Animals | Include | Include | Wildlife | 829 | 2023-03-25 | 12435 | keep | 0 | Mar | 2023 | 0.0084694 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-03-25 17:36 | 2023-03-26 11:28 | 7 | 17:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | A23032500405 | New_Event | Cutout Failure | Include | Include | Equipment | 1072 | 2023-03-25 | 7504 | keep | 0 | Mar | 2023 | 0.0051109 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-25 17:40 | 2023-03-25 19:22 | 3597 | 1:42 | S | PROTECCION DEFECTUOSA | BY-230325-03 SUBESTACION EN LOCKOUT | B23032500485 | New_Event | Protection Miscoordination | Include | Include | Other | 102 | 2023-03-25 | 366894 | keep | 0 | Mar | 2023 | 0.24989 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-03-25 17:40 | 2023-03-25 19:22 | 492 | 1:42 | S | PROTECCION DEFECTUOSA | BY-230325-03 SUBESTACION EN LOCKOUT | B23032500485 | New_Event | Protection Miscoordination | Include | Include | Other | 102 | 2023-03-25 | 50184 | keep | 0 | Mar | 2023 | 0.03418 | 0.0003351 | Sustained | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2023-03-25 17:40 | 2023-03-25 19:22 | 4028 | 1:42 | S | PROTECCION DEFECTUOSA | BY-230325-03 SUBESTACION EN LOCKOUT | B23032500485 | New_Event | Protection Miscoordination | Include | Include | Other | 102 | 2023-03-25 | 410856 | keep | 0 | Mar | 2023 | 0.27983 | 0.0027435 | Sustained | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2023-03-25 17:40 | 2023-03-25 19:22 | 2617 | 1:42 | S | PROTECCION DEFECTUOSA | BY-230325-03 SUBESTACION EN LOCKOUT | B23032500485 | New_Event | Protection Miscoordination | Include | Include | Other | 102 | 2023-03-25 | 266934 | keep | 0 | Mar | 2023 | 0.18181 | 0.0017824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2617
CAGUAS | 2023-03-25 18:13 | 2023-03-26 11:15 | 12 | 17:02 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO ALAMBRE DEL AEREO PROVISIONAL HACIA T-39 | C23032500014 | New_Event | Primary Wire Break | Include | Include | Equipment | 1022 | 2023-03-25 | 12264 | keep | 0 | Mar | 2023 | 0.008353 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-03-25 18:32 | 2023-03-25 20:30 | 441 | 1:58 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 100 EN C/L CRUCE X AVE | R23032500125 | New_Event | Animals | Include | Include | Wildlife | 118 | 2023-03-25 | 52038 | keep | 0 | Mar | 2023 | 0.035443 | 0.00030036 | Sustained | FALSE | FALSE | Not_TMED_Event | 441
UTUADO | 2023-03-25 18:44 | 2023-03-26 12:30 | 7 | 17:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23032500415 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1066 | 2023-03-25 | 7462 | keep | 0 | Mar | 2023 | 0.0050823 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-03-25 18:57 | 2023-03-25 20:35 | 80 | 1:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032500195 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 98 | 2023-03-25 | 7840 | keep | 0 | Mar | 2023 | 0.0053398 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-03-25 18:58 | 2023-03-25 21:20 | 21 | 2:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23032500158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-03-25 | 2982 | keep | 0 | Mar | 2023 | 0.002031 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
AGUADILLA | 2023-03-25 19:26 | 2023-03-26 11:04 | 50 | 15:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 Y 1 X 25 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | M23032500200 | New_Event | Cutout Failure | Include | Include | Equipment | 938 | 2023-03-25 | 46900 | keep | 0 | Mar | 2023 | 0.031943 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-03-25 19:53 | 2023-03-25 20:48 | 70 | 0:55 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23032500075 | New_Event | Animals | Include | Include | Wildlife | 55 | 2023-03-25 | 3850 | keep | 0 | Mar | 2023 | 0.0026222 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-03-25 21:35 | 2023-03-25 22:04 | 701 | 0:29 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO SJ-230325-04 | S23032500149 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 29 | 2023-03-25 | 20329 | keep | 0 | Mar | 2023 | 0.013846 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-25 21:45 | 2023-03-26 16:31 | 25 | 18:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L LLUVIA | B23032500750 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1126 | 2023-03-25 | 28150 | keep | 0 | Mar | 2023 | 0.019173 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-03-25 21:50 | 2023-03-26 14:55 | 6 | 17:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23032500463 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1025 | 2023-03-25 | 6150 | keep | 0 | Mar | 2023 | 0.0041887 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-03-25 21:59 | 2023-03-26 00:02 | 671 | 2:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23032500752 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2023-03-25 | 82533 | keep | 0 | Mar | 2023 | 0.056213 | 0.00045702 | Sustained | FALSE | FALSE | Not_TMED_Event | 671
ARECIBO | 2023-03-25 22:13 | 2023-03-26 08:43 | 100 | 10:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23032500467 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 630 | 2023-03-25 | 63000 | keep | 0 | Mar | 2023 | 0.042909 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-03-25 23:11 | 2023-03-26 11:40 | 100 | 12:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23032500226 | New_Event | Cutout Failure | Include | Include | Equipment | 749 | 2023-03-25 | 74900 | keep | 0 | Mar | 2023 | 0.051014 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-03-26 01:35 | 2023-03-26 04:37 | 3597 | 3:02 | S | PROTECCION DEFECTUOSA | LOCKOUT DE SUBESTACION PROBLEMAS CON EL DC, NO DISPARO MECANICO, NO DIFERENCIAL SE REMONTO LOCKOUT EN SERVICIO BY-230325-03 | B23032600017 | New_Event | Protection Miscoordination | Include | Include | Other | 182 | 2023-03-26 | 654654 | keep | 0 | Mar | 2023 | 0.44588 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-03-26 01:35 | 2023-03-26 04:38 | 492 | 3:03 | S | PROTECCION DEFECTUOSA | LOCKOUT DE SUBESTACION JUAN C FUENTES INFORMA QUE NO SE ENCONTRO NADA EN SUBESTACION NO BANDERAS DE PROTECCION, NO DISPARO MECANICO, NO DIFERENCIAL SE REMONTO LOCKOUT EN SERVICIO BY-230325-03 LLEVA LA CARGA DEL 1719-18 | B23032600017 | New_Event | Protection Miscoordination | Include | Include | Other | 183 | 2023-03-26 | 90036 | keep | 0 | Mar | 2023 | 0.061323 | 0.0003351 | Sustained | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2023-03-26 01:35 | 2023-03-26 04:38 | 4028 | 3:03 | S | PROTECCION DEFECTUOSA | LOCKOUT DE SUBESTACION JUAN C FUENTES INFORMA QUE NO SE ENCONTRO NADA EN SUBESTACION NO BANDERAS DE PROTECCION, NO DISPARO MECANICO, NO DIFERENCIAL SE REMONTO LOCKOUT EN SERVICIO BY-230325-03 CARGA POR EL 1719-16 | B23032600017 | New_Event | Protection Miscoordination | Include | Include | Other | 183 | 2023-03-26 | 737124 | keep | 0 | Mar | 2023 | 0.50205 | 0.0027435 | Sustained | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2023-03-26 01:35 | 2023-03-26 04:38 | 2617 | 3:03 | S | PROTECCION DEFECTUOSA | LOCKOUT DE SUBESTACION JUAN C FUENTES INFORMA QUE NO SE ENCONTRO NADA EN SUBESTACION NO BANDERAS DE PROTECCION, NO DISPARO MECANICO, NO DIFERENCIAL SE REMONTO LOCKOUT EN SERVICIO BY-230325-03 | B23032600017 | New_Event | Protection Miscoordination | Include | Include | Other | 183 | 2023-03-26 | 478911 | keep | 0 | Mar | 2023 | 0.32618 | 0.0017824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2617
CANOVANAS | 2023-03-26 03:05 | 2023-03-26 08:27 | 30 | 5:22 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23032600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2023-03-26 | 9660 | keep | 0 | Mar | 2023 | 0.0065794 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-03-26 03:31 | 2023-03-26 08:45 | 30 | 5:14 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 2 X 50 EN CORTES DE LINEA DISTINTOS SE REMPLAZO PARARRAYOS DEFECTUOSO | A23032600010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 314 | 2023-03-26 | 9420 | keep | 0 | Mar | 2023 | 0.0064159 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-26 04:05 | 2023-03-26 09:45 | 30 | 5:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032600004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 340 | 2023-03-26 | 10200 | keep | 0 | Mar | 2023 | 0.0069472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-03-26 04:06 | 2023-03-26 12:34 | 12 | 8:28 | P | NO SE REPORTO CAUSA | 2 X 65 Y 1 X 50 AMBOS EN RISER NO CAUSA | B23032600070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 508 | 2023-03-26 | 6096 | keep | 0 | Mar | 2023 | 0.004152 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-03-26 04:38 | 2023-03-26 11:05 | 212 | 6:27 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23032600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 387 | 2023-03-26 | 82044 | keep | 0 | Mar | 2023 | 0.05588 | 0.00014439 | Sustained | FALSE | FALSE | Not_TMED_Event | 212
CANOVANAS | 2023-03-26 05:41 | 2023-03-26 05:42 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 4085 | keep | 0 | Mar | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-03-26 06:08 | 2023-03-26 06:10 | 844 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 35% DEL 1345-05 | S23032600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-26 | 1688 | keep | 0 | Mar | 2023 | 0.0011497 | 0.00057484 | Momentary | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2023-03-26 06:08 | 2023-03-26 06:10 | 333 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 35% POR 1330-04 | S23032600005 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-26 | 666 | keep | 0 | Mar | 2023 | 0.00045361 | 0.0002268 | Momentary | FALSE | FALSE | Not_TMED_Event | 333
SAN JUAN | 2023-03-26 06:40 | 2023-03-26 08:04 | 1 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 TERMINACIÃ“N AVERIADA EN RISER HACIA SUB 1965 BELLAS ARTES GUAYNABO | S23032600025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-03-26 | 84 | keep | 0 | Mar | 2023 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-26 06:40 | 2023-03-26 08:04 | 737 | 1:24 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 LLEVA 40% DE SU CARGA TERMINACIÃ“N AVERIADA EN RISER HACIA SUB 1965 BELLAS ARTES GUAYNABO | S23032600025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-03-26 | 61908 | keep | 0 | Mar | 2023 | 0.042165 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2023-03-26 06:40 | 2023-03-26 08:04 | 2422 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 TERMINACIÃ“N AVERIADA EN RISER HACIA SUB 1965 BELLAS ARTES GUAYNABO | S23032600025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-03-26 | 203448 | keep | 0 | Mar | 2023 | 0.13857 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
BAYAMON | 2023-03-26 06:43 | 2023-03-26 08:07 | 959 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 TERMINACIÃ“N AVERIADA EN RISER HACIA SUB 1965 BELLAS ARTES GUAYNABO | S23032600020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-03-26 | 80556 | keep | 0 | Mar | 2023 | 0.054866 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-03-26 06:43 | 2023-03-26 08:07 | 1297 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 TERMINACIÃ“N AVERIADA EN RISER HACIA SUB 1965 BELLAS ARTES GUAYNABO | S23032600020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-03-26 | 108948 | keep | 0 | Mar | 2023 | 0.074204 | 0.00088338 | Sustained | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2023-03-26 06:43 | 2023-03-26 08:07 | 451 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 TERMINACIÃ“N AVERIADA EN RISER HACIA SUB 1965 BELLAS ARTES GUAYNABO | S23032600020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-03-26 | 37884 | keep | 0 | Mar | 2023 | 0.025803 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2023-03-26 06:43 | 2023-03-26 08:07 | 1264 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 TERMINACIÃ“N AVERIADA EN RISER HACIA SUB 1965 BELLAS ARTES GUAYNABO | S23032600020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-03-26 | 106176 | keep | 0 | Mar | 2023 | 0.072316 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-03-26 06:43 | 2023-03-26 08:07 | 620 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 TERMINACIÃ“N AVERIADA EN RISER HACIA SUB 1965 BELLAS ARTES GUAYNABO | S23032600020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-03-26 | 52080 | keep | 0 | Mar | 2023 | 0.035471 | 0.00042228 | Sustained | FALSE | FALSE | Not_TMED_Event | 620
PONCE | 2023-03-26 06:59 | 2023-03-26 07:00 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23032600017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 2379 | keep | 0 | Mar | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
YAUCO | 2023-03-26 07:38 | 2023-03-26 09:45 | 50 | 2:07 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M23032600013 | New_Event | Animals | Include | Include | Wildlife | 127 | 2023-03-26 | 6350 | keep | 0 | Mar | 2023 | 0.004325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-26 07:41 | 2023-03-26 08:15 | 1935 | 0:34 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN 9800 | B23032600154 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 34 | 2023-03-26 | 65790 | keep | 0 | Mar | 2023 | 0.044809 | 0.0013179 | Sustained | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2023-03-26 07:41 | 2023-03-26 08:15 | 3 | 0:34 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN 9800 | B23032600154 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 34 | 2023-03-26 | 102 | keep | 0 | Mar | 2023 | 6.9472e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-03-26 07:41 | 2023-03-26 08:15 | 61 | 0:34 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN 9800 | B23032600154 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 34 | 2023-03-26 | 2074 | keep | 0 | Mar | 2023 | 0.0014126 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2023-03-26 07:41 | 2023-03-26 08:15 | 1501 | 0:34 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN 9800 | B23032600154 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 34 | 2023-03-26 | 51034 | keep | 0 | Mar | 2023 | 0.034759 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2023-03-26 07:41 | 2023-03-26 08:15 | 546 | 0:34 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN 9800 | B23032600154 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 34 | 2023-03-26 | 18564 | keep | 0 | Mar | 2023 | 0.012644 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
SAN JUAN | 2023-03-26 07:52 | 2023-03-26 13:15 | 50 | 5:23 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | S23032600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2023-03-26 | 16150 | keep | 0 | Mar | 2023 | 0.011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-03-26 07:59 | 2023-03-26 09:37 | 40 | 1:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO AISLADOR | R23032600007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 98 | 2023-03-26 | 3920 | keep | 0 | Mar | 2023 | 0.0026699 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-03-26 08:04 | 2023-03-26 13:43 | 8 | 5:39 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23032600014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 339 | 2023-03-26 | 2712 | keep | 0 | Mar | 2023 | 0.0018471 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-03-26 08:07 | 2023-03-26 10:13 | 3 | 2:06 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23032600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2023-03-26 | 378 | keep | 0 | Mar | 2023 | 0.00025745 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-03-26 08:09 | 2023-03-26 08:10 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 85% POR 1206-03 | S23032600000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-26 | 8679 | keep | 0 | Mar | 2023 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-03-26 08:09 | 2023-03-26 08:10 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA 85% DEL 1204-05 | S23032600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 4133 | keep | 0 | Mar | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
AGUADILLA | 2023-03-26 08:16 | 2023-03-26 11:00 | 150 | 2:44 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-03-26 | 24600 | keep | 0 | Mar | 2023 | 0.016755 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-03-26 08:18 | 2023-03-26 13:04 | 6 | 4:46 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23032600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2023-03-26 | 1716 | keep | 0 | Mar | 2023 | 0.0011688 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-03-26 08:27 | 2023-03-26 10:42 | 1 | 2:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | C23032600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2023-03-26 | 135 | keep | 0 | Mar | 2023 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-03-26 08:37 | 2023-03-26 09:25 | 109 | 0:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE CORTE DE LNEA PARA REEMPLAZO SE AISLADOR PRIMARIO | P23032600044 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 48 | 2023-03-26 | 5232 | keep | 0 | Mar | 2023 | 0.0035635 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
HUMACAO | 2023-03-26 08:41 | 2023-03-26 09:35 | 28 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA PARA REEMPLAZAR BAJANTES SECUNDARIOS | C23032600005 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2023-03-26 | 1512 | keep | 0 | Mar | 2023 | 0.0010298 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2023-03-26 08:43 | 2023-03-26 10:24 | 15 | 1:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23032600063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-03-26 | 1515 | keep | 0 | Mar | 2023 | 0.0010319 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-03-26 08:56 | 2023-03-26 11:44 | 44 | 2:48 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | C23032600006 | New_Event | Animals | Include | Include | Wildlife | 168 | 2023-03-26 | 7392 | keep | 0 | Mar | 2023 | 0.0050347 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
FAJARDO | 2023-03-26 08:59 | 2023-03-26 11:41 | 20 | 2:42 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23032600010 | New_Event | Animals | Include | Include | Wildlife | 162 | 2023-03-26 | 3240 | keep | 0 | Mar | 2023 | 0.0022067 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-03-26 09:00 | 2023-03-26 09:45 | 50 | 0:45 | P | CONDUCTOR ROTO O ABIERTO | SE RETIRA CARGA A 5 TRANSFORMADORES PARA LEVANTAR HILO NEUTRAL | P23032600045 | New_Event | Primary Wire Break | Include | Include | Equipment | 45 | 2023-03-26 | 2250 | keep | 0 | Mar | 2023 | 0.0015325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-03-26 09:01 | 2023-03-26 11:10 | 75 | 2:09 | P | CAUSAS EXTERNAS | 2 X 50 EN CORTE DE LINEA VEHICULO IMPACTO POSTE Y CRUZARON LAS LINEAS | A23032600022 | New_Event | Damage From Public | Include | Include | Public | 129 | 2023-03-26 | 9675 | keep | 0 | Mar | 2023 | 0.0065896 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-03-26 09:06 | 2023-03-26 12:34 | 10 | 3:28 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | S23032600066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2023-03-26 | 2080 | keep | 0 | Mar | 2023 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-03-26 09:28 | 2023-03-26 12:00 | 25 | 2:32 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | A23032600027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2023-03-26 | 3800 | keep | 0 | Mar | 2023 | 0.0025882 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-03-26 09:40 | 2023-03-27 14:20 | 8 | 28:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | A23032600028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1720 | 2023-03-26 | 13760 | keep | 0 | Mar | 2023 | 0.0093719 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-03-26 09:50 | 2023-03-26 11:23 | 1 | 1:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 ENLAZADA CON LINEA 3400 | S23032600090 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 93 | 2023-03-26 | 93 | keep | 0 | Mar | 2023 | 6.3342e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-26 09:50 | 2023-03-26 11:23 | 737 | 1:33 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 ENLAZADA CON LINEA 3400 | S23032600090 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 93 | 2023-03-26 | 68541 | keep | 0 | Mar | 2023 | 0.046683 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-26 09:50 | 2023-03-26 11:23 | 2422 | 1:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 ENLAZADA CON LINEA 3400 | S23032600090 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 93 | 2023-03-26 | 225246 | keep | 0 | Mar | 2023 | 0.15341 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:30 | 1935 | 6:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 PARA ENERGIZAR LA 8900 LINEA 8900 ENLAZADA CON LINEA 3400 | B23032600240 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 400 | 2023-03-26 | 774000 | keep | 0 | Mar | 2023 | 0.52717 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:30 | 3 | 6:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 PARA ENERGIZAR LA 8900 | B23032600240 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 400 | 2023-03-26 | 1200 | keep | 0 | Mar | 2023 | 0.00081731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:30 | 61 | 6:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 PARA ENERGIZAR LA 8900 LINEA 8900 ENLAZADA CON LINEA 3400 | B23032600240 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 400 | 2023-03-26 | 24400 | keep | 0 | Mar | 2023 | 0.016619 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:30 | 1501 | 6:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 PARA ENERGIZAR LA 8900 LNEA 8900 ENLAZADA CON LINEA 3400 | B23032600240 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 400 | 2023-03-26 | 600400 | keep | 0 | Mar | 2023 | 0.40893 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:30 | 546 | 6:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 PARA ENERGIZAR LA 8900 LINEA 8900 ENLAZADA CON LINEA 3400 | B23032600240 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 400 | 2023-03-26 | 218400 | keep | 0 | Mar | 2023 | 0.14875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:32 | 959 | 6:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 Y ENERGIZO SUBESTACION A TRAVEZ DE ESTA LINEA 8900 ENLAZADA CON LINEA 3400 | S23032600137 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 402 | 2023-03-26 | 385518 | keep | 0 | Mar | 2023 | 0.26257 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:32 | 1297 | 6:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 Y ENERGIZO SUBESTACION A TRAVEZ DE ESTA LINEA 8900 ENLAZADA CON LINEA 3400 | S23032600137 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 402 | 2023-03-26 | 521394 | keep | 0 | Mar | 2023 | 0.35512 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:32 | 451 | 6:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 Y ENERGIZO SUBESTACION A TRAVEZ DE ESTA LINEA 8900 ENLAZADA CON LINEA 3400 | S23032600137 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 402 | 2023-03-26 | 181302 | keep | 0 | Mar | 2023 | 0.12348 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:32 | 1264 | 6:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 Y ENERGIZO SUBESTACION A TRAVEZ DE ESTA LINEA 8900 ENLAZADA CON LINEA 3400 | S23032600137 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 402 | 2023-03-26 | 508128 | keep | 0 | Mar | 2023 | 0.34608 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:50 | 2023-03-26 16:32 | 620 | 6:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 8900 SE REPARO PUENTE PRIMARIO EN LINEA 9800 Y ENERGIZO SUBESTACION A TRAVEZ DE ESTA LINEA 8900 ENLAZADA CON LINEA 3400 | S23032600137 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 402 | 2023-03-26 | 249240 | keep | 0 | Mar | 2023 | 0.16976 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 09:52 | 2023-03-27 10:32 | 1 | 24:40 | P | CONDUCTOR ROTO O ABIERTO | 1X20 EN BANCO DE XMRS SE REPARO BAJANTE PRIMARIO | B23032600179 | New_Event | Primary Wire Break | Include | Include | Equipment | 1480 | 2023-03-26 | 1480 | keep | 0 | Mar | 2023 | 0.001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-26 10:18 | 2023-03-26 10:19 | 997 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL INTERRUPTOR 7201-05 EL CUAL LLEVA LA CARGA DEL 7201-04 | M23032600036 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-26 | 997 | keep | 0 | Mar | 2023 | 0.00067905 | 0.00067905 | Momentary | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2023-03-26 10:18 | 2023-03-26 10:19 | 1497 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 7201-04 | M23032600036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 1497 | keep | 0 | Mar | 2023 | 0.0010196 | 0.0010196 | Momentary | FALSE | FALSE | Not_TMED_Event | 1497
BAYAMON | 2023-03-26 10:47 | 2023-03-26 16:14 | 50 | 5:27 | P | DESGANCHE | SE RETIRO RAMA Y 1 X 65 EN C/L | B23032600246 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2023-03-26 | 16350 | keep | 0 | Mar | 2023 | 0.011136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-26 11:00 | 2023-03-26 11:28 | 5809 | 0:28 | S | PROTECCION DEFECTUOSA | SE DEJO EN SERVICIO JUAN TORRES INSPECCIONO E INDICO QUE HAY PROBLEMAS CON EL DC DE LA SUBESTACION | B23032600291 | New_Event | Protection Miscoordination | Include | Include | Other | 28 | 2023-03-26 | 162652 | keep | 0 | Mar | 2023 | 0.11078 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2023-03-26 11:00 | 2023-03-26 11:28 | 3941 | 0:28 | S | PROTECCION DEFECTUOSA | SE DEJO EN SERVICIO JUAN TORRES INSPECCIONO E INDICO QUE HAY PROBLEMAS CON EL DC DE LA SUBESTACION | B23032600291 | New_Event | Protection Miscoordination | Include | Include | Other | 28 | 2023-03-26 | 110348 | keep | 0 | Mar | 2023 | 0.075158 | 0.0026842 | Sustained | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2023-03-26 11:00 | 2023-03-26 11:28 | 3871 | 0:28 | S | PROTECCION DEFECTUOSA | SE DEJO EN SERVICIO JUAN TORRES INSPECCIONO E INDICO QUE HAY PROBLEMAS CON EL DC DE LA SUBESTACION | B23032600291 | New_Event | Protection Miscoordination | Include | Include | Other | 28 | 2023-03-26 | 108388 | keep | 0 | Mar | 2023 | 0.073823 | 0.0026365 | Sustained | FALSE | FALSE | Not_TMED_Event | 3871
BAYAMON | 2023-03-26 11:00 | 2023-03-26 11:28 | 5191 | 0:28 | S | PROTECCION DEFECTUOSA | SE DEJO EN SERVICIO JUAN TORRES INSPECCIONO E INDICO QUE HAY PROBLEMAS CON EL DC DE LA SUBESTACION | B23032600291 | New_Event | Protection Miscoordination | Include | Include | Other | 28 | 2023-03-26 | 145348 | keep | 0 | Mar | 2023 | 0.098996 | 0.0035356 | Sustained | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2023-03-26 11:00 | 2023-03-26 11:28 | 492 | 0:28 | T | ALIMENTADOR AMARRADO | CARGA POR 1710-05 DISPARO DE SUBESTACION POR PROBLEMA DE DC | B23032600291 | New_Event | Feeder Load Transferred | Include | Include | Other | 28 | 2023-03-26 | 13776 | keep | 0 | Mar | 2023 | 0.0093828 | 0.0003351 | Sustained | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2023-03-26 11:00 | 2023-03-26 11:28 | 4028 | 0:28 | T | ALIMENTADOR AMARRADO | CARGA POR 1710-05 DISPARO DE SUBESTACION POR PROBLEMA DE DC | B23032600291 | New_Event | Feeder Load Transferred | Include | Include | Other | 28 | 2023-03-26 | 112784 | keep | 0 | Mar | 2023 | 0.076817 | 0.0027435 | Sustained | FALSE | FALSE | Not_TMED_Event | 4028
HUMACAO | 2023-03-26 11:11 | 2023-03-26 11:30 | 20 | 0:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23032600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 19 | 2023-03-26 | 380 | keep | 0 | Mar | 2023 | 0.00025882 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-26 11:13 | 2023-03-26 13:15 | 70 | 2:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | M23032600043 | New_Event | Primary Wire Break | Include | Include | Equipment | 122 | 2023-03-26 | 8540 | keep | 0 | Mar | 2023 | 0.0058166 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-03-26 11:13 | 2023-03-26 13:28 | 67 | 2:15 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23032600292 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-03-26 | 9045 | keep | 0 | Mar | 2023 | 0.0061605 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
AGUADILLA | 2023-03-26 11:28 | 2023-03-26 12:30 | 17 | 1:02 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CAJAS DE TRANSFORMADOR PARA RETIRAR CARGA Y REPARAR NEUTRAL PRIMARIO ROTO | M23032600044 | New_Event | Primary Wire Break | Include | Include | Equipment | 62 | 2023-03-26 | 1054 | keep | 0 | Mar | 2023 | 0.00071787 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 425 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 850 | keep | 0 | Mar | 2023 | 0.00057893 | 0.00028947 | Momentary | FALSE | FALSE | Not_TMED_Event | 425
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 1494 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 2988 | keep | 0 | Mar | 2023 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 3654 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 7308 | keep | 0 | Mar | 2023 | 0.0049774 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 2888 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 5776 | keep | 0 | Mar | 2023 | 0.003934 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 2107 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 4214 | keep | 0 | Mar | 2023 | 0.0028701 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 308 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 616 | keep | 0 | Mar | 2023 | 0.00041955 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 2697 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 5394 | keep | 0 | Mar | 2023 | 0.0036738 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 67 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 134 | keep | 0 | Mar | 2023 | 9.1267e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 1879 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600058 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 3758 | keep | 0 | Mar | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 2777 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600058 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 5554 | keep | 0 | Mar | 2023 | 0.0037828 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 2 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600058 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 4 | keep | 0 | Mar | 2023 | 2.7244e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 2839 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 5678 | keep | 0 | Mar | 2023 | 0.0038673 | 0.0019336 | Momentary | FALSE | FALSE | Not_TMED_Event | 2839
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 1160 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 2320 | keep | 0 | Mar | 2023 | 0.0015801 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 1860 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 BKR 2294 MANATÃ (PROBLEMAS CON PROTECCIÃ“N) NO ABRIÃ“ EN AVERÃA DE LINEA HACIA VEGA BAJA Y DISPARA EL BANCO 115/38/13 MANATÃ Y EL EXTREMO DE BARCELONETA EN RESGUARDO. | A23032600059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 3720 | keep | 0 | Mar | 2023 | 0.0025337 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 3000 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B23032600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 6000 | keep | 0 | Mar | 2023 | 0.0040866 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 908 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B23032600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 1816 | keep | 0 | Mar | 2023 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
VEGA BAJA | 2023-03-26 11:36 | 2023-03-26 11:38 | 3332 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B23032600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-26 | 6664 | keep | 0 | Mar | 2023 | 0.0045388 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
CANOVANAS | 2023-03-26 11:41 | 2023-03-26 12:13 | 15 | 0:32 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | R23032600009 | New_Event | Primary Wire Break | Include | Include | Equipment | 32 | 2023-03-26 | 480 | keep | 0 | Mar | 2023 | 0.00032693 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-03-26 11:51 | 2023-03-26 11:54 | 1825 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23032600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-26 | 5475 | keep | 0 | Mar | 2023 | 0.003729 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-03-26 11:51 | 2023-03-26 11:54 | 47 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23032600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-26 | 141 | keep | 0 | Mar | 2023 | 9.6034e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-03-26 11:51 | 2023-03-26 11:54 | 315 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23032600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-26 | 945 | keep | 0 | Mar | 2023 | 0.00064364 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2023-03-26 11:51 | 2023-03-26 11:54 | 2 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23032600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-26 | 6 | keep | 0 | Mar | 2023 | 4.0866e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-03-26 11:51 | 2023-03-26 11:54 | 2391 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23032600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-26 | 7173 | keep | 0 | Mar | 2023 | 0.0048855 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2023-03-26 11:51 | 2023-03-26 11:54 | 2276 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE MONACILLOS A CAGUAS | C23032600010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-26 | 6828 | keep | 0 | Mar | 2023 | 0.0046505 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2023-03-26 11:51 | 2023-03-26 11:54 | 777 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE MONACILLOS A CAGUAS | C23032600010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-26 | 2331 | keep | 0 | Mar | 2023 | 0.0015876 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2023-03-26 11:51 | 2023-03-26 11:54 | 12 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE MONACILLOS A CAGUAS | C23032600010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-26 | 36 | keep | 0 | Mar | 2023 | 2.4519e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-03-26 11:51 | 2023-03-26 11:54 | 1290 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE MONACILLOS A CAGUAS | C23032600010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-26 | 3870 | keep | 0 | Mar | 2023 | 0.0026358 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
UTUADO | 2023-03-26 12:10 | 2023-03-26 12:28 | 10 | 0:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23032600062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 18 | 2023-03-26 | 180 | keep | 0 | Mar | 2023 | 0.0001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-26 12:23 | 2023-03-26 12:24 | 2858 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2303260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 2858 | keep | 0 | Mar | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BARRANQUITAS | 2023-03-26 12:25 | 2023-03-26 15:47 | 21 | 3:22 | P | DESGANCHE | DESGANCHE Y 1 X 50 EN C/L | C23032600012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-03-26 | 4242 | keep | 0 | Mar | 2023 | 0.0028892 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2023-03-26 12:40 | 2023-03-26 12:57 | 5809 | 0:17 | S | PROTECCION DEFECTUOSA | SE DEJO EN SERVICIO JUAN TORRES INSPECCIONO E INDICO QUE HAY PROBLEMAS CON EL DC DE LA SUBESTACION | B23032600291 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 17 | 2023-03-26 | 98753 | keep | 0 | Mar | 2023 | 0.06726 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 12:40 | 2023-03-26 12:57 | 3941 | 0:17 | S | PROTECCION DEFECTUOSA | SE DEJO EN SERVICIO JUAN TORRES INSPECCIONO E INDICO QUE HAY PROBLEMAS CON EL DC DE LA SUBESTACION | B23032600291 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 17 | 2023-03-26 | 66997 | keep | 0 | Mar | 2023 | 0.045631 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 12:40 | 2023-03-26 12:57 | 3871 | 0:17 | S | PROTECCION DEFECTUOSA | SE DEJO EN SERVICIO JUAN TORRES INSPECCIONO E INDICO QUE HAY PROBLEMAS CON EL DC DE LA SUBESTACION | B23032600291 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 17 | 2023-03-26 | 65807 | keep | 0 | Mar | 2023 | 0.044821 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 12:40 | 2023-03-26 12:57 | 5191 | 0:17 | S | PROTECCION DEFECTUOSA | SE DEJO EN SERVICIO JUAN TORRES INSPECCIONO E INDICO QUE HAY PROBLEMAS CON EL DC DE LA SUBESTACION | B23032600291 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 17 | 2023-03-26 | 88247 | keep | 0 | Mar | 2023 | 0.060105 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 12:40 | 2023-03-26 12:57 | 492 | 0:17 | T | ALIMENTADOR AMARRADO | CARGA POR 1710-05 DISPARO DE SUBESTACION POR PROBLEMA DE DC | B23032600291 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 17 | 2023-03-26 | 8364 | keep | 0 | Mar | 2023 | 0.0056967 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 12:40 | 2023-03-26 12:57 | 4028 | 0:17 | T | ALIMENTADOR AMARRADO | CARGA POR 1710-05 DISPARO DE SUBESTACION POR PROBLEMA DE DC | B23032600291 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 17 | 2023-03-26 | 68476 | keep | 0 | Mar | 2023 | 0.046639 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-03-26 12:47 | 2023-03-26 13:00 | 1364 | 0:13 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA CAMION IMPACTO POSTE PRIMARIO | C23032600013 | New_Event | Damage From Public | Include | Include | Public | 13 | 2023-03-26 | 17732 | keep | 0 | Mar | 2023 | 0.012077 | 0.00092901 | Sustained | FALSE | FALSE | Not_TMED_Event | 1364
BAYAMON | 2023-03-26 12:55 | 2023-03-27 15:19 | 150 | 26:24 | P | DESGANCHE | 1X65 EN C/L 1X25 EN C/L DESGANCHE | B23032600377 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1584 | 2023-03-26 | 237600 | keep | 0 | Mar | 2023 | 0.16183 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-03-26 12:56 | 2023-03-26 13:02 | 1 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 Y 0050 PORTATIL #19 ESTABA POR EL BKR 0050, ESTE DISPARA DURANTE PRUEBAS AL BKR 3410 | S23032600218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-03-26 | 6 | keep | 0 | Mar | 2023 | 4.0866e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-26 12:56 | 2023-03-26 13:02 | 737 | 0:06 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 Y 0050 LLEVA 40% DE SU CARGA PORTATIL #19 ESTABA POR EL BKR 0050, ESTE DISPARA DURANTE PRUEBAS AL BKR 3410 | S23032600218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-03-26 | 4422 | keep | 0 | Mar | 2023 | 0.0030118 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2023-03-26 12:56 | 2023-03-26 13:02 | 2422 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 Y 0050 PORTATIL #19 ESTABA POR EL BKR 0050, ESTE DISPARA DURANTE PRUEBAS AL BKR 3410 | S23032600218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-03-26 | 14532 | keep | 0 | Mar | 2023 | 0.0098977 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
BAYAMON | 2023-03-26 13:04 | 2023-03-26 15:20 | 130 | 2:16 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEA SE REALIZO DESGANCHE | B23032600405 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-03-26 | 17680 | keep | 0 | Mar | 2023 | 0.012042 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
YAUCO | 2023-03-26 13:09 | 2023-03-26 13:12 | 3973 | 0:03 | T | NO SE REPORTO CAUSA | SE DISPARO ALIMENTADOR SE CERRO POR SCADA | P23032600091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-26 | 11919 | keep | 0 | Mar | 2023 | 0.008118 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
PONCE | 2023-03-26 13:15 | 2023-03-26 15:16 | 10 | 2:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO LINEA SECUNDARIA Y SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P23032600078 | New_Event | Cutout Failure | Include | Include | Equipment | 121 | 2023-03-26 | 1210 | keep | 0 | Mar | 2023 | 0.00082413 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-03-26 13:29 | 2023-03-26 15:28 | 39 | 1:59 | P | DESGANCHE | 3 X 50 EN C/L Y DESGANCHE | C23032600018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-03-26 | 4641 | keep | 0 | Mar | 2023 | 0.003161 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
GUAYAMA | 2023-03-26 13:30 | 2023-03-26 14:42 | 19 | 1:12 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | P23032600102 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 72 | 2023-03-26 | 1368 | keep | 0 | Mar | 2023 | 0.00093174 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
ARECIBO | 2023-03-26 13:36 | 2023-03-26 16:10 | 10 | 2:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23032600072 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 154 | 2023-03-26 | 1540 | keep | 0 | Mar | 2023 | 0.0010489 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-26 13:48 | 2023-03-26 17:43 | 302 | 3:55 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S23032600248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2023-03-26 | 70970 | keep | 0 | Mar | 2023 | 0.048337 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
YAUCO | 2023-03-26 13:52 | 2023-03-26 16:10 | 65 | 2:18 | P | FUEGO | 1 X 80 EN CORTE DE LINEA FUEGO EN PASTO | P23032600106 | New_Event | Fire | Include | Include | Public | 138 | 2023-03-26 | 8970 | keep | 0 | Mar | 2023 | 0.0061094 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2023-03-26 13:54 | 2023-03-26 13:55 | 11 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23032600058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 11 | keep | 0 | Mar | 2023 | 7.492e-06 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2023-03-26 13:54 | 2023-03-26 13:56 | 527 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO SE CERRO POR SCADA NO SE REPORTO CAUSA | M23032600057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-26 | 1054 | keep | 0 | Mar | 2023 | 0.00071787 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
ARECIBO | 2023-03-26 14:02 | 2023-03-27 18:23 | 6 | 28:21 | P | TRANSFORMADOR AVERIADO | CAMBIO DE TRANSFORMADOR AVERIADO DE 25KVA X 25KVA | A23032600074 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1701 | 2023-03-26 | 10206 | keep | 0 | Mar | 2023 | 0.0069513 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-03-26 14:18 | 2023-03-26 15:54 | 50 | 1:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P23032600144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-03-26 | 4800 | keep | 0 | Mar | 2023 | 0.0032693 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-26 14:25 | 2023-03-26 15:15 | 10 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REPARAR BARRA PEDESTAL | S23032500155 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-03-26 | 500 | keep | 0 | Mar | 2023 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-03-26 14:30 | 2023-03-26 14:40 | 12 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23032600076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-03-26 | 120 | keep | 0 | Mar | 2023 | 8.1731e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-03-26 14:36 | 2023-03-26 16:53 | 10 | 2:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P23032600117 | New_Event | Primary Wire Break | Include | Include | Equipment | 137 | 2023-03-26 | 1370 | keep | 0 | Mar | 2023 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-26 14:56 | 2023-03-27 11:52 | 140 | 20:56 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23032600451 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1256 | 2023-03-26 | 175840 | keep | 0 | Mar | 2023 | 0.11976 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
YAUCO | 2023-03-26 14:56 | 2023-03-26 17:41 | 15 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032600065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-03-26 | 2475 | keep | 0 | Mar | 2023 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-03-26 14:57 | 2023-03-26 19:04 | 30 | 4:07 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23032600024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2023-03-26 | 7410 | keep | 0 | Mar | 2023 | 0.0050469 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-03-26 14:59 | 2023-03-27 10:30 | 10 | 19:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO DOS CAJAS PRIMARIAS EN TRANSFORMADOR | A23032600078 | New_Event | Cutout Failure | Include | Include | Equipment | 1171 | 2023-03-26 | 11710 | keep | 0 | Mar | 2023 | 0.0079756 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-26 15:05 | 2023-03-26 18:10 | 40 | 3:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23032600079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-03-26 | 7400 | keep | 0 | Mar | 2023 | 0.0050401 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-03-26 15:08 | 2023-03-26 15:50 | 18 | 0:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | P23032600130 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 42 | 2023-03-26 | 756 | keep | 0 | Mar | 2023 | 0.00051491 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2023-03-26 15:12 | 2023-03-27 09:20 | 20 | 18:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032600066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1088 | 2023-03-26 | 21760 | keep | 0 | Mar | 2023 | 0.014821 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-03-26 15:20 | 2023-03-26 16:25 | 100 | 1:05 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO CORTE DE LINEA PARA DESENREDAR LINEAS | P23032600071 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 65 | 2023-03-26 | 6500 | keep | 0 | Mar | 2023 | 0.0044271 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-03-26 15:24 | 2023-03-26 16:05 | 19 | 0:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23032600027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2023-03-26 | 779 | keep | 0 | Mar | 2023 | 0.00053057 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
PONCE | 2023-03-26 15:36 | 2023-03-26 15:37 | 2039 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | P23032600133 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-26 | 2039 | keep | 0 | Mar | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2023-03-26 15:37 | 2023-03-26 17:04 | 281 | 1:27 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA PARTIDA | P23032600137 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 87 | 2023-03-26 | 24447 | keep | 0 | Mar | 2023 | 0.016651 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
SAN JUAN | 2023-03-26 15:56 | 2023-03-26 15:58 | 207 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S2303260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-26 | 414 | keep | 0 | Mar | 2023 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
AGUADILLA | 2023-03-26 15:57 | 2023-03-26 18:20 | 15 | 2:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23032600082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-03-26 | 2145 | keep | 0 | Mar | 2023 | 0.0014609 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-26 16:02 | 2023-03-26 16:07 | 5191 | 0:05 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR LLEVANDO 1719-18 Y 1719-16 SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | B23032600472 | New_Event | Primary Wire Break | Include | Include | Equipment | 5 | 2023-03-26 | 25955 | keep | 0 | Mar | 2023 | 0.017678 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2023-03-26 16:02 | 2023-03-26 16:07 | 492 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1710-05 LLEVANDO 1719-18 Y 1719-16 SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | B23032600472 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 5 | 2023-03-26 | 2460 | keep | 0 | Mar | 2023 | 0.0016755 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 16:02 | 2023-03-26 16:07 | 4028 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1710-05 LLEVANDO 1719-18 Y 1719-16 SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | B23032600472 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 5 | 2023-03-26 | 20140 | keep | 0 | Mar | 2023 | 0.013717 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 16:07 | 2023-03-26 22:12 | 261 | 6:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN MACHETES BY-230326-02 | B23032600485 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 365 | 2023-03-26 | 95265 | keep | 0 | Mar | 2023 | 0.064885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-03-26 16:10 | 2023-03-26 19:47 | 40 | 3:37 | P | FUEGO | SE RETEZO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | P23032600140 | Partial_restoration | Fire | Include | Include | Public | 217 | 2023-03-26 | 8680 | keep | 0 | Mar | 2023 | 0.0059119 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-26 16:13 | 2023-03-26 20:19 | 20 | 4:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A23032600085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2023-03-26 | 4920 | keep | 0 | Mar | 2023 | 0.003351 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-26 16:30 | 2023-03-26 17:05 | 4 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23032600062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-03-26 | 140 | keep | 0 | Mar | 2023 | 9.5353e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-03-26 16:40 | 2023-03-26 19:13 | 67 | 2:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23032600496 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2023-03-26 | 10251 | keep | 0 | Mar | 2023 | 0.0069819 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-03-26 16:46 | 2023-03-26 18:28 | 2 | 1:42 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE | S23032600302 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-03-26 | 204 | keep | 0 | Mar | 2023 | 0.00013894 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-03-26 16:57 | 2023-03-26 19:41 | 70 | 2:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23032600304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-03-26 | 11480 | keep | 0 | Mar | 2023 | 0.007819 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-03-26 17:57 | 2023-03-26 17:58 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA DEL 7404-06 SE ENCUENTRA POR EL 7404-07 QUE ES SPARE | A23032600097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 2379 | keep | 0 | Mar | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2023-03-26 18:17 | 2023-03-26 18:18 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO CARGA 1719-19 | B23032600601 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 2605 | keep | 0 | Mar | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-03-26 18:17 | 2023-03-26 18:18 | 2605 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO CARGA 1719-19 | B23032600601 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-26 | 2605 | keep | 0 | Mar | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
VEGA BAJA | 2023-03-26 18:20 | 2023-03-26 21:06 | 125 | 2:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR 3 X 65 EN C/L | B23032600603 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 166 | 2023-03-26 | 20750 | keep | 0 | Mar | 2023 | 0.014133 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-03-26 18:31 | 2023-03-26 21:03 | 5 | 2:32 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA REPARAR BAJANTE PRIMARIO LINEA A CAJA | S23032600317 | New_Event | Primary Wire Break | Include | Include | Equipment | 152 | 2023-03-26 | 760 | keep | 0 | Mar | 2023 | 0.00051763 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-03-26 19:06 | 2023-03-26 21:25 | 436 | 2:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L Y 2 X 80 EN C/L | C23032600057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2023-03-26 | 60604 | keep | 0 | Mar | 2023 | 0.041277 | 0.00029696 | Sustained | FALSE | FALSE | Not_TMED_Event | 436
AGUADILLA | 2023-03-26 19:12 | 2023-03-26 19:13 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23032600090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 3041 | keep | 0 | Mar | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
ARECIBO | 2023-03-26 19:31 | 2023-03-26 21:12 | 12 | 1:41 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A23032600103 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 101 | 2023-03-26 | 1212 | keep | 0 | Mar | 2023 | 0.00082549 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-26 19:34 | 2023-03-27 01:28 | 64 | 5:54 | P | CONDUCTOR ROTO O ABIERTO | 1X40 EN C/L 1X15 EN XMR SE REPARO PUENTE ABIERTO DE LINEA @ CAJA | S23032600320 | New_Event | Primary Wire Break | Include | Include | Equipment | 354 | 2023-03-26 | 22656 | keep | 0 | Mar | 2023 | 0.015431 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2023-03-26 19:40 | 2023-03-26 20:24 | 20 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S23032600310 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-03-26 | 880 | keep | 0 | Mar | 2023 | 0.00059936 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-03-26 19:41 | 2023-03-26 20:41 | 800 | 1:00 | P | MAL TIEMPO/LLUVIA O VIENTO | LINEA PRIMARIA PARTIDA EN TRONCAL DEL ALIMENTADOR A CAUSA DE FUERTE VIENTO | A23032600110 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 60 | 2023-03-26 | 48000 | keep | 0 | Mar | 2023 | 0.032693 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
CANOVANAS | 2023-03-26 20:11 | 2023-03-26 20:12 | 2106 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | R23032600023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 2106 | keep | 0 | Mar | 2023 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
VEGA BAJA | 2023-03-26 20:39 | 2023-03-27 01:28 | 8 | 4:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X25 EN C/L SE REMPLAZO PORTAFUSIBLE | B23032600893 | New_Event | Cutout Failure | Include | Include | Equipment | 289 | 2023-03-26 | 2312 | keep | 0 | Mar | 2023 | 0.0015747 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-03-26 20:41 | 2023-03-26 22:39 | 2379 | 1:58 | T | MAL TIEMPO/LLUVIA O VIENTO | SE ABRIO INTERRUPTOR PARA PODER REPARAR LINEA PRIMARIA PARTIDA EN TRONCAL DEL ALIMENTADOR | A23032600110 | Additional_clients | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2023-03-26 | 280722 | keep | 0 | Mar | 2023 | 0.1912 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-26 20:45 | 2023-03-27 08:53 | 10 | 12:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X10 EN XMR SE REMPLAZO PORTAFUSIBLE QUEMADO | B23032600905 | New_Event | Cutout Failure | Include | Include | Equipment | 728 | 2023-03-26 | 7280 | keep | 0 | Mar | 2023 | 0.0049584 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-26 20:47 | 2023-03-26 20:48 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO CARGA 1719-19 | B23032600911 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 2605 | keep | 0 | Mar | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-03-26 20:47 | 2023-03-26 20:48 | 2617 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO CARGA 1719-19 | B23032600911 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-26 | 2617 | keep | 0 | Mar | 2023 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2023-03-26 20:55 | 2023-03-26 20:56 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO CARGA 1719-19 | B23032600925 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 2605 | keep | 0 | Mar | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-03-26 20:55 | 2023-03-26 20:56 | 2617 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO CARGA 1719-19 | B23032600925 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 2617 | keep | 0 | Mar | 2023 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2023-03-26 21:47 | 2023-03-26 21:48 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO CARGA 1719-19 | B23032601015 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-26 | 2605 | keep | 0 | Mar | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-03-26 21:47 | 2023-03-26 21:48 | 2617 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO CARGA 1719-19 | B23032601015 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-26 | 2617 | keep | 0 | Mar | 2023 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2023-03-26 22:24 | 2023-03-27 13:05 | 33 | 14:41 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO NO FUNDIO | B23032600106 | New_Event | Primary Wire Break | Include | Include | Equipment | 881 | 2023-03-26 | 29073 | keep | 0 | Mar | 2023 | 0.019801 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
AGUADILLA | 2023-03-26 23:13 | 2023-03-27 09:05 | 200 | 9:52 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23032600106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 592 | 2023-03-26 | 118400 | keep | 0 | Mar | 2023 | 0.080642 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-03-27 00:16 | 2023-03-27 02:31 | 312 | 2:15 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISAPRO DE ALIMENTADOR SE INSTALO BYPASS A VACCUM SWITCH AVERIADO EN MH-03 Y SE ENERGIZO A CLIENTES | M23032700059 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 135 | 2023-03-27 | 42120 | keep | 0 | Mar | 2023 | 0.028688 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
CAGUAS | 2023-03-27 01:28 | 2023-03-27 01:38 | 1608 | 0:10 | P | ALIMENTADOR AMARRADO | RELEVO DE CARGA UNIDAD 2 AGUIRRE PARTE DE LA CARGA POR EL 3201-01 | C2303270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 10 | 2023-03-27 | 16080 | keep | 0 | Mar | 2023 | 0.010952 | 0.0010952 | Sustained | FALSE | FALSE | Not_TMED_Event | 1608
BAYAMON | 2023-03-27 01:34 | 2023-03-27 13:28 | 64 | 11:54 | P | CONDUCTOR ROTO O ABIERTO | 1X40 EN C/L 1X15 EN XMR SE REPARO PUENTE ABIERTO DE LINEA @ CAJA | S23032600320 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 714 | 2023-03-27 | 45696 | keep | 0 | Mar | 2023 | 0.031123 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-27 01:36 | 2023-03-27 07:19 | 8 | 5:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L SE REMPLAZO PORTAFUSIBLE | B23032600893 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 343 | 2023-03-27 | 2744 | keep | 0 | Mar | 2023 | 0.0018689 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-27 02:31 | 2023-03-27 15:07 | 100 | 12:36 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE INSTALO BYPASS A VACCUM SWITCH AVERIADO EN MH-03 Y SE ENERGIZO A CLIENTES | M23032700059 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 756 | 2023-03-27 | 75600 | keep | 0 | Mar | 2023 | 0.051491 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-03-27 03:08 | 2023-03-27 14:24 | 8 | 11:16 | P | ANIMAL | 1X18 EN T-218 CRUCE POR RATON | B23032700034 | New_Event | Animals | Include | Include | Wildlife | 676 | 2023-03-27 | 5408 | keep | 0 | Mar | 2023 | 0.0036834 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-27 03:23 | 2023-03-27 09:43 | 37 | 6:20 | P | TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO TERMINACION EN AEREO PROVISIONAL Y 1 X 40 EN AEREO | R23032700030 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 380 | 2023-03-27 | 14060 | keep | 0 | Mar | 2023 | 0.0095762 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CANOVANAS | 2023-03-27 05:04 | 2023-03-27 10:53 | 12 | 5:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO PORTAFUSIBLE Y 1 X 15 EN XMR | R23032700037 | New_Event | Cutout Failure | Include | Include | Equipment | 349 | 2023-03-27 | 4188 | keep | 0 | Mar | 2023 | 0.0028524 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-03-27 05:22 | 2023-03-27 19:18 | 8 | 13:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 30 EN C/L Y SE REPARO PUENTE DE CAJA HACIA TRANSFORMADOR | S23032700121 | New_Event | Secondary Wire Break | Include | Include | Equipment | 836 | 2023-03-27 | 6688 | keep | 0 | Mar | 2023 | 0.0045552 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-03-27 07:04 | 2023-03-27 09:16 | 10 | 2:12 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23032700075 | New_Event | Animals | Include | Include | Wildlife | 132 | 2023-03-27 | 1320 | keep | 0 | Mar | 2023 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-27 07:14 | 2023-03-27 09:50 | 1 | 2:36 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO CAUSA | M23032700073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2023-03-27 | 156 | keep | 0 | Mar | 2023 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-03-27 08:12 | 2023-03-27 12:50 | 100 | 4:38 | P | ARBOL SOBRE LINEA | 1 X 80 EN CORTE DE LINEA POR DESGANCHE DE ARBOL | P23032700048 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 278 | 2023-03-27 | 27800 | keep | 0 | Mar | 2023 | 0.018934 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-03-27 08:27 | 2023-03-27 22:00 | 12 | 13:33 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR AVERIADO DE 37.5KVA X 25KVA | A23032700016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 813 | 2023-03-27 | 9756 | keep | 0 | Mar | 2023 | 0.0066448 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-03-27 09:00 | 2023-03-27 10:11 | 10 | 1:11 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR POR AVE | A23032700021 | New_Event | Animals | Include | Include | Wildlife | 71 | 2023-03-27 | 710 | keep | 0 | Mar | 2023 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-27 09:07 | 2023-03-27 15:30 | 28 | 6:23 | P | NO SE REPORTO CAUSA | 1X20 EN RISER | B23032700098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 383 | 2023-03-27 | 10724 | keep | 0 | Mar | 2023 | 0.0073041 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BARRANQUITAS | 2023-03-27 09:22 | 2023-03-27 13:20 | 91 | 3:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA NO FUNDIO | C23032700093 | New_Event | Cutout Failure | Include | Include | Equipment | 238 | 2023-03-27 | 21658 | keep | 0 | Mar | 2023 | 0.014751 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
GUAYAMA | 2023-03-27 09:30 | 2023-03-27 11:30 | 1 | 2:00 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23032700068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-03-27 | 120 | keep | 0 | Mar | 2023 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-27 09:34 | 2023-03-27 12:28 | 100 | 2:54 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23032700099 | New_Event | Animals | Include | Include | Wildlife | 174 | 2023-03-27 | 17400 | keep | 0 | Mar | 2023 | 0.011851 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-03-27 09:59 | 2023-03-27 12:10 | 25 | 2:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23032700104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2023-03-27 | 3275 | keep | 0 | Mar | 2023 | 0.0022306 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-03-27 10:00 | 2023-03-27 12:40 | 4 | 2:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR SE SUBIO NEUTRAL PRIMARIO, SE REEMPLAZO BAJANTE SECUNDARIO Y SE RELOCALIZO LINEA SECUNDARIA. | C23032700101 | New_Event | Primary Wire Break | Include | Include | Equipment | 160 | 2023-03-27 | 640 | keep | 0 | Mar | 2023 | 0.0004359 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-03-27 10:10 | 2023-03-27 10:39 | 11 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR CONECTORES EN BAJANTES SECUNDARIOS | C23032700108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-03-27 | 319 | keep | 0 | Mar | 2023 | 0.00021727 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-03-27 10:13 | 2023-03-27 17:04 | 70 | 6:51 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23032700145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2023-03-27 | 28770 | keep | 0 | Mar | 2023 | 0.019595 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-03-27 10:13 | 2023-03-27 11:13 | 3 | 1:00 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER Y 1 X 65 EN C/L | R23032700055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-03-27 | 180 | keep | 0 | Mar | 2023 | 0.0001226 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-03-27 10:14 | 2023-03-27 12:47 | 35 | 2:33 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23032700123 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-03-27 | 5355 | keep | 0 | Mar | 2023 | 0.0036473 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-03-27 10:19 | 2023-03-27 10:20 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2303270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-27 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
CANOVANAS | 2023-03-27 10:22 | 2023-03-27 10:23 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032700058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-27 | 7621 | keep | 0 | Mar | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2023-03-27 10:22 | 2023-03-27 10:23 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032700057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-27 | 3699 | keep | 0 | Mar | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CAGUAS | 2023-03-27 10:23 | 2023-03-27 10:24 | 918 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | C2303270000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-27 | 918 | keep | 0 | Mar | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
SAN JUAN | 2023-03-27 10:24 | 2023-03-27 13:00 | 9 | 2:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA Y TOMA | S23032700031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 156 | 2023-03-27 | 1404 | keep | 0 | Mar | 2023 | 0.00095626 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-03-27 10:24 | 2023-03-27 14:55 | 173 | 4:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REEMPLAZO CAJA PRIAMRIA | C23032700116 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 271 | 2023-03-27 | 46883 | keep | 0 | Mar | 2023 | 0.031932 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
MAYAGÃœEZ | 2023-03-27 10:25 | 2023-03-27 12:35 | 100 | 2:10 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA Y 2 X 10 EN TRANSFORMADOR SE REPARO LINEA ZAFADA DE AISLADOR | M23032700112 | New_Event | Primary Wire Break | Include | Include | Equipment | 130 | 2023-03-27 | 13000 | keep | 0 | Mar | 2023 | 0.0088542 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-03-27 10:30 | 2023-03-27 10:31 | 551 | 0:01 | T | ANIMAL | RECIERRE | C23032700117 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-27 | 551 | keep | 0 | Mar | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2023-03-27 10:31 | 2023-03-27 15:24 | 2 | 4:53 | P | ANIMAL | 2 X 100 EN C/L CRUCE X AVE | C23032700145 | 1st_after_momentary | Animals | Include | Include | Wildlife | 293 | 2023-03-27 | 586 | keep | 0 | Mar | 2023 | 0.00039912 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-27 10:44 | 2023-03-27 10:45 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23032700170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-27 | 325 | keep | 0 | Mar | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
GUAYAMA | 2023-03-27 10:51 | 2023-03-27 13:21 | 5 | 2:30 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE | P23032700090 | New_Event | Animals | Include | Include | Wildlife | 150 | 2023-03-27 | 750 | keep | 0 | Mar | 2023 | 0.00051082 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-03-27 10:54 | 2023-03-27 13:50 | 6 | 2:56 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA CRUZADA | M23032700126 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 176 | 2023-03-27 | 1056 | keep | 0 | Mar | 2023 | 0.00071924 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-03-27 10:55 | 2023-03-27 13:22 | 40 | 2:27 | P | DESGANCHE | 1 X 65 1 X 50 EN C/L DESGANCHE | S23032700036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-03-27 | 5880 | keep | 0 | Mar | 2023 | 0.0040048 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-03-27 11:08 | 2023-03-27 17:35 | 1 | 6:27 | P | OTRAS CAUSAS | 1 X 10 EN CORTE DE LINEA A.A.A. , PLANTA DE AGUAS USADAS, SALITRE | A23032700038 | New_Event | Other Causes | Include | Include | Other | 387 | 2023-03-27 | 387 | keep | 0 | Mar | 2023 | 0.00026358 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-27 11:50 | 2023-03-27 13:47 | 10 | 1:57 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | B23032700214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-03-27 | 1170 | keep | 0 | Mar | 2023 | 0.00079688 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-03-27 11:51 | 2023-03-27 16:34 | 8 | 4:43 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA PAJARO CRUZO FASE | P23032700109 | New_Event | Animals | Include | Include | Wildlife | 283 | 2023-03-27 | 2264 | keep | 0 | Mar | 2023 | 0.001542 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-03-27 11:52 | 2023-03-27 14:54 | 5 | 3:02 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE SECUNDARIO | P23032700110 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 182 | 2023-03-27 | 910 | keep | 0 | Mar | 2023 | 0.0006198 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-03-27 11:54 | 2023-03-27 15:11 | 5 | 3:17 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23032700140 | New_Event | Animals | Include | Include | Wildlife | 197 | 2023-03-27 | 985 | keep | 0 | Mar | 2023 | 0.00067088 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-03-27 12:01 | 2023-03-27 16:49 | 20 | 4:48 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23032700141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2023-03-27 | 5760 | keep | 0 | Mar | 2023 | 0.0039231 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-03-27 12:15 | 2023-03-27 13:44 | 30 | 1:29 | P | DESGANCHE | 1 X 40 EN CONVERTIDOR SE REALIZO DESGANCHE | A23032700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-03-27 | 2670 | keep | 0 | Mar | 2023 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-03-27 12:25 | 2023-03-27 14:28 | 7 | 2:03 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE XMR 37.5KVA X 37.5KVA POR DERRAME DE ACEITE | C23032700143 | New_Event | Service Transformer Failure | Include | Include | Equipment | 123 | 2023-03-27 | 861 | keep | 0 | Mar | 2023 | 0.00058642 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-03-27 12:35 | 2023-03-27 14:23 | 7 | 1:48 | P | ANIMAL | 1 X 8 EN XMR CRUCE POR AVE | C23032700146 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-03-27 | 756 | keep | 0 | Mar | 2023 | 0.00051491 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-27 12:51 | 2023-03-27 12:52 | 19 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | S2303270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-27 | 19 | keep | 0 | Mar | 2023 | 1.2941e-05 | 1.2941e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-03-27 13:10 | 2023-03-27 17:01 | 8 | 3:51 | P | PARARRAYOS DEFECTUOSO | 1X15 EN XMR SE REMPLAZO PARARRAYOS | B23032700298 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 231 | 2023-03-27 | 1848 | keep | 0 | Mar | 2023 | 0.0012587 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-03-27 13:28 | 2023-03-27 13:29 | 820 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1115-01 LLEVA 1119-04 Y 95% 1119-02 | S2303270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-27 | 820 | keep | 0 | Mar | 2023 | 0.0005585 | 0.0005585 | Momentary | FALSE | FALSE | Not_TMED_Event | 820
SAN JUAN | 2023-03-27 13:28 | 2023-03-27 13:29 | 2720 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1115-01 LLEVA 1119-04 Y 95% 1119-02 | S2303270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-27 | 2720 | keep | 0 | Mar | 2023 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
AGUADILLA | 2023-03-27 13:28 | 2023-03-28 14:17 | 1 | 24:49 | P | OTRAS CAUSAS | SE REMPLAZO CT'S AVERIADOS | A23032700062 | New_Event | Other Causes | Include | Include | Other | 1489 | 2023-03-27 | 1489 | keep | 0 | Mar | 2023 | 0.0010142 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-27 13:36 | 2023-03-27 18:16 | 8 | 4:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23032700066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 280 | 2023-03-27 | 2240 | keep | 0 | Mar | 2023 | 0.0015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-27 13:45 | 2023-03-27 13:46 | 3597 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9405-05 LLEVA LA CARGA DEL 1719-15 | B2303270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-27 | 3597 | keep | 0 | Mar | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-03-27 13:45 | 2023-03-27 13:46 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9405-05 LLEVA LA CARGA DEL 1719-15 | B2303270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-27 | 3511 | keep | 0 | Mar | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
SAN JUAN | 2023-03-27 13:48 | 2023-03-27 15:44 | 870 | 1:56 | T | DESGANCHE | SE REALIZO DESGANCHE CON VARETA DESDE EL PISO EN SERVICIO 100% SE TRABAJO MEDIANTE SWF-230327-01 | S23032700081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-03-27 | 100920 | keep | 0 | Mar | 2023 | 0.068736 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
GUAYAMA | 2023-03-27 14:03 | 2023-03-27 15:50 | 8 | 1:47 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASE | P23032700125 | New_Event | Animals | Include | Include | Wildlife | 107 | 2023-03-27 | 856 | keep | 0 | Mar | 2023 | 0.00058302 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-03-27 14:06 | 2023-03-27 16:30 | 1 | 2:24 | P | NO SE REPORTO CAUSA | 1X30 EN MONTURA DE XMRS | B23032700309 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2023-03-27 | 144 | keep | 0 | Mar | 2023 | 9.8078e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-27 14:28 | 2023-03-27 17:02 | 100 | 2:34 | P | ANIMAL | 1X65 EN PROVISIONAL AEREO CRUCE POR AVE | B23032700312 | New_Event | Animals | Include | Include | Wildlife | 154 | 2023-03-27 | 15400 | keep | 0 | Mar | 2023 | 0.010489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-03-27 14:35 | 2023-03-27 17:58 | 150 | 3:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | A23032700071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2023-03-27 | 30450 | keep | 0 | Mar | 2023 | 0.020739 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-03-27 14:43 | 2023-03-27 16:14 | 50 | 1:31 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | A23032700131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-03-27 | 4550 | keep | 0 | Mar | 2023 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-27 14:55 | 2023-03-27 21:36 | 9 | 6:41 | P | ANIMAL | 1 X 20 EN SU-A CRUCE X CULEBRA | R23032700082 | New_Event | Animals | Include | Include | Wildlife | 401 | 2023-03-27 | 3609 | keep | 0 | Mar | 2023 | 0.0024581 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-03-27 15:07 | 2023-03-27 15:08 | 312 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE DE INTERRUPTOR | M23032700185 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-03-27 | 312 | keep | 0 | Mar | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2023-03-27 15:08 | 2023-03-28 15:37 | 100 | 24:29 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE INSTALO BYPASS A VACCUM SWITCH AVERIADO EN MH-03 Y SE ENERGIZO A CLIENTES | M23032700059 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1469 | 2023-03-27 | 146900 | keep | 0 | Mar | 2023 | 0.10005 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-03-27 15:15 | 2023-03-27 15:17 | 4830 | 0:02 | P | ANIMAL | DISPARO DE INTERRUPTOR 2603-08 SE CERRO POR CONTROL. 800 CLIENTES X 3205-07 | C23032700169 | New_Event | Animals | Include | Include | Wildlife | 2 | 2023-03-27 | 9660 | keep | 0 | Mar | 2023 | 0.0065794 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
HUMACAO | 2023-03-27 15:17 | 2023-03-27 16:46 | 50 | 1:29 | P | ANIMAL | 1 X 100 EN RISER CRUCE X AVE | C23032700174 | 1st_after_momentary | Animals | Include | Include | Wildlife | 89 | 2023-03-27 | 4450 | keep | 0 | Mar | 2023 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-27 15:25 | 2023-03-27 19:14 | 1 | 3:49 | P | ANIMAL | 1X20 DE SU-J @ RISER CRUCE POR AVE | B23032700323 | New_Event | Animals | Include | Include | Wildlife | 229 | 2023-03-27 | 229 | keep | 0 | Mar | 2023 | 0.00015597 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-27 15:27 | 2023-03-27 23:00 | 159 | 7:33 | P | ANIMAL | 1 X 65 EN C/L SE RETIRO AVE | B23032700325 | New_Event | Animals | Include | Include | Wildlife | 453 | 2023-03-27 | 72027 | keep | 0 | Mar | 2023 | 0.049057 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
BAYAMON | 2023-03-27 15:27 | 2023-03-28 11:03 | 1 | 19:36 | P | TRANSFORMADOR AVERIADO | 1X15 EN XMR SE REMPLAZO XMR 50KVA X 25KVA | B23032700324 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1176 | 2023-03-27 | 1176 | keep | 0 | Mar | 2023 | 0.00080097 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-03-27 15:49 | 2023-03-27 18:34 | 8 | 2:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO CONEXIONES | A23032700079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 165 | 2023-03-27 | 1320 | keep | 0 | Mar | 2023 | 0.00089905 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-03-27 16:00 | 2023-03-27 16:35 | 10 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23032700080 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-03-27 | 350 | keep | 0 | Mar | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-27 16:17 | 2023-03-27 21:23 | 10 | 5:06 | P | DESGANCHE | 1X50 EN C/L DESGANCHE EN EL MONTE | B23032700338 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2023-03-27 | 3060 | keep | 0 | Mar | 2023 | 0.0020842 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-03-27 17:03 | 2023-03-27 21:54 | 6 | 4:51 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO POSTE SECUNDARIO PARTIDO | R23032700085 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 291 | 2023-03-27 | 1746 | keep | 0 | Mar | 2023 | 0.0011892 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-27 17:05 | 2023-03-27 23:00 | 35 | 5:55 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 80 EN C/L SE REMPLAZO POSTE PARTIDO | B23032700325 | New_Event | Primary Pole Failure | Include | Include | Equipment | 355 | 2023-03-27 | 12425 | keep | 0 | Mar | 2023 | 0.0084626 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-03-27 17:06 | 2023-03-27 20:06 | 6 | 3:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y SE REEMPLAZO PORTAFUSIBLE | R23032700086 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2023-03-27 | 1080 | keep | 0 | Mar | 2023 | 0.00073558 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-03-27 17:28 | 2023-03-27 19:05 | 18 | 1:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJAS DE TRANSFORMADOR | M23032700192 | New_Event | Primary Wire Break | Include | Include | Equipment | 97 | 2023-03-27 | 1746 | keep | 0 | Mar | 2023 | 0.0011892 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-03-27 17:38 | 2023-03-28 10:20 | 20 | 16:42 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23032700194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1002 | 2023-03-27 | 20040 | keep | 0 | Mar | 2023 | 0.013649 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-03-27 17:39 | 2023-03-27 18:36 | 4 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23032700188 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-03-27 | 228 | keep | 0 | Mar | 2023 | 0.00015529 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-03-27 17:41 | 2023-03-27 20:00 | 35 | 2:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M23032700196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-03-27 | 4865 | keep | 0 | Mar | 2023 | 0.0033135 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-03-27 18:20 | 2023-03-27 19:51 | 6 | 1:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA Y PUENTE SAFADO | C23032700194 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2023-03-27 | 546 | keep | 0 | Mar | 2023 | 0.00037188 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-03-27 18:22 | 2023-03-27 18:23 | 1173 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23032700151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-27 | 1173 | keep | 0 | Mar | 2023 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
AGUADILLA | 2023-03-27 18:31 | 2023-03-28 09:05 | 15 | 14:34 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE | M23032700203 | New_Event | Primary Wire Break | Include | Include | Equipment | 874 | 2023-03-27 | 13110 | keep | 0 | Mar | 2023 | 0.0089292 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-03-27 19:00 | 2023-03-28 07:39 | 14 | 12:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REPARO CONECTORES SECUNDARIOS | C23032700200 | New_Event | Secondary Wire Break | Include | Include | Equipment | 759 | 2023-03-27 | 10626 | keep | 0 | Mar | 2023 | 0.0072373 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2023-03-27 19:16 | 2023-03-27 20:00 | 71 | 0:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER , PORTAFUSIBLE QUEMADO | P23032700152 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2023-03-27 | 3124 | keep | 0 | Mar | 2023 | 0.0021277 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
AGUADILLA | 2023-03-27 19:35 | 2023-03-27 21:25 | 200 | 1:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | M23032700209 | New_Event | Primary Pole Failure | Include | Include | Equipment | 110 | 2023-03-27 | 22000 | keep | 0 | Mar | 2023 | 0.014984 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-03-27 20:50 | 2023-03-28 07:11 | 12 | 10:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN XMR SE REMPLAZO PORTAFUSIBLE | B23032700376 | New_Event | Cutout Failure | Include | Include | Equipment | 621 | 2023-03-27 | 7452 | keep | 0 | Mar | 2023 | 0.0050755 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-03-27 21:25 | 2023-03-28 14:10 | 100 | 16:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO Y SE CERRO PUENTES | M23032700224 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1005 | 2023-03-27 | 100500 | keep | 0 | Mar | 2023 | 0.06845 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-27 21:53 | 2023-03-28 10:50 | 150 | 12:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M23032700225 | New_Event | Cutout Failure | Include | Include | Equipment | 777 | 2023-03-27 | 116550 | keep | 0 | Mar | 2023 | 0.079382 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2023-03-27 22:35 | 2023-03-28 09:31 | 40 | 10:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 65 EN C/L | R23032700098 | New_Event | Cutout Failure | Include | Include | Equipment | 656 | 2023-03-27 | 26240 | keep | 0 | Mar | 2023 | 0.017872 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-03-28 00:59 | 2023-03-28 16:36 | 10 | 15:37 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANFORMADOR TAPA EN TRANSFORMADOR AVERIADA | A23032800001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 937 | 2023-03-28 | 9370 | keep | 0 | Mar | 2023 | 0.0063819 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-28 01:49 | 2023-03-28 03:13 | 2858 | 1:24 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO BKR POR CONTROL 25% EN SERVICIO | B23032800001 | New_Event | Primary Wire Break | Include | Include | Equipment | 84 | 2023-03-28 | 240072 | keep | 0 | Mar | 2023 | 0.16351 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-03-28 03:13 | 2023-03-28 03:48 | 2143 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZARON OPERAIONES Y ENTRO UN 15% ADICIONAL | B23032800001 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 35 | 2023-03-28 | 75005 | keep | 0 | Mar | 2023 | 0.051086 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-28 03:19 | 2023-03-28 03:20 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23032800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 1702 | keep | 0 | Mar | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-03-28 03:23 | 2023-03-28 08:00 | 42 | 4:37 | P | ANIMAL | 1 X 30 EN C/L Y 1 X 65 EN C/L CRUCE X AVE | C23032800003 | New_Event | Animals | Include | Include | Wildlife | 277 | 2023-03-28 | 11634 | keep | 0 | Mar | 2023 | 0.0079239 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BAYAMON | 2023-03-28 03:48 | 2023-03-28 04:23 | 714 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZARON OPERACIONES Y ENTRO UN 20% ADICIONAL | B23032800001 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 35 | 2023-03-28 | 24990 | keep | 0 | Mar | 2023 | 0.017021 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-28 04:20 | 2023-03-28 04:21 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2303280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 2178 | keep | 0 | Mar | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2023-03-28 04:23 | 2023-03-28 05:22 | 571 | 0:59 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZARON OPERACIONES Y ENTRO EN SERVICIO 25% ADICIONAL | B23032800001 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 59 | 2023-03-28 | 33689 | keep | 0 | Mar | 2023 | 0.022945 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-03-28 05:16 | 2023-03-28 09:20 | 78 | 4:04 | P | DESCONECTIVO DEFECTUOSO | SJ-230328-01 SE SECCIONALIZO MACHETE QUEMADO Y SE CERRO MACHETES CONTRA 1111-01 | S23032800003 | New_Event | Switch Failure | Include | Include | Equipment | 244 | 2023-03-28 | 19032 | keep | 0 | Mar | 2023 | 0.012963 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
BAYAMON | 2023-03-28 05:22 | 2023-03-28 17:31 | 75 | 12:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2X80 EN C/L SE REMPLAZO CAJA PRIMARIA | B23032800001 | New_Event | Cutout Failure | Include | Include | Equipment | 729 | 2023-03-28 | 54675 | keep | 0 | Mar | 2023 | 0.037239 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-03-28 05:22 | 2023-03-28 17:43 | 428 | 12:21 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. BY-230328-01 - EN SERVICIO TOTAL | B23032800001 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 741 | 2023-03-28 | 317148 | keep | 0 | Mar | 2023 | 0.21601 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-28 05:31 | 2023-03-28 07:20 | 8 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23032800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2023-03-28 | 872 | keep | 0 | Mar | 2023 | 0.00059392 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-03-28 06:06 | 2023-03-28 06:07 | 3744 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23032800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 3744 | keep | 0 | Mar | 2023 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
SAN JUAN | 2023-03-28 06:10 | 2023-03-28 10:01 | 40 | 3:51 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO SE REPORTO CAUS | S23032800006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2023-03-28 | 9240 | keep | 0 | Mar | 2023 | 0.0062933 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-03-28 06:15 | 2023-03-28 06:17 | 329 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 99% 3015-06 | C23032800018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-28 | 658 | keep | 0 | Mar | 2023 | 0.00044816 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2023-03-28 06:15 | 2023-03-28 06:17 | 1339 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 3006-01 LLEVA 99% 3015-06 | C23032800018 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-28 | 2678 | keep | 0 | Mar | 2023 | 0.001824 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
VEGA BAJA | 2023-03-28 06:17 | 2023-03-28 12:42 | 50 | 6:25 | P | NO SE REPORTO CAUSA | 1X65 EN C/L Y 1X50 EN OTRO C/L | B23032800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 385 | 2023-03-28 | 19250 | keep | 0 | Mar | 2023 | 0.013111 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-28 06:38 | 2023-03-28 13:16 | 50 | 6:38 | P | CONDUCTOR ROTO O ABIERTO | 1X50 EN C/L 1X30 WN OTRO C/L SE REPARO NEUTRAL DEL SISTEMA | B23032800022 | New_Event | Primary Wire Break | Include | Include | Equipment | 398 | 2023-03-28 | 19900 | keep | 0 | Mar | 2023 | 0.013554 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-03-28 06:45 | 2023-03-28 09:52 | 7 | 3:07 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE PRIMARIO | C23032800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2023-03-28 | 1309 | keep | 0 | Mar | 2023 | 0.00089155 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-28 06:58 | 2023-03-28 06:59 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S2303280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 2466 | keep | 0 | Mar | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
CAGUAS | 2023-03-28 07:09 | 2023-03-28 09:04 | 27 | 1:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C23032800024 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 115 | 2023-03-28 | 3105 | keep | 0 | Mar | 2023 | 0.0021148 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
PONCE | 2023-03-28 07:28 | 2023-03-28 07:29 | 349 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA QUEDO EN SERVICIO | P23032800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 349 | keep | 0 | Mar | 2023 | 0.0002377 | 0.0002377 | Momentary | FALSE | FALSE | Not_TMED_Event | 349
SAN JUAN | 2023-03-28 07:42 | 2023-03-28 12:36 | 1 | 4:54 | P | DESGANCHE | SE RETIRO ENREDADERA DE LA SUB ESTACION 2 X 50 EN RISER | S23032800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-03-28 | 294 | keep | 0 | Mar | 2023 | 0.00020024 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-28 07:49 | 2023-03-28 07:50 | 271 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | S2303280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 271 | keep | 0 | Mar | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
AGUADILLA | 2023-03-28 07:52 | 2023-03-28 10:30 | 1 | 2:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA | M23032800040 | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2023-03-28 | 158 | keep | 0 | Mar | 2023 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-28 08:57 | 2023-03-28 10:59 | 6 | 2:02 | P | ANIMAL | 1 X 10 EN XMR AVE CRUZO LINEAS | R23032800013 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-03-28 | 732 | keep | 0 | Mar | 2023 | 0.00049856 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-28 09:10 | 2023-03-28 10:56 | 100 | 1:46 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23032800033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-03-28 | 10600 | keep | 0 | Mar | 2023 | 0.0072196 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-28 09:18 | 2023-03-28 12:55 | 11 | 3:37 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO 22-003-HC-FIONA | S23032800035 | New_Event | Primary Pole Failure | Include | Include | Equipment | 217 | 2023-03-28 | 2387 | keep | 0 | Mar | 2023 | 0.0016258 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-03-28 09:18 | 2023-03-28 12:26 | 70 | 3:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIEMPO VIENTOS | C23032800044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 188 | 2023-03-28 | 13160 | keep | 0 | Mar | 2023 | 0.0089632 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-03-28 09:18 | 2023-03-28 12:27 | 8 | 3:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR MAL TIEMPO VIENTOS | C23032800044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2023-03-28 | 1512 | keep | 0 | Mar | 2023 | 0.0010298 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-03-28 09:20 | 2023-03-28 11:45 | 14 | 2:25 | P | DESCONECTIVO DEFECTUOSO | SJ-230328-01 SE REPARO MACHETE QUEMADO Y SE DIO SERVICIO | S23032800003 | Partial_restoration | Switch Failure | Include | Include | Equipment | 145 | 2023-03-28 | 2030 | keep | 0 | Mar | 2023 | 0.0013826 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-28 09:35 | 2023-03-28 12:54 | 80 | 3:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L SE REMPLAZO CAJA PRIMARIA | B23032800038 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2023-03-28 | 15920 | keep | 0 | Mar | 2023 | 0.010843 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-03-28 09:59 | 2023-03-28 12:35 | 1 | 2:36 | P | ANIMAL | 2 X 15 EN BANCO DE TRANSFORMADOR CRUCE X AVE | S23032800056 | New_Event | Animals | Include | Include | Wildlife | 156 | 2023-03-28 | 156 | keep | 0 | Mar | 2023 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-28 10:05 | 2023-03-28 10:08 | 1399 | 0:03 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 10000 | B23032800066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-28 | 4197 | keep | 0 | Mar | 2023 | 0.0028586 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2023-03-28 10:05 | 2023-03-28 10:08 | 302 | 0:03 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 10000 | B23032800066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-28 | 906 | keep | 0 | Mar | 2023 | 0.00061707 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2023-03-28 10:05 | 2023-03-28 10:08 | 1048 | 0:03 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 10000 | B23032800066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-28 | 3144 | keep | 0 | Mar | 2023 | 0.0021414 | 0.00071379 | Momentary | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2023-03-28 10:05 | 2023-03-28 10:08 | 573 | 0:03 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 10000 | B23032800066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-28 | 1719 | keep | 0 | Mar | 2023 | 0.0011708 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2023-03-28 10:05 | 2023-03-28 10:08 | 1313 | 0:03 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 10000 | B23032800066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-03-28 | 3939 | keep | 0 | Mar | 2023 | 0.0026828 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
BAYAMON | 2023-03-28 10:05 | 2023-03-28 10:07 | 1715 | 0:02 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 10000 | B23032800067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-28 | 3430 | keep | 0 | Mar | 2023 | 0.0023362 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-03-28 10:05 | 2023-03-28 10:07 | 1498 | 0:02 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 10000 | B23032800067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-28 | 2996 | keep | 0 | Mar | 2023 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-03-28 10:05 | 2023-03-28 10:07 | 1221 | 0:02 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 10000 | B23032800067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-28 | 2442 | keep | 0 | Mar | 2023 | 0.0016632 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-03-28 10:05 | 2023-03-28 10:07 | 1100 | 0:02 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 10000 | B23032800067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-28 | 2200 | keep | 0 | Mar | 2023 | 0.0014984 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-03-28 10:14 | 2023-03-28 10:46 | 1 | 0:32 | P | ANIMAL | 1X40 EN TRANSCLOSURE DEL CLIENTE CRUCE POR ROEDOR (RATON) | S23032800061 | New_Event | Animals | Include | Include | Wildlife | 32 | 2023-03-28 | 32 | keep | 0 | Mar | 2023 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-03-28 10:18 | 2023-03-28 10:19 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23032800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 2379 | keep | 0 | Mar | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2023-03-28 10:31 | 2023-03-28 12:24 | 90 | 1:53 | P | CAUSAS EXTERNAS | 2X80 EN C/L PERSONAL AJENO A LUMA DESGANCHANDO | B23032800065 | New_Event | Damage From Public | Include | Include | Public | 113 | 2023-03-28 | 10170 | keep | 0 | Mar | 2023 | 0.0069267 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2023-03-28 10:46 | 2023-03-28 11:56 | 775 | 1:10 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1658-15 LLECANDO 40% 1657-05 Y 30% 1658-13. SE SECCIONALIZO Y SE CERRO POR SCADA. EN SERVICIO 10% 1657-02 FUERA 1658-15 Y 30% 1658-13 | R23032800022 | New_Event | UG Cable Fault | Include | Include | Equipment | 70 | 2023-03-28 | 54250 | keep | 0 | Mar | 2023 | 0.036949 | 0.00052785 | Sustained | FALSE | FALSE | Not_TMED_Event | 775
CANOVANAS | 2023-03-28 10:46 | 2023-03-28 12:21 | 673 | 1:35 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR 1657-02 POR AVERIA DE CABLE SOTERRADO Y SE CERRO POR CONTROL. | R23032800022 | New_Event | Feeder Load Transferred | Include | Include | Other | 95 | 2023-03-28 | 63935 | keep | 0 | Mar | 2023 | 0.043546 | 0.00045838 | Sustained | FALSE | FALSE | Not_TMED_Event | 673
CANOVANAS | 2023-03-28 10:46 | 2023-03-28 12:21 | 1 | 1:35 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR 1657-02 POR AVERIA DE CABLE SOTERRADO Y SE CERRO POR CONTROL. | R23032800022 | New_Event | Feeder Load Transferred | Include | Include | Other | 95 | 2023-03-28 | 95 | keep | 0 | Mar | 2023 | 6.4704e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-28 10:46 | 2023-03-28 12:32 | 1 | 1:46 | P | ANIMAL | 1 X 20 EN C/L Y 2 X 15 EN XMR CRUCE X AVE | C23032800060 | New_Event | Animals | Include | Include | Wildlife | 106 | 2023-03-28 | 106 | keep | 0 | Mar | 2023 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-03-28 11:00 | 2023-03-28 13:43 | 14 | 2:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BARRAS EN PEDESTAL | C23032800063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 163 | 2023-03-28 | 2282 | keep | 0 | Mar | 2023 | 0.0015543 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-03-28 11:23 | 2023-03-28 11:24 | 74 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2303280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 74 | keep | 0 | Mar | 2023 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
CAGUAS | 2023-03-28 11:35 | 2023-03-28 14:53 | 4 | 3:18 | P | OTRAS CAUSAS | SE ABRIO XMR T-15 PARA QUE LOW VOLTAGE REPARARA EN BASE DE CONTADOR | C23032800067 | New_Event | Other Causes | Include | Include | Other | 198 | 2023-03-28 | 792 | keep | 0 | Mar | 2023 | 0.00053943 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-03-28 11:56 | 2023-03-28 12:00 | 698 | 0:04 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR Y ENTRO EN SERVICIO 25% 1657-02 FUERA CARGA 1658-13 Y 1658-15 | R23032800022 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 4 | 2023-03-28 | 2792 | keep | 0 | Mar | 2023 | 0.0019016 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-28 12:00 | 2023-03-28 12:13 | 581 | 0:13 | P | CABLE SOTERRADO AVERIADO | OPERACIONES PARA SECCIONALIZAR ALIMENTADOR DISPARO INTERRUPTOR | R23032800022 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 13 | 2023-03-28 | 7553 | keep | 0 | Mar | 2023 | 0.0051443 | 0.00039572 | Sustained | FALSE | FALSE | Not_TMED_Event | 581
MAYAGÃœEZ | 2023-03-28 12:00 | 2023-03-28 18:19 | 70 | 6:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23032800143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 379 | 2023-03-28 | 26530 | keep | 0 | Mar | 2023 | 0.018069 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-03-28 12:13 | 2023-03-28 12:21 | 775 | 0:08 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZA INTERRUPTOR Y SE CIERRA POR SCADA EN SERVICIO 35% 1657-02 30% 1658-13 Y 100% 1658-15 | R23032800022 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 8 | 2023-03-28 | 6200 | keep | 0 | Mar | 2023 | 0.0042228 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-28 12:21 | 2023-03-28 13:08 | 39 | 0:47 | P | CABLE SOTERRADO AVERIADO | SECCIONALIZANDO AVERIA DE CABLE SOTERRADO DISPARO DE INTERRUPTOR | R23032800022 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 47 | 2023-03-28 | 1833 | keep | 0 | Mar | 2023 | 0.0012484 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-28 12:35 | 2023-03-28 14:30 | 8 | 1:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M23032800073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 115 | 2023-03-28 | 920 | keep | 0 | Mar | 2023 | 0.00062661 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-28 13:08 | 2023-03-28 13:10 | 775 | 0:02 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZA AVERIA SOTERRADA DE SU 65 A SU 28 Y SE CIERRA POR SCADA. EN SERVICIO 35% 1657-02 30% 1658-13 Y 100% 1658-15 | R23032800022 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 2 | 2023-03-28 | 1550 | keep | 0 | Mar | 2023 | 0.0010557 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-28 13:08 | 2023-03-28 13:10 | 673 | 0:02 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR 1657-02 POR AVERIA DE CABLE SOTERRADO Y SE CERRO POR CONTROL. | R23032800022 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-28 | 1346 | keep | 0 | Mar | 2023 | 0.00091675 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-28 13:08 | 2023-03-28 13:10 | 1 | 0:02 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR 1657-02 POR AVERIA DE CABLE SOTERRADO Y SE CERRO POR CONTROL. | R23032800022 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-28 | 2 | keep | 0 | Mar | 2023 | 1.3622e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-28 13:10 | 2023-03-28 13:19 | 39 | 0:09 | P | CABLE SOTERRADO AVERIADO | SE PASO 5% DEL 1657-04 CERRANDO BUS TIE EN SU 28 POR AVERIA DE CABLE SOTERRADO ENTRE SU 65 A SU 28 EN SERVICIO TOTAL | R23032800022 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 9 | 2023-03-28 | 351 | keep | 0 | Mar | 2023 | 0.00023906 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CANOVANAS | 2023-03-28 13:28 | 2023-03-28 14:49 | 20 | 1:21 | P | DESGANCHE | 1 X 20 EN C/L Y DESPEJE DE LINEA | R23032800057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-03-28 | 1620 | keep | 0 | Mar | 2023 | 0.0011034 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-03-28 13:36 | 2023-03-28 16:35 | 150 | 2:59 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CL LINEA PRIMARIA CRUZADA | A23032800068 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 179 | 2023-03-28 | 26850 | keep | 0 | Mar | 2023 | 0.018287 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-03-28 13:56 | 2023-03-28 18:38 | 40 | 4:42 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23032800071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2023-03-28 | 11280 | keep | 0 | Mar | 2023 | 0.0076828 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-03-28 14:10 | 2023-03-28 14:19 | 1608 | 0:09 | P | ALIMENTADOR AMARRADO | DISPARO UNIDAD 2 DE AES 1608 DE SUS CLIENTES POR EL 3201-01 | C2303280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-03-28 | 14472 | keep | 0 | Mar | 2023 | 0.0098568 | 0.0010952 | Sustained | FALSE | FALSE | Not_TMED_Event | 1608
ARECIBO | 2023-03-28 14:27 | 2023-03-28 17:07 | 28 | 2:40 | P | DESGANCHE | 1 X 50 CL DESGANCHE | A23032800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-03-28 | 4480 | keep | 0 | Mar | 2023 | 0.0030513 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 396 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 1584 | keep | 0 | Mar | 2023 | 0.0010789 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 119 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 476 | keep | 0 | Mar | 2023 | 0.0003242 | 8.105e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 119
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 290 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 1160 | keep | 0 | Mar | 2023 | 0.00079007 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 390 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 1560 | keep | 0 | Mar | 2023 | 0.0010625 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 719 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 2876 | keep | 0 | Mar | 2023 | 0.0019588 | 0.00048971 | Momentary | FALSE | FALSE | Not_TMED_Event | 719
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 67 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 268 | keep | 0 | Mar | 2023 | 0.00018253 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 4 | keep | 0 | Mar | 2023 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 275 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 1100 | keep | 0 | Mar | 2023 | 0.0007492 | 0.0001873 | Momentary | FALSE | FALSE | Not_TMED_Event | 275
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 142 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 568 | keep | 0 | Mar | 2023 | 0.00038686 | 9.6716e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 142
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 45 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 180 | keep | 0 | Mar | 2023 | 0.0001226 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 93 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 372 | keep | 0 | Mar | 2023 | 0.00025337 | 6.3342e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 93
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 418 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 1672 | keep | 0 | Mar | 2023 | 0.0011388 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 295 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800206 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 1180 | keep | 0 | Mar | 2023 | 0.00080369 | 0.00020092 | Momentary | FALSE | FALSE | Not_TMED_Event | 295
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 948 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800206 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 3792 | keep | 0 | Mar | 2023 | 0.0025827 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:37 | 641 | 0:08 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-03-28 | 5128 | keep | 0 | Mar | 2023 | 0.0034927 | 0.00043658 | Sustained | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:37 | 308 | 0:08 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-03-28 | 2464 | keep | 0 | Mar | 2023 | 0.0016782 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:37 | 559 | 0:08 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-03-28 | 4472 | keep | 0 | Mar | 2023 | 0.0030459 | 0.00038073 | Sustained | FALSE | FALSE | Not_TMED_Event | 559
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:37 | 370 | 0:08 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-03-28 | 2960 | keep | 0 | Mar | 2023 | 0.002016 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 1105 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800212 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 4420 | keep | 0 | Mar | 2023 | 0.0030104 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 181 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800212 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 724 | keep | 0 | Mar | 2023 | 0.00049311 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 14:33 | 351 | 0:04 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800212 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-28 | 1404 | keep | 0 | Mar | 2023 | 0.00095626 | 0.00023906 | Momentary | FALSE | FALSE | Not_TMED_Event | 351
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 18:15 | 570 | 3:46 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL FERNANDO FEBRES INFORMA QUE HABIA ENREDADERAS EN UNOS MACHETES Y SE REFIERE AL PERSONAL DE PODA | S23032800146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2023-03-28 | 128820 | keep | 0 | Mar | 2023 | 0.087739 | 0.00038822 | Sustained | FALSE | FALSE | Not_TMED_Event | 570
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 15:23 | 218 | 0:54 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2023-03-28 | 11772 | keep | 0 | Mar | 2023 | 0.0080179 | 0.00014848 | Sustained | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 15:23 | 455 | 0:54 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2023-03-28 | 24570 | keep | 0 | Mar | 2023 | 0.016735 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 15:23 | 1526 | 0:54 | S | LINEA DE TRANSMISION 38KV | POR DISPARO LINEA 3300 OHGW PARTIDO LINEAS 3200/3300. BKR 3390 VIADUCTO NO ABRIÃ“ EN AVERÃA. | S23032800217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2023-03-28 | 82404 | keep | 0 | Mar | 2023 | 0.056125 | 0.0010394 | Sustained | FALSE | FALSE | Not_TMED_Event | 1526
SAN JUAN | 2023-03-28 14:29 | 2023-03-28 17:32 | 867 | 3:03 | T | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO ALIMENTADOR Y SE REPARO OVER HEAD GROUND QUE CAYO ENCIMA DE LA LINEA 3300 Y 3200 SE TRABAJO MEDIANTE GOI-SJ-230328-02 | S23032800144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 183 | 2023-03-28 | 158661 | keep | 0 | Mar | 2023 | 0.10806 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
ARECIBO | 2023-03-28 14:36 | 2023-03-28 14:39 | 8 | 0:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO PORTA FUSIBLE AVERIADO | A23032800079 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2023-03-28 | 24 | keep | 0 | Mar | 2023 | 1.6346e-05 | 5.4488e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-03-28 14:42 | 2023-03-28 18:15 | 118 | 3:33 | T | CRUCETA DEFECTUOSA O AVERIADA | DISPARO DE INTERRUPTOR SE REMPLAZO CRUCETA MEDIANTE SWF-SJ-230328-03 | S23032800144 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 213 | 2023-03-28 | 25134 | keep | 0 | Mar | 2023 | 0.017119 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
GUAYAMA | 2023-03-28 15:00 | 2023-03-28 15:57 | 25 | 0:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO 1 X 65 Y 1 X 50 EN DIFERENTES CORTES DE LINEA | P23032800064 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 57 | 2023-03-28 | 1425 | keep | 0 | Mar | 2023 | 0.00097056 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-03-28 15:20 | 2023-03-28 18:05 | 15 | 2:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA 2 X 25 EN TRANSFORMADOR | P23032800114 | New_Event | Secondary Wire Break | Include | Include | Equipment | 165 | 2023-03-28 | 2475 | keep | 0 | Mar | 2023 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-28 15:23 | 2023-03-28 16:54 | 15 | 1:31 | P | ANIMAL | 1 X 30 EM CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23032800129 | New_Event | Animals | Include | Include | Wildlife | 91 | 2023-03-28 | 1365 | keep | 0 | Mar | 2023 | 0.0009297 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-03-28 15:37 | 2023-03-28 15:53 | 312 | 0:16 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR AL HACER OPERACION EN EL ALIMENTADOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23032800148 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 16 | 2023-03-28 | 4992 | keep | 0 | Mar | 2023 | 0.0034 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
AGUADILLA | 2023-03-28 15:40 | 2023-03-28 16:30 | 8 | 0:50 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR PARA RETIRAR TOMA DE CASA INCENDIADA | M23032800140 | New_Event |  |  |  |  | 50 | 2023-03-28 | 400 | keep | 0 | Mar | 2023 | 0.00027244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-03-28 15:44 | 2023-03-28 16:52 | 1 | 1:08 | P | PROBLEMA DEL CLIENTE | BUSHING SECUNDARIO DE TRANSFORMADOR PRIVADO AVERIADO | P23032800122 | New_Event | Customer-Related Interruption | Include | Include | Public | 68 | 2023-03-28 | 68 | keep | 0 | Mar | 2023 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-28 15:47 | 2023-03-28 18:42 | 35 | 2:55 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23032800184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-03-28 | 6125 | keep | 0 | Mar | 2023 | 0.0041717 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-03-28 15:53 | 2023-03-28 16:20 | 100 | 0:27 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE INSTALO BYPASS A VACCUM SWITCH AVERIADO EN MH-03 Y SE ENERGIZO A CLIENTES | M23032700059 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 27 | 2023-03-28 | 2700 | keep | 0 | Mar | 2023 | 0.001839 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-03-28 15:54 | 2023-03-28 16:17 | 7 | 0:23 | P | CAUSAS EXTERNAS | 2 X 10 SE CERRO MONTURA | P23032800076 | New_Event | Damage From Public | Include | Include | Public | 23 | 2023-03-28 | 161 | keep | 0 | Mar | 2023 | 0.00010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-03-28 16:08 | 2023-03-28 17:29 | 50 | 1:21 | P | DESGANCHE | 2X40 EN C/L DESGANCHE | B23032800186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-03-28 | 4050 | keep | 0 | Mar | 2023 | 0.0027584 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-28 16:17 | 2023-03-28 16:18 | 2708 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23032800126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 2708 | keep | 0 | Mar | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
MAYAGÃœEZ | 2023-03-28 16:20 | 2023-03-28 16:21 | 312 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR AL CERRAR MH-1 SE VERIFICO PERSONAL FUERA DEL AREA Y SE CERRO INTERRUPTOR | M23032800154 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-03-28 | 312 | keep | 0 | Mar | 2023 | 0.0002125 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-03-28 16:21 | 2023-03-28 18:32 | 100 | 2:11 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE INSTALO BYPASS A VACCUM SWITCH AVERIADO EN MH-03 Y SE ENERGIZO A CLIENTES | M23032700059 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 131 | 2023-03-28 | 13100 | keep | 0 | Mar | 2023 | 0.0089224 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-03-28 16:34 | 2023-03-28 16:36 | 315 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1903-02 SE CERRO POR CONTROL | S23032800230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-28 | 630 | keep | 0 | Mar | 2023 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2023-03-28 16:45 | 2023-03-28 19:02 | 10 | 2:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BARRAS EN PEDESTAL | C23032800310 | New_Event | Secondary Wire Break | Include | Include | Equipment | 137 | 2023-03-28 | 1370 | keep | 0 | Mar | 2023 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-28 16:49 | 2023-03-28 21:23 | 70 | 4:34 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23032800193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2023-03-28 | 19180 | keep | 0 | Mar | 2023 | 0.013063 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-03-28 17:16 | 2023-03-28 23:00 | 20 | 5:44 | P | TERMINACION SOTERRADA AVERIADA | 1 X 40 EN PROVISIONAL AEREO SE REMPLAZO PISTOLA EN T-5 | S23032800240 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 344 | 2023-03-28 | 6880 | keep | 0 | Mar | 2023 | 0.0046859 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-28 17:22 | 2023-03-28 17:23 | 74 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2303280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 74 | keep | 0 | Mar | 2023 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
ARECIBO | 2023-03-28 17:28 | 2023-03-28 18:31 | 45 | 1:03 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CL CRUCE POR BAJANTE SAFADO DE LINEA A CAJA DE TRANSFORMADOR | A23032800101 | New_Event | Primary Wire Break | Include | Include | Equipment | 63 | 2023-03-28 | 2835 | keep | 0 | Mar | 2023 | 0.0019309 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2023-03-28 17:38 | 2023-03-28 20:02 | 16 | 2:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE FIJO BAJANTE SECUNDARIO DE TRANSFORMADOR | P23032800143 | New_Event | Secondary Wire Break | Include | Include | Equipment | 144 | 2023-03-28 | 2304 | keep | 0 | Mar | 2023 | 0.0015692 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-03-28 17:40 | 2023-03-28 18:58 | 4 | 1:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO BARRA EN PEDESTAL | S23032800242 | New_Event | Secondary Wire Break | Include | Include | Equipment | 78 | 2023-03-28 | 312 | keep | 0 | Mar | 2023 | 0.0002125 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-03-28 17:49 | 2023-03-28 19:03 | 12 | 1:14 | P | ANIMAL | 1 X 20 EN XMR CRUCE X AVE | C23032800362 | New_Event | Animals | Include | Include | Wildlife | 74 | 2023-03-28 | 888 | keep | 0 | Mar | 2023 | 0.00060481 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-03-28 17:52 | 2023-03-28 19:49 | 7 | 1:57 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO FASE SECUNDARIA Y CLIENTES EN UNA FASE | P23032800145 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 117 | 2023-03-28 | 819 | keep | 0 | Mar | 2023 | 0.00055782 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-03-28 17:57 | 2023-03-29 08:44 | 8 | 14:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES Y BAJANTE SECUNDARIO | C2303280035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 887 | 2023-03-28 | 7096 | keep | 0 | Mar | 2023 | 0.0048331 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-03-28 18:06 | 2023-03-28 19:55 | 30 | 1:49 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | M23032800164 | New_Event | Primary Wire Break | Include | Include | Equipment | 109 | 2023-03-28 | 3270 | keep | 0 | Mar | 2023 | 0.0022272 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-28 18:29 | 2023-03-28 18:30 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23032800165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 108 | keep | 0 | Mar | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2023-03-28 18:30 | 2023-03-28 18:33 | 570 | 0:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL FERNANDO FEBRES INFORMA QUE HABIA ENREDADERAS EN UNOS MACHETES Y SE REFIERE AL PERSONAL DE PODA | S23032800249 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-03-28 | 1710 | keep | 0 | Mar | 2023 | 0.0011647 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-03-28 19:29 | 2023-03-28 21:50 | 80 | 2:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CL PORTA FUSIBLE AVERIADO | A23032800112 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2023-03-28 | 11280 | keep | 0 | Mar | 2023 | 0.0076828 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-03-28 21:01 | 2023-03-28 21:02 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2303280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
BAYAMON | 2023-03-28 21:09 | 2023-03-28 23:56 | 80 | 2:47 | P | DESGANCHE | 1 X 140 EN C/L | B23032800231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-03-28 | 13360 | keep | 0 | Mar | 2023 | 0.0090994 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-28 21:09 | 2023-03-28 21:10 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECRRO | B23032800232 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-28 | 1859 | keep | 0 | Mar | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2023-03-28 22:33 | 2023-03-29 00:59 | 75 | 2:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN PROVISIONAL AEREO | B23032800263 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2023-03-28 | 10950 | keep | 0 | Mar | 2023 | 0.007458 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-03-28 22:33 | 2023-03-29 02:11 | 3 | 3:38 | P | DESGANCHE | 1 X 15 EN MONTURA SE RETIRO RAMA DE LA LINEA | B23032800252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2023-03-28 | 654 | keep | 0 | Mar | 2023 | 0.00044544 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-03-29 02:04 | 2023-03-29 02:05 | 2770 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23032900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 2770 | keep | 0 | Mar | 2023 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
CAGUAS | 2023-03-29 02:05 | 2023-03-29 02:06 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2303290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 2178 | keep | 0 | Mar | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2023-03-29 02:18 | 2023-03-29 11:44 | 86 | 9:26 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23032900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 566 | 2023-03-29 | 48676 | keep | 0 | Mar | 2023 | 0.033153 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
BAYAMON | 2023-03-29 02:37 | 2023-03-29 02:38 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23032900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 3438 | keep | 0 | Mar | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
CANOVANAS | 2023-03-29 02:40 | 2023-03-29 09:50 | 50 | 7:10 | P | DESGANCHE | 1 X 50 EN C/L | R23032900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 430 | 2023-03-29 | 21500 | keep | 0 | Mar | 2023 | 0.014644 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-03-29 04:30 | 2023-03-29 07:42 | 180 | 3:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR LLUVIAS | B23032900005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 192 | 2023-03-29 | 34560 | keep | 0 | Mar | 2023 | 0.023539 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
ARECIBO | 2023-03-29 04:38 | 2023-03-29 09:50 | 120 | 5:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23032900014 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 312 | 2023-03-29 | 37440 | keep | 0 | Mar | 2023 | 0.0255 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2023-03-29 04:40 | 2023-03-29 10:55 | 50 | 6:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23032900016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 375 | 2023-03-29 | 18750 | keep | 0 | Mar | 2023 | 0.012771 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-03-29 04:50 | 2023-03-29 09:44 | 40 | 4:54 | P | DESGANCHE | 1 X 100 EN C/L | R23032900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-03-29 | 11760 | keep | 0 | Mar | 2023 | 0.0080097 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-29 05:27 | 2023-03-29 14:17 | 37 | 8:50 | P | TERMINACION SOTERRADA AVERIADA | 1X30 DE RISER @ T-3 SE REMPLAZO TERMINACION SOTERRADA AVERIADA | B23032900009 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 530 | 2023-03-29 | 19610 | keep | 0 | Mar | 2023 | 0.013356 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CANOVANAS | 2023-03-29 05:33 | 2023-03-29 05:34 | 3699 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R2303290000X | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-03-29 | 3699 | keep | 0 | Mar | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
AGUADILLA | 2023-03-29 05:37 | 2023-03-29 10:05 | 90 | 4:28 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN CL LINEA PRIMARIA CRUZADA | M23032900001 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 268 | 2023-03-29 | 24120 | keep | 0 | Mar | 2023 | 0.016428 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2023-03-29 05:38 | 2023-03-29 08:00 | 40 | 2:22 | P | ANIMAL | 1 X 25 1 X 15 EN C/L'S Y 1 X 10 EN XMR CRUCE X AVE | R23032900014 | New_Event | Animals | Include | Include | Wildlife | 142 | 2023-03-29 | 5680 | keep | 0 | Mar | 2023 | 0.0038686 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-29 05:44 | 2023-03-29 10:54 | 100 | 5:10 | P | ANIMAL | 1X30 EN C/L CRUCE POR AVE | B23032900011 | New_Event | Animals | Include | Include | Wildlife | 310 | 2023-03-29 | 31000 | keep | 0 | Mar | 2023 | 0.021114 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-29 05:48 | 2023-03-29 05:49 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23032900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 1026 | keep | 0 | Mar | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-03-29 05:52 | 2023-03-29 05:53 | 3699 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R23032900019 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-03-29 | 3699 | keep | 0 | Mar | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2023-03-29 05:53 | 2023-03-29 08:11 | 3464 | 2:18 | T | DESCONECTIVO DEFECTUOSO | SE TRANSFIRIO LA CARGA AL 2402-02 SUB EN LOCK OUT POR MACHETE DE BARRA QUEMADO EN EL 2404-07 | R23032900020 | New_Event | Switch Failure | Include | Include | Equipment | 138 | 2023-03-29 | 478032 | keep | 0 | Mar | 2023 | 0.32559 | 0.0023593 | Sustained | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2023-03-29 05:53 | 2023-03-29 07:12 | 6859 | 1:19 | P | DESCONECTIVO DEFECTUOSO | SUB EN LOCK OUT POR MACHETE DE BARRA QUEMADO EN EL 2404-07 90% DE LA CARGA X 1646-03 | R23032900018 | New_Event | Switch Failure | Include | Include | Equipment | 79 | 2023-03-29 | 541861 | keep | 0 | Mar | 2023 | 0.36906 | 0.0046716 | Sustained | FALSE | FALSE | Not_TMED_Event | 6859
CANOVANAS | 2023-03-29 05:53 | 2023-03-29 07:37 | 3699 | 1:44 | S | DESCONECTIVO DEFECTUOSO | SE TRANSFIRIO LA CARGA AL 2402-04 POR MACHETE DE BARRA QUEMADO | R23032900018 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 104 | 2023-03-29 | 384696 | keep | 0 | Mar | 2023 | 0.26201 | 0.0025194 | Sustained | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2023-03-29 05:53 | 2023-03-29 08:11 | 2675 | 2:18 | S | DESCONECTIVO DEFECTUOSO | SE TRANSFIRIO LA CARGA AL 2402-02 SUB EN LOCK OUT POR MACHETE DE BARRA QUEMADO EN EL 2404-07 | R23032900020 | New_Event | Switch Failure | Include | Include | Equipment | 138 | 2023-03-29 | 369150 | keep | 0 | Mar | 2023 | 0.25143 | 0.0018219 | Sustained | FALSE | FALSE | Not_TMED_Event | 2675
SAN JUAN | 2023-03-29 06:01 | 2023-03-29 06:02 | 1483 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1303-02 CERRADO POR CONTROL | S2303290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-29 | 1483 | keep | 0 | Mar | 2023 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-03-29 06:01 | 2023-03-29 06:02 | 2435 | 0:01 | T | DESGANCHE | DISPARO DE BKR CERRADO POR CONTROL LLEVA 30% 1204-04 | S2303290000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-29 | 2435 | keep | 0 | Mar | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-03-29 06:02 | 2023-03-29 07:43 | 603 | 1:41 | P | DESGANCHE | SJ-230329-010 SE SECCIONALIZO ALIMENTADOR PARA RETIRAR BAMBOO DE LA LINEA | S23032900023 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-03-29 | 60903 | keep | 0 | Mar | 2023 | 0.041481 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-03-29 06:06 | 2023-03-29 06:07 | 57 | 0:01 | T | DESGANCHE | RECERRO | S2303290000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-29 | 57 | keep | 0 | Mar | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2023-03-29 06:11 | 2023-03-29 06:12 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2303290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 45 | keep | 0 | Mar | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-03-29 06:14 | 2023-03-29 06:15 | 57 | 0:01 | T | DESGANCHE | RECERRO | S2303290000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-29 | 57 | keep | 0 | Mar | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-03-29 06:15 | 2023-03-29 18:27 | 2 | 12:12 | P | DESGANCHE | 3X40 EN C/L DESGANCHE | S23032900123 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 732 | 2023-03-29 | 1464 | keep | 0 | Mar | 2023 | 0.00099712 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-29 06:23 | 2023-03-29 10:28 | 60 | 4:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X65 EN AEREO PROVISIONAL POR AISLADOR | B23032900013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 245 | 2023-03-29 | 14700 | keep | 0 | Mar | 2023 | 0.010012 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-03-29 06:31 | 2023-03-29 11:55 | 12 | 5:24 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVE | M23032900005 | New_Event | Animals | Include | Include | Wildlife | 324 | 2023-03-29 | 3888 | keep | 0 | Mar | 2023 | 0.0026481 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-03-29 06:33 | 2023-03-29 09:00 | 1 | 2:27 | P | ANIMAL | 1 X 100 EN TRIFASICA POR AVE | P23032900006 | New_Event | Animals | Include | Include | Wildlife | 147 | 2023-03-29 | 147 | keep | 0 | Mar | 2023 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-29 06:44 | 2023-03-29 11:57 | 80 | 5:13 | P | CONDUCTOR ARRIADO O CRUZADO | 1X65 EN C/L SE LEVANTO CONDUCTOR PRIMARIO ARRIADO | B23032900018 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 313 | 2023-03-29 | 25040 | keep | 0 | Mar | 2023 | 0.017055 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-03-29 06:51 | 2023-03-29 08:49 | 2 | 1:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L SE REMPLAZO PORTAFUSIBLE | B23032900020 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2023-03-29 | 236 | keep | 0 | Mar | 2023 | 0.00016074 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-03-29 06:54 | 2023-03-29 06:55 | 4027 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO | B23032900022 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-03-29 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
BAYAMON | 2023-03-29 06:59 | 2023-03-29 10:20 | 80 | 3:21 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23032900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2023-03-29 | 16080 | keep | 0 | Mar | 2023 | 0.010952 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-03-29 07:12 | 2023-03-29 07:21 | 762 | 0:09 | P | DESCONECTIVO DEFECTUOSO | SUB EN LOCK OUT POR MACHETE DE BARRA QUEMADO EN EL 2404-07 10% DE LA CARGA X 2402-03 | R23032900018 | Partial_restoration | Switch Failure | Include | Include | Equipment | 9 | 2023-03-29 | 6858 | keep | 0 | Mar | 2023 | 0.004671 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-03-29 07:28 | 2023-03-29 08:50 | 20 | 1:22 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEAS CRUZADAS | A23032900050 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 82 | 2023-03-29 | 1640 | keep | 0 | Mar | 2023 | 0.001117 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2023-03-29 07:30 | 2023-03-29 09:29 | 1 | 1:59 | P | PROBLEMA DEL CLIENTE | 1 X 30 EN C/L ELIMINO PARARRAYO PRIVADO AVERIADO | R23032900133 | New_Event | Customer-Related Interruption | Include | Include | Public | 119 | 2023-03-29 | 119 | keep | 0 | Mar | 2023 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-03-29 07:34 | 2023-03-29 08:42 | 60 | 1:08 | P | DESGANCHE | 1 X 20 Y 1 X 30 EN C/L'S | R23032900139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-03-29 | 4080 | keep | 0 | Mar | 2023 | 0.0027789 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-03-29 07:36 | 2023-03-29 09:38 | 1 | 2:02 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | R23032900143 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-03-29 | 122 | keep | 0 | Mar | 2023 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-29 07:43 | 2023-03-29 07:58 | 60 | 0:15 | P | DESGANCHE | SJ-230329-01 SE RETIRO BAMBUAS DE LA LINEA Y SE CERRO MACHETES | S23032900023 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 15 | 2023-03-29 | 900 | keep | 0 | Mar | 2023 | 0.00061299 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-29 07:43 | 2023-03-29 09:55 | 208 | 2:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L POR LLUVIAS | B23032900037 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 132 | 2023-03-29 | 27456 | keep | 0 | Mar | 2023 | 0.0187 | 0.00014167 | Sustained | FALSE | FALSE | Not_TMED_Event | 208
HUMACAO | 2023-03-29 07:48 | 2023-03-29 10:08 | 295 | 2:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA | C23032900010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 140 | 2023-03-29 | 41300 | keep | 0 | Mar | 2023 | 0.028129 | 0.00020092 | Sustained | FALSE | FALSE | Not_TMED_Event | 295
ARECIBO | 2023-03-29 07:52 | 2023-03-29 11:50 | 200 | 3:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A23032900063 | New_Event | Cutout Failure | Include | Include | Equipment | 238 | 2023-03-29 | 47600 | keep | 0 | Mar | 2023 | 0.03242 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2023-03-29 08:01 | 2023-03-29 15:34 | 12 | 7:33 | P | TRANSFORMADOR AVERIADO | SE CAMBIA TRANSFORMADOR AVERIADO DE 75KVA A 7620 POR UNO MISMA CAPACIDAD 1 X 25 | P23032900011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 453 | 2023-03-29 | 5436 | keep | 0 | Mar | 2023 | 0.0037024 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-03-29 08:03 | 2023-03-29 11:22 | 30 | 3:19 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | B23032900045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2023-03-29 | 5970 | keep | 0 | Mar | 2023 | 0.0040661 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-29 08:05 | 2023-03-29 09:56 | 200 | 1:51 | P | ANIMAL | 1 X 80 EN CL CRUCE DE FASE POR IGUANA | M23032900013 | New_Event | Animals | Include | Include | Wildlife | 111 | 2023-03-29 | 22200 | keep | 0 | Mar | 2023 | 0.01512 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-03-29 08:10 | 2023-03-29 11:35 | 60 | 3:25 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23032900067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-03-29 | 12300 | keep | 0 | Mar | 2023 | 0.0083775 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-29 08:12 | 2023-03-29 12:59 | 20 | 4:47 | P | ANIMAL | 1X80 EN C/L 1X30 EN OTRO C/L CRUCE POR AVE | B23032900049 | New_Event | Animals | Include | Include | Wildlife | 287 | 2023-03-29 | 5740 | keep | 0 | Mar | 2023 | 0.0039095 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-03-29 08:41 | 2023-03-29 08:42 | 1879 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23032900038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 1879 | keep | 0 | Mar | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-03-29 08:41 | 2023-03-29 08:42 | 2608 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23032900036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 2608 | keep | 0 | Mar | 2023 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
BARRANQUITAS | 2023-03-29 08:48 | 2023-03-29 10:27 | 343 | 1:39 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23032900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-03-29 | 33957 | keep | 0 | Mar | 2023 | 0.023128 | 0.00023362 | Sustained | FALSE | FALSE | Not_TMED_Event | 343
BAYAMON | 2023-03-29 08:53 | 2023-03-29 12:54 | 8 | 4:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR TRAMO SECUNDARIO | B23032900059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 241 | 2023-03-29 | 1928 | keep | 0 | Mar | 2023 | 0.0013132 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-03-29 08:54 | 2023-03-29 17:09 | 56 | 8:15 | P | DESGANCHE | 1X30 EN C/L DESGANCHE | S23032900192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 495 | 2023-03-29 | 27720 | keep | 0 | Mar | 2023 | 0.01888 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
CAGUAS | 2023-03-29 09:00 | 2023-03-29 16:43 | 1 | 7:43 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C23032900048 | New_Event | Animals | Include | Include | Wildlife | 463 | 2023-03-29 | 463 | keep | 0 | Mar | 2023 | 0.00031535 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-29 09:07 | 2023-03-29 14:41 | 6 | 5:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES SECUNDARIOS @ SALIDA DEL XMR NO FUNDIO | B23032900065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 334 | 2023-03-29 | 2004 | keep | 0 | Mar | 2023 | 0.0013649 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-29 09:19 | 2023-03-29 11:39 | 1 | 2:20 | P | SOBRECARGA | 1X30 EN RISER POR CARGA | B23032900069 | New_Event | Trip Due To Overload | Include | Include | Other | 140 | 2023-03-29 | 140 | keep | 0 | Mar | 2023 | 9.5353e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-29 09:24 | 2023-03-29 10:56 | 65 | 1:32 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | R23032900195 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-03-29 | 5980 | keep | 0 | Mar | 2023 | 0.004073 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-03-29 09:36 | 2023-03-29 13:05 | 19 | 3:29 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | S23032900209 | New_Event | Animals | Include | Include | Wildlife | 209 | 2023-03-29 | 3971 | keep | 0 | Mar | 2023 | 0.0027046 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
VEGA BAJA | 2023-03-29 09:39 | 2023-03-29 09:40 | 4027 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO | B2303290000X | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-03-29 | 4027 | keep | 0 | Mar | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
CANOVANAS | 2023-03-29 09:44 | 2023-03-29 10:45 | 2106 | 1:01 | T | PARARRAYOS DEFECTUOSO | SE SECCIONALIZO PARARRAYO AVERIADO | R23032900262 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 61 | 2023-03-29 | 128466 | keep | 0 | Mar | 2023 | 0.087498 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
SAN JUAN | 2023-03-29 09:47 | 2023-03-29 09:48 | 293 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO BKR A PETICION DE PERSONAL EN EL CAMPO POR POSTE PRIMARIO PARTIDO ENCIMA DE LA CRUCETA | S23032900211 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2023-03-29 | 293 | keep | 0 | Mar | 2023 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2023-03-29 09:48 | 2023-03-29 14:38 | 84 | 4:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO ALIMENTADOR Y SE REMPLAZO CRUCETA PARTIDA MEDIANTE GOI SJ-230329-02 | S23032900212 | 1st_after_momentary | Primary Pole Failure | Include | Include | Equipment | 290 | 2023-03-29 | 24360 | keep | 0 | Mar | 2023 | 0.016591 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
AGUADILLA | 2023-03-29 09:52 | 2023-03-30 10:38 | 1 | 24:46 | P | CONDUCTOR ROTO O ABIERTO | SE CONECTO BAJANTE DE LINEA PRIMA A CAJA EN TRANSFORMADOR VERIFICADO EN BITACORA | M23032900038 | New_Event | Primary Wire Break | Include | Include | Equipment | 1486 | 2023-03-29 | 1486 | keep | 0 | Mar | 2023 | 0.0010121 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-29 09:58 | 2023-03-29 12:26 | 30 | 2:28 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23032900077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-03-29 | 4440 | keep | 0 | Mar | 2023 | 0.0030241 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-03-29 10:03 | 2023-03-29 14:04 | 11 | 4:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | C23032900078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 241 | 2023-03-29 | 2651 | keep | 0 | Mar | 2023 | 0.0018056 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-03-29 10:14 | 2023-03-29 13:34 | 38 | 3:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL CLIMA | S23032900220 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 200 | 2023-03-29 | 7600 | keep | 0 | Mar | 2023 | 0.0051763 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
GUAYAMA | 2023-03-29 10:16 | 2023-03-29 11:49 | 6 | 1:33 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | P23032900042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-03-29 | 558 | keep | 0 | Mar | 2023 | 0.00038005 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-03-29 10:28 | 2023-03-29 16:00 | 8 | 5:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | C23032900082 | New_Event | Cutout Failure | Include | Include | Equipment | 332 | 2023-03-29 | 2656 | keep | 0 | Mar | 2023 | 0.001809 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-03-29 10:43 | 2023-03-29 10:46 | 271 | 0:03 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR CERRADO POR CONTROL | S2303290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-29 | 813 | keep | 0 | Mar | 2023 | 0.00055373 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2023-03-29 10:45 | 2023-03-29 12:27 | 632 | 1:42 | P | PARARRAYOS DEFECTUOSO | SE REMPLAZO PARARRAYO CERCA DEL RISER DE SALIDA Y RETEZO LINEAS | R23032900262 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 102 | 2023-03-29 | 64464 | keep | 0 | Mar | 2023 | 0.043906 | 0.00043045 | Sustained | FALSE | FALSE | Not_TMED_Event | 632
SAN JUAN | 2023-03-29 11:01 | 2023-03-29 11:02 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2303290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 45 | keep | 0 | Mar | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-03-29 11:17 | 2023-03-29 11:34 | 1 | 0:17 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23032900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2023-03-29 | 17 | keep | 0 | Mar | 2023 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-29 11:21 | 2023-03-29 15:01 | 150 | 3:40 | P | TERMINACION SOTERRADA AVERIADA | SE REMPLAZO TERMINACION AVERIADA EN PROVISIONAL AEREO MEDIANTE GOI BY-230329-02 | B23032900101 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 220 | 2023-03-29 | 33000 | keep | 0 | Mar | 2023 | 0.022476 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-03-29 11:22 | 2023-03-29 12:43 | 40 | 1:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23032900238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2023-03-29 | 3240 | keep | 0 | Mar | 2023 | 0.0022067 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-03-29 11:26 | 2023-03-29 12:58 | 4027 | 1:32 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AVERIA POR AISLADOR PRIMARIO PARTIDO MEDIANTE GOI BY-230329-01 | B23032900108 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 92 | 2023-03-29 | 370484 | keep | 0 | Mar | 2023 | 0.25233 | 0.0027428 | Sustained | FALSE | FALSE | Not_TMED_Event | 4027
CAGUAS | 2023-03-29 11:32 | 2023-03-29 14:03 | 1 | 2:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C23032900093 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2023-03-29 | 151 | keep | 0 | Mar | 2023 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-03-29 11:57 | 2023-03-29 13:51 | 29 | 1:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO NO FUNDIO FUSIBLE | C23032900098 | New_Event | Primary Wire Break | Include | Include | Equipment | 114 | 2023-03-29 | 3306 | keep | 0 | Mar | 2023 | 0.0022517 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
VEGA BAJA | 2023-03-29 12:02 | 2023-03-29 13:24 | 10 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL SECUNDARIO TRASPATIO NO FUNDIO | B23032900119 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-03-29 | 820 | keep | 0 | Mar | 2023 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-29 12:05 | 2023-03-29 15:58 | 20 | 3:53 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA SE RETEZO TENSORES | M23032900073 | New_Event | Damage From Public | Include | Include | Public | 233 | 2023-03-29 | 4660 | keep | 0 | Mar | 2023 | 0.0031739 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-29 12:15 | 2023-03-29 12:50 | 12 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONEXIONES SECUNDARIAS | M23032900075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-03-29 | 420 | keep | 0 | Mar | 2023 | 0.00028606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-03-29 12:15 | 2023-03-29 13:30 | 75 | 1:15 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | M23032900076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-03-29 | 5625 | keep | 0 | Mar | 2023 | 0.0038312 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-03-29 12:17 | 2023-03-29 12:18 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2303290000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 45 | keep | 0 | Mar | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-03-29 12:20 | 2023-03-29 14:59 | 30 | 2:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR RAMA CRUZANDO LINEA | M23032900079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2023-03-29 | 4770 | keep | 0 | Mar | 2023 | 0.0032488 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-29 12:35 | 2023-03-29 12:36 | 1587 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23032900260 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 1587 | keep | 0 | Mar | 2023 | 0.0010809 | 0.0010809 | Momentary | FALSE | FALSE | Not_TMED_Event | 1587
BAYAMON | 2023-03-29 12:40 | 2023-03-29 14:40 | 29 | 2:00 | P | DESGANCHE | 1 X 65 DESGANCHE | S23032900262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-03-29 | 3480 | keep | 0 | Mar | 2023 | 0.0023702 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
VEGA BAJA | 2023-03-29 12:58 | 2023-03-29 13:50 | 2444 | 0:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PRIMARIO PARTIDO MEDIANTE GOI BY-230329-01 - EN SERVICIO TOTAL | B23032900108 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 52 | 2023-03-29 | 127088 | keep | 0 | Mar | 2023 | 0.086559 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-03-29 13:00 | 2023-03-29 14:15 | 6 | 1:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTO | C23032900041 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 75 | 2023-03-29 | 450 | keep | 0 | Mar | 2023 | 0.00030649 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-03-29 13:28 | 2023-03-29 13:41 | 1588 | 0:13 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1716-03 LLEVA LA CARGA DEL 1711-01 LLEVA LA CARGA DEL 1711-03 SE CONFIRMO PERSONAL FUERA DE LAS LINEAS Y SE CERRO POR CONTROL | B23032900148 | New_Event | Feeder Load Transferred | Include | Include | Other | 13 | 2023-03-29 | 20644 | keep | 0 | Mar | 2023 | 0.014061 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-03-29 13:28 | 2023-03-29 13:41 | 13 | 0:13 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1716-03 LLEVA LA CARGA DEL 1711-01 LLEVA LA CARGA DEL 1711-03 SE CONFIRMO PERSONAL FUERA DE LAS LINEAS Y SE CERRO POR CONTROL | B23032900148 | New_Event | Feeder Load Transferred | Include | Include | Other | 13 | 2023-03-29 | 169 | keep | 0 | Mar | 2023 | 0.00011511 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-03-29 13:28 | 2023-03-29 13:41 | 1812 | 0:13 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-03 LLEVA LA CARGA DEL 1711-01 LLEVA LA CARGA DEL 1711-03 SE CONFIRMO PERSONAL FUERA DE LAS LINEAS Y SE CERRO POR CONTROL | B23032900148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2023-03-29 | 23556 | keep | 0 | Mar | 2023 | 0.016044 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2023-03-29 13:35 | 2023-03-29 16:05 | 8 | 2:30 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZAR POSTE SECUNDARIO | B23032900152 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 150 | 2023-03-29 | 1200 | keep | 0 | Mar | 2023 | 0.00081731 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-03-29 13:43 | 2023-03-29 15:07 | 100 | 1:24 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | R23032900289 | New_Event | Animals | Include | Include | Wildlife | 84 | 2023-03-29 | 8400 | keep | 0 | Mar | 2023 | 0.0057212 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-03-29 14:00 | 2023-03-29 15:12 | 1 | 1:12 | P | ANIMAL | 1 X 30 EN RISER HACIA EL TRANSCLOSURE | C23032900109 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-03-29 | 72 | keep | 0 | Mar | 2023 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-29 14:01 | 2023-03-29 16:40 | 80 | 2:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23032900152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2023-03-29 | 12720 | keep | 0 | Mar | 2023 | 0.0086635 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-03-29 14:04 | 2023-03-29 16:10 | 17 | 2:06 | P | NO SE REPORTO CAUSA | 1 NX DE 15 AMPS | R23032900294 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2023-03-29 | 2142 | keep | 0 | Mar | 2023 | 0.0014589 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-03-29 14:04 | 2023-03-29 14:05 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23032900168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 3000 | keep | 0 | Mar | 2023 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2023-03-29 14:17 | 2023-03-29 17:27 | 80 | 3:10 | P | ANIMAL | 1X50 EN C/L 1X50 EN OTRO C/L CRUCE POR AVE | B23032900170 | New_Event | Animals | Include | Include | Wildlife | 190 | 2023-03-29 | 15200 | keep | 0 | Mar | 2023 | 0.010353 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-03-29 14:20 | 2023-03-29 16:22 | 25 | 2:02 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M23032900101 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-03-29 | 3050 | keep | 0 | Mar | 2023 | 0.0020773 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-03-29 14:35 | 2023-03-29 14:36 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 931 CLIENTES DEL 2402-02 | R23032900297 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 1648 | keep | 0 | Mar | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-03-29 14:35 | 2023-03-29 14:36 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 2302-03 | R23032900297 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-29 | 931 | keep | 0 | Mar | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
BAYAMON | 2023-03-29 14:36 | 2023-03-30 10:17 | 7 | 19:41 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR DESGANCHE SECUNDARIO | B23032900178 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1181 | 2023-03-29 | 8267 | keep | 0 | Mar | 2023 | 0.0056306 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-03-29 14:37 | 2023-03-29 17:23 | 2 | 2:46 | P | CONDUCTOR ROTO O ABIERTO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO HOT CLAMP EVENTO FUE TRANSFERIDO DE PONCE | P23032900095 | New_Event | Primary Wire Break | Include | Include | Equipment | 166 | 2023-03-29 | 332 | keep | 0 | Mar | 2023 | 0.00022612 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-03-29 14:40 | 2023-03-29 17:40 | 12 | 3:00 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A23032900166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-03-29 | 2160 | keep | 0 | Mar | 2023 | 0.0014712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-03-29 14:45 | 2023-03-29 18:38 | 152 | 3:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C23032900120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2023-03-29 | 35416 | keep | 0 | Mar | 2023 | 0.024122 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
AGUADILLA | 2023-03-29 14:46 | 2023-03-29 18:00 | 100 | 3:14 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23032900108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-03-29 | 19400 | keep | 0 | Mar | 2023 | 0.013213 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-03-29 14:49 | 2023-03-29 17:33 | 30 | 2:44 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR SE REALIZO DESGANCHE | B23032900180 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 164 | 2023-03-29 | 4920 | keep | 0 | Mar | 2023 | 0.003351 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-03-29 14:54 | 2023-03-29 16:36 | 10 | 1:42 | P | DESGANCHE | 1X15 EN XMR | B23032900183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-03-29 | 1020 | keep | 0 | Mar | 2023 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-03-29 14:55 | 2023-03-29 16:24 | 8 | 1:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23032900279 | New_Event | Secondary Wire Break | Include | Include | Equipment | 89 | 2023-03-29 | 712 | keep | 0 | Mar | 2023 | 0.00048494 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-03-29 15:07 | 2023-03-29 18:50 | 20 | 3:43 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23032900112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2023-03-29 | 4460 | keep | 0 | Mar | 2023 | 0.0030377 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-03-29 15:20 | 2023-03-29 15:21 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 931 CLIENTES DEL 2402-02 | R23032900300 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 1648 | keep | 0 | Mar | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-03-29 15:20 | 2023-03-29 15:21 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 2302-03 | R23032900300 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-29 | 931 | keep | 0 | Mar | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
CANOVANAS | 2023-03-29 15:45 | 2023-03-29 15:46 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 931 CLIENTES DEL 2402-02 | R23032900301 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 1648 | keep | 0 | Mar | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-03-29 15:45 | 2023-03-29 15:46 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 2302-03 | R23032900301 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-29 | 931 | keep | 0 | Mar | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
BAYAMON | 2023-03-29 15:46 | 2023-03-29 16:17 | 30 | 0:31 | P | ANIMAL | 1X65 EN C/L CRUCE POR AVE | B23032900191 | New_Event | Animals | Include | Include | Wildlife | 31 | 2023-03-29 | 930 | keep | 0 | Mar | 2023 | 0.00063342 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-03-29 16:05 | 2023-03-29 18:35 | 100 | 2:30 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEA ARRIADA SE INSTALO AISLACION | M23032900116 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 150 | 2023-03-29 | 15000 | keep | 0 | Mar | 2023 | 0.010216 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-03-29 16:31 | 2023-03-29 18:21 | 60 | 1:50 | P | DESGANCHE | 1 X 140 EN SALIDA CONVERTIDOR Y 1 X 100 EN CORTE DE LINEA DESGANCHE | P23032900107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-03-29 | 6600 | keep | 0 | Mar | 2023 | 0.0044952 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-29 16:39 | 2023-03-29 18:36 | 25 | 1:57 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | S23032900289 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-03-29 | 2925 | keep | 0 | Mar | 2023 | 0.0019922 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-03-29 16:40 | 2023-03-29 17:30 | 10 | 0:50 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR LINEAS CRUZADAS | A23032900189 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 50 | 2023-03-29 | 500 | keep | 0 | Mar | 2023 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-03-29 16:51 | 2023-03-29 16:52 | 1702 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C23032900144 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-29 | 1702 | keep | 0 | Mar | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-03-29 16:52 | 2023-03-29 19:00 | 99 | 2:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C23032900146 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 128 | 2023-03-29 | 12672 | keep | 0 | Mar | 2023 | 0.0086308 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
BAYAMON | 2023-03-29 17:01 | 2023-03-29 17:02 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23032900212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 2234 | keep | 0 | Mar | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2023-03-29 17:10 | 2023-03-29 18:49 | 15 | 1:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA | A23032900195 | New_Event | Cutout Failure | Include | Include | Equipment | 99 | 2023-03-29 | 1485 | keep | 0 | Mar | 2023 | 0.0010114 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-03-29 17:29 | 2023-03-30 12:40 | 1 | 19:11 | P | CAUSAS EXTERNAS | 1 X 15 EN TRANSFORMADOR SE RETIRO TENSOR CRUZANDO BAJANTES | M23032900128 | New_Event | Damage From Public | Include | Include | Public | 1151 | 2023-03-29 | 1151 | keep | 0 | Mar | 2023 | 0.00078394 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1